## All Data
Date | Time | Type | Concentrate Recirculation Flowrate Set Point (gpm) | CF IN Pressure (psi) | CF OUT Pressure (psi) | RO IN Feedwater Pressure (psi) | CF IN Feedwater pH | RO OUT Concentrate Pressure (psi) | CF Effluent EC (uS/cm) | CF Effluent Temperature (C) | RO Overall Permeate EC (uS/cm) | RO Overall Permeate pH | RO Overall Concentrate Flowrate (gpm) | RO Overall Permeate Flowrate (gpm) | RO Overall Concentrate EC (uS/cm) | CF Differential Pressure (psi) | Rejection (%) | Recovery (%) | CF Effluent EC (ppm) | RO Overall Permeate EC (ppm) | RO Overall Concentrate EC (ppm) | True Power (W) | Reactive Power (Var) | Apparent Power (VA) | Net Energy (kWh) | Power Factor | RO Overall Feed Flowrate/CF Effluent/Pilot Make-up Overall Flow (gpm)
2024-12-09 | 12:35 | Data | 0 | 37.213 | 37.301 | 27.185 | 0 | 26.009 | 0 | 25.42 | 0 | 0 | 0.118 | 0.335 | 0 | 0.128 | 0 | 73.8 | 0 | 0 | 0 | 1835.2 | 1754.5 | 2741.1 | 1182.8 | 0.6803 | 0.45
2024-12-09 | 12:35 | Data | 0 | 37.335 | 37.503 | 29.808 | 7.39 | 29.037 | 1866.41 | 25.66 | 43.651 | 6.16 | 0.353 | 0.485 | 5103.33 | 0.176 | 97.6 | 57.7 | 1224 | 22.28 | 3317.2 | 1818.2 | 1766.2 | 2732.2 | 1182.8 | 0.67404 | 0.84
2024-12-09 | 12:36 | Data | 0 | 35.62 | 34.796 | 55.365 | 7.53 | 51.091 | 1947.76 | 25.78 | 200.831 | 6.31 | 0.628 | 0.95 | 5243.52 | 0.824 | 89.7 | 60.2 | 1266 | 100.55 | 3408.3 | 1963.4 | 2248.1 | 3146.5 | 1182.8 | 0.59205 | 1.577
2024-12-09 | 12:36 | Data | 0 | 35.714 | 35.255 | 66.492 | 7.58 | 62.797 | 1943.24 | 25.82 | 408.387 | 6.69 | 0.815 | 1.574 | 5012.89 | 0.459 | 79 | 65.8 | 1263 | 204.64 | 3258.4 | 2032.6 | 2236.1 | 3191.3 | 1182.8 | 0.61755 | 2.383
2024-12-09 | 12:36 | Data | 0 | 35.485 | 34.857 | 74.634 | 7.63 | 70.796 | 1947.76 | 25.84 | 619.284 | 6.99 | 0.935 | 2.05 | 4705.38 | 0.628 | 68.2 | 68.7 | 1266 | 309.87 | 3058.5 | 2039.7 | 2248.8 | 3207.6 | 1182.8 | 0.6159 | 2.984
2024-12-09 | 12:36 | Data | 0 | 35.026 | 34.337 | 86.304 | 7.65 | 81.642 | 1954.99 | 25.89 | 728.524 | 7.16 | 0.972 | 2.216 | 4284.81 | 0.689 | 62.7 | 69.5 | 1270 | 364.53 | 2785.1 | 2119.1 | 2262.7 | 3260.5 | 1182.8 | 0.63532 | 3.187
2024-12-09 | 12:36 | Data | 0 | 34.121 | 33.183 | 99.24 | 7.65 | 93.528 | 1954.09 | 25.99 | 805.263 | 7.27 | 1.008 | 2.587 | 3895.9 | 0.925 | 58.8 | 71.9 | 1271 | 402.72 | 2532.3 | 2192.2 | 2320.3 | 3352.2 | 1182.8 | 0.63715 | 3.593
2024-12-09 | 12:36 | Data | 0 | 33.007 | 32.028 | 112.584 | 7.66 | 105.731 | 1965.84 | 26.07 | 785.221 | 7.35 | 1.059 | 2.923 | 3638.13 | 0.952 | 60.1 | 73.4 | 1278 | 392.57 | 2364.8 | 2278.3 | 2363.3 | 3432.4 | 1182.8 | 0.64892 | 3.981
2024-12-09 | 12:36 | Data | 0 | 31.569 | 30.388 | 126.832 | 7.67 | 118.837 | 1972.16 | 26.12 | 662.529 | 7.39 | 1.102 | 3.272 | 3579.34 | 1.208 | 66.5 | 74.8 | 1283 | 330.27 | 2326.6 | 2409.8 | 2419.4 | 3563.2 | 1182.9 | 0.66283 | 4.373
2024-12-09 | 12:36 | Data | 0 | 29.955 | 28.342 | 142.392 | 7.67 | 133.163 | 1973.97 | 26.16 | 591.026 | 7.4 | 1.147 | 3.633 | 3624.56 | 1.614 | 70.2 | 76 | 1283 | 294.52 | 2356 | 2563.8 | 2516.5 | 3731.5 | 1182.9 | 0.67076 | 4.778
2024-12-09 | 12:36 | Data | 0 | 29.044 | 27.214 | 159.625 | 7.67 | 148.891 | 1976.68 | 26.18 | 487.203 | 7.36 | 1.211 | 4.029 | 3877.81 | 1.884 | 75.5 | 76.9 | 1285 | 241.57 | 2520.6 | 2703.6 | 2600.8 | 3892.4 | 1182.9 | 0.68397 | 5.238
2024-12-09 | 12:36 | Data | 0 | 28.922 | 26.418 | 178.352 | 7.67 | 166.064 | 1979.39 | 26.18 | 382.838 | 7.33 | 1.271 | 4.408 | 4248.63 | 2.16 | 80.8 | 77.6 | 1287 | 190.34 | 2761.6 | 2906.2 | 2777.3 | 4120 | 1182.9 | 0.68514 | 5.676
2024-12-09 | 12:36 | Data | 0 | 27.876 | 25.236 | 198.571 | 7.67 | 184.142 | 1979.39 | 26.17 | 309.349 | 7.24 | 1.324 | 4.845 | 4623.98 | 2.741 | 84.6 | 78.5 | 1287 | 152.24 | 3005.6 | 3101.9 | 2979.5 | 4409.7 | 1182.9 | 0.6876 | 6.167
2024-12-09 | 12:36 | Data | 0 | 27.89 | 25.554 | 201.239 | 7.67 | 186.808 | 1980.3 | 26.16 | 231.436 | 7.14 | 1.378 | 5.215 | 5202.82 | 2.505 | 88.4 | 79.1 | 1287 | 113.55 | 3381.8 | 3151.2 | 3037.7 | 4487.2 | 1182.9 | 0.68604 | 6.594
2024-12-09 | 12:36 | Data | 0 | 29.037 | 26.31 | 195.811 | 7.68 | 182.153 | 1979.39 | 26.15 | 172.211 | 7.03 | 1.41 | 5.279 | 5510.33 | 2.484 | 91.4 | 78.9 | 1287 | 85.02 | 3581.7 | 3092.7 | 2985.6 | 4412.1 | 1182.9 | 0.68474 | 6.69
2024-12-09 | 12:36 | Data | 0 | 29.267 | 26.654 | 190.7 | 7.68 | 177.588 | 1978.49 | 26.12 | 131.946 | 6.92 | 1.395 | 5.158 | 5704.79 | 2.444 | 93.4 | 78.7 | 1286 | 65.39 | 3708.1 | 3025.3 | 2901.1 | 4302.2 | 1182.9 | 0.6877 | 6.555
2024-12-09 | 12:36 | Data | 0 | 29.436 | 27.309 | 186.629 | 7.67 | 173.973 | 1976.68 | 26.12 | 111.091 | 6.81 | 1.362 | 5.036 | 5759.06 | 2.295 | 94.4 | 78.7 | 1285 | 55.55 | 3743.4 | 2994.2 | 2873.1 | 4266.7 | 1182.9 | 0.68532 | 6.399
2024-12-09 | 12:36 | Data | 0 | 29.037 | 27.127 | 183.553 | 7.68 | 171.035 | 1973.07 | 26.12 | 90.597 | 6.72 | 1.349 | 4.928 | 5763.58 | 2.127 | 95.4 | 78.5 | 1282 | 45.3 | 3746.3 | 2944.7 | 2810.1 | 4189.5 | 1182.9 | 0.68748 | 6.277
2024-12-09 | 12:36 | Data | 0 | 28.875 | 26.796 | 181.473 | 7.68 | 169.273 | 1974.87 | 26.1 | 77.597 | 6.65 | 1.346 | 4.872 | 5826.89 | 2.019 | 96.1 | 78.4 | 1284 | 38.8 | 3787.5 | 2914.8 | 2802 | 4163.4 | 1182.9 | 0.68368 | 6.217
2024-12-09 | 12:36 | Data | 0 | 29.321 | 27.194 | 179.799 | 7.68 | 168.053 | 1971.26 | 26.11 | 68.298 | 6.59 | 1.342 | 4.8 | 5958.03 | 1.911 | 96.5 | 78.1 | 1281 | 34.01 | 3872.7 | 2909.4 | 2808.9 | 4162.5 | 1182.9 | 0.68257 | 6.142
2024-12-09 | 12:37 | Data | 0 | 29.611 | 27.647 | 179.121 | 7.67 | 167.284 | 1971.26 | 26.1 | 61.527 | 6.54 | 1.34 | 4.756 | 6102.74 | 2.127 | 96.9 | 78 | 1281 | 30.76 | 3966.8 | 2877 | 2766.6 | 4111.4 | 1182.9 | 0.68318 | 6.096
2024-12-09 | 12:37 | Data | 0 | 30.212 | 28.342 | 178.668 | 7.68 | 166.923 | 1971.26 | 26.11 | 56.832 | 6.5 | 1.323 | 4.747 | 6279.11 | 1.857 | 97.1 | 78.2 | 1281 | 28.42 | 4081.4 | 2862.8 | 2769.4 | 4130.2 | 1182.9 | 0.68181 | 6.071
2024-12-09 | 12:37 | Data | 0 | 29.949 | 27.674 | 178.171 | 7.68 | 166.471 | 1970.35 | 26.1 | 53.762 | 6.47 | 1.317 | 4.723 | 6414.78 | 2.268 | 97.3 | 78.2 | 1281 | 26.88 | 4169.6 | 2892.1 | 2719.9 | 4081.6 | 1182.9 | 0.69344 | 6.04
2024-12-09 | 12:37 | Data | 0 | 29.982 | 27.802 | 178.261 | 7.68 | 166.516 | 1967.64 | 26.11 | 51.596 | 6.45 | 1.32 | 4.689 | 6600.19 | 2.073 | 97.4 | 78 | 1279 | 25.8 | 4290.1 | 2878.5 | 2742.3 | 4092.5 | 1182.9 | 0.68179 | 6.009
2024-12-09 | 12:37 | Data | 0 | 30.415 | 28.443 | 178.578 | 7.68 | 166.742 | 1971.26 | 26.1 | 50.151 | 6.43 | 1.328 | 4.69 | 6735.86 | 2.086 | 97.5 | 77.9 | 1281 | 25.08 | 4378.3 | 2867.9 | 2774.7 | 4111 | 1182.9 | 0.67975 | 6.017
2024-12-09 | 12:37 | Data | 0 | 30.644 | 28.571 | 178.668 | 7.68 | 167.058 | 1972.16 | 26.1 | 49.61 | 6.42 | 1.32 | 4.716 | 6903.18 | 2.073 | 97.5 | 78.1 | 1281 | 24.8 | 4487.1 | 2865.3 | 2754.6 | 4097.8 | 1182.9 | 0.68183 | 6.035
2024-12-09 | 12:37 | Data | 0 | 29.969 | 28.227 | 178.352 | 7.68 | 166.697 | 1968.55 | 26.13 | 49.339 | 6.41 | 1.317 | 4.732 | 7043.37 | 1.931 | 97.5 | 78.3 | 1280 | 24.58 | 4578.2 | 2870.8 | 2764.8 | 4104.6 | 1182.9 | 0.68407 | 6.047
2024-12-09 | 12:37 | Data | 0 | 30.631 | 28.571 | 178.623 | 7.68 | 167.013 | 1967.64 | 26.12 | 48.797 | 6.4 | 1.307 | 4.702 | 7160.95 | 2.079 | 97.5 | 78.2 | 1278 | 24.4 | 4654.6 | 2871.7 | 2750.6 | 4094.3 | 1182.9 | 0.68663 | 6.009
2024-12-09 | 12:37 | Data | 0 | 30.475 | 28.247 | 178.759 | 7.67 | 167.104 | 1967.64 | 26.11 | 49.068 | 6.39 | 1.305 | 4.692 | 7246.87 | 2.073 | 97.5 | 78.2 | 1280 | 24.53 | 4710.5 | 2851.1 | 2745.4 | 4095.4 | 1182.9 | 0.68423 | 5.996
2024-12-09 | 12:37 | Data | 0 | 30.88 | 28.774 | 178.849 | 7.68 | 167.284 | 1965.84 | 26.13 | 48.978 | 6.39 | 1.315 | 4.716 | 7332.79 | 1.992 | 97.5 | 78.2 | 1278 | 24.49 | 4766.3 | 2854.7 | 2740.1 | 4075.8 | 1182.9 | 0.68469 | 6.031
2024-12-09 | 12:37 | Data | 0 | 30.813 | 28.794 | 178.985 | 7.68 | 167.375 | 1965.84 | 26.13 | 48.978 | 6.38 | 1.32 | 4.697 | 7382.54 | 2.255 | 97.5 | 78 | 1277 | 24.44 | 4798.6 | 2859.9 | 2733.9 | 4073 | 1182.9 | 0.68317 | 6.016
2024-12-09 | 12:37 | Data | 0 | 31.13 | 29.037 | 179.121 | 7.68 | 167.42 | 1963.12 | 26.13 | 48.707 | 6.37 | 1.324 | 4.687 | 7427.76 | 2.093 | 97.5 | 78 | 1276 | 24.26 | 4828 | 2855.5 | 2729.4 | 4076.3 | 1182.9 | 0.68391 | 6.01
2024-12-09 | 12:37 | Data | 0 | 31.11 | 29.031 | 179.166 | 7.68 | 167.555 | 1961.32 | 26.11 | 49.068 | 6.38 | 1.319 | 4.716 | 7477.5 | 2.1 | 97.5 | 78.2 | 1275 | 24.53 | 4860.4 | 2853.1 | 2745.6 | 4083.8 | 1182.9 | 0.68243 | 6.036
2024-12-09 | 12:37 | Data | 0 | 30.894 | 28.767 | 179.03 | 7.68 | 167.465 | 1960.41 | 26.12 | 49.068 | 6.38 | 1.317 | 4.732 | 7509.16 | 2.167 | 97.5 | 78.2 | 1275 | 24.53 | 4881 | 2863.5 | 2747 | 4096.2 | 1182.9 | 0.68126 | 6.049
2024-12-09 | 12:37 | Data | 0 | 30.88 | 28.821 | 178.895 | 7.68 | 167.239 | 1964.93 | 26.11 | 48.978 | 6.37 | 1.319 | 4.718 | 7576.99 | 2.113 | 97.5 | 78.2 | 1276 | 24.49 | 4925 | 2841.6 | 2772.3 | 4087.2 | 1182.9 | 0.67915 | 6.037
2024-12-09 | 12:37 | Data | 0 | 30.489 | 28.477 | 178.804 | 7.68 | 167.149 | 1955.89 | 26.11 | 49.068 | 6.37 | 1.314 | 4.71 | 7622.21 | 1.944 | 97.5 | 78.1 | 1271 | 24.53 | 4954.4 | 2849.1 | 2741.8 | 4086.6 | 1182.9 | 0.68259 | 6.026
2024-12-09 | 12:37 | Data | 0 | 31.164 | 29.051 | 178.985 | 7.67 | 167.42 | 1961.32 | 26.11 | 48.978 | 6.36 | 1.326 | 4.724 | 7662.91 | 1.938 | 97.5 | 78.1 | 1275 | 24.53 | 4980.9 | 2836.5 | 2739.1 | 4067.2 | 1182.9 | 0.68119 | 6.05
2024-12-09 | 12:37 | Data | 0 | 31.171 | 29.044 | 178.985 | 7.67 | 167.329 | 1956.8 | 26.11 | 49.068 | 6.37 | 1.32 | 4.74 | 7694.57 | 1.87 | 97.5 | 78.2 | 1272 | 24.53 | 5001.5 | 2864.6 | 2725.4 | 4075 | 1182.9 | 0.6854 | 6.059
2024-12-09 | 12:38 | Data | 0 | 31.225 | 29.307 | 179.121 | 7.68 | 167.375 | 1963.12 | 26.11 | 49.068 | 6.36 | 1.326 | 4.708 | 7730.75 | 2.079 | 97.5 | 78 | 1276 | 24.49 | 5025 | 2844.3 | 2742.4 | 4073.4 | 1182.9 | 0.68304 | 6.034
2024-12-09 | 12:38 | Data | 0 | 31.11 | 29.24 | 179.075 | 7.67 | 167.51 | 1965.84 | 26.1 | 49.068 | 6.36 | 1.331 | 4.704 | 7762.4 | 2.019 | 97.5 | 77.9 | 1278 | 24.58 | 5045.6 | 2853.6 | 2753.6 | 4089.7 | 1182.9 | 0.68011 | 6.036
2024-12-09 | 12:38 | Data | 0 | 31.117 | 29.213 | 179.211 | 7.67 | 167.601 | 1968.55 | 26.1 | 49.248 | 6.36 | 1.314 | 4.712 | 7798.58 | 1.951 | 97.5 | 78.2 | 1280 | 24.67 | 5069.1 | 2854.7 | 2759.4 | 4095 | 1182.9 | 0.68051 | 6.027
2024-12-09 | 12:38 | Data | 0 | 31.65 | 29.706 | 179.256 | 7.67 | 167.601 | 1967.64 | 26.11 | 49.339 | 6.37 | 1.321 | 4.733 | 7812.15 | 2.086 | 97.5 | 78.2 | 1280 | 24.62 | 5077.9 | 2847.5 | 2745.5 | 4078.9 | 1182.9 | 0.68351 | 6.054
2024-12-09 | 12:38 | Data | 0 | 31.481 | 29.267 | 179.075 | 7.67 | 167.42 | 1967.64 | 26.12 | 49.248 | 6.37 | 1.327 | 4.74 | 7830.24 | 1.958 | 97.5 | 78.1 | 1279 | 24.67 | 5089.7 | 2835 | 2735.9 | 4066.3 | 1182.9 | 0.68105 | 6.067
2024-12-09 | 12:38 | Data | 0 | 31.346 | 29.294 | 178.849 | 7.67 | 167.194 | 1970.35 | 26.11 | 49.248 | 6.37 | 1.315 | 4.707 | 7848.32 | 1.965 | 97.5 | 78.2 | 1281 | 24.67 | 5101.4 | 2844.6 | 2753 | 4079.8 | 1182.9 | 0.68042 | 6.022
2024-12-09 | 12:38 | Data | 0 | 31.414 | 29.496 | 178.94 | 7.67 | 167.284 | 1976.68 | 26.1 | 49.339 | 6.36 | 1.308 | 4.703 | 7866.41 | 1.863 | 97.5 | 78.2 | 1285 | 24.67 | 5113.2 | 2850.5 | 2746.1 | 4077.7 | 1182.9 | 0.68293 | 6.012
2024-12-09 | 12:38 | Data | 0 | 31.792 | 29.726 | 178.985 | 7.67 | 167.375 | 1977.58 | 26.11 | 49.339 | 6.37 | 1.329 | 4.71 | 7893.55 | 2.073 | 97.5 | 78 | 1285 | 24.67 | 5130.8 | 2840 | 2749.8 | 4072.5 | 1183 | 0.67946 | 6.04
2024-12-09 | 12:38 | Data | 0 | 31.67 | 29.78 | 178.985 | 7.67 | 167.42 | 1977.58 | 26.09 | 49.248 | 6.36 | 1.327 | 4.709 | 7907.11 | 2.187 | 97.5 | 78 | 1285 | 24.53 | 5139.6 | 2852 | 2749.2 | 4083.2 | 1183 | 0.68171 | 6.036
2024-12-09 | 12:38 | Data | 0 | 31.994 | 29.53 | 179.121 | 7.67 | 167.465 | 1974.87 | 26.1 | 49.068 | 6.37 | 1.315 | 4.691 | 7920.68 | 2.262 | 97.5 | 78.1 | 1285 | 24.49 | 5148.4 | 2838.9 | 2759.5 | 4084.5 | 1183 | 0.67904 | 6.008
2024-12-09 | 12:38 | Data | 0 | 32.136 | 29.793 | 179.03 | 7.67 | 167.51 | 1977.58 | 26.11 | 48.978 | 6.36 | 1.327 | 4.711 | 7527.25 | 2.073 | 97.5 | 78 | 1285 | 24.49 | 4892.7 | 2837.4 | 2749.4 | 4076.6 | 1183 | 0.67879 | 6.036
2024-12-09 | 12:38 | Data | 0 | 32.028 | 29.955 | 179.166 | 7.67 | 167.646 | 2078.81 | 26.1 | 49.158 | 6.37 | 1.329 | 4.733 | 7934.25 | 2.073 | 97.6 | 78.1 | 1351 | 24.53 | 5157.3 | 2852.2 | 2761.2 | 4091.1 | 1183 | 0.6797 | 6.062
2024-12-09 | 12:38 | Data | 0 | 32.096 | 29.962 | 179.392 | 7.67 | 167.827 | 2070.68 | 26.11 | 49.068 | 6.37 | 1.328 | 4.743 | 7943.29 | 1.971 | 97.6 | 78.1 | 1347 | 24.49 | 5163.1 | 2834.7 | 2742 | 4063.2 | 1183 | 0.6809 | 6.072
2024-12-09 | 12:38 | Data | 0 | 32.15 | 30.009 | 179.121 | 7.67 | 167.555 | 1974.87 | 26.11 | 48.978 | 6.36 | 1.325 | 4.716 | 7961.38 | 2.187 | 97.5 | 78.1 | 1283 | 24.53 | 5174.9 | 2859.7 | 2751.1 | 4085.7 | 1183 | 0.68343 | 6.041
2024-12-09 | 12:38 | Data | 0 | 32.001 | 30.246 | 179.121 | 7.67 | 167.465 | 1973.07 | 26.11 | 49.158 | 6.37 | 1.331 | 4.726 | 7956.86 | 2.181 | 97.5 | 78 | 1282 | 24.58 | 5172 | 2857.8 | 2740.1 | 4080.8 | 1183 | 0.68409 | 6.057
2024-12-09 | 12:38 | Data | 0 | 32.204 | 30.178 | 179.03 | 7.67 | 167.465 | 1968.55 | 26.11 | 48.797 | 6.36 | 1.326 | 4.726 | 7974.95 | 2.079 | 97.5 | 78.1 | 1280 | 24.35 | 5183.7 | 2852 | 2742.4 | 4078.2 | 1183 | 0.68251 | 6.052
2024-12-09 | 12:38 | Data | 0 | 32.264 | 30.185 | 179.211 | 7.66 | 167.601 | 1973.07 | 26.11 | 48.797 | 6.36 | 1.324 | 4.737 | 7970.42 | 2.079 | 97.5 | 78.2 | 1282 | 24.4 | 5180.8 | 2871.4 | 2755.8 | 4086 | 1183 | 0.68243 | 6.06
2024-12-09 | 12:38 | Data | 0 | 32.264 | 30.516 | 178.759 | 7.67 | 167.194 | 1973.97 | 26.12 | 48.797 | 6.36 | 1.329 | 4.729 | 7956.86 | 1.992 | 97.5 | 78.1 | 1282 | 24.44 | 5172 | 2847.6 | 2741.8 | 4074.7 | 1183 | 0.68027 | 6.06
2024-12-09 | 12:39 | Data | 0 | 32.318 | 30.307 | 178.759 | 7.67 | 167.194 | 1973.07 | 26.1 | 48.707 | 6.36 | 1.326 | 4.711 | 7956.86 | 2.079 | 97.5 | 78 | 1283 | 24.44 | 5172 | 2845.1 | 2765.4 | 4084.1 | 1183 | 0.68024 | 6.038
2024-12-09 | 12:39 | Data | 0 | 32.521 | 30.442 | 178.759 | 7.67 | 167.194 | 1973.07 | 26.11 | 48.797 | 6.36 | 1.32 | 4.714 | 7961.38 | 2.039 | 97.5 | 78.1 | 1282 | 24.4 | 5174.9 | 2817.7 | 2749.1 | 4066.4 | 1183 | 0.68049 | 6.035
2024-12-09 | 12:39 | Data | 0 | 32.278 | 30.415 | 178.668 | 7.66 | 167.149 | 1973.97 | 26.13 | 48.707 | 6.36 | 1.32 | 4.698 | 7961.38 | 1.857 | 97.5 | 78.1 | 1283 | 24.35 | 5174.9 | 2851.7 | 2748.3 | 4086.2 | 1183 | 0.68179 | 6.017
2024-12-09 | 12:39 | Data | 0 | 32.467 | 30.408 | 178.714 | 7.67 | 167.194 | 1976.68 | 26.11 | 48.707 | 6.36 | 1.326 | 4.709 | 8002.08 | 2.079 | 97.5 | 78 | 1284 | 24.4 | 5201.4 | 2840.1 | 2739.5 | 4067.4 | 1183 | 0.68207 | 6.035
2024-12-09 | 12:39 | Data | 0 | 32.723 | 30.536 | 178.804 | 7.67 | 167.329 | 1980.3 | 26.11 | 48.797 | 6.36 | 1.319 | 4.727 | 8002.08 | 2.079 | 97.5 | 78.2 | 1287 | 24.35 | 5201.4 | 2847.5 | 2749.2 | 4078.5 | 1183 | 0.6801 | 6.045
2024-12-09 | 12:39 | Data | 0 | 32.804 | 30.685 | 178.94 | 7.66 | 167.284 | 1978.49 | 26.12 | 48.436 | 6.35 | 1.317 | 4.675 | 8002.08 | 2.113 | 97.6 | 78 | 1287 | 24.22 | 5201.4 | 2841.4 | 2756.9 | 4083.3 | 1183 | 0.68024 | 5.993
2024-12-09 | 12:39 | Data | 0 | 32.703 | 30.651 | 178.94 | 7.67 | 167.284 | 1979.39 | 26.11 | 48.436 | 6.35 | 1.311 | 4.693 | 8006.6 | 2.079 | 97.6 | 78.2 | 1287 | 24.22 | 5204.3 | 2820.4 | 2748.1 | 4062.1 | 1183 | 0.67698 | 6.004
2024-12-09 | 12:39 | Data | 0 | 32.494 | 30.442 | 178.714 | 7.66 | 167.194 | 1979.39 | 26.12 | 48.436 | 6.36 | 1.312 | 4.703 | 7993.04 | 1.978 | 97.6 | 78.2 | 1287 | 24.22 | 5195.5 | 2842.8 | 2726.8 | 4060.8 | 1183 | 0.68137 | 6.016
2024-12-09 | 12:39 | Data | 0 | 32.723 | 30.428 | 178.849 | 7.66 | 167.284 | 1980.3 | 26.13 | 48.436 | 6.36 | 1.321 | 4.659 | 7983.99 | 2.079 | 97.6 | 77.9 | 1287 | 24.22 | 5189.6 | 2844.4 | 2719.2 | 4054.2 | 1183 | 0.68441 | 5.981
2024-12-09 | 12:39 | Data | 0 | 32.318 | 30.408 | 178.714 | 7.66 | 167.239 | 1978.49 | 26.12 | 48.436 | 6.35 | 1.31 | 4.69 | 7997.56 | 1.87 | 97.5 | 78.2 | 1285 | 24.22 | 5198.4 | 2846.1 | 2742.9 | 4069.1 | 1183 | 0.68263 | 6.001
2024-12-09 | 12:39 | Data | 0 | 32.683 | 30.806 | 178.759 | 7.67 | 167.194 | 1979.39 | 26.12 | 48.526 | 6.36 | 1.312 | 4.715 | 8015.65 | 2.127 | 97.6 | 78.2 | 1287 | 24.22 | 5210.2 | 2833.6 | 2755.4 | 4073.7 | 1183 | 0.67925 | 6.027
2024-12-09 | 12:39 | Data | 0 | 32.494 | 30.529 | 178.849 | 7.66 | 167.194 | 1980.3 | 26.11 | 48.526 | 6.35 | 1.317 | 4.727 | 8015.65 | 2.079 | 97.6 | 78.2 | 1287 | 24.22 | 5210.2 | 2825.4 | 2769.4 | 4075.8 | 1183 | 0.67617 | 6.042
2024-12-09 | 12:39 | Data | 0 | 32.264 | 30.388 | 178.714 | 7.66 | 167.194 | 1979.39 | 26.12 | 48.436 | 6.36 | 1.311 | 4.686 | 8015.65 | 2.079 | 97.6 | 78.1 | 1286 | 24.17 | 5210.2 | 2836.2 | 2751.1 | 4073.1 | 1183 | 0.67958 | 5.997
2024-12-09 | 12:39 | Data | 0 | 32.332 | 30.415 | 178.714 | 7.67 | 167.239 | 1979.39 | 26.13 | 48.436 | 6.36 | 1.32 | 4.666 | 8169.4 | 1.877 | 97.6 | 77.9 | 1287 | 24.22 | 5310.1 | 2837.8 | 2748.9 | 4072.1 | 1183 | 0.68089 | 5.988
2024-12-09 | 12:39 | Data | 0 | 32.46 | 30.401 | 178.668 | 7.67 | 167.194 | 1979.39 | 26.12 | 48.165 | 6.36 | 1.327 | 4.689 | 8205.58 | 2.086 | 97.6 | 77.9 | 1287 | 24.08 | 5333.6 | 2831 | 2764.1 | 4081.8 | 1183 | 0.67829 | 6.016
2024-12-09 | 12:39 | Data | 0 | 32.555 | 30.421 | 178.849 | 7.66 | 167.329 | 1976.68 | 26.12 | 48.075 | 6.36 | 1.323 | 4.711 | 8196.54 | 1.958 | 97.6 | 78.1 | 1285 | 24.04 | 5327.7 | 2822.8 | 2766.1 | 4073.4 | 1183 | 0.67724 | 6.034
2024-12-09 | 12:40 | Data | 0 | 32.298 | 30.192 | 178.759 | 7.66 | 167.284 | 1976.68 | 26.11 | 48.165 | 6.35 | 1.32 | 4.702 | 8210.1 | 2.079 | 97.6 | 78.1 | 1285 | 24.13 | 5336.6 | 2843.3 | 2756.1 | 4078.8 | 1183 | 0.68008 | 6.022
2024-12-09 | 12:40 | Data | 0 | 32.696 | 30.529 | 178.849 | 7.66 | 167.329 | 1980.3 | 26.12 | 48.255 | 6.35 | 1.317 | 4.686 | 8038.26 | 2.073 | 97.6 | 78.1 | 1287 | 24.08 | 5224.9 | 2839.4 | 2764.1 | 4086.9 | 1183 | 0.67886 | 6.002
2024-12-09 | 12:40 | Data | 0 | 32.501 | 30.597 | 178.804 | 7.66 | 167.284 | 1980.3 | 26.1 | 48.165 | 6.35 | 1.321 | 4.689 | 7997.56 | 1.958 | 97.6 | 78 | 1287 | 24.08 | 5198.4 | 2851.3 | 2767.5 | 4099.4 | 1183 | 0.6788 | 6.01
2024-12-09 | 12:40 | Data | 0 | 32.703 | 30.469 | 178.714 | 7.66 | 167.239 | 1979.39 | 26.11 | 48.165 | 6.35 | 1.317 | 4.673 | 8006.6 | 2.073 | 97.6 | 78 | 1286 | 24.08 | 5204.3 | 2834.6 | 2767.9 | 4085.5 | 1183 | 0.67677 | 5.983
2024-12-09 | 12:40 | Data | 0 | 32.649 | 30.428 | 178.759 | 7.66 | 167.284 | 1980.3 | 26.11 | 48.165 | 6.35 | 1.317 | 4.692 | 7635.78 | 2.167 | 97.6 | 78.1 | 1287 | 24.04 | 4963.3 | 2833.8 | 2789.4 | 4096.3 | 1183 | 0.67541 | 6.008
2024-12-09 | 12:40 | Data | 0 | 32.264 | 30.455 | 178.849 | 7.66 | 167.194 | 1977.58 | 26.12 | 48.165 | 6.35 | 1.32 | 4.683 | 8137.75 | 1.789 | 97.6 | 78 | 1286 | 24.13 | 5289.5 | 2840.6 | 2760.7 | 4108 | 1183 | 0.67954 | 6.003
2024-12-09 | 12:40 | Data | 0 | 32.717 | 30.421 | 178.849 | 7.66 | 167.329 | 1977.58 | 26.12 | 47.984 | 6.35 | 1.327 | 4.683 | 8214.63 | 2.1 | 97.6 | 77.9 | 1285 | 24.13 | 5339.5 | 2837.5 | 2762.6 | 4077.2 | 1183 | 0.67934 | 6.011
2024-12-09 | 12:40 | Data | 0 | 32.406 | 30.415 | 178.714 | 7.67 | 167.329 | 1973.07 | 26.12 | 48.165 | 6.35 | 1.306 | 4.709 | 8196.54 | 1.863 | 97.6 | 78.3 | 1283 | 24.08 | 5327.7 | 2850.3 | 2809.8 | 4126.7 | 1183 | 0.67387 | 6.016
2024-12-09 | 12:40 | Data | 0 | 32.48 | 30.806 | 178.804 | 7.66 | 167.284 | 1973.97 | 26.12 | 48.165 | 6.34 | 1.315 | 4.702 | 8187.49 | 2.012 | 97.6 | 78.1 | 1282 | 24.08 | 5321.9 | 2834.8 | 2798 | 4100.4 | 1183 | 0.67687 | 6.017
2024-12-09 | 12:40 | Data | 0 | 32.636 | 30.415 | 178.985 | 7.66 | 167.329 | 1973.07 | 26.11 | 48.165 | 6.34 | 1.326 | 4.721 | 7870.94 | 2.127 | 97.6 | 78.1 | 1282 | 24.04 | 5116.1 | 2813.1 | 2798.4 | 4090.5 | 1183.1 | 0.67027 | 6.046
2024-12-09 | 12:40 | Data | 0 | 32.69 | 30.475 | 178.804 | 7.66 | 167.329 | 1973.07 | 26.13 | 48.255 | 6.35 | 1.324 | 4.692 | 7780.49 | 2.066 | 97.6 | 78 | 1282 | 24.08 | 5057.3 | 2844.8 | 2812.9 | 4120.2 | 1183.1 | 0.67434 | 6.016
2024-12-09 | 12:40 | Data | 0 | 32.494 | 30.428 | 178.804 | 7.66 | 167.239 | 1973.07 | 26.13 | 48.165 | 6.35 | 1.324 | 4.649 | 7794.06 | 2.066 | 97.6 | 77.8 | 1282 | 23.99 | 5066.1 | 2850.2 | 2805.2 | 4117.6 | 1183.1 | 0.67384 | 5.972
2024-12-09 | 12:40 | Data | 0 | 32.75 | 30.307 | 178.895 | 7.66 | 167.284 | 1973.97 | 26.12 | 48.165 | 6.35 | 1.324 | 4.653 | 7812.15 | 2.073 | 97.6 | 77.9 | 1284 | 24.08 | 5077.9 | 2834.4 | 2761.2 | 4077.9 | 1183.1 | 0.678 | 5.974
2024-12-09 | 12:40 | Data | 0 | 32.271 | 30.198 | 178.759 | 7.66 | 167.239 | 1973.97 | 26.13 | 48.075 | 6.34 | 1.323 | 4.663 | 7839.28 | 2.025 | 97.6 | 77.9 | 1283 | 24.04 | 5095.5 | 2825.6 | 2766.5 | 4078.3 | 1183.1 | 0.67858 | 5.986
2024-12-09 | 12:40 | Data | 0 | 32.494 | 30.415 | 178.759 | 7.66 | 167.329 | 1980.3 | 26.11 | 48.165 | 6.35 | 1.317 | 4.686 | 7852.85 | 2.079 | 97.6 | 78.1 | 1286 | 24.08 | 5104.3 | 2837.7 | 2759.2 | 4080.9 | 1183.1 | 0.67923 | 6.002
2024-12-09 | 12:40 | Data | 0 | 32.44 | 30.59 | 178.759 | 7.66 | 167.239 | 1973.07 | 26.12 | 48.255 | 6.35 | 1.317 | 4.707 | 8110.61 | 2.1 | 97.6 | 78.1 | 1283 | 24.13 | 5271.9 | 2832.4 | 2730 | 4056.2 | 1183.1 | 0.68001 | 6.024
2024-12-09 | 12:40 | Data | 0 | 32.723 | 30.428 | 178.895 | 7.66 | 167.284 | 1973.97 | 26.11 | 48.075 | 6.35 | 1.325 | 4.699 | 8164.88 | 2.1 | 97.6 | 78 | 1283 | 24.08 | 5307.2 | 2840.4 | 2743.6 | 4069 | 1183.1 | 0.68228 | 6.024
2024-12-09 | 12:40 | Data | 0 | 32.19 | 30.394 | 178.94 | 7.66 | 167.329 | 1973.07 | 26.12 | 48.165 | 6.35 | 1.32 | 4.717 | 8155.84 | 1.776 | 97.6 | 78.1 | 1282 | 24.08 | 5301.3 | 2822.5 | 2752.4 | 4069.6 | 1183.1 | 0.67671 | 6.037
2024-12-09 | 12:41 | Data | 0 | 32.48 | 30.415 | 178.849 | 7.66 | 167.239 | 1973.07 | 26.12 | 48.255 | 6.34 | 1.325 | 4.693 | 8182.97 | 2.079 | 97.6 | 78 | 1283 | 24.13 | 5318.9 | 2851.3 | 2759.1 | 4088.2 | 1183.1 | 0.68088 | 6.018
2024-12-09 | 12:41 | Data | 0 | 32.561 | 30.597 | 179.03 | 7.66 | 167.329 | 1977.58 | 26.12 | 48.165 | 6.34 | 1.32 | 4.718 | 8182.97 | 1.971 | 97.6 | 78.1 | 1285 | 24.13 | 5318.9 | 2845.7 | 2764.7 | 4089.3 | 1183.1 | 0.67946 | 6.036
2024-12-09 | 12:41 | Data | 0 | 32.811 | 30.543 | 178.849 | 7.66 | 167.375 | 1979.39 | 26.1 | 48.165 | 6.35 | 1.321 | 4.712 | 8182.97 | 2.066 | 97.6 | 78.1 | 1287 | 24.08 | 5318.9 | 2831.2 | 2742.5 | 4068.1 | 1183.1 | 0.67976 | 6.035
2024-12-09 | 12:41 | Data | 0 | 32.501 | 30.415 | 178.714 | 7.66 | 167.329 | 1979.39 | 26.13 | 48.075 | 6.34 | 1.324 | 4.702 | 8178.45 | 2.079 | 97.6 | 78 | 1287 | 23.95 | 5316 | 2825.1 | 2749.1 | 4067.2 | 1183.1 | 0.67687 | 6.026
2024-12-09 | 12:41 | Data | 0 | 32.575 | 30.442 | 178.714 | 7.66 | 167.284 | 1980.3 | 26.13 | 48.165 | 6.34 | 1.317 | 4.702 | 8169.4 | 2.187 | 97.6 | 78.1 | 1285 | 24.08 | 5310.1 | 2845.2 | 2753.7 | 4081.2 | 1183.1 | 0.68004 | 6.02
2024-12-09 | 12:41 | Data | 0 | 32.528 | 30.435 | 178.849 | 7.66 | 167.375 | 1983.01 | 26.12 | 48.075 | 6.35 | 1.321 | 4.682 | 8164.88 | 1.843 | 97.6 | 78 | 1288 | 23.95 | 5307.2 | 2839.2 | 2750.3 | 4074.8 | 1183.1 | 0.68041 | 6.002
2024-12-09 | 12:41 | Data | 0 | 32.723 | 30.428 | 178.94 | 7.66 | 167.42 | 1980.3 | 26.12 | 48.165 | 6.34 | 1.31 | 4.679 | 8146.79 | 1.978 | 97.6 | 78.1 | 1288 | 24.08 | 5295.4 | 2843.9 | 2762.1 | 4089.7 | 1183.1 | 0.67898 | 5.99
2024-12-09 | 12:41 | Data | 0 | 32.487 | 30.428 | 178.759 | 7.66 | 167.239 | 1987.53 | 26.12 | 48.165 | 6.34 | 1.31 | 4.681 | 8142.27 | 2.127 | 97.6 | 78.1 | 1292 | 24.08 | 5292.5 | 2845.6 | 2775.9 | 4098.5 | 1183.1 | 0.67863 | 5.991
2024-12-09 | 12:41 | Data | 0 | 32.264 | 30.361 | 178.668 | 7.66 | 167.239 | 1980.3 | 26.12 | 48.165 | 6.34 | 1.31 | 4.711 | 8128.7 | 2.073 | 97.6 | 78.3 | 1287 | 24.08 | 5283.7 | 2834.9 | 2744.4 | 4069.6 | 1183.1 | 0.67846 | 6.021
2024-12-09 | 12:41 | Data | 0 | 32.494 | 30.739 | 178.895 | 7.65 | 167.284 | 1982.1 | 26.11 | 48.165 | 6.34 | 1.314 | 4.699 | 8110.61 | 1.904 | 97.6 | 78.1 | 1288 | 24.13 | 5271.9 | 2837.2 | 2756 | 4079.1 | 1183.1 | 0.67865 | 6.013
2024-12-09 | 12:41 | Data | 0 | 32.521 | 30.428 | 178.895 | 7.66 | 167.284 | 1982.1 | 26.12 | 48.075 | 6.34 | 1.32 | 4.7 | 8110.61 | 2.059 | 97.6 | 78.1 | 1288 | 24.04 | 5271.9 | 2842.3 | 2717.4 | 4055.6 | 1183.1 | 0.68332 | 6.019
2024-12-09 | 12:41 | Data | 0 | 32.494 | 30.415 | 178.849 | 7.66 | 167.239 | 1981.2 | 26.12 | 47.894 | 6.34 | 1.33 | 4.704 | 8101.57 | 1.877 | 97.6 | 77.9 | 1288 | 23.9 | 5266 | 2834.5 | 2739.3 | 4064.4 | 1183.1 | 0.68045 | 6.036
2024-12-09 | 12:41 | Data | 0 | 32.494 | 30.59 | 178.804 | 7.66 | 167.329 | 1984.82 | 26.12 | 47.894 | 6.34 | 1.328 | 4.702 | 8092.52 | 2.079 | 97.6 | 78 | 1290 | 23.95 | 5260.1 | 2852.9 | 2744.7 | 4079.6 | 1183.1 | 0.68335 | 6.029
2024-12-09 | 12:41 | Data | 0 | 32.771 | 30.421 | 178.849 | 7.65 | 167.329 | 1984.82 | 26.1 | 47.984 | 6.34 | 1.321 | 4.69 | 8074.44 | 2.079 | 97.6 | 78 | 1290 | 24.04 | 5248.4 | 2857.8 | 2751.4 | 4077.3 | 1183.1 | 0.68163 | 6.01
2024-12-09 | 12:41 | Data | 0 | 32.494 | 30.556 | 178.804 | 7.66 | 167.284 | 1980.3 | 26.12 | 47.894 | 6.34 | 1.321 | 4.702 | 8069.91 | 1.992 | 97.6 | 78.1 | 1288 | 23.95 | 5245.4 | 2837.8 | 2741.2 | 4074.8 | 1183.1 | 0.68161 | 6.025
2024-12-09 | 12:41 | Data | 0 | 32.717 | 30.435 | 178.895 | 7.65 | 167.239 | 1984.82 | 26.12 | 47.804 | 6.34 | 1.32 | 4.683 | 8056.35 | 2.1 | 97.6 | 78 | 1291 | 23.9 | 5236.6 | 2849.9 | 2739.9 | 4074.4 | 1183.1 | 0.68319 | 6.004
2024-12-09 | 12:41 | Data | 0 | 32.825 | 30.705 | 178.985 | 7.66 | 167.42 | 1984.82 | 26.12 | 47.894 | 6.33 | 1.324 | 4.692 | 8029.21 | 2.066 | 97.6 | 78 | 1290 | 23.95 | 5219 | 2815.4 | 2750.4 | 4061.5 | 1183.1 | 0.67691 | 6.016
2024-12-09 | 12:42 | Data | 0 | 32.339 | 30.536 | 178.759 | 7.65 | 167.329 | 1984.82 | 26.11 | 47.894 | 6.33 | 1.308 | 4.707 | 8015.65 | 1.857 | 97.6 | 78.3 | 1290 | 24.04 | 5210.2 | 2847.8 | 2750.9 | 4079.6 | 1183.1 | 0.68026 | 6.013
2024-12-09 | 12:42 | Data | 0 | 32.467 | 30.86 | 178.94 | 7.66 | 167.375 | 1984.82 | 26.11 | 47.894 | 6.34 | 1.314 | 4.699 | 8011.13 | 2.032 | 97.6 | 78.1 | 1290 | 23.95 | 5207.2 | 2842.5 | 2754.3 | 4093.5 | 1183.1 | 0.6814 | 6.015
2024-12-09 | 12:42 | Data | 0 | 32.271 | 30.59 | 178.849 | 7.66 | 167.375 | 1984.82 | 26.1 | 47.894 | 6.34 | 1.323 | 4.692 | 8020.17 | 1.843 | 97.6 | 78 | 1291 | 23.95 | 5213.1 | 2849.5 | 2753.1 | 4083.6 | 1183.1 | 0.68016 | 6.016
2024-12-09 | 12:42 | Data | 0 | 32.669 | 30.469 | 178.759 | 7.66 | 167.329 | 1988.43 | 26.11 | 47.984 | 6.34 | 1.314 | 4.683 | 8024.69 | 2.052 | 97.6 | 78.1 | 1292 | 23.95 | 5216 | 2840 | 2741.9 | 4073 | 1183.1 | 0.68167 | 5.998
2024-12-09 | 12:42 | Data | 0 | 32.555 | 30.691 | 178.94 | 7.66 | 167.465 | 1987.53 | 26.11 | 48.436 | 6.34 | 1.322 | 4.706 | 8015.65 | 1.911 | 97.6 | 78.1 | 1292 | 24.17 | 5210.2 | 2844.8 | 2750.4 | 4079.2 | 1183.1 | 0.67913 | 6.029
2024-12-09 | 12:42 | Data | 0 | 32.325 | 30.415 | 178.895 | 7.65 | 167.284 | 1987.53 | 26.12 | 47.894 | 6.34 | 1.323 | 4.686 | 8029.21 | 1.863 | 97.6 | 78 | 1292 | 23.95 | 5219 | 2834.6 | 2768.1 | 4088.5 | 1183.1 | 0.67836 | 6.01
2024-12-09 | 12:42 | Data | 0 | 32.264 | 30.313 | 178.759 | 7.66 | 167.375 | 1987.53 | 26.12 | 47.894 | 6.34 | 1.317 | 4.688 | 8015.65 | 2.194 | 97.6 | 78.1 | 1292 | 23.95 | 5210.2 | 2855.5 | 2768.2 | 4096.6 | 1183.1 | 0.67993 | 6.006
2024-12-09 | 12:42 | Data | 0 | 32.413 | 30.475 | 178.895 | 7.66 | 167.375 | 1987.53 | 26.12 | 47.804 | 6.33 | 1.307 | 4.66 | 8042.78 | 1.911 | 97.6 | 78.1 | 1292 | 23.99 | 5227.8 | 2836.3 | 2746.5 | 4074.2 | 1183.1 | 0.68049 | 5.965
2024-12-09 | 12:42 | Data | 0 | 32.44 | 30.529 | 178.804 | 7.66 | 167.239 | 1987.53 | 26.12 | 47.804 | 6.33 | 1.303 | 4.692 | 8038.26 | 2.079 | 97.6 | 78.3 | 1292 | 23.95 | 5224.9 | 2858.2 | 2789.3 | 4116.4 | 1183.1 | 0.67769 | 5.995
2024-12-09 | 12:42 | Data | 0 | 32.467 | 30.415 | 178.804 | 7.66 | 167.329 | 1990.24 | 26.12 | 47.894 | 6.33 | 1.306 | 4.702 | 8042.78 | 2.248 | 97.6 | 78.3 | 1294 | 23.99 | 5227.8 | 2843.9 | 2740.8 | 4074.7 | 1183.1 | 0.68166 | 6.007
2024-12-09 | 12:42 | Data | 0 | 32.615 | 30.428 | 178.895 | 7.66 | 167.42 | 1990.24 | 26.11 | 48.075 | 6.34 | 1.317 | 4.697 | 8042.78 | 1.87 | 97.6 | 78.1 | 1294 | 24.04 | 5227.8 | 2857 | 2782.1 | 4108.1 | 1183.1 | 0.67756 | 6.014
2024-12-09 | 12:42 | Data | 0 | 32.298 | 30.212 | 178.714 | 7.66 | 167.284 | 1989.33 | 26.11 | 47.894 | 6.33 | 1.323 | 4.702 | 8015.65 | 2.025 | 97.6 | 78.1 | 1293 | 23.95 | 5210.2 | 2852.7 | 2776.1 | 4109 | 1183.2 | 0.6805 | 6.026
2024-12-09 | 12:42 | Data | 0 | 32.44 | 30.624 | 178.849 | 7.65 | 167.329 | 1991.14 | 26.14 | 47.894 | 6.33 | 1.324 | 4.7 | 8006.6 | 1.89 | 97.6 | 78 | 1294 | 23.95 | 5204.3 | 2843.5 | 2765.4 | 4084 | 1183.2 | 0.67788 | 6.024
2024-12-09 | 12:42 | Data | 0 | 32.474 | 30.415 | 178.895 | 7.66 | 167.375 | 1993.85 | 26.13 | 47.894 | 6.34 | 1.322 | 4.697 | 8002.08 | 2.079 | 97.6 | 78 | 1295 | 23.95 | 5201.4 | 2834.3 | 2787.4 | 4099.2 | 1183.2 | 0.67501 | 6.019
2024-12-09 | 12:42 | Data | 0 | 32.494 | 30.806 | 178.895 | 7.65 | 167.329 | 1995.66 | 26.12 | 47.894 | 6.34 | 1.323 | 4.693 | 8011.13 | 1.931 | 97.6 | 78 | 1297 | 23.95 | 5207.2 | 2855.7 | 2799.7 | 4114.6 | 1183.2 | 0.67715 | 6.017
2024-12-09 | 12:42 | Data | 0 | 32.271 | 30.415 | 178.849 | 7.66 | 167.329 | 1996.57 | 26.12 | 47.804 | 6.34 | 1.311 | 4.7 | 8015.65 | 2.025 | 97.6 | 78.2 | 1298 | 23.99 | 5210.2 | 2846.9 | 2800.6 | 4112.3 | 1183.2 | 0.67537 | 6.011
2024-12-09 | 12:42 | Data | 0 | 32.703 | 30.421 | 178.849 | 7.65 | 167.375 | 1997.47 | 26.12 | 47.894 | 6.33 | 1.32 | 4.668 | 8029.21 | 2.12 | 97.6 | 78 | 1298 | 23.95 | 5219 | 2853.7 | 2800.7 | 4119.6 | 1183.2 | 0.67423 | 5.989
2024-12-09 | 12:42 | Data | 0 | 32.494 | 30.847 | 178.804 | 7.66 | 167.329 | 1992.05 | 26.12 | 47.894 | 6.34 | 1.327 | 4.654 | 8029.21 | 1.803 | 97.6 | 77.8 | 1295 | 23.95 | 5219 | 2825.8 | 2793.2 | 4095.8 | 1183.2 | 0.6732 | 5.981
2024-12-09 | 12:43 | Data | 0 | 32.609 | 30.543 | 178.895 | 7.66 | 167.375 | 1990.24 | 26.1 | 47.894 | 6.33 | 1.325 | 4.7 | 8015.65 | 1.924 | 97.6 | 78 | 1294 | 23.99 | 5210.2 | 2833.3 | 2791.3 | 4109 | 1183.2 | 0.67999 | 6.024
2024-12-09 | 12:43 | Data | 0 | 32.507 | 30.421 | 178.94 | 7.66 | 167.42 | 1990.24 | 26.11 | 47.894 | 6.33 | 1.324 | 4.711 | 8060.87 | 2.079 | 97.6 | 78.1 | 1294 | 23.99 | 5239.6 | 2855.5 | 2764.6 | 4097.6 | 1183.2 | 0.67958 | 6.034
2024-12-09 | 12:43 | Data | 0 | 32.298 | 30.367 | 178.849 | 7.65 | 167.375 | 1990.24 | 26.12 | 47.804 | 6.33 | 1.312 | 4.707 | 8056.35 | 2.059 | 97.6 | 78.2 | 1294 | 23.9 | 5236.6 | 2832.4 | 2773.5 | 4086.5 | 1183.2 | 0.67619 | 6.018
2024-12-09 | 12:43 | Data | 0 | 32.44 | 30.536 | 178.895 | 7.66 | 167.329 | 1989.33 | 26.11 | 47.804 | 6.33 | 1.317 | 4.712 | 8056.35 | 2.073 | 97.6 | 78.2 | 1293 | 23.95 | 5236.6 | 2849.2 | 2764.8 | 4087.9 | 1183.2 | 0.67946 | 6.031
2024-12-09 | 12:43 | Data | 0 | 32.501 | 30.523 | 178.895 | 7.65 | 167.375 | 1990.24 | 26.11 | 47.894 | 6.33 | 1.318 | 4.715 | 8056.35 | 1.87 | 97.6 | 78.2 | 1294 | 23.95 | 5236.6 | 2842.3 | 2758.8 | 4081.9 | 1183.2 | 0.67893 | 6.03
2024-12-09 | 12:43 | Data | 0 | 32.723 | 30.435 | 178.895 | 7.65 | 167.375 | 1986.62 | 26.11 | 47.894 | 6.33 | 1.323 | 4.692 | 8042.78 | 2.073 | 97.6 | 78 | 1291 | 23.95 | 5227.8 | 2837.9 | 2768.6 | 4088.9 | 1183.2 | 0.67963 | 6.015
2024-12-09 | 12:43 | Data | 0 | 32.636 | 30.421 | 178.849 | 7.66 | 167.329 | 1987.53 | 26.12 | 47.894 | 6.33 | 1.329 | 4.685 | 8015.65 | 1.978 | 97.6 | 77.9 | 1292 | 23.95 | 5210.2 | 2846.4 | 2765.3 | 4090.9 | 1183.2 | 0.67953 | 6.013
2024-12-09 | 12:43 | Data | 0 | 32.69 | 30.732 | 178.94 | 7.65 | 167.42 | 1984.82 | 26.11 | 47.894 | 6.33 | 1.312 | 4.706 | 8020.17 | 1.978 | 97.6 | 78.2 | 1290 | 23.95 | 5213.1 | 2850 | 2749.5 | 4087 | 1183.2 | 0.68006 | 6.018
2024-12-09 | 12:43 | Data | 0 | 32.811 | 30.678 | 178.895 | 7.66 | 167.375 | 1981.2 | 26.13 | 47.984 | 6.33 | 1.308 | 4.69 | 8015.65 | 2.133 | 97.6 | 78.2 | 1288 | 23.95 | 5210.2 | 2835.6 | 2743.7 | 4069.9 | 1183.2 | 0.67824 | 5.998
2024-12-09 | 12:43 | Data | 0 | 32.649 | 30.415 | 178.804 | 7.65 | 167.284 | 1980.3 | 26.11 | 47.804 | 6.34 | 1.313 | 4.7 | 8047.3 | 2.187 | 97.6 | 78.1 | 1287 | 23.9 | 5230.7 | 2838.6 | 2752.9 | 4076.5 | 1183.2 | 0.67997 | 6.014
2024-12-09 | 12:43 | Data | 0 | 32.433 | 30.415 | 178.849 | 7.65 | 167.375 | 1979.39 | 26.12 | 47.894 | 6.33 | 1.321 | 4.682 | 8074.44 | 2.046 | 97.6 | 78 | 1287 | 23.99 | 5248.4 | 2842.9 | 2775 | 4097.4 | 1183.2 | 0.67737 | 6.005
2024-12-09 | 12:43 | Data | 0 | 32.71 | 30.739 | 178.94 | 7.65 | 167.375 | 1979.39 | 26.11 | 47.804 | 6.33 | 1.322 | 4.683 | 8069.91 | 2.127 | 97.6 | 78 | 1287 | 23.9 | 5245.4 | 2827.8 | 2799.5 | 4103.7 | 1183.2 | 0.67092 | 6.005
2024-12-09 | 12:43 | Data | 0 | 32.298 | 30.374 | 178.895 | 7.65 | 167.375 | 1976.68 | 26.1 | 47.894 | 6.33 | 1.313 | 4.677 | 8088 | 1.944 | 97.6 | 78.1 | 1284 | 23.95 | 5257.2 | 2823.9 | 2822.3 | 4111.2 | 1183.2 | 0.67078 | 5.991
2024-12-09 | 12:43 | Data | 0 | 32.69 | 30.442 | 178.895 | 7.65 | 167.329 | 1976.68 | 26.12 | 47.894 | 6.33 | 1.317 | 4.691 | 8069.91 | 2.248 | 97.6 | 78.1 | 1285 | 23.95 | 5245.4 | 2827.8 | 2806.1 | 4101.5 | 1183.2 | 0.67302 | 6.006
2024-12-09 | 12:43 | Data | 0 | 32.609 | 30.55 | 178.849 | 7.65 | 167.375 | 1976.68 | 26.12 | 47.894 | 6.33 | 1.317 | 4.694 | 8074.44 | 2.268 | 97.6 | 78.1 | 1285 | 23.95 | 5248.4 | 2825.5 | 2801.4 | 4101.5 | 1183.2 | 0.67187 | 6.01
2024-12-09 | 12:43 | Data | 0 | 32.494 | 30.415 | 178.895 | 7.65 | 167.375 | 1976.68 | 26.11 | 47.894 | 6.34 | 1.32 | 4.7 | 8092.52 | 2.079 | 97.6 | 78.1 | 1285 | 23.95 | 5260.1 | 2843.5 | 2812.3 | 4124.5 | 1183.2 | 0.67331 | 6.02
2024-12-09 | 12:43 | Data | 0 | 32.744 | 30.428 | 178.759 | 7.65 | 167.375 | 1977.58 | 26.12 | 47.623 | 6.34 | 1.319 | 4.72 | 8069.91 | 2.079 | 97.6 | 78.2 | 1285 | 23.81 | 5245.4 | 2832 | 2788.8 | 4098.8 | 1183.2 | 0.67543 | 6.038
2024-12-09 | 12:43 | Data | 0 | 32.413 | 30.536 | 178.895 | 7.65 | 167.42 | 1973.07 | 26.1 | 47.714 | 6.33 | 1.32 | 4.694 | 8088 | 2.052 | 97.6 | 78 | 1282 | 23.81 | 5257.2 | 2836 | 2779.7 | 4098.1 | 1183.2 | 0.67542 | 6.016
2024-12-09 | 12:44 | Data | 0 | 32.339 | 30.415 | 178.94 | 7.65 | 167.375 | 1976.68 | 26.12 | 47.714 | 6.33 | 1.323 | 4.703 | 8092.52 | 1.857 | 97.6 | 78 | 1284 | 23.86 | 5260.1 | 2860.5 | 2757.3 | 4093 | 1183.2 | 0.68258 | 6.026
2024-12-09 | 12:44 | Data | 0 | 32.663 | 30.55 | 178.94 | 7.66 | 167.465 | 1973.97 | 26.13 | 47.623 | 6.33 | 1.32 | 4.687 | 8088 | 2.066 | 97.6 | 78 | 1283 | 23.81 | 5257.2 | 2835.9 | 2756.7 | 4079.2 | 1183.2 | 0.67713 | 6.007
2024-12-09 | 12:44 | Data | 0 | 32.723 | 30.543 | 178.849 | 7.66 | 167.375 | 1976.68 | 26.11 | 47.623 | 6.33 | 1.31 | 4.711 | 8088 | 2.086 | 97.6 | 78.3 | 1286 | 23.81 | 5257.2 | 2831.9 | 2751 | 4073.9 | 1183.2 | 0.67784 | 6.022
2024-12-09 | 12:44 | Data | 0 | 32.467 | 30.415 | 178.804 | 7.65 | 167.329 | 1973.97 | 26.13 | 47.533 | 6.34 | 1.314 | 4.702 | 8033.74 | 2.073 | 97.6 | 78.2 | 1283 | 23.81 | 5221.9 | 2841.7 | 2752.2 | 4080.3 | 1183.2 | 0.67862 | 6.017
2024-12-09 | 12:44 | Data | 0 | 32.44 | 30.529 | 179.03 | 7.65 | 167.465 | 1972.16 | 26.13 | 47.714 | 6.33 | 1.312 | 4.699 | 8042.78 | 2.012 | 97.6 | 78.2 | 1282 | 23.81 | 5227.8 | 2856.3 | 2764.3 | 4097.5 | 1183.2 | 0.68013 | 6.01
2024-12-09 | 12:44 | Data | 0 | 32.305 | 30.624 | 178.985 | 7.65 | 167.465 | 1976.68 | 26.1 | 47.623 | 6.34 | 1.318 | 4.699 | 8427.17 | 1.789 | 97.6 | 78.1 | 1285 | 23.81 | 5477.7 | 2849.5 | 2745.9 | 4080.2 | 1183.2 | 0.68056 | 6.017
2024-12-09 | 12:44 | Data | 0 | 32.487 | 30.847 | 178.895 | 7.65 | 167.375 | 1977.58 | 26.1 | 47.623 | 6.33 | 1.313 | 4.692 | 8029.21 | 1.924 | 97.6 | 78.1 | 1285 | 23.81 | 5219 | 2840.3 | 2749.3 | 4074.3 | 1183.2 | 0.681 | 6.006
2024-12-09 | 12:44 | Data | 0 | 32.913 | 30.705 | 178.985 | 7.65 | 167.42 | 1979.39 | 26.11 | 47.623 | 6.33 | 1.312 | 4.7 | 8042.78 | 2.187 | 97.6 | 78.2 | 1287 | 23.81 | 5227.8 | 2843.8 | 2743 | 4072.7 | 1183.2 | 0.68093 | 6.011
2024-12-09 | 12:44 | Data | 0 | 32.723 | 30.529 | 178.985 | 7.65 | 167.42 | 1979.39 | 26.11 | 47.714 | 6.33 | 1.32 | 4.686 | 8029.21 | 2.073 | 97.6 | 78 | 1287 | 23.81 | 5219 | 2834.6 | 2777.9 | 4098.6 | 1183.2 | 0.67367 | 6.007
2024-12-09 | 12:44 | Data | 0 | 32.649 | 30.59 | 178.985 | 7.65 | 167.42 | 1976.68 | 26.11 | 47.714 | 6.33 | 1.315 | 4.708 | 8024.69 | 2.275 | 97.6 | 78.2 | 1285 | 23.86 | 5216 | 2844 | 2739 | 4070.9 | 1183.2 | 0.682 | 6.023
2024-12-09 | 12:44 | Data | 0 | 32.494 | 30.536 | 178.759 | 7.65 | 167.329 | 1980.3 | 26.13 | 47.623 | 6.34 | 1.309 | 4.711 | 8029.21 | 1.958 | 97.6 | 78.3 | 1287 | 23.77 | 5219 | 2834.7 | 2753.6 | 4073.4 | 1183.2 | 0.68125 | 6.019
2024-12-09 | 12:44 | Data | 0 | 32.46 | 30.556 | 178.895 | 7.65 | 167.375 | 1982.1 | 26.11 | 47.714 | 6.33 | 1.311 | 4.691 | 8029.21 | 2.012 | 97.6 | 78.2 | 1288 | 23.81 | 5219 | 2839.8 | 2725.8 | 4060.2 | 1183.2 | 0.68265 | 6
2024-12-09 | 12:44 | Data | 0 | 32.359 | 30.637 | 178.94 | 7.65 | 167.375 | 1986.62 | 26.11 | 47.804 | 6.33 | 1.328 | 4.695 | 8020.17 | 2.154 | 97.6 | 78 | 1291 | 23.86 | 5213.1 | 2858.3 | 2742.9 | 4080.4 | 1183.2 | 0.68487 | 6.022
2024-12-09 | 12:44 | Data | 0 | 32.501 | 30.475 | 178.985 | 7.65 | 167.375 | 1982.1 | 26.12 | 47.714 | 6.33 | 1.331 | 4.676 | 8011.13 | 1.958 | 97.6 | 77.8 | 1289 | 23.81 | 5207.2 | 2832.7 | 2728.4 | 4055.2 | 1183.3 | 0.68224 | 6.005
2024-12-09 | 12:44 | Data | 0 | 32.548 | 30.428 | 178.985 | 7.65 | 167.329 | 1984.82 | 26.11 | 47.623 | 6.33 | 1.325 | 4.681 | 8015.65 | 2.046 | 97.6 | 77.9 | 1290 | 23.81 | 5210.2 | 2848.9 | 2746.5 | 4080.8 | 1183.3 | 0.68083 | 6.007
2024-12-09 | 12:44 | Data | 0 | 32.494 | 30.637 | 178.94 | 7.65 | 167.329 | 1983.01 | 26.11 | 47.443 | 6.33 | 1.319 | 4.698 | 8015.65 | 1.985 | 97.6 | 78.1 | 1289 | 23.81 | 5210.2 | 2837.7 | 2734.3 | 4064.2 | 1183.3 | 0.68115 | 6.018
2024-12-09 | 12:44 | Data | 0 | 32.602 | 30.86 | 178.895 | 7.65 | 167.42 | 1983.01 | 26.1 | 47.714 | 6.33 | 1.317 | 4.684 | 8011.13 | 1.958 | 97.6 | 78.1 | 1289 | 23.86 | 5207.2 | 2829.7 | 2726.4 | 4050.8 | 1183.3 | 0.68326 | 6.001
2024-12-09 | 12:45 | Data | 0 | 32.271 | 30.691 | 178.985 | 7.65 | 167.375 | 1987.53 | 26.13 | 47.623 | 6.33 | 1.32 | 4.649 | 8020.17 | 1.877 | 97.6 | 77.9 | 1292 | 23.77 | 5213.1 | 2833.6 | 2737.9 | 4064.8 | 1183.3 | 0.68332 | 5.967
2024-12-09 | 12:45 | Data | 0 | 32.663 | 30.82 | 178.985 | 7.65 | 167.375 | 1987.53 | 26.1 | 47.623 | 6.33 | 1.326 | 4.671 | 8015.65 | 1.958 | 97.6 | 77.9 | 1292 | 23.86 | 5210.2 | 2838.3 | 2738.7 | 4071.1 | 1183.3 | 0.68111 | 5.997
2024-12-09 | 12:45 | Data | 0 | 32.717 | 30.847 | 178.804 | 7.65 | 167.375 | 1990.24 | 26.1 | 47.623 | 6.33 | 1.321 | 4.691 | 8042.78 | 1.971 | 97.6 | 78 | 1293 | 23.81 | 5227.8 | 2848.3 | 2746.3 | 4078.1 | 1183.3 | 0.6833 | 6.011
2024-12-09 | 12:45 | Data | 0 | 32.609 | 30.448 | 178.94 | 7.65 | 167.42 | 1988.43 | 26.12 | 47.623 | 6.33 | 1.315 | 4.682 | 8042.78 | 2.073 | 97.6 | 78.1 | 1292 | 23.86 | 5227.8 | 2837.8 | 2746.8 | 4067.6 | 1183.3 | 0.68118 | 5.997
2024-12-09 | 12:45 | Data | 0 | 32.885 | 30.489 | 178.759 | 7.65 | 167.375 | 1988.43 | 26.11 | 47.623 | 6.33 | 1.312 | 4.69 | 8042.78 | 2.046 | 97.6 | 78.1 | 1292 | 23.86 | 5227.8 | 2837.3 | 2759.3 | 4080.5 | 1183.3 | 0.67899 | 6.002
2024-12-09 | 12:45 | Data | 0 | 32.48 | 30.637 | 178.849 | 7.65 | 167.42 | 1988.43 | 26.11 | 47.714 | 6.33 | 1.318 | 4.667 | 8042.78 | 2.073 | 97.6 | 78 | 1292 | 23.81 | 5227.8 | 2829 | 2730.9 | 4059.5 | 1183.3 | 0.68055 | 5.984
2024-12-09 | 12:45 | Data | 0 | 32.723 | 30.853 | 178.94 | 7.65 | 167.555 | 1987.53 | 26.11 | 47.623 | 6.33 | 1.32 | 4.662 | 8042.78 | 1.958 | 97.6 | 77.9 | 1292 | 23.81 | 5227.8 | 2836 | 2748.9 | 4071.4 | 1183.3 | 0.67995 | 5.981
2024-12-09 | 12:45 | Data | 0 | 32.548 | 30.523 | 178.895 | 7.65 | 167.329 | 1990.24 | 26.12 | 47.714 | 6.33 | 1.317 | 4.664 | 8042.78 | 1.992 | 97.6 | 78 | 1294 | 23.81 | 5227.8 | 2840.3 | 2734.6 | 4064.2 | 1183.3 | 0.68397 | 5.981
2024-12-09 | 12:45 | Data | 0 | 32.831 | 30.536 | 178.895 | 7.65 | 167.465 | 1990.24 | 26.11 | 47.623 | 6.33 | 1.314 | 4.671 | 8056.35 | 1.965 | 97.6 | 78.1 | 1294 | 23.81 | 5236.6 | 2831.8 | 2739.3 | 4059.7 | 1183.3 | 0.68214 | 5.984
2024-12-09 | 12:45 | Data | 0 | 32.723 | 30.543 | 178.94 | 7.65 | 167.465 | 1990.24 | 26.1 | 47.714 | 6.33 | 1.306 | 4.664 | 8038.26 | 1.978 | 97.6 | 78.1 | 1294 | 23.86 | 5224.9 | 2834.5 | 2729.1 | 4057.3 | 1183.3 | 0.68227 | 5.97
2024-12-09 | 12:45 | Data | 0 | 32.609 | 30.421 | 178.985 | 7.65 | 167.51 | 1987.53 | 26.11 | 47.894 | 6.33 | 1.314 | 4.687 | 8038.26 | 2.113 | 97.6 | 78.1 | 1291 | 23.95 | 5224.9 | 2872.8 | 2737.8 | 4089.6 | 1183.3 | 0.68493 | 6.001
2024-12-09 | 12:45 | Data | 0 | 32.501 | 30.59 | 179.03 | 7.65 | 167.42 | 1989.33 | 26.1 | 47.894 | 6.33 | 1.324 | 4.699 | 8047.3 | 2.194 | 97.6 | 78 | 1294 | 23.95 | 5230.7 | 2837.4 | 2740 | 4070.1 | 1183.3 | 0.68122 | 6.024
2024-12-09 | 12:45 | Data | 0 | 32.393 | 30.394 | 179.03 | 7.65 | 167.42 | 1990.24 | 26.11 | 47.894 | 6.33 | 1.325 | 4.707 | 8047.3 | 1.998 | 97.6 | 78 | 1294 | 23.95 | 5230.7 | 2837.7 | 2739.2 | 4061.7 | 1183.3 | 0.68311 | 6.031
2024-12-09 | 12:45 | Data | 0 | 32.71 | 30.644 | 178.94 | 7.65 | 167.375 | 1990.24 | 26.11 | 47.804 | 6.33 | 1.319 | 4.702 | 8038.26 | 2.127 | 97.6 | 78.1 | 1294 | 23.95 | 5224.9 | 2846.7 | 2742.4 | 4078.4 | 1183.3 | 0.68152 | 6.02
2024-12-09 | 12:45 | Data | 0 | 32.723 | 30.698 | 178.985 | 7.65 | 167.51 | 1989.33 | 26.1 | 47.894 | 6.33 | 1.322 | 4.692 | 8042.78 | 1.897 | 97.6 | 78 | 1294 | 23.99 | 5227.8 | 2837.1 | 2753.1 | 4076.4 | 1183.3 | 0.68025 | 6.015
2024-12-09 | 12:45 | Data | 0 | 32.494 | 30.469 | 178.94 | 7.65 | 167.465 | 1990.24 | 26.11 | 47.894 | 6.33 | 1.312 | 4.695 | 8033.74 | 1.971 | 97.6 | 78.2 | 1294 | 23.95 | 5221.9 | 2833.3 | 2725.1 | 4055.7 | 1183.3 | 0.68203 | 6.007
2024-12-09 | 12:45 | Data | 0 | 32.831 | 30.543 | 178.895 | 7.65 | 167.51 | 1987.53 | 26.1 | 47.894 | 6.33 | 1.312 | 4.692 | 8042.78 | 1.985 | 97.6 | 78.1 | 1292 | 23.95 | 5227.8 | 2843.1 | 2733.1 | 4069.1 | 1183.3 | 0.68293 | 6.005
2024-12-09 | 12:45 | Data | 0 | 32.44 | 30.631 | 179.03 | 7.65 | 167.375 | 1985.72 | 26.11 | 47.804 | 6.33 | 1.318 | 4.716 | 8011.13 | 1.992 | 97.6 | 78.2 | 1290 | 23.9 | 5207.2 | 2830.3 | 2721.7 | 4050.5 | 1183.3 | 0.68219 | 6.034
2024-12-09 | 12:46 | Data | 0 | 32.406 | 30.415 | 178.849 | 7.65 | 167.375 | 1984.82 | 26.11 | 47.714 | 6.33 | 1.304 | 4.7 | 8033.74 | 1.917 | 97.6 | 78.3 | 1290 | 23.9 | 5221.9 | 2858.5 | 2716.1 | 4063.6 | 1183.3 | 0.68745 | 6.004
2024-12-09 | 12:46 | Data | 0 | 32.831 | 30.658 | 178.94 | 7.65 | 167.51 | 1984.82 | 26.1 | 47.894 | 6.33 | 1.318 | 4.683 | 8047.3 | 1.897 | 97.6 | 78 | 1290 | 23.9 | 5230.7 | 2844.5 | 2741.7 | 4072.9 | 1183.3 | 0.6841 | 6.001
2024-12-09 | 12:46 | Data | 0 | 32.838 | 30.658 | 179.03 | 7.65 | 167.465 | 1983.01 | 26.11 | 48.075 | 6.33 | 1.327 | 4.705 | 8056.35 | 2.106 | 97.6 | 78 | 1288 | 24.08 | 5236.6 | 2839.2 | 2742.4 | 4071.2 | 1183.3 | 0.68124 | 6.032
2024-12-09 | 12:46 | Data | 0 | 32.744 | 30.651 | 179.03 | 7.65 | 167.51 | 1982.1 | 26.1 | 47.894 | 6.33 | 1.312 | 4.686 | 8051.82 | 2.066 | 97.6 | 78.1 | 1288 | 23.99 | 5233.7 | 2862.4 | 2729.9 | 4075.3 | 1183.3 | 0.686 | 5.998
2024-12-09 | 12:46 | Data | 0 | 32.298 | 30.415 | 178.759 | 7.65 | 167.555 | 1983.01 | 26.11 | 47.894 | 6.33 | 1.317 | 4.677 | 8078.96 | 1.965 | 97.6 | 78 | 1288 | 23.9 | 5251.3 | 2832.8 | 2725.6 | 4055.1 | 1183.3 | 0.68149 | 5.994
2024-12-09 | 12:46 | Data | 0 | 32.285 | 30.59 | 178.94 | 7.65 | 167.465 | 1983.01 | 26.11 | 47.623 | 6.32 | 1.317 | 4.671 | 8074.44 | 1.965 | 97.6 | 78 | 1289 | 23.77 | 5248.4 | 2842 | 2740.7 | 4068 | 1183.3 | 0.68159 | 5.988
2024-12-09 | 12:46 | Data | 0 | 32.494 | 30.421 | 178.94 | 7.65 | 167.42 | 1981.2 | 26.11 | 47.984 | 6.33 | 1.318 | 4.693 | 8074.44 | 2.073 | 97.6 | 78.1 | 1288 | 23.99 | 5248.4 | 2845.9 | 2729.6 | 4068.2 | 1183.3 | 0.68423 | 6.01
2024-12-09 | 12:46 | Data | 0 | 32.777 | 30.766 | 179.075 | 7.65 | 167.51 | 1982.1 | 26.1 | 47.894 | 6.33 | 1.325 | 4.687 | 8069.91 | 1.857 | 97.6 | 78 | 1289 | 23.95 | 5245.4 | 2840.1 | 2726.5 | 4063.2 | 1183.3 | 0.68275 | 6.013
2024-12-09 | 12:46 | Data | 0 | 32.521 | 30.651 | 178.94 | 7.65 | 167.51 | 1979.39 | 26.11 | 47.894 | 6.33 | 1.321 | 4.711 | 8088 | 1.971 | 97.6 | 78.1 | 1287 | 23.95 | 5257.2 | 2852.8 | 2743.1 | 4078.4 | 1183.3 | 0.68299 | 6.033
2024-12-09 | 12:46 | Data | 0 | 32.609 | 30.651 | 179.03 | 7.65 | 167.51 | 1980.3 | 26.1 | 47.804 | 6.33 | 1.309 | 4.7 | 8083.48 | 1.85 | 97.6 | 78.2 | 1287 | 24.04 | 5254.3 | 2842 | 2740 | 4067.1 | 1183.3 | 0.68295 | 6.009
2024-12-09 | 12:46 | Data | 0 | 33.135 | 30.88 | 179.075 | 7.65 | 167.51 | 1980.3 | 26.11 | 47.894 | 6.33 | 1.318 | 4.679 | 8074.44 | 2.167 | 97.6 | 78 | 1287 | 23.95 | 5248.4 | 2857.3 | 2734.7 | 4076.5 | 1183.3 | 0.6856 | 5.997
2024-12-09 | 12:46 | Data | 0 | 32.379 | 30.415 | 178.849 | 7.65 | 167.42 | 1983.01 | 26.12 | 47.804 | 6.33 | 1.331 | 4.675 | 8078.96 | 2.066 | 97.6 | 77.8 | 1288 | 23.9 | 5251.3 | 2849.4 | 2733.5 | 4073.3 | 1183.3 | 0.68252 | 6.007
2024-12-09 | 12:46 | Data | 0 | 32.71 | 30.644 | 178.985 | 7.65 | 167.465 | 1984.82 | 26.13 | 47.894 | 6.33 | 1.328 | 4.667 | 8060.87 | 2.079 | 97.6 | 77.8 | 1290 | 23.95 | 5239.6 | 2831.6 | 2740.8 | 4064.2 | 1183.3 | 0.67991 | 5.997
2024-12-09 | 12:46 | Data | 0 | 33 | 30.921 | 178.985 | 7.65 | 167.465 | 1987.53 | 26.11 | 47.714 | 6.33 | 1.324 | 4.687 | 8051.82 | 2.127 | 97.6 | 78 | 1292 | 23.86 | 5233.7 | 2852.3 | 2737.4 | 4073.8 | 1183.3 | 0.68403 | 6.011
2024-12-09 | 12:46 | Data | 0 | 32.717 | 30.421 | 178.985 | 7.64 | 167.465 | 1987.53 | 26.13 | 47.623 | 6.33 | 1.32 | 4.711 | 8060.87 | 2.14 | 97.6 | 78.1 | 1292 | 23.86 | 5239.6 | 2831.1 | 2741 | 4062.3 | 1183.3 | 0.68019 | 6.027
2024-12-09 | 12:46 | Data | 0 | 32.494 | 30.624 | 178.985 | 7.65 | 167.42 | 1987.53 | 26.11 | 47.623 | 6.33 | 1.313 | 4.715 | 8069.91 | 1.904 | 97.6 | 78.2 | 1291 | 23.86 | 5245.4 | 2834.2 | 2726.1 | 4055 | 1183.4 | 0.68239 | 6.03
2024-12-09 | 12:46 | Data | 0 | 32.494 | 30.637 | 178.985 | 7.65 | 167.42 | 1987.53 | 26.11 | 47.714 | 6.33 | 1.326 | 4.728 | 8083.48 | 1.985 | 97.6 | 78.1 | 1292 | 23.86 | 5254.3 | 2845.4 | 2725.9 | 4064.1 | 1183.4 | 0.68113 | 6.053
2024-12-09 | 12:47 | Data | 0 | 32.494 | 30.442 | 178.94 | 7.65 | 167.42 | 1987.53 | 26.11 | 47.804 | 6.33 | 1.323 | 4.71 | 8088 | 1.965 | 97.6 | 78.1 | 1292 | 23.9 | 5257.2 | 2838.9 | 2751 | 4076.2 | 1183.4 | 0.68005 | 6.035
2024-12-09 | 12:47 | Data | 0 | 32.501 | 30.806 | 178.895 | 7.65 | 167.465 | 1989.33 | 26.11 | 47.714 | 6.33 | 1.313 | 4.691 | 8106.09 | 1.897 | 97.6 | 78.1 | 1294 | 23.86 | 5269 | 2840.8 | 2748.8 | 4078 | 1183.4 | 0.67967 | 6.003
2024-12-09 | 12:47 | Data | 0 | 32.494 | 30.759 | 179.03 | 7.65 | 167.51 | 1990.24 | 26.12 | 47.443 | 6.33 | 1.322 | 4.724 | 8101.57 | 2.16 | 97.6 | 78.1 | 1294 | 23.81 | 5266 | 2845 | 2733.7 | 4067.8 | 1183.4 | 0.68392 | 6.047
2024-12-09 | 12:47 | Data | 0 | 32.507 | 30.442 | 178.94 | 7.64 | 167.42 | 1991.14 | 26.11 | 47.623 | 6.33 | 1.317 | 4.704 | 8069.91 | 1.85 | 97.6 | 78.1 | 1294 | 23.81 | 5245.4 | 2851.4 | 2724.6 | 4069 | 1183.4 | 0.68421 | 6.023
2024-12-09 | 12:47 | Data | 0 | 32.507 | 30.651 | 178.895 | 7.64 | 167.42 | 1989.33 | 26.11 | 47.623 | 6.33 | 1.321 | 4.673 | 8069.91 | 1.863 | 97.6 | 78 | 1294 | 23.81 | 5245.4 | 2840.8 | 2727.2 | 4057.7 | 1183.4 | 0.68301 | 5.994
2024-12-09 | 12:47 | Data | 0 | 32.487 | 30.59 | 178.895 | 7.65 | 167.375 | 1991.14 | 26.12 | 47.714 | 6.33 | 1.325 | 4.683 | 8074.44 | 1.958 | 97.6 | 78 | 1295 | 23.81 | 5248.4 | 2825.1 | 2729.8 | 4051.6 | 1183.4 | 0.68072 | 6.007
2024-12-09 | 12:47 | Data | 0 | 32.467 | 30.637 | 178.895 | 7.65 | 167.465 | 1991.14 | 26.1 | 47.623 | 6.33 | 1.324 | 4.699 | 8069.91 | 2.093 | 97.6 | 78 | 1294 | 23.81 | 5245.4 | 2853.1 | 2728.1 | 4067.2 | 1183.4 | 0.6853 | 6.024
2024-12-09 | 12:47 | Data | 0 | 32.71 | 30.82 | 179.03 | 7.64 | 167.51 | 1996.57 | 26.12 | 47.533 | 6.33 | 1.322 | 4.695 | 8078.96 | 2.066 | 97.6 | 78 | 1297 | 23.81 | 5251.3 | 2835.7 | 2727.3 | 4059.7 | 1183.4 | 0.68203 | 6.017
2024-12-09 | 12:47 | Data | 0 | 32.312 | 30.421 | 178.985 | 7.65 | 167.51 | 1993.85 | 26.1 | 47.714 | 6.33 | 1.325 | 4.702 | 8088 | 1.85 | 97.6 | 78 | 1294 | 23.81 | 5257.2 | 2833.4 | 2715.7 | 4046.9 | 1183.4 | 0.68394 | 6.027
2024-12-09 | 12:47 | Data | 0 | 32.494 | 30.847 | 178.985 | 7.64 | 167.51 | 1993.85 | 26.11 | 47.623 | 6.32 | 1.323 | 4.701 | 8092.52 | 1.87 | 97.6 | 78 | 1296 | 23.81 | 5260.1 | 2833.3 | 2728.7 | 4052.5 | 1183.4 | 0.68419 | 6.025
2024-12-09 | 12:47 | Data | 0 | 32.487 | 30.624 | 178.985 | 7.65 | 167.465 | 1993.85 | 26.11 | 47.623 | 6.32 | 1.317 | 4.699 | 8083.48 | 2.106 | 97.6 | 78.1 | 1296 | 23.81 | 5254.3 | 2845.4 | 2729.8 | 4065.3 | 1183.4 | 0.68355 | 6.017
2024-12-09 | 12:47 | Data | 0 | 32.609 | 30.543 | 179.03 | 7.65 | 167.51 | 1993.85 | 26.12 | 47.714 | 6.33 | 1.309 | 4.698 | 8088 | 2.046 | 97.6 | 78.2 | 1296 | 23.81 | 5257.2 | 2826.6 | 2725.9 | 4049.8 | 1183.4 | 0.68252 | 6.003
2024-12-09 | 12:47 | Data | 0 | 32.507 | 30.421 | 178.849 | 7.65 | 167.465 | 1993.85 | 26.11 | 47.804 | 6.33 | 1.31 | 4.673 | 8088 | 2.073 | 97.6 | 78.1 | 1295 | 23.86 | 5257.2 | 2828.2 | 2711.9 | 4041.8 | 1183.4 | 0.68234 | 5.983
2024-12-09 | 12:47 | Data | 0 | 32.494 | 30.415 | 178.849 | 7.65 | 167.465 | 1992.05 | 26.1 | 47.623 | 6.33 | 1.32 | 4.685 | 8097.05 | 2.194 | 97.6 | 78 | 1296 | 23.86 | 5263.1 | 2831.5 | 2716.9 | 4049.3 | 1183.4 | 0.68344 | 6.006
2024-12-09 | 12:47 | Data | 0 | 32.845 | 30.489 | 179.03 | 7.65 | 167.555 | 1992.05 | 26.12 | 47.533 | 6.32 | 1.329 | 4.674 | 8088 | 1.911 | 97.6 | 77.8 | 1296 | 23.86 | 5257.2 | 2844.3 | 2721.5 | 4057.6 | 1183.4 | 0.68488 | 6.005
2024-12-09 | 12:47 | Data | 0 | 32.609 | 30.651 | 179.03 | 7.65 | 167.555 | 1995.66 | 26.11 | 47.533 | 6.33 | 1.328 | 4.692 | 8069.91 | 1.985 | 97.6 | 77.9 | 1297 | 23.81 | 5245.4 | 2831.6 | 2717.8 | 4053.1 | 1183.4 | 0.68093 | 6.019
2024-12-09 | 12:47 | Data | 0 | 32.852 | 30.664 | 179.03 | 7.65 | 167.601 | 1993.85 | 26.13 | 47.714 | 6.33 | 1.32 | 4.676 | 8042.78 | 1.884 | 97.6 | 78 | 1295 | 23.81 | 5227.8 | 2836.5 | 2741.9 | 4065.1 | 1183.4 | 0.68298 | 5.997
2024-12-09 | 12:47 | Data | 0 | 32.521 | 30.604 | 179.03 | 7.65 | 167.42 | 1991.14 | 26.1 | 47.533 | 6.33 | 1.32 | 4.666 | 8051.82 | 1.897 | 97.6 | 78 | 1293 | 23.81 | 5233.7 | 2832.3 | 2722.6 | 4052.1 | 1183.4 | 0.68192 | 5.986
2024-12-09 | 12:48 | Data | 0 | 32.885 | 30.421 | 179.03 | 7.65 | 167.555 | 1987.53 | 26.1 | 47.714 | 6.33 | 1.318 | 4.672 | 8078.96 | 1.938 | 97.6 | 78 | 1291 | 23.86 | 5251.3 | 2844.3 | 2747.4 | 4072.6 | 1183.4 | 0.68161 | 5.989
2024-12-09 | 12:48 | Data | 0 | 32.717 | 30.637 | 178.804 | 7.65 | 167.465 | 1985.72 | 26.1 | 47.533 | 6.33 | 1.313 | 4.643 | 8088 | 1.978 | 97.6 | 78 | 1291 | 23.81 | 5257.2 | 2837.9 | 2741.2 | 4066 | 1183.4 | 0.68143 | 5.955
2024-12-09 | 12:48 | Data | 0 | 32.474 | 30.84 | 178.94 | 7.64 | 167.465 | 1984.82 | 26.11 | 47.714 | 6.33 | 1.32 | 4.677 | 8069.91 | 1.904 | 97.6 | 78 | 1290 | 23.86 | 5245.4 | 2834.1 | 2704 | 4039 | 1183.4 | 0.68529 | 5.998
2024-12-09 | 12:48 | Data | 0 | 32.494 | 30.536 | 178.849 | 7.64 | 167.465 | 1982.1 | 26.11 | 47.804 | 6.32 | 1.32 | 4.705 | 8083.48 | 2.079 | 97.6 | 78.1 | 1288 | 23.86 | 5254.3 | 2856.4 | 2728.5 | 4068.9 | 1183.4 | 0.68415 | 6.026
2024-12-09 | 12:48 | Data | 0 | 32.94 | 30.88 | 178.94 | 7.65 | 167.555 | 1983.01 | 26.1 | 47.623 | 6.33 | 1.323 | 4.697 | 8083.48 | 2.073 | 97.6 | 78 | 1288 | 23.81 | 5254.3 | 2860.5 | 2731.2 | 4069.3 | 1183.4 | 0.68279 | 6.021
2024-12-09 | 12:48 | Data | 0 | 32.521 | 30.637 | 178.985 | 7.65 | 167.51 | 1985.72 | 26.11 | 47.623 | 6.32 | 1.321 | 4.671 | 8097.05 | 1.863 | 97.6 | 77.9 | 1291 | 23.81 | 5263.1 | 2854 | 2709.7 | 4055.3 | 1183.4 | 0.68803 | 5.992
2024-12-09 | 12:48 | Data | 0 | 32.717 | 30.968 | 179.121 | 7.64 | 167.51 | 1985.72 | 26.1 | 47.623 | 6.33 | 1.329 | 4.682 | 8088 | 1.755 | 97.6 | 77.9 | 1290 | 23.86 | 5257.2 | 2846.2 | 2733.7 | 4067.5 | 1183.4 | 0.68267 | 6.01
2024-12-09 | 12:48 | Data | 0 | 32.777 | 30.421 | 178.985 | 7.65 | 167.42 | 1983.91 | 26.11 | 47.984 | 6.33 | 1.329 | 4.673 | 8088 | 1.911 | 97.6 | 77.9 | 1290 | 23.99 | 5257.2 | 2850.6 | 2743.8 | 4079.3 | 1183.4 | 0.68247 | 6
2024-12-09 | 12:48 | Data | 0 | 32.777 | 30.428 | 178.985 | 7.64 | 167.42 | 1985.72 | 26.11 | 47.894 | 6.32 | 1.323 | 4.669 | 8088 | 2.174 | 97.6 | 77.9 | 1290 | 23.95 | 5257.2 | 2838.3 | 2733.3 | 4064.6 | 1183.4 | 0.68167 | 5.992
2024-12-09 | 12:48 | Data | 0 | 32.548 | 30.82 | 178.94 | 7.64 | 167.465 | 1984.82 | 26.11 | 47.894 | 6.33 | 1.324 | 4.7 | 7671.96 | 2.025 | 97.6 | 78 | 1290 | 23.95 | 4986.8 | 2840.1 | 2729.8 | 4065.7 | 1183.4 | 0.68442 | 6.024
2024-12-09 | 12:48 | Data | 0 | 32.386 | 30.59 | 178.895 | 7.64 | 167.51 | 1983.91 | 26.11 | 47.984 | 6.33 | 1.325 | 4.685 | 7644.82 | 2.005 | 97.6 | 77.9 | 1290 | 23.95 | 4969.1 | 2839 | 2745.6 | 4075.8 | 1183.4 | 0.68132 | 6.011
2024-12-09 | 12:48 | Data | 0 | 32.838 | 30.88 | 179.121 | 7.64 | 167.51 | 1987.53 | 26.1 | 47.623 | 6.33 | 1.32 | 4.693 | 8011.13 | 2.066 | 97.6 | 78 | 1292 | 23.81 | 5207.2 | 2836.5 | 2749.2 | 4071.8 | 1183.4 | 0.6807 | 6.013
2024-12-09 | 12:48 | Data | 0 | 32.609 | 30.448 | 178.94 | 7.64 | 167.465 | 1986.62 | 26.12 | 47.894 | 6.33 | 1.315 | 4.694 | 8029.21 | 2.127 | 97.6 | 78.1 | 1292 | 23.95 | 5219 | 2832.4 | 2745.1 | 4073.3 | 1183.4 | 0.68027 | 6.009
2024-12-09 | 12:48 | Data | 0 | 32.75 | 30.853 | 179.075 | 7.65 | 167.601 | 1987.53 | 26.12 | 47.804 | 6.32 | 1.323 | 4.705 | 8002.08 | 1.971 | 97.6 | 78 | 1292 | 23.95 | 5201.4 | 2838.6 | 2729.6 | 4062.3 | 1183.4 | 0.68176 | 6.029
2024-12-09 | 12:48 | Data | 0 | 32.71 | 30.806 | 179.03 | 7.65 | 167.465 | 1987.53 | 26.11 | 47.623 | 6.33 | 1.323 | 4.706 | 8051.82 | 2.086 | 97.6 | 78.1 | 1292 | 23.86 | 5233.7 | 2868 | 2739.8 | 4085.6 | 1183.4 | 0.68494 | 6.029
2024-12-09 | 12:48 | Data | 0 | 32.494 | 30.415 | 178.985 | 7.65 | 167.51 | 1990.24 | 26.11 | 47.443 | 6.33 | 1.314 | 4.67 | 8038.26 | 2.079 | 97.6 | 78 | 1294 | 23.72 | 5224.9 | 2858.8 | 2757.2 | 4090.2 | 1183.4 | 0.68288 | 5.985
2024-12-09 | 12:48 | Data | 0 | 32.494 | 30.644 | 178.94 | 7.64 | 167.42 | 1993.85 | 26.1 | 47.714 | 6.33 | 1.327 | 4.66 | 8047.3 | 1.857 | 97.6 | 77.8 | 1296 | 23.81 | 5230.7 | 2852.9 | 2753.2 | 4089.8 | 1183.4 | 0.68122 | 5.987
2024-12-09 | 12:48 | Data | 0 | 32.501 | 30.644 | 178.895 | 7.64 | 167.42 | 1989.33 | 26.11 | 47.714 | 6.32 | 1.317 | 4.691 | 8056.35 | 2.066 | 97.6 | 78.1 | 1292 | 23.86 | 5236.6 | 2831.8 | 2740.9 | 4066.9 | 1183.5 | 0.68159 | 6.007
2024-12-09 | 12:49 | Data | 0 | 32.784 | 30.448 | 179.075 | 7.64 | 167.601 | 1987.53 | 26.1 | 47.623 | 6.32 | 1.314 | 4.699 | 8042.78 | 1.931 | 97.6 | 78.1 | 1292 | 23.77 | 5227.8 | 2843.1 | 2742.8 | 4076.5 | 1183.5 | 0.6812 | 6.013
2024-12-09 | 12:49 | Data | 0 | 32.609 | 30.651 | 178.985 | 7.65 | 167.601 | 1994.76 | 26.1 | 47.533 | 6.32 | 1.318 | 4.686 | 8029.21 | 2.019 | 97.6 | 78 | 1298 | 23.81 | 5219 | 2835.1 | 2736.3 | 4061.7 | 1183.5 | 0.68175 | 6.003
2024-12-09 | 12:49 | Data | 0 | 32.94 | 30.651 | 179.121 | 7.65 | 167.646 | 1997.47 | 26.12 | 47.533 | 6.32 | 1.319 | 4.686 | 8042.78 | 2.093 | 97.6 | 78.1 | 1298 | 23.81 | 5227.8 | 2833.6 | 2737.5 | 4059.6 | 1183.5 | 0.68139 | 6.004
2024-12-09 | 12:49 | Data | 0 | 32.514 | 30.421 | 178.94 | 7.65 | 167.601 | 1998.37 | 26.11 | 47.714 | 6.33 | 1.317 | 4.681 | 8056.35 | 2.066 | 97.6 | 78.1 | 1299 | 23.81 | 5236.6 | 2838.8 | 2751.2 | 4074.7 | 1183.5 | 0.68184 | 5.996
2024-12-09 | 12:49 | Data | 0 | 32.75 | 30.61 | 178.985 | 7.65 | 167.601 | 2001.99 | 26.1 | 47.623 | 6.32 | 1.319 | 4.684 | 8495 | 2.133 | 97.6 | 78 | 1301 | 23.81 | 5521.8 | 2841 | 2748.4 | 4086.8 | 1183.5 | 0.68018 | 6.003
2024-12-09 | 12:49 | Data | 0 | 32.494 | 30.428 | 178.94 | 7.65 | 167.465 | 2001.08 | 26.1 | 47.714 | 6.32 | 1.327 | 4.681 | 8097.05 | 2.066 | 97.6 | 77.9 | 1301 | 23.86 | 5263.1 | 2861.7 | 2745.1 | 4086.5 | 1183.5 | 0.68356 | 6.007
2024-12-09 | 12:49 | Data | 0 | 32.609 | 30.421 | 179.03 | 7.64 | 167.555 | 2002.89 | 26.11 | 47.623 | 6.32 | 1.326 | 4.695 | 8074.44 | 2.268 | 97.6 | 78 | 1302 | 23.81 | 5248.4 | 2848.2 | 2738.4 | 4074.6 | 1183.5 | 0.68394 | 6.02
2024-12-09 | 12:49 | Data | 0 | 32.777 | 30.651 | 178.985 | 7.64 | 167.555 | 2004.7 | 26.1 | 47.714 | 6.32 | 1.327 | 4.682 | 8060.87 | 1.877 | 97.6 | 77.9 | 1304 | 23.81 | 5239.6 | 2836.9 | 2728.3 | 4056.1 | 1183.5 | 0.68231 | 6.007
2024-12-09 | 12:49 | Data | 0 | 32.838 | 30.631 | 179.075 | 7.64 | 167.646 | 2006.51 | 26.11 | 47.623 | 6.32 | 1.317 | 4.666 | 8047.3 | 1.938 | 97.6 | 78 | 1304 | 23.81 | 5230.7 | 2834.9 | 2731.4 | 4065.2 | 1183.5 | 0.68394 | 5.986
2024-12-09 | 12:49 | Data | 0 | 32.669 | 30.651 | 178.985 | 7.65 | 167.51 | 2007.41 | 26.1 | 47.623 | 6.32 | 1.313 | 4.677 | 8056.35 | 2.059 | 97.6 | 78.1 | 1304 | 23.81 | 5236.6 | 2861.2 | 2734.9 | 4076.6 | 1183.5 | 0.68495 | 5.99
2024-12-09 | 12:49 | Data | 0 | 33.048 | 31.13 | 179.121 | 7.65 | 167.646 | 2006.51 | 26.11 | 47.623 | 6.33 | 1.309 | 4.688 | 8042.78 | 1.958 | 97.6 | 78.2 | 1304 | 23.81 | 5227.8 | 2850.6 | 2725.3 | 4066 | 1183.5 | 0.68373 | 5.995
2024-12-09 | 12:49 | Data | 0 | 32.669 | 30.955 | 179.075 | 7.64 | 167.51 | 2007.41 | 26.11 | 47.623 | 6.32 | 1.317 | 4.656 | 8047.3 | 2.079 | 97.6 | 78 | 1304 | 23.81 | 5230.7 | 2849.3 | 2729.9 | 4061.9 | 1183.5 | 0.68282 | 5.973
2024-12-09 | 12:49 | Data | 0 | 32.892 | 30.658 | 179.03 | 7.64 | 167.601 | 2007.41 | 26.1 | 47.623 | 6.32 | 1.311 | 4.662 | 8042.78 | 1.877 | 97.6 | 78 | 1305 | 23.81 | 5227.8 | 2818.3 | 2734.5 | 4052.5 | 1183.5 | 0.67915 | 5.973
2024-12-09 | 12:49 | Data | 0 | 32.94 | 30.705 | 179.03 | 7.64 | 167.601 | 2005.6 | 26.11 | 47.623 | 6.32 | 1.315 | 4.663 | 8056.35 | 2.019 | 97.6 | 78 | 1304 | 23.81 | 5236.6 | 2838.7 | 2751 | 4075.4 | 1183.5 | 0.67923 | 5.979
2024-12-09 | 12:49 | Data | 0 | 32.723 | 30.759 | 179.075 | 7.64 | 167.646 | 2006.51 | 26.11 | 47.533 | 6.33 | 1.322 | 4.65 | 8056.35 | 2.039 | 97.6 | 77.9 | 1304 | 23.81 | 5236.6 | 2855.5 | 2752.5 | 4103.8 | 1183.5 | 0.68089 | 5.972
2024-12-09 | 12:49 | Data | 0 | 32.946 | 30.88 | 179.121 | 7.64 | 167.646 | 2004.7 | 26.1 | 47.533 | 6.33 | 1.321 | 4.671 | 8051.82 | 2.073 | 97.6 | 77.9 | 1302 | 23.77 | 5233.7 | 2837.3 | 2750.4 | 4081.1 | 1183.5 | 0.68077 | 5.992
2024-12-09 | 12:49 | Data | 0 | 32.669 | 30.543 | 178.985 | 7.64 | 167.555 | 2004.7 | 26.11 | 47.623 | 6.32 | 1.314 | 4.66 | 8051.82 | 2.093 | 97.6 | 78 | 1302 | 23.86 | 5233.7 | 2837.4 | 2722.8 | 4056 | 1183.5 | 0.68145 | 5.973
2024-12-09 | 12:50 | Data | 0 | 32.501 | 30.766 | 179.03 | 7.64 | 167.555 | 2003.8 | 26.09 | 47.623 | 6.32 | 1.327 | 4.702 | 8454.3 | 1.904 | 97.6 | 78 | 1302 | 23.81 | 5495.3 | 2827.6 | 2731.4 | 4055.4 | 1183.5 | 0.68161 | 6.027
2024-12-09 | 12:50 | Data | 0 | 32.501 | 30.428 | 178.94 | 7.65 | 167.465 | 2001.99 | 26.11 | 47.714 | 6.32 | 1.322 | 4.707 | 8097.05 | 2.113 | 97.6 | 78.1 | 1301 | 23.86 | 5263.1 | 2850.5 | 2767.2 | 4096.5 | 1183.5 | 0.67865 | 6.03
2024-12-09 | 12:50 | Data | 0 | 32.717 | 30.651 | 178.985 | 7.65 | 167.555 | 2001.99 | 26.1 | 47.623 | 6.32 | 1.314 | 4.689 | 8051.82 | 2.073 | 97.6 | 78.1 | 1301 | 23.86 | 5233.7 | 2842.5 | 2746.2 | 4074.4 | 1183.5 | 0.68147 | 6.003
2024-12-09 | 12:50 | Data | 0 | 32.892 | 30.874 | 179.121 | 7.65 | 167.646 | 2001.08 | 26.11 | 47.262 | 6.33 | 1.314 | 4.675 | 8042.78 | 2.052 | 97.6 | 78 | 1301 | 23.68 | 5227.8 | 2844.6 | 2738.3 | 4070.2 | 1183.5 | 0.68214 | 5.99
2024-12-09 | 12:50 | Data | 0 | 32.656 | 30.651 | 178.895 | 7.64 | 167.51 | 1999.28 | 26.1 | 47.443 | 6.33 | 1.321 | 4.669 | 8056.35 | 2.039 | 97.6 | 77.9 | 1300 | 23.72 | 5236.6 | 2845.5 | 2728.4 | 4063.9 | 1183.5 | 0.68437 | 5.989
2024-12-09 | 12:50 | Data | 0 | 32.514 | 30.637 | 178.985 | 7.64 | 167.646 | 1999.28 | 26.1 | 47.353 | 6.32 | 1.323 | 4.68 | 8060.87 | 1.877 | 97.6 | 78 | 1300 | 23.72 | 5239.6 | 2821 | 2727.1 | 4052.8 | 1183.5 | 0.68144 | 6.003
2024-12-09 | 12:50 | Data | 0 | 32.69 | 30.759 | 178.985 | 7.64 | 167.465 | 1995.66 | 26.1 | 47.353 | 6.32 | 1.321 | 4.706 | 8074.44 | 2.066 | 97.6 | 78.1 | 1297 | 23.72 | 5248.4 | 2846.1 | 2750.2 | 4079.3 | 1183.5 | 0.68258 | 6.028
2024-12-09 | 12:50 | Data | 0 | 32.723 | 30.833 | 179.075 | 7.64 | 167.555 | 1997.47 | 26.12 | 47.353 | 6.33 | 1.32 | 4.684 | 8074.44 | 2.086 | 97.6 | 78 | 1299 | 23.68 | 5248.4 | 2827.9 | 2764.7 | 4078.8 | 1183.5 | 0.67709 | 6.005
2024-12-09 | 12:50 | Data | 0 | 32.609 | 30.651 | 178.94 | 7.65 | 167.51 | 1995.66 | 26.1 | 47.353 | 6.32 | 1.327 | 4.674 | 8060.87 | 1.857 | 97.6 | 77.9 | 1298 | 23.68 | 5239.6 | 2833.1 | 2773.4 | 4091 | 1183.5 | 0.67685 | 6.002
2024-12-09 | 12:50 | Data | 0 | 32.501 | 31.083 | 179.121 | 7.64 | 167.51 | 1999.28 | 26.11 | 47.353 | 6.31 | 1.324 | 4.69 | 8060.87 | 1.857 | 97.6 | 78 | 1300 | 23.68 | 5239.6 | 2840.6 | 2723.5 | 4057.9 | 1183.5 | 0.68286 | 6.014
2024-12-09 | 12:50 | Data | 0 | 32.393 | 30.651 | 178.94 | 7.64 | 167.601 | 1996.57 | 26.11 | 47.353 | 6.32 | 1.321 | 4.686 | 8083.48 | 2.12 | 97.6 | 78 | 1297 | 23.68 | 5254.3 | 2843.5 | 2770.1 | 4094.5 | 1183.5 | 0.67835 | 6.007
2024-12-09 | 12:50 | Data | 0 | 32.933 | 30.705 | 179.03 | 7.64 | 167.555 | 1995.66 | 26.08 | 46.359 | 6.32 | 1.315 | 4.702 | 8069.91 | 2.046 | 97.7 | 78.1 | 1297 | 23.18 | 5245.4 | 2845.4 | 2780.8 | 4098.2 | 1183.5 | 0.67798 | 6.017
2024-12-09 | 12:50 | Data | 0 | 32.723 | 30.82 | 178.94 | 7.64 | 167.601 | 1995.66 | 26.1 | 46.269 | 6.32 | 1.324 | 4.692 | 8074.44 | 1.897 | 97.7 | 78 | 1297 | 23.13 | 5248.4 | 2843.5 | 2810.5 | 4120.1 | 1183.5 | 0.67314 | 6.016
2024-12-09 | 12:50 | Data | 0 | 32.561 | 30.428 | 178.985 | 7.64 | 167.601 | 1994.76 | 26.12 | 46.089 | 6.32 | 1.321 | 4.702 | 8074.44 | 1.904 | 97.7 | 78.1 | 1296 | 23.13 | 5248.4 | 2849.7 | 2793.7 | 4117 | 1183.5 | 0.67544 | 6.024
2024-12-09 | 12:50 | Data | 0 | 32.73 | 30.84 | 179.166 | 7.64 | 167.691 | 1993.85 | 26.1 | 47.353 | 6.32 | 1.322 | 4.684 | 8088 | 2.046 | 97.6 | 78 | 1295 | 23.72 | 5257.2 | 2829.7 | 2733.9 | 4062 | 1183.5 | 0.67894 | 6.007
2024-12-09 | 12:50 | Data | 0 | 32.75 | 30.651 | 179.075 | 7.64 | 167.555 | 1992.05 | 26.11 | 47.623 | 6.32 | 1.315 | 4.672 | 8083.48 | 1.877 | 97.6 | 78 | 1296 | 23.77 | 5254.3 | 2845.3 | 2742.6 | 4074.9 | 1183.5 | 0.68237 | 5.987
2024-12-09 | 12:50 | Data | 0 | 32.568 | 30.651 | 179.03 | 7.64 | 167.601 | 1990.24 | 26.11 | 47.353 | 6.32 | 1.319 | 4.693 | 8088 | 1.85 | 97.6 | 78.1 | 1294 | 23.72 | 5257.2 | 2833.8 | 2746.5 | 4069.7 | 1183.5 | 0.68036 | 6.012
2024-12-09 | 12:51 | Data | 0 | 33.135 | 30.88 | 179.075 | 7.64 | 167.691 | 1997.47 | 26.1 | 47.623 | 6.32 | 1.323 | 4.694 | 8088 | 2.012 | 97.6 | 78 | 1299 | 23.81 | 5257.2 | 2834.3 | 2764.5 | 4078.5 | 1183.5 | 0.67891 | 6.018
2024-12-09 | 12:51 | Data | 0 | 32.615 | 30.968 | 179.166 | 7.64 | 167.555 | 1998.37 | 26.11 | 47.623 | 6.33 | 1.329 | 4.683 | 8083.48 | 2.059 | 97.6 | 77.9 | 1298 | 23.81 | 5254.3 | 2843.7 | 2737.2 | 4069.3 | 1183.6 | 0.6822 | 6.014
2024-12-09 | 12:51 | Data | 0 | 32.723 | 30.651 | 178.985 | 7.65 | 167.51 | 1998.37 | 26.11 | 47.714 | 6.32 | 1.32 | 4.675 | 8088 | 2.073 | 97.6 | 78 | 1299 | 23.81 | 5257.2 | 2822.4 | 2745.4 | 4059.4 | 1183.6 | 0.68052 | 5.995
2024-12-09 | 12:51 | Data | 0 | 32.723 | 30.651 | 179.03 | 7.64 | 167.601 | 1998.37 | 26.11 | 47.262 | 6.32 | 1.319 | 4.675 | 8101.57 | 1.958 | 97.6 | 78 | 1299 | 23.68 | 5266 | 2820.1 | 2733 | 4051.3 | 1183.6 | 0.67914 | 5.994
2024-12-09 | 12:51 | Data | 0 | 32.953 | 30.88 | 179.121 | 7.64 | 167.691 | 1999.28 | 26.1 | 47.623 | 6.33 | 1.311 | 4.693 | 8115.14 | 2.073 | 97.6 | 78.2 | 1300 | 23.77 | 5274.8 | 2840.3 | 2728.8 | 4062.8 | 1183.6 | 0.6831 | 6.005
2024-12-09 | 12:51 | Data | 0 | 32.467 | 30.536 | 178.895 | 7.64 | 167.51 | 1999.28 | 26.11 | 47.714 | 6.32 | 1.309 | 4.682 | 8110.61 | 2.268 | 97.6 | 78.2 | 1300 | 23.81 | 5271.9 | 2864.2 | 2747.1 | 4085.9 | 1183.6 | 0.68441 | 5.99
2024-12-09 | 12:51 | Data | 0 | 33.054 | 30.658 | 179.075 | 7.64 | 167.601 | 1999.28 | 26.1 | 47.714 | 6.33 | 1.313 | 4.681 | 8124.18 | 1.83 | 97.6 | 78.1 | 1300 | 23.86 | 5280.7 | 2842.2 | 2725.5 | 4059.3 | 1183.6 | 0.68401 | 5.993
2024-12-09 | 12:51 | Data | 0 | 32.75 | 30.651 | 179.075 | 7.65 | 167.601 | 1999.28 | 26.1 | 47.623 | 6.32 | 1.321 | 4.673 | 8128.7 | 1.857 | 97.6 | 78 | 1299 | 23.86 | 5283.7 | 2840.9 | 2728.4 | 4060.4 | 1183.6 | 0.68396 | 5.993
2024-12-09 | 12:51 | Data | 0 | 32.723 | 30.651 | 179.121 | 7.64 | 167.601 | 1999.28 | 26.11 | 47.623 | 6.32 | 1.319 | 4.669 | 8083.48 | 2.073 | 97.6 | 78 | 1300 | 23.77 | 5254.3 | 2856.5 | 2746.5 | 4083.4 | 1183.6 | 0.68433 | 5.988
2024-12-09 | 12:51 | Data | 0 | 32.723 | 30.543 | 178.94 | 7.64 | 167.601 | 1998.37 | 26.11 | 47.623 | 6.32 | 1.322 | 4.68 | 8097.05 | 2.025 | 97.6 | 78 | 1299 | 23.81 | 5263.1 | 2842.3 | 2747.9 | 4077.2 | 1183.6 | 0.67906 | 6.002
2024-12-09 | 12:51 | Data | 0 | 32.609 | 30.624 | 178.94 | 7.64 | 167.465 | 1903.47 | 26.11 | 47.623 | 6.32 | 1.322 | 4.673 | 8106.09 | 1.884 | 97.5 | 77.9 | 1237 | 23.81 | 5269 | 2840.5 | 2718.2 | 4052.8 | 1183.6 | 0.68511 | 5.996
2024-12-09 | 12:51 | Data | 0 | 32.933 | 30.88 | 179.075 | 7.64 | 167.646 | 1996.57 | 26.11 | 47.623 | 6.32 | 1.315 | 4.688 | 8097.05 | 2.073 | 97.6 | 78.1 | 1298 | 23.81 | 5263.1 | 2838.4 | 2745.2 | 4071.7 | 1183.6 | 0.6806 | 6.002
2024-12-09 | 12:51 | Data | 0 | 33 | 30.482 | 179.121 | 7.64 | 167.691 | 1999.28 | 26.11 | 47.714 | 6.32 | 1.314 | 4.685 | 8101.57 | 1.965 | 97.6 | 78.1 | 1298 | 23.81 | 5266 | 2843.9 | 2736.7 | 4069.5 | 1183.6 | 0.68186 | 5.999
2024-12-09 | 12:51 | Data | 0 | 33.088 | 31.029 | 179.121 | 7.64 | 167.827 | 1998.37 | 26.11 | 47.623 | 6.33 | 1.328 | 4.66 | 8088 | 2.046 | 97.6 | 77.8 | 1299 | 23.9 | 5257.2 | 2843.8 | 2742.5 | 4073.7 | 1183.6 | 0.68134 | 5.988
2024-12-09 | 12:51 | Data | 0 | 32.825 | 30.968 | 179.302 | 7.64 | 167.601 | 2001.08 | 26.11 | 47.623 | 6.32 | 1.327 | 4.664 | 8106.09 | 2.086 | 97.6 | 77.9 | 1301 | 23.86 | 5269 | 2833.4 | 2708.8 | 4046.7 | 1183.6 | 0.6841 | 5.989
2024-12-09 | 12:51 | Data | 0 | 32.73 | 30.759 | 179.075 | 7.64 | 167.601 | 2001.99 | 26.11 | 47.623 | 6.33 | 1.322 | 4.655 | 8115.14 | 1.863 | 97.6 | 77.9 | 1301 | 23.77 | 5274.8 | 2853.3 | 2734.6 | 4072 | 1183.6 | 0.68438 | 5.978
2024-12-09 | 12:51 | Data | 0 | 32.723 | 30.766 | 179.075 | 7.64 | 167.601 | 2001.99 | 26.11 | 47.623 | 6.32 | 1.327 | 4.664 | 8097.05 | 2.066 | 97.6 | 77.9 | 1301 | 23.81 | 5263.1 | 2829.5 | 2735 | 4058.9 | 1183.6 | 0.68097 | 5.992
2024-12-09 | 12:52 | Data | 0 | 32.663 | 30.624 | 178.985 | 7.65 | 167.601 | 2001.08 | 26.11 | 47.623 | 6.32 | 1.321 | 4.654 | 8101.57 | 1.695 | 97.6 | 77.9 | 1300 | 23.77 | 5266 | 2842 | 2738.5 | 4068 | 1183.6 | 0.68308 | 5.977
2024-12-09 | 12:52 | Data | 0 | 32.777 | 30.658 | 179.075 | 7.64 | 167.646 | 2001.08 | 26.09 | 47.623 | 6.32 | 1.321 | 4.625 | 8097.05 | 1.87 | 97.6 | 77.8 | 1301 | 23.81 | 5263.1 | 2846.1 | 2718.7 | 4065.2 | 1183.6 | 0.68618 | 5.947
2024-12-09 | 12:52 | Data | 0 | 32.649 | 30.651 | 179.121 | 7.65 | 167.555 | 2001.99 | 26.11 | 47.714 | 6.32 | 1.317 | 4.665 | 8101.57 | 2.228 | 97.6 | 78 | 1301 | 23.86 | 5266 | 2865.8 | 2743.6 | 4093.2 | 1183.6 | 0.68367 | 5.979
2024-12-09 | 12:52 | Data | 0 | 32.622 | 30.678 | 179.075 | 7.64 | 167.601 | 2001.99 | 26.11 | 47.714 | 6.32 | 1.312 | 4.695 | 8101.57 | 2.133 | 97.6 | 78.2 | 1301 | 23.81 | 5266 | 2857.7 | 2730.7 | 4080.7 | 1183.6 | 0.68385 | 6.007
2024-12-09 | 12:52 | Data | 0 | 32.75 | 30.867 | 179.121 | 7.64 | 167.555 | 1998.37 | 26.09 | 47.623 | 6.33 | 1.312 | 4.691 | 8088 | 1.87 | 97.6 | 78.1 | 1299 | 23.81 | 5257.2 | 2857.1 | 2739.8 | 4085 | 1183.6 | 0.68374 | 6.006
2024-12-09 | 12:52 | Data | 0 | 32.94 | 30.874 | 179.121 | 7.64 | 167.646 | 1991.14 | 26.11 | 47.714 | 6.32 | 1.318 | 4.701 | 8051.82 | 1.992 | 97.6 | 78.1 | 1294 | 23.86 | 5233.7 | 2864.4 | 2723.9 | 4067.8 | 1183.6 | 0.68825 | 6.018
2024-12-09 | 12:52 | Data | 0 | 33.115 | 30.779 | 179.211 | 7.64 | 167.691 | 1995.66 | 26.11 | 47.623 | 6.33 | 1.314 | 4.681 | 8078.96 | 2.106 | 97.6 | 78.1 | 1298 | 23.81 | 5251.3 | 2862.6 | 2722.6 | 4077 | 1183.6 | 0.68557 | 5.995
2024-12-09 | 12:52 | Data | 0 | 32.71 | 30.651 | 179.075 | 7.64 | 167.601 | 1994.76 | 26.11 | 47.623 | 6.33 | 1.318 | 4.682 | 8056.35 | 2.073 | 97.6 | 78 | 1297 | 23.81 | 5236.6 | 2840.9 | 2721.7 | 4063 | 1183.6 | 0.68273 | 5.999
2024-12-09 | 12:52 | Data | 0 | 32.737 | 30.988 | 179.121 | 7.64 | 167.646 | 1996.57 | 26.1 | 47.623 | 6.33 | 1.323 | 4.667 | 8069.91 | 1.735 | 97.6 | 77.9 | 1298 | 23.9 | 5245.4 | 2857.7 | 2730 | 4072.7 | 1183.6 | 0.6849 | 5.99
2024-12-09 | 12:52 | Data | 0 | 33.048 | 30.934 | 179.166 | 7.64 | 167.691 | 1996.57 | 26.1 | 47.623 | 6.32 | 1.32 | 4.685 | 8051.82 | 2.066 | 97.6 | 78 | 1297 | 23.81 | 5233.7 | 2877.7 | 2721.9 | 4089.7 | 1183.6 | 0.68459 | 6.006
2024-12-09 | 12:52 | Data | 0 | 33.088 | 31.083 | 179.211 | 7.63 | 167.691 | 1996.57 | 26.11 | 47.623 | 6.32 | 1.315 | 4.681 | 8069.91 | 2.16 | 97.6 | 78 | 1298 | 23.81 | 5245.4 | 2877.7 | 2733.2 | 4095.8 | 1183.6 | 0.68469 | 5.997
2024-12-09 | 12:52 | Data | 0 | 32.723 | 30.651 | 179.166 | 7.64 | 167.646 | 1995.66 | 26.1 | 47.623 | 6.32 | 1.314 | 4.689 | 8056.35 | 2.073 | 97.6 | 78.1 | 1297 | 23.81 | 5236.6 | 2863.6 | 2713.8 | 4071 | 1183.6 | 0.68681 | 6.003
2024-12-09 | 12:52 | Data | 0 | 32.798 | 30.772 | 179.211 | 7.64 | 167.736 | 1995.66 | 26.1 | 47.623 | 6.32 | 1.319 | 4.698 | 8083.48 | 2.073 | 97.6 | 78.1 | 1297 | 23.81 | 5254.3 | 2869.5 | 2707.7 | 4074 | 1183.6 | 0.68669 | 6.017
2024-12-09 | 12:52 | Data | 0 | 32.757 | 30.658 | 179.121 | 7.64 | 167.646 | 1996.57 | 26.11 | 47.533 | 6.32 | 1.323 | 4.721 | 8056.35 | 2.019 | 97.6 | 78.1 | 1298 | 23.86 | 5236.6 | 2871.2 | 2737.4 | 4096.1 | 1183.6 | 0.68452 | 6.043
2024-12-09 | 12:52 | Data | 0 | 32.615 | 30.637 | 179.075 | 7.64 | 167.601 | 1996.57 | 26.1 | 47.623 | 6.33 | 1.319 | 4.691 | 8078.96 | 1.958 | 97.6 | 78.1 | 1298 | 23.86 | 5251.3 | 2885 | 2748.5 | 4104.2 | 1183.6 | 0.68748 | 6.008
2024-12-09 | 12:52 | Data | 0 | 32.926 | 30.88 | 179.121 | 7.64 | 167.646 | 1996.57 | 26.11 | 47.714 | 6.32 | 1.313 | 4.656 | 8074.44 | 2.066 | 97.6 | 78 | 1298 | 23.77 | 5248.4 | 2886.8 | 2751 | 4112 | 1183.6 | 0.68453 | 5.97
2024-12-09 | 12:52 | Data | 0 | 33.054 | 30.705 | 179.166 | 7.64 | 167.827 | 1996.57 | 26.09 | 47.623 | 6.33 | 1.314 | 4.67 | 8056.35 | 2.025 | 97.6 | 78 | 1297 | 23.81 | 5236.6 | 2878.6 | 2737.6 | 4096.4 | 1183.6 | 0.68664 | 5.986
2024-12-09 | 12:52 | Data | 0 | 32.838 | 30.489 | 179.03 | 7.64 | 167.646 | 2000.18 | 26.1 | 47.714 | 6.32 | 1.318 | 4.675 | 8069.91 | 2.066 | 97.6 | 78 | 1301 | 23.81 | 5245.4 | 2875.2 | 2747 | 4101.9 | 1183.6 | 0.68397 | 5.992
2024-12-09 | 12:52 | Data | 0 | 32.757 | 30.766 | 179.121 | 7.64 | 167.736 | 1990.24 | 26.11 | 47.623 | 6.32 | 1.314 | 4.685 | 8056.35 | 1.87 | 97.6 | 78.1 | 1294 | 23.81 | 5236.6 | 2869.2 | 2723 | 4100.4 | 1183.6 | 0.68607 | 6
2024-12-09 | 12:53 | Data | 0 | 32.777 | 30.489 | 179.075 | 7.64 | 167.646 | 1990.24 | 26.11 | 47.623 | 6.32 | 1.315 | 4.675 | 8033.74 | 2.066 | 97.6 | 78 | 1294 | 23.81 | 5221.9 | 2860.8 | 2739.8 | 4086.6 | 1183.6 | 0.68348 | 5.99
2024-12-09 | 12:53 | Data | 0 | 32.501 | 30.637 | 178.985 | 7.64 | 167.601 | 1990.24 | 26.11 | 47.714 | 6.32 | 1.324 | 4.691 | 8038.26 | 1.857 | 97.6 | 78 | 1294 | 23.81 | 5224.9 | 2871.8 | 2735.4 | 4093 | 1183.6 | 0.68464 | 6.016
2024-12-09 | 12:53 | Data | 0 | 32.737 | 30.705 | 179.075 | 7.64 | 167.646 | 1986.62 | 26.11 | 47.714 | 6.32 | 1.328 | 4.673 | 8024.69 | 1.965 | 97.6 | 77.9 | 1291 | 23.81 | 5216 | 2867.9 | 2730.5 | 4085.8 | 1183.6 | 0.68425 | 6
2024-12-09 | 12:53 | Data | 0 | 33.108 | 30.732 | 179.166 | 7.64 | 167.646 | 1990.24 | 26.11 | 47.623 | 6.32 | 1.328 | 4.69 | 8029.21 | 2.174 | 97.6 | 77.9 | 1294 | 23.81 | 5219 | 2863.3 | 2736 | 4088.8 | 1183.7 | 0.68235 | 6.017
2024-12-09 | 12:53 | Data | 0 | 32.838 | 30.88 | 179.075 | 7.64 | 167.646 | 1990.24 | 26.11 | 47.623 | 6.32 | 1.322 | 4.687 | 8047.3 | 2.019 | 97.6 | 78 | 1293 | 23.86 | 5230.7 | 2859.5 | 2762.5 | 4103.9 | 1183.7 | 0.68077 | 6.008
2024-12-09 | 12:53 | Data | 0 | 32.892 | 30.982 | 179.121 | 7.64 | 167.736 | 1993.85 | 26.11 | 47.623 | 6.32 | 1.31 | 4.682 | 8083.48 | 1.857 | 97.6 | 78.1 | 1295 | 23.77 | 5254.3 | 2859.4 | 2752.1 | 4095 | 1183.7 | 0.68484 | 5.991
2024-12-09 | 12:53 | Data | 0 | 32.642 | 30.651 | 179.121 | 7.64 | 167.691 | 1999.28 | 26.11 | 47.533 | 6.32 | 1.308 | 4.683 | 8088 | 1.863 | 97.6 | 78.2 | 1300 | 23.86 | 5257.2 | 2877.6 | 2756.4 | 4111.1 | 1183.7 | 0.68338 | 5.988
2024-12-09 | 12:53 | Data | 0 | 32.723 | 30.826 | 179.075 | 7.64 | 167.555 | 1996.57 | 26.09 | 47.623 | 6.32 | 1.311 | 4.676 | 8074.44 | 1.958 | 97.6 | 78.1 | 1298 | 23.77 | 5248.4 | 2866.9 | 2764 | 4114.3 | 1183.7 | 0.6802 | 5.988
2024-12-09 | 12:53 | Data | 0 | 32.926 | 30.685 | 179.075 | 7.64 | 167.646 | 1996.57 | 26.1 | 47.623 | 6.32 | 1.318 | 4.688 | 8092.52 | 2.046 | 97.6 | 78.1 | 1298 | 23.86 | 5260.1 | 2902.6 | 2741.4 | 4120.4 | 1183.7 | 0.68641 | 6.003
2024-12-09 | 12:53 | Data | 0 | 32.723 | 30.651 | 179.166 | 7.64 | 167.646 | 1990.24 | 26.11 | 47.623 | 6.32 | 1.315 | 4.69 | 8088 | 2.073 | 97.6 | 78.1 | 1294 | 23.81 | 5257.2 | 2808.4 | 2731 | 4037.4 | 1183.7 | 0.67992 | 6.005
2024-12-09 | 12:53 | Data | 0 | 32.723 | 30.651 | 179.121 | 7.64 | 167.601 | 1995.66 | 26.11 | 47.714 | 6.32 | 1.315 | 4.664 | 8101.57 | 2.066 | 97.6 | 78 | 1297 | 23.86 | 5266 | 2793.4 | 2725.7 | 4025 | 1183.7 | 0.6753 | 5.979
2024-12-09 | 12:53 | Data | 0 | 32.669 | 30.651 | 179.075 | 7.64 | 167.646 | 1995.66 | 26.11 | 47.533 | 6.32 | 1.309 | 4.664 | 8092.52 | 2.066 | 97.6 | 78.1 | 1298 | 23.81 | 5260.1 | 2796.9 | 2743.4 | 4037.2 | 1183.7 | 0.67756 | 5.973
2024-12-09 | 12:53 | Data | 0 | 32.723 | 30.651 | 179.075 | 7.64 | 167.646 | 1998.37 | 26.11 | 47.623 | 6.33 | 1.32 | 4.676 | 8097.05 | 2.073 | 97.6 | 78 | 1299 | 23.86 | 5263.1 | 2785.6 | 2740.5 | 4028.4 | 1183.7 | 0.67606 | 5.997
2024-12-09 | 12:53 | Data | 0 | 32.838 | 30.435 | 179.211 | 7.64 | 167.691 | 1998.37 | 26.12 | 47.623 | 6.33 | 1.312 | 4.681 | 8106.09 | 2.12 | 97.6 | 78.1 | 1300 | 23.86 | 5269 | 2797.3 | 2718.3 | 4024 | 1183.7 | 0.67937 | 5.992
2024-12-09 | 12:53 | Data | 0 | 32.71 | 30.631 | 179.03 | 7.64 | 167.646 | 1998.37 | 26.11 | 47.714 | 6.32 | 1.33 | 4.669 | 8101.57 | 2.16 | 97.6 | 77.8 | 1299 | 23.86 | 5266 | 2790.1 | 2725.5 | 4020.5 | 1183.7 | 0.6774 | 5.998
2024-12-09 | 12:53 | Data | 0 | 32.71 | 30.651 | 179.121 | 7.64 | 167.51 | 2001.08 | 26.11 | 47.714 | 6.32 | 1.329 | 4.702 | 8097.05 | 2.073 | 97.6 | 78 | 1301 | 23.81 | 5263.1 | 2792.2 | 2730 | 4017.7 | 1183.7 | 0.67614 | 6.033
2024-12-09 | 12:53 | Data | 0 | 32.501 | 30.637 | 178.94 | 7.64 | 167.646 | 2001.99 | 26.1 | 47.533 | 6.32 | 1.322 | 4.683 | 8051.82 | 2.032 | 97.6 | 78 | 1301 | 23.81 | 5233.7 | 2798.7 | 2725.6 | 4038.5 | 1183.7 | 0.67815 | 6.006
2024-12-09 | 12:54 | Data | 0 | 32.609 | 30.651 | 179.075 | 7.65 | 167.691 | 2001.99 | 26.1 | 47.714 | 6.32 | 1.321 | 4.694 | 8074.44 | 1.857 | 97.6 | 78 | 1301 | 23.81 | 5248.4 | 2852.8 | 2733.4 | 4076.3 | 1183.7 | 0.68348 | 6.016
2024-12-09 | 12:54 | Data | 0 | 32.73 | 30.826 | 179.121 | 7.64 | 167.736 | 1999.28 | 26.1 | 47.623 | 6.33 | 1.32 | 4.697 | 8074.44 | 1.958 | 97.6 | 78.1 | 1300 | 23.81 | 5248.4 | 2852.2 | 2740.9 | 4079.5 | 1183.7 | 0.68247 | 6.018
2024-12-09 | 12:54 | Data | 0 | 33 | 30.664 | 179.03 | 7.64 | 167.736 | 2005.6 | 26.1 | 47.623 | 6.32 | 1.321 | 4.688 | 8056.35 | 1.911 | 97.6 | 78 | 1304 | 23.9 | 5236.6 | 2850.7 | 2731.6 | 4078.4 | 1183.7 | 0.68189 | 6.007
2024-12-09 | 12:54 | Data | 0 | 32.953 | 30.786 | 178.94 | 7.64 | 167.646 | 2005.6 | 26.11 | 47.623 | 6.32 | 1.325 | 4.682 | 8060.87 | 2.052 | 97.6 | 77.9 | 1303 | 23.86 | 5239.6 | 2860.2 | 2726.6 | 4077.5 | 1183.7 | 0.68497 | 6.008
2024-12-09 | 12:54 | Data | 0 | 32.548 | 30.475 | 179.121 | 7.64 | 167.646 | 2004.7 | 26.1 | 47.623 | 6.32 | 1.309 | 4.677 | 8056.35 | 1.911 | 97.6 | 78.1 | 1303 | 23.77 | 5236.6 | 2847.6 | 2743.7 | 4080.4 | 1183.7 | 0.68134 | 5.985
2024-12-09 | 12:54 | Data | 0 | 32.723 | 30.678 | 179.03 | 7.64 | 167.646 | 2007.41 | 26.11 | 47.623 | 6.32 | 1.322 | 4.659 | 8056.35 | 1.965 | 97.6 | 77.9 | 1305 | 23.86 | 5236.6 | 2861.5 | 2738.4 | 4085 | 1183.7 | 0.68602 | 5.982
2024-12-09 | 12:54 | Data | 0 | 32.71 | 30.651 | 178.985 | 7.65 | 167.691 | 2008.32 | 26.11 | 47.714 | 6.32 | 1.322 | 4.668 | 8051.82 | 2.073 | 97.6 | 77.9 | 1306 | 23.86 | 5233.7 | 2853.5 | 2732.8 | 4073.7 | 1183.7 | 0.68383 | 5.99
2024-12-09 | 12:54 | Data | 0 | 32.683 | 30.448 | 179.03 | 7.64 | 167.646 | 2009.22 | 26.1 | 47.623 | 6.32 | 1.317 | 4.716 | 8074.44 | 2.235 | 97.6 | 78.2 | 1306 | 23.86 | 5248.4 | 2847.7 | 2731.1 | 4071.1 | 1183.7 | 0.68304 | 6.033
2024-12-09 | 12:54 | Data | 0 | 32.946 | 30.705 | 179.211 | 7.64 | 167.736 | 2007.41 | 26.11 | 47.623 | 6.32 | 1.317 | 4.691 | 8074.44 | 2.073 | 97.6 | 78.1 | 1304 | 23.86 | 5248.4 | 2855 | 2735.7 | 4078.9 | 1183.7 | 0.68373 | 6.007
2024-12-09 | 12:54 | Data | 0 | 32.609 | 30.55 | 178.985 | 7.64 | 167.646 | 2007.41 | 26.11 | 47.623 | 6.33 | 1.32 | 4.673 | 8074.44 | 1.884 | 97.6 | 78 | 1305 | 23.81 | 5248.4 | 2853.8 | 2741.9 | 4083.4 | 1183.7 | 0.68294 | 5.991
2024-12-09 | 12:54 | Data | 0 | 32.501 | 30.543 | 178.985 | 7.64 | 167.555 | 2006.51 | 26.1 | 47.714 | 6.32 | 1.319 | 4.703 | 8069.91 | 2.052 | 97.6 | 78.1 | 1304 | 23.81 | 5245.4 | 2848.8 | 2727.4 | 4070.6 | 1183.7 | 0.6838 | 6.021
2024-12-09 | 12:54 | Data | 0 | 32.548 | 30.739 | 179.03 | 7.65 | 167.601 | 2006.51 | 26.11 | 47.533 | 6.32 | 1.32 | 4.694 | 8069.91 | 1.877 | 97.6 | 78.1 | 1304 | 23.81 | 5245.4 | 2845.9 | 2720.9 | 4065.8 | 1183.7 | 0.6817 | 6.014
2024-12-09 | 12:54 | Data | 0 | 32.568 | 30.428 | 179.03 | 7.64 | 167.601 | 2003.8 | 26.11 | 47.623 | 6.32 | 1.329 | 4.682 | 8088 | 1.951 | 97.6 | 77.9 | 1302 | 23.81 | 5257.2 | 2844.7 | 2739.4 | 4077.1 | 1183.7 | 0.6816 | 6.007
2024-12-09 | 12:54 | Data | 0 | 32.494 | 30.543 | 178.94 | 7.64 | 167.601 | 2003.8 | 26.11 | 47.714 | 6.32 | 1.32 | 4.684 | 8097.05 | 2.167 | 97.6 | 78 | 1302 | 23.86 | 5263.1 | 2839.4 | 2729.9 | 4064.1 | 1183.7 | 0.68262 | 6.004
2024-12-09 | 12:54 | Data | 0 | 32.278 | 30.428 | 178.849 | 7.64 | 167.465 | 2003.8 | 26.1 | 47.714 | 6.33 | 1.317 | 4.667 | 8115.14 | 2.025 | 97.6 | 78 | 1302 | 23.86 | 5274.8 | 2857.1 | 2674.1 | 4037.7 | 1183.7 | 0.69187 | 5.983
2024-12-09 | 12:54 | Data | 0 | 32.669 | 30.874 | 178.94 | 7.64 | 167.51 | 2002.89 | 26.11 | 47.623 | 6.32 | 1.317 | 4.639 | 8115.14 | 1.965 | 97.6 | 77.9 | 1302 | 23.86 | 5274.8 | 2868.6 | 2713.3 | 4071.4 | 1183.7 | 0.68937 | 5.956
2024-12-09 | 12:54 | Data | 0 | 32.507 | 30.597 | 178.985 | 7.64 | 167.465 | 2001.08 | 26.11 | 47.533 | 6.32 | 1.32 | 4.666 | 8069.91 | 1.897 | 97.6 | 77.9 | 1301 | 23.81 | 5245.4 | 2853.5 | 2751.5 | 4085.5 | 1183.7 | 0.68039 | 5.987
2024-12-09 | 12:54 | Data | 0 | 32.494 | 30.799 | 178.985 | 7.64 | 167.555 | 2000.18 | 26.11 | 47.623 | 6.32 | 1.328 | 4.673 | 8078.96 | 1.965 | 97.6 | 77.8 | 1300 | 23.77 | 5251.3 | 2851.8 | 2744.7 | 4081.2 | 1183.7 | 0.68315 | 6.003
2024-12-09 | 12:55 | Data | 0 | 32.494 | 30.536 | 178.895 | 7.65 | 167.465 | 2001.08 | 26.11 | 47.714 | 6.32 | 1.331 | 4.689 | 8074.44 | 2.073 | 97.6 | 77.9 | 1301 | 23.86 | 5248.4 | 2840 | 2718.9 | 4051.3 | 1183.7 | 0.68528 | 6.02
2024-12-09 | 12:55 | Data | 0 | 32.548 | 30.252 | 178.759 | 7.64 | 167.375 | 2001.99 | 26.11 | 47.714 | 6.32 | 1.321 | 4.682 | 8083.48 | 2.093 | 97.6 | 78 | 1301 | 23.86 | 5254.3 | 2847.2 | 2718.9 | 4059.7 | 1183.7 | 0.68435 | 6.004
2024-12-09 | 12:55 | Data | 0 | 32.096 | 30.307 | 178.668 | 7.64 | 167.375 | 2001.99 | 26.1 | 47.714 | 6.32 | 1.318 | 4.657 | 8128.7 | 1.965 | 97.6 | 77.9 | 1301 | 23.81 | 5283.7 | 2849.3 | 2737.2 | 4069.9 | 1183.7 | 0.68268 | 5.975
2024-12-09 | 12:55 | Data | 0 | 32.278 | 30.246 | 178.804 | 7.64 | 167.42 | 2001.08 | 26.11 | 47.533 | 6.33 | 1.314 | 4.657 | 8101.57 | 1.843 | 97.6 | 78 | 1301 | 23.86 | 5266 | 2830.4 | 2711 | 4037.9 | 1183.7 | 0.68182 | 5.974
2024-12-09 | 12:55 | Data | 0 | 32.71 | 30.759 | 179.03 | 7.64 | 167.601 | 2002.89 | 26.11 | 47.172 | 6.32 | 1.32 | 4.672 | 8110.61 | 1.978 | 97.7 | 78 | 1302 | 23.59 | 5271.9 | 2838.7 | 2717.8 | 4051.5 | 1183.7 | 0.68413 | 5.99
2024-12-09 | 12:55 | Data | 0 | 32.501 | 30.428 | 178.985 | 7.64 | 167.601 | 2001.08 | 26.1 | 47.262 | 6.32 | 1.329 | 4.674 | 8097.05 | 2.052 | 97.6 | 77.9 | 1301 | 23.63 | 5263.1 | 2845.9 | 2736.2 | 4071.7 | 1183.8 | 0.68354 | 6.003
2024-12-09 | 12:55 | Data | 0 | 32.636 | 30.428 | 178.985 | 7.64 | 167.51 | 2002.89 | 26.11 | 47.262 | 6.32 | 1.329 | 4.651 | 8083.48 | 1.978 | 97.6 | 77.8 | 1301 | 23.68 | 5254.3 | 2832.9 | 2739.2 | 4063.2 | 1183.8 | 0.6798 | 5.98
2024-12-09 | 12:55 | Data | 0 | 32.683 | 30.442 | 179.075 | 7.64 | 167.555 | 2006.51 | 26.12 | 47.262 | 6.32 | 1.311 | 4.652 | 8097.05 | 2.127 | 97.6 | 78 | 1305 | 23.68 | 5263.1 | 2851 | 2724.4 | 4066.9 | 1183.8 | 0.68245 | 5.961
2024-12-09 | 12:55 | Data | 0 | 32.892 | 30.867 | 178.985 | 7.64 | 167.51 | 2001.99 | 26.1 | 47.353 | 6.32 | 1.312 | 4.685 | 8083.48 | 2.106 | 97.6 | 78.1 | 1301 | 23.68 | 5254.3 | 2838.5 | 2727 | 4056.1 | 1183.8 | 0.68477 | 5.997
2024-12-09 | 12:55 | Data | 0 | 32.669 | 30.442 | 179.121 | 7.64 | 167.555 | 2001.08 | 26.13 | 47.353 | 6.32 | 1.322 | 4.672 | 8083.48 | 2.241 | 97.6 | 77.9 | 1301 | 23.72 | 5254.3 | 2845.1 | 2723 | 4058.5 | 1183.8 | 0.68484 | 5.994
2024-12-09 | 12:55 | Data | 0 | 32.919 | 30.826 | 179.075 | 7.64 | 167.646 | 2001.99 | 26.12 | 47.353 | 6.32 | 1.33 | 4.677 | 8092.52 | 2.12 | 97.6 | 77.9 | 1301 | 23.72 | 5260.1 | 2827.6 | 2724.2 | 4047 | 1183.8 | 0.68172 | 6.007
2024-12-09 | 12:55 | Data | 0 | 32.528 | 30.597 | 179.03 | 7.64 | 167.555 | 2001.08 | 26.13 | 47.353 | 6.32 | 1.32 | 4.666 | 8092.52 | 2.073 | 97.6 | 78 | 1300 | 23.68 | 5260.1 | 2837.8 | 2733.4 | 4061.4 | 1183.8 | 0.68216 | 5.986
2024-12-09 | 12:55 | Data | 0 | 32.467 | 30.651 | 178.94 | 7.64 | 167.601 | 2003.8 | 26.12 | 47.353 | 6.32 | 1.32 | 4.685 | 8097.05 | 2.059 | 97.6 | 78 | 1302 | 23.63 | 5263.1 | 2851.7 | 2744.7 | 4079.2 | 1183.8 | 0.68373 | 6.005
2024-12-09 | 12:55 | Data | 0 | 32.71 | 30.664 | 179.075 | 7.64 | 167.646 | 2003.8 | 26.12 | 47.353 | 6.32 | 1.317 | 4.683 | 8115.14 | 2.241 | 97.6 | 78.1 | 1303 | 23.68 | 5274.8 | 2834 | 2757.1 | 4078.9 | 1183.8 | 0.67923 | 5.998
2024-12-09 | 12:55 | Data | 0 | 32.467 | 30.739 | 178.895 | 7.64 | 167.555 | 2005.6 | 26.12 | 47.533 | 6.32 | 1.322 | 4.663 | 8074.44 | 2.066 | 97.6 | 77.9 | 1303 | 23.72 | 5248.4 | 2843.5 | 2742 | 4075.7 | 1183.8 | 0.6825 | 5.986
2024-12-09 | 12:55 | Data | 0 | 32.548 | 30.651 | 178.985 | 7.64 | 167.555 | 2004.7 | 26.12 | 47.353 | 6.32 | 1.325 | 4.671 | 8069.91 | 2.046 | 97.6 | 77.9 | 1302 | 23.68 | 5245.4 | 2861.3 | 2741.1 | 4078.9 | 1183.8 | 0.68565 | 5.997
2024-12-09 | 12:55 | Data | 0 | 32.744 | 30.475 | 179.075 | 7.64 | 167.555 | 2003.8 | 26.12 | 47.353 | 6.33 | 1.319 | 4.664 | 8513.09 | 1.863 | 97.6 | 78 | 1303 | 23.68 | 5533.5 | 2854.8 | 2729.5 | 4072.3 | 1183.8 | 0.68441 | 5.982
2024-12-09 | 12:56 | Data | 0 | 33.142 | 30.779 | 179.121 | 7.64 | 167.691 | 2003.8 | 26.13 | 47.262 | 6.32 | 1.318 | 4.682 | 8490.48 | 2.093 | 97.6 | 78 | 1302 | 23.68 | 5518.8 | 2843.7 | 2735.7 | 4064.8 | 1183.8 | 0.68263 | 5.998
2024-12-09 | 12:56 | Data | 0 | 32.717 | 30.475 | 179.03 | 7.64 | 167.601 | 2002.89 | 26.12 | 47.353 | 6.32 | 1.312 | 4.689 | 8069.91 | 1.897 | 97.6 | 78.1 | 1302 | 23.68 | 5245.4 | 2846.6 | 2730.9 | 4069.9 | 1183.8 | 0.683 | 6.002
2024-12-09 | 12:56 | Data | 0 | 32.811 | 30.448 | 178.985 | 7.64 | 167.555 | 2001.99 | 26.12 | 47.443 | 6.32 | 1.317 | 4.698 | 8088 | 2.248 | 97.6 | 78.1 | 1301 | 23.68 | 5257.2 | 2856.3 | 2737.9 | 4074.4 | 1183.8 | 0.68455 | 6.016
2024-12-09 | 12:56 | Data | 0 | 32.494 | 30.678 | 179.075 | 7.64 | 167.555 | 2001.99 | 26.12 | 47.262 | 6.32 | 1.317 | 4.702 | 8074.44 | 1.992 | 97.6 | 78.1 | 1302 | 23.68 | 5248.4 | 2838 | 2739.4 | 4066.9 | 1183.8 | 0.68157 | 6.018
2024-12-09 | 12:56 | Data | 0 | 32.865 | 30.658 | 179.211 | 7.64 | 167.736 | 2001.99 | 26.12 | 47.533 | 6.32 | 1.313 | 4.702 | 8097.05 | 2.106 | 97.6 | 78.2 | 1301 | 23.72 | 5263.1 | 2843 | 2751.7 | 4078.9 | 1183.8 | 0.68111 | 6.015
2024-12-09 | 12:56 | Data | 0 | 32.933 | 30.766 | 179.03 | 7.64 | 167.691 | 2001.08 | 26.11 | 47.262 | 6.33 | 1.321 | 4.672 | 8088 | 2.073 | 97.6 | 78 | 1301 | 23.68 | 5257.2 | 2840.3 | 2737.3 | 4066.9 | 1183.8 | 0.68242 | 5.993
2024-12-09 | 12:56 | Data | 0 | 32.723 | 30.59 | 178.985 | 7.64 | 167.555 | 2001.08 | 26.12 | 47.353 | 6.33 | 1.321 | 4.658 | 8083.48 | 1.992 | 97.6 | 77.9 | 1300 | 23.68 | 5254.3 | 2833.7 | 2721.2 | 4049.9 | 1183.8 | 0.68542 | 5.979
2024-12-09 | 12:56 | Data | 0 | 32.44 | 30.536 | 178.94 | 7.63 | 167.51 | 2001.08 | 26.11 | 47.353 | 6.32 | 1.305 | 4.667 | 8083.48 | 2.181 | 97.6 | 78.1 | 1301 | 23.68 | 5254.3 | 2852.2 | 2734.7 | 4072 | 1183.8 | 0.68302 | 5.972
2024-12-09 | 12:56 | Data | 0 | 32.723 | 30.637 | 179.03 | 7.64 | 167.601 | 2001.99 | 26.12 | 47.262 | 6.32 | 1.31 | 4.682 | 8088 | 2.012 | 97.6 | 78.1 | 1301 | 23.68 | 5257.2 | 2842.7 | 2748.3 | 4075.8 | 1183.8 | 0.68156 | 5.991
2024-12-09 | 12:56 | Data | 0 | 32.75 | 30.421 | 179.03 | 7.64 | 167.646 | 2001.08 | 26.12 | 47.443 | 6.32 | 1.317 | 4.697 | 8083.48 | 2.174 | 97.6 | 78.1 | 1301 | 23.72 | 5254.3 | 2849.1 | 2740.3 | 4074.3 | 1183.8 | 0.68134 | 6.012
2024-12-09 | 12:56 | Data | 0 | 32.507 | 30.84 | 179.166 | 7.64 | 167.555 | 1997.47 | 26.12 | 47.443 | 6.32 | 1.314 | 4.673 | 8069.91 | 1.904 | 97.6 | 78.1 | 1298 | 23.72 | 5245.4 | 2842.1 | 2739.4 | 4071.6 | 1183.8 | 0.68099 | 5.986
2024-12-09 | 12:56 | Data | 0 | 32.501 | 30.536 | 178.985 | 7.64 | 167.51 | 2001.99 | 26.11 | 47.353 | 6.32 | 1.314 | 4.657 | 8088 | 2.073 | 97.6 | 78 | 1301 | 23.68 | 5257.2 | 2840.9 | 2722 | 4058.6 | 1183.8 | 0.68226 | 5.972
2024-12-09 | 12:56 | Data | 0 | 32.926 | 30.793 | 179.03 | 7.64 | 167.646 | 1999.28 | 26.13 | 47.353 | 6.32 | 1.32 | 4.702 | 8083.48 | 2.052 | 97.6 | 78.1 | 1300 | 23.68 | 5254.3 | 2830 | 2735.9 | 4058.9 | 1183.8 | 0.68158 | 6.02
2024-12-09 | 12:56 | Data | 0 | 32.892 | 30.806 | 179.075 | 7.64 | 167.646 | 1998.37 | 26.11 | 47.443 | 6.32 | 1.319 | 4.677 | 8074.44 | 1.978 | 97.6 | 78 | 1298 | 23.63 | 5248.4 | 2853.1 | 2750.9 | 4081.5 | 1183.8 | 0.68296 | 5.993
2024-12-09 | 12:56 | Data | 0 | 32.73 | 30.658 | 179.075 | 7.64 | 167.691 | 1998.37 | 26.11 | 47.443 | 6.32 | 1.314 | 4.679 | 8074.44 | 2.059 | 97.6 | 78.1 | 1298 | 23.72 | 5248.4 | 2842.8 | 2758.5 | 4085.9 | 1183.8 | 0.67843 | 5.994
2024-12-09 | 12:56 | Data | 0 | 32.953 | 30.732 | 179.256 | 7.64 | 167.691 | 1999.28 | 26.11 | 47.443 | 6.32 | 1.323 | 4.687 | 8074.44 | 1.965 | 97.6 | 78 | 1300 | 23.72 | 5248.4 | 2852.5 | 2780.2 | 4104.2 | 1183.8 | 0.67847 | 6.01
2024-12-09 | 12:56 | Data | 0 | 32.764 | 30.658 | 179.075 | 7.64 | 167.646 | 1997.47 | 26.12 | 47.443 | 6.32 | 1.324 | 4.698 | 8074.44 | 2.079 | 97.6 | 78 | 1298 | 23.72 | 5248.4 | 2845.9 | 2735.4 | 4067 | 1183.8 | 0.68306 | 6.021
2024-12-09 | 12:56 | Data | 0 | 32.831 | 30.435 | 179.166 | 7.64 | 167.646 | 1997.47 | 26.11 | 46.991 | 6.32 | 1.323 | 4.692 | 8115.14 | 2.079 | 97.6 | 78 | 1298 | 23.54 | 5274.8 | 2832.8 | 2726 | 4053 | 1183.8 | 0.68259 | 6.015
2024-12-09 | 12:57 | Data | 0 | 32.696 | 30.489 | 178.94 | 7.63 | 167.555 | 1992.05 | 26.11 | 47.623 | 6.32 | 1.325 | 4.672 | 8101.57 | 2.025 | 97.6 | 77.9 | 1295 | 23.81 | 5266 | 2846.8 | 2739.6 | 4071.3 | 1183.8 | 0.6836 | 5.998
2024-12-09 | 12:57 | Data | 0 | 32.561 | 30.597 | 179.03 | 7.64 | 167.555 | 1993.85 | 26.11 | 47.443 | 6.32 | 1.315 | 4.655 | 8101.57 | 1.796 | 97.6 | 78 | 1296 | 23.77 | 5266 | 2844.7 | 2724.6 | 4059.2 | 1183.8 | 0.68501 | 5.972
2024-12-09 | 12:57 | Data | 0 | 32.534 | 30.563 | 179.03 | 7.64 | 167.601 | 1995.66 | 26.1 | 47.533 | 6.32 | 1.314 | 4.663 | 8101.57 | 1.843 | 97.6 | 78 | 1297 | 23.77 | 5266 | 2826.2 | 2732.5 | 4050.8 | 1183.8 | 0.68014 | 5.978
2024-12-09 | 12:57 | Data | 0 | 32.561 | 30.874 | 179.075 | 7.64 | 167.736 | 1996.57 | 26.11 | 47.533 | 6.32 | 1.318 | 4.64 | 8101.57 | 1.674 | 97.6 | 77.9 | 1298 | 23.81 | 5266 | 2850.1 | 2732.2 | 4054 | 1183.8 | 0.68264 | 5.959
2024-12-09 | 12:57 | Data | 0 | 32.994 | 30.793 | 179.256 | 7.64 | 167.736 | 1995.66 | 26.13 | 47.623 | 6.32 | 1.327 | 4.639 | 8110.61 | 2.059 | 97.6 | 77.8 | 1297 | 23.81 | 5271.9 | 2851.4 | 2743.2 | 4075.4 | 1183.8 | 0.68357 | 5.966
2024-12-09 | 12:57 | Data | 0 | 32.777 | 30.651 | 179.075 | 7.63 | 167.827 | 1998.37 | 26.12 | 47.623 | 6.33 | 1.326 | 4.666 | 8110.61 | 1.904 | 97.6 | 77.9 | 1299 | 23.81 | 5271.9 | 2845.4 | 2720.9 | 4061 | 1183.8 | 0.68487 | 5.993
2024-12-09 | 12:57 | Data | 0 | 32.71 | 30.847 | 179.075 | 7.64 | 167.555 | 1998.37 | 26.1 | 47.623 | 6.32 | 1.327 | 4.689 | 8110.61 | 1.958 | 97.6 | 77.9 | 1299 | 23.81 | 5271.9 | 2854.2 | 2722.7 | 4069.8 | 1183.8 | 0.6843 | 6.016
2024-12-09 | 12:57 | Data | 0 | 32.339 | 30.536 | 179.03 | 7.64 | 167.691 | 1999.28 | 26.12 | 47.533 | 6.32 | 1.317 | 4.703 | 8101.57 | 1.816 | 97.6 | 78.1 | 1299 | 23.81 | 5266 | 2828.8 | 2717.8 | 4043.7 | 1183.9 | 0.68181 | 6.018
2024-12-09 | 12:57 | Data | 0 | 32.892 | 30.982 | 179.166 | 7.64 | 167.691 | 2001.08 | 26.11 | 47.623 | 6.32 | 1.305 | 4.654 | 8115.14 | 1.857 | 97.6 | 78.1 | 1300 | 23.81 | 5274.8 | 2839.4 | 2750.6 | 4077.4 | 1183.9 | 0.67984 | 5.959
2024-12-09 | 12:57 | Data | 0 | 32.885 | 31.103 | 179.166 | 7.64 | 167.736 | 2001.08 | 26.12 | 47.533 | 6.32 | 1.32 | 4.633 | 8115.14 | 2.046 | 97.6 | 77.8 | 1301 | 23.81 | 5274.8 | 2847.2 | 2746.5 | 4079.4 | 1183.9 | 0.68113 | 5.952
2024-12-09 | 12:57 | Data | 0 | 32.568 | 30.475 | 179.03 | 7.64 | 167.646 | 2001.08 | 26.1 | 47.714 | 6.32 | 1.322 | 4.683 | 8115.14 | 1.857 | 97.6 | 78 | 1301 | 23.86 | 5274.8 | 2845.5 | 2728.7 | 4062 | 1183.9 | 0.68317 | 6.005
2024-12-09 | 12:57 | Data | 0 | 32.548 | 30.739 | 179.121 | 7.64 | 167.601 | 2002.89 | 26.11 | 47.714 | 6.32 | 1.317 | 4.675 | 8088 | 1.971 | 97.6 | 78 | 1301 | 23.81 | 5257.2 | 2848.9 | 2745.7 | 4078.6 | 1183.9 | 0.68155 | 5.99
2024-12-09 | 12:57 | Data | 0 | 32.831 | 30.651 | 179.075 | 7.64 | 167.646 | 2001.99 | 26.1 | 47.623 | 6.32 | 1.323 | 4.692 | 8097.05 | 1.965 | 97.6 | 78 | 1301 | 23.77 | 5263.1 | 2856.8 | 2735.5 | 4075.4 | 1183.9 | 0.68399 | 6.015
2024-12-09 | 12:57 | Data | 0 | 32.777 | 30.536 | 179.03 | 7.64 | 167.646 | 2001.99 | 26.1 | 47.714 | 6.32 | 1.321 | 4.682 | 8092.52 | 1.87 | 97.6 | 78 | 1301 | 23.81 | 5260.1 | 2830.8 | 2728.7 | 4056.5 | 1183.9 | 0.6817 | 6.004
2024-12-09 | 12:57 | Data | 0 | 32.71 | 30.874 | 179.166 | 7.63 | 167.601 | 2001.08 | 26.11 | 47.623 | 6.32 | 1.31 | 4.679 | 8110.61 | 2.025 | 97.6 | 78.1 | 1301 | 23.77 | 5271.9 | 2834.9 | 2729.8 | 4059.4 | 1183.9 | 0.68178 | 5.99
2024-12-09 | 12:57 | Data | 0 | 32.602 | 30.624 | 179.03 | 7.64 | 167.601 | 2001.99 | 26.11 | 47.623 | 6.32 | 1.314 | 4.67 | 8110.61 | 2.154 | 97.6 | 78 | 1301 | 23.81 | 5271.9 | 2843.5 | 2730.6 | 4061.9 | 1183.9 | 0.68184 | 5.984
2024-12-09 | 12:57 | Data | 0 | 32.521 | 30.651 | 178.985 | 7.63 | 167.601 | 2001.08 | 26.12 | 47.623 | 6.32 | 1.318 | 4.634 | 8106.09 | 1.857 | 97.6 | 77.9 | 1301 | 23.81 | 5269 | 2836.1 | 2754.8 | 4078.1 | 1183.9 | 0.67902 | 5.955
2024-12-09 | 12:57 | Data | 0 | 32.447 | 30.637 | 179.075 | 7.64 | 167.646 | 2003.8 | 26.12 | 47.623 | 6.32 | 1.314 | 4.654 | 8101.57 | 2.066 | 97.6 | 78 | 1302 | 23.86 | 5266 | 2833.5 | 2740.9 | 4064.2 | 1183.9 | 0.68195 | 5.968
2024-12-09 | 12:58 | Data | 0 | 32.919 | 30.766 | 179.211 | 7.64 | 167.872 | 2006.51 | 26.11 | 47.714 | 6.32 | 1.324 | 4.673 | 8097.05 | 1.897 | 97.6 | 77.9 | 1304 | 23.81 | 5263.1 | 2847.2 | 2746.4 | 4076.6 | 1183.9 | 0.68009 | 5.996
2024-12-09 | 12:58 | Data | 0 | 32.669 | 30.442 | 179.03 | 7.63 | 167.601 | 2009.22 | 26.12 | 47.533 | 6.32 | 1.327 | 4.643 | 8101.57 | 2.046 | 97.6 | 77.8 | 1306 | 23.81 | 5266 | 2837.2 | 2766.5 | 4089 | 1183.9 | 0.68061 | 5.969
2024-12-09 | 12:58 | Data | 0 | 32.723 | 30.948 | 179.075 | 7.64 | 167.691 | 2012.83 | 26.11 | 47.623 | 6.33 | 1.319 | 4.659 | 8106.09 | 1.911 | 97.6 | 77.9 | 1308 | 23.81 | 5269 | 2852.3 | 2748.4 | 4085.5 | 1183.9 | 0.68225 | 5.978
2024-12-09 | 12:58 | Data | 0 | 32.811 | 30.658 | 179.121 | 7.64 | 167.691 | 2011.93 | 26.11 | 47.623 | 6.32 | 1.318 | 4.687 | 8106.09 | 1.958 | 97.6 | 78.1 | 1308 | 23.81 | 5269 | 2832.9 | 2748.1 | 4075.3 | 1183.9 | 0.68223 | 6.005
2024-12-09 | 12:58 | Data | 0 | 32.777 | 30.658 | 179.121 | 7.64 | 167.691 | 2007.41 | 26.12 | 47.623 | 6.32 | 1.32 | 4.686 | 8110.61 | 1.951 | 97.6 | 78 | 1305 | 23.81 | 5271.9 | 2825.2 | 2723.8 | 4048.2 | 1183.9 | 0.68255 | 6.006
2024-12-09 | 12:58 | Data | 0 | 32.926 | 30.921 | 179.121 | 7.63 | 167.736 | 2005.6 | 26.11 | 47.623 | 6.32 | 1.321 | 4.656 | 8115.14 | 1.89 | 97.6 | 77.9 | 1304 | 23.81 | 5274.8 | 2833.9 | 2725 | 4053.6 | 1183.9 | 0.68256 | 5.978
2024-12-09 | 12:58 | Data | 0 | 32.723 | 30.651 | 179.03 | 7.64 | 167.691 | 2007.41 | 26.11 | 47.082 | 6.32 | 1.326 | 4.663 | 8110.61 | 2.073 | 97.7 | 77.8 | 1304 | 23.63 | 5271.9 | 2848.6 | 2732.7 | 4070.1 | 1183.9 | 0.68267 | 5.989
2024-12-09 | 12:58 | Data | 0 | 32.953 | 31.096 | 179.166 | 7.64 | 167.872 | 2011.93 | 26.11 | 47.714 | 6.32 | 1.322 | 4.676 | 8115.14 | 1.904 | 97.6 | 78 | 1308 | 23.86 | 5274.8 | 2830.6 | 2746.6 | 4070.4 | 1183.9 | 0.67825 | 5.998
2024-12-09 | 12:58 | Data | 0 | 32.723 | 30.455 | 179.121 | 7.63 | 167.646 | 2006.51 | 26.11 | 47.714 | 6.32 | 1.319 | 4.686 | 8110.61 | 2.147 | 97.6 | 78.1 | 1304 | 23.81 | 5271.9 | 2838.1 | 2705.2 | 4042.2 | 1183.9 | 0.68525 | 6.004
2024-12-09 | 12:58 | Data | 0 | 32.723 | 30.88 | 178.985 | 7.64 | 167.691 | 2007.41 | 26.1 | 47.623 | 6.31 | 1.311 | 4.645 | 8124.18 | 1.85 | 97.6 | 78 | 1306 | 23.81 | 5280.7 | 2832.3 | 2735.6 | 4062.7 | 1183.9 | 0.68107 | 5.957
2024-12-09 | 12:58 | Data | 0 | 32.285 | 30.739 | 178.985 | 7.64 | 167.691 | 2010.12 | 26.11 | 47.623 | 6.32 | 1.32 | 4.674 | 8142.27 | 1.843 | 97.6 | 78 | 1306 | 23.9 | 5292.5 | 2854.3 | 2718.1 | 4054.9 | 1183.9 | 0.68421 | 5.994
2024-12-09 | 12:58 | Data | 0 | 33.156 | 30.577 | 179.166 | 7.63 | 167.691 | 2006.51 | 26.1 | 47.623 | 6.32 | 1.31 | 4.685 | 8146.79 | 2.073 | 97.6 | 78.1 | 1304 | 23.81 | 5295.4 | 2834.2 | 2719.8 | 4058 | 1183.9 | 0.68333 | 5.995
2024-12-09 | 12:58 | Data | 0 | 32.507 | 30.536 | 179.121 | 7.63 | 167.691 | 2006.51 | 26.11 | 47.353 | 6.32 | 1.32 | 4.702 | 8160.36 | 1.85 | 97.6 | 78.1 | 1304 | 23.68 | 5304.2 | 2828 | 2709.7 | 4038.5 | 1183.9 | 0.68293 | 6.026
2024-12-09 | 12:58 | Data | 0 | 32.723 | 30.55 | 179.03 | 7.64 | 167.646 | 2007.41 | 26.11 | 47.623 | 6.31 | 1.329 | 4.686 | 8124.18 | 2.133 | 97.6 | 77.9 | 1305 | 23.81 | 5280.7 | 2842.1 | 2729.9 | 4064.6 | 1183.9 | 0.68143 | 6.015
2024-12-09 | 12:58 | Data | 0 | 32.723 | 30.766 | 179.075 | 7.64 | 167.646 | 2006.51 | 26.1 | 47.172 | 6.32 | 1.314 | 4.689 | 8137.75 | 1.958 | 97.6 | 78.1 | 1304 | 23.59 | 5289.5 | 2832 | 2732.1 | 4056.4 | 1183.9 | 0.68128 | 6.004
2024-12-09 | 12:58 | Data | 0 | 32.501 | 30.921 | 179.03 | 7.63 | 167.691 | 2006.51 | 26.1 | 47.623 | 6.32 | 1.318 | 4.67 | 8124.18 | 1.958 | 97.6 | 78 | 1304 | 23.81 | 5280.7 | 2825.4 | 2724.9 | 4047.5 | 1183.9 | 0.68259 | 5.988
2024-12-09 | 12:58 | Data | 0 | 32.723 | 30.651 | 179.075 | 7.64 | 167.691 | 2001.99 | 26.1 | 47.623 | 6.32 | 1.32 | 4.665 | 8137.75 | 2.066 | 97.6 | 77.9 | 1301 | 23.86 | 5289.5 | 2847.5 | 2707.3 | 4049.1 | 1183.9 | 0.68703 | 5.984
2024-12-09 | 12:58 | Data | 0 | 32.723 | 30.651 | 179.03 | 7.64 | 167.646 | 2004.7 | 26.11 | 47.623 | 6.32 | 1.325 | 4.672 | 8155.84 | 2.073 | 97.6 | 77.9 | 1303 | 23.81 | 5301.3 | 2821 | 2740.7 | 4052.4 | 1183.9 | 0.67964 | 5.996
2024-12-09 | 12:59 | Data | 0 | 32.507 | 30.644 | 179.121 | 7.64 | 167.691 | 2003.8 | 26.11 | 47.623 | 6.32 | 1.321 | 4.683 | 8164.88 | 1.877 | 97.6 | 78 | 1302 | 23.77 | 5307.2 | 2850.7 | 2734.3 | 4070.4 | 1183.9 | 0.68418 | 6.004
2024-12-09 | 12:59 | Data | 0 | 33.135 | 30.718 | 179.256 | 7.64 | 167.872 | 2001.99 | 26.11 | 47.714 | 6.32 | 1.31 | 4.692 | 8169.4 | 2.1 | 97.6 | 78.2 | 1301 | 23.86 | 5310.1 | 2831.2 | 2743 | 4062.3 | 1183.9 | 0.68214 | 6
2024-12-09 | 12:59 | Data | 0 | 32.885 | 30.678 | 178.985 | 7.63 | 167.736 | 2001.99 | 26.11 | 47.533 | 6.32 | 1.311 | 4.679 | 8173.92 | 2.154 | 97.6 | 78.1 | 1301 | 23.77 | 5313.1 | 2840.9 | 2726.1 | 4058.2 | 1183.9 | 0.68315 | 5.988
2024-12-09 | 12:59 | Data | 0 | 32.717 | 30.651 | 179.075 | 7.64 | 167.691 | 2000.18 | 26.1 | 47.623 | 6.32 | 1.331 | 4.689 | 8155.84 | 2.073 | 97.6 | 77.9 | 1301 | 23.81 | 5301.3 | 2832.3 | 2722.9 | 4050.4 | 1183.9 | 0.6837 | 6.021
2024-12-09 | 12:59 | Data | 0 | 32.75 | 30.658 | 179.03 | 7.64 | 167.691 | 2001.08 | 26.11 | 47.714 | 6.32 | 1.324 | 4.668 | 8164.88 | 1.89 | 97.6 | 77.9 | 1301 | 23.86 | 5307.2 | 2841.6 | 2715.6 | 4044.5 | 1183.9 | 0.68404 | 5.992
2024-12-09 | 12:59 | Data | 0 | 32.825 | 30.988 | 179.121 | 7.64 | 167.646 | 2001.08 | 26.1 | 47.623 | 6.32 | 1.32 | 4.668 | 8155.84 | 2.066 | 97.6 | 78 | 1301 | 23.86 | 5301.3 | 2841 | 2728 | 4060.9 | 1183.9 | 0.68281 | 5.988
2024-12-09 | 12:59 | Data | 0 | 33.169 | 30.799 | 179.166 | 7.64 | 167.827 | 2001.08 | 26.11 | 47.623 | 6.32 | 1.313 | 4.7 | 8155.84 | 2.127 | 97.6 | 78.2 | 1301 | 23.81 | 5301.3 | 2833.3 | 2717.2 | 4051.7 | 1183.9 | 0.68305 | 6.016
2024-12-09 | 12:59 | Data | 0 | 33.054 | 30.928 | 179.121 | 7.64 | 167.827 | 2003.8 | 26.11 | 47.533 | 6.32 | 1.32 | 4.702 | 8164.88 | 2.073 | 97.6 | 78.1 | 1302 | 23.77 | 5307.2 | 2823.3 | 2718.9 | 4041.1 | 1183.9 | 0.68373 | 6.023
2024-12-09 | 12:59 | Data | 0 | 32.791 | 30.685 | 179.211 | 7.63 | 167.827 | 2002.89 | 26.11 | 47.714 | 6.32 | 1.31 | 4.674 | 8169.4 | 1.87 | 97.6 | 78.1 | 1302 | 23.81 | 5310.1 | 2826.2 | 2732.7 | 4051.9 | 1183.9 | 0.67987 | 5.984
2024-12-09 | 12:59 | Data | 0 | 33.048 | 30.685 | 179.211 | 7.64 | 167.827 | 2004.7 | 26.11 | 47.623 | 6.32 | 1.313 | 4.673 | 8169.4 | 2.262 | 97.6 | 78.1 | 1303 | 23.86 | 5310.1 | 2856.4 | 2741.2 | 4079.6 | 1184 | 0.68265 | 5.986
2024-12-09 | 12:59 | Data | 0 | 32.73 | 30.678 | 179.121 | 7.63 | 167.827 | 2004.7 | 26.09 | 47.623 | 6.32 | 1.318 | 4.663 | 8164.88 | 2.032 | 97.6 | 78 | 1303 | 23.86 | 5307.2 | 2828.4 | 2725.8 | 4054.4 | 1184 | 0.68186 | 5.979
2024-12-09 | 12:59 | Data | 0 | 32.73 | 30.651 | 179.03 | 7.64 | 167.736 | 2005.6 | 26.11 | 47.714 | 6.32 | 1.311 | 4.671 | 8133.23 | 1.897 | 97.6 | 78.1 | 1303 | 23.81 | 5286.6 | 2840.5 | 2743.5 | 4073.8 | 1184 | 0.68206 | 5.982
2024-12-09 | 12:59 | Data | 0 | 32.723 | 30.671 | 179.075 | 7.64 | 167.646 | 2003.8 | 26.12 | 47.533 | 6.32 | 1.313 | 4.69 | 8097.05 | 2.032 | 97.6 | 78.1 | 1302 | 23.81 | 5263.1 | 2831.1 | 2737.8 | 4061.6 | 1184 | 0.68109 | 6.004
2024-12-09 | 12:59 | Data | 0 | 32.595 | 30.644 | 179.075 | 7.64 | 167.691 | 2007.41 | 26.1 | 47.623 | 6.32 | 1.32 | 4.652 | 8101.57 | 2.12 | 97.6 | 77.9 | 1305 | 23.86 | 5266 | 2836.3 | 2730 | 4058.7 | 1184 | 0.68268 | 5.971
2024-12-09 | 12:59 | Data | 0 | 32.494 | 30.624 | 179.075 | 7.64 | 167.691 | 2001.99 | 26.11 | 47.623 | 6.32 | 1.32 | 4.683 | 8092.52 | 2.073 | 97.6 | 78 | 1301 | 23.81 | 5260.1 | 2849.6 | 2745.5 | 4074.9 | 1184 | 0.68318 | 6.001
2024-12-09 | 12:59 | Data | 0 | 32.494 | 30.651 | 179.121 | 7.63 | 167.691 | 2000.18 | 26.1 | 47.714 | 6.32 | 1.318 | 4.651 | 8110.61 | 1.843 | 97.6 | 77.9 | 1300 | 23.81 | 5271.9 | 2837.3 | 2720 | 4055.3 | 1184 | 0.68367 | 5.967
2024-12-09 | 12:59 | Data | 0 | 32.73 | 30.651 | 179.03 | 7.64 | 167.646 | 1999.28 | 26.11 | 47.623 | 6.32 | 1.318 | 4.647 | 8101.57 | 1.87 | 97.6 | 77.9 | 1300 | 23.81 | 5266 | 2864.1 | 2726.1 | 4073.3 | 1184 | 0.68599 | 5.964
2024-12-09 | 13:00 | Data | 0 | 32.723 | 30.867 | 179.166 | 7.64 | 167.827 | 2001.99 | 26.1 | 47.623 | 6.32 | 1.311 | 4.688 | 8110.61 | 1.897 | 97.6 | 78.2 | 1301 | 23.81 | 5271.9 | 2854 | 2750.7 | 4087.2 | 1184 | 0.68197 | 6.002
2024-12-09 | 13:00 | Data | 0 | 32.609 | 30.853 | 179.211 | 7.63 | 167.691 | 2002.89 | 26.11 | 47.714 | 6.32 | 1.31 | 4.66 | 8119.66 | 1.985 | 97.6 | 78 | 1302 | 23.86 | 5277.8 | 2840.2 | 2731.7 | 4063 | 1184 | 0.68316 | 5.973
2024-12-09 | 13:00 | Data | 0 | 32.913 | 30.874 | 179.392 | 7.63 | 167.736 | 2006.51 | 26.11 | 47.533 | 6.33 | 1.32 | 4.664 | 8124.18 | 2.127 | 97.6 | 77.9 | 1304 | 23.81 | 5280.7 | 2831 | 2743.2 | 4062.8 | 1184 | 0.68088 | 5.984
2024-12-09 | 13:00 | Data | 0 | 32.501 | 30.813 | 179.166 | 7.63 | 167.736 | 2006.51 | 26.11 | 47.533 | 6.32 | 1.325 | 4.677 | 8119.66 | 1.796 | 97.6 | 77.9 | 1305 | 23.77 | 5277.8 | 2827.4 | 2733.2 | 4066.6 | 1184 | 0.68145 | 6.001
2024-12-09 | 13:00 | Data | 0 | 32.501 | 30.651 | 179.03 | 7.64 | 167.646 | 2009.22 | 26.11 | 47.714 | 6.31 | 1.318 | 4.683 | 8124.18 | 1.958 | 97.6 | 78.1 | 1306 | 23.9 | 5280.7 | 2828.7 | 2719.7 | 4047.5 | 1184 | 0.68164 | 5.999
2024-12-09 | 13:00 | Data | 0 | 32.507 | 30.651 | 178.985 | 7.64 | 167.646 | 2009.22 | 26.1 | 47.623 | 6.32 | 1.318 | 4.693 | 8137.75 | 1.843 | 97.6 | 78.1 | 1306 | 23.86 | 5289.5 | 2824.8 | 2706.4 | 4035 | 1184 | 0.68276 | 6.01
2024-12-09 | 13:00 | Data | 0 | 33.149 | 30.57 | 179.121 | 7.64 | 167.827 | 1977.58 | 26.1 | 47.623 | 6.32 | 1.32 | 4.673 | 8101.57 | 2.093 | 97.6 | 78 | 1284 | 23.81 | 5266 | 2844.3 | 2729.4 | 4063.6 | 1184 | 0.68269 | 5.994
2024-12-09 | 13:00 | Data | 0 | 32.548 | 30.664 | 179.03 | 7.64 | 167.736 | 1960.41 | 26.12 | 47.623 | 6.32 | 1.322 | 4.675 | 8088 | 2.046 | 97.6 | 77.9 | 1274 | 23.81 | 5257.2 | 2843.1 | 2742.2 | 4073.2 | 1184 | 0.68374 | 6
2024-12-09 | 13:00 | Data | 0 | 32.71 | 30.651 | 179.166 | 7.64 | 167.691 | 1959.51 | 26.12 | 47.623 | 6.31 | 1.314 | 4.677 | 8097.05 | 2.181 | 97.6 | 78.1 | 1274 | 23.81 | 5263.1 | 2834.2 | 2724.5 | 4055.3 | 1184 | 0.68234 | 5.99
2024-12-09 | 13:00 | Data | 0 | 32.98 | 30.685 | 179.256 | 7.64 | 167.736 | 1959.51 | 26.11 | 47.443 | 6.33 | 1.318 | 4.68 | 8110.61 | 1.992 | 97.6 | 78 | 1274 | 23.86 | 5271.9 | 2842.5 | 2735.9 | 4068.3 | 1184 | 0.68298 | 5.998
2024-12-09 | 13:00 | Data | 0 | 32.642 | 30.826 | 179.075 | 7.63 | 167.736 | 1962.22 | 26.12 | 47.623 | 6.32 | 1.314 | 4.67 | 8119.66 | 1.85 | 97.6 | 78.1 | 1275 | 23.81 | 5277.8 | 2832.9 | 2716.1 | 4046.8 | 1184 | 0.68187 | 5.982
2024-12-09 | 13:00 | Data | 0 | 32.507 | 30.651 | 178.985 | 7.64 | 167.646 | 2010.12 | 26.1 | 47.714 | 6.32 | 1.321 | 4.662 | 8124.18 | 1.843 | 97.6 | 77.9 | 1307 | 23.86 | 5280.7 | 2839.3 | 2738.4 | 4067.8 | 1184 | 0.6819 | 5.984
2024-12-09 | 13:00 | Data | 0 | 32.723 | 30.874 | 179.075 | 7.64 | 167.691 | 2012.83 | 26.11 | 47.714 | 6.31 | 1.319 | 4.656 | 8115.14 | 1.897 | 97.6 | 77.9 | 1308 | 23.77 | 5274.8 | 2851.3 | 2721.5 | 4061.9 | 1184 | 0.68442 | 5.974
2024-12-09 | 13:00 | Data | 0 | 32.507 | 30.766 | 179.075 | 7.63 | 167.646 | 2011.93 | 26.1 | 47.353 | 6.32 | 1.311 | 4.681 | 8110.61 | 1.904 | 97.6 | 78.1 | 1308 | 23.68 | 5271.9 | 2832.7 | 2712.4 | 4045.4 | 1184 | 0.68513 | 5.992
2024-12-09 | 13:00 | Data | 0 | 32.501 | 30.637 | 179.03 | 7.64 | 167.646 | 2012.83 | 26.11 | 47.714 | 6.33 | 1.32 | 4.666 | 8115.14 | 2.019 | 97.6 | 78 | 1308 | 23.77 | 5274.8 | 2812.7 | 2708.1 | 4029.9 | 1184 | 0.68265 | 5.986
2024-12-09 | 13:00 | Data | 0 | 32.723 | 30.907 | 179.166 | 7.64 | 167.827 | 2011.93 | 26.1 | 47.443 | 6.32 | 1.321 | 4.655 | 8119.66 | 2.025 | 97.6 | 77.9 | 1308 | 23.68 | 5277.8 | 2835.4 | 2704.3 | 4042.3 | 1184 | 0.68496 | 5.977
2024-12-09 | 13:00 | Data | 0 | 32.892 | 31.076 | 179.166 | 7.64 | 167.827 | 2012.83 | 26.11 | 47.443 | 6.32 | 1.305 | 4.634 | 8124.18 | 2.032 | 97.6 | 78 | 1308 | 23.72 | 5280.7 | 2837.8 | 2715 | 4047.2 | 1184 | 0.68435 | 5.939
2024-12-09 | 13:00 | Data | 0 | 32.723 | 30.705 | 179.075 | 7.64 | 167.736 | 2012.83 | 26.1 | 47.353 | 6.32 | 1.313 | 4.65 | 8124.18 | 1.958 | 97.6 | 78 | 1308 | 23.72 | 5280.7 | 2820 | 2716.6 | 4041.7 | 1184 | 0.68185 | 5.962
2024-12-09 | 13:01 | Data | 0 | 32.946 | 30.874 | 179.166 | 7.63 | 167.736 | 2014.64 | 26.1 | 47.353 | 6.32 | 1.314 | 4.638 | 8128.7 | 1.992 | 97.6 | 77.9 | 1310 | 23.72 | 5283.7 | 2840.7 | 2709.8 | 4051.3 | 1184 | 0.68278 | 5.952
2024-12-09 | 13:01 | Data | 0 | 32.649 | 30.651 | 179.075 | 7.63 | 167.691 | 2017.35 | 26.1 | 47.353 | 6.32 | 1.319 | 4.664 | 8115.14 | 1.661 | 97.7 | 78 | 1312 | 23.68 | 5274.8 | 2839.9 | 2730 | 4053.3 | 1184 | 0.68452 | 5.98
2024-12-09 | 13:01 | Data | 0 | 32.514 | 30.597 | 179.121 | 7.63 | 167.827 | 2014.64 | 26.11 | 47.353 | 6.32 | 1.326 | 4.704 | 8097.05 | 1.897 | 97.6 | 78 | 1310 | 23.72 | 5263.1 | 2838.4 | 2708.3 | 4048.5 | 1184 | 0.68381 | 6.03
2024-12-09 | 13:01 | Data | 0 | 32.723 | 30.631 | 179.121 | 7.64 | 167.691 | 2010.12 | 26.11 | 47.262 | 6.32 | 1.326 | 4.66 | 8097.05 | 2.093 | 97.6 | 77.8 | 1308 | 23.63 | 5263.1 | 2826.8 | 2733.6 | 4054.3 | 1184 | 0.68219 | 5.987
2024-12-09 | 13:01 | Data | 0 | 32.305 | 30.847 | 179.211 | 7.64 | 167.691 | 2010.12 | 26.1 | 47.443 | 6.32 | 1.322 | 4.68 | 8119.66 | 1.776 | 97.6 | 78 | 1306 | 23.72 | 5277.8 | 2819.4 | 2718.2 | 4037 | 1184 | 0.68241 | 6.002
2024-12-09 | 13:01 | Data | 0 | 32.528 | 30.766 | 179.03 | 7.64 | 167.736 | 2009.22 | 26.1 | 47.353 | 6.32 | 1.327 | 4.687 | 8106.09 | 1.85 | 97.6 | 77.9 | 1307 | 23.68 | 5269 | 2825.3 | 2695.4 | 4030.1 | 1184 | 0.68459 | 6.015
2024-12-09 | 13:01 | Data | 0 | 32.723 | 30.448 | 179.121 | 7.63 | 167.736 | 2007.41 | 26.1 | 47.353 | 6.32 | 1.314 | 4.695 | 8097.05 | 2.039 | 97.6 | 78.2 | 1305 | 23.63 | 5263.1 | 2841.7 | 2715.5 | 4052.6 | 1184 | 0.68525 | 6.01
2024-12-09 | 13:01 | Data | 0 | 32.946 | 30.658 | 179.211 | 7.63 | 167.827 | 2003.8 | 26.11 | 47.353 | 6.31 | 1.313 | 4.673 | 8097.05 | 2.12 | 97.6 | 78 | 1302 | 23.72 | 5263.1 | 2841.4 | 2725.3 | 4059 | 1184 | 0.68333 | 5.987
2024-12-09 | 13:01 | Data | 0 | 32.75 | 30.678 | 179.166 | 7.64 | 167.736 | 2003.8 | 26.11 | 47.262 | 6.32 | 1.309 | 4.675 | 8119.66 | 2.025 | 97.6 | 78.1 | 1302 | 23.63 | 5277.8 | 2852.7 | 2728.8 | 4065.2 | 1184 | 0.68337 | 5.984
2024-12-09 | 13:01 | Data | 0 | 32.723 | 30.766 | 179.03 | 7.63 | 167.736 | 2004.7 | 26.11 | 47.353 | 6.32 | 1.323 | 4.663 | 8119.66 | 2.059 | 97.6 | 77.9 | 1303 | 23.72 | 5277.8 | 2833.8 | 2731.5 | 4055 | 1184 | 0.68401 | 5.986
2024-12-09 | 13:01 | Data | 0 | 32.501 | 30.651 | 179.211 | 7.64 | 167.736 | 2001.99 | 26.11 | 47.443 | 6.32 | 1.319 | 4.689 | 8124.18 | 2.019 | 97.6 | 78.1 | 1301 | 23.68 | 5280.7 | 2834.2 | 2736 | 4059.3 | 1184 | 0.6806 | 6.007
2024-12-09 | 13:01 | Data | 0 | 32.892 | 30.772 | 179.121 | 7.64 | 167.736 | 1999.28 | 26.11 | 47.443 | 6.32 | 1.318 | 4.651 | 8115.14 | 1.863 | 97.6 | 77.9 | 1299 | 23.68 | 5274.8 | 2838.2 | 2720 | 4051.2 | 1184.1 | 0.68495 | 5.969
2024-12-09 | 13:01 | Data | 0 | 32.885 | 30.941 | 179.166 | 7.64 | 167.872 | 1995.66 | 26.11 | 47.443 | 6.32 | 1.313 | 4.64 | 8088 | 2.106 | 97.6 | 77.9 | 1297 | 23.68 | 5257.2 | 2837.2 | 2730.3 | 4060 | 1184.1 | 0.68399 | 5.953
2024-12-09 | 13:01 | Data | 0 | 32.953 | 30.88 | 179.347 | 7.64 | 167.917 | 1999.28 | 26.09 | 47.262 | 6.32 | 1.312 | 4.654 | 8051.82 | 2.073 | 97.6 | 78 | 1300 | 23.68 | 5233.7 | 2838.6 | 2726.9 | 4059.9 | 1184.1 | 0.68421 | 5.966
2024-12-09 | 13:01 | Data | 0 | 32.622 | 30.874 | 179.211 | 7.64 | 167.827 | 1994.76 | 26.09 | 47.353 | 6.32 | 1.306 | 4.673 | 8060.87 | 1.634 | 97.6 | 78.2 | 1298 | 23.68 | 5239.6 | 2839.1 | 2719.4 | 4052.2 | 1184.1 | 0.6849 | 5.979
2024-12-09 | 13:01 | Data | 0 | 32.811 | 30.88 | 179.121 | 7.64 | 167.736 | 1995.66 | 26.11 | 47.443 | 6.32 | 1.312 | 4.664 | 8056.35 | 2.16 | 97.6 | 78 | 1297 | 23.72 | 5236.6 | 2835.3 | 2710.4 | 4042.9 | 1184.1 | 0.68533 | 5.977
2024-12-09 | 13:01 | Data | 0 | 32.534 | 30.651 | 179.166 | 7.63 | 167.736 | 1998.37 | 26.12 | 47.353 | 6.32 | 1.321 | 4.664 | 8056.35 | 1.85 | 97.6 | 77.9 | 1299 | 23.68 | 5236.6 | 2839.3 | 2726.4 | 4056.7 | 1184.1 | 0.68451 | 5.987
2024-12-09 | 13:01 | Data | 0 | 32.831 | 30.907 | 179.166 | 7.64 | 167.827 | 2001.08 | 26.1 | 47.443 | 6.32 | 1.32 | 4.669 | 8101.57 | 1.85 | 97.6 | 78 | 1301 | 23.68 | 5266 | 2819.1 | 2733.1 | 4053 | 1184.1 | 0.67961 | 5.988
2024-12-09 | 13:02 | Data | 0 | 32.994 | 30.88 | 179.211 | 7.63 | 167.872 | 2001.99 | 26.1 | 47.353 | 6.32 | 1.315 | 4.662 | 8097.05 | 2.093 | 97.6 | 78 | 1301 | 23.72 | 5263.1 | 2833.5 | 2716.4 | 4045.4 | 1184.1 | 0.68233 | 5.976
2024-12-09 | 13:02 | Data | 0 | 32.521 | 30.766 | 179.166 | 7.64 | 167.736 | 2001.08 | 26.1 | 47.353 | 6.32 | 1.32 | 4.664 | 8092.52 | 1.965 | 97.6 | 77.9 | 1301 | 23.68 | 5260.1 | 2843.7 | 2720 | 4052.4 | 1184.1 | 0.68453 | 5.982
2024-12-09 | 13:02 | Data | 0 | 32.953 | 30.732 | 179.302 | 7.63 | 167.872 | 2001.99 | 26.11 | 47.353 | 6.32 | 1.319 | 4.652 | 8069.91 | 1.965 | 97.6 | 77.9 | 1301 | 23.68 | 5245.4 | 2844 | 2731.3 | 4069.6 | 1184.1 | 0.68543 | 5.971
2024-12-09 | 13:02 | Data | 0 | 32.615 | 30.833 | 179.121 | 7.63 | 167.736 | 2001.08 | 26.11 | 47.353 | 6.32 | 1.325 | 4.68 | 8078.96 | 1.917 | 97.6 | 77.9 | 1301 | 23.72 | 5251.3 | 2837.3 | 2722.4 | 4056 | 1184.1 | 0.68234 | 6.004
2024-12-09 | 13:02 | Data | 0 | 32.899 | 30.685 | 179.256 | 7.63 | 167.917 | 2000.18 | 26.11 | 47.443 | 6.32 | 1.311 | 4.646 | 8092.52 | 2.052 | 97.6 | 78 | 1301 | 23.72 | 5260.1 | 2836.8 | 2738.2 | 4064.8 | 1184.1 | 0.6812 | 5.959
2024-12-09 | 13:02 | Data | 0 | 32.669 | 30.651 | 179.075 | 7.64 | 167.646 | 2006.51 | 26.1 | 47.262 | 6.32 | 1.317 | 4.657 | 8083.48 | 2.059 | 97.6 | 78 | 1304 | 23.63 | 5254.3 | 2835.7 | 2714 | 4044.8 | 1184.1 | 0.68444 | 5.974
2024-12-09 | 13:02 | Data | 0 | 32.825 | 30.766 | 179.166 | 7.64 | 167.827 | 2001.08 | 26.1 | 47.443 | 6.31 | 1.317 | 4.631 | 8078.96 | 1.971 | 97.6 | 77.9 | 1300 | 23.68 | 5251.3 | 2842.7 | 2724.2 | 4058.9 | 1184.1 | 0.6844 | 5.948
2024-12-09 | 13:02 | Data | 0 | 32.791 | 30.671 | 179.166 | 7.64 | 167.827 | 2003.8 | 26.1 | 47.353 | 6.32 | 1.318 | 4.669 | 8051.82 | 2.039 | 97.6 | 78 | 1303 | 23.68 | 5233.7 | 2850 | 2733.8 | 4066.3 | 1184.1 | 0.68285 | 5.986
2024-12-09 | 13:02 | Data | 0 | 32.575 | 30.867 | 179.256 | 7.63 | 167.917 | 2006.51 | 26.1 | 47.353 | 6.32 | 1.32 | 4.673 | 8056.35 | 1.89 | 97.6 | 78 | 1305 | 23.72 | 5236.6 | 2833.2 | 2744 | 4064.7 | 1184.1 | 0.68118 | 5.991
2024-12-09 | 13:02 | Data | 0 | 32.534 | 30.55 | 179.121 | 7.64 | 167.872 | 2011.93 | 26.1 | 47.353 | 6.32 | 1.312 | 4.634 | 8051.82 | 1.951 | 97.6 | 77.9 | 1307 | 23.72 | 5233.7 | 2842.9 | 2720.2 | 4052.8 | 1184.1 | 0.68459 | 5.947
2024-12-09 | 13:02 | Data | 0 | 32.831 | 30.664 | 179.211 | 7.64 | 167.827 | 2009.22 | 26.11 | 47.353 | 6.32 | 1.32 | 4.647 | 8042.78 | 2.012 | 97.6 | 77.9 | 1306 | 23.68 | 5227.8 | 2846.8 | 2713.9 | 4054.6 | 1184.1 | 0.68439 | 5.967
2024-12-09 | 13:02 | Data | 0 | 32.622 | 30.664 | 179.166 | 7.64 | 167.827 | 2009.22 | 26.11 | 47.353 | 6.32 | 1.31 | 4.641 | 8092.52 | 1.944 | 97.6 | 78 | 1305 | 23.72 | 5260.1 | 2828.7 | 2727.8 | 4055.8 | 1184.1 | 0.68109 | 5.95
2024-12-09 | 13:02 | Data | 0 | 32.811 | 30.968 | 179.166 | 7.64 | 167.736 | 2015.55 | 26.11 | 47.353 | 6.32 | 1.321 | 4.663 | 8069.91 | 2.079 | 97.7 | 77.9 | 1310 | 23.68 | 5245.4 | 2831.8 | 2711.5 | 4044.1 | 1184.1 | 0.68282 | 5.982
2024-12-09 | 13:02 | Data | 0 | 32.926 | 30.651 | 179.256 | 7.64 | 167.691 | 2018.26 | 26.1 | 47.353 | 6.32 | 1.328 | 4.668 | 8083.48 | 2.1 | 97.7 | 77.9 | 1312 | 23.63 | 5254.3 | 2831.3 | 2718.9 | 4047.6 | 1184.1 | 0.68239 | 5.996
2024-12-09 | 13:02 | Data | 0 | 32.501 | 30.691 | 179.166 | 7.64 | 167.827 | 2017.35 | 26.1 | 47.353 | 6.32 | 1.32 | 4.664 | 8088 | 1.931 | 97.6 | 77.9 | 1312 | 23.72 | 5257.2 | 2839.7 | 2723.6 | 4056.6 | 1184.1 | 0.68475 | 5.984
2024-12-09 | 13:02 | Data | 0 | 32.669 | 30.786 | 179.211 | 7.64 | 167.917 | 2020.97 | 26.11 | 47.443 | 6.33 | 1.322 | 4.668 | 8069.91 | 2.167 | 97.7 | 77.9 | 1314 | 23.72 | 5245.4 | 2839.6 | 2721.4 | 4056.3 | 1184.1 | 0.68414 | 5.989
2024-12-09 | 13:03 | Data | 0 | 32.717 | 30.631 | 179.121 | 7.63 | 167.736 | 2020.97 | 26.1 | 47.443 | 6.32 | 1.313 | 4.665 | 8051.82 | 2.154 | 97.7 | 78 | 1314 | 23.68 | 5233.7 | 2864.5 | 2721.5 | 4072.8 | 1184.1 | 0.68762 | 5.978
2024-12-09 | 13:03 | Data | 0 | 32.723 | 30.826 | 179.075 | 7.64 | 167.736 | 2015.55 | 26.11 | 47.443 | 6.32 | 1.313 | 4.68 | 8056.35 | 2.133 | 97.7 | 78.1 | 1310 | 23.68 | 5236.6 | 2838.4 | 2708.4 | 4044.4 | 1184.1 | 0.68551 | 5.993
2024-12-09 | 13:03 | Data | 0 | 32.75 | 30.874 | 179.256 | 7.63 | 167.827 | 2015.55 | 26.11 | 47.353 | 6.31 | 1.313 | 4.664 | 8490.48 | 1.863 | 97.7 | 78 | 1310 | 23.68 | 5518.8 | 2866.6 | 2720.1 | 4069.3 | 1184.1 | 0.68866 | 5.976
2024-12-09 | 13:03 | Data | 0 | 32.568 | 30.658 | 179.211 | 7.64 | 167.872 | 2008.32 | 26.1 | 47.443 | 6.32 | 1.31 | 4.683 | 8110.61 | 1.836 | 97.6 | 78.1 | 1305 | 23.72 | 5271.9 | 2839.2 | 2727.9 | 4061 | 1184.1 | 0.68338 | 5.995
2024-12-09 | 13:03 | Data | 0 | 32.555 | 30.826 | 179.256 | 7.64 | 167.827 | 2012.83 | 26.11 | 47.353 | 6.32 | 1.318 | 4.677 | 8101.57 | 1.87 | 97.6 | 78 | 1308 | 23.68 | 5266 | 2835.2 | 2710.6 | 4042.7 | 1184.1 | 0.68539 | 5.996
2024-12-09 | 13:03 | Data | 0 | 32.825 | 30.88 | 179.166 | 7.64 | 167.827 | 2011.93 | 26.11 | 47.353 | 6.32 | 1.32 | 4.673 | 8558.31 | 1.87 | 97.6 | 77.9 | 1309 | 23.72 | 5562.9 | 2835 | 2737.2 | 4063.4 | 1184.1 | 0.68119 | 5.995
2024-12-09 | 13:03 | Data | 0 | 32.285 | 30.82 | 179.121 | 7.64 | 167.691 | 2016.45 | 26.11 | 46.811 | 6.31 | 1.319 | 4.664 | 8146.79 | 1.944 | 97.7 | 77.9 | 1311 | 23.41 | 5295.4 | 2821.4 | 2705.7 | 4029.5 | 1184.1 | 0.6827 | 5.983
2024-12-09 | 13:03 | Data | 0 | 32.723 | 30.651 | 179.166 | 7.63 | 167.691 | 2012.83 | 26.1 | 47.443 | 6.31 | 1.319 | 4.676 | 8128.7 | 1.87 | 97.6 | 78 | 1308 | 23.68 | 5283.7 | 2848.3 | 2733.3 | 4068.1 | 1184.1 | 0.68322 | 5.994
2024-12-09 | 13:03 | Data | 0 | 32.723 | 31.103 | 179.211 | 7.63 | 167.827 | 2013.74 | 26.11 | 47.353 | 6.32 | 1.315 | 4.681 | 8155.84 | 1.816 | 97.6 | 78.1 | 1308 | 23.68 | 5301.3 | 2837.5 | 2736.5 | 4060 | 1184.1 | 0.68245 | 5.995
2024-12-09 | 13:03 | Data | 0 | 32.703 | 31.076 | 179.211 | 7.64 | 167.917 | 2012.83 | 26.11 | 47.443 | 6.32 | 1.324 | 4.655 | 8137.75 | 1.958 | 97.6 | 77.9 | 1308 | 23.63 | 5289.5 | 2841.9 | 2737.2 | 4067 | 1184.1 | 0.68169 | 5.979
2024-12-09 | 13:03 | Data | 0 | 32.858 | 30.779 | 179.075 | 7.64 | 167.827 | 2013.74 | 26.1 | 47.353 | 6.32 | 1.323 | 4.651 | 8142.27 | 2.079 | 97.6 | 77.9 | 1308 | 23.72 | 5292.5 | 2830.7 | 2716.4 | 4060.6 | 1184.1 | 0.68098 | 5.974
2024-12-09 | 13:03 | Data | 0 | 32.723 | 30.705 | 179.166 | 7.63 | 167.827 | 2016.45 | 26.1 | 47.353 | 6.32 | 1.319 | 4.67 | 8137.75 | 1.958 | 97.6 | 78 | 1310 | 23.68 | 5289.5 | 2835.4 | 2737.4 | 4060.5 | 1184.1 | 0.68134 | 5.988
2024-12-09 | 13:03 | Data | 0 | 33.068 | 31.13 | 179.392 | 7.63 | 167.962 | 2015.55 | 26.1 | 47.353 | 6.32 | 1.319 | 4.654 | 8124.18 | 2.005 | 97.7 | 77.9 | 1310 | 23.72 | 5280.7 | 2838.3 | 2724.8 | 4058.1 | 1184.1 | 0.6847 | 5.973
2024-12-09 | 13:03 | Data | 0 | 33.318 | 30.941 | 179.347 | 7.63 | 167.962 | 2015.55 | 26.1 | 47.353 | 6.31 | 1.315 | 4.662 | 8110.61 | 2.154 | 97.6 | 78 | 1310 | 23.68 | 5271.9 | 2832.8 | 2720.2 | 4046.8 | 1184.2 | 0.68404 | 5.979
2024-12-09 | 13:03 | Data | 0 | 32.804 | 30.678 | 179.211 | 7.64 | 167.917 | 2015.55 | 26.11 | 47.353 | 6.32 | 1.314 | 4.664 | 8115.14 | 1.857 | 97.6 | 78 | 1311 | 23.63 | 5274.8 | 2833.8 | 2721.7 | 4052.7 | 1184.2 | 0.68203 | 5.978
2024-12-09 | 13:03 | Data | 0 | 33.176 | 31.11 | 179.302 | 7.64 | 167.917 | 2014.64 | 26.11 | 47.353 | 6.32 | 1.32 | 4.653 | 8110.61 | 2.066 | 97.6 | 77.9 | 1309 | 23.68 | 5271.9 | 2838.3 | 2736.9 | 4063.3 | 1184.2 | 0.68185 | 5.973
2024-12-09 | 13:03 | Data | 0 | 32.75 | 30.766 | 179.256 | 7.63 | 167.736 | 2011.93 | 26.11 | 47.533 | 6.32 | 1.31 | 4.68 | 8110.61 | 2.073 | 97.6 | 78.1 | 1308 | 23.72 | 5271.9 | 2848.2 | 2756.3 | 4086.1 | 1184.2 | 0.67945 | 5.99
2024-12-09 | 13:03 | Data | 0 | 32.879 | 30.88 | 179.256 | 7.63 | 167.827 | 2015.55 | 26.1 | 47.443 | 6.32 | 1.312 | 4.665 | 8124.18 | 2.066 | 97.7 | 78 | 1310 | 23.72 | 5280.7 | 2824 | 2737.7 | 4058 | 1184.2 | 0.68008 | 5.978
2024-12-09 | 13:04 | Data | 0 | 33.061 | 30.887 | 179.256 | 7.64 | 168.007 | 2013.74 | 26.11 | 47.443 | 6.32 | 1.33 | 4.67 | 8137.75 | 1.897 | 97.6 | 77.8 | 1308 | 23.68 | 5289.5 | 2840.2 | 2736.6 | 4067.1 | 1184.2 | 0.68114 | 5.999
2024-12-09 | 13:04 | Data | 0 | 32.75 | 30.853 | 179.256 | 7.63 | 167.827 | 2013.74 | 26.11 | 47.262 | 6.31 | 1.321 | 4.668 | 8133.23 | 1.951 | 97.7 | 78 | 1308 | 23.68 | 5286.6 | 2825.2 | 2716.8 | 4042.6 | 1184.2 | 0.68263 | 5.988
2024-12-09 | 13:04 | Data | 0 | 32.737 | 30.853 | 179.256 | 7.63 | 167.917 | 2014.64 | 26.11 | 47.353 | 6.32 | 1.325 | 4.687 | 8155.84 | 1.897 | 97.6 | 78 | 1309 | 23.68 | 5301.3 | 2851.7 | 2746.4 | 4078.3 | 1184.2 | 0.68301 | 6.012
2024-12-09 | 13:04 | Data | 0 | 32.953 | 31.096 | 179.302 | 7.63 | 167.872 | 2009.22 | 26.11 | 47.262 | 6.31 | 1.307 | 4.69 | 8137.75 | 1.904 | 97.6 | 78.2 | 1307 | 23.68 | 5289.5 | 2848 | 2763.8 | 4078 | 1184.2 | 0.68056 | 5.998
2024-12-09 | 13:04 | Data | 0 | 32.588 | 30.671 | 179.256 | 7.64 | 167.962 | 2012.83 | 26.09 | 47.353 | 6.33 | 1.315 | 4.66 | 8137.75 | 1.816 | 97.6 | 78 | 1308 | 23.68 | 5289.5 | 2843.7 | 2734.1 | 4067.1 | 1184.2 | 0.68201 | 5.975
2024-12-09 | 13:04 | Data | 0 | 32.98 | 30.772 | 179.166 | 7.63 | 167.872 | 2011.93 | 26.11 | 47.353 | 6.32 | 1.319 | 4.653 | 8128.7 | 2.16 | 97.6 | 77.9 | 1308 | 23.68 | 5283.7 | 2837.2 | 2729.6 | 4059.8 | 1184.2 | 0.68127 | 5.971
2024-12-09 | 13:04 | Data | 0 | 32.723 | 30.88 | 179.347 | 7.63 | 168.007 | 2009.22 | 26.1 | 47.443 | 6.32 | 1.31 | 4.668 | 8119.66 | 1.958 | 97.6 | 78.1 | 1306 | 23.72 | 5277.8 | 2830.5 | 2746 | 4062.3 | 1184.2 | 0.6787 | 5.979
2024-12-09 | 13:04 | Data | 0 | 32.669 | 30.874 | 179.166 | 7.63 | 167.872 | 2009.22 | 26.11 | 47.443 | 6.32 | 1.32 | 4.686 | 8115.14 | 1.85 | 97.6 | 78 | 1305 | 23.72 | 5274.8 | 2832.7 | 2755.3 | 4073.9 | 1184.2 | 0.68044 | 6.005
2024-12-09 | 13:04 | Data | 0 | 32.845 | 30.658 | 179.166 | 7.63 | 167.872 | 2009.22 | 26.11 | 47.353 | 6.32 | 1.31 | 4.659 | 8110.61 | 2.079 | 97.6 | 78 | 1307 | 23.68 | 5271.9 | 2829.8 | 2759 | 4072.6 | 1184.2 | 0.67723 | 5.969
2024-12-09 | 13:04 | Data | 0 | 33.048 | 30.678 | 179.392 | 7.63 | 167.917 | 2009.22 | 26.1 | 47.262 | 6.32 | 1.312 | 4.656 | 8115.14 | 1.985 | 97.6 | 78 | 1306 | 23.68 | 5274.8 | 2845.7 | 2762.4 | 4087.4 | 1184.2 | 0.68065 | 5.967
2024-12-09 | 13:04 | Data | 0 | 33.176 | 31.11 | 179.302 | 7.63 | 167.962 | 2009.22 | 26.11 | 47.443 | 6.32 | 1.308 | 4.677 | 8110.61 | 1.897 | 97.6 | 78.2 | 1306 | 23.72 | 5271.9 | 2843 | 2747.5 | 4077.8 | 1184.2 | 0.6797 | 5.984
2024-12-09 | 13:04 | Data | 0 | 32.94 | 31.096 | 179.302 | 7.64 | 167.917 | 2009.22 | 26.1 | 47.353 | 6.32 | 1.324 | 4.651 | 8106.09 | 2.032 | 97.6 | 77.8 | 1307 | 23.68 | 5269 | 2831.1 | 2728.1 | 4053 | 1184.2 | 0.68206 | 5.974
2024-12-09 | 13:04 | Data | 0 | 32.953 | 31.11 | 179.347 | 7.64 | 167.917 | 2006.51 | 26.1 | 47.353 | 6.32 | 1.317 | 4.645 | 8115.14 | 1.857 | 97.6 | 77.9 | 1305 | 23.72 | 5274.8 | 2825 | 2751.5 | 4064.9 | 1184.2 | 0.67962 | 5.963
2024-12-09 | 13:04 | Data | 0 | 32.629 | 30.678 | 179.256 | 7.64 | 167.872 | 2002.89 | 26.11 | 47.443 | 6.32 | 1.32 | 4.666 | 8128.7 | 1.85 | 97.6 | 77.9 | 1302 | 23.68 | 5283.7 | 2847.4 | 2752 | 4080.7 | 1184.2 | 0.68098 | 5.988
2024-12-09 | 13:04 | Data | 0 | 32.838 | 30.88 | 179.121 | 7.64 | 167.872 | 2006.51 | 26.11 | 47.353 | 6.31 | 1.32 | 4.665 | 8155.84 | 2.059 | 97.6 | 78 | 1304 | 23.63 | 5301.3 | 2855.4 | 2758.6 | 4088.7 | 1184.2 | 0.68309 | 5.985
2024-12-09 | 13:04 | Data | 0 | 32.723 | 30.88 | 179.302 | 7.63 | 167.827 | 2006.51 | 26.1 | 47.353 | 6.31 | 1.31 | 4.664 | 8155.84 | 2.046 | 97.6 | 78 | 1305 | 23.68 | 5301.3 | 2826 | 2754.9 | 4070.5 | 1184.2 | 0.67663 | 5.977
2024-12-09 | 13:05 | Data | 0 | 32.73 | 30.651 | 179.211 | 7.63 | 167.962 | 2004.7 | 26.11 | 47.443 | 6.32 | 1.314 | 4.682 | 8146.79 | 2.066 | 97.6 | 78.1 | 1303 | 23.72 | 5295.4 | 2828.9 | 2738.5 | 4062.6 | 1184.2 | 0.68198 | 5.997
2024-12-09 | 13:05 | Data | 0 | 32.669 | 30.975 | 179.392 | 7.64 | 167.917 | 2004.7 | 26.1 | 47.443 | 6.32 | 1.324 | 4.671 | 8128.7 | 1.944 | 97.6 | 77.9 | 1302 | 23.72 | 5283.7 | 2843 | 2749.3 | 4073.9 | 1184.2 | 0.68094 | 5.996
2024-12-09 | 13:05 | Data | 0 | 32.946 | 30.894 | 179.211 | 7.64 | 167.917 | 2004.7 | 26.1 | 47.443 | 6.32 | 1.331 | 4.664 | 8115.14 | 2.059 | 97.6 | 77.8 | 1302 | 23.68 | 5274.8 | 2840.2 | 2746.2 | 4073.6 | 1184.2 | 0.68062 | 5.994
2024-12-09 | 13:05 | Data | 0 | 33.176 | 30.914 | 179.256 | 7.63 | 167.917 | 2003.8 | 26.11 | 47.353 | 6.32 | 1.311 | 4.664 | 8097.05 | 2.167 | 97.6 | 78.1 | 1303 | 23.68 | 5263.1 | 2824.6 | 2743 | 4060.9 | 1184.2 | 0.67874 | 5.976
2024-12-09 | 13:05 | Data | 0 | 32.737 | 30.658 | 179.166 | 7.63 | 167.872 | 2004.7 | 26.1 | 47.353 | 6.32 | 1.32 | 4.65 | 8097.05 | 2.066 | 97.6 | 77.9 | 1304 | 23.68 | 5263.1 | 2831.8 | 2750.1 | 4068 | 1184.2 | 0.67978 | 5.973
2024-12-09 | 13:05 | Data | 0 | 32.919 | 31.049 | 179.211 | 7.63 | 167.872 | 2010.12 | 26.11 | 47.353 | 6.32 | 1.322 | 4.654 | 8097.05 | 2.187 | 97.6 | 77.9 | 1307 | 23.63 | 5263.1 | 1756.5 | 2160.5 | 2796.7 | 1184.2 | 0.62538 | 5.977
2024-12-09 | 13:05 | Data | 0 | 32.629 | 30.826 | 179.211 | 7.63 | 167.962 | 2010.12 | 26.09 | 47.443 | 6.32 | 1.326 | 4.652 | 8558.31 | 1.755 | 97.6 | 77.8 | 1307 | 23.72 | 5562.9 | 1760 | 2145.1 | 2777.2 | 1184.2 | 0.62649 | 5.977
2024-12-09 | 13:05 | Data | 0 | 32.831 | 30.658 | 179.121 | 7.63 | 167.872 | 2009.22 | 26.1 | 47.443 | 6.32 | 1.325 | 4.655 | 8133.23 | 2.073 | 97.6 | 77.8 | 1306 | 23.72 | 5286.6 | 1770.3 | 2160.9 | 2806.2 | 1184.2 | 0.6276 | 5.98
2024-12-09 | 13:05 | Data | 0 | 32.96 | 30.907 | 179.256 | 7.63 | 168.007 | 2010.12 | 26.11 | 47.353 | 6.31 | 1.321 | 4.676 | 8137.75 | 1.971 | 97.6 | 78 | 1306 | 23.68 | 5289.5 | 1750 | 2157.8 | 2784.3 | 1184.2 | 0.62572 | 5.998
2024-12-09 | 13:05 | Data | 0 | 32.926 | 31.103 | 179.347 | 7.64 | 167.962 | 2011.93 | 26.11 | 47.623 | 6.32 | 1.313 | 4.675 | 8133.23 | 2.052 | 97.6 | 78.1 | 1308 | 23.81 | 5286.6 | 1748.9 | 2167.4 | 2799.5 | 1184.2 | 0.6223 | 5.987
2024-12-09 | 13:05 | Data | 0 | 32.723 | 30.847 | 179.211 | 7.63 | 167.917 | 2009.22 | 26.11 | 47.262 | 6.33 | 1.32 | 4.683 | 8110.61 | 1.971 | 97.6 | 78 | 1307 | 23.63 | 5271.9 | 1770 | 2167.5 | 2813.3 | 1184.2 | 0.6266 | 6.002
2024-12-09 | 13:05 | Data | 0 | 32.723 | 30.874 | 179.211 | 7.64 | 167.736 | 2009.22 | 26.11 | 47.353 | 6.32 | 1.324 | 4.662 | 8101.57 | 1.965 | 97.6 | 77.9 | 1305 | 23.68 | 5266 | 1757.1 | 2157.9 | 2797.5 | 1184.2 | 0.62511 | 5.985
2024-12-09 | 13:05 | Data | 0 | 32.717 | 30.874 | 179.211 | 7.63 | 167.917 | 2009.22 | 26.1 | 47.443 | 6.32 | 1.322 | 4.676 | 8101.57 | 2.059 | 97.6 | 78 | 1306 | 23.72 | 5266 | 1747.5 | 2146.4 | 2780.2 | 1184.2 | 0.6259 | 5.997
2024-12-09 | 13:05 | Data | 0 | 32.764 | 30.658 | 179.302 | 7.63 | 167.917 | 2011.93 | 26.1 | 47.353 | 6.32 | 1.317 | 4.673 | 8097.05 | 2.073 | 97.6 | 78 | 1307 | 23.72 | 5263.1 | 1752.3 | 2143.2 | 2781.3 | 1184.2 | 0.62746 | 5.99
2024-12-09 | 13:05 | Data | 0 | 33.176 | 30.894 | 179.302 | 7.63 | 167.962 | 2009.22 | 26.11 | 47.353 | 6.32 | 1.319 | 4.673 | 8106.09 | 2.127 | 97.6 | 78 | 1306 | 23.68 | 5269 | 1751.1 | 2138.3 | 2776.1 | 1184.2 | 0.62777 | 5.992
2024-12-09 | 13:05 | Data | 0 | 32.94 | 30.664 | 179.347 | 7.64 | 167.872 | 2009.22 | 26.1 | 47.443 | 6.31 | 1.325 | 4.685 | 8115.14 | 2.073 | 97.6 | 78 | 1306 | 23.68 | 5274.8 | 1744.6 | 2145.8 | 2778.2 | 1184.2 | 0.62509 | 6.009
2024-12-09 | 13:05 | Data | 0 | 32.811 | 30.88 | 179.256 | 7.64 | 167.872 | 2009.22 | 26.1 | 47.353 | 6.32 | 1.323 | 4.697 | 8106.09 | 2.046 | 97.6 | 78 | 1306 | 23.68 | 5269 | 1746.2 | 2157.2 | 2789.2 | 1184.2 | 0.62493 | 6.019
2024-12-09 | 13:06 | Data | 0 | 32.723 | 30.651 | 179.121 | 7.64 | 167.827 | 2008.32 | 26.11 | 47.443 | 6.32 | 1.315 | 4.68 | 8106.09 | 2.073 | 97.6 | 78.1 | 1305 | 23.72 | 5269 | 1766.6 | 2149.8 | 2796.4 | 1184.2 | 0.62857 | 5.994
2024-12-09 | 13:06 | Data | 0 | 32.757 | 30.678 | 179.302 | 7.64 | 167.962 | 2004.7 | 26.1 | 47.353 | 6.32 | 1.311 | 4.673 | 8069.91 | 2.019 | 97.6 | 78.1 | 1303 | 23.68 | 5245.4 | 1749.1 | 2164 | 2796.1 | 1184.2 | 0.62354 | 5.983
2024-12-09 | 13:06 | Data | 0 | 32.838 | 30.88 | 179.166 | 7.63 | 167.917 | 2006.51 | 26.1 | 47.353 | 6.32 | 1.32 | 4.664 | 8074.44 | 1.742 | 97.6 | 77.9 | 1305 | 23.68 | 5248.4 | 1769.9 | 2163.5 | 2812.4 | 1184.2 | 0.62963 | 5.984
2024-12-09 | 13:06 | Data | 0 | 32.723 | 30.651 | 179.256 | 7.64 | 167.827 | 2006.51 | 26.11 | 47.172 | 6.32 | 1.32 | 4.679 | 8074.44 | 2.066 | 97.6 | 78 | 1304 | 23.72 | 5248.4 | 1749.9 | 2160.1 | 2781.1 | 1184.2 | 0.61905 | 6.001
2024-12-09 | 13:06 | Data | 0 | 32.723 | 30.705 | 179.121 | 7.64 | 167.827 | 2006.51 | 26.1 | 47.353 | 6.32 | 1.313 | 4.662 | 8074.44 | 1.884 | 97.6 | 78 | 1304 | 23.68 | 5248.4 | 1750 | 2159 | 2791.7 | 1184.2 | 0.62475 | 5.975
2024-12-09 | 13:06 | Data | 0 | 32.514 | 30.766 | 179.256 | 7.64 | 167.962 | 2004.7 | 26.11 | 47.533 | 6.31 | 1.318 | 4.655 | 8088 | 1.843 | 97.6 | 77.9 | 1302 | 23.68 | 5257.2 | 1756.4 | 2156.4 | 2792.8 | 1184.3 | 0.62583 | 5.973
2024-12-09 | 13:06 | Data | 0 | 32.791 | 30.658 | 179.211 | 7.64 | 167.917 | 2001.08 | 26.11 | 47.262 | 6.32 | 1.322 | 4.654 | 8083.48 | 1.897 | 97.6 | 77.9 | 1301 | 23.68 | 5254.3 | 1759.9 | 2144.7 | 2787 | 1184.3 | 0.62903 | 5.976
2024-12-09 | 13:06 | Data | 0 | 32.838 | 30.826 | 179.256 | 7.64 | 167.962 | 2001.99 | 26.11 | 47.353 | 6.32 | 1.32 | 4.702 | 8088 | 2.079 | 97.6 | 78.1 | 1301 | 23.72 | 5257.2 | 1741.9 | 2137.2 | 2769.9 | 1184.3 | 0.62705 | 6.021
2024-12-09 | 13:06 | Data | 0 | 32.784 | 30.874 | 179.121 | 7.63 | 167.827 | 2001.99 | 26.09 | 47.353 | 6.33 | 1.314 | 4.707 | 8088 | 2.019 | 97.6 | 78.2 | 1301 | 23.72 | 5257.2 | 1737.3 | 2152.1 | 2780.4 | 1184.3 | 0.62297 | 6.021
2024-12-09 | 13:06 | Data | 0 | 32.723 | 30.664 | 179.256 | 7.64 | 167.917 | 2001.99 | 26.11 | 47.353 | 6.32 | 1.318 | 4.693 | 8101.57 | 2.046 | 97.6 | 78.1 | 1301 | 23.68 | 5266 | 1758.4 | 2155.1 | 2797.5 | 1184.3 | 0.62526 | 6.011
2024-12-09 | 13:06 | Data | 0 | 32.831 | 30.678 | 179.166 | 7.63 | 167.872 | 2002.89 | 26.11 | 47.353 | 6.32 | 1.314 | 4.662 | 8101.57 | 2.012 | 97.6 | 78 | 1301 | 23.63 | 5266 | 1745.2 | 2148.3 | 2781.2 | 1184.3 | 0.62498 | 5.977
2024-12-09 | 13:06 | Data | 0 | 32.838 | 30.772 | 179.256 | 7.63 | 167.827 | 2001.99 | 26.1 | 47.353 | 6.32 | 1.325 | 4.654 | 8097.05 | 1.87 | 97.6 | 77.8 | 1301 | 23.72 | 5263.1 | 1754.1 | 2145.6 | 2784.2 | 1184.3 | 0.62721 | 5.977
2024-12-09 | 13:06 | Data | 0 | 32.521 | 30.651 | 179.211 | 7.63 | 167.827 | 2003.8 | 26.11 | 47.353 | 6.32 | 1.324 | 4.662 | 8101.57 | 1.965 | 97.6 | 77.9 | 1303 | 23.68 | 5266 | 1751.2 | 2133.3 | 2773.5 | 1184.3 | 0.62878 | 5.985
2024-12-09 | 13:06 | Data | 0 | 32.926 | 31.076 | 179.256 | 7.63 | 167.872 | 2003.8 | 26.11 | 47.353 | 6.32 | 1.315 | 4.643 | 8038.26 | 1.904 | 97.6 | 77.9 | 1302 | 23.63 | 5224.9 | 1768.5 | 2128.8 | 2779.2 | 1184.3 | 0.63346 | 5.958
2024-12-09 | 13:06 | Data | 0 | 33.169 | 30.779 | 179.211 | 7.63 | 167.962 | 2005.6 | 26.1 | 47.443 | 6.31 | 1.317 | 4.683 | 8083.48 | 2.127 | 97.6 | 78.1 | 1304 | 23.68 | 5254.3 | 1771.4 | 2132.4 | 2785.3 | 1184.3 | 0.6331 | 6
2024-12-09 | 13:06 | Data | 0 | 32.669 | 30.88 | 179.211 | 7.63 | 167.872 | 2007.41 | 26.09 | 47.172 | 6.32 | 1.32 | 4.673 | 8069.91 | 2.012 | 97.6 | 78 | 1304 | 23.68 | 5245.4 | 1760.7 | 2154.1 | 2795.5 | 1184.3 | 0.62765 | 5.992
2024-12-09 | 13:06 | Data | 0 | 32.615 | 30.698 | 179.121 | 7.63 | 167.872 | 2006.51 | 26.11 | 47.172 | 6.32 | 1.313 | 4.67 | 8088 | 1.843 | 97.6 | 78.1 | 1302 | 23.59 | 5257.2 | 1748.1 | 2144.7 | 2779.4 | 1184.3 | 0.62694 | 5.983
2024-12-09 | 13:06 | Data | 0 | 32.737 | 31.076 | 179.302 | 7.63 | 167.917 | 2006.51 | 26.1 | 47.353 | 6.32 | 1.311 | 4.689 | 8074.44 | 1.681 | 97.6 | 78.1 | 1304 | 23.68 | 5248.4 | 1755.9 | 2144.4 | 2797.7 | 1184.3 | 0.63031 | 6
2024-12-09 | 13:07 | Data | 0 | 32.669 | 30.651 | 179.121 | 7.63 | 167.736 | 2006.51 | 26.11 | 47.262 | 6.33 | 1.315 | 4.692 | 8074.44 | 1.85 | 97.6 | 78.1 | 1304 | 23.63 | 5248.4 | 1752.6 | 2147.2 | 2785.1 | 1184.3 | 0.63036 | 6.007
2024-12-09 | 13:07 | Data | 0 | 32.919 | 31.09 | 179.166 | 7.63 | 167.917 | 2006.51 | 26.11 | 47.443 | 6.32 | 1.325 | 4.659 | 8069.91 | 2.073 | 97.6 | 77.9 | 1304 | 23.68 | 5245.4 | 1752.8 | 2159.4 | 2793.5 | 1184.3 | 0.62791 | 5.984
2024-12-09 | 13:07 | Data | 0 | 32.723 | 31.157 | 179.302 | 7.63 | 167.917 | 2006.51 | 26.11 | 47.353 | 6.32 | 1.313 | 4.663 | 8074.44 | 1.85 | 97.6 | 78 | 1304 | 23.72 | 5248.4 | 1757.3 | 2149.8 | 2787.7 | 1184.3 | 0.62478 | 5.977
2024-12-09 | 13:07 | Data | 0 | 32.521 | 30.766 | 179.211 | 7.63 | 167.827 | 2001.99 | 26.11 | 47.443 | 6.32 | 1.31 | 4.664 | 8124.18 | 1.857 | 97.6 | 78.1 | 1301 | 23.72 | 5280.7 | 1739.2 | 2137.2 | 2768.5 | 1184.3 | 0.62559 | 5.973
2024-12-09 | 13:07 | Data | 0 | 32.615 | 30.651 | 179.121 | 7.63 | 167.872 | 2010.12 | 26.11 | 47.353 | 6.31 | 1.312 | 4.636 | 8124.18 | 2.032 | 97.6 | 77.9 | 1307 | 23.72 | 5280.7 | 1759.1 | 2143.7 | 2786.8 | 1184.3 | 0.62866 | 5.95
2024-12-09 | 13:07 | Data | 0 | 33.007 | 30.786 | 179.211 | 7.64 | 167.872 | 2008.32 | 26.11 | 47.353 | 6.32 | 1.32 | 4.66 | 8142.27 | 2.073 | 97.6 | 77.9 | 1306 | 23.68 | 5292.5 | 1745.7 | 2127.1 | 2764.6 | 1184.3 | 0.62853 | 5.979
2024-12-09 | 13:07 | Data | 0 | 32.501 | 30.651 | 179.166 | 7.63 | 167.827 | 2009.22 | 26.11 | 47.443 | 6.32 | 1.324 | 4.671 | 8137.75 | 2.012 | 97.6 | 77.9 | 1307 | 23.72 | 5289.5 | 1745.2 | 2139.1 | 2771.2 | 1184.3 | 0.63187 | 5.994
2024-12-09 | 13:07 | Data | 0 | 32.94 | 30.658 | 179.211 | 7.63 | 167.872 | 2012.83 | 26.1 | 46.811 | 6.31 | 1.31 | 4.688 | 8133.23 | 1.971 | 97.7 | 78.1 | 1308 | 23.36 | 5286.6 | 1743.2 | 2141.5 | 2775 | 1184.3 | 0.6265 | 5.998
2024-12-09 | 13:07 | Data | 0 | 32.845 | 30.604 | 179.256 | 7.63 | 167.917 | 2015.55 | 26.11 | 47.353 | 6.32 | 1.32 | 4.653 | 8137.75 | 1.971 | 97.7 | 77.9 | 1310 | 23.68 | 5289.5 | 1755 | 2135.5 | 2777 | 1184.3 | 0.62901 | 5.975
2024-12-09 | 13:07 | Data | 0 | 32.636 | 30.874 | 179.211 | 7.64 | 167.917 | 2014.64 | 26.11 | 46.811 | 6.32 | 1.326 | 4.638 | 8137.75 | 1.83 | 97.7 | 77.8 | 1311 | 23.54 | 5289.5 | 1758.9 | 2147.3 | 2788.2 | 1184.3 | 0.62893 | 5.964
2024-12-09 | 13:07 | Data | 0 | 32.926 | 30.732 | 179.121 | 7.63 | 167.917 | 2015.55 | 26.11 | 47.443 | 6.32 | 1.329 | 4.635 | 8133.23 | 1.85 | 97.6 | 77.7 | 1310 | 23.72 | 5286.6 | 1752.8 | 2141.6 | 2786 | 1184.3 | 0.62647 | 5.966
2024-12-09 | 13:07 | Data | 0 | 32.838 | 30.651 | 179.166 | 7.63 | 167.917 | 2015.55 | 26.11 | 46.811 | 6.32 | 1.318 | 4.624 | 8115.14 | 1.911 | 97.7 | 77.8 | 1310 | 23.36 | 5274.8 | 1752.7 | 2145.8 | 2782.8 | 1184.3 | 0.62775 | 5.941
2024-12-09 | 13:07 | Data | 0 | 32.744 | 30.988 | 179.121 | 7.63 | 167.827 | 2014.64 | 26.09 | 47.353 | 6.32 | 1.324 | 4.663 | 8124.18 | 1.863 | 97.7 | 77.9 | 1310 | 23.63 | 5280.7 | 1751.1 | 2134.2 | 2773.6 | 1184.3 | 0.62958 | 5.986
2024-12-09 | 13:07 | Data | 0 | 32.723 | 30.651 | 179.075 | 7.63 | 167.736 | 2015.55 | 26.11 | 47.353 | 6.32 | 1.321 | 4.673 | 8115.14 | 2.073 | 97.7 | 78 | 1310 | 23.68 | 5274.8 | 1742.7 | 2151.5 | 2774.2 | 1184.3 | 0.62538 | 5.994
2024-12-09 | 13:07 | Data | 0 | 32.696 | 30.793 | 179.166 | 7.63 | 167.827 | 2013.74 | 26.11 | 47.353 | 6.32 | 1.313 | 4.646 | 8106.09 | 2.005 | 97.7 | 78 | 1308 | 23.68 | 5269 | 1754.4 | 2150.5 | 2787.9 | 1184.3 | 0.62677 | 5.96
2024-12-09 | 13:07 | Data | 0 | 32.609 | 30.651 | 179.121 | 7.63 | 167.736 | 2011.93 | 26.1 | 47.443 | 6.32 | 1.312 | 4.645 | 8133.23 | 2.059 | 97.6 | 78 | 1308 | 23.68 | 5286.6 | 1760.2 | 2136.4 | 2781.6 | 1184.3 | 0.6298 | 5.959
2024-12-09 | 13:07 | Data | 0 | 32.615 | 30.853 | 179.302 | 7.63 | 167.872 | 2012.83 | 26.1 | 47.353 | 6.32 | 1.311 | 4.677 | 8146.79 | 1.904 | 97.6 | 78.1 | 1309 | 23.72 | 5295.4 | 1750.9 | 2142.7 | 2779 | 1184.3 | 0.62862 | 5.988
2024-12-09 | 13:07 | Data | 0 | 32.804 | 30.88 | 179.256 | 7.63 | 167.917 | 2013.74 | 26.09 | 47.443 | 6.32 | 1.308 | 4.679 | 8142.27 | 1.681 | 97.6 | 78.2 | 1309 | 23.72 | 5292.5 | 1762.8 | 2156.3 | 2795.1 | 1184.3 | 0.62579 | 5.987
2024-12-09 | 13:08 | Data | 0 | 33.061 | 30.583 | 179.211 | 7.64 | 167.917 | 2009.22 | 26.11 | 47.443 | 6.32 | 1.322 | 4.7 | 8155.84 | 2.093 | 97.6 | 78.1 | 1306 | 23.72 | 5301.3 | 1750.6 | 2158.5 | 2792 | 1184.3 | 0.62468 | 6.021
2024-12-09 | 13:08 | Data | 0 | 32.669 | 30.752 | 179.03 | 7.63 | 167.691 | 2012.83 | 26.11 | 47.262 | 6.32 | 1.324 | 4.691 | 8146.79 | 2.167 | 97.7 | 78 | 1308 | 23.63 | 5295.4 | 1741.7 | 2138.8 | 2772.3 | 1184.3 | 0.62587 | 6.015
2024-12-09 | 13:08 | Data | 0 | 32.507 | 30.543 | 179.211 | 7.63 | 167.872 | 2012.83 | 26.11 | 47.353 | 6.32 | 1.32 | 4.683 | 8155.84 | 2.052 | 97.6 | 78 | 1308 | 23.72 | 5301.3 | 1746.9 | 2139.4 | 2775.6 | 1184.3 | 0.62758 | 6.003
2024-12-09 | 13:08 | Data | 0 | 32.777 | 30.678 | 179.166 | 7.63 | 167.917 | 2013.74 | 26.11 | 47.443 | 6.31 | 1.315 | 4.68 | 8160.36 | 1.917 | 97.6 | 78.1 | 1308 | 23.63 | 5304.2 | 1762.7 | 2143 | 2787.1 | 1184.3 | 0.63031 | 5.995
2024-12-09 | 13:08 | Data | 0 | 32.94 | 30.705 | 179.121 | 7.63 | 167.872 | 2012.83 | 26.11 | 47.443 | 6.32 | 1.321 | 4.649 | 8160.36 | 2.066 | 97.6 | 77.8 | 1309 | 23.68 | 5304.2 | 1996.8 | 2514.5 | 3219.2 | 1184.3 | 0.61198 | 5.972
2024-12-09 | 13:08 | Data | 0 | 32.501 | 30.651 | 179.166 | 7.63 | 167.872 | 2010.12 | 26.11 | 47.443 | 6.32 | 1.322 | 4.654 | 8169.4 | 2.019 | 97.6 | 77.9 | 1308 | 23.72 | 5310.1 | 2830.8 | 2731.5 | 4058.5 | 1184.3 | 0.68212 | 5.975
2024-12-09 | 13:08 | Data | 0 | 32.696 | 30.739 | 179.121 | 7.63 | 167.827 | 2012.83 | 26.11 | 47.353 | 6.32 | 1.318 | 4.68 | 8169.4 | 2.059 | 97.6 | 78 | 1308 | 23.63 | 5310.1 | 2833.9 | 2747.9 | 4075.3 | 1184.3 | 0.67884 | 5.998
2024-12-09 | 13:08 | Data | 0 | 32.994 | 30.712 | 179.302 | 7.63 | 167.917 | 2012.83 | 26.1 | 47.443 | 6.32 | 1.325 | 4.673 | 8178.45 | 2.066 | 97.6 | 77.9 | 1308 | 23.68 | 5316 | 2841 | 2751.1 | 4081.6 | 1184.3 | 0.67777 | 5.998
2024-12-09 | 13:08 | Data | 0 | 32.507 | 30.982 | 179.256 | 7.63 | 167.827 | 2013.74 | 26.11 | 47.443 | 6.32 | 1.317 | 4.679 | 8164.88 | 1.931 | 97.6 | 78 | 1309 | 23.72 | 5307.2 | 2836.7 | 2768.1 | 4086.9 | 1184.3 | 0.67915 | 5.996
2024-12-09 | 13:08 | Data | 0 | 32.723 | 30.874 | 179.166 | 7.63 | 167.691 | 2013.74 | 26.1 | 47.443 | 6.32 | 1.311 | 4.671 | 8173.92 | 1.971 | 97.6 | 78.1 | 1308 | 23.72 | 5313.1 | 2847.1 | 2753.7 | 4080.7 | 1184.3 | 0.68215 | 5.983
2024-12-09 | 13:08 | Data | 0 | 32.393 | 30.442 | 179.211 | 7.63 | 167.827 | 2010.12 | 26.11 | 47.353 | 6.32 | 1.31 | 4.673 | 8164.88 | 2.228 | 97.6 | 78.1 | 1307 | 23.72 | 5307.2 | 2833 | 2763.2 | 4078.9 | 1184.3 | 0.67857 | 5.983
2024-12-09 | 13:08 | Data | 0 | 32.831 | 30.664 | 179.211 | 7.63 | 167.872 | 2008.32 | 26.11 | 47.353 | 6.31 | 1.313 | 4.675 | 8169.4 | 1.971 | 97.6 | 78.1 | 1306 | 23.68 | 5310.1 | 2839.7 | 2774.5 | 4093.3 | 1184.3 | 0.67673 | 5.988
2024-12-09 | 13:08 | Data | 0 | 32.636 | 30.651 | 179.03 | 7.63 | 167.827 | 2010.12 | 26.11 | 47.353 | 6.32 | 1.329 | 4.657 | 8169.4 | 2.052 | 97.6 | 77.8 | 1305 | 23.72 | 5310.1 | 2846.4 | 2746.9 | 4080 | 1184.3 | 0.6808 | 5.987
2024-12-09 | 13:08 | Data | 0 | 32.723 | 30.867 | 179.166 | 7.63 | 167.736 | 2009.22 | 26.09 | 47.353 | 6.32 | 1.326 | 4.685 | 8173.92 | 2.073 | 97.6 | 77.9 | 1306 | 23.68 | 5313.1 | 2825.4 | 2743.8 | 4066.1 | 1184.3 | 0.67849 | 6.01
2024-12-09 | 13:08 | Data | 0 | 32.474 | 30.651 | 179.075 | 7.63 | 167.827 | 2009.22 | 26.08 | 47.353 | 6.32 | 1.319 | 4.694 | 8155.84 | 2.039 | 97.6 | 78.1 | 1306 | 23.68 | 5301.3 | 2816.2 | 2746.1 | 4058.4 | 1184.3 | 0.67846 | 6.013
2024-12-09 | 13:08 | Data | 0 | 32.784 | 30.563 | 179.211 | 7.63 | 167.917 | 2010.12 | 26.08 | 47.443 | 6.32 | 1.323 | 4.688 | 8155.84 | 1.985 | 97.6 | 78 | 1306 | 23.68 | 5301.3 | 2826.3 | 2722.8 | 4050.8 | 1184.3 | 0.68076 | 6.011
2024-12-09 | 13:08 | Data | 0 | 32.723 | 30.651 | 179.075 | 7.63 | 167.691 | 2009.22 | 26.08 | 47.533 | 6.33 | 1.322 | 4.673 | 8164.88 | 1.897 | 97.6 | 77.9 | 1306 | 23.68 | 5307.2 | 2836.9 | 2743.7 | 4067.4 | 1184.3 | 0.68149 | 5.998
2024-12-09 | 13:08 | Data | 0 | 32.555 | 30.651 | 179.075 | 7.63 | 167.872 | 2012.83 | 26.06 | 47.353 | 6.32 | 1.322 | 4.673 | 8169.4 | 1.85 | 97.6 | 77.9 | 1308 | 23.68 | 5310.1 | 2837.9 | 2733 | 4065.2 | 1184.3 | 0.68138 | 5.995
2024-12-09 | 13:09 | Data | 0 | 32.669 | 30.651 | 179.121 | 7.63 | 167.736 | 2013.74 | 26.06 | 47.262 | 6.32 | 1.322 | 4.679 | 8137.75 | 2.066 | 97.6 | 78 | 1308 | 23.68 | 5289.5 | 2824.4 | 2725.9 | 4048.4 | 1184.3 | 0.68065 | 5.998
2024-12-09 | 13:09 | Data | 0 | 32.582 | 30.86 | 179.211 | 7.63 | 167.872 | 2010.12 | 26.07 | 47.443 | 6.32 | 1.324 | 4.65 | 8137.75 | 1.85 | 97.6 | 77.8 | 1308 | 23.72 | 5289.5 | 2846.4 | 2719.6 | 4061.7 | 1184.3 | 0.68452 | 5.975
2024-12-09 | 13:09 | Data | 0 | 32.757 | 30.55 | 179.03 | 7.64 | 167.827 | 2013.74 | 26.06 | 47.082 | 6.31 | 1.327 | 4.654 | 8137.75 | 2.073 | 97.6 | 77.8 | 1308 | 23.72 | 5289.5 | 2832.6 | 2734.5 | 4059.7 | 1184.4 | 0.68115 | 5.978
2024-12-09 | 13:09 | Data | 0 | 32.723 | 30.651 | 179.121 | 7.63 | 167.736 | 2017.35 | 26.06 | 47.443 | 6.32 | 1.326 | 4.668 | 8110.61 | 2.073 | 97.7 | 77.9 | 1312 | 23.68 | 5271.9 | 2842.3 | 2750.4 | 4076.4 | 1184.4 | 0.6814 | 5.993
2024-12-09 | 13:09 | Data | 0 | 32.663 | 30.651 | 179.256 | 7.63 | 167.917 | 2018.26 | 26.08 | 47.443 | 6.32 | 1.319 | 4.685 | 8155.84 | 2.039 | 97.7 | 78 | 1312 | 23.68 | 5301.3 | 2841.8 | 2736.1 | 4065.9 | 1184.4 | 0.68377 | 6.003
2024-12-09 | 13:09 | Data | 0 | 32.933 | 30.766 | 179.302 | 7.63 | 167.917 | 2018.26 | 26.08 | 47.172 | 6.32 | 1.325 | 4.673 | 8155.84 | 2.066 | 97.6 | 77.9 | 1311 | 23.68 | 5301.3 | 2849.4 | 2741.6 | 4075.4 | 1184.4 | 0.68215 | 5.997
2024-12-09 | 13:09 | Data | 0 | 32.953 | 30.685 | 179.166 | 7.63 | 167.917 | 2016.45 | 26.08 | 47.623 | 6.32 | 1.324 | 4.645 | 8124.18 | 1.897 | 97.6 | 77.8 | 1311 | 23.86 | 5280.7 | 2827.8 | 2749.8 | 4069 | 1184.4 | 0.67734 | 5.969
2024-12-09 | 13:09 | Data | 0 | 32.71 | 30.766 | 179.121 | 7.63 | 167.872 | 2018.26 | 26.08 | 47.172 | 6.32 | 1.32 | 4.643 | 8142.27 | 2.066 | 97.7 | 77.9 | 1312 | 23.54 | 5292.5 | 2847.8 | 2736 | 4071 | 1184.4 | 0.68304 | 5.963
2024-12-09 | 13:09 | Data | 0 | 32.568 | 30.651 | 179.121 | 7.63 | 167.872 | 2019.16 | 26.08 | 47.082 | 6.32 | 1.313 | 4.658 | 8124.18 | 1.863 | 97.7 | 78 | 1312 | 23.59 | 5280.7 | 2830.7 | 2727.2 | 4050.7 | 1184.4 | 0.68122 | 5.972
2024-12-09 | 13:09 | Data | 0 | 32.831 | 30.705 | 179.302 | 7.63 | 167.872 | 2016.45 | 26.08 | 47.172 | 6.32 | 1.315 | 4.653 | 8142.27 | 1.897 | 97.7 | 78 | 1311 | 23.54 | 5292.5 | 2824.4 | 2749.1 | 4066.9 | 1184.4 | 0.67807 | 5.968
2024-12-09 | 13:09 | Data | 0 | 32.73 | 30.779 | 179.166 | 7.63 | 167.917 | 2015.55 | 26.09 | 47.082 | 6.32 | 1.319 | 4.664 | 8133.23 | 2.052 | 97.7 | 78 | 1311 | 23.54 | 5286.6 | 2839.9 | 2774.6 | 4093 | 1184.4 | 0.67759 | 5.982
2024-12-09 | 13:09 | Data | 0 | 32.507 | 30.651 | 179.166 | 7.63 | 167.827 | 2015.55 | 26.08 | 47.082 | 6.31 | 1.314 | 4.635 | 8128.7 | 1.958 | 97.7 | 77.9 | 1310 | 23.54 | 5283.7 | 2846.6 | 2760 | 4089 | 1184.4 | 0.67976 | 5.95
2024-12-09 | 13:09 | Data | 0 | 32.71 | 30.651 | 179.166 | 7.63 | 167.736 | 2012.83 | 26.08 | 46.811 | 6.31 | 1.32 | 4.638 | 8110.61 | 2.066 | 97.7 | 77.8 | 1308 | 23.41 | 5271.9 | 2838.1 | 2737.4 | 4066.7 | 1184.4 | 0.68067 | 5.958
2024-12-09 | 13:09 | Data | 0 | 32.501 | 30.739 | 179.302 | 7.63 | 167.827 | 2012.83 | 26.09 | 47.172 | 6.32 | 1.326 | 4.669 | 8110.61 | 1.843 | 97.7 | 77.9 | 1308 | 23.59 | 5271.9 | 2841.2 | 2748.5 | 4072.6 | 1184.4 | 0.68048 | 5.996
2024-12-09 | 13:09 | Data | 0 | 32.75 | 30.651 | 179.075 | 7.63 | 167.736 | 2015.55 | 26.09 | 47.262 | 6.32 | 1.321 | 4.656 | 8115.14 | 2.073 | 97.7 | 77.9 | 1310 | 23.59 | 5274.8 | 2841.4 | 2743.5 | 4071.9 | 1184.4 | 0.68051 | 5.977
2024-12-09 | 13:09 | Data | 0 | 32.946 | 30.766 | 179.211 | 7.63 | 167.917 | 2013.74 | 26.08 | 47.262 | 6.32 | 1.32 | 4.636 | 8110.61 | 1.951 | 97.7 | 77.8 | 1308 | 23.63 | 5271.9 | 2834.9 | 2729.6 | 4056.3 | 1184.4 | 0.68242 | 5.957
2024-12-09 | 13:09 | Data | 0 | 32.811 | 31.09 | 179.211 | 7.63 | 167.917 | 2012.83 | 26.09 | 47.172 | 6.31 | 1.327 | 4.645 | 8097.05 | 1.971 | 97.7 | 77.8 | 1309 | 23.59 | 5263.1 | 2854 | 2733 | 4070.6 | 1184.4 | 0.68496 | 5.971
2024-12-09 | 13:10 | Data | 0 | 32.514 | 30.793 | 179.121 | 7.63 | 167.872 | 2012.83 | 26.09 | 47.082 | 6.32 | 1.321 | 4.654 | 8092.52 | 1.897 | 97.7 | 77.9 | 1308 | 23.54 | 5260.1 | 2843 | 2730.6 | 4069.6 | 1184.4 | 0.68365 | 5.975
2024-12-09 | 13:10 | Data | 0 | 32.723 | 30.739 | 179.166 | 7.63 | 167.736 | 2010.12 | 26.09 | 47.082 | 6.32 | 1.312 | 4.645 | 8110.61 | 1.958 | 97.7 | 78 | 1308 | 23.54 | 5271.9 | 2836.3 | 2739.8 | 4067.3 | 1184.4 | 0.68113 | 5.958
2024-12-09 | 13:10 | Data | 0 | 32.723 | 30.455 | 179.166 | 7.63 | 167.917 | 2011.93 | 26.09 | 47.172 | 6.32 | 1.319 | 4.675 | 8101.57 | 2.221 | 97.7 | 78 | 1308 | 23.54 | 5266 | 2846.9 | 2735.1 | 4065.1 | 1184.4 | 0.6849 | 5.996
2024-12-09 | 13:10 | Data | 0 | 32.717 | 30.651 | 179.121 | 7.63 | 167.827 | 2012.83 | 26.08 | 47.082 | 6.33 | 1.323 | 4.666 | 8124.18 | 1.897 | 97.7 | 77.9 | 1308 | 23.54 | 5280.7 | 2848 | 2745.8 | 4078.6 | 1184.4 | 0.682 | 5.989
2024-12-09 | 13:10 | Data | 0 | 32.669 | 30.651 | 179.211 | 7.63 | 167.872 | 2013.74 | 26.09 | 47.172 | 6.31 | 1.32 | 4.646 | 8128.7 | 2.046 | 97.7 | 77.9 | 1308 | 23.54 | 5283.7 | 2844.2 | 2761.9 | 4086.2 | 1184.4 | 0.6788 | 5.967
2024-12-09 | 13:10 | Data | 0 | 32.71 | 30.867 | 179.211 | 7.64 | 167.827 | 2013.74 | 26.09 | 47.172 | 6.32 | 1.32 | 4.639 | 8124.18 | 2.005 | 97.7 | 77.9 | 1308 | 23.59 | 5280.7 | 2841 | 2762.8 | 4086.3 | 1184.4 | 0.6781 | 5.959
2024-12-09 | 13:10 | Data | 0 | 32.73 | 30.651 | 179.211 | 7.63 | 167.917 | 2013.74 | 26.08 | 47.082 | 6.32 | 1.321 | 4.67 | 8142.27 | 2.073 | 97.7 | 78 | 1308 | 23.59 | 5292.5 | 2855.7 | 2772.2 | 4097.9 | 1184.4 | 0.67684 | 5.993
2024-12-09 | 13:10 | Data | 0 | 32.946 | 31.103 | 179.392 | 7.63 | 167.962 | 2012.83 | 26.08 | 47.082 | 6.32 | 1.312 | 4.652 | 8092.52 | 2.052 | 97.7 | 78 | 1308 | 23.41 | 5260.1 | 2841.8 | 2773.2 | 4092.1 | 1184.4 | 0.67866 | 5.964
2024-12-09 | 13:10 | Data | 0 | 32.899 | 30.88 | 179.121 | 7.63 | 167.827 | 2009.22 | 26.08 | 47.082 | 6.32 | 1.314 | 4.648 | 8097.05 | 2.066 | 97.7 | 78 | 1305 | 23.54 | 5263.1 | 2839.2 | 2763.6 | 4085.6 | 1184.4 | 0.67726 | 5.962
2024-12-09 | 13:10 | Data | 0 | 32.548 | 30.651 | 179.211 | 7.64 | 167.872 | 2003.8 | 26.08 | 47.172 | 6.32 | 1.315 | 4.664 | 8097.05 | 2.025 | 97.7 | 78 | 1302 | 23.54 | 5263.1 | 2852.2 | 2741.3 | 4079.9 | 1184.4 | 0.6823 | 5.98
2024-12-09 | 13:10 | Data | 0 | 32.94 | 30.88 | 179.256 | 7.63 | 167.872 | 2010.12 | 26.08 | 47.172 | 6.31 | 1.32 | 4.648 | 8088 | 2.073 | 97.7 | 77.9 | 1306 | 23.59 | 5257.2 | 2844.1 | 2734 | 4068.8 | 1184.4 | 0.68283 | 5.967
2024-12-09 | 13:10 | Data | 0 | 32.723 | 30.651 | 179.121 | 7.63 | 167.872 | 2009.22 | 26.08 | 47.353 | 6.31 | 1.319 | 4.662 | 7934.25 | 2.059 | 97.6 | 78 | 1306 | 23.68 | 5157.3 | 2849.5 | 2728.1 | 4068 | 1184.4 | 0.68394 | 5.98
2024-12-09 | 13:10 | Data | 0 | 32.703 | 30.894 | 179.347 | 7.63 | 167.917 | 2009.22 | 26.08 | 47.082 | 6.31 | 1.318 | 4.687 | 7956.86 | 2.052 | 97.6 | 78.1 | 1306 | 23.63 | 5172 | 2846.5 | 2731.2 | 4063.9 | 1184.4 | 0.68306 | 6.005
2024-12-09 | 13:10 | Data | 0 | 32.46 | 30.867 | 179.256 | 7.63 | 167.962 | 2003.8 | 26.08 | 47.353 | 6.31 | 1.311 | 4.664 | 7956.86 | 1.803 | 97.6 | 78.1 | 1302 | 23.68 | 5172 | 2833.8 | 2743.2 | 4068.3 | 1184.4 | 0.67971 | 5.976
2024-12-09 | 13:10 | Data | 0 | 32.926 | 30.705 | 179.211 | 7.64 | 167.827 | 2009.22 | 26.09 | 47.353 | 6.32 | 1.321 | 4.664 | 7965.9 | 2.066 | 97.6 | 77.9 | 1306 | 23.72 | 5177.8 | 2859.2 | 2772 | 4103.4 | 1184.4 | 0.68025 | 5.986
2024-12-09 | 13:10 | Data | 0 | 32.494 | 30.752 | 179.166 | 7.63 | 167.827 | 2006.51 | 26.09 | 47.533 | 6.32 | 1.307 | 4.664 | 8169.4 | 1.985 | 97.6 | 78.1 | 1304 | 23.68 | 5310.1 | 2833.6 | 2767.5 | 4081.9 | 1184.4 | 0.67662 | 5.97
2024-12-09 | 13:10 | Data | 0 | 32.717 | 30.482 | 179.121 | 7.64 | 167.872 | 2007.41 | 26.08 | 47.443 | 6.32 | 1.315 | 4.663 | 8146.79 | 2.241 | 97.6 | 78 | 1305 | 23.72 | 5295.4 | 2839.4 | 2766.6 | 4085.5 | 1184.4 | 0.67785 | 5.978
2024-12-09 | 13:10 | Data | 0 | 32.94 | 30.88 | 179.256 | 7.63 | 167.917 | 2011.93 | 26.09 | 47.262 | 6.31 | 1.326 | 4.646 | 8137.75 | 2.066 | 97.6 | 77.8 | 1307 | 23.68 | 5289.5 | 2842.4 | 2767.9 | 4085.9 | 1184.4 | 0.67952 | 5.971
2024-12-09 | 13:11 | Data | 0 | 32.723 | 30.793 | 179.256 | 7.63 | 167.917 | 2011.93 | 26.09 | 47.353 | 6.32 | 1.321 | 4.657 | 8155.84 | 2.046 | 97.6 | 77.9 | 1305 | 23.72 | 5301.3 | 2832.3 | 2762.5 | 4081.9 | 1184.4 | 0.67591 | 5.979
2024-12-09 | 13:11 | Data | 0 | 32.723 | 30.968 | 179.302 | 7.63 | 167.872 | 2012.83 | 26.09 | 47.262 | 6.32 | 1.32 | 4.672 | 8155.84 | 1.897 | 97.7 | 78 | 1308 | 23.59 | 5301.3 | 2842.1 | 2784.5 | 4101.9 | 1184.4 | 0.67614 | 5.991
2024-12-09 | 13:11 | Data | 0 | 32.919 | 30.88 | 179.121 | 7.63 | 167.872 | 2013.74 | 26.08 | 47.353 | 6.32 | 1.315 | 4.664 | 8164.88 | 2.073 | 97.6 | 78 | 1308 | 23.68 | 5307.2 | 2841.3 | 2756.1 | 4080.3 | 1184.4 | 0.67979 | 5.979
2024-12-09 | 13:11 | Data | 0 | 32.858 | 30.658 | 179.256 | 7.63 | 167.917 | 2009.22 | 26.09 | 47.353 | 6.31 | 1.324 | 4.67 | 8137.75 | 1.884 | 97.6 | 77.9 | 1306 | 23.72 | 5289.5 | 2841 | 2734.5 | 4068.6 | 1184.4 | 0.6815 | 5.993
2024-12-09 | 13:11 | Data | 0 | 32.717 | 31.083 | 179.166 | 7.63 | 167.872 | 2010.12 | 26.09 | 47.353 | 6.31 | 1.322 | 4.654 | 8155.84 | 2.127 | 97.6 | 77.9 | 1306 | 23.68 | 5301.3 | 2811.7 | 2728.2 | 4044.6 | 1184.5 | 0.67996 | 5.976
2024-12-09 | 13:11 | Data | 0 | 32.899 | 30.651 | 179.211 | 7.63 | 167.917 | 2008.32 | 26.08 | 47.443 | 6.32 | 1.32 | 4.652 | 8133.23 | 2.1 | 97.6 | 77.9 | 1306 | 23.72 | 5286.6 | 2838.4 | 2755.4 | 4078.5 | 1184.5 | 0.67853 | 5.971
2024-12-09 | 13:11 | Data | 0 | 33.007 | 30.691 | 179.256 | 7.63 | 168.007 | 2009.22 | 26.09 | 47.353 | 6.32 | 1.322 | 4.642 | 8110.61 | 1.897 | 97.6 | 77.8 | 1306 | 23.68 | 5271.9 | 2844.1 | 2743.5 | 4075.5 | 1184.5 | 0.68035 | 5.964
2024-12-09 | 13:11 | Data | 0 | 32.94 | 30.88 | 179.121 | 7.63 | 167.827 | 2010.12 | 26.08 | 47.353 | 6.32 | 1.324 | 4.648 | 8128.7 | 1.958 | 97.6 | 77.8 | 1305 | 23.72 | 5283.7 | 2845.3 | 2752.1 | 4078.5 | 1184.5 | 0.68091 | 5.973
2024-12-09 | 13:11 | Data | 0 | 32.73 | 30.658 | 179.075 | 7.63 | 167.872 | 2008.32 | 26.1 | 47.353 | 6.32 | 1.324 | 4.64 | 8119.66 | 2.046 | 97.6 | 77.8 | 1305 | 23.68 | 5277.8 | 2842.3 | 2773.8 | 4093.4 | 1184.5 | 0.67846 | 5.964
2024-12-09 | 13:11 | Data | 0 | 32.75 | 30.853 | 179.256 | 7.63 | 167.917 | 2012.83 | 26.09 | 47.353 | 6.32 | 1.339 | 4.654 | 8146.79 | 1.904 | 97.6 | 77.7 | 1308 | 23.68 | 5295.4 | 2843.2 | 2788.5 | 4105.5 | 1184.5 | 0.67496 | 5.994
2024-12-09 | 13:11 | Data | 0 | 32.831 | 30.988 | 179.256 | 7.63 | 167.872 | 2011.93 | 26.08 | 47.353 | 6.32 | 1.322 | 4.662 | 8133.23 | 1.85 | 97.6 | 77.9 | 1308 | 23.68 | 5286.6 | 2832.4 | 2785.4 | 4093.8 | 1184.5 | 0.67475 | 5.984
2024-12-09 | 13:11 | Data | 0 | 32.852 | 30.658 | 179.347 | 7.63 | 167.962 | 2010.12 | 26.08 | 47.443 | 6.32 | 1.324 | 4.681 | 8137.75 | 1.971 | 97.6 | 78 | 1307 | 23.72 | 5289.5 | 2841.9 | 2759.1 | 4083.9 | 1184.5 | 0.67901 | 6.005
2024-12-09 | 13:11 | Data | 0 | 32.831 | 30.766 | 179.121 | 7.63 | 167.827 | 2013.74 | 26.09 | 47.443 | 6.32 | 1.32 | 4.682 | 8155.84 | 2.066 | 97.6 | 78 | 1308 | 23.68 | 5301.3 | 2824 | 2760.5 | 4072 | 1184.5 | 0.67687 | 5.998
2024-12-09 | 13:11 | Data | 0 | 32.305 | 30.651 | 179.211 | 7.63 | 167.917 | 2012.83 | 26.09 | 47.443 | 6.32 | 1.329 | 4.664 | 8169.4 | 1.796 | 97.6 | 77.8 | 1308 | 23.68 | 5310.1 | 2828.1 | 2760.1 | 4077 | 1184.5 | 0.67758 | 5.991
2024-12-09 | 13:11 | Data | 0 | 32.838 | 31.069 | 179.347 | 7.63 | 168.007 | 2012.83 | 26.08 | 47.262 | 6.32 | 1.315 | 4.669 | 8142.27 | 1.938 | 97.7 | 78 | 1308 | 23.59 | 5292.5 | 2832.7 | 2735.1 | 4058.9 | 1184.5 | 0.6805 | 5.984
2024-12-09 | 13:11 | Data | 0 | 32.561 | 30.658 | 179.166 | 7.63 | 167.917 | 2014.64 | 26.08 | 47.353 | 6.32 | 1.318 | 4.68 | 8119.66 | 1.958 | 97.7 | 78 | 1310 | 23.68 | 5277.8 | 2826.9 | 2739.6 | 4061.1 | 1184.5 | 0.6781 | 5.998
2024-12-09 | 13:11 | Data | 0 | 32.501 | 30.766 | 179.211 | 7.63 | 167.736 | 2015.55 | 26.08 | 47.353 | 6.32 | 1.317 | 4.679 | 8101.57 | 2.019 | 97.7 | 78 | 1310 | 23.68 | 5266 | 2845.7 | 2770.5 | 4094.6 | 1184.5 | 0.67846 | 5.995
2024-12-09 | 13:11 | Data | 0 | 33.007 | 31.056 | 179.392 | 7.63 | 167.962 | 2017.35 | 26.09 | 47.443 | 6.32 | 1.309 | 4.638 | 8264.37 | 1.904 | 97.6 | 78 | 1311 | 23.72 | 5371.8 | 2846.8 | 2758 | 4085.5 | 1184.5 | 0.68006 | 5.947
2024-12-09 | 13:12 | Data | 0 | 32.723 | 30.826 | 179.211 | 7.63 | 167.917 | 2020.97 | 26.08 | 47.533 | 6.32 | 1.32 | 4.641 | 8291.5 | 1.897 | 97.7 | 77.9 | 1314 | 23.72 | 5389.5 | 2838.1 | 2744.8 | 4074.2 | 1184.5 | 0.67942 | 5.961
2024-12-09 | 13:12 | Data | 0 | 32.501 | 30.536 | 179.121 | 7.63 | 167.872 | 2020.07 | 26.08 | 47.443 | 6.32 | 1.32 | 4.657 | 8286.98 | 1.958 | 97.7 | 77.9 | 1313 | 23.68 | 5386.5 | 2837.9 | 2765.6 | 4086.5 | 1184.5 | 0.6769 | 5.977
2024-12-09 | 13:12 | Data | 0 | 32.528 | 30.766 | 179.166 | 7.63 | 167.917 | 2014.64 | 26.09 | 47.443 | 6.31 | 1.315 | 4.662 | 8291.5 | 1.965 | 97.6 | 78 | 1310 | 23.72 | 5389.5 | 2836.1 | 2798.9 | 4103.1 | 1184.5 | 0.67813 | 5.975
2024-12-09 | 13:12 | Data | 0 | 32.831 | 30.705 | 179.256 | 7.63 | 167.962 | 2015.55 | 26.09 | 47.353 | 6.32 | 1.321 | 4.67 | 8124.18 | 1.863 | 97.7 | 77.9 | 1310 | 23.68 | 5280.7 | 2819.7 | 2765.4 | 4070.4 | 1184.5 | 0.67477 | 5.991
2024-12-09 | 13:12 | Data | 0 | 32.514 | 30.442 | 179.166 | 7.63 | 167.917 | 2014.64 | 26.09 | 47.353 | 6.32 | 1.324 | 4.643 | 8124.18 | 1.965 | 97.6 | 77.8 | 1310 | 23.72 | 5280.7 | 2835.6 | 2760.6 | 4080.9 | 1184.5 | 0.67786 | 5.967
2024-12-09 | 13:12 | Data | 0 | 32.507 | 30.644 | 179.121 | 7.63 | 167.872 | 2016.45 | 26.09 | 47.353 | 6.31 | 1.324 | 4.647 | 8128.7 | 1.863 | 97.7 | 77.8 | 1311 | 23.68 | 5283.7 | 2822.2 | 2759.3 | 4065.8 | 1184.5 | 0.67693 | 5.97
2024-12-09 | 13:12 | Data | 0 | 32.838 | 30.88 | 179.392 | 7.64 | 167.962 | 2018.26 | 26.09 | 47.443 | 6.32 | 1.319 | 4.672 | 8124.18 | 2.066 | 97.7 | 78 | 1312 | 23.72 | 5280.7 | 2813 | 2765.6 | 4067.4 | 1184.5 | 0.67342 | 5.991
2024-12-09 | 13:12 | Data | 0 | 32.723 | 30.448 | 179.256 | 7.63 | 167.872 | 2019.16 | 26.08 | 47.353 | 6.32 | 1.313 | 4.656 | 8124.18 | 2.066 | 97.7 | 78 | 1312 | 23.72 | 5280.7 | 2839.4 | 2760.9 | 4079 | 1184.5 | 0.67952 | 5.97
2024-12-09 | 13:12 | Data | 0 | 32.696 | 30.968 | 179.302 | 7.63 | 167.872 | 2018.26 | 26.09 | 47.082 | 6.32 | 1.313 | 4.645 | 8110.61 | 2.059 | 97.7 | 78 | 1312 | 23.59 | 5271.9 | 2833.2 | 2766.7 | 4082.6 | 1184.5 | 0.67588 | 5.959
2024-12-09 | 13:12 | Data | 0 | 32.994 | 30.907 | 179.347 | 7.63 | 167.962 | 2017.35 | 26.08 | 47.353 | 6.32 | 1.318 | 4.645 | 8128.7 | 2.228 | 97.7 | 77.9 | 1311 | 23.72 | 5283.7 | 2851 | 2763.6 | 4094.5 | 1184.5 | 0.67855 | 5.965
2024-12-09 | 13:12 | Data | 0 | 32.838 | 31.103 | 179.392 | 7.63 | 168.098 | 2015.55 | 26.1 | 47.353 | 6.32 | 1.319 | 4.667 | 8110.61 | 2.012 | 97.7 | 78 | 1310 | 23.68 | 5271.9 | 2832.1 | 2776.3 | 4088.7 | 1184.5 | 0.67491 | 5.986
2024-12-09 | 13:12 | Data | 0 | 32.946 | 30.874 | 179.347 | 7.63 | 167.962 | 2015.55 | 26.08 | 47.172 | 6.31 | 1.312 | 4.657 | 8110.61 | 1.992 | 97.7 | 78 | 1310 | 23.54 | 5271.9 | 2835.7 | 2799 | 4107.7 | 1184.5 | 0.6723 | 5.969
2024-12-09 | 13:12 | Data | 0 | 33.162 | 30.934 | 179.392 | 7.63 | 168.053 | 2013.74 | 26.09 | 47.443 | 6.32 | 1.319 | 4.65 | 8128.7 | 2.019 | 97.6 | 77.9 | 1308 | 23.68 | 5283.7 | 2846.9 | 2765.3 | 4090.8 | 1184.5 | 0.67932 | 5.968
2024-12-09 | 13:12 | Data | 0 | 32.723 | 30.874 | 179.166 | 7.63 | 167.872 | 2012.83 | 26.1 | 47.353 | 6.31 | 1.32 | 4.626 | 8110.61 | 1.971 | 97.6 | 77.8 | 1308 | 23.72 | 5271.9 | 2843.8 | 2775.5 | 4092.3 | 1184.5 | 0.67698 | 5.947
2024-12-09 | 13:12 | Data | 0 | 32.953 | 30.934 | 179.347 | 7.63 | 168.007 | 2011.93 | 26.08 | 47.443 | 6.32 | 1.31 | 4.646 | 8124.18 | 1.965 | 97.6 | 78 | 1308 | 23.68 | 5280.7 | 2834.8 | 2773.6 | 4092.3 | 1184.5 | 0.67472 | 5.958
2024-12-09 | 13:12 | Data | 0 | 32.953 | 31.083 | 179.302 | 7.63 | 168.007 | 2007.41 | 26.09 | 47.262 | 6.32 | 1.313 | 4.648 | 8115.14 | 1.87 | 97.6 | 78 | 1305 | 23.68 | 5274.8 | 2840.9 | 2765.4 | 4085.9 | 1184.5 | 0.67795 | 5.961
2024-12-09 | 13:12 | Data | 0 | 32.953 | 30.88 | 179.347 | 7.63 | 168.007 | 2017.35 | 26.09 | 47.353 | 6.32 | 1.31 | 4.641 | 8124.18 | 2.073 | 97.7 | 78 | 1311 | 23.68 | 5280.7 | 2843.5 | 2770.7 | 4078.9 | 1184.5 | 0.6759 | 5.95
2024-12-09 | 13:12 | Data | 0 | 32.946 | 30.88 | 179.211 | 7.63 | 167.917 | 2012.83 | 26.1 | 47.172 | 6.31 | 1.319 | 4.662 | 8133.23 | 2.012 | 97.7 | 78 | 1308 | 23.59 | 5286.6 | 2837.6 | 2757.4 | 4078.6 | 1184.5 | 0.68227 | 5.98
2024-12-09 | 13:13 | Data | 0 | 32.973 | 30.793 | 179.347 | 7.63 | 167.962 | 2008.32 | 26.08 | 47.443 | 6.31 | 1.31 | 4.659 | 8133.23 | 2.174 | 97.6 | 78 | 1305 | 23.72 | 5286.6 | 2836.2 | 2770.3 | 4083.6 | 1184.5 | 0.67621 | 5.969
2024-12-09 | 13:13 | Data | 0 | 33.054 | 31.103 | 179.347 | 7.63 | 168.053 | 2009.22 | 26.09 | 47.172 | 6.31 | 1.311 | 4.673 | 8173.92 | 2.066 | 97.7 | 78.1 | 1305 | 23.54 | 5313.1 | 2848.3 | 2753.6 | 4087.8 | 1184.5 | 0.68025 | 5.985
2024-12-09 | 13:13 | Data | 0 | 32.825 | 31.096 | 179.392 | 7.63 | 168.007 | 2009.22 | 26.09 | 47.262 | 6.32 | 1.317 | 4.672 | 8160.36 | 1.958 | 97.6 | 78 | 1306 | 23.72 | 5304.2 | 2842.7 | 2737.4 | 4068 | 1184.5 | 0.68041 | 5.988
2024-12-09 | 13:13 | Data | 0 | 33.169 | 31.042 | 179.347 | 7.63 | 167.962 | 2009.22 | 26.1 | 47.172 | 6.32 | 1.307 | 4.642 | 8155.84 | 2.025 | 97.7 | 78 | 1306 | 23.59 | 5301.3 | 2840.9 | 2739.3 | 4063.2 | 1184.5 | 0.68068 | 5.948
2024-12-09 | 13:13 | Data | 0 | 32.825 | 31.171 | 179.347 | 7.63 | 167.917 | 2012.83 | 26.11 | 47.172 | 6.31 | 1.312 | 4.647 | 8146.79 | 1.965 | 97.7 | 78 | 1309 | 23.5 | 5295.4 | 2824.2 | 2725.2 | 4049 | 1184.5 | 0.6804 | 5.96
2024-12-09 | 13:13 | Data | 0 | 32.953 | 30.766 | 179.483 | 7.63 | 167.962 | 2013.74 | 26.09 | 47.082 | 6.33 | 1.311 | 4.667 | 8137.75 | 2.073 | 97.7 | 78.1 | 1309 | 23.63 | 5289.5 | 2843.6 | 2739.4 | 4072.7 | 1184.5 | 0.68197 | 5.979
2024-12-09 | 13:13 | Data | 0 | 32.899 | 30.968 | 179.256 | 7.63 | 167.962 | 2012.83 | 26.08 | 47.082 | 6.32 | 1.314 | 4.683 | 8142.27 | 2.154 | 97.7 | 78.1 | 1308 | 23.54 | 5292.5 | 2850.8 | 2758.1 | 4089.1 | 1184.6 | 0.68086 | 5.998
2024-12-09 | 13:13 | Data | 0 | 32.865 | 30.772 | 179.347 | 7.63 | 168.007 | 2012.83 | 26.1 | 47.082 | 6.32 | 1.31 | 4.685 | 8137.75 | 1.965 | 97.7 | 78.1 | 1308 | 23.54 | 5289.5 | 2825.3 | 2772.5 | 4079.4 | 1184.6 | 0.67718 | 5.996
2024-12-09 | 13:13 | Data | 0 | 33.176 | 30.772 | 179.347 | 7.63 | 168.053 | 2012.83 | 26.09 | 47.443 | 6.32 | 1.318 | 4.673 | 8146.79 | 2.113 | 97.6 | 78 | 1308 | 23.68 | 5295.4 | 2848.4 | 2779 | 4097.8 | 1184.6 | 0.67847 | 5.991
2024-12-09 | 13:13 | Data | 0 | 32.98 | 30.712 | 179.302 | 7.63 | 167.962 | 2012.83 | 26.09 | 47.082 | 6.31 | 1.321 | 4.666 | 8137.75 | 2.046 | 97.7 | 77.9 | 1308 | 23.54 | 5289.5 | 2844.8 | 2791.7 | 4109.4 | 1184.6 | 0.67417 | 5.988
2024-12-09 | 13:13 | Data | 0 | 33.007 | 30.691 | 179.256 | 7.63 | 168.007 | 2014.64 | 26.09 | 47.443 | 6.32 | 1.313 | 4.666 | 8146.79 | 2.032 | 97.6 | 78 | 1308 | 23.68 | 5295.4 | 2830.9 | 2776.4 | 4086.1 | 1184.6 | 0.67519 | 5.98
2024-12-09 | 13:13 | Data | 0 | 32.669 | 30.853 | 179.302 | 7.63 | 167.917 | 2009.22 | 26.09 | 47.172 | 6.32 | 1.315 | 4.669 | 8128.7 | 2.066 | 97.7 | 78 | 1306 | 23.54 | 5283.7 | 2821.8 | 2775.5 | 4080 | 1184.6 | 0.67383 | 5.986
2024-12-09 | 13:13 | Data | 0 | 32.777 | 30.88 | 179.302 | 7.64 | 168.007 | 2013.74 | 26.08 | 47.262 | 6.32 | 1.324 | 4.676 | 8137.75 | 2.052 | 97.7 | 77.9 | 1309 | 23.59 | 5289.5 | 2824.6 | 2740.6 | 4060.2 | 1184.6 | 0.67673 | 6.001
2024-12-09 | 13:13 | Data | 0 | 32.507 | 30.698 | 179.166 | 7.63 | 167.917 | 2010.12 | 26.09 | 47.353 | 6.31 | 1.32 | 4.652 | 8142.27 | 1.971 | 97.6 | 77.9 | 1308 | 23.68 | 5292.5 | 2840.9 | 2744.8 | 4073.6 | 1184.6 | 0.68019 | 5.972
2024-12-09 | 13:13 | Data | 0 | 33.007 | 30.988 | 179.392 | 7.63 | 168.053 | 2015.55 | 26.09 | 47.262 | 6.31 | 1.314 | 4.641 | 8142.27 | 2.066 | 97.7 | 77.9 | 1310 | 23.63 | 5292.5 | 2854.9 | 2723 | 4065.5 | 1184.6 | 0.68327 | 5.955
2024-12-09 | 13:13 | Data | 0 | 32.831 | 30.867 | 179.302 | 7.63 | 168.053 | 2015.55 | 26.09 | 47.262 | 6.33 | 1.313 | 4.654 | 8133.23 | 1.87 | 97.7 | 78 | 1310 | 23.68 | 5286.6 | 2829 | 2734.2 | 4053 | 1184.6 | 0.68154 | 5.965
2024-12-09 | 13:13 | Data | 0 | 32.723 | 30.826 | 179.211 | 7.63 | 167.917 | 2014.64 | 26.1 | 47.262 | 6.32 | 1.323 | 4.652 | 8133.23 | 2.073 | 97.7 | 77.8 | 1311 | 23.68 | 5286.6 | 2833.6 | 2729.1 | 4055 | 1184.6 | 0.68158 | 5.975
2024-12-09 | 13:14 | Data | 0 | 32.791 | 30.793 | 179.211 | 7.63 | 168.007 | 2015.55 | 26.09 | 47.443 | 6.31 | 1.311 | 4.657 | 8155.84 | 1.904 | 97.7 | 78 | 1310 | 23.68 | 5301.3 | 2832.5 | 2739.1 | 4064 | 1184.6 | 0.68072 | 5.969
2024-12-09 | 13:14 | Data | 0 | 32.899 | 30.921 | 179.302 | 7.63 | 167.962 | 2014.64 | 26.09 | 47.353 | 6.32 | 1.305 | 4.646 | 8142.27 | 1.978 | 97.7 | 78.1 | 1310 | 23.68 | 5292.5 | 2843.7 | 2762.3 | 4085.6 | 1184.6 | 0.67925 | 5.952
2024-12-09 | 13:14 | Data | 0 | 32.723 | 30.982 | 179.302 | 7.63 | 168.007 | 2015.55 | 26.09 | 47.262 | 6.32 | 1.311 | 4.643 | 8128.7 | 1.897 | 97.7 | 78 | 1310 | 23.63 | 5283.7 | 2826.7 | 2740.6 | 4057.2 | 1184.6 | 0.67972 | 5.954
2024-12-09 | 13:14 | Data | 0 | 32.831 | 30.853 | 179.211 | 7.63 | 167.917 | 2015.55 | 26.1 | 47.353 | 6.32 | 1.321 | 4.647 | 8119.66 | 2.086 | 97.6 | 77.9 | 1311 | 23.68 | 5277.8 | 2837 | 2734.2 | 4059.8 | 1184.6 | 0.68258 | 5.969
2024-12-09 | 13:14 | Data | 0 | 32.723 | 30.678 | 179.256 | 7.63 | 167.962 | 2017.35 | 26.09 | 47.172 | 6.32 | 1.321 | 4.664 | 8128.7 | 2.073 | 97.7 | 77.9 | 1312 | 23.59 | 5283.7 | 2828.6 | 2764.8 | 4078 | 1184.6 | 0.67893 | 5.984
2024-12-09 | 13:14 | Data | 0 | 32.831 | 30.651 | 179.347 | 7.63 | 168.007 | 2017.35 | 26.08 | 47.353 | 6.32 | 1.324 | 4.632 | 8128.7 | 2.086 | 97.6 | 77.8 | 1312 | 23.72 | 5283.7 | 2845.8 | 2743.5 | 4075.5 | 1184.6 | 0.68002 | 5.955
2024-12-09 | 13:14 | Data | 0 | 32.723 | 30.482 | 179.302 | 7.63 | 167.962 | 2018.26 | 26.08 | 47.443 | 6.32 | 1.318 | 4.628 | 8137.75 | 2.174 | 97.7 | 77.8 | 1312 | 23.68 | 5289.5 | 2846.1 | 2762.7 | 4087.6 | 1184.6 | 0.67806 | 5.944
2024-12-09 | 13:14 | Data | 0 | 32.73 | 30.995 | 179.256 | 7.63 | 167.962 | 2018.26 | 26.09 | 46.991 | 6.32 | 1.319 | 4.668 | 8128.7 | 1.958 | 97.7 | 78 | 1312 | 23.54 | 5283.7 | 2823.9 | 2757.8 | 4071.9 | 1184.6 | 0.67644 | 5.987
2024-12-09 | 13:14 | Data | 0 | 32.757 | 30.968 | 179.302 | 7.63 | 168.007 | 2017.35 | 26.09 | 47.172 | 6.31 | 1.321 | 4.64 | 8133.23 | 1.762 | 97.7 | 77.8 | 1312 | 23.54 | 5286.6 | 2842 | 2736.1 | 4066.5 | 1184.6 | 0.68254 | 5.961
2024-12-09 | 13:14 | Data | 0 | 32.345 | 30.624 | 179.392 | 7.63 | 168.053 | 2017.35 | 26.09 | 47.082 | 6.32 | 1.315 | 4.648 | 8155.84 | 1.877 | 97.7 | 77.9 | 1312 | 23.5 | 5301.3 | 2848.8 | 2721.6 | 4061.5 | 1184.6 | 0.68511 | 5.962
2024-12-09 | 13:14 | Data | 0 | 32.75 | 30.705 | 179.302 | 7.63 | 167.962 | 2017.35 | 26.09 | 47.082 | 6.32 | 1.319 | 4.635 | 8142.27 | 1.965 | 97.7 | 77.9 | 1312 | 23.54 | 5292.5 | 2839.2 | 2726.4 | 4046.5 | 1184.6 | 0.68242 | 5.953
2024-12-09 | 13:14 | Data | 0 | 32.946 | 31.204 | 179.483 | 7.63 | 168.007 | 2018.26 | 26.09 | 47.082 | 6.32 | 1.322 | 4.626 | 8142.27 | 2.133 | 97.7 | 77.8 | 1312 | 23.54 | 5292.5 | 2829.5 | 2721.8 | 4052.2 | 1184.6 | 0.68215 | 5.95
2024-12-09 | 13:14 | Data | 0 | 32.94 | 30.907 | 179.392 | 7.63 | 168.007 | 2018.26 | 26.1 | 47.262 | 6.32 | 1.313 | 4.645 | 8128.7 | 2.019 | 97.7 | 78 | 1312 | 23.59 | 5283.7 | 2839.4 | 2734.4 | 4063.9 | 1184.6 | 0.68168 | 5.959
2024-12-09 | 13:14 | Data | 0 | 32.737 | 30.867 | 179.392 | 7.63 | 168.007 | 2018.26 | 26.09 | 47.353 | 6.32 | 1.31 | 4.671 | 8128.7 | 1.857 | 97.7 | 78.1 | 1312 | 23.68 | 5283.7 | 2840.1 | 2736 | 4063.9 | 1184.6 | 0.6812 | 5.98
2024-12-09 | 13:14 | Data | 0 | 32.723 | 30.826 | 179.166 | 7.63 | 168.007 | 2017.35 | 26.09 | 46.991 | 6.31 | 1.317 | 4.663 | 8119.66 | 2.073 | 97.7 | 78 | 1312 | 23.5 | 5277.8 | 2830.7 | 2740.2 | 4065.5 | 1184.6 | 0.68078 | 5.981
2024-12-09 | 13:14 | Data | 0 | 32.73 | 30.941 | 179.347 | 7.63 | 168.007 | 2018.26 | 26.09 | 47.082 | 6.32 | 1.307 | 4.65 | 8124.18 | 1.782 | 97.7 | 78.1 | 1312 | 23.59 | 5280.7 | 2836.6 | 2741 | 4063.6 | 1184.6 | 0.68159 | 5.957
2024-12-09 | 13:14 | Data | 0 | 32.75 | 30.853 | 179.256 | 7.63 | 167.962 | 2018.26 | 26.09 | 47.082 | 6.31 | 1.31 | 4.658 | 8124.18 | 1.904 | 97.7 | 78.1 | 1312 | 23.63 | 5280.7 | 2844.8 | 2775.3 | 4092.4 | 1184.6 | 0.67621 | 5.969
2024-12-09 | 13:14 | Data | 0 | 32.723 | 30.853 | 179.256 | 7.63 | 168.007 | 2018.26 | 26.08 | 47.172 | 6.32 | 1.319 | 4.673 | 8106.09 | 2.025 | 97.7 | 78 | 1312 | 23.59 | 5269 | 2844.2 | 2770.3 | 4089.6 | 1184.6 | 0.67794 | 5.992
2024-12-09 | 13:15 | Data | 0 | 32.723 | 30.651 | 179.256 | 7.63 | 168.007 | 2017.35 | 26.09 | 47.172 | 6.32 | 1.311 | 4.653 | 8115.14 | 2.073 | 97.7 | 78 | 1312 | 23.63 | 5274.8 | 2841.5 | 2782.8 | 4099.8 | 1184.6 | 0.67555 | 5.963
2024-12-09 | 13:15 | Data | 0 | 32.669 | 30.88 | 179.392 | 7.63 | 168.007 | 2019.16 | 26.09 | 47.262 | 6.32 | 1.31 | 4.647 | 8124.18 | 2.012 | 97.7 | 78 | 1312 | 23.68 | 5280.7 | 2857.6 | 2751 | 4096.9 | 1184.6 | 0.6824 | 5.959
2024-12-09 | 13:15 | Data | 0 | 32.953 | 30.982 | 179.256 | 7.63 | 168.007 | 2017.35 | 26.09 | 47.082 | 6.31 | 1.324 | 4.679 | 8128.7 | 1.87 | 97.7 | 78 | 1311 | 23.54 | 5283.7 | 2863.1 | 2735.3 | 4081.4 | 1184.6 | 0.6853 | 6.002
2024-12-09 | 13:15 | Data | 0 | 32.953 | 30.853 | 179.347 | 7.63 | 168.053 | 2018.26 | 26.1 | 47.082 | 6.31 | 1.312 | 4.689 | 8137.75 | 1.971 | 97.7 | 78.1 | 1311 | 23.54 | 5289.5 | 2847.4 | 2747.2 | 4082.9 | 1184.6 | 0.68111 | 6
2024-12-09 | 13:15 | Data | 0 | 32.555 | 30.968 | 179.347 | 7.63 | 168.053 | 2017.35 | 26.1 | 47.353 | 6.31 | 1.32 | 4.664 | 8124.18 | 1.647 | 97.7 | 77.9 | 1312 | 23.68 | 5280.7 | 2873.2 | 2747.2 | 4099.3 | 1184.6 | 0.68394 | 5.986
2024-12-09 | 13:15 | Data | 0 | 32.723 | 30.759 | 179.347 | 7.63 | 168.053 | 2020.07 | 26.09 | 47.172 | 6.32 | 1.32 | 4.665 | 8137.75 | 1.992 | 97.7 | 78 | 1314 | 23.59 | 5289.5 | 2847.1 | 2742.8 | 4079.2 | 1184.6 | 0.68226 | 5.985
2024-12-09 | 13:15 | Data | 0 | 32.696 | 30.766 | 179.211 | 7.63 | 167.962 | 2020.97 | 26.1 | 47.172 | 6.31 | 1.329 | 4.656 | 8137.75 | 2.066 | 97.7 | 77.8 | 1314 | 23.54 | 5289.5 | 2863.1 | 2742.3 | 4087.6 | 1184.6 | 0.68052 | 5.987
2024-12-09 | 13:15 | Data | 0 | 32.73 | 30.664 | 179.347 | 7.63 | 168.053 | 2020.07 | 26.09 | 47.172 | 6.32 | 1.319 | 4.654 | 8137.75 | 2.019 | 97.7 | 77.9 | 1314 | 23.59 | 5289.5 | 2847.9 | 2745.7 | 4079.8 | 1184.6 | 0.68056 | 5.971
2024-12-09 | 13:15 | Data | 0 | 33.007 | 30.772 | 179.347 | 7.63 | 168.053 | 2020.97 | 26.09 | 47.262 | 6.32 | 1.31 | 4.671 | 8133.23 | 1.863 | 97.7 | 78.1 | 1314 | 23.63 | 5286.6 | 2875.2 | 2757.2 | 4102.4 | 1184.7 | 0.68442 | 5.98
2024-12-09 | 13:15 | Data | 0 | 32.852 | 30.671 | 179.347 | 7.63 | 168.098 | 2020.07 | 26.09 | 47.082 | 6.32 | 1.312 | 4.664 | 8124.18 | 1.897 | 97.7 | 78 | 1313 | 23.54 | 5280.7 | 2888.4 | 2786.3 | 4139 | 1184.7 | 0.67749 | 5.977
2024-12-09 | 13:15 | Data | 0 | 32.953 | 30.88 | 179.302 | 7.63 | 168.007 | 2020.07 | 26.09 | 47.172 | 6.32 | 1.321 | 4.65 | 8137.75 | 1.958 | 97.7 | 77.9 | 1313 | 23.54 | 5289.5 | 2862.7 | 2771.9 | 4107.5 | 1184.7 | 0.67891 | 5.971
2024-12-09 | 13:15 | Data | 0 | 32.723 | 31.036 | 179.302 | 7.63 | 168.053 | 2020.97 | 26.09 | 47.172 | 6.32 | 1.324 | 4.653 | 8137.75 | 1.978 | 97.7 | 77.8 | 1314 | 23.54 | 5289.5 | 2876.4 | 2786.9 | 4127.9 | 1184.7 | 0.67854 | 5.977
2024-12-09 | 13:15 | Data | 0 | 33.054 | 31.204 | 179.392 | 7.63 | 168.007 | 2022.78 | 26.09 | 47.172 | 6.32 | 1.323 | 4.671 | 8142.27 | 1.877 | 97.7 | 77.9 | 1315 | 23.59 | 5292.5 | 2864.2 | 2755.5 | 4099.3 | 1184.7 | 0.68057 | 5.993
2024-12-09 | 13:15 | Data | 0 | 32.892 | 30.982 | 179.256 | 7.63 | 168.007 | 2023.68 | 26.1 | 47.172 | 6.32 | 1.335 | 4.677 | 8142.27 | 1.877 | 97.7 | 77.8 | 1316 | 23.59 | 5292.5 | 2857 | 2739.7 | 4082.7 | 1184.7 | 0.68221 | 6.012
2024-12-09 | 13:15 | Data | 0 | 32.744 | 30.658 | 179.256 | 7.63 | 168.007 | 2020.07 | 26.08 | 47.172 | 6.32 | 1.323 | 4.682 | 8155.84 | 2.019 | 97.7 | 78 | 1313 | 23.54 | 5301.3 | 2863.6 | 2737.2 | 4087 | 1184.7 | 0.68353 | 6.003
2024-12-09 | 13:15 | Data | 0 | 32.75 | 30.826 | 179.256 | 7.63 | 168.053 | 2020.07 | 26.1 | 46.991 | 6.31 | 1.313 | 4.665 | 8133.23 | 1.897 | 97.7 | 78 | 1314 | 23.5 | 5286.6 | 2874.2 | 2742.1 | 4094.9 | 1184.7 | 0.68499 | 5.978
2024-12-09 | 13:15 | Data | 0 | 33.183 | 30.907 | 179.392 | 7.63 | 168.053 | 2018.26 | 26.1 | 47.082 | 6.31 | 1.317 | 4.663 | 8137.75 | 1.89 | 97.7 | 78 | 1312 | 23.54 | 5289.5 | 2876.7 | 2731.7 | 4086.3 | 1184.7 | 0.68499 | 5.979
2024-12-09 | 13:15 | Data | 0 | 32.723 | 30.766 | 179.302 | 7.63 | 167.962 | 2017.35 | 26.1 | 47.262 | 6.32 | 1.322 | 4.664 | 8128.7 | 2.066 | 97.7 | 77.9 | 1312 | 23.68 | 5283.7 | 2860.4 | 2738.1 | 4085 | 1184.7 | 0.68297 | 5.985
2024-12-09 | 13:16 | Data | 0 | 33.115 | 30.779 | 179.347 | 7.63 | 168.143 | 2017.35 | 26.09 | 47.262 | 6.32 | 1.326 | 4.664 | 8124.18 | 2.221 | 97.7 | 77.9 | 1312 | 23.68 | 5280.7 | 2864.1 | 2753.3 | 4095.6 | 1184.7 | 0.68129 | 5.99
2024-12-09 | 13:16 | Data | 0 | 32.723 | 30.88 | 179.256 | 7.63 | 167.917 | 2019.16 | 26.09 | 47.172 | 6.32 | 1.313 | 4.647 | 8137.75 | 1.843 | 97.7 | 78 | 1312 | 23.59 | 5289.5 | 2869.3 | 2733.6 | 4091.2 | 1184.7 | 0.68488 | 5.961
2024-12-09 | 13:16 | Data | 0 | 32.777 | 30.88 | 179.302 | 7.63 | 168.007 | 2019.16 | 26.09 | 47.353 | 6.31 | 1.314 | 4.635 | 8146.79 | 1.857 | 97.7 | 77.9 | 1312 | 23.68 | 5295.4 | 2863.6 | 2768.7 | 4108.7 | 1184.7 | 0.68022 | 5.95
2024-12-09 | 13:16 | Data | 0 | 32.615 | 30.678 | 179.166 | 7.63 | 168.007 | 2017.35 | 26.1 | 47.353 | 6.31 | 1.313 | 4.658 | 8155.84 | 2.174 | 97.6 | 78 | 1312 | 23.72 | 5301.3 | 2865.5 | 2760.5 | 4102.7 | 1184.7 | 0.68093 | 5.971
2024-12-09 | 13:16 | Data | 0 | 32.723 | 30.88 | 179.256 | 7.63 | 167.962 | 2018.26 | 26.1 | 47.353 | 6.32 | 1.317 | 4.63 | 8142.27 | 1.965 | 97.7 | 77.9 | 1312 | 23.72 | 5292.5 | 2856.7 | 2737.1 | 4079.9 | 1184.7 | 0.68321 | 5.945
2024-12-09 | 13:16 | Data | 0 | 32.501 | 30.651 | 179.302 | 7.63 | 168.053 | 2020.97 | 26.09 | 47.262 | 6.31 | 1.317 | 4.653 | 8142.27 | 2.046 | 97.7 | 77.9 | 1314 | 23.63 | 5292.5 | 2868.7 | 2732.5 | 4082.3 | 1184.7 | 0.68516 | 5.969
2024-12-09 | 13:16 | Data | 0 | 32.669 | 30.658 | 179.256 | 7.63 | 168.053 | 2020.97 | 26.11 | 47.623 | 6.31 | 1.32 | 4.687 | 8115.14 | 2.019 | 97.6 | 78 | 1314 | 23.77 | 5274.8 | 2863.1 | 2749.2 | 4093.3 | 1184.7 | 0.68278 | 6.007
2024-12-09 | 13:16 | Data | 0 | 33.061 | 30.894 | 179.347 | 7.63 | 168.007 | 2061.64 | 26.08 | 47.353 | 6.32 | 1.312 | 4.656 | 8142.27 | 1.897 | 97.7 | 78 | 1340 | 23.68 | 5292.5 | 2846.4 | 2737.7 | 4073.7 | 1184.7 | 0.68237 | 5.969
2024-12-09 | 13:16 | Data | 0 | 32.926 | 31.103 | 179.392 | 7.63 | 168.007 | 2065.26 | 26.08 | 47.443 | 6.33 | 1.319 | 4.629 | 8142.27 | 1.958 | 97.7 | 77.8 | 1343 | 23.68 | 5292.5 | 2888.6 | 2742.4 | 4109.5 | 1184.7 | 0.6855 | 5.947
2024-12-09 | 13:16 | Data | 0 | 32.71 | 30.853 | 179.347 | 7.63 | 168.053 | 2065.26 | 26.08 | 47.353 | 6.32 | 1.327 | 4.659 | 8146.79 | 1.985 | 97.7 | 77.8 | 1342 | 23.72 | 5295.4 | 2793.9 | 2750.7 | 4041.1 | 1184.7 | 0.67514 | 5.986
2024-12-09 | 13:16 | Data | 0 | 32.75 | 30.766 | 179.347 | 7.63 | 168.007 | 2064.35 | 26.1 | 47.262 | 6.32 | 1.31 | 4.673 | 8155.84 | 1.863 | 97.7 | 78.1 | 1342 | 23.68 | 5301.3 | 2794.8 | 2742 | 4037 | 1184.7 | 0.67443 | 5.983
2024-12-09 | 13:16 | Data | 0 | 32.723 | 30.766 | 179.211 | 7.63 | 168.098 | 2018.26 | 26.09 | 47.443 | 6.31 | 1.312 | 4.671 | 8164.88 | 1.958 | 97.6 | 78.1 | 1311 | 23.72 | 5307.2 | 2798.3 | 2744.6 | 4040.2 | 1184.7 | 0.67566 | 5.984
2024-12-09 | 13:16 | Data | 0 | 32.831 | 30.88 | 179.392 | 7.63 | 168.007 | 2018.26 | 26.09 | 47.353 | 6.32 | 1.317 | 4.664 | 8169.4 | 2.066 | 97.6 | 78 | 1312 | 23.72 | 5310.1 | 2796 | 2756.3 | 4049.1 | 1184.7 | 0.6737 | 5.982
2024-12-09 | 13:16 | Data | 0 | 32.717 | 30.793 | 179.211 | 7.63 | 168.007 | 2018.26 | 26.08 | 47.443 | 6.32 | 1.315 | 4.682 | 8133.23 | 2.019 | 97.6 | 78.1 | 1312 | 23.72 | 5286.6 | 2802.4 | 2742.4 | 4040.1 | 1184.7 | 0.67765 | 5.997
2024-12-09 | 13:16 | Data | 0 | 32.757 | 30.651 | 179.302 | 7.63 | 168.007 | 2019.16 | 26.09 | 47.353 | 6.32 | 1.317 | 4.669 | 8128.7 | 2.073 | 97.7 | 78 | 1312 | 23.68 | 5283.7 | 2783 | 2769.3 | 4046.7 | 1184.7 | 0.67248 | 5.988
2024-12-09 | 13:16 | Data | 0 | 32.717 | 30.651 | 179.302 | 7.64 | 168.007 | 2016.45 | 26.06 | 47.714 | 6.32 | 1.321 | 4.666 | 8128.7 | 2.073 | 97.6 | 77.9 | 1311 | 23.81 | 5283.7 | 2793.7 | 2745.1 | 4030.4 | 1184.7 | 0.67499 | 5.987
2024-12-09 | 13:16 | Data | 0 | 32.507 | 30.651 | 179.256 | 7.63 | 167.962 | 2014.64 | 26.1 | 47.353 | 6.31 | 1.321 | 4.654 | 8119.66 | 1.85 | 97.6 | 77.9 | 1310 | 23.68 | 5277.8 | 2799.3 | 2726.8 | 4028.6 | 1184.7 | 0.67734 | 5.977
2024-12-09 | 13:16 | Data | 0 | 32.94 | 30.664 | 179.302 | 7.63 | 167.917 | 2018.26 | 26.08 | 47.262 | 6.32 | 1.319 | 4.653 | 8137.75 | 1.944 | 97.6 | 77.9 | 1312 | 23.68 | 5289.5 | 2790.8 | 2742 | 4032.3 | 1184.7 | 0.6762 | 5.973
2024-12-09 | 13:17 | Data | 0 | 32.838 | 30.766 | 179.256 | 7.64 | 168.007 | 2022.78 | 26.09 | 47.443 | 6.32 | 1.307 | 4.658 | 8160.36 | 1.857 | 97.7 | 78.1 | 1315 | 23.68 | 5304.2 | 2859.7 | 2753.8 | 4091.8 | 1184.7 | 0.68266 | 5.964
2024-12-09 | 13:17 | Data | 0 | 33.338 | 31.015 | 179.528 | 7.63 | 168.098 | 2018.26 | 26.08 | 47.172 | 6.32 | 1.319 | 4.632 | 8169.4 | 2.181 | 97.7 | 77.8 | 1312 | 23.63 | 5310.1 | 2856.2 | 2751.6 | 4084.7 | 1184.7 | 0.68335 | 5.952
2024-12-09 | 13:17 | Data | 0 | 32.521 | 30.813 | 179.166 | 7.63 | 167.872 | 2018.26 | 26.09 | 47.172 | 6.32 | 1.312 | 4.627 | 8155.84 | 1.884 | 97.7 | 77.9 | 1312 | 23.54 | 5301.3 | 2850 | 2746.9 | 4081.3 | 1184.7 | 0.68122 | 5.94
2024-12-09 | 13:17 | Data | 0 | 32.696 | 30.867 | 179.121 | 7.63 | 167.962 | 2017.35 | 26.09 | 47.082 | 6.32 | 1.309 | 4.676 | 8155.84 | 2.039 | 97.7 | 78.1 | 1312 | 23.59 | 5301.3 | 2860.2 | 2779.2 | 4105.6 | 1184.7 | 0.68031 | 5.984
2024-12-09 | 13:17 | Data | 0 | 33.054 | 30.934 | 179.483 | 7.63 | 168.053 | 2019.16 | 26.09 | 47.172 | 6.32 | 1.317 | 4.657 | 8155.84 | 1.992 | 97.7 | 78 | 1312 | 23.54 | 5301.3 | 2853.3 | 2759.1 | 4089.4 | 1184.7 | 0.68228 | 5.974
2024-12-09 | 13:17 | Data | 0 | 32.541 | 30.624 | 179.166 | 7.63 | 168.053 | 2020.97 | 26.09 | 47.082 | 6.31 | 1.32 | 4.645 | 8160.36 | 1.877 | 97.7 | 77.9 | 1313 | 23.54 | 5304.2 | 2844.8 | 2762.9 | 4088.3 | 1184.7 | 0.67784 | 5.965
2024-12-09 | 13:17 | Data | 0 | 32.609 | 30.637 | 179.166 | 7.63 | 167.827 | 2020.97 | 26.1 | 47.172 | 6.32 | 1.318 | 4.65 | 8169.4 | 1.917 | 97.7 | 77.9 | 1313 | 23.54 | 5310.1 | 2842.8 | 2738.4 | 4071.2 | 1184.7 | 0.67959 | 5.969
2024-12-09 | 13:17 | Data | 0 | 32.831 | 30.88 | 179.256 | 7.63 | 168.007 | 2020.97 | 26.07 | 46.991 | 6.32 | 1.325 | 4.673 | 8146.79 | 1.857 | 97.7 | 77.9 | 1314 | 23.59 | 5295.4 | 2843.3 | 2731.3 | 4066.9 | 1184.7 | 0.68224 | 5.998
2024-12-09 | 13:17 | Data | 0 | 32.946 | 30.88 | 179.302 | 7.63 | 168.007 | 2020.07 | 26.08 | 47.082 | 6.32 | 1.325 | 4.65 | 8155.84 | 1.958 | 97.7 | 77.8 | 1314 | 23.59 | 5301.3 | 2844.5 | 2753.4 | 4076.2 | 1184.7 | 0.67962 | 5.974
2024-12-09 | 13:17 | Data | 0 | 32.838 | 31.096 | 179.347 | 7.63 | 168.053 | 2013.74 | 26.08 | 47.082 | 6.32 | 1.32 | 4.643 | 8155.84 | 2.012 | 97.7 | 77.9 | 1309 | 23.5 | 5301.3 | 2858.6 | 2740.7 | 4081 | 1184.8 | 0.68338 | 5.962
2024-12-09 | 13:17 | Data | 0 | 32.669 | 30.853 | 179.302 | 7.63 | 167.917 | 2017.35 | 26.09 | 47.172 | 6.32 | 1.309 | 4.642 | 8142.27 | 1.944 | 97.7 | 78 | 1311 | 23.54 | 5292.5 | 2855.7 | 2726.6 | 4069.1 | 1184.8 | 0.68494 | 5.95
2024-12-09 | 13:17 | Data | 0 | 32.528 | 30.853 | 179.302 | 7.63 | 167.962 | 2018.26 | 26.08 | 47.082 | 6.32 | 1.321 | 4.645 | 8164.88 | 1.87 | 97.7 | 77.8 | 1311 | 23.54 | 5307.2 | 2849.8 | 2729.1 | 4073.6 | 1184.8 | 0.68161 | 5.968
2024-12-09 | 13:17 | Data | 0 | 32.582 | 30.651 | 179.166 | 7.63 | 167.872 | 2018.26 | 26.09 | 47.082 | 6.31 | 1.328 | 4.63 | 8169.4 | 2.039 | 97.7 | 77.7 | 1312 | 23.54 | 5310.1 | 2851.9 | 2728.9 | 4064.6 | 1184.8 | 0.68401 | 5.957
2024-12-09 | 13:17 | Data | 0 | 32.926 | 30.88 | 179.347 | 7.63 | 168.007 | 2018.26 | 26.08 | 47.082 | 6.31 | 1.311 | 4.643 | 8155.84 | 1.951 | 97.7 | 78 | 1312 | 23.54 | 5301.3 | 2848.1 | 2734.3 | 4067.8 | 1184.8 | 0.68351 | 5.955
2024-12-09 | 13:17 | Data | 0 | 32.44 | 30.644 | 179.121 | 7.63 | 167.872 | 2018.26 | 26.06 | 47.172 | 6.32 | 1.319 | 4.653 | 8169.4 | 2.025 | 97.7 | 77.9 | 1312 | 23.59 | 5310.1 | 2854.2 | 2759 | 4090.6 | 1184.8 | 0.68077 | 5.972
2024-12-09 | 13:17 | Data | 0 | 32.919 | 30.88 | 179.302 | 7.63 | 167.962 | 2017.35 | 26.08 | 47.172 | 6.32 | 1.32 | 4.656 | 8155.84 | 2.1 | 97.7 | 77.9 | 1311 | 23.54 | 5301.3 | 2858.9 | 2751.6 | 4089.5 | 1184.8 | 0.68154 | 5.976
2024-12-09 | 13:17 | Data | 0 | 32.892 | 30.766 | 179.256 | 7.63 | 167.962 | 2018.26 | 26.08 | 47.172 | 6.31 | 1.313 | 4.673 | 8173.92 | 1.863 | 97.7 | 78.1 | 1311 | 23.59 | 5313.1 | 2854.5 | 2753.8 | 4090.7 | 1184.8 | 0.67958 | 5.986
2024-12-09 | 13:18 | Data | 0 | 32.825 | 30.705 | 179.211 | 7.63 | 167.827 | 2017.35 | 26.07 | 47.082 | 6.32 | 1.312 | 4.65 | 8169.4 | 1.917 | 97.7 | 78 | 1312 | 23.59 | 5310.1 | 2849.3 | 2746.1 | 4081.2 | 1184.8 | 0.68273 | 5.963
2024-12-09 | 13:18 | Data | 0 | 32.879 | 30.705 | 179.166 | 7.64 | 167.827 | 2018.26 | 26.08 | 47.172 | 6.32 | 1.314 | 4.664 | 8155.84 | 2.059 | 97.7 | 78 | 1312 | 23.59 | 5301.3 | 2836.1 | 2746.3 | 4072.2 | 1184.8 | 0.6808 | 5.978
2024-12-09 | 13:18 | Data | 0 | 32.264 | 30.536 | 179.03 | 7.63 | 167.872 | 2016.45 | 26.08 | 47.172 | 6.32 | 1.319 | 4.653 | 8155.84 | 1.965 | 97.7 | 77.9 | 1311 | 23.54 | 5301.3 | 2840.2 | 2724.2 | 4056 | 1184.8 | 0.684 | 5.97
2024-12-09 | 13:18 | Data | 0 | 32.467 | 30.428 | 179.166 | 7.63 | 167.827 | 2015.55 | 26.09 | 47.172 | 6.32 | 1.32 | 4.636 | 8133.23 | 2.221 | 97.7 | 77.8 | 1310 | 23.54 | 5286.6 | 2834.2 | 2745.5 | 4067.1 | 1184.8 | 0.68056 | 5.959
2024-12-09 | 13:18 | Data | 0 | 32.919 | 30.664 | 179.166 | 7.63 | 167.872 | 2015.55 | 26.08 | 47.082 | 6.31 | 1.312 | 4.646 | 8160.36 | 2.113 | 97.7 | 78 | 1310 | 23.5 | 5304.2 | 2840.9 | 2781.5 | 4097.9 | 1184.8 | 0.67728 | 5.959
2024-12-09 | 13:18 | Data | 0 | 32.494 | 30.442 | 179.075 | 7.63 | 167.917 | 2012.83 | 26.09 | 47.172 | 6.31 | 1.314 | 4.658 | 8124.18 | 2.194 | 97.7 | 78 | 1309 | 23.54 | 5280.7 | 2838.6 | 2773.7 | 4091.7 | 1184.8 | 0.67664 | 5.976
2024-12-09 | 13:18 | Data | 0 | 32.723 | 30.678 | 179.211 | 7.63 | 167.962 | 2015.55 | 26.11 | 47.172 | 6.32 | 1.317 | 4.653 | 8128.7 | 2.019 | 97.7 | 78 | 1310 | 23.59 | 5283.7 | 2846.5 | 2810.2 | 4120.3 | 1184.8 | 0.6744 | 5.968
2024-12-09 | 13:18 | Data | 0 | 32.494 | 30.644 | 179.302 | 7.63 | 167.962 | 2016.45 | 26.1 | 47.082 | 6.32 | 1.31 | 4.639 | 8146.79 | 1.87 | 97.7 | 78 | 1310 | 23.59 | 5295.4 | 2823.5 | 2745.5 | 4068.3 | 1184.8 | 0.67969 | 5.948
2024-12-09 | 13:18 | Data | 0 | 32.946 | 30.88 | 179.211 | 7.63 | 167.917 | 2015.55 | 26.1 | 47.082 | 6.32 | 1.308 | 4.659 | 8101.57 | 1.958 | 97.7 | 78.1 | 1311 | 23.54 | 5266 | 2832.2 | 2780.7 | 4089.5 | 1184.8 | 0.67558 | 5.967
2024-12-09 | 13:18 | Data | 0 | 32.771 | 30.766 | 179.211 | 7.63 | 167.962 | 2015.55 | 26.1 | 47.082 | 6.31 | 1.32 | 4.648 | 8124.18 | 2.079 | 97.7 | 77.9 | 1310 | 23.54 | 5280.7 | 2838 | 2764.9 | 4085 | 1184.8 | 0.67743 | 5.969
2024-12-09 | 13:18 | Data | 0 | 32.332 | 30.651 | 179.211 | 7.63 | 167.917 | 2008.32 | 26.1 | 47.082 | 6.32 | 1.32 | 4.646 | 8128.7 | 1.803 | 97.7 | 77.9 | 1305 | 23.5 | 5283.7 | 2832.9 | 2767.5 | 4082.8 | 1184.8 | 0.67608 | 5.968
2024-12-09 | 13:18 | Data | 0 | 32.744 | 30.88 | 179.302 | 7.63 | 167.917 | 2015.55 | 26.1 | 47.082 | 6.32 | 1.327 | 4.657 | 8110.61 | 1.843 | 97.7 | 77.8 | 1310 | 23.54 | 5271.9 | 2839.9 | 2777.4 | 4097.9 | 1184.8 | 0.67763 | 5.983
2024-12-09 | 13:18 | Data | 0 | 32.892 | 30.867 | 179.166 | 7.63 | 167.917 | 2015.55 | 26.11 | 47.082 | 6.31 | 1.32 | 4.655 | 8128.7 | 1.944 | 97.7 | 77.9 | 1310 | 23.59 | 5283.7 | 2830.7 | 2744.7 | 4061.9 | 1184.8 | 0.68036 | 5.974
2024-12-09 | 13:18 | Data | 0 | 32.771 | 30.664 | 179.211 | 7.63 | 167.917 | 2015.55 | 26.11 | 47.172 | 6.31 | 1.311 | 4.65 | 8124.18 | 2.059 | 97.7 | 78 | 1310 | 23.54 | 5280.7 | 2850 | 2734.7 | 4070.2 | 1184.8 | 0.68271 | 5.961
2024-12-09 | 13:18 | Data | 0 | 32.737 | 30.867 | 179.256 | 7.63 | 167.962 | 2016.45 | 26.1 | 47.172 | 6.32 | 1.31 | 4.683 | 8137.75 | 1.904 | 97.7 | 78.1 | 1310 | 23.59 | 5289.5 | 2840.4 | 2734 | 4062.9 | 1184.8 | 0.68174 | 5.993
2024-12-09 | 13:18 | Data | 0 | 32.94 | 30.88 | 179.302 | 7.64 | 168.007 | 2018.26 | 26.11 | 47.082 | 6.32 | 1.325 | 4.656 | 8155.84 | 2.066 | 97.7 | 77.8 | 1312 | 23.54 | 5301.3 | 2843.6 | 2737.4 | 4067.7 | 1184.8 | 0.68275 | 5.981
2024-12-09 | 13:18 | Data | 0 | 32.588 | 30.543 | 179.166 | 7.63 | 167.962 | 2017.35 | 26.11 | 46.991 | 6.32 | 1.319 | 4.653 | 8137.75 | 1.965 | 97.7 | 77.9 | 1311 | 23.5 | 5289.5 | 2827.6 | 2752.4 | 4069.7 | 1184.8 | 0.67842 | 5.971
2024-12-09 | 13:18 | Data | 0 | 32.723 | 30.678 | 179.166 | 7.63 | 167.962 | 2015.55 | 26.1 | 47.082 | 6.32 | 1.314 | 4.654 | 8160.36 | 2.025 | 97.7 | 78 | 1311 | 23.54 | 5304.2 | 2845.2 | 2757.8 | 4080.8 | 1184.8 | 0.67972 | 5.969
2024-12-09 | 13:19 | Data | 0 | 32.777 | 30.671 | 179.256 | 7.63 | 168.007 | 2017.35 | 26.11 | 47.082 | 6.31 | 1.315 | 4.673 | 8137.75 | 2.046 | 97.7 | 78 | 1312 | 23.54 | 5289.5 | 2850.5 | 2767.1 | 4094.8 | 1184.8 | 0.67909 | 5.988
2024-12-09 | 13:19 | Data | 0 | 32.487 | 30.637 | 179.166 | 7.63 | 167.827 | 2018.26 | 26.1 | 47.082 | 6.32 | 1.314 | 4.66 | 8133.23 | 1.87 | 97.7 | 78 | 1312 | 23.54 | 5286.6 | 2836 | 2780.8 | 4085.5 | 1184.8 | 0.67686 | 5.974
2024-12-09 | 13:19 | Data | 0 | 32.831 | 30.691 | 179.302 | 7.63 | 167.962 | 2018.26 | 26.11 | 47.172 | 6.31 | 1.312 | 4.669 | 8146.79 | 1.789 | 97.7 | 78 | 1312 | 23.59 | 5295.4 | 2861.6 | 2771.2 | 4089.1 | 1184.8 | 0.67953 | 5.982
2024-12-09 | 13:19 | Data | 0 | 32.501 | 30.86 | 179.256 | 7.63 | 167.962 | 2018.26 | 26.11 | 47.082 | 6.31 | 1.313 | 4.659 | 8155.84 | 1.803 | 97.7 | 78 | 1312 | 23.54 | 5301.3 | 2842.9 | 2769.9 | 4089.2 | 1184.8 | 0.67806 | 5.972
2024-12-09 | 13:19 | Data | 0 | 32.298 | 30.597 | 179.075 | 7.63 | 167.872 | 2022.78 | 26.1 | 47.172 | 6.32 | 1.317 | 4.653 | 8155.84 | 2.005 | 97.7 | 78 | 1315 | 23.59 | 5301.3 | 2837.3 | 2776 | 4091.1 | 1184.8 | 0.67748 | 5.969
2024-12-09 | 13:19 | Data | 0 | 32.494 | 30.421 | 179.121 | 7.63 | 167.827 | 2020.97 | 26.11 | 47.082 | 6.33 | 1.327 | 4.632 | 8155.84 | 2.066 | 97.7 | 77.7 | 1313 | 23.54 | 5301.3 | 2871.6 | 2743.3 | 4090.1 | 1184.8 | 0.68657 | 5.959
2024-12-09 | 13:19 | Data | 0 | 32.507 | 30.766 | 179.211 | 7.63 | 167.962 | 2020.97 | 26.11 | 46.991 | 6.32 | 1.315 | 4.651 | 8155.84 | 2.046 | 97.7 | 78 | 1314 | 23.68 | 5301.3 | 2839.7 | 2739.7 | 4067.1 | 1184.8 | 0.68063 | 5.964
2024-12-09 | 13:19 | Data | 0 | 32.771 | 30.901 | 179.166 | 7.63 | 167.917 | 2022.78 | 26.1 | 47.172 | 6.33 | 1.317 | 4.641 | 8155.84 | 2.228 | 97.7 | 77.9 | 1315 | 23.63 | 5301.3 | 2856.3 | 2767.3 | 4097.1 | 1184.8 | 0.6802 | 5.959
2024-12-09 | 13:19 | Data | 0 | 32.514 | 30.826 | 179.302 | 7.63 | 167.962 | 2020.97 | 26.09 | 47.082 | 6.31 | 1.329 | 4.598 | 8137.75 | 1.931 | 97.7 | 77.6 | 1314 | 23.59 | 5289.5 | 2840.2 | 2768.2 | 4088.7 | 1184.8 | 0.67759 | 5.926
2024-12-09 | 13:19 | Data | 0 | 32.676 | 30.597 | 179.166 | 7.63 | 167.962 | 2020.97 | 26.1 | 47.082 | 6.31 | 1.314 | 4.624 | 8133.23 | 1.971 | 97.7 | 77.9 | 1314 | 23.59 | 5286.6 | 2851 | 2745.4 | 4081.5 | 1184.8 | 0.68112 | 5.937
2024-12-09 | 13:19 | Data | 0 | 32.723 | 30.874 | 179.347 | 7.63 | 167.962 | 2020.97 | 26.11 | 46.991 | 6.31 | 1.306 | 4.667 | 8155.84 | 1.877 | 97.7 | 78.1 | 1314 | 23.5 | 5301.3 | 2854 | 2746.5 | 4079.3 | 1184.8 | 0.68342 | 5.976
2024-12-09 | 13:19 | Data | 0 | 32.94 | 30.678 | 179.256 | 7.63 | 167.917 | 2020.07 | 26.11 | 47.172 | 6.31 | 1.315 | 4.66 | 8137.75 | 1.857 | 97.7 | 78 | 1313 | 23.54 | 5289.5 | 2838.9 | 2749.3 | 4077.9 | 1184.8 | 0.68158 | 5.975
2024-12-09 | 13:19 | Data | 0 | 32.723 | 30.658 | 179.211 | 7.63 | 167.917 | 2022.78 | 26.1 | 47.082 | 6.31 | 1.33 | 4.654 | 8164.88 | 2.066 | 97.7 | 77.8 | 1315 | 23.63 | 5307.2 | 2847.7 | 2752.2 | 4083.5 | 1184.9 | 0.68004 | 5.984
2024-12-09 | 13:19 | Data | 0 | 32.838 | 30.995 | 179.347 | 7.63 | 168.007 | 2024.58 | 26.1 | 47.082 | 6.32 | 1.314 | 4.653 | 8178.45 | 2.039 | 97.7 | 78 | 1315 | 23.54 | 5316 | 2843 | 2752.9 | 4075.9 | 1184.9 | 0.68057 | 5.967
2024-12-09 | 13:19 | Data | 0 | 32.521 | 30.624 | 179.211 | 7.63 | 167.872 | 2023.68 | 26.11 | 47.172 | 6.31 | 1.315 | 4.664 | 8164.88 | 1.877 | 97.7 | 78 | 1315 | 23.59 | 5307.2 | 2857.4 | 2769.5 | 4098.2 | 1184.9 | 0.68051 | 5.979
2024-12-09 | 13:19 | Data | 0 | 32.71 | 30.651 | 179.166 | 7.63 | 167.827 | 2023.68 | 26.11 | 47.172 | 6.32 | 1.315 | 4.657 | 8173.92 | 2.073 | 97.7 | 78 | 1315 | 23.5 | 5313.1 | 2830.1 | 2769.6 | 4079.4 | 1184.9 | 0.67751 | 5.971
2024-12-09 | 13:19 | Data | 0 | 32.71 | 30.651 | 179.211 | 7.63 | 167.872 | 2021.87 | 26.1 | 47.082 | 6.32 | 1.297 | 4.662 | 8137.75 | 2.066 | 97.7 | 78.2 | 1314 | 23.59 | 5289.5 | 2842.9 | 2773.2 | 4085.5 | 1184.9 | 0.67496 | 5.959
2024-12-09 | 13:19 | Data | 0 | 32.953 | 30.88 | 179.347 | 7.63 | 168.007 | 2020.07 | 26.11 | 46.991 | 6.31 | 1.318 | 4.657 | 8142.27 | 1.958 | 97.7 | 78 | 1314 | 23.54 | 5292.5 | 2827.1 | 2763.9 | 4076 | 1184.9 | 0.6767 | 5.976
2024-12-09 | 13:20 | Data | 0 | 32.879 | 30.874 | 179.166 | 7.63 | 167.917 | 2001.08 | 26.11 | 47.082 | 6.32 | 1.319 | 4.653 | 8133.23 | 2.066 | 97.6 | 77.9 | 1293 | 23.54 | 5286.6 | 2834.5 | 2740 | 4064.8 | 1184.9 | 0.68039 | 5.971
2024-12-09 | 13:20 | Data | 0 | 33.048 | 30.88 | 179.256 | 7.63 | 168.007 | 1926.97 | 26.1 | 47.082 | 6.32 | 1.326 | 4.635 | 8128.7 | 1.978 | 97.6 | 77.8 | 1257 | 23.59 | 5283.7 | 2851.7 | 2731 | 4067.4 | 1184.9 | 0.68461 | 5.96
2024-12-09 | 13:20 | Data | 0 | 32.764 | 30.448 | 179.166 | 7.63 | 167.962 | 2022.78 | 26.11 | 47.262 | 6.32 | 1.321 | 4.639 | 8133.23 | 2.113 | 97.7 | 77.8 | 1314 | 23.54 | 5286.6 | 2846.7 | 2751.8 | 4079.5 | 1184.9 | 0.6826 | 5.96
2024-12-09 | 13:20 | Data | 0 | 32.494 | 30.59 | 179.166 | 7.63 | 167.872 | 2017.35 | 26.11 | 47.082 | 6.32 | 1.324 | 4.648 | 8124.18 | 1.958 | 97.7 | 77.8 | 1312 | 23.59 | 5280.7 | 2842.6 | 2748.8 | 4077.2 | 1184.9 | 0.68149 | 5.972
2024-12-09 | 13:20 | Data | 0 | 32.723 | 30.658 | 179.121 | 7.63 | 167.917 | 2018.26 | 26.1 | 47.082 | 6.32 | 1.317 | 4.64 | 8128.7 | 2.052 | 97.7 | 77.9 | 1312 | 23.59 | 5283.7 | 2834.7 | 2749.7 | 4071.5 | 1184.9 | 0.68032 | 5.956
2024-12-09 | 13:20 | Data | 0 | 32.723 | 30.887 | 179.211 | 7.63 | 167.962 | 2018.26 | 26.11 | 47.082 | 6.32 | 1.302 | 4.655 | 8128.7 | 1.83 | 97.7 | 78.1 | 1312 | 23.54 | 5283.7 | 2859.5 | 2769.5 | 4096.9 | 1184.9 | 0.68131 | 5.959
2024-12-09 | 13:20 | Data | 0 | 32.777 | 30.658 | 179.211 | 7.63 | 168.007 | 2017.35 | 26.11 | 47.172 | 6.32 | 1.305 | 4.67 | 8124.18 | 2.073 | 97.7 | 78.1 | 1311 | 23.54 | 5280.7 | 2844.9 | 2732.9 | 4066.2 | 1184.9 | 0.6822 | 5.976
2024-12-09 | 13:20 | Data | 0 | 32.723 | 30.651 | 179.211 | 7.63 | 167.962 | 2025.49 | 26.1 | 47.172 | 6.32 | 1.319 | 4.633 | 8119.66 | 1.87 | 97.7 | 77.9 | 1317 | 23.59 | 5277.8 | 2825.6 | 2751.6 | 4061.8 | 1184.9 | 0.68 | 5.951
2024-12-09 | 13:20 | Data | 0 | 33 | 30.766 | 179.256 | 7.63 | 168.007 | 2021.87 | 26.1 | 47.172 | 6.32 | 1.317 | 4.639 | 8128.7 | 1.911 | 97.7 | 77.9 | 1314 | 23.59 | 5283.7 | 2835.7 | 2752.6 | 4066.7 | 1184.9 | 0.67639 | 5.956
2024-12-09 | 13:20 | Data | 0 | 32.494 | 30.624 | 179.121 | 7.64 | 167.917 | 2020.97 | 26.1 | 47.082 | 6.32 | 1.314 | 4.642 | 8133.23 | 2.046 | 97.7 | 77.9 | 1314 | 23.59 | 5286.6 | 2844.6 | 2784.4 | 4100.9 | 1184.9 | 0.67709 | 5.957
2024-12-09 | 13:20 | Data | 0 | 32.94 | 30.88 | 179.347 | 7.63 | 167.962 | 2017.35 | 26.11 | 46.811 | 6.32 | 1.312 | 4.658 | 8155.84 | 2.066 | 97.7 | 78 | 1311 | 23.41 | 5301.3 | 2829.3 | 2769.3 | 4080 | 1184.9 | 0.67709 | 5.97
2024-12-09 | 13:20 | Data | 0 | 32.899 | 31.049 | 179.347 | 7.63 | 167.962 | 2018.26 | 26.11 | 47.082 | 6.32 | 1.311 | 4.68 | 8182.97 | 2.059 | 97.7 | 78.1 | 1312 | 23.54 | 5318.9 | 2842.3 | 2743.2 | 4072.9 | 1184.9 | 0.68061 | 5.991
2024-12-09 | 13:20 | Data | 0 | 32.723 | 30.874 | 179.211 | 7.63 | 167.917 | 2018.26 | 26.12 | 46.991 | 6.31 | 1.308 | 4.67 | 8178.45 | 1.87 | 97.7 | 78.1 | 1312 | 23.41 | 5316 | 2834.7 | 2738.8 | 4060.7 | 1184.9 | 0.68034 | 5.977
2024-12-09 | 13:20 | Data | 0 | 32.723 | 30.651 | 179.211 | 7.64 | 167.962 | 2020.97 | 26.11 | 47.082 | 6.32 | 1.305 | 4.65 | 8155.84 | 1.87 | 97.7 | 78.1 | 1314 | 23.54 | 5301.3 | 2824.7 | 2778.7 | 4083.5 | 1184.9 | 0.67508 | 5.954
2024-12-09 | 13:20 | Data | 0 | 32.953 | 30.88 | 179.392 | 7.63 | 168.053 | 2020.07 | 26.1 | 47.172 | 6.32 | 1.309 | 4.65 | 8128.7 | 1.958 | 97.7 | 78 | 1314 | 23.54 | 5283.7 | 2834.2 | 2750.7 | 4070.6 | 1184.9 | 0.67791 | 5.959
2024-12-09 | 13:20 | Data | 0 | 33.034 | 30.766 | 179.302 | 7.63 | 168.098 | 2020.07 | 26.11 | 47.262 | 6.32 | 1.317 | 4.635 | 8115.14 | 2.093 | 97.7 | 77.9 | 1313 | 23.59 | 5274.8 | 2831.4 | 2733.5 | 4057.1 | 1184.9 | 0.68116 | 5.953
2024-12-09 | 13:20 | Data | 0 | 32.703 | 30.658 | 179.347 | 7.63 | 168.098 | 2020.97 | 26.11 | 47.082 | 6.33 | 1.31 | 4.679 | 8119.66 | 1.85 | 97.7 | 78.1 | 1314 | 23.54 | 5277.8 | 2830.2 | 2730.1 | 4058.1 | 1184.9 | 0.67976 | 5.988
2024-12-09 | 13:20 | Data | 0 | 32.609 | 31.076 | 179.302 | 7.63 | 168.007 | 2020.07 | 26.11 | 47.172 | 6.32 | 1.311 | 4.668 | 8128.7 | 1.843 | 97.7 | 78.1 | 1313 | 23.59 | 5283.7 | 2863.3 | 2750.5 | 4090.3 | 1184.9 | 0.68264 | 5.979
2024-12-09 | 13:21 | Data | 0 | 32.717 | 30.651 | 179.256 | 7.63 | 167.962 | 2020.07 | 26.12 | 47.172 | 6.32 | 1.324 | 4.667 | 8133.23 | 2.073 | 97.7 | 77.9 | 1313 | 23.54 | 5286.6 | 2826.7 | 2742.9 | 4059.9 | 1184.9 | 0.67855 | 5.991
2024-12-09 | 13:21 | Data | 0 | 32.723 | 30.853 | 179.211 | 7.63 | 167.872 | 2020.07 | 26.11 | 47.082 | 6.32 | 1.321 | 4.676 | 8128.7 | 1.958 | 97.7 | 78 | 1312 | 23.54 | 5283.7 | 2835.4 | 2724.5 | 4051.5 | 1184.9 | 0.68551 | 5.998
2024-12-09 | 13:21 | Data | 0 | 32.967 | 30.712 | 179.392 | 7.63 | 168.007 | 2021.87 | 26.11 | 47.172 | 6.32 | 1.319 | 4.671 | 8115.14 | 2.039 | 97.7 | 78 | 1314 | 23.59 | 5274.8 | 2830.6 | 2725.1 | 4046.7 | 1184.9 | 0.68209 | 5.99
2024-12-09 | 13:21 | Data | 0 | 32.973 | 30.57 | 179.302 | 7.63 | 167.962 | 2021.87 | 26.11 | 47.172 | 6.31 | 1.315 | 4.648 | 8128.7 | 1.917 | 97.7 | 78 | 1314 | 23.54 | 5283.7 | 2833.6 | 2728.3 | 4055.1 | 1184.9 | 0.68112 | 5.964
2024-12-09 | 13:21 | Data | 0 | 33.149 | 30.698 | 179.392 | 7.63 | 168.053 | 2020.97 | 26.1 | 47.082 | 6.32 | 1.306 | 4.654 | 8137.75 | 2.127 | 97.7 | 78.1 | 1314 | 23.54 | 5289.5 | 2836.7 | 2733.7 | 4058.6 | 1184.9 | 0.68085 | 5.96
2024-12-09 | 13:21 | Data | 0 | 32.892 | 30.874 | 179.256 | 7.63 | 167.962 | 2020.97 | 26.11 | 47.082 | 6.32 | 1.31 | 4.675 | 8133.23 | 2.073 | 97.7 | 78.1 | 1314 | 23.59 | 5286.6 | 2836.2 | 2754.2 | 4077.7 | 1184.9 | 0.68274 | 5.986
2024-12-09 | 13:21 | Data | 0 | 32.723 | 30.651 | 179.121 | 7.63 | 167.917 | 2020.97 | 26.11 | 47.082 | 6.32 | 1.313 | 4.668 | 8155.84 | 1.958 | 97.7 | 78 | 1314 | 23.59 | 5301.3 | 2842.2 | 2772.6 | 4090.9 | 1184.9 | 0.67916 | 5.978
2024-12-09 | 13:21 | Data | 0 | 32.865 | 30.664 | 179.347 | 7.63 | 168.053 | 2020.07 | 26.11 | 47.172 | 6.32 | 1.312 | 4.646 | 8133.23 | 1.857 | 97.7 | 78 | 1314 | 23.59 | 5286.6 | 2854.9 | 2738.9 | 4078.8 | 1184.9 | 0.68237 | 5.958
2024-12-09 | 13:21 | Data | 0 | 32.73 | 30.766 | 179.256 | 7.63 | 168.053 | 2020.97 | 26.1 | 47.082 | 6.32 | 1.311 | 4.645 | 8142.27 | 2.059 | 97.7 | 78 | 1314 | 23.59 | 5292.5 | 2847.9 | 2758.4 | 4085.1 | 1184.9 | 0.68003 | 5.954
2024-12-09 | 13:21 | Data | 0 | 32.717 | 30.651 | 179.302 | 7.63 | 167.962 | 2018.26 | 26.1 | 47.082 | 6.32 | 1.307 | 4.67 | 8133.23 | 2.059 | 97.7 | 78.1 | 1311 | 23.54 | 5286.6 | 2850 | 2744.4 | 4080.7 | 1184.9 | 0.68227 | 5.976
2024-12-09 | 13:21 | Data | 0 | 32.737 | 30.766 | 179.347 | 7.63 | 168.007 | 2018.26 | 26.1 | 47.172 | 6.32 | 1.31 | 4.676 | 8449.78 | 1.857 | 97.7 | 78.1 | 1312 | 23.63 | 5492.4 | 2846.3 | 2748 | 4076 | 1184.9 | 0.68181 | 5.987
2024-12-09 | 13:21 | Data | 0 | 32.669 | 30.651 | 179.256 | 7.63 | 167.962 | 2017.35 | 26.1 | 47.172 | 6.31 | 1.313 | 4.679 | 8567.36 | 2.059 | 97.7 | 78.1 | 1312 | 23.59 | 5568.8 | 2843.6 | 2739.2 | 4073.2 | 1184.9 | 0.68066 | 5.992
2024-12-09 | 13:21 | Data | 0 | 32.723 | 30.658 | 179.347 | 7.64 | 167.917 | 2020.07 | 26.11 | 46.721 | 6.32 | 1.315 | 4.681 | 8277.94 | 2.059 | 97.7 | 78.1 | 1312 | 23.36 | 5380.7 | 2835.3 | 2732.3 | 4061.2 | 1184.9 | 0.6818 | 5.996
2024-12-09 | 13:21 | Data | 0 | 32.595 | 30.813 | 179.166 | 7.63 | 167.917 | 2016.45 | 26.11 | 47.082 | 6.32 | 1.319 | 4.649 | 8128.7 | 2.039 | 97.7 | 77.9 | 1311 | 23.59 | 5283.7 | 2843.4 | 2730.3 | 4068 | 1185 | 0.68394 | 5.968
2024-12-09 | 13:21 | Data | 0 | 32.926 | 30.907 | 179.528 | 7.63 | 168.098 | 2012.83 | 26.11 | 47.082 | 6.32 | 1.317 | 4.651 | 8115.14 | 1.965 | 97.7 | 77.9 | 1310 | 23.59 | 5274.8 | 2831.5 | 2746.6 | 4065.9 | 1185 | 0.68022 | 5.968
2024-12-09 | 13:21 | Data | 0 | 32.561 | 30.651 | 179.256 | 7.63 | 168.053 | 2019.16 | 26.11 | 47.082 | 6.32 | 1.313 | 4.657 | 8119.66 | 1.965 | 97.7 | 78 | 1312 | 23.54 | 5277.8 | 2829.7 | 2738.5 | 4060.7 | 1185 | 0.67901 | 5.969
2024-12-09 | 13:21 | Data | 0 | 32.723 | 30.448 | 179.166 | 7.63 | 167.962 | 2018.26 | 26.1 | 47.172 | 6.32 | 1.312 | 4.659 | 8110.61 | 2.12 | 97.7 | 78 | 1311 | 23.63 | 5271.9 | 2836.9 | 2748.2 | 4072.3 | 1185 | 0.67988 | 5.972
2024-12-09 | 13:22 | Data | 0 | 32.71 | 30.678 | 179.211 | 7.63 | 168.053 | 2015.55 | 26.11 | 47.082 | 6.32 | 1.326 | 4.666 | 8110.61 | 2.039 | 97.7 | 77.9 | 1310 | 23.54 | 5271.9 | 2832.9 | 2760 | 4075.6 | 1185 | 0.67788 | 5.99
2024-12-09 | 13:22 | Data | 0 | 33.149 | 30.914 | 179.256 | 7.63 | 168.098 | 2015.55 | 26.11 | 46.991 | 6.32 | 1.319 | 4.662 | 8124.18 | 2.147 | 97.7 | 77.9 | 1310 | 23.54 | 5280.7 | 2829 | 2742 | 4063 | 1185 | 0.67853 | 5.981
2024-12-09 | 13:22 | Data | 0 | 32.555 | 30.82 | 179.166 | 7.63 | 168.053 | 2015.55 | 26.11 | 47.082 | 6.31 | 1.329 | 4.684 | 8110.61 | 2.052 | 97.7 | 77.9 | 1310 | 23.63 | 5271.9 | 2829.8 | 2741.4 | 4056.5 | 1185 | 0.68064 | 6.013
2024-12-09 | 13:22 | Data | 0 | 33.068 | 30.685 | 179.347 | 7.63 | 168.053 | 2015.55 | 26.11 | 47.172 | 6.31 | 1.325 | 4.648 | 8106.09 | 2.181 | 97.7 | 77.8 | 1310 | 23.63 | 5269 | 2843 | 2733.7 | 4066.1 | 1185 | 0.68188 | 5.972
2024-12-09 | 13:22 | Data | 0 | 32.811 | 30.88 | 179.347 | 7.63 | 168.053 | 2015.55 | 26.1 | 47.172 | 6.32 | 1.315 | 4.622 | 8110.61 | 2.005 | 97.7 | 77.8 | 1310 | 23.59 | 5271.9 | 2832.1 | 2730.2 | 4054.7 | 1185 | 0.68156 | 5.936
2024-12-09 | 13:22 | Data | 0 | 32.615 | 30.826 | 179.347 | 7.63 | 168.053 | 2016.45 | 26.1 | 47.082 | 6.32 | 1.315 | 4.654 | 8106.09 | 1.944 | 97.7 | 78 | 1310 | 23.54 | 5269 | 2856.4 | 2727.3 | 4070.9 | 1185 | 0.68291 | 5.969
2024-12-09 | 13:22 | Data | 0 | 32.777 | 30.779 | 179.211 | 7.63 | 167.962 | 2010.12 | 26.1 | 47.443 | 6.31 | 1.313 | 4.657 | 8106.09 | 2.059 | 97.6 | 78 | 1307 | 23.72 | 5269 | 2827.9 | 2747 | 4066.7 | 1185 | 0.68077 | 5.971
2024-12-09 | 13:22 | Data | 0 | 33.054 | 30.658 | 179.528 | 7.63 | 168.053 | 2014.64 | 26.11 | 47.082 | 6.32 | 1.309 | 4.646 | 8097.05 | 1.985 | 97.7 | 78 | 1310 | 23.59 | 5263.1 | 2840 | 2735 | 4064.8 | 1185 | 0.68163 | 5.956
2024-12-09 | 13:22 | Data | 0 | 32.717 | 31.042 | 179.302 | 7.63 | 168.007 | 2015.55 | 26.1 | 46.991 | 6.32 | 1.31 | 4.642 | 8110.61 | 1.944 | 97.7 | 78 | 1310 | 23.5 | 5271.9 | 2827.2 | 2730 | 4056.3 | 1185 | 0.68069 | 5.952
2024-12-09 | 13:22 | Data | 0 | 32.811 | 30.678 | 179.256 | 7.63 | 168.053 | 2015.55 | 26.11 | 47.082 | 6.32 | 1.328 | 4.625 | 8115.14 | 2.032 | 97.7 | 77.7 | 1310 | 23.54 | 5274.8 | 2823 | 2731.1 | 4060.5 | 1185 | 0.68187 | 5.952
2024-12-09 | 13:22 | Data | 0 | 32.953 | 30.766 | 179.347 | 7.63 | 168.007 | 2015.55 | 26.11 | 47.082 | 6.33 | 1.327 | 4.652 | 8110.61 | 1.897 | 97.7 | 77.8 | 1310 | 23.59 | 5271.9 | 2825.1 | 2720 | 4046.6 | 1185 | 0.68207 | 5.979
2024-12-09 | 13:22 | Data | 0 | 33.156 | 30.685 | 179.392 | 7.63 | 168.098 | 2014.64 | 26.1 | 47.082 | 6.31 | 1.321 | 4.649 | 8110.61 | 2.073 | 97.7 | 77.9 | 1310 | 23.54 | 5271.9 | 2845 | 2731.2 | 4065.6 | 1185 | 0.68423 | 5.969
2024-12-09 | 13:22 | Data | 0 | 32.811 | 30.874 | 179.392 | 7.63 | 168.053 | 2015.55 | 26.1 | 47.172 | 6.32 | 1.325 | 4.645 | 8137.75 | 2.16 | 97.7 | 77.8 | 1311 | 23.59 | 5289.5 | 2844.6 | 2729.7 | 4061.5 | 1185 | 0.68409 | 5.968
2024-12-09 | 13:22 | Data | 0 | 32.514 | 30.651 | 179.302 | 7.63 | 168.143 | 2016.45 | 26.1 | 47.082 | 6.32 | 1.325 | 4.654 | 8137.75 | 1.857 | 97.7 | 77.8 | 1311 | 23.5 | 5289.5 | 2833.7 | 2740.1 | 4065.4 | 1185 | 0.67808 | 5.979
2024-12-09 | 13:22 | Data | 0 | 32.946 | 30.88 | 179.347 | 7.63 | 168.053 | 2015.55 | 26.1 | 47.082 | 6.32 | 1.323 | 4.673 | 8146.79 | 1.87 | 97.7 | 77.9 | 1310 | 23.54 | 5295.4 | 2835.8 | 2733.4 | 4064 | 1185 | 0.68142 | 5.997
2024-12-09 | 13:22 | Data | 0 | 32.723 | 31.13 | 179.256 | 7.63 | 168.053 | 2015.55 | 26.11 | 47.172 | 6.32 | 1.322 | 4.657 | 8160.36 | 1.911 | 97.7 | 77.9 | 1310 | 23.59 | 5304.2 | 2830.4 | 2751.2 | 4069.2 | 1185 | 0.67976 | 5.98
2024-12-09 | 13:22 | Data | 0 | 32.906 | 30.88 | 179.347 | 7.63 | 168.053 | 2012.83 | 26.1 | 47.082 | 6.32 | 1.32 | 4.668 | 8124.18 | 1.897 | 97.7 | 78 | 1309 | 23.54 | 5280.7 | 2847.4 | 2756.5 | 4085.8 | 1185 | 0.68 | 5.988
2024-12-09 | 13:22 | Data | 0 | 32.777 | 30.88 | 179.347 | 7.63 | 168.007 | 2012.83 | 26.11 | 47.172 | 6.33 | 1.32 | 4.673 | 8124.18 | 1.985 | 97.7 | 78 | 1308 | 23.59 | 5280.7 | 2839.7 | 2738.7 | 4068 | 1185 | 0.68051 | 5.992
2024-12-09 | 13:23 | Data | 0 | 32.744 | 30.853 | 179.392 | 7.64 | 168.143 | 2012.83 | 26.12 | 47.082 | 6.31 | 1.32 | 4.658 | 8128.7 | 1.904 | 97.7 | 77.9 | 1308 | 23.54 | 5283.7 | 2835.7 | 2739.7 | 4064.1 | 1185 | 0.6823 | 5.977
2024-12-09 | 13:23 | Data | 0 | 32.98 | 30.887 | 179.347 | 7.63 | 168.053 | 2015.55 | 26.11 | 47.262 | 6.32 | 1.325 | 4.651 | 8142.27 | 1.938 | 97.7 | 77.8 | 1311 | 23.54 | 5292.5 | 2853.9 | 2744.4 | 4084.8 | 1185 | 0.68086 | 5.977
2024-12-09 | 13:23 | Data | 0 | 32.71 | 30.968 | 179.392 | 7.63 | 168.053 | 2012.83 | 26.1 | 47.082 | 6.32 | 1.317 | 4.632 | 8155.84 | 2.154 | 97.7 | 77.9 | 1308 | 23.54 | 5301.3 | 2837.3 | 2736.7 | 4064.4 | 1185 | 0.68118 | 5.948
2024-12-09 | 13:23 | Data | 0 | 32.723 | 30.88 | 179.347 | 7.63 | 168.098 | 2012.83 | 26.09 | 47.082 | 6.32 | 1.311 | 4.626 | 8124.18 | 2.046 | 97.7 | 77.9 | 1308 | 23.59 | 5280.7 | 2844.9 | 2736.9 | 4070.5 | 1185 | 0.68135 | 5.938
2024-12-09 | 13:23 | Data | 0 | 32.838 | 31.252 | 179.392 | 7.63 | 168.007 | 2009.22 | 26.11 | 47.082 | 6.32 | 1.312 | 4.638 | 8142.27 | 1.944 | 97.7 | 77.9 | 1306 | 23.59 | 5292.5 | 2849.6 | 2741.3 | 4076.9 | 1185 | 0.68185 | 5.95
2024-12-09 | 13:23 | Data | 0 | 32.501 | 31.036 | 179.392 | 7.63 | 168.053 | 2009.22 | 26.09 | 47.262 | 6.31 | 1.319 | 4.649 | 8128.7 | 2.039 | 97.7 | 77.9 | 1306 | 23.59 | 5283.7 | 2837.7 | 2735 | 4065.4 | 1185 | 0.68143 | 5.967
2024-12-09 | 13:23 | Data | 0 | 32.73 | 30.874 | 179.256 | 7.64 | 168.053 | 2011.93 | 26.11 | 47.082 | 6.32 | 1.326 | 4.664 | 8124.18 | 1.857 | 97.7 | 77.9 | 1308 | 23.59 | 5280.7 | 2844.2 | 2726.8 | 4067.1 | 1185 | 0.68303 | 5.99
2024-12-09 | 13:23 | Data | 0 | 32.892 | 30.718 | 179.347 | 7.64 | 168.007 | 2009.22 | 26.1 | 46.991 | 6.32 | 1.329 | 4.671 | 8128.7 | 1.978 | 97.7 | 77.8 | 1306 | 23.54 | 5283.7 | 2832.9 | 2724.2 | 4055.4 | 1185 | 0.68126 | 6
2024-12-09 | 13:23 | Data | 0 | 32.994 | 30.955 | 179.302 | 7.63 | 168.098 | 2009.22 | 26.11 | 47.082 | 6.32 | 1.322 | 4.663 | 7726.22 | 2.127 | 97.7 | 77.9 | 1305 | 23.54 | 5022 | 2828.3 | 2724.9 | 4053.1 | 1185 | 0.68091 | 5.986
2024-12-09 | 13:23 | Data | 0 | 33.061 | 30.718 | 179.528 | 7.63 | 168.143 | 2013.74 | 26.11 | 46.991 | 6.32 | 1.311 | 4.651 | 8146.79 | 2.032 | 97.7 | 78 | 1309 | 23.54 | 5295.4 | 2835.5 | 2721.1 | 4051.3 | 1185 | 0.68291 | 5.962
2024-12-09 | 13:23 | Data | 0 | 32.723 | 30.867 | 179.302 | 7.63 | 167.962 | 2009.22 | 26.1 | 47.172 | 6.32 | 1.315 | 4.639 | 8137.75 | 1.985 | 97.7 | 77.9 | 1306 | 23.59 | 5289.5 | 2839.6 | 2730.9 | 4062.8 | 1185 | 0.67743 | 5.954
2024-12-09 | 13:23 | Data | 0 | 32.73 | 30.698 | 179.347 | 7.63 | 168.007 | 2008.32 | 26.11 | 47.172 | 6.32 | 1.313 | 4.658 | 8133.23 | 2.025 | 97.7 | 78 | 1307 | 23.59 | 5286.6 | 2843.3 | 2732.3 | 4067.1 | 1185 | 0.6842 | 5.97
2024-12-09 | 13:23 | Data | 0 | 32.676 | 31.184 | 179.302 | 7.63 | 168.053 | 2009.22 | 26.1 | 47.082 | 6.32 | 1.315 | 4.647 | 8142.27 | 1.85 | 97.7 | 77.9 | 1307 | 23.54 | 5292.5 | 2840.2 | 2723 | 4056.6 | 1185 | 0.68293 | 5.962
2024-12-09 | 13:23 | Data | 0 | 32.723 | 30.853 | 179.347 | 7.64 | 168.007 | 2008.32 | 26.11 | 47.082 | 6.32 | 1.315 | 4.667 | 8137.75 | 2.059 | 97.7 | 78 | 1306 | 23.54 | 5289.5 | 2845.3 | 2728.3 | 4060.3 | 1185 | 0.68186 | 5.981
2024-12-09 | 13:23 | Data | 0 | 32.953 | 30.928 | 179.302 | 7.63 | 168.098 | 2009.22 | 26.11 | 46.991 | 6.32 | 1.317 | 4.664 | 8137.75 | 1.971 | 97.7 | 78 | 1307 | 23.54 | 5289.5 | 2855.4 | 2719.7 | 4065.5 | 1185 | 0.68585 | 5.982
2024-12-09 | 13:23 | Data | 0 | 32.953 | 30.496 | 179.256 | 7.63 | 168.098 | 2009.22 | 26.09 | 47.172 | 6.32 | 1.318 | 4.674 | 8128.7 | 2.262 | 97.7 | 78 | 1307 | 23.54 | 5283.7 | 2842.7 | 2722.1 | 4059 | 1185 | 0.68402 | 5.991
2024-12-09 | 13:23 | Data | 0 | 33.169 | 30.779 | 179.392 | 7.63 | 168.143 | 2015.55 | 26.11 | 47.172 | 6.31 | 1.305 | 4.655 | 8133.23 | 2.066 | 97.7 | 78.1 | 1309 | 23.59 | 5286.6 | 2854.5 | 2729 | 4067.4 | 1185.1 | 0.68436 | 5.962
2024-12-09 | 13:23 | Data | 0 | 32.568 | 30.658 | 179.256 | 7.63 | 167.962 | 2012.83 | 26.11 | 47.172 | 6.31 | 1.317 | 4.648 | 8133.23 | 1.87 | 97.7 | 77.9 | 1308 | 23.54 | 5286.6 | 2825.2 | 2750.7 | 4070.1 | 1185.1 | 0.67661 | 5.965
2024-12-09 | 13:24 | Data | 0 | 32.71 | 30.853 | 179.302 | 7.63 | 167.962 | 2012.83 | 26.11 | 46.721 | 6.32 | 1.315 | 4.668 | 8124.18 | 1.951 | 97.7 | 78 | 1309 | 23.36 | 5280.7 | 2849.9 | 2729.1 | 4067.2 | 1185.1 | 0.68421 | 5.985
2024-12-09 | 13:24 | Data | 0 | 32.71 | 30.833 | 179.302 | 7.63 | 168.053 | 2014.64 | 26.11 | 46.721 | 6.32 | 1.31 | 4.647 | 8115.14 | 2.052 | 97.7 | 78 | 1310 | 23.27 | 5274.8 | 2820.4 | 2757.2 | 4067.4 | 1185.1 | 0.67749 | 5.96
2024-12-09 | 13:24 | Data | 0 | 33.054 | 30.799 | 179.483 | 7.63 | 168.188 | 2015.55 | 26.1 | 46.721 | 6.32 | 1.318 | 4.63 | 8101.57 | 1.998 | 97.7 | 77.8 | 1310 | 23.41 | 5266 | 2849.8 | 2726.6 | 4068.9 | 1185.1 | 0.68255 | 5.948
2024-12-09 | 13:24 | Data | 0 | 32.784 | 30.766 | 179.392 | 7.63 | 168.053 | 2016.45 | 26.11 | 46.721 | 6.32 | 1.311 | 4.645 | 8106.09 | 1.681 | 97.7 | 78 | 1311 | 23.36 | 5269 | 2828.4 | 2749.1 | 4070.1 | 1185.1 | 0.67866 | 5.956
2024-12-09 | 13:24 | Data | 0 | 33.156 | 30.934 | 179.392 | 7.63 | 168.098 | 2013.74 | 26.1 | 46.811 | 6.32 | 1.315 | 4.639 | 8110.61 | 2.066 | 97.7 | 77.9 | 1309 | 23.41 | 5271.9 | 2835.6 | 2744.8 | 4068.2 | 1185.1 | 0.67795 | 5.955
2024-12-09 | 13:24 | Data | 0 | 32.669 | 31.191 | 179.483 | 7.63 | 168.098 | 2012.83 | 26.11 | 46.721 | 6.31 | 1.32 | 4.643 | 8110.61 | 2.052 | 97.7 | 77.9 | 1308 | 23.36 | 5271.9 | 2831.7 | 2750.8 | 4072.9 | 1185.1 | 0.67893 | 5.962
2024-12-09 | 13:24 | Data | 0 | 33.054 | 30.88 | 179.392 | 7.63 | 168.233 | 2012.83 | 26.11 | 46.721 | 6.31 | 1.319 | 4.645 | 8110.61 | 1.965 | 97.7 | 77.9 | 1308 | 23.36 | 5271.9 | 2842.6 | 2741.2 | 4071.2 | 1185.1 | 0.68038 | 5.963
2024-12-09 | 13:24 | Data | 0 | 33.108 | 31.036 | 179.347 | 7.63 | 168.007 | 2014.64 | 26.11 | 46.721 | 6.31 | 1.313 | 4.648 | 8119.66 | 1.978 | 97.7 | 78 | 1310 | 23.36 | 5277.8 | 2825.8 | 2735 | 4054.4 | 1185.1 | 0.67945 | 5.961
2024-12-09 | 13:24 | Data | 0 | 32.75 | 30.705 | 179.211 | 7.63 | 168.007 | 2012.83 | 26.1 | 46.811 | 6.33 | 1.319 | 4.633 | 8097.05 | 1.965 | 97.7 | 77.9 | 1308 | 23.41 | 5263.1 | 2846.5 | 2741 | 4070.7 | 1185.1 | 0.68191 | 5.95
2024-12-09 | 13:24 | Data | 0 | 32.953 | 31.083 | 179.347 | 7.63 | 168.053 | 2015.55 | 26.1 | 46.811 | 6.32 | 1.324 | 4.647 | 8106.09 | 1.958 | 97.7 | 77.8 | 1310 | 23.36 | 5269 | 2845.3 | 2743.5 | 4072.8 | 1185.1 | 0.68072 | 5.971
2024-12-09 | 13:24 | Data | 0 | 32.73 | 31.258 | 179.302 | 7.63 | 168.007 | 2013.74 | 26.1 | 46.811 | 6.32 | 1.317 | 4.658 | 8097.05 | 1.87 | 97.7 | 77.9 | 1308 | 23.41 | 5263.1 | 2844.5 | 2731.3 | 4063.4 | 1185.1 | 0.68358 | 5.976
2024-12-09 | 13:24 | Data | 0 | 32.838 | 30.725 | 179.528 | 7.63 | 168.098 | 2012.83 | 26.1 | 46.811 | 6.32 | 1.309 | 4.659 | 8097.05 | 2.221 | 97.7 | 78.1 | 1308 | 23.36 | 5263.1 | 2841.6 | 2745.4 | 4074.5 | 1185.1 | 0.68032 | 5.97
2024-12-09 | 13:24 | Data | 0 | 32.94 | 30.887 | 179.392 | 7.63 | 168.007 | 2014.64 | 26.11 | 46.811 | 6.32 | 1.309 | 4.648 | 8137.75 | 2.059 | 97.7 | 78 | 1309 | 23.41 | 5289.5 | 2822 | 2757.5 | 4069.5 | 1185.1 | 0.67521 | 5.958
2024-12-09 | 13:24 | Data | 0 | 33.068 | 30.725 | 179.392 | 7.63 | 168.143 | 2007.41 | 26.11 | 46.721 | 6.31 | 1.319 | 4.652 | 8133.23 | 2.059 | 97.7 | 77.9 | 1304 | 23.36 | 5286.6 | 2827.8 | 2748 | 4065.5 | 1185.1 | 0.67714 | 5.971
2024-12-09 | 13:24 | Data | 0 | 32.723 | 30.961 | 179.347 | 7.63 | 168.098 | 2007.41 | 26.1 | 46.811 | 6.32 | 1.32 | 4.654 | 8124.18 | 1.89 | 97.7 | 77.9 | 1304 | 23.36 | 5280.7 | 2824.2 | 2742.8 | 4062.2 | 1185.1 | 0.67661 | 5.973
2024-12-09 | 13:24 | Data | 0 | 32.831 | 30.88 | 179.302 | 7.63 | 168.098 | 2007.41 | 26.11 | 46.721 | 6.31 | 1.326 | 4.647 | 8128.7 | 1.971 | 97.7 | 77.8 | 1305 | 23.36 | 5283.7 | 2846.2 | 2745.6 | 4075.2 | 1185.1 | 0.68266 | 5.974
2024-12-09 | 13:24 | Data | 0 | 32.926 | 31.306 | 179.347 | 7.63 | 168.143 | 2007.41 | 26.1 | 46.721 | 6.32 | 1.314 | 4.631 | 8137.75 | 2.019 | 97.7 | 77.9 | 1305 | 23.36 | 5289.5 | 2831.6 | 2747 | 4067.8 | 1185.1 | 0.67991 | 5.945
2024-12-09 | 13:24 | Data | 0 | 32.946 | 30.88 | 179.302 | 7.63 | 168.053 | 2009.22 | 26.1 | 46.811 | 6.32 | 1.323 | 4.647 | 8133.23 | 2.073 | 97.7 | 77.8 | 1307 | 23.41 | 5286.6 | 2860.2 | 2749.4 | 4083.2 | 1185.1 | 0.68374 | 5.97
2024-12-09 | 13:25 | Data | 0 | 32.852 | 30.772 | 179.302 | 7.63 | 168.053 | 2006.51 | 26.11 | 46.721 | 6.32 | 1.323 | 4.659 | 8142.27 | 1.958 | 97.7 | 77.9 | 1305 | 23.36 | 5292.5 | 2840.7 | 2735.5 | 4057.9 | 1185.1 | 0.68142 | 5.981
2024-12-09 | 13:25 | Data | 0 | 32.791 | 30.664 | 179.483 | 7.63 | 168.098 | 2006.51 | 26.09 | 46.721 | 6.31 | 1.315 | 4.67 | 8146.79 | 1.87 | 97.7 | 78 | 1305 | 23.41 | 5295.4 | 2829.1 | 2744.9 | 4065.7 | 1185.1 | 0.67827 | 5.985
2024-12-09 | 13:25 | Data | 0 | 32.696 | 30.874 | 179.347 | 7.63 | 168.007 | 2006.51 | 26.11 | 46.811 | 6.32 | 1.308 | 4.681 | 8146.79 | 2.046 | 97.7 | 78.2 | 1303 | 23.41 | 5295.4 | 2849.2 | 2726.6 | 4063.4 | 1185.1 | 0.68471 | 5.988
2024-12-09 | 13:25 | Data | 0 | 33.068 | 30.671 | 179.392 | 7.63 | 168.188 | 2006.51 | 26.1 | 46.991 | 6.31 | 1.314 | 4.654 | 8146.79 | 1.944 | 97.7 | 78 | 1305 | 23.41 | 5295.4 | 2846.4 | 2748.1 | 4077.9 | 1185.1 | 0.68077 | 5.968
2024-12-09 | 13:25 | Data | 0 | 33.007 | 30.826 | 179.392 | 7.63 | 168.143 | 2009.22 | 26.1 | 46.721 | 6.32 | 1.33 | 4.635 | 8155.84 | 1.965 | 97.7 | 77.7 | 1306 | 23.41 | 5301.3 | 2840.7 | 2733.1 | 4065.3 | 1185.1 | 0.68303 | 5.966
2024-12-09 | 13:25 | Data | 0 | 32.615 | 31.076 | 179.347 | 7.63 | 168.053 | 2009.22 | 26.1 | 46.721 | 6.32 | 1.326 | 4.656 | 8155.84 | 1.951 | 97.7 | 77.8 | 1306 | 23.41 | 5301.3 | 2850.9 | 2735.3 | 4070.5 | 1185.1 | 0.68296 | 5.983
2024-12-09 | 13:25 | Data | 0 | 32.723 | 31.076 | 179.302 | 7.63 | 168.053 | 2012.83 | 26.1 | 46.721 | 6.33 | 1.31 | 4.635 | 8160.36 | 1.89 | 97.7 | 77.9 | 1308 | 23.41 | 5304.2 | 2857.8 | 2749.9 | 4065.6 | 1185.1 | 0.68299 | 5.947
2024-12-09 | 13:25 | Data | 0 | 32.609 | 30.874 | 179.302 | 7.63 | 168.007 | 2010.12 | 26.11 | 46.721 | 6.32 | 1.326 | 4.626 | 8160.36 | 1.816 | 97.7 | 77.7 | 1306 | 23.32 | 5304.2 | 2837.4 | 2741.8 | 4069.4 | 1185.1 | 0.68217 | 5.95
2024-12-09 | 13:25 | Data | 0 | 32.744 | 31.083 | 179.483 | 7.64 | 168.053 | 2012.83 | 26.11 | 46.721 | 6.31 | 1.326 | 4.663 | 8164.88 | 1.674 | 97.7 | 77.9 | 1308 | 23.36 | 5307.2 | 2850.3 | 2752.6 | 4082 | 1185.1 | 0.68142 | 5.988
2024-12-09 | 13:25 | Data | 0 | 32.791 | 30.658 | 179.347 | 7.63 | 168.053 | 2009.22 | 26.1 | 46.811 | 6.31 | 1.315 | 4.662 | 8164.88 | 1.85 | 97.7 | 78 | 1305 | 23.41 | 5307.2 | 2838.5 | 2748.4 | 4076.5 | 1185.1 | 0.68132 | 5.977
2024-12-09 | 13:25 | Data | 0 | 33.176 | 30.691 | 179.573 | 7.63 | 168.098 | 2009.22 | 26.1 | 46.721 | 6.32 | 1.306 | 4.657 | 8133.23 | 2.181 | 97.7 | 78.1 | 1307 | 23.41 | 5286.6 | 2836 | 2736.9 | 4062.1 | 1185.1 | 0.68077 | 5.963
2024-12-09 | 13:25 | Data | 0 | 33.331 | 30.948 | 179.392 | 7.63 | 168.098 | 2010.12 | 26.1 | 46.811 | 6.31 | 1.323 | 4.637 | 8133.23 | 2.073 | 97.7 | 77.8 | 1306 | 23.41 | 5286.6 | 2831.3 | 2750.1 | 4073.3 | 1185.1 | 0.67835 | 5.96
2024-12-09 | 13:25 | Data | 0 | 32.926 | 31.103 | 179.483 | 7.63 | 168.053 | 2010.12 | 26.11 | 46.811 | 6.31 | 1.317 | 4.649 | 8142.27 | 1.843 | 97.7 | 78 | 1306 | 23.41 | 5292.5 | 2846.2 | 2741 | 4071.2 | 1185.1 | 0.68239 | 5.963
2024-12-09 | 13:25 | Data | 0 | 33.041 | 30.995 | 179.483 | 7.63 | 168.098 | 2009.22 | 26.11 | 46.811 | 6.31 | 1.314 | 4.637 | 8128.7 | 2.059 | 97.7 | 77.9 | 1305 | 23.36 | 5283.7 | 2747.4 | 2795.2 | 4016.9 | 1185.1 | 0.67286 | 5.951
2024-12-09 | 13:25 | Data | 0 | 32.737 | 30.88 | 179.347 | 7.63 | 168.053 | 2009.22 | 26.11 | 46.811 | 6.31 | 1.317 | 4.657 | 8106.09 | 1.85 | 97.7 | 78 | 1305 | 23.36 | 5269 | 1736.1 | 2156.4 | 2780.3 | 1185.1 | 0.62146 | 5.972
2024-12-09 | 13:25 | Data | 0 | 32.723 | 30.88 | 179.347 | 7.63 | 168.007 | 2015.55 | 26.11 | 46.63 | 6.32 | 1.326 | 4.662 | 8101.57 | 2.052 | 97.7 | 77.8 | 1310 | 23.41 | 5266 | 1761.4 | 2177.4 | 2803.3 | 1185.1 | 0.6224 | 5.988
2024-12-09 | 13:25 | Data | 0 | 32.507 | 30.874 | 179.302 | 7.63 | 168.007 | 2015.55 | 26.1 | 46.811 | 6.32 | 1.332 | 4.667 | 8110.61 | 1.823 | 97.7 | 77.8 | 1310 | 23.36 | 5271.9 | 1774.7 | 2166.9 | 2813.1 | 1185.1 | 0.62839 | 5.998
2024-12-09 | 13:26 | Data | 0 | 32.723 | 31.191 | 179.483 | 7.63 | 168.098 | 2014.64 | 26.11 | 46.811 | 6.32 | 1.324 | 4.669 | 8110.61 | 1.992 | 97.7 | 77.9 | 1310 | 23.41 | 5271.9 | 1760.1 | 2152.1 | 2792.5 | 1185.1 | 0.62751 | 5.992
2024-12-09 | 13:26 | Data | 0 | 32.926 | 30.678 | 179.483 | 7.63 | 168.053 | 2015.55 | 26.1 | 46.811 | 6.32 | 1.324 | 4.67 | 8124.18 | 2.174 | 97.7 | 77.9 | 1310 | 23.41 | 5280.7 | 1754.1 | 2156.2 | 2794.1 | 1185.1 | 0.62473 | 5.994
2024-12-09 | 13:26 | Data | 0 | 32.757 | 30.779 | 179.302 | 7.63 | 168.053 | 2015.55 | 26.11 | 46.63 | 6.32 | 1.322 | 4.649 | 8128.7 | 2.025 | 97.7 | 77.9 | 1310 | 23.36 | 5283.7 | 1758.6 | 2171 | 2807.3 | 1185.2 | 0.62421 | 5.971
2024-12-09 | 13:26 | Data | 0 | 32.838 | 30.732 | 179.483 | 7.64 | 168.143 | 2015.55 | 26.1 | 46.721 | 6.32 | 1.324 | 4.658 | 8115.14 | 1.803 | 97.7 | 77.9 | 1310 | 23.32 | 5274.8 | 1780 | 2161.1 | 2812.1 | 1185.2 | 0.63036 | 5.981
2024-12-09 | 13:26 | Data | 0 | 32.723 | 30.88 | 179.347 | 7.63 | 168.098 | 2014.64 | 26.12 | 46.721 | 6.33 | 1.322 | 4.662 | 8124.18 | 1.843 | 97.7 | 77.9 | 1310 | 23.36 | 5280.7 | 1761.2 | 2166.7 | 2804.9 | 1185.2 | 0.62508 | 5.984
2024-12-09 | 13:26 | Data | 0 | 33.223 | 31.157 | 179.528 | 7.63 | 168.053 | 2014.64 | 26.11 | 46.721 | 6.33 | 1.313 | 4.645 | 8110.61 | 2.154 | 97.7 | 78 | 1310 | 23.41 | 5271.9 | 1769.7 | 2147.2 | 2796 | 1185.2 | 0.63018 | 5.958
2024-12-09 | 13:26 | Data | 0 | 32.946 | 30.88 | 179.302 | 7.63 | 168.098 | 2015.55 | 26.1 | 46.721 | 6.32 | 1.307 | 4.648 | 8110.61 | 1.958 | 97.7 | 78.1 | 1310 | 23.41 | 5271.9 | 1767.4 | 2160.7 | 2803.1 | 1185.2 | 0.63199 | 5.955
2024-12-09 | 13:26 | Data | 0 | 32.528 | 30.874 | 179.256 | 7.63 | 168.007 | 2021.87 | 26.1 | 46.811 | 6.32 | 1.314 | 4.656 | 8106.09 | 2.012 | 97.7 | 78 | 1314 | 23.41 | 5269 | 1760.6 | 2173.2 | 2811 | 1185.2 | 0.62463 | 5.97
2024-12-09 | 13:26 | Data | 0 | 33.061 | 30.934 | 179.347 | 7.63 | 168.098 | 2017.35 | 26.11 | 46.811 | 6.32 | 1.32 | 4.659 | 8115.14 | 1.985 | 97.7 | 77.9 | 1312 | 23.36 | 5274.8 | 1753.1 | 2155.3 | 2790.2 | 1185.2 | 0.62542 | 5.979
2024-12-09 | 13:26 | Data | 0 | 32.946 | 30.961 | 179.483 | 7.63 | 168.098 | 2017.35 | 26.09 | 46.721 | 6.32 | 1.32 | 4.632 | 8124.18 | 1.992 | 97.7 | 77.8 | 1311 | 23.41 | 5280.7 | 1761.5 | 2150.8 | 2793.3 | 1185.2 | 0.62707 | 5.951
2024-12-09 | 13:26 | Data | 0 | 33.142 | 30.88 | 179.483 | 7.63 | 168.143 | 2017.35 | 26.1 | 46.811 | 6.31 | 1.322 | 4.645 | 8115.14 | 2.086 | 97.7 | 77.8 | 1311 | 23.36 | 5274.8 | 1758.8 | 2156.3 | 2794.7 | 1185.2 | 0.62617 | 5.967
2024-12-09 | 13:26 | Data | 0 | 32.906 | 30.88 | 179.347 | 7.63 | 168.143 | 2014.64 | 26.11 | 46.721 | 6.31 | 1.314 | 4.657 | 8124.18 | 1.938 | 97.7 | 78 | 1310 | 23.36 | 5280.7 | 1754.8 | 2156.7 | 2793.3 | 1185.2 | 0.6254 | 5.971
2024-12-09 | 13:26 | Data | 0 | 32.777 | 30.88 | 179.483 | 7.63 | 168.053 | 2020.97 | 26.11 | 46.45 | 6.32 | 1.324 | 4.634 | 8124.18 | 1.857 | 97.7 | 77.8 | 1313 | 23.27 | 5280.7 | 1745.2 | 2162.1 | 2791.7 | 1185.2 | 0.6221 | 5.957
2024-12-09 | 13:26 | Data | 0 | 33.061 | 30.982 | 179.347 | 7.63 | 168.188 | 2015.55 | 26.1 | 46.991 | 6.32 | 1.325 | 4.645 | 8562.84 | 1.951 | 97.7 | 77.8 | 1310 | 23.41 | 5565.8 | 1762.7 | 2176.6 | 2813.5 | 1185.2 | 0.62432 | 5.969
2024-12-09 | 13:26 | Data | 0 | 33.149 | 30.901 | 179.528 | 7.63 | 168.143 | 2015.55 | 26.09 | 46.811 | 6.32 | 1.32 | 4.652 | 7929.72 | 2.12 | 97.7 | 77.9 | 1310 | 23.41 | 5154.3 | 1775.9 | 2170.2 | 2815.4 | 1185.2 | 0.6287 | 5.972
2024-12-09 | 13:26 | Data | 0 | 32.723 | 30.86 | 179.347 | 7.63 | 168.053 | 2018.26 | 26.1 | 46.721 | 6.32 | 1.315 | 4.657 | 7938.77 | 1.884 | 97.7 | 78 | 1312 | 23.36 | 5160.2 | 1746.1 | 2166.9 | 2797 | 1185.2 | 0.6264 | 5.97
2024-12-09 | 13:26 | Data | 0 | 32.575 | 30.651 | 179.347 | 7.63 | 168.143 | 2017.35 | 26.09 | 46.721 | 6.31 | 1.319 | 4.642 | 7943.29 | 1.769 | 97.7 | 77.9 | 1311 | 23.36 | 5163.1 | 1762.2 | 2173.6 | 2815.6 | 1185.2 | 0.62226 | 5.961
2024-12-09 | 13:26 | Data | 0 | 32.892 | 30.975 | 179.528 | 7.63 | 167.962 | 2016.45 | 26.09 | 46.45 | 6.32 | 1.312 | 4.664 | 7961.38 | 1.89 | 97.7 | 78 | 1311 | 23.27 | 5174.9 | 1757.6 | 2177.4 | 2810.4 | 1185.2 | 0.62337 | 5.978
2024-12-09 | 13:27 | Data | 0 | 33.149 | 30.934 | 179.347 | 7.63 | 168.098 | 2019.16 | 26.1 | 46.811 | 6.33 | 1.319 | 4.673 | 7943.29 | 2.073 | 97.7 | 78 | 1312 | 23.41 | 5163.1 | 1756.7 | 2167.5 | 2798.8 | 1185.2 | 0.62402 | 5.992
2024-12-09 | 13:27 | Data | 0 | 33.149 | 30.934 | 179.483 | 7.63 | 168.188 | 2020.97 | 26.11 | 46.811 | 6.31 | 1.319 | 4.651 | 7947.81 | 2.181 | 97.7 | 77.9 | 1314 | 23.36 | 5166.1 | 1748.7 | 2160.9 | 2791.8 | 1185.2 | 0.62391 | 5.97
2024-12-09 | 13:27 | Data | 0 | 32.757 | 31.056 | 179.483 | 7.63 | 168.143 | 2020.97 | 26.1 | 46.721 | 6.32 | 1.318 | 4.663 | 7956.86 | 1.863 | 97.7 | 78 | 1314 | 23.36 | 5172 | 1756.3 | 2158 | 2795.2 | 1185.2 | 0.62419 | 5.98
2024-12-09 | 13:27 | Data | 0 | 32.94 | 30.88 | 179.573 | 7.63 | 168.098 | 2020.07 | 26.1 | 46.811 | 6.32 | 1.32 | 4.665 | 8291.5 | 2.066 | 97.7 | 77.9 | 1312 | 23.41 | 5389.5 | 1766.3 | 2173.8 | 2803.6 | 1185.2 | 0.628 | 5.987
2024-12-09 | 13:27 | Data | 0 | 33.007 | 30.664 | 179.392 | 7.63 | 168.143 | 2020.97 | 26.09 | 46.991 | 6.32 | 1.32 | 4.643 | 8314.11 | 2.073 | 97.7 | 77.8 | 1314 | 23.41 | 5404.2 | 1756.3 | 2179.8 | 2811.7 | 1185.2 | 0.62544 | 5.963
2024-12-09 | 13:27 | Data | 0 | 32.669 | 30.678 | 179.256 | 7.63 | 168.098 | 2020.97 | 26.09 | 46.721 | 6.31 | 1.312 | 4.634 | 8291.5 | 1.931 | 97.7 | 77.9 | 1314 | 23.36 | 5389.5 | 1763.9 | 2169.8 | 2810.1 | 1185.2 | 0.62442 | 5.946
2024-12-09 | 13:27 | Data | 0 | 32.494 | 30.651 | 179.347 | 7.63 | 167.917 | 2020.07 | 26.1 | 46.991 | 6.32 | 1.319 | 4.654 | 8291.5 | 1.843 | 97.7 | 77.9 | 1314 | 23.41 | 5389.5 | 1771.9 | 2157 | 2804.3 | 1185.2 | 0.6294 | 5.974
2024-12-09 | 13:27 | Data | 0 | 32.757 | 30.678 | 179.256 | 7.63 | 168.007 | 2020.07 | 26.08 | 46.811 | 6.32 | 1.315 | 4.662 | 8273.41 | 1.863 | 97.7 | 78 | 1314 | 23.36 | 5377.7 | 1749.9 | 2157 | 2800.1 | 1185.2 | 0.62713 | 5.976
2024-12-09 | 13:27 | Data | 0 | 32.75 | 30.766 | 179.166 | 7.63 | 168.053 | 2020.07 | 26.09 | 46.721 | 6.32 | 1.318 | 4.646 | 8296.02 | 2.073 | 97.7 | 77.9 | 1314 | 23.41 | 5392.4 | 1748.5 | 2164.2 | 2794.8 | 1185.2 | 0.62333 | 5.964
2024-12-09 | 13:27 | Data | 0 | 32.723 | 31.09 | 179.347 | 7.63 | 168.007 | 2012.83 | 26.08 | 46.721 | 6.31 | 1.319 | 4.634 | 8277.94 | 1.958 | 97.7 | 77.9 | 1308 | 23.41 | 5380.7 | 1751.3 | 2182.2 | 2811.3 | 1185.2 | 0.61927 | 5.95
2024-12-09 | 13:27 | Data | 0 | 32.723 | 30.651 | 179.166 | 7.63 | 168.053 | 2017.35 | 26.09 | 46.721 | 6.31 | 1.325 | 4.625 | 8277.94 | 1.958 | 97.7 | 77.7 | 1312 | 23.36 | 5380.7 | 1759.2 | 2182.4 | 2815.8 | 1185.2 | 0.62245 | 5.95
2024-12-09 | 13:27 | Data | 0 | 32.723 | 30.826 | 179.483 | 7.63 | 168.053 | 2018.26 | 26.1 | 46.811 | 6.32 | 1.315 | 4.635 | 7916.16 | 2.059 | 97.7 | 77.9 | 1312 | 23.41 | 5145.5 | 1767.9 | 2179.5 | 2819.3 | 1185.2 | 0.62319 | 5.95
2024-12-09 | 13:27 | Data | 0 | 33.034 | 30.907 | 179.347 | 7.63 | 168.098 | 2018.26 | 26.09 | 46.721 | 6.32 | 1.326 | 4.659 | 7875.46 | 2.032 | 97.7 | 77.9 | 1312 | 23.41 | 5119 | 1761 | 2171.3 | 2808.2 | 1185.2 | 0.62103 | 5.985
2024-12-09 | 13:27 | Data | 0 | 32.696 | 30.826 | 179.392 | 7.63 | 168.007 | 2017.35 | 26.09 | 46.811 | 6.32 | 1.323 | 4.645 | 7902.59 | 2.12 | 97.7 | 77.8 | 1311 | 23.41 | 5136.7 | 1761.5 | 2164.6 | 2802.8 | 1185.2 | 0.62622 | 5.968
2024-12-09 | 13:27 | Data | 0 | 32.885 | 30.651 | 179.483 | 7.64 | 168.053 | 2018.26 | 26.09 | 46.721 | 6.32 | 1.319 | 4.658 | 7898.07 | 2.113 | 97.7 | 77.9 | 1312 | 23.41 | 5133.7 | 1758.5 | 2171.5 | 2806.7 | 1185.2 | 0.62343 | 5.977
2024-12-09 | 13:27 | Data | 0 | 32.669 | 30.88 | 179.347 | 7.63 | 168.007 | 2017.35 | 26.11 | 46.721 | 6.31 | 1.324 | 4.654 | 8291.5 | 2.005 | 97.7 | 77.9 | 1312 | 23.41 | 5389.5 | 1762.6 | 2180.8 | 2816.9 | 1185.2 | 0.62278 | 5.977
2024-12-09 | 13:27 | Data | 0 | 32.717 | 30.482 | 179.302 | 7.63 | 168.053 | 2013.74 | 26.1 | 46.721 | 6.32 | 1.319 | 4.647 | 8332.2 | 2.181 | 97.7 | 77.9 | 1310 | 23.32 | 5415.9 | 1765.7 | 2165.5 | 2806.6 | 1185.2 | 0.6252 | 5.967
2024-12-09 | 13:27 | Data | 0 | 32.723 | 30.766 | 179.256 | 7.63 | 168.007 | 2018.26 | 26.09 | 46.721 | 6.31 | 1.319 | 4.653 | 8314.11 | 1.985 | 97.7 | 77.9 | 1312 | 23.36 | 5404.2 | 1759.5 | 2161 | 2799.9 | 1185.2 | 0.62544 | 5.972
2024-12-09 | 13:28 | Data | 0 | 32.723 | 30.759 | 179.302 | 7.63 | 167.962 | 2018.26 | 26.09 | 46.811 | 6.32 | 1.319 | 4.673 | 8305.07 | 2.086 | 97.7 | 78 | 1312 | 23.36 | 5398.3 | 1751.5 | 2158.6 | 2792.2 | 1185.2 | 0.62475 | 5.991
2024-12-09 | 13:28 | Data | 0 | 32.94 | 30.489 | 179.302 | 7.63 | 168.053 | 2018.26 | 26.09 | 46.63 | 6.31 | 1.323 | 4.638 | 8286.98 | 2.214 | 97.7 | 77.8 | 1311 | 23.36 | 5386.5 | 1763 | 2153.1 | 2795.4 | 1185.2 | 0.62791 | 5.962
2024-12-09 | 13:28 | Data | 0 | 33.068 | 30.88 | 179.483 | 7.63 | 168.143 | 2014.64 | 26.1 | 46.811 | 6.32 | 1.32 | 4.625 | 7938.77 | 2.12 | 97.7 | 77.8 | 1310 | 23.32 | 5160.2 | 1749.3 | 2124.8 | 2765.3 | 1185.2 | 0.63017 | 5.944
2024-12-09 | 13:28 | Data | 0 | 32.946 | 30.712 | 179.347 | 7.63 | 168.053 | 2015.55 | 26.09 | 46.811 | 6.31 | 1.319 | 4.636 | 7920.68 | 2.066 | 97.7 | 77.9 | 1310 | 23.36 | 5148.4 | 1750.2 | 2139 | 2769.6 | 1185.2 | 0.62278 | 5.955
2024-12-09 | 13:28 | Data | 0 | 32.494 | 30.428 | 179.211 | 7.63 | 168.007 | 2011.93 | 26.09 | 46.811 | 6.32 | 1.317 | 4.649 | 7947.81 | 2.181 | 97.7 | 77.9 | 1309 | 23.41 | 5166.1 | 1738 | 2131.7 | 2763.7 | 1185.2 | 0.626 | 5.966
2024-12-09 | 13:28 | Data | 0 | 32.669 | 30.604 | 179.347 | 7.63 | 168.053 | 2012.83 | 26.11 | 46.991 | 6.32 | 1.32 | 4.653 | 7961.38 | 2.106 | 97.7 | 77.9 | 1308 | 23.41 | 5174.9 | 1765.3 | 2161.1 | 2804.8 | 1185.2 | 0.62641 | 5.973
2024-12-09 | 13:28 | Data | 0 | 32.953 | 30.725 | 179.483 | 7.63 | 168.007 | 2007.41 | 26.1 | 46.721 | 6.32 | 1.325 | 4.642 | 7943.29 | 1.897 | 97.7 | 77.8 | 1305 | 23.41 | 5163.1 | 1751.2 | 2147.2 | 2783.4 | 1185.2 | 0.6259 | 5.967
2024-12-09 | 13:28 | Data | 0 | 32.777 | 30.448 | 179.256 | 7.63 | 168.007 | 2012.83 | 26.1 | 46.721 | 6.32 | 1.31 | 4.635 | 7947.81 | 1.965 | 97.7 | 78 | 1308 | 23.36 | 5166.1 | 1756.3 | 2150.1 | 2789 | 1185.2 | 0.63029 | 5.946
2024-12-09 | 13:28 | Data | 0 | 32.615 | 30.82 | 179.347 | 7.63 | 168.007 | 2016.45 | 26.09 | 46.721 | 6.31 | 1.323 | 4.633 | 8282.46 | 2.059 | 97.7 | 77.8 | 1310 | 23.32 | 5383.6 | 1741 | 2160.2 | 2788 | 1185.2 | 0.62221 | 5.955
2024-12-09 | 13:28 | Data | 0 | 32.838 | 30.664 | 179.256 | 7.63 | 168.007 | 2010.12 | 26.09 | 46.811 | 6.33 | 1.323 | 4.635 | 7934.25 | 2.066 | 97.7 | 77.8 | 1308 | 23.41 | 5157.3 | 1755.2 | 2141.8 | 2781.3 | 1185.2 | 0.62869 | 5.959
2024-12-09 | 13:28 | Data | 0 | 32.548 | 30.651 | 179.302 | 7.63 | 168.007 | 2018.26 | 26.09 | 46.721 | 6.32 | 1.311 | 4.646 | 7898.07 | 2.032 | 97.7 | 78 | 1312 | 23.36 | 5133.7 | 1756.5 | 2146.5 | 2786.6 | 1185.2 | 0.62732 | 5.958
2024-12-09 | 13:28 | Data | 0 | 32.723 | 30.847 | 179.347 | 7.63 | 168.053 | 2018.26 | 26.08 | 46.721 | 6.32 | 1.313 | 4.645 | 7907.11 | 1.884 | 97.7 | 77.9 | 1312 | 23.36 | 5139.6 | 1762.6 | 2149.1 | 2794.3 | 1185.2 | 0.6276 | 5.96
2024-12-09 | 13:28 | Data | 0 | 32.838 | 30.766 | 179.302 | 7.63 | 168.053 | 2017.35 | 26.1 | 46.811 | 6.31 | 1.32 | 4.624 | 7943.29 | 1.803 | 97.7 | 77.8 | 1311 | 23.41 | 5163.1 | 2827.9 | 2730.8 | 4054 | 1185.2 | 0.67865 | 5.943
2024-12-09 | 13:28 | Data | 0 | 32.723 | 30.563 | 179.302 | 7.63 | 167.962 | 2015.55 | 26.1 | 46.63 | 6.31 | 1.318 | 4.651 | 7947.81 | 2.079 | 97.7 | 77.9 | 1310 | 23.32 | 5166.1 | 2851.2 | 2741.5 | 4069.6 | 1185.2 | 0.68096 | 5.968
2024-12-09 | 13:28 | Data | 0 | 32.892 | 30.975 | 179.256 | 7.63 | 167.962 | 2012.83 | 26.1 | 46.811 | 6.32 | 1.319 | 4.638 | 7961.38 | 1.884 | 97.7 | 77.9 | 1308 | 23.41 | 5174.9 | 2846.8 | 2756.5 | 4083.1 | 1185.2 | 0.68164 | 5.957
2024-12-09 | 13:28 | Data | 0 | 32.271 | 30.644 | 179.302 | 7.63 | 167.962 | 2013.74 | 26.09 | 46.811 | 6.32 | 1.306 | 4.656 | 7970.42 | 1.762 | 97.7 | 78.1 | 1308 | 23.5 | 5180.8 | 2846.3 | 2757.4 | 4086.8 | 1185.2 | 0.67924 | 5.964
2024-12-09 | 13:29 | Data | 0 | 32.548 | 30.766 | 179.256 | 7.63 | 167.962 | 2012.83 | 26.08 | 46.811 | 6.31 | 1.329 | 4.674 | 7997.56 | 1.911 | 97.7 | 77.9 | 1308 | 23.41 | 5198.4 | 2846.5 | 2747.9 | 4080.8 | 1185.2 | 0.67931 | 6.003
2024-12-09 | 13:29 | Data | 0 | 32.73 | 30.536 | 179.256 | 7.63 | 168.098 | 2009.22 | 26.08 | 46.721 | 6.32 | 1.324 | 4.653 | 7993.04 | 1.904 | 97.7 | 77.9 | 1308 | 23.36 | 5195.5 | 2854.4 | 2750.5 | 4086.4 | 1185.2 | 0.68311 | 5.976
2024-12-09 | 13:29 | Data | 0 | 32.494 | 30.536 | 179.166 | 7.63 | 167.872 | 2008.32 | 26.08 | 46.811 | 6.32 | 1.315 | 4.631 | 8015.65 | 2.079 | 97.7 | 77.9 | 1306 | 23.36 | 5210.2 | 2816.1 | 2719.8 | 4044.5 | 1185.2 | 0.67873 | 5.946
2024-12-09 | 13:29 | Data | 0 | 32.663 | 30.799 | 179.256 | 7.63 | 167.962 | 2010.12 | 26.07 | 46.991 | 6.32 | 1.323 | 4.633 | 8002.08 | 1.965 | 97.7 | 77.8 | 1307 | 23.41 | 5201.4 | 2821.5 | 2737.1 | 4057.2 | 1185.2 | 0.67718 | 5.954
2024-12-09 | 13:29 | Data | 0 | 32.494 | 30.637 | 179.256 | 7.63 | 167.917 | 2007.41 | 26.08 | 46.721 | 6.32 | 1.321 | 4.634 | 8323.16 | 1.857 | 97.7 | 77.8 | 1305 | 23.41 | 5410.1 | 2840.7 | 2762.2 | 4085.6 | 1185.3 | 0.67881 | 5.955
2024-12-09 | 13:29 | Data | 0 | 32.501 | 30.847 | 179.256 | 7.63 | 168.007 | 2009.22 | 26.08 | 46.721 | 6.33 | 1.317 | 4.642 | 7907.11 | 1.823 | 97.7 | 77.9 | 1306 | 23.36 | 5139.6 | 2837.9 | 2752.3 | 4076.1 | 1185.3 | 0.67784 | 5.959
2024-12-09 | 13:29 | Data | 0 | 32.75 | 30.651 | 179.256 | 7.63 | 168.007 | 2006.51 | 26.08 | 46.721 | 6.32 | 1.318 | 4.645 | 7929.72 | 2.106 | 97.7 | 77.9 | 1306 | 23.41 | 5154.3 | 2835.6 | 2754.1 | 4082.4 | 1185.3 | 0.67764 | 5.962
2024-12-09 | 13:29 | Data | 0 | 32.636 | 30.651 | 179.256 | 7.63 | 168.007 | 2009.22 | 26.06 | 46.811 | 6.32 | 1.31 | 4.637 | 8318.64 | 1.857 | 97.7 | 78 | 1306 | 23.36 | 5407.1 | 2837.9 | 2760 | 4082.9 | 1185.3 | 0.6782 | 5.948
2024-12-09 | 13:29 | Data | 0 | 32.75 | 30.658 | 179.302 | 7.63 | 168.007 | 2015.55 | 26.06 | 46.721 | 6.32 | 1.32 | 4.635 | 8323.16 | 2.073 | 97.7 | 77.8 | 1310 | 23.36 | 5410.1 | 2851.4 | 2736.5 | 4073.8 | 1185.3 | 0.68383 | 5.955
2024-12-09 | 13:29 | Data | 0 | 32.723 | 30.766 | 179.302 | 7.63 | 168.007 | 2009.22 | 26.06 | 46.721 | 6.33 | 1.324 | 4.639 | 8300.55 | 2.052 | 97.7 | 77.8 | 1306 | 23.41 | 5395.4 | 2838.3 | 2754.1 | 4070.5 | 1185.3 | 0.68066 | 5.963
2024-12-09 | 13:29 | Data | 0 | 32.838 | 30.658 | 179.302 | 7.63 | 168.007 | 2009.22 | 26.06 | 46.811 | 6.31 | 1.32 | 4.651 | 8305.07 | 1.958 | 97.7 | 77.9 | 1306 | 23.36 | 5398.3 | 2840.4 | 2745.5 | 4076 | 1185.3 | 0.68148 | 5.971
2024-12-09 | 13:29 | Data | 0 | 32.521 | 30.82 | 179.211 | 7.63 | 168.007 | 2012.83 | 26.07 | 46.811 | 6.32 | 1.321 | 4.625 | 8305.07 | 1.863 | 97.7 | 77.8 | 1308 | 23.41 | 5398.3 | 2857.7 | 2757.5 | 4093.7 | 1185.3 | 0.68227 | 5.946
2024-12-09 | 13:29 | Data | 0 | 32.723 | 30.658 | 179.302 | 7.63 | 168.007 | 2010.12 | 26.06 | 46.63 | 6.32 | 1.318 | 4.639 | 8305.07 | 2.046 | 97.7 | 77.9 | 1306 | 23.5 | 5398.3 | 2856.3 | 2740.3 | 4077.8 | 1185.3 | 0.68211 | 5.958
2024-12-09 | 13:29 | Data | 0 | 32.494 | 30.637 | 179.166 | 7.63 | 168.053 | 2009.22 | 26.06 | 46.721 | 6.32 | 1.309 | 4.667 | 8291.5 | 2.046 | 97.7 | 78.1 | 1307 | 23.41 | 5389.5 | 2841.4 | 2736.6 | 4062.1 | 1185.3 | 0.68258 | 5.976
2024-12-09 | 13:29 | Data | 0 | 32.494 | 30.651 | 179.302 | 7.63 | 168.007 | 2010.12 | 26.06 | 46.721 | 6.32 | 1.321 | 4.664 | 8264.37 | 2.046 | 97.7 | 77.9 | 1306 | 23.36 | 5371.8 | 2832.1 | 2738.6 | 4063.5 | 1185.3 | 0.67991 | 5.985
2024-12-09 | 13:29 | Data | 0 | 32.717 | 31.042 | 179.211 | 7.63 | 168.053 | 2006.51 | 26.08 | 46.721 | 6.32 | 1.32 | 4.648 | 8264.37 | 1.87 | 97.7 | 77.9 | 1305 | 23.36 | 5371.8 | 2829.7 | 2729.2 | 4053.5 | 1185.3 | 0.68214 | 5.968
2024-12-09 | 13:29 | Data | 0 | 32.696 | 30.651 | 179.256 | 7.63 | 168.007 | 2008.32 | 26.07 | 46.811 | 6.31 | 1.312 | 4.664 | 8264.37 | 2.066 | 97.7 | 78 | 1305 | 23.36 | 5371.8 | 2850.4 | 2746.7 | 4079.4 | 1185.3 | 0.68338 | 5.976
2024-12-09 | 13:29 | Data | 0 | 32.528 | 30.428 | 179.121 | 7.63 | 167.962 | 2010.12 | 26.07 | 46.721 | 6.31 | 1.319 | 4.656 | 8250.8 | 1.85 | 97.7 | 77.9 | 1306 | 23.32 | 5363 | 2849.4 | 2725.5 | 4063.4 | 1185.3 | 0.68555 | 5.975
2024-12-09 | 13:30 | Data | 0 | 33.034 | 30.988 | 179.392 | 7.63 | 168.053 | 2011.93 | 26.08 | 46.721 | 6.32 | 1.314 | 4.652 | 8237.24 | 1.944 | 97.7 | 78 | 1309 | 23.41 | 5354.2 | 2842.9 | 2738 | 4068.7 | 1185.3 | 0.68161 | 5.966
2024-12-09 | 13:30 | Data | 0 | 32.494 | 30.421 | 179.166 | 7.63 | 167.962 | 2014.64 | 26.08 | 47.082 | 6.32 | 1.319 | 4.662 | 8223.67 | 2.073 | 97.7 | 78 | 1311 | 23.36 | 5345.4 | 2844.7 | 2737.8 | 4068.8 | 1185.3 | 0.68253 | 5.979
2024-12-09 | 13:30 | Data | 0 | 32.528 | 30.536 | 179.347 | 7.63 | 168.098 | 2017.35 | 26.07 | 46.811 | 6.31 | 1.332 | 4.658 | 8192.01 | 1.796 | 97.7 | 77.7 | 1312 | 23.36 | 5324.8 | 2825.9 | 2706.1 | 4043.2 | 1185.3 | 0.68187 | 5.992
2024-12-09 | 13:30 | Data | 0 | 32.501 | 30.529 | 179.166 | 7.63 | 167.962 | 2017.35 | 26.08 | 46.811 | 6.31 | 1.323 | 4.675 | 8169.4 | 1.85 | 97.7 | 77.9 | 1311 | 23.41 | 5310.1 | 2839.9 | 2729 | 4064.4 | 1185.3 | 0.68139 | 6
2024-12-09 | 13:30 | Data | 0 | 32.71 | 30.637 | 179.256 | 7.63 | 168.007 | 2018.26 | 26.07 | 46.811 | 6.31 | 1.326 | 4.673 | 8169.4 | 1.911 | 97.7 | 77.9 | 1312 | 23.36 | 5310.1 | 2832.7 | 2729.2 | 4059.9 | 1185.3 | 0.68167 | 5.998
2024-12-09 | 13:30 | Data | 0 | 32.723 | 30.475 | 179.211 | 7.63 | 167.962 | 2020.07 | 26.08 | 46.721 | 6.32 | 1.329 | 4.659 | 8155.84 | 1.944 | 97.7 | 77.8 | 1313 | 23.41 | 5301.3 | 2848.7 | 2739.2 | 4077.3 | 1185.3 | 0.68121 | 5.988
2024-12-09 | 13:30 | Data | 0 | 32.44 | 30.847 | 179.166 | 7.63 | 168.053 | 2024.58 | 26.08 | 46.63 | 6.32 | 1.33 | 4.653 | 8155.84 | 1.823 | 97.7 | 77.8 | 1315 | 23.36 | 5301.3 | 2838.9 | 2731.7 | 4065.7 | 1185.3 | 0.6817 | 5.984
2024-12-09 | 13:30 | Data | 0 | 32.669 | 30.536 | 179.211 | 7.63 | 167.962 | 2023.68 | 26.08 | 46.811 | 6.32 | 1.326 | 4.646 | 8164.88 | 2.268 | 97.7 | 77.8 | 1316 | 23.5 | 5307.2 | 2845.7 | 2721.7 | 4062.8 | 1185.3 | 0.68427 | 5.972
2024-12-09 | 13:30 | Data | 0 | 32.507 | 30.644 | 179.256 | 7.63 | 168.053 | 2022.78 | 26.08 | 46.721 | 6.32 | 1.319 | 4.645 | 8155.84 | 1.965 | 97.7 | 77.9 | 1315 | 23.41 | 5301.3 | 2831.8 | 2726.9 | 4057.8 | 1185.3 | 0.68101 | 5.963
2024-12-09 | 13:30 | Data | 0 | 32.737 | 30.651 | 179.211 | 7.64 | 168.007 | 2026.39 | 26.08 | 46.811 | 6.31 | 1.311 | 4.635 | 8137.75 | 1.85 | 97.7 | 77.9 | 1317 | 23.36 | 5289.5 | 2835.3 | 2737.3 | 4065.1 | 1185.3 | 0.67966 | 5.947
2024-12-09 | 13:30 | Data | 0 | 32.75 | 30.658 | 179.256 | 7.63 | 168.143 | 2022.78 | 26.08 | 46.811 | 6.32 | 1.317 | 4.664 | 8137.75 | 1.985 | 97.7 | 78 | 1316 | 23.36 | 5289.5 | 2844.3 | 2744.4 | 4075.7 | 1185.3 | 0.68148 | 5.981
2024-12-09 | 13:30 | Data | 0 | 32.501 | 30.664 | 179.256 | 7.63 | 168.007 | 2022.78 | 26.08 | 46.721 | 6.31 | 1.315 | 4.662 | 8142.27 | 1.965 | 97.7 | 78 | 1315 | 23.41 | 5292.5 | 2835.6 | 2738.5 | 4061.6 | 1185.3 | 0.68044 | 5.977
2024-12-09 | 13:30 | Data | 0 | 32.723 | 30.874 | 179.302 | 7.63 | 168.053 | 2023.68 | 26.08 | 46.63 | 6.32 | 1.317 | 4.663 | 8133.23 | 1.87 | 97.7 | 78 | 1316 | 23.27 | 5286.6 | 2848.4 | 2733.8 | 4067.5 | 1185.3 | 0.6845 | 5.979
2024-12-09 | 13:30 | Data | 0 | 32.494 | 30.475 | 179.121 | 7.63 | 167.827 | 2020.97 | 26.07 | 46.54 | 6.31 | 1.315 | 4.67 | 8124.18 | 1.843 | 97.7 | 78 | 1314 | 23.27 | 5280.7 | 2842.7 | 2726.7 | 4064.9 | 1185.3 | 0.68329 | 5.987
2024-12-09 | 13:30 | Data | 0 | 32.879 | 30.664 | 179.256 | 7.63 | 167.962 | 2020.97 | 26.08 | 46.54 | 6.32 | 1.317 | 4.649 | 8133.23 | 2.167 | 97.7 | 77.9 | 1314 | 23.27 | 5286.6 | 2836.7 | 2753.7 | 4076.6 | 1185.3 | 0.68056 | 5.966
2024-12-09 | 13:30 | Data | 0 | 32.737 | 30.766 | 179.302 | 7.63 | 168.053 | 2020.97 | 26.07 | 46.54 | 6.32 | 1.313 | 4.632 | 8124.18 | 1.85 | 97.7 | 77.9 | 1313 | 23.22 | 5280.7 | 2841.9 | 2736.7 | 4066.4 | 1185.3 | 0.68227 | 5.944
2024-12-09 | 13:30 | Data | 0 | 32.71 | 30.766 | 179.166 | 7.63 | 168.053 | 2020.07 | 26.08 | 46.359 | 6.31 | 1.321 | 4.635 | 8128.7 | 2.187 | 97.7 | 77.8 | 1314 | 23.18 | 5283.7 | 2845.1 | 2727.6 | 4064.3 | 1185.3 | 0.68282 | 5.956
2024-12-09 | 13:31 | Data | 0 | 32.723 | 30.651 | 179.256 | 7.63 | 168.007 | 2020.07 | 26.08 | 46.45 | 6.32 | 1.32 | 4.639 | 8124.18 | 2.073 | 97.7 | 77.9 | 1314 | 23.32 | 5280.7 | 2852.6 | 2747.9 | 4082 | 1185.3 | 0.68198 | 5.959
2024-12-09 | 13:31 | Data | 0 | 32.852 | 30.671 | 179.347 | 7.63 | 168.053 | 2020.07 | 26.08 | 46.54 | 6.32 | 1.311 | 4.665 | 8142.27 | 1.87 | 97.7 | 78.1 | 1313 | 23.27 | 5292.5 | 2857.6 | 2750.1 | 4088.9 | 1185.3 | 0.68298 | 5.977
2024-12-09 | 13:31 | Data | 0 | 32.94 | 30.732 | 179.392 | 7.63 | 168.143 | 2023.68 | 26.08 | 46.63 | 6.32 | 1.325 | 4.658 | 8124.18 | 2.133 | 97.7 | 77.9 | 1315 | 23.27 | 5280.7 | 2841.9 | 2738.6 | 4070.5 | 1185.3 | 0.68062 | 5.983
2024-12-09 | 13:31 | Data | 0 | 32.494 | 30.766 | 179.211 | 7.63 | 168.053 | 2023.68 | 26.08 | 46.63 | 6.32 | 1.313 | 4.69 | 8124.18 | 1.931 | 97.7 | 78.1 | 1315 | 23.32 | 5280.7 | 2826.2 | 2771.9 | 4082.2 | 1185.3 | 0.6809 | 6.003
2024-12-09 | 13:31 | Data | 0 | 32.723 | 30.712 | 179.302 | 7.63 | 168.007 | 2023.68 | 26.07 | 46.45 | 6.32 | 1.315 | 4.682 | 8119.66 | 1.958 | 97.7 | 78.1 | 1315 | 23.22 | 5277.8 | 2833.5 | 2757.5 | 4078.8 | 1185.3 | 0.68153 | 5.996
2024-12-09 | 13:31 | Data | 0 | 32.717 | 30.766 | 179.347 | 7.63 | 168.007 | 2022.78 | 26.08 | 46.45 | 6.31 | 1.326 | 4.655 | 8110.61 | 2.073 | 97.7 | 77.8 | 1315 | 23.22 | 5271.9 | 2836.2 | 2751.7 | 4073.4 | 1185.3 | 0.68026 | 5.98
2024-12-09 | 13:31 | Data | 0 | 32.973 | 30.88 | 179.347 | 7.63 | 168.143 | 2020.97 | 26.08 | 46.45 | 6.31 | 1.325 | 4.655 | 8110.61 | 2.073 | 97.7 | 77.9 | 1314 | 23.27 | 5271.9 | 2827 | 2718 | 4047.4 | 1185.4 | 0.68188 | 5.982
2024-12-09 | 13:31 | Data | 0 | 32.946 | 31.103 | 179.392 | 7.63 | 168.143 | 2023.68 | 26.08 | 46.45 | 6.32 | 1.324 | 4.655 | 8115.14 | 2.052 | 97.7 | 77.9 | 1315 | 23.27 | 5274.8 | 2855.5 | 2733.5 | 4074.5 | 1185.4 | 0.68382 | 5.979
2024-12-09 | 13:31 | Data | 0 | 32.913 | 30.793 | 179.256 | 7.63 | 168.098 | 2018.26 | 26.08 | 46.54 | 6.32 | 1.324 | 4.624 | 8110.61 | 1.965 | 97.7 | 77.7 | 1312 | 23.22 | 5271.9 | 2846.7 | 2740.5 | 4070.4 | 1185.4 | 0.68067 | 5.948
2024-12-09 | 13:31 | Data | 0 | 32.501 | 30.651 | 179.256 | 7.63 | 168.098 | 2018.26 | 26.08 | 46.359 | 6.32 | 1.323 | 4.625 | 8097.05 | 1.843 | 97.7 | 77.8 | 1312 | 23.27 | 5263.1 | 2850 | 2731.8 | 4072.8 | 1185.4 | 0.6835 | 5.947
2024-12-09 | 13:31 | Data | 0 | 32.75 | 30.658 | 179.211 | 7.63 | 167.962 | 2018.26 | 26.08 | 46.54 | 6.31 | 1.317 | 4.633 | 8088 | 2.073 | 97.7 | 77.9 | 1312 | 23.27 | 5257.2 | 2834.8 | 2745.9 | 4066.2 | 1185.4 | 0.68065 | 5.95
2024-12-09 | 13:31 | Data | 0 | 32.723 | 30.874 | 179.347 | 7.63 | 168.007 | 2020.97 | 26.08 | 46.54 | 6.32 | 1.323 | 4.637 | 8097.05 | 1.857 | 97.7 | 77.8 | 1314 | 23.22 | 5263.1 | 2846.7 | 2727.4 | 4067.8 | 1185.4 | 0.68246 | 5.96
2024-12-09 | 13:31 | Data | 0 | 32.723 | 30.651 | 179.347 | 7.63 | 168.053 | 2020.07 | 26.08 | 46.54 | 6.31 | 1.32 | 4.647 | 8074.44 | 2.066 | 97.7 | 77.9 | 1314 | 23.27 | 5248.4 | 2843.2 | 2750.9 | 4075.7 | 1185.4 | 0.68141 | 5.968
2024-12-09 | 13:31 | Data | 0 | 32.838 | 31.103 | 179.347 | 7.64 | 168.053 | 2018.26 | 26.08 | 46.45 | 6.31 | 1.322 | 4.685 | 8101.57 | 1.809 | 97.7 | 78 | 1312 | 23.22 | 5266 | 2838.8 | 2737.8 | 4067.9 | 1185.4 | 0.68096 | 6.007
2024-12-09 | 13:31 | Data | 0 | 32.953 | 30.88 | 179.347 | 7.63 | 168.143 | 2023.68 | 26.08 | 46.45 | 6.31 | 1.314 | 4.683 | 8083.48 | 2.073 | 97.7 | 78.1 | 1315 | 23.27 | 5254.3 | 2847 | 2741.8 | 4079.8 | 1185.4 | 0.68333 | 5.997
2024-12-09 | 13:31 | Data | 0 | 32.717 | 30.651 | 179.302 | 7.63 | 168.188 | 2019.16 | 26.07 | 46.54 | 6.32 | 1.321 | 4.652 | 8092.52 | 2.073 | 97.7 | 77.9 | 1312 | 23.27 | 5260.1 | 2834.8 | 2751.6 | 4074.2 | 1185.4 | 0.67926 | 5.975
2024-12-09 | 13:31 | Data | 0 | 32.723 | 30.475 | 179.302 | 7.63 | 168.098 | 2018.26 | 26.08 | 46.45 | 6.32 | 1.315 | 4.64 | 8092.52 | 2.187 | 97.7 | 77.9 | 1312 | 23.22 | 5260.1 | 2846.2 | 2759.8 | 4090.6 | 1185.4 | 0.67846 | 5.957
2024-12-09 | 13:31 | Data | 0 | 32.399 | 30.536 | 179.166 | 7.64 | 168.007 | 2018.26 | 26.08 | 46.54 | 6.32 | 1.32 | 4.648 | 8101.57 | 1.965 | 97.7 | 77.9 | 1312 | 23.27 | 5266 | 2830.1 | 2745.4 | 4069.7 | 1185.4 | 0.6798 | 5.969
2024-12-09 | 13:32 | Data | 0 | 32.723 | 30.651 | 179.347 | 7.63 | 168.053 | 2017.35 | 26.08 | 46.45 | 6.32 | 1.323 | 4.646 | 8097.05 | 2.073 | 97.7 | 77.8 | 1312 | 23.27 | 5263.1 | 2847.3 | 2721.8 | 4063.2 | 1185.4 | 0.68432 | 5.97
2024-12-09 | 13:32 | Data | 0 | 32.42 | 30.853 | 179.528 | 7.63 | 168.098 | 2018.26 | 26.08 | 46.54 | 6.31 | 1.325 | 4.639 | 8088 | 2.052 | 97.7 | 77.8 | 1312 | 23.27 | 5257.2 | 2847.7 | 2742.2 | 4075.9 | 1185.4 | 0.68408 | 5.964
2024-12-09 | 13:32 | Data | 0 | 32.71 | 30.664 | 179.256 | 7.63 | 168.053 | 2020.07 | 26.08 | 46.54 | 6.32 | 1.314 | 4.66 | 8097.05 | 2.046 | 97.7 | 78 | 1313 | 23.27 | 5263.1 | 2837.8 | 2742.9 | 4068.5 | 1185.4 | 0.68108 | 5.973
2024-12-09 | 13:32 | Data | 0 | 32.669 | 30.658 | 179.256 | 7.63 | 167.962 | 2019.16 | 26.08 | 46.54 | 6.32 | 1.32 | 4.671 | 8101.57 | 1.992 | 97.7 | 78 | 1312 | 23.22 | 5266 | 2839.9 | 2715.8 | 4047.2 | 1185.4 | 0.68516 | 5.989
2024-12-09 | 13:32 | Data | 0 | 32.521 | 30.651 | 179.256 | 7.63 | 168.053 | 2013.74 | 26.08 | 46.54 | 6.32 | 1.322 | 4.627 | 8115.14 | 1.85 | 97.7 | 77.8 | 1309 | 23.27 | 5274.8 | 2836.6 | 2745.3 | 4073.1 | 1185.4 | 0.67995 | 5.95
2024-12-09 | 13:32 | Data | 0 | 32.73 | 31.022 | 179.211 | 7.63 | 168.053 | 2019.16 | 26.08 | 46.45 | 6.32 | 1.314 | 4.629 | 8110.61 | 1.951 | 97.7 | 77.9 | 1312 | 23.22 | 5271.9 | 2838.1 | 2732.9 | 4064.9 | 1185.4 | 0.68187 | 5.943
2024-12-09 | 13:32 | Data | 0 | 32.777 | 30.658 | 179.256 | 7.63 | 168.143 | 2018.26 | 26.07 | 46.54 | 6.31 | 1.327 | 4.625 | 8110.61 | 1.904 | 97.7 | 77.7 | 1312 | 23.22 | 5271.9 | 2838.6 | 2755.4 | 4081.5 | 1185.4 | 0.67964 | 5.951
2024-12-09 | 13:32 | Data | 0 | 32.919 | 30.766 | 179.166 | 7.63 | 168.053 | 2015.55 | 26.08 | 46.54 | 6.31 | 1.324 | 4.638 | 8110.61 | 2.1 | 97.7 | 77.8 | 1310 | 23.27 | 5271.9 | 2845.6 | 2734.6 | 4064.1 | 1185.4 | 0.682 | 5.961
2024-12-09 | 13:32 | Data | 0 | 32.777 | 30.705 | 179.211 | 7.63 | 168.143 | 2015.55 | 26.08 | 46.54 | 6.32 | 1.313 | 4.655 | 8101.57 | 1.87 | 97.7 | 78 | 1310 | 23.13 | 5266 | 2840.4 | 2732.5 | 4068.3 | 1185.4 | 0.67985 | 5.969
2024-12-09 | 13:32 | Data | 0 | 32.669 | 30.563 | 179.347 | 7.63 | 168.007 | 2009.22 | 26.08 | 46.45 | 6.31 | 1.313 | 4.649 | 8106.09 | 2.066 | 97.7 | 78 | 1306 | 23.22 | 5269 | 2843.2 | 2752 | 4080.5 | 1185.4 | 0.68068 | 5.963
2024-12-09 | 13:32 | Data | 0 | 32.717 | 30.718 | 179.256 | 7.63 | 168.053 | 2010.12 | 26.08 | 46.54 | 6.32 | 1.313 | 4.659 | 8115.14 | 2.208 | 97.7 | 78 | 1306 | 23.22 | 5274.8 | 2855.3 | 2742.5 | 4080.7 | 1185.4 | 0.68403 | 5.972
2024-12-09 | 13:32 | Data | 0 | 32.494 | 30.82 | 179.211 | 7.63 | 168.007 | 2014.64 | 26.08 | 46.63 | 6.31 | 1.307 | 4.657 | 8128.7 | 1.877 | 97.7 | 78.1 | 1310 | 23.27 | 5283.7 | 2847.4 | 2739.6 | 4074.3 | 1185.4 | 0.68389 | 5.966
2024-12-09 | 13:32 | Data | 0 | 32.865 | 30.664 | 179.302 | 7.63 | 168.143 | 2008.32 | 26.08 | 46.54 | 6.32 | 1.32 | 4.642 | 8124.18 | 1.884 | 97.7 | 77.9 | 1307 | 23.27 | 5280.7 | 2843.9 | 2731 | 4069.6 | 1185.4 | 0.68183 | 5.962
2024-12-09 | 13:32 | Data | 0 | 33.162 | 30.88 | 179.483 | 7.63 | 168.188 | 2015.55 | 26.09 | 46.54 | 6.31 | 1.315 | 4.642 | 8128.7 | 2.093 | 97.7 | 77.9 | 1310 | 23.27 | 5283.7 | 2853.7 | 2734.1 | 4072.7 | 1185.4 | 0.68388 | 5.957
2024-12-09 | 13:32 | Data | 0 | 33.034 | 31.103 | 179.528 | 7.63 | 168.143 | 2018.26 | 26.09 | 46.45 | 6.33 | 1.318 | 4.632 | 8133.23 | 2.059 | 97.7 | 77.9 | 1311 | 23.32 | 5286.6 | 2851.7 | 2730 | 4067.6 | 1185.4 | 0.68455 | 5.95
2024-12-09 | 13:32 | Data | 0 | 32.514 | 30.651 | 179.347 | 7.63 | 168.098 | 2018.26 | 26.08 | 46.54 | 6.31 | 1.326 | 4.649 | 8128.7 | 1.85 | 97.7 | 77.8 | 1311 | 23.27 | 5283.7 | 2841.3 | 2743.5 | 4067.3 | 1185.4 | 0.68179 | 5.974
2024-12-09 | 13:32 | Data | 0 | 32.717 | 30.651 | 179.211 | 7.63 | 168.053 | 2017.35 | 26.09 | 46.721 | 6.32 | 1.326 | 4.627 | 8133.23 | 1.958 | 97.7 | 77.7 | 1311 | 23.36 | 5286.6 | 2842.8 | 2672.9 | 4026.6 | 1185.4 | 0.69012 | 5.952
2024-12-09 | 13:33 | Data | 0 | 32.494 | 30.597 | 179.211 | 7.63 | 167.962 | 2017.35 | 26.08 | 46.721 | 6.32 | 1.329 | 4.628 | 8124.18 | 2.073 | 97.7 | 77.7 | 1312 | 23.36 | 5280.7 | 2850.6 | 2747.3 | 4080.9 | 1185.4 | 0.68086 | 5.957
2024-12-09 | 13:33 | Data | 0 | 32.669 | 30.826 | 179.347 | 7.63 | 168.098 | 2019.16 | 26.08 | 46.721 | 6.32 | 1.322 | 4.641 | 8133.23 | 2.005 | 97.7 | 77.8 | 1312 | 23.32 | 5286.6 | 2823.9 | 2744.2 | 4059.2 | 1185.4 | 0.6774 | 5.963
2024-12-09 | 13:33 | Data | 0 | 32.892 | 30.685 | 179.392 | 7.63 | 168.233 | 2018.26 | 26.08 | 46.54 | 6.33 | 1.31 | 4.665 | 8133.23 | 1.911 | 97.7 | 78.1 | 1312 | 23.27 | 5286.6 | 2832.8 | 2738.3 | 4066.3 | 1185.4 | 0.67932 | 5.974
2024-12-09 | 13:33 | Data | 0 | 32.919 | 30.766 | 179.302 | 7.63 | 168.053 | 2020.97 | 26.08 | 46.63 | 6.31 | 1.312 | 4.659 | 8137.75 | 2.086 | 97.7 | 78 | 1314 | 23.41 | 5289.5 | 2849.9 | 2738.4 | 4072.9 | 1185.4 | 0.68317 | 5.974
2024-12-09 | 13:33 | Data | 0 | 32.946 | 31.096 | 179.528 | 7.63 | 168.053 | 2024.58 | 26.08 | 46.721 | 6.31 | 1.315 | 4.662 | 8124.18 | 1.897 | 97.7 | 78 | 1316 | 23.32 | 5280.7 | 2844.2 | 2744.9 | 4076.4 | 1185.4 | 0.6806 | 5.977
2024-12-09 | 13:33 | Data | 0 | 32.548 | 30.651 | 179.166 | 7.63 | 168.007 | 2017.35 | 26.08 | 46.45 | 6.31 | 1.324 | 4.651 | 8137.75 | 1.85 | 97.7 | 77.9 | 1311 | 23.27 | 5289.5 | 2838.9 | 2732.1 | 4059 | 1185.4 | 0.68314 | 5.974
2024-12-09 | 13:33 | Data | 0 | 32.723 | 30.961 | 179.347 | 7.63 | 168.143 | 2015.55 | 26.08 | 46.45 | 6.32 | 1.322 | 4.62 | 8137.75 | 2.046 | 97.7 | 77.7 | 1310 | 23.27 | 5289.5 | 2829.5 | 2757.4 | 4074.7 | 1185.4 | 0.67623 | 5.942
2024-12-09 | 13:33 | Data | 0 | 32.953 | 30.934 | 179.483 | 7.63 | 168.188 | 2017.35 | 26.08 | 46.54 | 6.31 | 1.314 | 4.641 | 8137.75 | 1.965 | 97.7 | 77.9 | 1311 | 23.32 | 5289.5 | 2843 | 2736.9 | 4071.1 | 1185.4 | 0.68141 | 5.955
2024-12-09 | 13:33 | Data | 0 | 32.642 | 30.658 | 179.347 | 7.63 | 168.098 | 2018.26 | 26.08 | 46.45 | 6.32 | 1.31 | 4.674 | 8155.84 | 1.877 | 97.7 | 78.1 | 1312 | 23.22 | 5301.3 | 2821.9 | 2746.7 | 4062.6 | 1185.5 | 0.67713 | 5.985
2024-12-09 | 13:33 | Data | 0 | 32.426 | 30.563 | 179.528 | 7.63 | 168.098 | 2016.45 | 26.08 | 46.54 | 6.32 | 1.322 | 4.616 | 8137.75 | 1.89 | 97.7 | 77.7 | 1312 | 23.27 | 5289.5 | 2844.6 | 2761.5 | 4071.6 | 1185.5 | 0.68051 | 5.94
2024-12-09 | 13:33 | Data | 0 | 32.501 | 30.651 | 179.256 | 7.63 | 168.098 | 2019.16 | 26.08 | 46.45 | 6.32 | 1.314 | 4.635 | 8128.7 | 1.843 | 97.7 | 77.9 | 1312 | 23.27 | 5283.7 | 2839.5 | 2731.9 | 4065 | 1185.5 | 0.68138 | 5.949
2024-12-09 | 13:33 | Data | 0 | 32.636 | 30.651 | 179.392 | 7.64 | 168.143 | 2013.74 | 26.08 | 46.54 | 6.31 | 1.312 | 4.639 | 8110.61 | 1.863 | 97.7 | 77.9 | 1310 | 23.27 | 5271.9 | 2847.3 | 2750.4 | 4076.9 | 1185.5 | 0.68303 | 5.952
2024-12-09 | 13:33 | Data | 0 | 32.791 | 30.651 | 179.392 | 7.63 | 168.143 | 2015.55 | 26.08 | 46.359 | 6.31 | 1.314 | 4.635 | 8128.7 | 1.877 | 97.7 | 77.9 | 1310 | 23.22 | 5283.7 | 2848.4 | 2743.5 | 4077.3 | 1185.5 | 0.6838 | 5.954
2024-12-09 | 13:33 | Data | 0 | 32.723 | 30.651 | 179.347 | 7.63 | 168.007 | 2015.55 | 26.07 | 46.54 | 6.32 | 1.312 | 4.643 | 8124.18 | 2.073 | 97.7 | 78 | 1310 | 23.27 | 5280.7 | 2824.9 | 2745.5 | 4082.4 | 1185.5 | 0.68037 | 5.955
2024-12-09 | 13:33 | Data | 0 | 32.946 | 31.299 | 179.483 | 7.63 | 168.143 | 2015.55 | 26.08 | 46.63 | 6.31 | 1.328 | 4.649 | 8110.61 | 1.904 | 97.7 | 77.8 | 1310 | 23.27 | 5271.9 | 2832.1 | 2748.4 | 4070.9 | 1185.5 | 0.67867 | 5.977
2024-12-09 | 13:33 | Data | 0 | 33.041 | 30.988 | 179.347 | 7.63 | 168.098 | 2018.26 | 26.09 | 46.45 | 6.31 | 1.319 | 4.65 | 8137.75 | 2.046 | 97.7 | 77.9 | 1312 | 23.13 | 5289.5 | 2834.3 | 2736.1 | 4063 | 1185.5 | 0.68114 | 5.968
2024-12-09 | 13:33 | Data | 0 | 32.899 | 30.88 | 179.302 | 7.63 | 168.098 | 2019.16 | 26.08 | 46.45 | 6.32 | 1.315 | 4.645 | 8124.18 | 2.066 | 97.7 | 77.9 | 1312 | 23.27 | 5280.7 | 2843.8 | 2747.4 | 4076.9 | 1185.5 | 0.68162 | 5.96
2024-12-09 | 13:33 | Data | 0 | 33.149 | 30.887 | 179.483 | 7.63 | 168.143 | 2017.35 | 26.09 | 46.45 | 6.32 | 1.314 | 4.654 | 8124.18 | 2.1 | 97.7 | 78 | 1312 | 23.27 | 5280.7 | 2841.1 | 2740 | 4071.7 | 1185.5 | 0.68066 | 5.966
2024-12-09 | 13:34 | Data | 0 | 32.717 | 30.874 | 179.392 | 7.63 | 168.053 | 1918.84 | 26.08 | 46.45 | 6.32 | 1.31 | 4.635 | 8124.18 | 2.019 | 97.6 | 78 | 1247 | 23.22 | 5280.7 | 2839.3 | 2743.7 | 4073.1 | 1185.5 | 0.68012 | 5.945
2024-12-09 | 13:34 | Data | 0 | 32.534 | 30.651 | 179.302 | 7.63 | 168.098 | 1909.8 | 26.09 | 46.45 | 6.32 | 1.312 | 4.647 | 8124.18 | 1.843 | 97.6 | 78 | 1241 | 23.22 | 5280.7 | 2851.2 | 2745.6 | 4081.1 | 1185.5 | 0.6826 | 5.96
2024-12-09 | 13:34 | Data | 0 | 32.514 | 30.759 | 179.483 | 7.63 | 168.188 | 2001.99 | 26.07 | 46.63 | 6.31 | 1.318 | 4.628 | 8124.18 | 1.803 | 97.7 | 77.8 | 1301 | 23.22 | 5280.7 | 2849.6 | 2742.6 | 4076.8 | 1185.5 | 0.68272 | 5.947
2024-12-09 | 13:34 | Data | 0 | 32.622 | 30.867 | 179.347 | 7.63 | 168.143 | 1999.28 | 26.07 | 46.63 | 6.32 | 1.326 | 4.633 | 8115.14 | 1.87 | 97.7 | 77.8 | 1300 | 23.32 | 5274.8 | 2830.3 | 2726.3 | 4054.8 | 1185.5 | 0.68133 | 5.958
2024-12-09 | 13:34 | Data | 0 | 32.723 | 30.772 | 179.528 | 7.63 | 168.143 | 2001.08 | 26.08 | 46.54 | 6.32 | 1.31 | 4.657 | 8110.61 | 2.059 | 97.7 | 78.1 | 1301 | 23.22 | 5271.9 | 2836.1 | 2742.1 | 4065.6 | 1185.5 | 0.68074 | 5.968
2024-12-09 | 13:34 | Data | 0 | 33.095 | 30.833 | 179.483 | 7.63 | 168.233 | 2008.32 | 26.08 | 46.54 | 6.31 | 1.311 | 4.638 | 8173.92 | 2.019 | 97.7 | 77.9 | 1305 | 23.22 | 5313.1 | 2839.9 | 2741.4 | 4073.3 | 1185.5 | 0.68044 | 5.95
2024-12-09 | 13:34 | Data | 0 | 32.723 | 30.658 | 179.302 | 7.63 | 168.188 | 2015.55 | 26.1 | 46.54 | 6.33 | 1.309 | 4.607 | 8169.4 | 2.052 | 97.7 | 77.9 | 1310 | 23.27 | 5310.1 | 2847.7 | 2748.9 | 4079.2 | 1185.5 | 0.68127 | 5.915
2024-12-09 | 13:34 | Data | 0 | 32.717 | 30.867 | 179.302 | 7.63 | 168.098 | 2015.55 | 26.08 | 46.45 | 6.32 | 1.312 | 4.654 | 8169.4 | 2.066 | 97.7 | 78 | 1310 | 23.27 | 5310.1 | 2831.1 | 2743 | 4065.2 | 1185.5 | 0.68011 | 5.966
2024-12-09 | 13:34 | Data | 0 | 32.892 | 30.664 | 179.347 | 7.63 | 168.188 | 2015.55 | 26.09 | 46.45 | 6.31 | 1.317 | 4.645 | 8169.4 | 1.857 | 97.7 | 77.9 | 1310 | 23.22 | 5310.1 | 2833.8 | 2713.1 | 4046.1 | 1185.5 | 0.68403 | 5.962
2024-12-09 | 13:34 | Data | 0 | 32.75 | 30.772 | 179.302 | 7.63 | 168.053 | 2016.45 | 26.09 | 46.45 | 6.32 | 1.311 | 4.659 | 8169.4 | 2.059 | 97.7 | 78 | 1310 | 23.22 | 5310.1 | 2838.5 | 2715 | 4047.9 | 1185.5 | 0.68391 | 5.97
2024-12-09 | 13:34 | Data | 0 | 32.73 | 30.651 | 179.347 | 7.63 | 168.007 | 2013.74 | 26.08 | 46.45 | 6.31 | 1.32 | 4.631 | 8182.97 | 1.951 | 97.7 | 77.8 | 1308 | 23.22 | 5318.9 | 2837.7 | 2731.4 | 4065.4 | 1185.5 | 0.68232 | 5.95
2024-12-09 | 13:34 | Data | 0 | 32.838 | 31.103 | 179.347 | 7.63 | 168.098 | 2012.83 | 26.09 | 46.54 | 6.32 | 1.324 | 4.655 | 8173.92 | 2.019 | 97.7 | 77.9 | 1308 | 23.32 | 5313.1 | 2851.3 | 2748.8 | 4082.6 | 1185.5 | 0.68196 | 5.979
2024-12-09 | 13:34 | Data | 0 | 32.339 | 30.644 | 179.392 | 7.63 | 168.053 | 2012.83 | 26.08 | 46.54 | 6.31 | 1.32 | 4.662 | 8196.54 | 1.809 | 97.7 | 77.9 | 1309 | 23.27 | 5327.7 | 2851.9 | 2719.5 | 4060.2 | 1185.5 | 0.68624 | 5.981
2024-12-09 | 13:34 | Data | 0 | 32.75 | 30.867 | 179.302 | 7.63 | 168.143 | 2011.93 | 26.09 | 46.45 | 6.32 | 1.32 | 4.645 | 8187.49 | 1.877 | 97.7 | 77.8 | 1308 | 23.27 | 5321.9 | 2833.6 | 2753.2 | 4073.4 | 1185.5 | 0.67822 | 5.965
2024-12-09 | 13:34 | Data | 0 | 32.642 | 30.88 | 179.392 | 7.63 | 168.098 | 2014.64 | 26.09 | 46.359 | 6.31 | 1.32 | 4.646 | 8192.01 | 1.681 | 97.7 | 77.9 | 1310 | 23.22 | 5324.8 | 2844.7 | 2740.4 | 4072.8 | 1185.5 | 0.68214 | 5.967
2024-12-09 | 13:34 | Data | 0 | 32.953 | 30.88 | 179.573 | 7.63 | 168.188 | 2015.55 | 26.08 | 46.54 | 6.31 | 1.32 | 4.645 | 8201.06 | 1.89 | 97.7 | 77.9 | 1310 | 23.32 | 5330.7 | 2837.4 | 2749.8 | 4071.4 | 1185.5 | 0.6809 | 5.965
2024-12-09 | 13:34 | Data | 0 | 33.176 | 30.793 | 179.483 | 7.63 | 168.188 | 2016.45 | 26.08 | 46.721 | 6.32 | 1.32 | 4.654 | 8210.1 | 2.073 | 97.7 | 77.9 | 1310 | 23.5 | 5336.6 | 2833.9 | 2713.5 | 4043.1 | 1185.5 | 0.68422 | 5.974
2024-12-09 | 13:34 | Data | 0 | 32.615 | 30.658 | 179.302 | 7.63 | 168.098 | 2018.26 | 26.09 | 46.45 | 6.32 | 1.32 | 4.649 | 8196.54 | 2.032 | 97.7 | 77.9 | 1312 | 23.22 | 5327.7 | 2833.6 | 2726.6 | 4055.2 | 1185.5 | 0.68259 | 5.97
2024-12-09 | 13:35 | Data | 0 | 32.75 | 30.88 | 179.483 | 7.63 | 168.188 | 2012.83 | 26.08 | 46.45 | 6.32 | 1.312 | 4.666 | 8178.45 | 1.965 | 97.7 | 78 | 1308 | 23.27 | 5316 | 2842.9 | 2719.2 | 4055.5 | 1185.5 | 0.68412 | 5.979
2024-12-09 | 13:35 | Data | 0 | 33.169 | 30.907 | 179.573 | 7.63 | 168.188 | 2017.35 | 26.09 | 46.721 | 6.32 | 1.306 | 4.636 | 8164.88 | 2.1 | 97.7 | 78 | 1312 | 23.36 | 5307.2 | 2852.9 | 2726.7 | 4066.1 | 1185.5 | 0.68497 | 5.943
2024-12-09 | 13:35 | Data | 0 | 32.528 | 30.826 | 179.347 | 7.63 | 168.188 | 2017.35 | 26.1 | 46.54 | 6.32 | 1.319 | 4.649 | 8173.92 | 1.857 | 97.7 | 77.9 | 1311 | 23.22 | 5313.1 | 2843.4 | 2737.4 | 4064.6 | 1185.5 | 0.68324 | 5.968
2024-12-09 | 13:35 | Data | 0 | 32.723 | 30.874 | 179.483 | 7.63 | 168.098 | 2020.07 | 26.09 | 46.45 | 6.32 | 1.317 | 4.667 | 8182.97 | 1.897 | 97.7 | 78 | 1314 | 23.27 | 5318.9 | 2826.8 | 2735.7 | 4059.1 | 1185.5 | 0.67915 | 5.983
2024-12-09 | 13:35 | Data | 0 | 32.946 | 30.718 | 179.302 | 7.63 | 168.143 | 2020.07 | 26.09 | 46.721 | 6.31 | 1.318 | 4.632 | 8182.97 | 2.059 | 97.7 | 77.8 | 1314 | 23.36 | 5318.9 | 2834.1 | 2732.6 | 4057.9 | 1185.5 | 0.68183 | 5.95
2024-12-09 | 13:35 | Data | 0 | 32.723 | 30.475 | 179.347 | 7.63 | 168.188 | 2020.97 | 26.09 | 46.63 | 6.32 | 1.32 | 4.635 | 8169.4 | 2.066 | 97.7 | 77.8 | 1314 | 23.32 | 5310.1 | 2834.2 | 2731.6 | 4056.1 | 1185.5 | 0.68107 | 5.955
2024-12-09 | 13:35 | Data | 0 | 32.514 | 30.698 | 179.302 | 7.63 | 168.098 | 2020.97 | 26.09 | 46.45 | 6.31 | 1.326 | 4.651 | 8169.4 | 1.816 | 97.7 | 77.8 | 1314 | 23.27 | 5310.1 | 2851.3 | 2732.3 | 4069.9 | 1185.5 | 0.68536 | 5.978
2024-12-09 | 13:35 | Data | 0 | 32.926 | 30.88 | 179.302 | 7.63 | 168.143 | 2020.07 | 26.09 | 46.54 | 6.32 | 1.324 | 4.641 | 8178.45 | 2.066 | 97.7 | 77.8 | 1313 | 23.27 | 5316 | 2832 | 2737.7 | 4057.7 | 1185.5 | 0.68182 | 5.965
2024-12-09 | 13:35 | Data | 0 | 32.568 | 30.766 | 179.256 | 7.63 | 168.233 | 2015.55 | 26.08 | 46.45 | 6.32 | 1.326 | 4.615 | 8178.45 | 2.025 | 97.7 | 77.7 | 1310 | 23.18 | 5316 | 2835 | 2749.8 | 4070 | 1185.5 | 0.68118 | 5.941
2024-12-09 | 13:35 | Data | 0 | 32.723 | 30.766 | 179.256 | 7.63 | 168.098 | 2016.45 | 26.09 | 46.45 | 6.31 | 1.313 | 4.645 | 8169.4 | 2.073 | 97.7 | 78 | 1310 | 23.27 | 5310.1 | 2846.9 | 2747 | 4077.5 | 1185.5 | 0.68219 | 5.958
2024-12-09 | 13:35 | Data | 0 | 33.007 | 30.793 | 179.483 | 7.63 | 168.188 | 2015.55 | 26.08 | 46.54 | 6.32 | 1.321 | 4.627 | 8169.4 | 1.985 | 97.7 | 77.8 | 1311 | 23.27 | 5310.1 | 2825.1 | 2728.6 | 4053.8 | 1185.6 | 0.67973 | 5.949
2024-12-09 | 13:35 | Data | 0 | 32.838 | 30.664 | 179.302 | 7.63 | 168.143 | 2015.55 | 26.08 | 46.54 | 6.32 | 1.32 | 4.665 | 8115.14 | 2.221 | 97.7 | 77.9 | 1311 | 23.27 | 5274.8 | 2826.1 | 2704.8 | 4032.7 | 1185.6 | 0.68445 | 5.984
2024-12-09 | 13:35 | Data | 0 | 32.825 | 30.651 | 179.256 | 7.63 | 168.098 | 2017.35 | 26.09 | 46.54 | 6.31 | 1.32 | 4.674 | 8101.57 | 2.1 | 97.7 | 78 | 1311 | 23.32 | 5266 | 2826.4 | 2734.9 | 4054.2 | 1185.6 | 0.6807 | 5.995
2024-12-09 | 13:35 | Data | 0 | 33.183 | 31.137 | 179.618 | 7.63 | 168.324 | 2020.97 | 26.09 | 46.359 | 6.31 | 1.324 | 4.632 | 8106.09 | 2.025 | 97.7 | 77.8 | 1314 | 23.18 | 5269 | 2836.2 | 2753.2 | 4074.9 | 1185.6 | 0.68057 | 5.955
2024-12-09 | 13:35 | Data | 0 | 32.94 | 30.88 | 179.347 | 7.63 | 168.188 | 2020.07 | 26.09 | 46.45 | 6.32 | 1.322 | 4.654 | 8101.57 | 1.897 | 97.7 | 77.9 | 1313 | 23.27 | 5266 | 2859.8 | 2732.6 | 4075.4 | 1185.6 | 0.68419 | 5.978
2024-12-09 | 13:35 | Data | 0 | 32.953 | 30.718 | 179.392 | 7.63 | 168.233 | 2022.78 | 26.09 | 46.54 | 6.32 | 1.326 | 4.68 | 8088 | 2.174 | 97.7 | 77.9 | 1315 | 23.18 | 5257.2 | 2841.7 | 2749.7 | 4074.3 | 1185.6 | 0.68061 | 6.007
2024-12-09 | 13:35 | Data | 0 | 32.811 | 31.245 | 179.618 | 7.63 | 168.143 | 2023.68 | 26.08 | 46.54 | 6.32 | 1.324 | 4.653 | 8101.57 | 1.938 | 97.7 | 77.8 | 1315 | 23.32 | 5266 | 2829.9 | 2737.2 | 4058.9 | 1185.6 | 0.68059 | 5.977
2024-12-09 | 13:35 | Data | 0 | 32.723 | 31.076 | 179.528 | 7.63 | 168.233 | 2018.26 | 26.08 | 46.45 | 6.31 | 1.318 | 4.682 | 8097.05 | 1.924 | 97.7 | 78 | 1312 | 23.27 | 5263.1 | 2846.1 | 2722 | 4059.7 | 1185.6 | 0.68492 | 5.999
2024-12-09 | 13:36 | Data | 0 | 33.156 | 31.11 | 179.573 | 7.63 | 168.324 | 2018.26 | 26.09 | 46.45 | 6.32 | 1.317 | 4.685 | 7717.18 | 2.059 | 97.7 | 78.1 | 1312 | 23.22 | 5016.2 | 2832.7 | 2718.5 | 4046.2 | 1185.6 | 0.68296 | 6.002
2024-12-09 | 13:36 | Data | 0 | 33.176 | 30.995 | 179.483 | 7.63 | 168.188 | 2018.26 | 26.09 | 46.45 | 6.31 | 1.32 | 4.656 | 8336.72 | 1.965 | 97.7 | 77.9 | 1312 | 23.22 | 5418.9 | 2854.1 | 2731.5 | 4071.9 | 1185.6 | 0.68333 | 5.977
2024-12-09 | 13:36 | Data | 0 | 32.838 | 30.658 | 179.483 | 7.63 | 168.188 | 2015.55 | 26.09 | 46.45 | 6.32 | 1.321 | 4.633 | 8341.25 | 2.052 | 97.7 | 77.8 | 1310 | 23.22 | 5421.8 | 2836 | 2721.4 | 4055.1 | 1185.6 | 0.6822 | 5.955
2024-12-09 | 13:36 | Data | 0 | 32.737 | 30.739 | 179.347 | 7.63 | 168.143 | 2013.74 | 26.08 | 46.45 | 6.31 | 1.332 | 4.629 | 8318.64 | 1.985 | 97.7 | 77.7 | 1309 | 23.22 | 5407.1 | 2841.9 | 2713.3 | 4055.5 | 1185.6 | 0.68439 | 5.96
2024-12-09 | 13:36 | Data | 0 | 32.94 | 31.11 | 177.718 | 7.63 | 166.561 | 2018.26 | 26.09 | 46.45 | 6.32 | 1.327 | 4.652 | 8305.07 | 2.012 | 97.7 | 77.8 | 1312 | 23.27 | 5398.3 | 2816.4 | 2721.7 | 4045 | 1185.6 | 0.67892 | 5.979
2024-12-09 | 13:36 | Data | 0 | 33.297 | 31.393 | 168.265 | 7.63 | 158.11 | 2017.35 | 26.08 | 46.721 | 6.32 | 1.314 | 4.557 | 8309.59 | 1.944 | 97.7 | 77.6 | 1311 | 23.22 | 5401.2 | 2750.8 | 2664.4 | 3958.8 | 1185.6 | 0.67866 | 5.872
2024-12-09 | 13:36 | Data | 0 | 33.804 | 32.055 | 160.394 | 7.63 | 150.834 | 2016.45 | 26.08 | 46.269 | 6.32 | 1.275 | 4.373 | 8286.98 | 1.789 | 97.7 | 77.4 | 1311 | 23.13 | 5386.5 | 2681.6 | 2585.4 | 3858.6 | 1185.6 | 0.67937 | 5.649
2024-12-09 | 13:36 | Data | 0 | 34.128 | 32.352 | 154.017 | 7.63 | 145.094 | 2014.64 | 26.09 | 46.179 | 6.31 | 1.253 | 4.219 | 8273.41 | 1.499 | 97.7 | 77.1 | 1308 | 23.09 | 5377.7 | 2604.9 | 2540.7 | 3774 | 1185.6 | 0.67607 | 5.474
2024-12-09 | 13:36 | Data | 0 | 34.33 | 32.784 | 149.086 | 7.63 | 140.439 | 2015.55 | 26.1 | 46.269 | 6.33 | 1.23 | 4.044 | 8264.37 | 1.357 | 97.7 | 76.7 | 1310 | 23.09 | 5371.8 | 2556.9 | 2497.5 | 3713.9 | 1185.6 | 0.67069 | 5.276
2024-12-09 | 13:36 | Data | 0 | 34.134 | 32.94 | 145.061 | 7.63 | 136.824 | 2014.64 | 26.09 | 46.721 | 6.32 | 1.222 | 3.952 | 8237.24 | 1.289 | 97.7 | 76.4 | 1310 | 23.36 | 5354.2 | 2519 | 2476.6 | 3668 | 1185.6 | 0.67212 | 5.173
2024-12-09 | 13:36 | Data | 0 | 34.729 | 33.23 | 141.985 | 7.63 | 133.977 | 2020.07 | 26.1 | 47.443 | 6.33 | 1.201 | 3.851 | 8219.15 | 1.31 | 97.7 | 76.2 | 1313 | 23.72 | 5342.4 | 2494.9 | 2447.1 | 3639.2 | 1185.6 | 0.66955 | 5.052
2024-12-09 | 13:36 | Data | 0 | 34.56 | 33.183 | 139.497 | 7.63 | 131.717 | 2020.97 | 26.1 | 47.894 | 6.33 | 1.189 | 3.761 | 8201.06 | 1.384 | 97.6 | 76 | 1314 | 23.95 | 5330.7 | 2474.7 | 2434.1 | 3611.1 | 1185.6 | 0.66977 | 4.95
2024-12-09 | 13:36 | Data | 0 | 34.479 | 33.196 | 137.778 | 7.63 | 130.18 | 2021.87 | 26.11 | 48.707 | 6.34 | 1.183 | 3.694 | 8155.84 | 1.31 | 97.6 | 75.7 | 1314 | 24.35 | 5301.3 | 2466.8 | 2441.2 | 3605.9 | 1185.6 | 0.66975 | 4.876
2024-12-09 | 13:36 | Data | 0 | 34.769 | 33.412 | 136.421 | 7.63 | 129.005 | 2020.07 | 26.11 | 49.519 | 6.36 | 1.179 | 3.641 | 7830.24 | 1.377 | 97.5 | 75.5 | 1313 | 24.8 | 5089.7 | 2439.4 | 2430.9 | 3592.6 | 1185.6 | 0.66225 | 4.821
2024-12-09 | 13:36 | Data | 0 | 34.546 | 33.412 | 135.517 | 7.63 | 128.011 | 2018.26 | 26.11 | 50.242 | 6.36 | 1.169 | 3.614 | 7757.88 | 1.141 | 97.5 | 75.6 | 1312 | 25.21 | 5042.6 | 1350 | 1800.1 | 2268.4 | 1185.6 | 0.59429 | 4.784
2024-12-09 | 13:36 | Data | 0 | 34.567 | 33.527 | 134.612 | 7.63 | 127.243 | 2019.16 | 26.1 | 50.964 | 6.36 | 1.162 | 3.597 | 8115.14 | 1.33 | 97.5 | 75.6 | 1312 | 25.48 | 5274.8 | 1359.7 | 1785.4 | 2258.3 | 1185.6 | 0.60064 | 4.761
2024-12-09 | 13:36 | Data | 0 | 34.783 | 33.412 | 134.476 | 7.63 | 127.107 | 2016.45 | 26.11 | 51.776 | 6.37 | 1.168 | 3.567 | 8069.91 | 1.384 | 97.4 | 75.4 | 1310 | 25.89 | 5245.4 | 1349.3 | 1772.1 | 2245.6 | 1185.6 | 0.59915 | 4.734
2024-12-09 | 13:36 | Data | 0 | 34.641 | 33.419 | 134.476 | 7.63 | 127.107 | 2012.83 | 26.12 | 51.867 | 6.37 | 1.166 | 3.578 | 8042.78 | 1.161 | 97.4 | 75.4 | 1308 | 25.98 | 5227.8 | 1354.9 | 1774.8 | 2249.4 | 1185.6 | 0.60096 | 4.744
2024-12-09 | 13:37 | Data | 0 | 34.789 | 33.797 | 134.521 | 7.63 | 127.062 | 2011.93 | 26.12 | 52.86 | 6.38 | 1.166 | 3.589 | 8011.13 | 1.269 | 97.4 | 75.5 | 1308 | 26.47 | 5207.2 | 1342 | 1779.4 | 2247.6 | 1185.6 | 0.59563 | 4.753
2024-12-09 | 13:37 | Data | 0 | 34.654 | 33.412 | 134.521 | 7.63 | 127.062 | 2015.55 | 26.12 | 53.04 | 6.38 | 1.173 | 3.572 | 7974.95 | 1.175 | 97.4 | 75.3 | 1310 | 26.52 | 5183.7 | 1345.1 | 1793 | 2260.8 | 1185.6 | 0.59417 | 4.745
2024-12-09 | 13:37 | Data | 0 | 34.911 | 33.642 | 134.612 | 7.63 | 127.107 | 2015.55 | 26.12 | 53.582 | 6.38 | 1.171 | 3.569 | 7925.2 | 1.357 | 97.3 | 75.3 | 1310 | 26.79 | 5151.4 | 1340.5 | 1794.8 | 2260.2 | 1185.6 | 0.59244 | 4.744
2024-12-09 | 13:37 | Data | 0 | 34.796 | 33.527 | 134.341 | 7.63 | 126.972 | 2015.55 | 26.13 | 53.943 | 6.39 | 1.164 | 3.578 | 7879.98 | 1.168 | 97.3 | 75.5 | 1310 | 26.97 | 5122 | 1343.2 | 1783.7 | 2249.4 | 1185.6 | 0.59486 | 4.742
2024-12-09 | 13:37 | Data | 0 | 34.715 | 33.534 | 134.476 | 7.63 | 127.107 | 2015.55 | 26.11 | 54.214 | 6.39 | 1.167 | 3.575 | 7852.85 | 1.175 | 97.3 | 75.4 | 1310 | 27.11 | 5104.3 | 1357.9 | 1776.4 | 2252.8 | 1185.6 | 0.6017 | 4.742
2024-12-09 | 13:37 | Data | 0 | 34.594 | 33.527 | 134.431 | 7.63 | 127.017 | 2015.55 | 26.12 | 54.304 | 6.39 | 1.165 | 3.575 | 7821.19 | 1.161 | 97.3 | 75.4 | 1310 | 27.15 | 5083.8 | 1346.6 | 1775.3 | 2248.5 | 1185.6 | 0.59705 | 4.737
2024-12-09 | 13:37 | Data | 0 | 34.681 | 33.628 | 134.024 | 7.64 | 126.7 | 2015.55 | 26.13 | 54.304 | 6.4 | 1.167 | 3.609 | 7785.01 | 1.229 | 97.3 | 75.6 | 1310 | 27.11 | 5060.3 | 1336.2 | 1773.7 | 2245 | 1185.6 | 0.59707 | 4.776
2024-12-09 | 13:37 | Data | 0 | 34.999 | 33.75 | 133.3 | 7.63 | 125.977 | 2013.74 | 26.12 | 54.485 | 6.4 | 1.16 | 3.594 | 7766.92 | 1.161 | 97.3 | 75.6 | 1310 | 27.29 | 5048.5 | 1332.6 | 1772.8 | 2236.1 | 1185.6 | 0.59431 | 4.756
2024-12-09 | 13:37 | Data | 0 | 34.796 | 33.743 | 133.164 | 7.63 | 125.887 | 2017.35 | 26.12 | 54.485 | 6.39 | 1.16 | 3.559 | 7735.27 | 1.181 | 97.3 | 75.4 | 1311 | 27.24 | 5027.9 | 1335.2 | 1781 | 2245.6 | 1185.6 | 0.59411 | 4.72
2024-12-09 | 13:37 | Data | 0 | 34.85 | 33.419 | 133.164 | 7.63 | 125.932 | 2016.45 | 26.12 | 54.575 | 6.4 | 1.159 | 3.569 | 7730.75 | 1.195 | 97.3 | 75.5 | 1311 | 27.29 | 5025 | 1331.6 | 1770 | 2234.8 | 1185.6 | 0.59413 | 4.728
2024-12-09 | 13:37 | Data | 0 | 34.796 | 33.513 | 133.119 | 7.63 | 125.706 | 2012.83 | 26.12 | 54.575 | 6.4 | 1.159 | 3.569 | 7694.57 | 1.181 | 97.3 | 75.5 | 1308 | 27.24 | 5001.5 | 1334.4 | 1787.3 | 2249.5 | 1185.6 | 0.59336 | 4.727
2024-12-09 | 13:37 | Data | 0 | 34.904 | 33.642 | 133.21 | 7.64 | 125.842 | 2012.83 | 26.12 | 54.485 | 6.4 | 1.16 | 3.554 | 7681 | 0.992 | 97.3 | 75.4 | 1308 | 27.24 | 4992.7 | 1326.3 | 1768 | 2229.8 | 1185.6 | 0.59366 | 4.713
2024-12-09 | 13:37 | Data | 0 | 34.681 | 33.439 | 133.074 | 7.63 | 125.842 | 2014.64 | 26.12 | 54.485 | 6.4 | 1.154 | 3.533 | 7640.3 | 1.114 | 97.3 | 75.4 | 1310 | 27.29 | 4966.2 | 1320.2 | 1774.7 | 2232.1 | 1185.6 | 0.59057 | 4.688
2024-12-09 | 13:37 | Data | 0 | 34.904 | 33.648 | 133.21 | 7.63 | 125.887 | 2015.55 | 26.12 | 54.575 | 6.4 | 1.156 | 3.548 | 7613.17 | 1.154 | 97.3 | 75.4 | 1310 | 27.29 | 4948.6 | 1322.8 | 1762.2 | 2221.6 | 1185.6 | 0.59338 | 4.704
2024-12-09 | 13:37 | Data | 0 | 34.897 | 33.858 | 133.255 | 7.63 | 125.842 | 2016.45 | 26.12 | 54.485 | 6.4 | 1.167 | 3.54 | 7586.04 | 1.323 | 97.3 | 75.2 | 1310 | 27.29 | 4930.9 | 1324.7 | 1763.4 | 2223.5 | 1185.6 | 0.59418 | 4.707
2024-12-09 | 13:37 | Data | 0 | 34.877 | 33.466 | 133.119 | 7.64 | 125.797 | 2011.93 | 26.12 | 54.846 | 6.41 | 1.179 | 3.547 | 7576.99 | 1.289 | 97.3 | 75 | 1308 | 27.42 | 4925 | 1332.1 | 1763.6 | 2226.5 | 1185.6 | 0.59694 | 4.728
2024-12-09 | 13:37 | Data | 0 | 34.904 | 33.662 | 133.119 | 7.63 | 125.887 | 2012.83 | 26.12 | 54.936 | 6.4 | 1.17 | 3.541 | 7590.56 | 1.33 | 97.3 | 75.2 | 1308 | 27.47 | 4933.9 | 1338.6 | 1770 | 2236.4 | 1185.6 | 0.5972 | 4.711
2024-12-09 | 13:38 | Data | 0 | 34.594 | 33.412 | 132.984 | 7.63 | 125.797 | 2017.35 | 26.13 | 54.756 | 6.4 | 1.157 | 3.559 | 7572.47 | 1.161 | 97.3 | 75.5 | 1312 | 27.38 | 4922.1 | 1328.3 | 1764.9 | 2229.1 | 1185.6 | 0.59364 | 4.716
2024-12-09 | 13:38 | Data | 0 | 34.567 | 33.412 | 133.074 | 7.63 | 125.706 | 2017.35 | 26.13 | 54.394 | 6.4 | 1.154 | 3.559 | 7563.42 | 1.269 | 97.3 | 75.5 | 1311 | 27.15 | 4916.2 | 1347.5 | 1765.8 | 2237.2 | 1185.6 | 0.59734 | 4.713
2024-12-09 | 13:38 | Data | 0 | 34.621 | 33.412 | 133.074 | 7.63 | 125.797 | 2021.87 | 26.12 | 54.575 | 6.4 | 1.154 | 3.564 | 7549.86 | 1.168 | 97.3 | 75.5 | 1314 | 27.29 | 4907.4 | 1336.8 | 1764.9 | 2233.4 | 1185.6 | 0.59846 | 4.719
2024-12-09 | 13:38 | Data | 0 | 34.627 | 33.412 | 133.119 | 7.63 | 125.842 | 2013.74 | 26.12 | 54.485 | 6.4 | 1.151 | 3.558 | 7531.77 | 1.175 | 97.3 | 75.6 | 1308 | 27.24 | 4895.6 | 1347.2 | 1767.5 | 2241.5 | 1185.6 | 0.59997 | 4.71
2024-12-09 | 13:38 | Data | 0 | 34.668 | 33.513 | 132.984 | 7.63 | 125.797 | 2019.16 | 26.12 | 54.485 | 6.4 | 1.151 | 3.561 | 7531.77 | 1.168 | 97.3 | 75.6 | 1313 | 27.29 | 4895.6 | 1343 | 1777.6 | 2245.6 | 1185.6 | 0.59594 | 4.713
2024-12-09 | 13:38 | Data | 0 | 34.688 | 33.513 | 132.984 | 7.63 | 125.797 | 2018.26 | 26.13 | 54.304 | 6.4 | 1.153 | 3.533 | 7518.2 | 1.154 | 97.3 | 75.4 | 1312 | 27.2 | 4886.8 | 1329.1 | 1766.3 | 2230.6 | 1185.6 | 0.59451 | 4.687
2024-12-09 | 13:38 | Data | 0 | 34.573 | 33.628 | 133.119 | 7.63 | 125.797 | 2018.26 | 26.12 | 54.485 | 6.4 | 1.155 | 3.542 | 7518.2 | 1.114 | 97.3 | 75.4 | 1312 | 27.2 | 4886.8 | 1349.1 | 1789.4 | 2259.8 | 1185.6 | 0.59659 | 4.698
2024-12-09 | 13:38 | Data | 0 | 34.465 | 33.588 | 132.984 | 7.63 | 125.797 | 2014.64 | 26.12 | 54.575 | 6.4 | 1.16 | 3.542 | 7518.2 | 1.127 | 97.3 | 75.3 | 1310 | 27.24 | 4886.8 | 1337.9 | 1789.3 | 2253.7 | 1185.6 | 0.59252 | 4.703
2024-12-09 | 13:38 | Data | 0 | 34.904 | 33.527 | 133.119 | 7.63 | 125.706 | 2015.55 | 26.12 | 53.943 | 6.4 | 1.159 | 3.565 | 7509.16 | 1.215 | 97.3 | 75.5 | 1310 | 26.97 | 4881 | 1346.8 | 1783.9 | 2252.7 | 1185.6 | 0.5964 | 4.725
2024-12-09 | 13:38 | Data | 0 | 34.58 | 33.642 | 133.119 | 7.63 | 125.706 | 2015.55 | 26.12 | 54.485 | 6.4 | 1.163 | 3.555 | 7518.2 | 1.134 | 97.3 | 75.3 | 1310 | 27.24 | 4886.8 | 1386.3 | 1768.4 | 2270.4 | 1185.6 | 0.60687 | 4.718
2024-12-09 | 13:38 | Data | 0 | 34.573 | 33.628 | 132.984 | 7.63 | 125.797 | 2011.93 | 26.12 | 54.575 | 6.4 | 1.167 | 3.541 | 7495.59 | 0.986 | 97.3 | 75.2 | 1309 | 27.29 | 4872.1 | 1365.3 | 1780 | 2264.1 | 1185.6 | 0.60103 | 4.707
2024-12-09 | 13:38 | Data | 0 | 34.681 | 33.615 | 133.074 | 7.63 | 125.706 | 2012.83 | 26.12 | 54.575 | 6.4 | 1.169 | 3.553 | 7513.68 | 0.965 | 97.3 | 75.2 | 1308 | 27.24 | 4883.9 | 1348.7 | 1762.9 | 2240.6 | 1185.6 | 0.60018 | 4.723
2024-12-09 | 13:38 | Data | 0 | 34.789 | 33.615 | 132.984 | 7.64 | 125.797 | 2013.74 | 26.12 | 54.485 | 6.4 | 1.161 | 3.551 | 7509.16 | 1.094 | 97.3 | 75.4 | 1308 | 27.29 | 4881 | 1359.4 | 1775.7 | 2255.4 | 1185.6 | 0.60044 | 4.712
2024-12-09 | 13:38 | Data | 0 | 34.681 | 33.412 | 133.074 | 7.64 | 125.797 | 2012.83 | 26.13 | 54.575 | 6.4 | 1.161 | 3.541 | 7486.55 | 1.175 | 97.3 | 75.3 | 1308 | 27.24 | 4866.3 | 1363.2 | 1807.9 | 2284.7 | 1185.6 | 0.59563 | 4.702
2024-12-09 | 13:38 | Data | 0 | 34.796 | 33.426 | 133.074 | 7.64 | 125.706 | 2011.93 | 26.12 | 54.485 | 6.4 | 1.159 | 3.534 | 7500.11 | 1.256 | 97.3 | 75.3 | 1308 | 27.29 | 4875.1 | 1349 | 1795.7 | 2265.9 | 1185.7 | 0.59477 | 4.694
2024-12-09 | 13:38 | Data | 0 | 34.789 | 33.628 | 133.074 | 7.63 | 125.706 | 2009.22 | 26.12 | 54.575 | 6.4 | 1.161 | 3.534 | 7504.64 | 1.202 | 97.3 | 75.3 | 1306 | 27.29 | 4878 | 1344.5 | 1774.4 | 2245 | 1185.7 | 0.59692 | 4.696
2024-12-09 | 13:38 | Data | 0 | 34.681 | 33.426 | 132.984 | 7.63 | 125.842 | 2010.12 | 26.12 | 54.485 | 6.4 | 1.164 | 3.571 | 7500.11 | 1.141 | 97.3 | 75.4 | 1307 | 27.24 | 4875.1 | 1364.9 | 1765 | 2250.9 | 1185.7 | 0.60417 | 4.735
2024-12-09 | 13:38 | Data | 0 | 34.789 | 33.439 | 132.938 | 7.63 | 125.797 | 2010.12 | 26.12 | 54.575 | 6.4 | 1.159 | 3.565 | 7504.64 | 1.33 | 97.3 | 75.5 | 1305 | 27.24 | 4878 | 1357.3 | 1780.3 | 2258.9 | 1185.7 | 0.59833 | 4.724
2024-12-09 | 13:39 | Data | 0 | 34.796 | 33.426 | 133.119 | 7.64 | 125.706 | 2012.83 | 26.13 | 54.485 | 6.41 | 1.163 | 3.569 | 7482.02 | 1.371 | 97.3 | 75.4 | 1308 | 27.24 | 4863.3 | 1354.7 | 1763.6 | 2243.6 | 1185.7 | 0.59915 | 4.733
2024-12-09 | 13:39 | Data | 0 | 34.621 | 33.243 | 132.938 | 7.63 | 125.842 | 2010.12 | 26.12 | 54.575 | 6.4 | 1.167 | 3.565 | 7482.02 | 1.33 | 97.3 | 75.3 | 1308 | 27.29 | 4863.3 | 1360.8 | 1784.1 | 2263.4 | 1185.7 | 0.59945 | 4.732
2024-12-09 | 13:39 | Data | 0 | 34.742 | 33.642 | 133.074 | 7.64 | 125.797 | 2010.12 | 26.12 | 54.394 | 6.4 | 1.161 | 3.55 | 7477.5 | 1.141 | 97.3 | 75.3 | 1307 | 27.24 | 4860.4 | 1360.8 | 1780.4 | 2260.4 | 1185.7 | 0.60161 | 4.71
2024-12-09 | 13:39 | Data | 0 | 34.641 | 33.439 | 133.119 | 7.63 | 125.797 | 2007.41 | 26.11 | 54.485 | 6.4 | 1.151 | 3.577 | 7472.98 | 1.114 | 97.3 | 75.6 | 1305 | 27.24 | 4857.4 | 1357.4 | 1773.1 | 2251.3 | 1185.7 | 0.601 | 4.728
2024-12-09 | 13:39 | Data | 0 | 34.573 | 33.527 | 133.119 | 7.63 | 125.706 | 2008.32 | 26.12 | 54.575 | 6.4 | 1.156 | 3.579 | 7500.11 | 1.154 | 97.3 | 75.6 | 1306 | 27.24 | 4875.1 | 1371.2 | 1791 | 2274.6 | 1185.7 | 0.60172 | 4.735
2024-12-09 | 13:39 | Data | 0 | 34.796 | 33.527 | 133.074 | 7.63 | 125.797 | 2010.12 | 26.12 | 54.575 | 6.4 | 1.167 | 3.574 | 7477.5 | 1.161 | 97.3 | 75.4 | 1306 | 27.29 | 4860.4 | 1354.1 | 1772.4 | 2249.8 | 1185.7 | 0.59912 | 4.739
2024-12-09 | 13:39 | Data | 0 | 34.513 | 33.567 | 133.074 | 7.63 | 125.706 | 2012.83 | 26.11 | 54.575 | 6.4 | 1.165 | 3.555 | 7491.07 | 1.06 | 97.3 | 75.3 | 1308 | 27.29 | 4869.2 | 1352.4 | 1772 | 2247 | 1185.7 | 0.59805 | 4.718
2024-12-09 | 13:39 | Data | 0 | 34.567 | 33.615 | 133.074 | 7.63 | 125.706 | 2012.83 | 26.12 | 54.214 | 6.4 | 1.16 | 3.568 | 7491.07 | 1.181 | 97.3 | 75.5 | 1308 | 27.11 | 4869.2 | 1358.9 | 1788.9 | 2264.6 | 1185.7 | 0.59781 | 4.729
2024-12-09 | 13:39 | Data | 0 | 35.012 | 33.642 | 133.119 | 7.63 | 125.842 | 2015.55 | 26.14 | 54.485 | 6.4 | 1.155 | 3.563 | 7495.59 | 1.181 | 97.3 | 75.5 | 1311 | 27.24 | 4872.1 | 1354.2 | 1792.5 | 2265 | 1185.7 | 0.59627 | 4.718
2024-12-09 | 13:39 | Data | 0 | 34.594 | 33.419 | 133.119 | 7.63 | 125.706 | 2015.55 | 26.13 | 54.485 | 6.4 | 1.159 | 3.54 | 7477.5 | 1.154 | 97.3 | 75.3 | 1311 | 27.29 | 4860.4 | 1332.7 | 1760 | 2226.2 | 1185.7 | 0.59723 | 4.7
2024-12-09 | 13:39 | Data | 0 | 34.621 | 33.615 | 132.984 | 7.64 | 125.616 | 2015.55 | 26.11 | 54.575 | 6.4 | 1.163 | 3.552 | 7486.55 | 1.141 | 97.3 | 75.3 | 1310 | 27.29 | 4866.3 | 1342.9 | 1773.4 | 2245.6 | 1185.7 | 0.59722 | 4.716
2024-12-09 | 13:39 | Data | 0 | 34.796 | 33.466 | 132.984 | 7.63 | 125.661 | 2018.26 | 26.13 | 54.575 | 6.4 | 1.157 | 3.546 | 7482.02 | 1.154 | 97.3 | 75.4 | 1311 | 27.24 | 4863.3 | 1340.3 | 1759.1 | 2231.8 | 1185.7 | 0.59832 | 4.702
2024-12-09 | 13:39 | Data | 0 | 34.465 | 33.412 | 132.938 | 7.63 | 125.661 | 2019.16 | 26.13 | 54.575 | 6.4 | 1.148 | 3.562 | 7454.89 | 1.134 | 97.3 | 75.6 | 1312 | 27.29 | 4845.7 | 1343.3 | 1762.6 | 2235.2 | 1185.7 | 0.59671 | 4.71
2024-12-09 | 13:39 | Data | 0 | 34.567 | 33.412 | 132.938 | 7.63 | 125.706 | 2018.26 | 26.14 | 54.665 | 6.4 | 1.164 | 3.555 | 7468.46 | 1.154 | 97.3 | 75.3 | 1312 | 27.29 | 4854.5 | 1337.9 | 1750.6 | 2223.7 | 1185.7 | 0.60012 | 4.72
2024-12-09 | 13:39 | Data | 0 | 34.567 | 33.412 | 132.984 | 7.64 | 125.706 | 2017.35 | 26.12 | 54.485 | 6.41 | 1.151 | 3.552 | 7468.46 | 1.154 | 97.3 | 75.5 | 1311 | 27.24 | 4854.5 | 1343.2 | 1763.7 | 2236.1 | 1185.7 | 0.59828 | 4.704
2024-12-09 | 13:39 | Data | 0 | 34.796 | 33.642 | 133.164 | 7.63 | 125.706 | 2018.26 | 26.12 | 54.485 | 6.4 | 1.157 | 3.561 | 7445.85 | 1.154 | 97.3 | 75.5 | 1312 | 27.2 | 4839.8 | 1344.2 | 1765.7 | 2240.8 | 1185.7 | 0.59537 | 4.718
2024-12-09 | 13:39 | Data | 0 | 34.573 | 33.412 | 132.938 | 7.63 | 125.706 | 2018.26 | 26.11 | 54.665 | 6.4 | 1.156 | 3.559 | 7463.94 | 1.154 | 97.3 | 75.5 | 1311 | 27.29 | 4851.6 | 1354 | 1758.4 | 2248.3 | 1185.7 | 0.59542 | 4.71
2024-12-09 | 13:39 | Data | 0 | 34.681 | 33.439 | 132.984 | 7.64 | 125.661 | 2017.35 | 26.12 | 54.485 | 6.4 | 1.157 | 3.545 | 7477.5 | 1.215 | 97.3 | 75.4 | 1312 | 27.24 | 4860.4 | 1337.5 | 1765.2 | 2233.9 | 1185.7 | 0.59699 | 4.702
2024-12-09 | 13:40 | Data | 0 | 34.398 | 33.412 | 132.938 | 7.63 | 125.616 | 2018.26 | 26.11 | 54.665 | 6.4 | 1.153 | 3.546 | 7477.5 | 0.952 | 97.3 | 75.4 | 1311 | 27.29 | 4860.4 | 1350.9 | 1776.9 | 2252.8 | 1185.7 | 0.59782 | 4.701
2024-12-09 | 13:40 | Data | 0 | 34.675 | 33.331 | 132.984 | 7.63 | 125.706 | 2018.26 | 26.12 | 54.485 | 6.4 | 1.163 | 3.55 | 7477.5 | 1.337 | 97.3 | 75.3 | 1312 | 27.29 | 4860.4 | 1356.1 | 1795.6 | 2269.5 | 1185.7 | 0.5965 | 4.712
2024-12-09 | 13:40 | Data | 0 | 34.742 | 33.412 | 133.074 | 7.64 | 125.706 | 2018.26 | 26.12 | 54.485 | 6.4 | 1.159 | 3.538 | 7482.02 | 1.175 | 97.3 | 75.3 | 1311 | 27.29 | 4863.3 | 1352.8 | 1760.2 | 2240.1 | 1185.7 | 0.60203 | 4.697
2024-12-09 | 13:40 | Data | 0 | 34.789 | 33.581 | 133.119 | 7.63 | 125.661 | 2018.26 | 26.12 | 54.575 | 6.41 | 1.159 | 3.56 | 7477.5 | 1.013 | 97.3 | 75.4 | 1312 | 27.29 | 4860.4 | 1364.6 | 1772.5 | 2256 | 1185.7 | 0.60031 | 4.72
2024-12-09 | 13:40 | Data | 0 | 34.735 | 33.297 | 132.893 | 7.63 | 125.706 | 2017.35 | 26.13 | 54.485 | 6.39 | 1.163 | 3.565 | 7468.46 | 1.202 | 97.3 | 75.4 | 1311 | 27.29 | 4854.5 | 1565.5 | 2415.9 | 2924.7 | 1185.7 | 0.5743 | 4.729
2024-12-09 | 13:40 | Data | 0 | 34.769 | 33.412 | 132.938 | 7.64 | 125.661 | 2017.35 | 26.12 | 54.485 | 6.4 | 1.164 | 3.574 | 7477.5 | 1.371 | 97.3 | 75.4 | 1311 | 27.29 | 4860.4 | 2434.4 | 2426.8 | 3581.6 | 1185.7 | 0.66436 | 4.738
2024-12-09 | 13:40 | Data | 0 | 34.567 | 33.412 | 132.938 | 7.63 | 125.616 | 2018.26 | 26.12 | 54.485 | 6.4 | 1.157 | 3.565 | 7454.89 | 1.161 | 97.3 | 75.5 | 1312 | 27.29 | 4845.7 | 2431.6 | 2423.7 | 3583.2 | 1185.7 | 0.6626 | 4.721
2024-12-09 | 13:40 | Data | 0 | 34.769 | 33.439 | 132.893 | 7.64 | 125.571 | 2018.26 | 26.11 | 54.575 | 6.4 | 1.156 | 3.559 | 7445.85 | 1.269 | 97.3 | 75.5 | 1312 | 27.29 | 4839.8 | 2421.1 | 2430.3 | 3580.7 | 1185.7 | 0.6613 | 4.716
2024-12-09 | 13:40 | Data | 0 | 34.621 | 33.581 | 132.893 | 7.64 | 125.616 | 2017.35 | 26.13 | 54.575 | 6.41 | 1.165 | 3.571 | 7454.89 | 1.046 | 97.3 | 75.4 | 1312 | 27.29 | 4845.7 | 2417 | 2432 | 3581.8 | 1185.7 | 0.65816 | 4.736
2024-12-09 | 13:40 | Data | 0 | 34.789 | 33.412 | 132.984 | 7.63 | 125.661 | 2018.26 | 26.12 | 54.394 | 6.4 | 1.169 | 3.57 | 7463.94 | 1.377 | 97.3 | 75.3 | 1312 | 27.24 | 4851.6 | 2431.7 | 2428.2 | 3585.8 | 1185.7 | 0.66212 | 4.739
2024-12-09 | 13:40 | Data | 0 | 34.567 | 33.412 | 132.893 | 7.64 | 125.661 | 2017.35 | 26.12 | 54.575 | 6.4 | 1.162 | 3.584 | 7463.94 | 1.154 | 97.3 | 75.5 | 1311 | 27.24 | 4851.6 | 2428.9 | 2444.1 | 3591.2 | 1185.7 | 0.6616 | 4.745
2024-12-09 | 13:40 | Data | 0 | 34.398 | 33.297 | 132.984 | 7.64 | 125.661 | 2018.26 | 26.13 | 54.485 | 6.4 | 1.151 | 3.564 | 7454.89 | 1.175 | 97.3 | 75.6 | 1312 | 27.24 | 4845.7 | 2424.3 | 2428.6 | 3579.3 | 1185.7 | 0.66144 | 4.714
2024-12-09 | 13:40 | Data | 0 | 34.789 | 33.412 | 132.938 | 7.64 | 125.661 | 2018.26 | 26.11 | 54.575 | 6.4 | 1.149 | 3.57 | 7436.8 | 1.208 | 97.3 | 75.6 | 1312 | 27.29 | 4833.9 | 2410 | 2446.1 | 3584.6 | 1185.7 | 0.65551 | 4.72
2024-12-09 | 13:40 | Data | 0 | 34.594 | 33.412 | 132.984 | 7.63 | 125.797 | 2017.35 | 26.13 | 54.575 | 6.4 | 1.151 | 3.556 | 7445.85 | 1.161 | 97.3 | 75.5 | 1311 | 27.29 | 4839.8 | 2427.7 | 2431.4 | 3582 | 1185.7 | 0.66227 | 4.707
2024-12-09 | 13:40 | Data | 0 | 34.344 | 33.372 | 132.938 | 7.64 | 125.661 | 2014.64 | 26.12 | 54.756 | 6.4 | 1.167 | 3.537 | 7454.89 | 1.242 | 97.3 | 75.2 | 1310 | 27.38 | 4845.7 | 2439.9 | 2430.8 | 3585.6 | 1185.7 | 0.66615 | 4.702
2024-12-09 | 13:40 | Data | 0 | 34.411 | 33.399 | 132.984 | 7.63 | 125.706 | 2015.55 | 26.12 | 54.485 | 6.4 | 1.16 | 3.567 | 7454.89 | 1.148 | 97.3 | 75.5 | 1310 | 27.24 | 4845.7 | 2430.9 | 2442.2 | 3591.5 | 1185.7 | 0.66123 | 4.727
2024-12-09 | 13:40 | Data | 0 | 34.452 | 33.412 | 132.938 | 7.64 | 125.616 | 2015.55 | 26.13 | 54.485 | 6.4 | 1.16 | 3.559 | 7454.89 | 1.317 | 97.3 | 75.4 | 1310 | 27.24 | 4845.7 | 2432.4 | 2436.9 | 3590.1 | 1185.7 | 0.66226 | 4.719
2024-12-09 | 13:40 | Data | 0 | 34.668 | 33.412 | 132.984 | 7.63 | 125.616 | 2016.45 | 26.12 | 54.575 | 6.4 | 1.159 | 3.559 | 7459.41 | 1.35 | 97.3 | 75.4 | 1311 | 27.29 | 4848.6 | 2427 | 2432.7 | 3586.6 | 1185.7 | 0.66013 | 4.72
2024-12-09 | 13:41 | Data | 0 | 34.681 | 33.412 | 132.984 | 7.63 | 125.706 | 2015.55 | 26.13 | 54.214 | 6.4 | 1.163 | 3.546 | 7459.41 | 1.161 | 97.3 | 75.3 | 1310 | 27.15 | 4848.6 | 2429.3 | 2416.6 | 3573.3 | 1185.7 | 0.66367 | 4.711
2024-12-09 | 13:41 | Data | 0 | 34.567 | 33.412 | 132.848 | 7.63 | 125.616 | 2015.55 | 26.13 | 54.485 | 6.4 | 1.169 | 3.562 | 7454.89 | 1.154 | 97.3 | 75.3 | 1310 | 27.24 | 4845.7 | 2420.8 | 2415.9 | 3566.6 | 1185.7 | 0.66154 | 4.731
2024-12-09 | 13:41 | Data | 0 | 34.567 | 33.412 | 132.848 | 7.63 | 125.616 | 2018.26 | 26.13 | 54.485 | 6.4 | 1.162 | 3.563 | 7468.46 | 1.154 | 97.3 | 75.4 | 1312 | 27.29 | 4854.5 | 2410.8 | 2398.9 | 3552.9 | 1185.7 | 0.66502 | 4.725
2024-12-09 | 13:41 | Data | 0 | 34.452 | 33.189 | 132.848 | 7.63 | 125.571 | 2017.35 | 26.12 | 54.394 | 6.4 | 1.152 | 3.553 | 7477.5 | 1.344 | 97.3 | 75.5 | 1311 | 27.2 | 4860.4 | 2416.1 | 2428.9 | 3570.4 | 1185.7 | 0.66004 | 4.705
2024-12-09 | 13:41 | Data | 0 | 34.54 | 33.527 | 133.119 | 7.63 | 125.661 | 2019.16 | 26.12 | 54.485 | 6.41 | 1.167 | 3.581 | 7445.85 | 1.344 | 97.3 | 75.4 | 1313 | 27.29 | 4839.8 | 2419.6 | 2423.9 | 3572.1 | 1185.7 | 0.66172 | 4.748
2024-12-09 | 13:41 | Data | 0 | 34.742 | 33.628 | 132.893 | 7.63 | 125.616 | 2016.45 | 26.12 | 53.672 | 6.4 | 1.168 | 3.579 | 7468.46 | 1.175 | 97.3 | 75.4 | 1311 | 26.84 | 4854.5 | 2415.8 | 2400 | 3547.7 | 1185.7 | 0.66638 | 4.747
2024-12-09 | 13:41 | Data | 0 | 34.587 | 33.412 | 132.984 | 7.63 | 125.661 | 2020.97 | 26.12 | 54.575 | 6.41 | 1.16 | 3.575 | 7491.07 | 1.168 | 97.3 | 75.5 | 1314 | 27.29 | 4869.2 | 2415.4 | 2403.7 | 3554.7 | 1185.7 | 0.66416 | 4.734
2024-12-09 | 13:41 | Data | 0 | 34.513 | 33.567 | 132.938 | 7.63 | 125.571 | 2021.87 | 26.12 | 54.575 | 6.4 | 1.162 | 3.578 | 7495.59 | 1.168 | 97.3 | 75.5 | 1313 | 27.29 | 4872.1 | 2416.7 | 2427.6 | 3572.2 | 1185.7 | 0.65906 | 4.741
2024-12-09 | 13:41 | Data | 0 | 34.681 | 33.642 | 133.074 | 7.63 | 125.661 | 2020.97 | 26.12 | 54.485 | 6.4 | 1.157 | 3.573 | 7491.07 | 1.175 | 97.3 | 75.5 | 1314 | 27.29 | 4869.2 | 2427.3 | 2405.7 | 3564.7 | 1185.7 | 0.66521 | 4.729
2024-12-09 | 13:41 | Data | 0 | 34.459 | 33.52 | 132.893 | 7.64 | 125.661 | 2020.07 | 26.12 | 54.485 | 6.4 | 1.147 | 3.562 | 7491.07 | 1.114 | 97.3 | 75.6 | 1313 | 27.29 | 4869.2 | 2430.2 | 2434 | 3584 | 1185.7 | 0.66374 | 4.708
2024-12-09 | 13:41 | Data | 0 | 34.364 | 33.412 | 133.074 | 7.64 | 125.661 | 2020.97 | 26.12 | 54.485 | 6.4 | 1.159 | 3.555 | 7482.02 | 1.046 | 97.3 | 75.4 | 1314 | 27.24 | 4863.3 | 2415.7 | 2419.6 | 3564.4 | 1185.7 | 0.66007 | 4.714
2024-12-09 | 13:41 | Data | 0 | 34.567 | 33.412 | 132.893 | 7.64 | 125.616 | 2023.68 | 26.12 | 54.485 | 6.4 | 1.161 | 3.584 | 7468.46 | 1.154 | 97.3 | 75.5 | 1315 | 27.29 | 4854.5 | 2419.1 | 2418.5 | 3565.2 | 1185.7 | 0.6626 | 4.746
2024-12-09 | 13:41 | Data | 0 | 34.371 | 33.385 | 132.938 | 7.63 | 125.661 | 2022.78 | 26.12 | 54.575 | 6.4 | 1.159 | 3.548 | 7459.41 | 0.986 | 97.3 | 75.4 | 1315 | 27.29 | 4848.6 | 2423.4 | 2417.8 | 3569.9 | 1185.7 | 0.66467 | 4.706
2024-12-09 | 13:41 | Data | 0 | 34.789 | 33.412 | 132.938 | 7.63 | 125.616 | 2022.78 | 26.11 | 54.575 | 6.4 | 1.147 | 3.561 | 7463.94 | 1.208 | 97.3 | 75.6 | 1315 | 27.29 | 4851.6 | 2410.8 | 2421.8 | 3560 | 1185.7 | 0.66061 | 4.708
2024-12-09 | 13:41 | Data | 0 | 34.668 | 33.21 | 132.848 | 7.64 | 125.571 | 2018.26 | 26.12 | 54.575 | 6.4 | 1.165 | 3.53 | 7454.89 | 1.161 | 97.3 | 75.2 | 1312 | 27.24 | 4845.7 | 2419.1 | 2430.3 | 3576.8 | 1185.7 | 0.6588 | 4.695
2024-12-09 | 13:41 | Data | 0 | 34.877 | 33.837 | 133.119 | 7.64 | 125.661 | 2023.68 | 26.12 | 54.575 | 6.4 | 1.163 | 3.548 | 7454.89 | 1.168 | 97.3 | 75.3 | 1315 | 27.24 | 4845.7 | 2429.3 | 2412.5 | 3569.1 | 1185.8 | 0.66699 | 4.71
2024-12-09 | 13:41 | Data | 0 | 34.675 | 33.243 | 132.938 | 7.63 | 125.661 | 2030.01 | 26.13 | 54.575 | 6.41 | 1.164 | 3.572 | 7445.85 | 1.195 | 97.3 | 75.4 | 1318 | 27.24 | 4839.8 | 2420.7 | 2405.8 | 3558.1 | 1185.8 | 0.66341 | 4.738
2024-12-09 | 13:42 | Data | 0 | 34.567 | 33.412 | 132.984 | 7.63 | 125.616 | 2030.01 | 26.12 | 54.575 | 6.4 | 1.166 | 3.556 | 7468.46 | 1.154 | 97.3 | 75.3 | 1320 | 27.24 | 4854.5 | 2432.4 | 2412.6 | 3564.4 | 1185.8 | 0.6641 | 4.721
2024-12-09 | 13:42 | Data | 0 | 34.567 | 33.581 | 132.984 | 7.64 | 125.661 | 2030.01 | 26.11 | 54.575 | 6.4 | 1.156 | 3.566 | 7468.46 | 1.154 | 97.3 | 75.5 | 1319 | 27.29 | 4854.5 | 2439.9 | 2417 | 3575.2 | 1185.8 | 0.6658 | 4.721
2024-12-09 | 13:42 | Data | 0 | 34.567 | 33.324 | 132.984 | 7.63 | 125.616 | 2027.3 | 26.12 | 54.575 | 6.4 | 1.159 | 3.554 | 7463.94 | 1.242 | 97.3 | 75.4 | 1317 | 27.24 | 4851.6 | 2431.4 | 2428.3 | 3579.5 | 1185.8 | 0.66354 | 4.712
2024-12-09 | 13:42 | Data | 0 | 34.54 | 33.628 | 132.893 | 7.64 | 125.661 | 2030.01 | 26.13 | 54.485 | 6.41 | 1.161 | 3.563 | 7459.41 | 1.087 | 97.3 | 75.4 | 1320 | 27.24 | 4848.6 | 2429.1 | 2412.6 | 3570 | 1185.8 | 0.66299 | 4.724
2024-12-09 | 13:42 | Data | 0 | 34.344 | 33.399 | 132.803 | 7.64 | 125.571 | 2029.1 | 26.12 | 54.575 | 6.41 | 1.164 | 3.556 | 7477.5 | 1.094 | 97.3 | 75.3 | 1318 | 27.24 | 4860.4 | 2416.6 | 2430.8 | 3572.8 | 1185.8 | 0.6617 | 4.723
2024-12-09 | 13:42 | Data | 0 | 34.742 | 33.243 | 132.984 | 7.64 | 125.661 | 2027.3 | 26.13 | 54.575 | 6.41 | 1.162 | 3.566 | 7454.89 | 1.181 | 97.3 | 75.4 | 1319 | 27.2 | 4845.7 | 2426.3 | 2406.7 | 3560.4 | 1185.8 | 0.66389 | 4.729
2024-12-09 | 13:42 | Data | 0 | 34.567 | 33.534 | 132.984 | 7.63 | 125.571 | 2030.01 | 26.12 | 54.575 | 6.4 | 1.156 | 3.571 | 7454.89 | 1.316 | 97.3 | 75.5 | 1319 | 27.29 | 4845.7 | 2407.9 | 2438.6 | 3574.2 | 1185.8 | 0.65705 | 4.727
2024-12-09 | 13:42 | Data | 0 | 34.769 | 33.642 | 132.984 | 7.63 | 125.616 | 2025.49 | 26.13 | 54.304 | 6.4 | 1.166 | 3.552 | 7436.8 | 1.154 | 97.3 | 75.3 | 1317 | 27.15 | 4833.9 | 2418.1 | 2413.9 | 3559.9 | 1185.8 | 0.66257 | 4.719
2024-12-09 | 13:42 | Data | 0 | 34.567 | 33.331 | 132.984 | 7.64 | 125.661 | 2025.49 | 26.13 | 54.304 | 6.4 | 1.164 | 3.56 | 7454.89 | 1.127 | 97.3 | 75.4 | 1317 | 27.15 | 4845.7 | 2426.5 | 2431.8 | 3578.6 | 1185.8 | 0.6617 | 4.722
2024-12-09 | 13:42 | Data | 0 | 34.567 | 33.621 | 132.984 | 7.64 | 125.616 | 2022.78 | 26.12 | 54.214 | 6.4 | 1.152 | 3.544 | 7445.85 | 1.073 | 97.3 | 75.5 | 1315 | 27.11 | 4839.8 | 2433.9 | 2413.7 | 3574.2 | 1185.8 | 0.66645 | 4.696
2024-12-09 | 13:42 | Data | 0 | 34.58 | 33.412 | 132.938 | 7.64 | 125.706 | 2026.39 | 26.12 | 54.214 | 6.41 | 1.151 | 3.559 | 7454.89 | 1.161 | 97.3 | 75.6 | 1317 | 27.15 | 4845.7 | 2425.5 | 2428.6 | 3576.1 | 1185.8 | 0.6632 | 4.71
2024-12-09 | 13:42 | Data | 0 | 34.607 | 33.588 | 133.074 | 7.64 | 125.661 | 2026.39 | 26.12 | 54.304 | 6.41 | 1.168 | 3.555 | 7454.89 | 1.161 | 97.3 | 75.2 | 1317 | 27.15 | 4845.7 | 2424 | 2426.5 | 3571.2 | 1185.8 | 0.66403 | 4.724
2024-12-09 | 13:42 | Data | 0 | 34.789 | 33.439 | 133.074 | 7.63 | 125.661 | 2029.1 | 26.12 | 54.304 | 6.4 | 1.163 | 3.554 | 7459.41 | 1.323 | 97.3 | 75.3 | 1319 | 27.15 | 4848.6 | 2423.2 | 2419.9 | 3569.2 | 1185.8 | 0.66435 | 4.717
2024-12-09 | 13:42 | Data | 0 | 34.668 | 33.412 | 132.938 | 7.64 | 125.706 | 2026.39 | 26.14 | 54.124 | 6.4 | 1.162 | 3.568 | 7432.28 | 1.323 | 97.3 | 75.4 | 1317 | 27.11 | 4831 | 2420.2 | 2418.1 | 3567.8 | 1185.8 | 0.66155 | 4.73
2024-12-09 | 13:42 | Data | 0 | 34.742 | 33.52 | 132.984 | 7.64 | 125.706 | 2025.49 | 26.12 | 54.214 | 6.41 | 1.166 | 3.572 | 7441.32 | 1.269 | 97.3 | 75.4 | 1317 | 27.15 | 4836.9 | 2423.3 | 2405.8 | 3557.1 | 1185.8 | 0.66644 | 4.738
2024-12-09 | 13:42 | Data | 0 | 34.378 | 33.473 | 132.938 | 7.63 | 125.616 | 2020.97 | 26.13 | 54.214 | 6.4 | 1.16 | 3.56 | 7454.89 | 1.154 | 97.3 | 75.4 | 1314 | 27.15 | 4845.7 | 2428.4 | 2418.5 | 3569.6 | 1185.8 | 0.66121 | 4.72
2024-12-09 | 13:42 | Data | 0 | 34.371 | 33.405 | 132.984 | 7.63 | 125.706 | 2024.58 | 26.11 | 54.214 | 6.4 | 1.156 | 3.559 | 7468.46 | 1.06 | 97.3 | 75.5 | 1315 | 27.11 | 4854.5 | 2444.1 | 2422.6 | 3579.8 | 1185.8 | 0.66655 | 4.713
2024-12-09 | 13:42 | Data | 0 | 34.58 | 33.419 | 132.984 | 7.64 | 125.706 | 2022.78 | 26.12 | 54.304 | 6.41 | 1.16 | 3.559 | 7459.41 | 1.148 | 97.3 | 75.4 | 1315 | 27.15 | 4848.6 | 2424.6 | 2435.6 | 3580.7 | 1185.8 | 0.66027 | 4.719
2024-12-09 | 13:43 | Data | 0 | 34.526 | 33.412 | 133.074 | 7.63 | 125.706 | 2022.78 | 26.12 | 54.485 | 6.4 | 1.16 | 3.548 | 7468.46 | 1.154 | 97.3 | 75.4 | 1315 | 27.2 | 4854.5 | 2418.5 | 2426.5 | 3574 | 1185.8 | 0.6627 | 4.709
2024-12-09 | 13:43 | Data | 0 | 34.681 | 33.52 | 133.074 | 7.64 | 125.661 | 2026.39 | 26.12 | 54.304 | 6.41 | 1.156 | 3.556 | 7468.46 | 1.262 | 97.3 | 75.5 | 1317 | 27.15 | 4854.5 | 2421.2 | 2400.5 | 3558.6 | 1185.8 | 0.6639 | 4.712
2024-12-09 | 13:43 | Data | 0 | 34.735 | 33.527 | 132.938 | 7.64 | 125.661 | 2026.39 | 26.13 | 54.214 | 6.4 | 1.166 | 3.564 | 7482.02 | 1.256 | 97.3 | 75.3 | 1317 | 27.15 | 4863.3 | 2424 | 2414.8 | 3566.8 | 1185.8 | 0.66439 | 4.728
2024-12-09 | 13:43 | Data | 0 | 34.573 | 33.412 | 133.074 | 7.64 | 125.706 | 2023.68 | 26.12 | 54.394 | 6.41 | 1.163 | 3.556 | 7495.59 | 1.154 | 97.3 | 75.4 | 1316 | 27.15 | 4872.1 | 2431.8 | 2408.3 | 3566 | 1185.8 | 0.66499 | 4.72
2024-12-09 | 13:43 | Data | 0 | 34.567 | 33.527 | 132.984 | 7.64 | 125.706 | 2026.39 | 26.12 | 54.394 | 6.4 | 1.147 | 3.56 | 7477.5 | 1.154 | 97.3 | 75.6 | 1316 | 27.15 | 4860.4 | 2440.5 | 2413.5 | 3576.1 | 1185.8 | 0.66869 | 4.708
2024-12-09 | 13:43 | Data | 0 | 34.573 | 33.405 | 132.984 | 7.63 | 125.661 | 2019.16 | 26.13 | 54.214 | 6.4 | 1.154 | 3.569 | 7482.02 | 1.161 | 97.3 | 75.6 | 1313 | 27.15 | 4863.3 | 2422.1 | 2424.5 | 3568.3 | 1185.8 | 0.66177 | 4.723
2024-12-09 | 13:43 | Data | 0 | 34.958 | 33.662 | 133.164 | 7.64 | 125.706 | 2023.68 | 26.13 | 54.304 | 6.41 | 1.154 | 3.534 | 7482.02 | 1.242 | 97.3 | 75.4 | 1315 | 27.15 | 4863.3 | 2425.8 | 2413.7 | 3576.5 | 1185.8 | 0.66777 | 4.689
2024-12-09 | 13:43 | Data | 0 | 34.567 | 33.581 | 132.984 | 7.64 | 125.706 | 2023.68 | 26.13 | 54.575 | 6.4 | 1.16 | 3.551 | 7486.55 | 1.269 | 97.3 | 75.4 | 1315 | 27.29 | 4866.3 | 2415.4 | 2419.6 | 3561.7 | 1185.8 | 0.66369 | 4.711
2024-12-09 | 13:43 | Data | 0 | 34.573 | 33.527 | 133.074 | 7.64 | 125.706 | 2020.97 | 26.13 | 54.304 | 6.4 | 1.165 | 3.549 | 7486.55 | 1.242 | 97.3 | 75.3 | 1313 | 27.15 | 4866.3 | 2415.6 | 2397.3 | 3551.4 | 1185.8 | 0.66476 | 4.715
2024-12-09 | 13:43 | Data | 0 | 34.681 | 33.635 | 133.074 | 7.64 | 125.661 | 2020.07 | 26.13 | 54.214 | 6.4 | 1.15 | 3.561 | 7491.07 | 1.134 | 97.3 | 75.6 | 1314 | 27.15 | 4869.2 | 2424.9 | 2418 | 3566.4 | 1185.8 | 0.66445 | 4.711
2024-12-09 | 13:43 | Data | 0 | 34.681 | 33.412 | 133.119 | 7.64 | 125.661 | 2025.49 | 26.12 | 54.485 | 6.4 | 1.162 | 3.562 | 7495.59 | 1.175 | 97.3 | 75.4 | 1317 | 27.29 | 4872.1 | 2421.3 | 2440.2 | 3579.2 | 1185.8 | 0.66256 | 4.725
2024-12-09 | 13:43 | Data | 0 | 34.796 | 33.439 | 133.074 | 7.63 | 125.797 | 2022.78 | 26.13 | 54.485 | 6.4 | 1.162 | 3.558 | 7482.02 | 1.33 | 97.3 | 75.4 | 1315 | 27.24 | 4863.3 | 2413.5 | 2404.5 | 3553.8 | 1185.8 | 0.66456 | 4.72
2024-12-09 | 13:43 | Data | 0 | 34.891 | 33.419 | 132.984 | 7.64 | 125.797 | 2026.39 | 26.13 | 54.485 | 6.4 | 1.154 | 3.578 | 7482.02 | 1.161 | 97.3 | 75.6 | 1317 | 27.24 | 4863.3 | 2417.5 | 2426.3 | 3566.3 | 1185.8 | 0.663 | 4.733
2024-12-09 | 13:43 | Data | 0 | 34.789 | 33.642 | 133.119 | 7.64 | 125.706 | 2023.68 | 26.13 | 54.575 | 6.41 | 1.154 | 3.58 | 7468.46 | 1.154 | 97.3 | 75.6 | 1315 | 27.29 | 4854.5 | 2416 | 2414.4 | 3561.7 | 1185.8 | 0.66135 | 4.736
2024-12-09 | 13:43 | Data | 0 | 34.587 | 33.412 | 132.893 | 7.63 | 125.706 | 2021.87 | 26.12 | 54.485 | 6.4 | 1.16 | 3.572 | 7482.02 | 1.154 | 97.3 | 75.5 | 1315 | 27.29 | 4863.3 | 2411.5 | 2434.7 | 3573.3 | 1185.8 | 0.65866 | 4.733
2024-12-09 | 13:43 | Data | 0 | 34.573 | 33.635 | 133.119 | 7.63 | 125.706 | 2025.49 | 26.13 | 54.575 | 6.4 | 1.16 | 3.559 | 7482.02 | 1.053 | 97.3 | 75.4 | 1317 | 27.33 | 4863.3 | 2426.7 | 2403.4 | 3562.3 | 1185.8 | 0.66389 | 4.72
2024-12-09 | 13:43 | Data | 0 | 34.567 | 33.628 | 133.074 | 7.64 | 125.797 | 2025.49 | 26.13 | 54.485 | 6.41 | 1.161 | 3.562 | 7454.89 | 1.141 | 97.3 | 75.4 | 1317 | 27.2 | 4845.7 | 2422.5 | 2395.8 | 3547 | 1185.8 | 0.66853 | 4.722
2024-12-09 | 13:44 | Data | 0 | 34.681 | 33.243 | 132.938 | 7.64 | 125.706 | 2026.39 | 26.12 | 54.485 | 6.4 | 1.165 | 3.566 | 7454.89 | 1.337 | 97.3 | 75.4 | 1317 | 27.24 | 4845.7 | 2425.1 | 2423.5 | 3572.5 | 1185.8 | 0.66222 | 4.731
2024-12-09 | 13:44 | Data | 0 | 34.621 | 33.412 | 132.984 | 7.63 | 125.661 | 2026.39 | 26.12 | 54.575 | 6.41 | 1.167 | 3.571 | 7472.98 | 1.168 | 97.3 | 75.4 | 1317 | 27.24 | 4857.4 | 2413.4 | 2404.8 | 3552.6 | 1185.8 | 0.66272 | 4.738
2024-12-09 | 13:44 | Data | 0 | 34.992 | 33.534 | 133.164 | 7.63 | 125.842 | 2026.39 | 26.12 | 54.485 | 6.39 | 1.166 | 3.536 | 7468.46 | 1.242 | 97.3 | 75.2 | 1317 | 27.24 | 4854.5 | 2426.9 | 2420.5 | 3575.6 | 1185.8 | 0.66234 | 4.702
2024-12-09 | 13:44 | Data | 0 | 34.992 | 33.48 | 133.119 | 7.64 | 125.797 | 2026.39 | 26.12 | 54.665 | 6.4 | 1.16 | 3.544 | 7463.94 | 1.35 | 97.3 | 75.3 | 1317 | 27.29 | 4851.6 | 2406 | 2436.8 | 3569.6 | 1185.8 | 0.65821 | 4.704
2024-12-09 | 13:44 | Data | 0 | 34.769 | 33.48 | 132.938 | 7.64 | 125.706 | 2025.49 | 26.12 | 54.485 | 6.4 | 1.161 | 3.551 | 7454.89 | 1.249 | 97.3 | 75.4 | 1317 | 27.29 | 4845.7 | 2402.7 | 2441.4 | 3568 | 1185.8 | 0.65671 | 4.713
2024-12-09 | 13:44 | Data | 0 | 34.85 | 33.642 | 133.074 | 7.64 | 125.842 | 2029.1 | 26.12 | 54.756 | 6.4 | 1.166 | 3.57 | 7454.89 | 1.168 | 97.3 | 75.4 | 1319 | 27.38 | 4845.7 | 2423.1 | 2440.1 | 3579.6 | 1185.8 | 0.6611 | 4.735
2024-12-09 | 13:44 | Data | 0 | 34.465 | 33.507 | 133.074 | 7.63 | 125.706 | 2029.1 | 26.12 | 54.575 | 6.4 | 1.169 | 3.575 | 7468.46 | 1.127 | 97.3 | 75.4 | 1318 | 27.24 | 4854.5 | 2405.7 | 2433 | 3562 | 1185.8 | 0.65828 | 4.745
2024-12-09 | 13:44 | Data | 0 | 34.621 | 33.527 | 132.984 | 7.63 | 125.706 | 2030.01 | 26.13 | 54.394 | 6.4 | 1.173 | 3.561 | 7463.94 | 1.161 | 97.3 | 75.2 | 1320 | 27.29 | 4851.6 | 2415.4 | 2419 | 3562.6 | 1185.9 | 0.66374 | 4.734
2024-12-09 | 13:44 | Data | 0 | 34.546 | 33.412 | 133.164 | 7.64 | 125.797 | 2030.01 | 26.12 | 54.575 | 6.4 | 1.157 | 3.536 | 7445.85 | 1.141 | 97.3 | 75.4 | 1319 | 27.29 | 4839.8 | 2433 | 2422.2 | 3576.2 | 1185.9 | 0.66347 | 4.693
2024-12-09 | 13:44 | Data | 0 | 34.783 | 33.615 | 133.119 | 7.63 | 125.797 | 2026.39 | 26.13 | 54.214 | 6.4 | 1.161 | 3.564 | 7454.89 | 1.087 | 97.3 | 75.4 | 1317 | 27.15 | 4845.7 | 2429.8 | 2412.1 | 3564.4 | 1185.9 | 0.66672 | 4.725
2024-12-09 | 13:44 | Data | 0 | 34.573 | 33.412 | 132.984 | 7.63 | 125.706 | 2022.78 | 26.12 | 54.485 | 6.4 | 1.167 | 3.561 | 7468.46 | 1.154 | 97.3 | 75.3 | 1316 | 27.33 | 4854.5 | 2416.7 | 2413.8 | 3564.2 | 1185.9 | 0.66369 | 4.726
2024-12-09 | 13:44 | Data | 0 | 34.567 | 33.527 | 132.938 | 7.63 | 125.797 | 2022.78 | 26.13 | 54.485 | 6.41 | 1.152 | 3.538 | 7468.46 | 1.154 | 97.3 | 75.4 | 1315 | 27.24 | 4854.5 | 2418 | 2418.9 | 3567.1 | 1185.9 | 0.66091 | 4.691
2024-12-09 | 13:44 | Data | 0 | 34.796 | 33.48 | 133.119 | 7.63 | 125.842 | 2018.26 | 26.13 | 54.394 | 6.4 | 1.165 | 3.536 | 7468.46 | 1.337 | 97.3 | 75.2 | 1311 | 27.24 | 4854.5 | 2418.7 | 2426.9 | 3567.3 | 1185.9 | 0.66129 | 4.701
2024-12-09 | 13:44 | Data | 0 | 34.573 | 33.5 | 132.984 | 7.64 | 125.706 | 2021.87 | 26.12 | 54.575 | 6.4 | 1.159 | 3.54 | 7454.89 | 1.04 | 97.3 | 75.3 | 1315 | 27.24 | 4845.7 | 2421.6 | 2435.6 | 3581.7 | 1185.9 | 0.66058 | 4.699
2024-12-09 | 13:44 | Data | 0 | 34.796 | 33.756 | 133.074 | 7.64 | 125.797 | 2023.68 | 26.12 | 54.304 | 6.4 | 1.16 | 3.554 | 7468.46 | 1.181 | 97.3 | 75.4 | 1315 | 27.15 | 4854.5 | 2413.9 | 2433 | 3569.5 | 1185.9 | 0.65919 | 4.713
2024-12-09 | 13:44 | Data | 0 | 34.931 | 33.696 | 133.119 | 7.64 | 125.797 | 2020.97 | 26.14 | 54.485 | 6.4 | 1.162 | 3.58 | 7477.5 | 1.404 | 97.3 | 75.5 | 1314 | 27.24 | 4860.4 | 2418.9 | 2441 | 3583.2 | 1185.9 | 0.65909 | 4.74
2024-12-09 | 13:44 | Data | 0 | 34.789 | 33.25 | 132.984 | 7.63 | 125.797 | 2020.07 | 26.12 | 54.575 | 6.4 | 1.156 | 3.576 | 7477.5 | 1.283 | 97.3 | 75.6 | 1314 | 27.29 | 4860.4 | 2420.1 | 2429.6 | 3571.8 | 1185.9 | 0.66129 | 4.731
2024-12-09 | 13:44 | Data | 0 | 34.573 | 33.419 | 133.074 | 7.64 | 125.706 | 2022.78 | 26.13 | 54.575 | 6.4 | 1.156 | 3.573 | 7482.02 | 1.303 | 97.3 | 75.6 | 1315 | 27.24 | 4863.3 | 2421.9 | 2442.8 | 3586.7 | 1185.9 | 0.6583 | 4.729
2024-12-09 | 13:45 | Data | 0 | 34.573 | 33.628 | 133.074 | 7.64 | 125.797 | 2020.97 | 26.12 | 54.575 | 6.4 | 1.162 | 3.555 | 7472.98 | 0.979 | 97.3 | 75.4 | 1314 | 27.24 | 4857.4 | 2421 | 2416 | 3561.4 | 1185.9 | 0.66211 | 4.716
2024-12-09 | 13:45 | Data | 0 | 34.789 | 33.52 | 132.984 | 7.64 | 125.706 | 2020.97 | 26.13 | 54.485 | 6.4 | 1.155 | 3.582 | 7477.5 | 1.161 | 97.3 | 75.6 | 1313 | 27.24 | 4860.4 | 2410.6 | 2437.5 | 3573.5 | 1185.9 | 0.65882 | 4.738
2024-12-09 | 13:45 | Data | 0 | 34.681 | 33.628 | 132.984 | 7.63 | 125.706 | 2020.07 | 26.12 | 54.485 | 6.39 | 1.162 | 3.555 | 7482.02 | 1.154 | 97.3 | 75.4 | 1314 | 27.24 | 4863.3 | 2422 | 2415.3 | 3563.2 | 1185.9 | 0.66218 | 4.717
2024-12-09 | 13:45 | Data | 0 | 34.681 | 33.615 | 133.074 | 7.64 | 125.706 | 2020.97 | 26.12 | 54.575 | 6.4 | 1.15 | 3.537 | 7486.55 | 1.195 | 97.3 | 75.5 | 1314 | 27.29 | 4866.3 | 2417.6 | 2422.8 | 3566.9 | 1185.9 | 0.66242 | 4.687
2024-12-09 | 13:45 | Data | 0 | 34.58 | 33.412 | 133.119 | 7.64 | 125.706 | 2021.87 | 26.12 | 54.575 | 6.41 | 1.161 | 3.551 | 7468.46 | 1.154 | 97.3 | 75.4 | 1314 | 27.29 | 4854.5 | 2410.1 | 2413.4 | 3558.4 | 1185.9 | 0.66001 | 4.711
2024-12-09 | 13:45 | Data | 0 | 34.6 | 33.594 | 133.119 | 7.64 | 125.706 | 2017.35 | 26.12 | 54.575 | 6.4 | 1.164 | 3.563 | 7463.94 | 1.033 | 97.3 | 75.4 | 1312 | 27.29 | 4851.6 | 2418 | 2421.1 | 3566.4 | 1185.9 | 0.66296 | 4.727
2024-12-09 | 13:45 | Data | 0 | 34.681 | 33.527 | 133.074 | 7.63 | 125.706 | 2018.26 | 26.13 | 54.665 | 6.4 | 1.166 | 3.578 | 7482.02 | 1.371 | 97.3 | 75.4 | 1312 | 27.29 | 4863.3 | 2404.3 | 2417.1 | 3553.3 | 1185.9 | 0.66032 | 4.743
2024-12-09 | 13:45 | Data | 0 | 34.708 | 33.412 | 133.074 | 7.63 | 125.797 | 2018.26 | 26.13 | 54.485 | 6.41 | 1.159 | 3.564 | 7468.46 | 0.959 | 97.3 | 75.5 | 1311 | 27.29 | 4854.5 | 2408.2 | 2416.9 | 3554.3 | 1185.9 | 0.66145 | 4.723
2024-12-09 | 13:45 | Data | 0 | 34.681 | 33.736 | 133.21 | 7.64 | 125.797 | 2018.26 | 26.12 | 54.575 | 6.4 | 1.168 | 3.54 | 7468.46 | 1.087 | 97.3 | 75.2 | 1311 | 27.29 | 4854.5 | 2414.5 | 2430.6 | 3562.9 | 1185.9 | 0.66148 | 4.708
2024-12-09 | 13:45 | Data | 0 | 34.789 | 33.419 | 133.119 | 7.63 | 125.842 | 2018.26 | 26.12 | 54.575 | 6.4 | 1.164 | 3.531 | 7468.46 | 1.33 | 97.3 | 75.2 | 1312 | 27.29 | 4854.5 | 2418.4 | 2426.9 | 3570.4 | 1185.9 | 0.65969 | 4.694
2024-12-09 | 13:45 | Data | 0 | 34.634 | 33.419 | 132.984 | 7.63 | 125.797 | 2018.26 | 26.12 | 54.575 | 6.4 | 1.167 | 3.546 | 7463.94 | 1.168 | 97.3 | 75.2 | 1312 | 27.33 | 4851.6 | 2412.7 | 2410.4 | 3554.1 | 1185.9 | 0.66336 | 4.712
2024-12-09 | 13:45 | Data | 0 | 34.783 | 33.615 | 133.164 | 7.64 | 125.797 | 2018.26 | 26.12 | 54.575 | 6.4 | 1.172 | 3.577 | 7463.94 | 1.087 | 97.3 | 75.3 | 1312 | 27.24 | 4851.6 | 2415.6 | 2421.1 | 3563.8 | 1185.9 | 0.66219 | 4.751
2024-12-09 | 13:45 | Data | 0 | 34.911 | 33.466 | 133.21 | 7.64 | 125.842 | 2020.07 | 26.13 | 54.575 | 6.4 | 1.166 | 3.582 | 7482.02 | 1.283 | 97.3 | 75.4 | 1313 | 27.29 | 4863.3 | 2425.1 | 2409.7 | 3561.5 | 1185.9 | 0.66546 | 4.747
2024-12-09 | 13:45 | Data | 0 | 34.58 | 33.615 | 133.119 | 7.63 | 125.797 | 2020.07 | 26.13 | 54.485 | 6.4 | 1.161 | 3.558 | 7459.41 | 1.215 | 97.3 | 75.4 | 1313 | 27.24 | 4848.6 | 2424.4 | 2414 | 3565 | 1185.9 | 0.66251 | 4.72
2024-12-09 | 13:45 | Data | 0 | 34.594 | 33.432 | 133.074 | 7.64 | 125.706 | 2017.35 | 26.11 | 54.485 | 6.4 | 1.151 | 3.57 | 7468.46 | 1.289 | 97.3 | 75.6 | 1312 | 27.29 | 4854.5 | 2405.5 | 2411.3 | 3554 | 1185.9 | 0.66103 | 4.722
2024-12-09 | 13:45 | Data | 0 | 34.911 | 33.669 | 133.164 | 7.64 | 125.887 | 2020.97 | 26.13 | 54.575 | 6.4 | 1.152 | 3.551 | 7463.94 | 1.262 | 97.3 | 75.5 | 1314 | 27.29 | 4851.6 | 2401 | 2415.4 | 3550.3 | 1185.9 | 0.66422 | 4.703
2024-12-09 | 13:45 | Data | 0 | 34.573 | 33.635 | 133.164 | 7.63 | 125.842 | 2023.68 | 26.11 | 54.575 | 6.4 | 1.153 | 3.54 | 7463.94 | 1.134 | 97.3 | 75.4 | 1315 | 27.29 | 4851.6 | 2415.5 | 2420.7 | 3565.6 | 1185.9 | 0.6616 | 4.694
2024-12-09 | 13:45 | Data | 0 | 34.573 | 33.527 | 133.164 | 7.64 | 125.797 | 2025.49 | 26.12 | 54.575 | 6.4 | 1.159 | 3.553 | 7468.46 | 1.161 | 97.3 | 75.4 | 1317 | 27.29 | 4854.5 | 2419.6 | 2417.3 | 3561.2 | 1185.9 | 0.66334 | 4.712
2024-12-09 | 13:46 | Data | 0 | 34.911 | 33.554 | 133.074 | 7.64 | 125.842 | 2025.49 | 26.12 | 54.485 | 6.4 | 1.166 | 3.563 | 7477.5 | 1.087 | 97.3 | 75.3 | 1317 | 27.29 | 4860.4 | 2419.7 | 2394.3 | 3547.6 | 1185.9 | 0.6663 | 4.729
2024-12-09 | 13:46 | Data | 0 | 34.958 | 33.466 | 133.164 | 7.63 | 125.887 | 2025.49 | 26.12 | 54.485 | 6.4 | 1.161 | 3.581 | 7463.94 | 1.35 | 97.3 | 75.5 | 1317 | 27.29 | 4851.6 | 2410.3 | 2414.6 | 3555.1 | 1185.9 | 0.66139 | 4.742
2024-12-09 | 13:46 | Data | 0 | 34.594 | 33.642 | 133.164 | 7.63 | 125.887 | 2022.78 | 26.13 | 54.485 | 6.4 | 1.162 | 3.559 | 7486.55 | 1.053 | 97.3 | 75.4 | 1315 | 27.24 | 4866.3 | 2423.6 | 2420.2 | 3571 | 1185.9 | 0.66208 | 4.719
2024-12-09 | 13:46 | Data | 0 | 34.573 | 33.588 | 133.119 | 7.64 | 125.797 | 2022.78 | 26.12 | 54.575 | 6.41 | 1.15 | 3.576 | 7477.5 | 1.154 | 97.3 | 75.7 | 1315 | 27.29 | 4860.4 | 2420 | 2416.7 | 3563.7 | 1185.9 | 0.66416 | 4.727
2024-12-09 | 13:46 | Data | 0 | 34.796 | 33.419 | 133.074 | 7.64 | 125.797 | 2024.58 | 26.12 | 54.575 | 6.4 | 1.164 | 3.575 | 7477.5 | 1.33 | 97.3 | 75.4 | 1316 | 27.29 | 4860.4 | 2416.2 | 2399.2 | 3550.4 | 1185.9 | 0.66478 | 4.739
2024-12-09 | 13:46 | Data | 0 | 34.594 | 33.588 | 133.119 | 7.63 | 125.797 | 2024.58 | 26.13 | 54.485 | 6.4 | 1.161 | 3.572 | 7477.5 | 1.1 | 97.3 | 75.5 | 1315 | 27.24 | 4860.4 | 2421 | 2411.9 | 3559.7 | 1185.9 | 0.66632 | 4.733
2024-12-09 | 13:46 | Data | 0 | 34.627 | 33.412 | 133.074 | 7.63 | 125.887 | 2022.78 | 26.13 | 54.304 | 6.4 | 1.159 | 3.564 | 7477.5 | 1.154 | 97.3 | 75.5 | 1315 | 27.15 | 4860.4 | 2417 | 2417.7 | 3561.5 | 1185.9 | 0.66239 | 4.723
2024-12-09 | 13:46 | Data | 0 | 34.783 | 33.642 | 133.21 | 7.64 | 125.797 | 2023.68 | 26.12 | 54.575 | 6.4 | 1.16 | 3.572 | 7468.46 | 1.371 | 97.3 | 75.5 | 1315 | 27.29 | 4854.5 | 2409.3 | 2428.3 | 3567.5 | 1185.9 | 0.66035 | 4.731
2024-12-09 | 13:46 | Data | 0 | 34.789 | 33.642 | 133.164 | 7.64 | 125.797 | 2025.49 | 26.12 | 54.575 | 6.4 | 1.152 | 3.575 | 7463.94 | 1.154 | 97.3 | 75.6 | 1317 | 27.29 | 4851.6 | 2405 | 2411.9 | 3551 | 1185.9 | 0.66259 | 4.728
2024-12-09 | 13:46 | Data | 0 | 34.911 | 33.534 | 133.074 | 7.63 | 125.887 | 2026.39 | 26.12 | 54.575 | 6.41 | 1.166 | 3.556 | 7477.5 | 1.181 | 97.3 | 75.3 | 1317 | 27.29 | 4860.4 | 2404.5 | 2434.1 | 3566.2 | 1185.9 | 0.65713 | 4.721
2024-12-09 | 13:46 | Data | 0 | 34.796 | 33.527 | 133.119 | 7.64 | 125.797 | 2025.49 | 26.12 | 54.575 | 6.4 | 1.159 | 3.566 | 7482.02 | 1.269 | 97.3 | 75.5 | 1317 | 27.29 | 4863.3 | 2414.8 | 2420 | 3562 | 1185.9 | 0.66075 | 4.724
2024-12-09 | 13:46 | Data | 0 | 34.621 | 33.426 | 133.119 | 7.64 | 125.842 | 2025.49 | 26.12 | 54.575 | 6.4 | 1.163 | 3.538 | 7472.98 | 1.141 | 97.3 | 75.2 | 1317 | 27.33 | 4857.4 | 2403.4 | 2419.7 | 3556 | 1185.9 | 0.65991 | 4.702
2024-12-09 | 13:46 | Data | 0 | 34.904 | 33.642 | 133.119 | 7.63 | 125.797 | 2029.1 | 26.12 | 54.485 | 6.41 | 1.165 | 3.547 | 7468.46 | 1.256 | 97.3 | 75.3 | 1320 | 27.24 | 4854.5 | 2432.6 | 2431.1 | 3579.9 | 1185.9 | 0.66509 | 4.711
2024-12-09 | 13:46 | Data | 0 | 35.019 | 33.696 | 133.21 | 7.64 | 125.977 | 2030.01 | 26.13 | 55.026 | 6.4 | 1.169 | 3.574 | 7468.46 | 1.148 | 97.3 | 75.3 | 1319 | 27.51 | 4854.5 | 2422 | 2404.1 | 3547.5 | 1185.9 | 0.66331 | 4.743
2024-12-09 | 13:46 | Data | 0 | 34.796 | 33.588 | 133.074 | 7.64 | 125.797 | 2026.39 | 26.13 | 54.485 | 6.4 | 1.159 | 3.576 | 7472.98 | 1.06 | 97.3 | 75.5 | 1317 | 27.29 | 4857.4 | 2434.6 | 2433 | 3580.5 | 1185.9 | 0.66362 | 4.735
2024-12-09 | 13:46 | Data | 0 | 34.796 | 33.642 | 133.074 | 7.63 | 125.842 | 2026.39 | 26.11 | 54.485 | 6.4 | 1.155 | 3.562 | 7463.94 | 1.161 | 97.3 | 75.5 | 1317 | 27.29 | 4851.6 | 2419.7 | 2415.2 | 3559 | 1186 | 0.66438 | 4.718
2024-12-09 | 13:46 | Data | 0 | 34.85 | 33.669 | 133.164 | 7.64 | 125.887 | 2025.49 | 26.12 | 54.575 | 6.41 | 1.154 | 3.569 | 7468.46 | 1.046 | 97.3 | 75.6 | 1317 | 27.29 | 4854.5 | 2413.6 | 2414.4 | 3559.4 | 1186 | 0.66111 | 4.723
2024-12-09 | 13:46 | Data | 0 | 34.796 | 33.723 | 133.21 | 7.64 | 125.842 | 2030.01 | 26.12 | 54.485 | 6.4 | 1.15 | 3.565 | 7463.94 | 1.1 | 97.3 | 75.6 | 1319 | 27.24 | 4851.6 | 2406 | 2421.7 | 3557.1 | 1186 | 0.66223 | 4.716
2024-12-09 | 13:47 | Data | 0 | 34.769 | 33.864 | 133.21 | 7.63 | 125.932 | 2029.1 | 26.12 | 54.575 | 6.4 | 1.164 | 3.57 | 7468.46 | 1.175 | 97.3 | 75.4 | 1319 | 27.24 | 4854.5 | 2421.2 | 2413.1 | 3554.6 | 1186 | 0.66177 | 4.734
2024-12-09 | 13:47 | Data | 0 | 35.113 | 33.648 | 133.255 | 7.64 | 125.887 | 2029.1 | 26.13 | 54.485 | 6.4 | 1.161 | 3.579 | 7477.5 | 1.337 | 97.3 | 75.5 | 1320 | 27.24 | 4860.4 | 2425.5 | 2415.4 | 3565.1 | 1186 | 0.66373 | 4.74
2024-12-09 | 13:47 | Data | 0 | 34.681 | 33.615 | 133.21 | 7.63 | 125.887 | 2031.81 | 26.12 | 54.394 | 6.4 | 1.162 | 3.567 | 7491.07 | 1.195 | 97.3 | 75.4 | 1321 | 27.15 | 4869.2 | 1328.8 | 1777.7 | 2237 | 1186 | 0.59156 | 4.729
2024-12-09 | 13:47 | Data | 0 | 34.681 | 33.527 | 133.164 | 7.63 | 125.932 | 2032.72 | 26.12 | 54.575 | 6.41 | 1.152 | 3.555 | 7482.02 | 1.357 | 97.3 | 75.5 | 1320 | 27.33 | 4863.3 | 1332.6 | 1772.8 | 2236.6 | 1186 | 0.59414 | 4.706
2024-12-09 | 13:47 | Data | 0 | 34.573 | 33.439 | 133.255 | 7.63 | 125.887 | 2031.81 | 26.12 | 54.485 | 6.4 | 1.161 | 3.556 | 7477.5 | 1.161 | 97.3 | 75.4 | 1321 | 27.24 | 4860.4 | 1325.3 | 1807.8 | 2260.3 | 1186 | 0.58512 | 4.717
2024-12-09 | 13:47 | Data | 0 | 34.796 | 33.473 | 133.164 | 7.64 | 125.842 | 2034.53 | 26.12 | 54.575 | 6.4 | 1.165 | 3.547 | 7491.07 | 1.154 | 97.3 | 75.3 | 1322 | 27.29 | 4869.2 | 1341.8 | 1777.2 | 2244.8 | 1186 | 0.59599 | 4.712
2024-12-09 | 13:47 | Data | 0 | 34.796 | 33.588 | 133.074 | 7.64 | 125.842 | 2034.53 | 26.12 | 54.485 | 6.4 | 1.165 | 3.551 | 7472.98 | 1.377 | 97.3 | 75.3 | 1322 | 27.2 | 4857.4 | 1339.4 | 1794 | 2256.3 | 1186 | 0.59195 | 4.717
2024-12-09 | 13:47 | Data | 0 | 35.012 | 33.696 | 133.255 | 7.63 | 125.977 | 2031.81 | 26.12 | 54.485 | 6.41 | 1.164 | 3.548 | 7477.5 | 1.148 | 97.3 | 75.3 | 1321 | 27.29 | 4860.4 | 1341.2 | 1772.1 | 2241.7 | 1186 | 0.59761 | 4.712
2024-12-09 | 13:47 | Data | 0 | 34.756 | 33.669 | 133.164 | 7.64 | 125.887 | 2031.81 | 26.13 | 54.485 | 6.4 | 1.161 | 3.578 | 7482.02 | 1.087 | 97.3 | 75.5 | 1321 | 27.29 | 4863.3 | 1333.5 | 1766.7 | 2230.7 | 1186 | 0.59665 | 4.739
2024-12-09 | 13:47 | Data | 0 | 34.796 | 33.507 | 133.255 | 7.63 | 125.932 | 2031.81 | 26.12 | 54.665 | 6.4 | 1.162 | 3.56 | 7477.5 | 1.195 | 97.3 | 75.4 | 1321 | 27.29 | 4860.4 | 1336.1 | 1776.2 | 2241.7 | 1186 | 0.59404 | 4.722
2024-12-09 | 13:47 | Data | 0 | 34.796 | 33.534 | 133.074 | 7.64 | 125.797 | 2031.81 | 26.12 | 54.575 | 6.41 | 1.162 | 3.545 | 7495.59 | 1.208 | 97.3 | 75.3 | 1320 | 27.29 | 4872.1 | 1339 | 1783.3 | 2247.7 | 1186 | 0.59484 | 4.706
2024-12-09 | 13:47 | Data | 0 | 35.026 | 33.75 | 133.255 | 7.64 | 125.932 | 2031.81 | 26.13 | 54.485 | 6.4 | 1.162 | 3.561 | 7477.5 | 1.161 | 97.3 | 75.4 | 1321 | 27.29 | 4860.4 | 1330.7 | 1791.3 | 2251.3 | 1186 | 0.58992 | 4.723
2024-12-09 | 13:47 | Data | 0 | 34.85 | 33.662 | 133.164 | 7.63 | 125.932 | 2030.91 | 26.13 | 54.575 | 6.4 | 1.168 | 3.565 | 7477.5 | 1.08 | 97.3 | 75.3 | 1320 | 27.29 | 4860.4 | 1334.1 | 1775.5 | 2236.9 | 1186 | 0.59374 | 4.732
2024-12-09 | 13:47 | Data | 0 | 34.587 | 33.743 | 133.119 | 7.64 | 125.887 | 2031.81 | 26.12 | 54.394 | 6.4 | 1.166 | 3.573 | 7477.5 | 1.1 | 97.3 | 75.4 | 1321 | 27.2 | 4860.4 | 1342.5 | 1792.6 | 2258.5 | 1186 | 0.59072 | 4.738
2024-12-09 | 13:47 | Data | 0 | 34.695 | 33.621 | 133.21 | 7.64 | 125.842 | 2033.62 | 26.1 | 54.575 | 6.4 | 1.157 | 3.552 | 7482.02 | 0.979 | 97.3 | 75.4 | 1320 | 27.29 | 4863.3 | 1323.1 | 1764.6 | 2224.8 | 1186 | 0.59378 | 4.709
2024-12-09 | 13:47 | Data | 0 | 34.749 | 33.635 | 133.119 | 7.63 | 125.706 | 2032.72 | 26.12 | 54.575 | 6.4 | 1.155 | 3.545 | 7495.59 | 1.33 | 97.3 | 75.4 | 1321 | 27.29 | 4872.1 | 1325.3 | 1777.1 | 2236.4 | 1186 | 0.59129 | 4.699
2024-12-09 | 13:47 | Data | 0 | 34.681 | 33.473 | 133.164 | 7.63 | 125.842 | 2029.1 | 26.13 | 54.485 | 6.4 | 1.159 | 3.555 | 7482.02 | 1.215 | 97.3 | 75.4 | 1319 | 27.24 | 4863.3 | 1338.7 | 1772.1 | 2238.9 | 1186 | 0.59579 | 4.713
2024-12-09 | 13:48 | Data | 0 | 34.58 | 33.655 | 133.164 | 7.64 | 125.842 | 2029.1 | 26.12 | 55.026 | 6.4 | 1.154 | 3.551 | 7482.02 | 1.296 | 97.3 | 75.5 | 1319 | 27.51 | 4863.3 | 1344.9 | 1795.1 | 2260.7 | 1186 | 0.59127 | 4.706
2024-12-09 | 13:48 | Data | 0 | 34.573 | 33.635 | 133.345 | 7.64 | 125.887 | 2031.81 | 26.12 | 54.394 | 6.41 | 1.159 | 3.573 | 7468.46 | 1.141 | 97.3 | 75.5 | 1321 | 27.24 | 4854.5 | 1343.1 | 1794.9 | 2258.3 | 1186 | 0.58974 | 4.73
2024-12-09 | 13:48 | Data | 0 | 34.796 | 33.534 | 133.119 | 7.63 | 125.842 | 2031.81 | 26.12 | 54.575 | 6.4 | 1.166 | 3.584 | 7468.46 | 1.371 | 97.3 | 75.5 | 1321 | 27.29 | 4854.5 | 1338.8 | 1798.2 | 2253.9 | 1186 | 0.58863 | 4.749
2024-12-09 | 13:48 | Data | 0 | 34.695 | 33.54 | 133.164 | 7.63 | 125.887 | 2032.72 | 26.12 | 54.575 | 6.4 | 1.159 | 3.569 | 7468.46 | 1.154 | 97.3 | 75.5 | 1321 | 27.29 | 4854.5 | 1324.4 | 1810.3 | 2261.7 | 1186 | 0.58414 | 4.729
2024-12-09 | 13:48 | Data | 0 | 34.783 | 33.635 | 133.164 | 7.64 | 125.842 | 2029.1 | 26.12 | 54.575 | 6.41 | 1.151 | 3.563 | 7454.89 | 1.175 | 97.3 | 75.6 | 1320 | 27.29 | 4845.7 | 1340.2 | 1805.8 | 2277.7 | 1186 | 0.59026 | 4.714
2024-12-09 | 13:48 | Data | 0 | 34.742 | 33.689 | 133.21 | 7.64 | 125.887 | 2030.91 | 26.12 | 54.575 | 6.4 | 1.155 | 3.558 | 7454.89 | 1.262 | 97.3 | 75.5 | 1319 | 27.29 | 4845.7 | 1341.3 | 1783.2 | 2249.8 | 1186 | 0.59382 | 4.715
2024-12-09 | 13:48 | Data | 0 | 34.783 | 33.5 | 133.074 | 7.64 | 125.706 | 2030.01 | 26.13 | 54.665 | 6.41 | 1.168 | 3.567 | 7463.94 | 1.208 | 97.3 | 75.3 | 1319 | 27.2 | 4851.6 | 1345.4 | 1800.3 | 2265.7 | 1186 | 0.59106 | 4.737
2024-12-09 | 13:48 | Data | 0 | 34.573 | 33.412 | 133.119 | 7.64 | 125.842 | 2025.49 | 26.13 | 54.485 | 6.41 | 1.17 | 3.559 | 7463.94 | 1.262 | 97.3 | 75.2 | 1316 | 27.29 | 4851.6 | 1328.4 | 1779.2 | 2240.7 | 1186 | 0.59174 | 4.73
2024-12-09 | 13:48 | Data | 0 | 34.688 | 33.594 | 133.164 | 7.63 | 125.842 | 2026.39 | 26.12 | 54.485 | 6.4 | 1.16 | 3.546 | 7482.02 | 0.986 | 97.3 | 75.4 | 1317 | 27.24 | 4863.3 | 1340.1 | 1779.2 | 2245.8 | 1186 | 0.59514 | 4.706
2024-12-09 | 13:48 | Data | 0 | 34.796 | 33.466 | 132.984 | 7.63 | 125.797 | 2026.39 | 26.12 | 54.485 | 6.41 | 1.163 | 3.573 | 7454.89 | 1.154 | 97.3 | 75.4 | 1317 | 27.29 | 4845.7 | 1319.8 | 1785.4 | 2241.8 | 1186 | 0.58753 | 4.736
2024-12-09 | 13:48 | Data | 0 | 34.796 | 33.648 | 133.119 | 7.64 | 125.842 | 2023.68 | 26.13 | 54.575 | 6.4 | 1.167 | 3.577 | 7486.55 | 1.33 | 97.3 | 75.4 | 1315 | 27.29 | 4866.3 | 1332.1 | 1781.6 | 2241.9 | 1186 | 0.59325 | 4.743
2024-12-09 | 13:48 | Data | 0 | 34.816 | 33.426 | 133.164 | 7.63 | 125.887 | 2024.58 | 26.13 | 54.485 | 6.41 | 1.171 | 3.553 | 7482.02 | 1.249 | 97.3 | 75.2 | 1316 | 27.24 | 4863.3 | 1327 | 1784.8 | 2241.7 | 1186 | 0.5923 | 4.724
2024-12-09 | 13:48 | Data | 0 | 34.58 | 33.527 | 133.119 | 7.63 | 125.797 | 2022.78 | 26.12 | 54.485 | 6.4 | 1.167 | 3.553 | 7482.02 | 1.161 | 97.3 | 75.3 | 1315 | 27.29 | 4863.3 | 1338.4 | 1790.4 | 2252.4 | 1186 | 0.59465 | 4.72
2024-12-09 | 13:48 | Data | 0 | 34.567 | 33.635 | 133.119 | 7.63 | 125.797 | 2025.49 | 26.12 | 54.846 | 6.4 | 1.162 | 3.563 | 7482.02 | 1.067 | 97.3 | 75.4 | 1317 | 27.38 | 4863.3 | 1338.7 | 1806.5 | 2264.7 | 1186 | 0.58953 | 4.724
2024-12-09 | 13:48 | Data | 0 | 34.796 | 33.642 | 133.119 | 7.64 | 125.797 | 2022.78 | 26.13 | 54.485 | 6.4 | 1.16 | 3.578 | 7459.41 | 1.161 | 97.3 | 75.5 | 1315 | 27.29 | 4848.6 | 1345.9 | 1812.4 | 2275 | 1186 | 0.58901 | 4.738
2024-12-09 | 13:48 | Data | 0 | 34.796 | 33.642 | 133.21 | 7.63 | 125.887 | 2022.78 | 26.12 | 54.485 | 6.4 | 1.161 | 3.559 | 7477.5 | 1.154 | 97.3 | 75.4 | 1315 | 27.29 | 4860.4 | 1338.6 | 1791.5 | 2252 | 1186 | 0.59263 | 4.72
2024-12-09 | 13:48 | Data | 0 | 34.567 | 33.52 | 133.164 | 7.63 | 125.842 | 2022.78 | 26.12 | 54.394 | 6.4 | 1.165 | 3.56 | 7477.5 | 1.127 | 97.3 | 75.3 | 1315 | 27.24 | 4860.4 | 1329.8 | 1803 | 2258.9 | 1186 | 0.587 | 4.724
2024-12-09 | 13:48 | Data | 0 | 34.594 | 33.588 | 133.074 | 7.64 | 125.797 | 2023.68 | 26.12 | 54.485 | 6.4 | 1.164 | 3.573 | 7468.46 | 1.161 | 97.3 | 75.4 | 1315 | 27.29 | 4854.5 | 1333.2 | 1787.6 | 2248.4 | 1186 | 0.59081 | 4.738
2024-12-09 | 13:49 | Data | 0 | 34.789 | 33.297 | 132.984 | 7.64 | 125.842 | 2023.68 | 26.13 | 54.485 | 6.41 | 1.169 | 3.551 | 7477.5 | 1.256 | 97.3 | 75.2 | 1315 | 27.24 | 4860.4 | 1337 | 1775.1 | 2240.6 | 1186 | 0.59458 | 4.721
2024-12-09 | 13:49 | Data | 0 | 34.594 | 33.439 | 133.074 | 7.64 | 125.797 | 2022.78 | 26.12 | 54.485 | 6.41 | 1.168 | 3.558 | 7477.5 | 1.114 | 97.3 | 75.3 | 1315 | 27.24 | 4860.4 | 1330.7 | 1790.1 | 2249.5 | 1186 | 0.59003 | 4.726
2024-12-09 | 13:49 | Data | 0 | 34.681 | 33.52 | 133.164 | 7.64 | 125.887 | 2020.97 | 26.12 | 54.575 | 6.41 | 1.166 | 3.552 | 7477.5 | 1.175 | 97.3 | 75.3 | 1312 | 27.24 | 4860.4 | 1327.7 | 1775.2 | 2235.2 | 1186 | 0.59311 | 4.718
2024-12-09 | 13:49 | Data | 0 | 34.769 | 33.635 | 133.21 | 7.64 | 125.797 | 2018.26 | 26.12 | 54.485 | 6.4 | 1.165 | 3.566 | 7482.02 | 1.175 | 97.3 | 75.4 | 1312 | 27.24 | 4863.3 | 1330.7 | 1778.5 | 2240.4 | 1186 | 0.5929 | 4.732
2024-12-09 | 13:49 | Data | 0 | 34.708 | 33.412 | 133.074 | 7.63 | 125.797 | 2018.26 | 26.13 | 54.485 | 6.4 | 1.166 | 3.532 | 7486.55 | 1.188 | 97.3 | 75.2 | 1312 | 27.29 | 4866.3 | 1328.4 | 1769.2 | 2231.1 | 1186 | 0.59618 | 4.698
2024-12-09 | 13:49 | Data | 0 | 34.627 | 33.412 | 133.119 | 7.63 | 125.887 | 2015.55 | 26.11 | 54.485 | 6.4 | 1.163 | 3.565 | 7468.46 | 1.168 | 97.3 | 75.4 | 1311 | 27.29 | 4854.5 | 1330.7 | 1766.8 | 2228.8 | 1186 | 0.59193 | 4.728
2024-12-09 | 13:49 | Data | 0 | 34.769 | 33.412 | 133.074 | 7.63 | 125.797 | 2017.35 | 26.13 | 54.575 | 6.4 | 1.159 | 3.584 | 7491.07 | 1.377 | 97.3 | 75.6 | 1311 | 27.29 | 4869.2 | 1330.7 | 1783.8 | 2245 | 1186 | 0.59155 | 4.743
2024-12-09 | 13:49 | Data | 0 | 34.796 | 33.534 | 132.757 | 7.64 | 125.48 | 2020.97 | 26.12 | 54.304 | 6.41 | 1.159 | 3.585 | 7482.02 | 1.31 | 97.3 | 75.6 | 1314 | 27.11 | 4863.3 | 1337.2 | 1787.1 | 2250.7 | 1186 | 0.59144 | 4.745
2024-12-09 | 13:49 | Data | 0 | 34.621 | 33.527 | 132.757 | 7.64 | 125.39 | 2018.26 | 26.12 | 54.485 | 6.4 | 1.157 | 3.558 | 7463.94 | 1.168 | 97.3 | 75.5 | 1311 | 27.24 | 4851.6 | 1335.7 | 1785.2 | 2246.6 | 1186 | 0.59283 | 4.715
2024-12-09 | 13:49 | Data | 0 | 34.789 | 33.642 | 132.712 | 7.64 | 125.435 | 2019.16 | 26.13 | 54.575 | 6.4 | 1.16 | 3.561 | 7477.5 | 1.161 | 97.3 | 75.4 | 1312 | 27.29 | 4860.4 | 1322.8 | 1785.8 | 2241.2 | 1186 | 0.58855 | 4.721
2024-12-09 | 13:49 | Data | 0 | 34.594 | 33.419 | 132.622 | 7.63 | 125.39 | 2015.55 | 26.12 | 54.575 | 6.4 | 1.154 | 3.57 | 7477.5 | 1.154 | 97.3 | 75.6 | 1310 | 27.33 | 4860.4 | 1315.9 | 1775.4 | 2228.1 | 1186 | 0.58859 | 4.725
2024-12-09 | 13:49 | Data | 0 | 34.567 | 33.466 | 132.712 | 7.63 | 125.39 | 2016.45 | 26.11 | 54.665 | 6.41 | 1.159 | 3.528 | 7495.59 | 0.979 | 97.3 | 75.3 | 1311 | 27.29 | 4872.1 | 1349.2 | 1793.5 | 2261.1 | 1186 | 0.59432 | 4.69
2024-12-09 | 13:49 | Data | 0 | 34.796 | 33.419 | 132.712 | 7.63 | 125.39 | 2015.55 | 26.12 | 54.485 | 6.41 | 1.159 | 3.532 | 7477.5 | 1.175 | 97.3 | 75.3 | 1310 | 27.24 | 4860.4 | 1321.2 | 1757.4 | 2217.5 | 1186 | 0.59511 | 4.689
2024-12-09 | 13:49 | Data | 0 | 34.573 | 33.635 | 132.712 | 7.63 | 125.435 | 2016.45 | 26.12 | 54.485 | 6.4 | 1.166 | 3.553 | 7468.46 | 1.114 | 97.3 | 75.3 | 1310 | 27.29 | 4854.5 | 1352.7 | 1752.5 | 2214.8 | 1186 | 0.60058 | 4.719
2024-12-09 | 13:49 | Data | 0 | 34.614 | 33.412 | 132.667 | 7.64 | 125.39 | 2014.64 | 26.13 | 54.575 | 6.4 | 1.155 | 3.55 | 7482.02 | 1.161 | 97.3 | 75.5 | 1310 | 27.24 | 4863.3 | 1333.3 | 1744.6 | 2214.4 | 1186 | 0.60039 | 4.706
2024-12-09 | 13:49 | Data | 0 | 34.553 | 33.412 | 132.667 | 7.64 | 125.435 | 2015.55 | 26.12 | 54.485 | 6.4 | 1.159 | 3.551 | 7468.46 | 1.262 | 97.3 | 75.4 | 1310 | 27.29 | 4854.5 | 1337 | 1761.2 | 2230.4 | 1186 | 0.59808 | 4.71
2024-12-09 | 13:49 | Data | 0 | 34.783 | 33.466 | 132.667 | 7.64 | 125.39 | 2016.45 | 26.12 | 54.485 | 6.4 | 1.159 | 3.542 | 7482.02 | 1.33 | 97.3 | 75.3 | 1311 | 27.29 | 4863.3 | 1325.8 | 1754.6 | 2219.4 | 1186 | 0.59905 | 4.701
2024-12-09 | 13:50 | Data | 0 | 34.567 | 33.426 | 132.712 | 7.63 | 125.48 | 2020.97 | 26.13 | 54.485 | 6.4 | 1.155 | 3.57 | 7477.5 | 1.31 | 97.3 | 75.6 | 1313 | 27.24 | 4860.4 | 1311.4 | 1767.2 | 2221.3 | 1186 | 0.58531 | 4.725
2024-12-09 | 13:50 | Data | 0 | 34.783 | 33.642 | 132.712 | 7.63 | 125.435 | 2020.97 | 26.12 | 54.575 | 6.4 | 1.159 | 3.563 | 7482.02 | 1.154 | 97.3 | 75.5 | 1314 | 27.29 | 4863.3 | 1331.7 | 1787 | 2246 | 1186 | 0.59127 | 4.719
2024-12-09 | 13:50 | Data | 0 | 34.567 | 33.412 | 132.667 | 7.63 | 125.345 | 2020.07 | 26.12 | 54.846 | 6.41 | 1.157 | 3.534 | 7472.98 | 1.154 | 97.3 | 75.3 | 1314 | 27.42 | 4857.4 | 1328.5 | 1780.5 | 2239.2 | 1186 | 0.59179 | 4.693
2024-12-09 | 13:50 | Data | 0 | 34.567 | 33.459 | 132.667 | 7.64 | 125.345 | 2020.97 | 26.12 | 54.485 | 6.41 | 1.167 | 3.541 | 7491.07 | 1.222 | 97.3 | 75.2 | 1314 | 27.24 | 4869.2 | 1348.1 | 1782.4 | 2253.8 | 1186 | 0.5963 | 4.708
2024-12-09 | 13:50 | Data | 0 | 34.911 | 33.642 | 132.667 | 7.63 | 125.48 | 2022.78 | 26.12 | 54.575 | 6.4 | 1.156 | 3.558 | 7482.02 | 1.195 | 97.3 | 75.5 | 1315 | 27.29 | 4863.3 | 1327.3 | 1796 | 2251.6 | 1186 | 0.58804 | 4.714
2024-12-09 | 13:50 | Data | 0 | 34.796 | 33.628 | 132.757 | 7.64 | 125.39 | 2020.97 | 26.13 | 54.485 | 6.4 | 1.155 | 3.552 | 7482.02 | 1.175 | 97.3 | 75.5 | 1314 | 27.24 | 4863.3 | 1328.4 | 1774.9 | 2236.1 | 1186 | 0.5924 | 4.706
2024-12-09 | 13:50 | Data | 0 | 34.796 | 33.642 | 132.712 | 7.64 | 125.48 | 2022.78 | 26.13 | 54.665 | 6.4 | 1.159 | 3.551 | 7491.07 | 1.154 | 97.3 | 75.4 | 1315 | 27.24 | 4869.2 | 1340.4 | 1791.8 | 2257 | 1186 | 0.59233 | 4.71
2024-12-09 | 13:50 | Data | 0 | 34.702 | 33.419 | 132.576 | 7.63 | 125.345 | 2022.78 | 26.12 | 54.575 | 6.4 | 1.163 | 3.565 | 7486.55 | 1.303 | 97.3 | 75.4 | 1315 | 27.24 | 4866.3 | 1332.4 | 1801 | 2259.2 | 1186 | 0.58857 | 4.729
2024-12-09 | 13:50 | Data | 0 | 34.992 | 33.689 | 132.712 | 7.63 | 125.435 | 2023.68 | 26.11 | 54.575 | 6.4 | 1.167 | 3.537 | 7504.64 | 1.276 | 97.3 | 75.2 | 1316 | 27.29 | 4878 | 1320.1 | 1787.8 | 2240.4 | 1186 | 0.58805 | 4.702
2024-12-09 | 13:50 | Data | 0 | 34.999 | 33.473 | 132.712 | 7.63 | 125.435 | 2025.49 | 26.13 | 54.575 | 6.41 | 1.159 | 3.544 | 7509.16 | 1.148 | 97.3 | 75.3 | 1317 | 27.24 | 4881 | 1348.6 | 1797.1 | 2264.9 | 1186 | 0.59407 | 4.703
2024-12-09 | 13:50 | Data | 0 | 34.769 | 33.642 | 132.622 | 7.63 | 125.39 | 2025.49 | 26.14 | 54.575 | 6.41 | 1.15 | 3.558 | 7491.07 | 1.148 | 97.3 | 75.6 | 1317 | 27.29 | 4869.2 | 1317.6 | 1774.4 | 2227.8 | 1186 | 0.59046 | 4.707
2024-12-09 | 13:50 | Data | 0 | 34.573 | 33.419 | 132.667 | 7.63 | 125.39 | 2025.49 | 26.13 | 54.575 | 6.4 | 1.145 | 3.535 | 7500.11 | 1.148 | 97.3 | 75.5 | 1316 | 27.29 | 4875.1 | 1333.1 | 1762.8 | 2229.8 | 1186 | 0.59618 | 4.679
2024-12-09 | 13:50 | Data | 0 | 34.627 | 33.642 | 132.576 | 7.63 | 125.39 | 2030.01 | 26.12 | 54.756 | 6.4 | 1.153 | 3.537 | 7491.07 | 0.932 | 97.3 | 75.4 | 1320 | 27.38 | 4869.2 | 1342.7 | 1777.9 | 2246 | 1186 | 0.59689 | 4.691
2024-12-09 | 13:50 | Data | 0 | 34.769 | 33.621 | 132.667 | 7.64 | 125.39 | 2030.01 | 26.12 | 54.575 | 6.41 | 1.157 | 3.534 | 7491.07 | 1.168 | 97.3 | 75.3 | 1319 | 27.29 | 4869.2 | 1332 | 1792.7 | 2252 | 1186 | 0.59015 | 4.692
2024-12-09 | 13:50 | Data | 0 | 34.567 | 33.412 | 132.667 | 7.63 | 125.345 | 2029.1 | 26.13 | 54.846 | 6.4 | 1.154 | 3.538 | 7504.64 | 1.154 | 97.3 | 75.5 | 1319 | 27.42 | 4878 | 1313.2 | 1782.8 | 2238.7 | 1186 | 0.59057 | 4.69
2024-12-09 | 13:50 | Data | 0 | 34.398 | 33.385 | 132.667 | 7.64 | 125.345 | 2030.01 | 26.12 | 54.756 | 6.41 | 1.162 | 3.546 | 7500.11 | 1.161 | 97.3 | 75.3 | 1319 | 27.38 | 4875.1 | 1356.5 | 1786.9 | 2262.3 | 1186 | 0.59794 | 4.707
2024-12-09 | 13:50 | Data | 0 | 34.681 | 33.466 | 132.667 | 7.63 | 125.345 | 2029.1 | 26.12 | 54.575 | 6.4 | 1.157 | 3.546 | 7495.59 | 1.141 | 97.3 | 75.4 | 1318 | 27.29 | 4872.1 | 1333.2 | 1789 | 2249.5 | 1186 | 0.59093 | 4.705
2024-12-09 | 13:50 | Data | 0 | 34.567 | 33.412 | 132.667 | 7.64 | 125.39 | 2030.91 | 26.12 | 54.665 | 6.4 | 1.163 | 3.546 | 7504.64 | 1.154 | 97.3 | 75.3 | 1321 | 27.33 | 4878 | 1327.6 | 1762.2 | 2227.3 | 1186 | 0.59343 | 4.71
2024-12-09 | 13:51 | Data | 0 | 34.513 | 33.412 | 132.667 | 7.64 | 125.39 | 2023.68 | 26.12 | 54.846 | 6.4 | 1.159 | 3.514 | 7491.07 | 0.945 | 97.3 | 75.2 | 1315 | 27.42 | 4869.2 | 1334.3 | 1768.6 | 2234.1 | 1186 | 0.59638 | 4.673
2024-12-09 | 13:51 | Data | 0 | 34.681 | 33.412 | 132.622 | 7.63 | 125.39 | 2030.01 | 26.12 | 54.936 | 6.41 | 1.154 | 3.523 | 7477.5 | 1.202 | 97.3 | 75.3 | 1320 | 27.47 | 4860.4 | 2733.2 | 2835.1 | 4047.5 | 1186 | 0.64275 | 4.678
2024-12-09 | 13:51 | Data | 0 | 34.344 | 33.412 | 132.622 | 7.63 | 125.345 | 2029.1 | 26.12 | 54.846 | 6.4 | 1.156 | 3.532 | 7468.46 | 1.046 | 97.3 | 75.3 | 1319 | 27.38 | 4854.5 | 2442.6 | 2448 | 3599.4 | 1186.1 | 0.66389 | 4.688
2024-12-09 | 13:51 | Data | 0 | 34.742 | 33.412 | 132.576 | 7.64 | 125.345 | 2029.1 | 26.13 | 54.756 | 6.4 | 1.162 | 3.519 | 7463.94 | 1.175 | 97.3 | 75.2 | 1319 | 27.38 | 4851.6 | 2432.4 | 2444.2 | 3590.4 | 1186.1 | 0.66278 | 4.682
2024-12-09 | 13:51 | Data | 0 | 34.796 | 33.628 | 132.667 | 7.63 | 125.39 | 2031.81 | 26.13 | 54.756 | 6.4 | 1.159 | 3.541 | 7477.5 | 1.202 | 97.3 | 75.3 | 1321 | 27.33 | 4860.4 | 2413.3 | 2442.7 | 3584.3 | 1186.1 | 0.65744 | 4.701
2024-12-09 | 13:51 | Data | 0 | 34.769 | 33.642 | 132.667 | 7.64 | 125.345 | 2030.91 | 26.13 | 54.756 | 6.4 | 1.16 | 3.536 | 7477.5 | 1.154 | 97.3 | 75.3 | 1321 | 27.38 | 4860.4 | 2404 | 2441.8 | 3574.3 | 1186.1 | 0.65576 | 4.696
2024-12-09 | 13:51 | Data | 0 | 34.567 | 33.615 | 132.622 | 7.64 | 125.345 | 2031.81 | 26.12 | 54.756 | 6.4 | 1.151 | 3.536 | 7468.46 | 1.1 | 97.3 | 75.4 | 1321 | 27.42 | 4854.5 | 2422.4 | 2473.7 | 3606 | 1186.1 | 0.65508 | 4.687
2024-12-09 | 13:51 | Data | 0 | 34.796 | 33.419 | 132.622 | 7.63 | 125.345 | 2032.72 | 26.11 | 54.756 | 6.41 | 1.156 | 3.556 | 7482.02 | 1.195 | 97.3 | 75.5 | 1321 | 27.42 | 4863.3 | 2398.5 | 2446.4 | 3573.9 | 1186.1 | 0.65268 | 4.712
2024-12-09 | 13:51 | Data | 0 | 34.371 | 33.466 | 132.576 | 7.64 | 125.345 | 2031.81 | 26.11 | 54.846 | 6.4 | 1.155 | 3.545 | 7463.94 | 1.141 | 97.3 | 75.4 | 1321 | 27.42 | 4851.6 | 2426.2 | 2424.5 | 3587.9 | 1186.1 | 0.6664 | 4.7
2024-12-09 | 13:51 | Data | 0 | 34.567 | 33.615 | 132.712 | 7.64 | 125.345 | 2031.81 | 26.1 | 54.846 | 6.41 | 1.157 | 3.555 | 7468.46 | 1.181 | 97.3 | 75.4 | 1321 | 27.38 | 4854.5 | 2422.1 | 2459.5 | 3599.9 | 1186.1 | 0.66033 | 4.711
2024-12-09 | 13:51 | Data | 0 | 34.742 | 33.412 | 132.712 | 7.64 | 125.39 | 2030.91 | 26.1 | 54.756 | 6.41 | 1.153 | 3.571 | 7477.5 | 1.181 | 97.3 | 75.6 | 1320 | 27.38 | 4860.4 | 2399.7 | 2450.7 | 3575.7 | 1186.1 | 0.65584 | 4.724
2024-12-09 | 13:51 | Data | 0 | 34.897 | 33.689 | 132.667 | 7.63 | 125.39 | 2032.72 | 26.11 | 54.756 | 6.41 | 1.156 | 3.569 | 7472.98 | 1.269 | 97.3 | 75.5 | 1321 | 27.33 | 4857.4 | 2405.5 | 2412.5 | 3559.2 | 1186.1 | 0.66111 | 4.724
2024-12-09 | 13:51 | Data | 0 | 34.675 | 33.243 | 132.576 | 7.63 | 125.345 | 2030.91 | 26.1 | 54.846 | 6.4 | 1.163 | 3.531 | 7482.02 | 1.222 | 97.3 | 75.3 | 1320 | 27.42 | 4863.3 | 2415.7 | 2425.7 | 3565.3 | 1186.1 | 0.66319 | 4.692
2024-12-09 | 13:51 | Data | 0 | 34.769 | 33.426 | 132.667 | 7.63 | 125.39 | 2035.43 | 26.11 | 54.575 | 6.4 | 1.163 | 3.542 | 7468.46 | 1.323 | 97.3 | 75.3 | 1323 | 27.33 | 4854.5 | 2410.1 | 2430.3 | 3567.9 | 1186.1 | 0.65899 | 4.707
2024-12-09 | 13:51 | Data | 0 | 34.796 | 33.642 | 132.667 | 7.64 | 125.435 | 2036.33 | 26.11 | 54.575 | 6.41 | 1.161 | 3.543 | 7482.02 | 1.154 | 97.3 | 75.3 | 1324 | 27.24 | 4863.3 | 2423.3 | 2438.3 | 3584.4 | 1186.1 | 0.65885 | 4.703
2024-12-09 | 13:51 | Data | 0 | 34.965 | 33.655 | 132.757 | 7.63 | 125.48 | 2037.24 | 26.11 | 54.575 | 6.4 | 1.16 | 3.548 | 7482.02 | 1.249 | 97.3 | 75.4 | 1324 | 27.29 | 4863.3 | 2419.4 | 2461 | 3594.5 | 1186.1 | 0.65996 | 4.709
2024-12-09 | 13:51 | Data | 0 | 34.58 | 33.412 | 132.667 | 7.63 | 125.345 | 2037.24 | 26.1 | 54.575 | 6.4 | 1.159 | 3.526 | 7463.94 | 1.154 | 97.3 | 75.3 | 1324 | 27.29 | 4851.6 | 2423.1 | 2416.4 | 3568.7 | 1186.1 | 0.66252 | 4.686
2024-12-09 | 13:51 | Data | 0 | 34.769 | 33.588 | 132.712 | 7.63 | 125.435 | 2032.72 | 26.11 | 54.575 | 6.41 | 1.161 | 3.527 | 7445.85 | 1.377 | 97.3 | 75.2 | 1315 | 27.24 | 4839.8 | 2409 | 2450.1 | 3585.3 | 1186.1 | 0.65445 | 4.689
2024-12-09 | 13:52 | Data | 0 | 34.567 | 33.588 | 132.667 | 7.64 | 125.345 | 1936.91 | 26.11 | 54.575 | 6.41 | 1.152 | 3.548 | 7468.46 | 1.04 | 97.2 | 75.5 | 1265 | 27.29 | 4854.5 | 2417.4 | 2435.6 | 3574.1 | 1186.1 | 0.66239 | 4.701
2024-12-09 | 13:52 | Data | 0 | 34.783 | 33.412 | 132.622 | 7.63 | 125.345 | 2084.24 | 26.1 | 54.575 | 6.4 | 1.157 | 3.558 | 7454.89 | 1.181 | 97.4 | 75.5 | 1355 | 27.24 | 4845.7 | 2434.5 | 2419 | 3573.4 | 1186.1 | 0.66564 | 4.715
2024-12-09 | 13:52 | Data | 0 | 34.742 | 33.439 | 132.667 | 7.64 | 125.435 | 2082.43 | 26.1 | 54.575 | 6.41 | 1.166 | 3.546 | 7477.5 | 1.269 | 97.4 | 75.3 | 1354 | 27.29 | 4860.4 | 2428.7 | 2409.1 | 3559.3 | 1186.1 | 0.66658 | 4.711
2024-12-09 | 13:52 | Data | 0 | 34.783 | 33.419 | 132.622 | 7.64 | 125.39 | 2078.81 | 26.11 | 54.485 | 6.4 | 1.149 | 3.545 | 7468.46 | 1.364 | 97.4 | 75.5 | 1351 | 27.2 | 4854.5 | 2405.7 | 2433.3 | 3567.7 | 1186.1 | 0.65922 | 4.693
2024-12-09 | 13:52 | Data | 0 | 34.58 | 33.615 | 132.712 | 7.64 | 125.345 | 2076.1 | 26.1 | 54.575 | 6.4 | 1.153 | 3.547 | 7477.5 | 1.154 | 97.4 | 75.5 | 1349 | 27.24 | 4860.4 | 2393.8 | 2428.3 | 3562.3 | 1186.1 | 0.65638 | 4.699
2024-12-09 | 13:52 | Data | 0 | 34.567 | 33.412 | 132.667 | 7.64 | 125.39 | 2073.39 | 26.11 | 54.485 | 6.41 | 1.147 | 3.57 | 7495.59 | 1.154 | 97.4 | 75.7 | 1348 | 27.29 | 4872.1 | 2407 | 2433.6 | 3573.4 | 1186.1 | 0.65756 | 4.716
2024-12-09 | 13:52 | Data | 0 | 34.567 | 33.412 | 132.576 | 7.64 | 125.345 | 2070.68 | 26.1 | 54.575 | 6.4 | 1.172 | 3.578 | 7477.5 | 1.269 | 97.4 | 75.3 | 1346 | 27.29 | 4860.4 | 2432.6 | 2416.3 | 3574 | 1186.1 | 0.66773 | 4.749
2024-12-09 | 13:52 | Data | 0 | 34.911 | 33.642 | 132.712 | 7.63 | 125.48 | 2069.78 | 26.11 | 54.485 | 6.4 | 1.165 | 3.564 | 7482.02 | 1.323 | 97.4 | 75.4 | 1346 | 27.29 | 4863.3 | 2399.7 | 2426.8 | 3553.6 | 1186.1 | 0.65869 | 4.729
2024-12-09 | 13:52 | Data | 0 | 34.742 | 33.52 | 132.667 | 7.63 | 125.48 | 2068.87 | 26.09 | 54.485 | 6.4 | 1.149 | 3.538 | 7468.46 | 1.262 | 97.4 | 75.5 | 1344 | 27.11 | 4854.5 | 2425 | 2427.2 | 3576.1 | 1186.1 | 0.66337 | 4.689
2024-12-09 | 13:52 | Data | 0 | 34.769 | 33.311 | 132.757 | 7.64 | 125.39 | 2066.16 | 26.11 | 54.575 | 6.4 | 1.156 | 3.543 | 7482.02 | 1.276 | 97.4 | 75.4 | 1342 | 27.29 | 4863.3 | 2415.2 | 2404.3 | 3548.9 | 1186.1 | 0.6648 | 4.698
2024-12-09 | 13:52 | Data | 0 | 34.796 | 33.419 | 132.757 | 7.64 | 125.48 | 2065.26 | 26.11 | 54.575 | 6.41 | 1.155 | 3.563 | 7463.94 | 1.256 | 97.4 | 75.5 | 1342 | 27.24 | 4851.6 | 2424.8 | 2417.3 | 3563.2 | 1186.1 | 0.66334 | 4.718
2024-12-09 | 13:52 | Data | 0 | 34.58 | 33.412 | 132.622 | 7.64 | 125.435 | 2061.64 | 26.1 | 54.575 | 6.41 | 1.149 | 3.548 | 7482.02 | 1.161 | 97.4 | 75.5 | 1341 | 27.29 | 4863.3 | 2416.2 | 2430.4 | 3576.2 | 1186.1 | 0.66234 | 4.698
2024-12-09 | 13:52 | Data | 0 | 34.594 | 33.615 | 132.712 | 7.64 | 125.435 | 2059.83 | 26.11 | 54.665 | 6.41 | 1.155 | 3.553 | 7468.46 | 0.992 | 97.3 | 75.5 | 1339 | 27.29 | 4854.5 | 2430.7 | 2422.1 | 3572.9 | 1186.1 | 0.66557 | 4.709
2024-12-09 | 13:52 | Data | 0 | 34.796 | 33.419 | 132.712 | 7.63 | 125.435 | 2056.22 | 26.1 | 54.575 | 6.41 | 1.159 | 3.546 | 7482.02 | 1.371 | 97.3 | 75.4 | 1337 | 27.29 | 4863.3 | 2396.4 | 2419.9 | 3552.5 | 1186.1 | 0.65909 | 4.706
2024-12-09 | 13:52 | Data | 0 | 34.796 | 33.642 | 132.667 | 7.64 | 125.345 | 2052.6 | 26.11 | 54.846 | 6.41 | 1.152 | 3.559 | 7468.46 | 1.154 | 97.3 | 75.5 | 1333 | 27.42 | 4854.5 | 2427.4 | 2427.9 | 3579 | 1186.1 | 0.66495 | 4.713
2024-12-09 | 13:52 | Data | 0 | 34.708 | 33.466 | 132.757 | 7.64 | 125.39 | 2049.89 | 26.1 | 54.846 | 6.4 | 1.156 | 3.56 | 7463.94 | 1.154 | 97.3 | 75.5 | 1332 | 27.33 | 4851.6 | 2438.9 | 2434.9 | 3586.7 | 1186.1 | 0.66385 | 4.716
2024-12-09 | 13:52 | Data | 0 | 34.573 | 33.412 | 132.622 | 7.64 | 125.39 | 2046.28 | 26.11 | 54.575 | 6.4 | 1.162 | 3.564 | 7468.46 | 1.154 | 97.3 | 75.4 | 1328 | 27.29 | 4854.5 | 2451.6 | 2446 | 3607 | 1186.1 | 0.66347 | 4.728
2024-12-09 | 13:52 | Data | 0 | 34.573 | 33.419 | 132.712 | 7.63 | 125.435 | 2042.66 | 26.11 | 54.665 | 6.4 | 1.161 | 3.537 | 7454.89 | 1.141 | 97.3 | 75.3 | 1328 | 27.24 | 4845.7 | 2389.8 | 2421.5 | 3553 | 1186.1 | 0.65628 | 4.698
2024-12-09 | 13:53 | Data | 0 | 34.843 | 33.419 | 132.712 | 7.64 | 125.435 | 2039.95 | 26.1 | 54.575 | 6.41 | 1.156 | 3.546 | 7477.5 | 1.161 | 97.3 | 75.4 | 1326 | 27.29 | 4860.4 | 2392.9 | 2429.9 | 3561.2 | 1186.1 | 0.65495 | 4.702
2024-12-09 | 13:53 | Data | 0 | 34.621 | 33.419 | 132.712 | 7.64 | 125.39 | 2035.43 | 26.1 | 54.575 | 6.4 | 1.16 | 3.546 | 7482.02 | 1.161 | 97.3 | 75.3 | 1324 | 27.29 | 4863.3 | 2397.9 | 2425.4 | 3563 | 1186.1 | 0.65625 | 4.707
2024-12-09 | 13:53 | Data | 0 | 34.567 | 33.412 | 132.757 | 7.63 | 125.39 | 2034.53 | 26.11 | 54.394 | 6.41 | 1.159 | 3.543 | 7482.02 | 1.357 | 97.3 | 75.4 | 1322 | 27.24 | 4863.3 | 2400.5 | 2413.3 | 3555.3 | 1186.1 | 0.66031 | 4.701
2024-12-09 | 13:53 | Data | 0 | 34.627 | 33.513 | 132.757 | 7.64 | 125.435 | 2030.91 | 26.11 | 54.485 | 6.41 | 1.161 | 3.565 | 7482.02 | 0.959 | 97.3 | 75.4 | 1321 | 27.24 | 4863.3 | 2417.5 | 2407.2 | 3559.2 | 1186.1 | 0.66567 | 4.726
2024-12-09 | 13:53 | Data | 0 | 34.668 | 33.635 | 132.757 | 7.64 | 125.435 | 2034.53 | 26.11 | 54.936 | 6.4 | 1.163 | 3.554 | 7463.94 | 1.323 | 97.3 | 75.3 | 1322 | 27.42 | 4851.6 | 2404.1 | 2444.3 | 3562 | 1186.1 | 0.6575 | 4.717
2024-12-09 | 13:53 | Data | 0 | 34.783 | 33.412 | 132.667 | 7.63 | 125.39 | 2035.43 | 26.11 | 54.756 | 6.4 | 1.162 | 3.547 | 7459.41 | 1.377 | 97.3 | 75.3 | 1323 | 27.38 | 4848.6 | 2426.1 | 2430.5 | 3576.1 | 1186.1 | 0.66087 | 4.709
2024-12-09 | 13:53 | Data | 0 | 34.911 | 33.372 | 132.848 | 7.64 | 125.48 | 2034.53 | 26.11 | 54.665 | 6.4 | 1.164 | 3.544 | 7463.94 | 1.168 | 97.3 | 75.3 | 1322 | 27.33 | 4851.6 | 2426.1 | 2415.5 | 3563.8 | 1186.1 | 0.66506 | 4.708
2024-12-09 | 13:53 | Data | 0 | 34.641 | 33.635 | 132.712 | 7.64 | 125.48 | 2034.53 | 26.11 | 54.846 | 6.4 | 1.16 | 3.558 | 7463.94 | 0.945 | 97.3 | 75.4 | 1322 | 27.38 | 4851.6 | 2424.1 | 2406.1 | 3560.2 | 1186.1 | 0.66393 | 4.719
2024-12-09 | 13:53 | Data | 0 | 34.708 | 33.439 | 132.757 | 7.64 | 125.525 | 2031.81 | 26.11 | 54.846 | 6.41 | 1.16 | 3.553 | 7454.89 | 1.161 | 97.3 | 75.4 | 1320 | 27.42 | 4845.7 | 2403.9 | 2408 | 3548 | 1186.1 | 0.66261 | 4.713
2024-12-09 | 13:53 | Data | 0 | 34.789 | 33.534 | 132.712 | 7.64 | 125.435 | 2032.72 | 26.11 | 54.485 | 6.4 | 1.162 | 3.531 | 7441.32 | 1.06 | 97.3 | 75.2 | 1321 | 27.24 | 4836.9 | 2430.1 | 2404.7 | 3562.9 | 1186.1 | 0.66696 | 4.693
2024-12-09 | 13:53 | Data | 0 | 34.783 | 33.426 | 132.667 | 7.64 | 125.435 | 2030.01 | 26.1 | 54.485 | 6.4 | 1.159 | 3.537 | 7441.32 | 1.357 | 97.3 | 75.3 | 1319 | 27.29 | 4836.9 | 2422.5 | 2406.7 | 3556.2 | 1186.2 | 0.66706 | 4.697
2024-12-09 | 13:53 | Data | 0 | 34.742 | 33.81 | 132.757 | 7.64 | 125.48 | 2030.91 | 26.1 | 54.575 | 6.41 | 1.159 | 3.538 | 7432.28 | 1.235 | 97.3 | 75.3 | 1320 | 27.29 | 4831 | 2432.1 | 2407.3 | 3563.1 | 1186.2 | 0.66777 | 4.699
2024-12-09 | 13:53 | Data | 0 | 34.796 | 33.642 | 132.712 | 7.64 | 125.435 | 2030.01 | 26.12 | 54.575 | 6.4 | 1.163 | 3.534 | 7445.85 | 1.161 | 97.3 | 75.2 | 1320 | 27.24 | 4839.8 | 2421.7 | 2433.5 | 3573.9 | 1186.2 | 0.66199 | 4.699
2024-12-09 | 13:53 | Data | 0 | 34.58 | 33.527 | 132.622 | 7.63 | 125.39 | 2025.49 | 26.1 | 54.485 | 6.4 | 1.159 | 3.553 | 7459.41 | 1.107 | 97.3 | 75.4 | 1317 | 27.24 | 4848.6 | 2407.4 | 2444 | 3576.5 | 1186.2 | 0.65687 | 4.71
2024-12-09 | 13:53 | Data | 0 | 34.789 | 33.412 | 132.803 | 7.64 | 125.48 | 2026.39 | 26.11 | 54.485 | 6.4 | 1.153 | 3.576 | 7445.85 | 1.181 | 97.3 | 75.6 | 1317 | 27.29 | 4839.8 | 2424.4 | 2432 | 3575.8 | 1186.2 | 0.66219 | 4.73
2024-12-09 | 13:53 | Data | 0 | 34.681 | 33.635 | 132.848 | 7.64 | 125.435 | 2025.49 | 26.11 | 54.485 | 6.4 | 1.159 | 3.56 | 7459.41 | 1.317 | 97.3 | 75.4 | 1317 | 27.24 | 4848.6 | 2419.7 | 2421.8 | 3569.1 | 1186.2 | 0.66295 | 4.72
2024-12-09 | 13:53 | Data | 0 | 34.796 | 33.756 | 132.757 | 7.64 | 125.48 | 2026.39 | 26.11 | 54.575 | 6.4 | 1.164 | 3.569 | 7454.89 | 1.154 | 97.3 | 75.4 | 1317 | 27.24 | 4845.7 | 2412 | 2415.5 | 3558.9 | 1186.2 | 0.6622 | 4.733
2024-12-09 | 13:54 | Data | 0 | 34.796 | 33.669 | 132.803 | 7.64 | 125.48 | 2026.39 | 26.11 | 54.485 | 6.4 | 1.173 | 3.55 | 7454.89 | 1.229 | 97.3 | 75.2 | 1317 | 27.29 | 4845.7 | 2413.4 | 2413.7 | 3560.1 | 1186.2 | 0.66318 | 4.722
2024-12-09 | 13:54 | Data | 0 | 34.58 | 33.642 | 132.712 | 7.64 | 125.435 | 2029.1 | 26.11 | 54.665 | 6.4 | 1.167 | 3.565 | 7445.85 | 0.932 | 97.3 | 75.3 | 1319 | 27.33 | 4839.8 | 2401.2 | 2417.1 | 3557.2 | 1186.2 | 0.65814 | 4.731
2024-12-09 | 13:54 | Data | 0 | 34.681 | 33.669 | 132.803 | 7.64 | 125.48 | 2030.01 | 26.1 | 54.575 | 6.4 | 1.155 | 3.538 | 7459.41 | 1.283 | 97.3 | 75.4 | 1320 | 27.24 | 4848.6 | 2408.9 | 2411.2 | 3550.9 | 1186.2 | 0.66256 | 4.693
2024-12-09 | 13:54 | Data | 0 | 34.573 | 33.412 | 132.712 | 7.64 | 125.525 | 2029.1 | 26.1 | 54.665 | 6.4 | 1.161 | 3.544 | 7445.85 | 1.323 | 97.3 | 75.3 | 1319 | 27.29 | 4839.8 | 2416 | 2421.8 | 3567.6 | 1186.2 | 0.66193 | 4.706
2024-12-09 | 13:54 | Data | 0 | 34.796 | 33.466 | 132.757 | 7.64 | 125.48 | 2020.97 | 26.11 | 54.485 | 6.41 | 1.161 | 3.537 | 7445.85 | 1.269 | 97.3 | 75.3 | 1314 | 27.29 | 4839.8 | 2423.1 | 2428.3 | 3569.7 | 1186.2 | 0.66462 | 4.699
2024-12-09 | 13:54 | Data | 0 | 34.681 | 33.635 | 132.757 | 7.64 | 125.435 | 2026.39 | 26.12 | 54.485 | 6.4 | 1.154 | 3.548 | 7445.85 | 1.121 | 97.3 | 75.5 | 1317 | 27.29 | 4839.8 | 2417.3 | 2405.8 | 3556.2 | 1186.2 | 0.66386 | 4.703
2024-12-09 | 13:54 | Data | 0 | 34.796 | 33.844 | 132.803 | 7.64 | 125.571 | 2025.49 | 26.1 | 54.575 | 6.4 | 1.16 | 3.556 | 7468.46 | 1.188 | 97.3 | 75.4 | 1317 | 27.24 | 4854.5 | 2417.7 | 2415.9 | 3564 | 1186.2 | 0.66297 | 4.716
2024-12-09 | 13:54 | Data | 0 | 34.756 | 33.527 | 132.667 | 7.64 | 125.435 | 2026.39 | 26.09 | 54.575 | 6.41 | 1.165 | 3.546 | 7477.5 | 1.134 | 97.3 | 75.3 | 1317 | 27.11 | 4860.4 | 2419.5 | 2430.1 | 3576.5 | 1186.2 | 0.66037 | 4.71
2024-12-09 | 13:54 | Data | 0 | 34.621 | 33.419 | 132.622 | 7.63 | 125.48 | 2023.68 | 26.1 | 54.575 | 6.4 | 1.166 | 3.535 | 7472.98 | 1.168 | 97.3 | 75.2 | 1315 | 27.29 | 4857.4 | 2418.8 | 2401.5 | 3551.4 | 1186.2 | 0.66202 | 4.701
2024-12-09 | 13:54 | Data | 0 | 34.796 | 33.642 | 132.803 | 7.63 | 125.48 | 2023.68 | 26.11 | 54.485 | 6.41 | 1.156 | 3.537 | 7463.94 | 1.242 | 97.3 | 75.4 | 1315 | 27.29 | 4851.6 | 2409.4 | 2412.4 | 3551.9 | 1186.2 | 0.66259 | 4.693
2024-12-09 | 13:54 | Data | 0 | 34.81 | 33.642 | 132.757 | 7.64 | 125.48 | 2021.87 | 26.1 | 54.485 | 6.41 | 1.152 | 3.546 | 7454.89 | 1.154 | 97.3 | 75.5 | 1314 | 27.33 | 4845.7 | 2414.1 | 2400.8 | 3550.8 | 1186.2 | 0.66373 | 4.699
2024-12-09 | 13:54 | Data | 0 | 34.594 | 33.588 | 132.712 | 7.64 | 125.48 | 2020.97 | 26.11 | 54.575 | 6.41 | 1.159 | 3.546 | 7454.89 | 1.208 | 97.3 | 75.4 | 1314 | 27.24 | 4845.7 | 2421.6 | 2405.6 | 3561.6 | 1186.2 | 0.66772 | 4.705
2024-12-09 | 13:54 | Data | 0 | 34.81 | 33.419 | 132.667 | 7.64 | 125.435 | 2021.87 | 26.1 | 54.756 | 6.4 | 1.151 | 3.553 | 7463.94 | 1.202 | 97.3 | 75.5 | 1314 | 27.38 | 4851.6 | 2397.1 | 2402.9 | 3539.9 | 1186.2 | 0.66207 | 4.705
2024-12-09 | 13:54 | Data | 0 | 34.796 | 33.642 | 132.803 | 7.63 | 125.571 | 2020.97 | 26.11 | 54.846 | 6.4 | 1.152 | 3.558 | 7472.98 | 1.168 | 97.3 | 75.5 | 1313 | 27.42 | 4857.4 | 2421.2 | 2402.5 | 3546.2 | 1186.2 | 0.66475 | 4.711
2024-12-09 | 13:54 | Data | 0 | 35.026 | 33.446 | 133.074 | 7.64 | 125.616 | 2020.07 | 26.11 | 54.665 | 6.4 | 1.163 | 3.57 | 7468.46 | 1.296 | 97.3 | 75.5 | 1314 | 27.24 | 4854.5 | 2409 | 2410.1 | 3558.4 | 1186.2 | 0.6666 | 4.731
2024-12-09 | 13:54 | Data | 0 | 34.796 | 33.426 | 132.848 | 7.63 | 125.48 | 2023.68 | 26.1 | 54.575 | 6.4 | 1.154 | 3.556 | 7477.5 | 1.323 | 97.3 | 75.5 | 1315 | 27.29 | 4860.4 | 2412.9 | 2426.9 | 3580.2 | 1186.2 | 0.66271 | 4.711
2024-12-09 | 13:54 | Data | 0 | 34.58 | 33.459 | 132.667 | 7.63 | 125.525 | 2022.78 | 26.11 | 54.756 | 6.4 | 1.151 | 3.534 | 7445.85 | 1.283 | 97.3 | 75.4 | 1315 | 27.38 | 4839.8 | 2435.3 | 2405.7 | 3562.3 | 1186.2 | 0.66862 | 4.686
2024-12-09 | 13:54 | Data | 0 | 34.783 | 33.527 | 132.848 | 7.64 | 125.525 | 2023.68 | 26.1 | 54.485 | 6.41 | 1.159 | 3.528 | 7445.85 | 1.094 | 97.3 | 75.3 | 1315 | 27.29 | 4839.8 | 2426.9 | 2420.4 | 3568.7 | 1186.2 | 0.66724 | 4.688
2024-12-09 | 13:55 | Data | 0 | 34.796 | 33.439 | 132.712 | 7.64 | 125.48 | 2021.87 | 26.11 | 54.756 | 6.4 | 1.16 | 3.549 | 7436.8 | 1.323 | 97.3 | 75.4 | 1315 | 27.38 | 4833.9 | 2422.4 | 2407.8 | 3555.6 | 1186.2 | 0.66655 | 4.709
2024-12-09 | 13:55 | Data | 0 | 34.796 | 33.642 | 132.757 | 7.63 | 125.571 | 2023.68 | 26.1 | 54.846 | 6.4 | 1.163 | 3.554 | 7436.8 | 1.154 | 97.3 | 75.3 | 1315 | 27.42 | 4833.9 | 2432.9 | 2415.5 | 3574.8 | 1186.2 | 0.66494 | 4.716
2024-12-09 | 13:55 | Data | 0 | 34.803 | 33.527 | 132.803 | 7.64 | 125.48 | 2022.78 | 26.1 | 54.846 | 6.4 | 1.154 | 3.546 | 7472.98 | 1.154 | 97.3 | 75.4 | 1315 | 27.42 | 4857.4 | 2400.7 | 2424.7 | 3556.7 | 1186.2 | 0.65905 | 4.701
2024-12-09 | 13:55 | Data | 0 | 34.695 | 33.527 | 132.803 | 7.64 | 125.525 | 2024.58 | 26.1 | 54.846 | 6.4 | 1.164 | 3.531 | 7468.46 | 0.992 | 97.3 | 75.2 | 1315 | 27.42 | 4854.5 | 2395.7 | 2400.3 | 3542.7 | 1186.2 | 0.6583 | 4.697
2024-12-09 | 13:55 | Data | 0 | 34.681 | 33.588 | 132.757 | 7.64 | 125.525 | 2025.49 | 26.12 | 54.485 | 6.4 | 1.165 | 3.549 | 7468.46 | 1.168 | 97.3 | 75.3 | 1317 | 27.15 | 4854.5 | 2417.6 | 2409.9 | 3558 | 1186.2 | 0.66648 | 4.714
2024-12-09 | 13:55 | Data | 0 | 35.026 | 33.669 | 132.848 | 7.64 | 125.571 | 2025.49 | 26.11 | 54.846 | 6.4 | 1.155 | 3.562 | 7482.02 | 1.154 | 97.3 | 75.5 | 1317 | 27.38 | 4863.3 | 2411.2 | 2410.7 | 3558.6 | 1186.2 | 0.66357 | 4.716
2024-12-09 | 13:55 | Data | 0 | 34.796 | 33.642 | 132.893 | 7.64 | 125.525 | 2027.3 | 26.11 | 54.846 | 6.4 | 1.155 | 3.555 | 7482.02 | 1.195 | 97.3 | 75.5 | 1318 | 27.42 | 4863.3 | 2415.5 | 2423.7 | 3567.8 | 1186.2 | 0.66167 | 4.71
2024-12-09 | 13:55 | Data | 0 | 34.972 | 33.642 | 132.848 | 7.64 | 125.571 | 2029.1 | 26.1 | 54.756 | 6.4 | 1.148 | 3.547 | 7472.98 | 1.357 | 97.3 | 75.5 | 1319 | 27.33 | 4857.4 | 2416.8 | 2423.4 | 3568.6 | 1186.2 | 0.66261 | 4.693
2024-12-09 | 13:55 | Data | 0 | 34.904 | 33.642 | 132.803 | 7.64 | 125.525 | 2031.81 | 26.11 | 54.846 | 6.41 | 1.155 | 3.545 | 7468.46 | 1.168 | 97.3 | 75.4 | 1321 | 27.38 | 4854.5 | 2414.9 | 2396.4 | 3548.7 | 1186.2 | 0.66537 | 4.7
2024-12-09 | 13:55 | Data | 0 | 34.81 | 33.426 | 132.803 | 7.63 | 125.571 | 2031.81 | 26.1 | 54.575 | 6.4 | 1.156 | 3.536 | 7468.46 | 1.208 | 97.3 | 75.3 | 1320 | 27.33 | 4854.5 | 2419.6 | 2422.6 | 3571 | 1186.2 | 0.66119 | 4.692
2024-12-09 | 13:55 | Data | 0 | 34.931 | 33.858 | 132.848 | 7.64 | 125.616 | 2031.81 | 26.11 | 54.846 | 6.4 | 1.151 | 3.531 | 7463.94 | 1.168 | 97.3 | 75.4 | 1320 | 27.38 | 4851.6 | 2403.2 | 2394.1 | 3541 | 1186.2 | 0.66225 | 4.682
2024-12-09 | 13:55 | Data | 0 | 34.911 | 33.864 | 132.848 | 7.64 | 125.48 | 2031.81 | 26.12 | 54.756 | 6.41 | 1.152 | 3.561 | 7468.46 | 1.154 | 97.3 | 75.5 | 1321 | 27.42 | 4854.5 | 2431.9 | 2423 | 3572.7 | 1186.2 | 0.66537 | 4.714
2024-12-09 | 13:55 | Data | 0 | 34.864 | 33.655 | 132.848 | 7.64 | 125.571 | 2029.1 | 26.11 | 54.756 | 6.41 | 1.152 | 3.556 | 7468.46 | 1.134 | 97.3 | 75.5 | 1318 | 27.38 | 4854.5 | 2401.5 | 2419 | 3560.6 | 1186.2 | 0.6583 | 4.709
2024-12-09 | 13:55 | Data | 0 | 34.81 | 33.446 | 132.893 | 7.64 | 125.616 | 2029.1 | 26.11 | 54.756 | 6.41 | 1.159 | 3.566 | 7468.46 | 1.141 | 97.3 | 75.5 | 1319 | 27.42 | 4854.5 | 2405.2 | 2426.7 | 3559.5 | 1186.2 | 0.6598 | 4.725
2024-12-09 | 13:55 | Data | 0 | 34.627 | 33.615 | 132.803 | 7.63 | 125.48 | 2032.72 | 26.12 | 54.846 | 6.4 | 1.155 | 3.571 | 8078.96 | 0.965 | 97.3 | 75.6 | 1321 | 27.38 | 5251.3 | 2415.2 | 2432 | 3571.3 | 1186.2 | 0.66035 | 4.726
2024-12-09 | 13:55 | Data | 0 | 34.965 | 33.655 | 132.757 | 7.64 | 125.525 | 2031.81 | 26.11 | 54.756 | 6.41 | 1.15 | 3.565 | 7463.94 | 1.303 | 97.3 | 75.6 | 1321 | 27.38 | 4851.6 | 2377.7 | 2463.2 | 3560.2 | 1186.2 | 0.65335 | 4.715
2024-12-09 | 13:55 | Data | 0 | 34.796 | 33.473 | 132.712 | 7.64 | 125.571 | 2032.72 | 26.12 | 54.846 | 6.4 | 1.155 | 3.534 | 7482.02 | 1.154 | 97.3 | 75.4 | 1321 | 27.42 | 4863.3 | 1333.5 | 1771.8 | 2236.5 | 1186.2 | 0.59909 | 4.689
2024-12-09 | 13:55 | Data | 0 | 34.573 | 33.729 | 132.803 | 7.63 | 125.571 | 2025.49 | 26.12 | 54.756 | 6.4 | 1.167 | 3.542 | 7468.46 | 1.013 | 97.3 | 75.2 | 1317 | 27.42 | 4854.5 | 1334.8 | 1785.6 | 2248.1 | 1186.2 | 0.59251 | 4.709
2024-12-09 | 13:56 | Data | 0 | 34.965 | 33.554 | 132.893 | 7.64 | 125.571 | 2031.81 | 26.1 | 54.756 | 6.41 | 1.164 | 3.568 | 7468.46 | 1.073 | 97.3 | 75.4 | 1321 | 27.42 | 4854.5 | 1327.6 | 1769 | 2229.3 | 1186.2 | 0.59353 | 4.733
2024-12-09 | 13:56 | Data | 0 | 35.188 | 33.871 | 132.938 | 7.63 | 125.571 | 2034.53 | 26.11 | 54.756 | 6.4 | 1.16 | 3.561 | 7468.46 | 1.256 | 97.3 | 75.4 | 1322 | 27.42 | 4854.5 | 1316.4 | 1777.4 | 2230.1 | 1186.2 | 0.58744 | 4.722
2024-12-09 | 13:56 | Data | 0 | 35.026 | 33.642 | 132.757 | 7.64 | 125.525 | 2039.95 | 26.11 | 54.756 | 6.4 | 1.15 | 3.546 | 7459.41 | 1.269 | 97.3 | 75.5 | 1326 | 27.33 | 4848.6 | 1348.7 | 1802.1 | 2269.2 | 1186.2 | 0.59491 | 4.696
2024-12-09 | 13:56 | Data | 0 | 35.221 | 33.669 | 132.938 | 7.64 | 125.661 | 2034.53 | 26.1 | 54.936 | 6.4 | 1.159 | 3.537 | 7463.94 | 1.208 | 97.3 | 75.3 | 1323 | 27.42 | 4851.6 | 1321.4 | 1765.2 | 2222.8 | 1186.2 | 0.59302 | 4.696
2024-12-09 | 13:56 | Data | 0 | 34.85 | 33.648 | 132.848 | 7.64 | 125.571 | 2034.53 | 26.11 | 54.846 | 6.41 | 1.161 | 3.54 | 7463.94 | 1.154 | 97.3 | 75.3 | 1323 | 27.42 | 4851.6 | 1336 | 1760.6 | 2228.3 | 1186.3 | 0.59651 | 4.701
2024-12-09 | 13:56 | Data | 0 | 34.999 | 33.642 | 132.803 | 7.64 | 125.571 | 2034.53 | 26.11 | 54.665 | 6.41 | 1.162 | 3.543 | 7468.46 | 1.222 | 97.3 | 75.3 | 1323 | 27.38 | 4854.5 | 1321 | 1772 | 2228 | 1186.3 | 0.59071 | 4.707
2024-12-09 | 13:56 | Data | 0 | 34.708 | 33.642 | 132.803 | 7.63 | 125.525 | 2033.62 | 26.11 | 54.756 | 6.4 | 1.149 | 3.543 | 7468.46 | 1.141 | 97.3 | 75.5 | 1322 | 27.42 | 4854.5 | 1347.3 | 1775.4 | 2247.1 | 1186.3 | 0.5994 | 4.692
2024-12-09 | 13:56 | Data | 0 | 34.641 | 33.588 | 132.757 | 7.64 | 125.525 | 2032.72 | 26.11 | 54.756 | 6.4 | 1.154 | 3.579 | 7468.46 | 1.235 | 97.3 | 75.6 | 1321 | 27.38 | 4854.5 | 1331.2 | 1758.9 | 2223 | 1186.3 | 0.59741 | 4.733
2024-12-09 | 13:56 | Data | 0 | 34.634 | 33.459 | 132.757 | 7.63 | 125.525 | 2032.72 | 26.1 | 54.756 | 6.4 | 1.16 | 3.569 | 7477.5 | 1.006 | 97.3 | 75.5 | 1321 | 27.38 | 4860.4 | 1353.7 | 1774.5 | 2250.6 | 1186.3 | 0.601 | 4.729
2024-12-09 | 13:56 | Data | 0 | 34.688 | 33.527 | 132.712 | 7.64 | 125.525 | 2031.81 | 26.1 | 54.756 | 6.4 | 1.159 | 3.542 | 7477.5 | 1.127 | 97.3 | 75.3 | 1321 | 27.38 | 4860.4 | 1333 | 1792 | 2250.5 | 1186.3 | 0.5914 | 4.702
2024-12-09 | 13:56 | Data | 0 | 34.81 | 33.669 | 132.803 | 7.64 | 125.525 | 2033.62 | 26.09 | 54.846 | 6.4 | 1.159 | 3.535 | 7468.46 | 1.094 | 97.3 | 75.3 | 1321 | 27.38 | 4854.5 | 1323.8 | 1785.3 | 2239.8 | 1186.3 | 0.59003 | 4.692
2024-12-09 | 13:56 | Data | 0 | 34.992 | 33.642 | 132.848 | 7.63 | 125.571 | 2032.72 | 26.1 | 54.846 | 6.4 | 1.172 | 3.554 | 7495.59 | 1.377 | 97.3 | 75.2 | 1321 | 27.42 | 4872.1 | 1340 | 1757.4 | 2231.8 | 1186.3 | 0.60086 | 4.726
2024-12-09 | 13:56 | Data | 0 | 35.012 | 33.696 | 132.848 | 7.64 | 125.571 | 2032.72 | 26.11 | 54.756 | 6.41 | 1.168 | 3.546 | 7468.46 | 1.262 | 97.3 | 75.2 | 1321 | 27.33 | 4854.5 | 1319.6 | 1768.5 | 2228.9 | 1186.3 | 0.59056 | 4.711
2024-12-09 | 13:56 | Data | 0 | 34.911 | 33.642 | 132.803 | 7.63 | 125.525 | 2029.1 | 26.1 | 54.756 | 6.4 | 1.169 | 3.546 | 7441.32 | 1.202 | 97.3 | 75.2 | 1320 | 27.38 | 4836.9 | 1336.2 | 1764.1 | 2232.5 | 1186.3 | 0.59799 | 4.713
2024-12-09 | 13:56 | Data | 0 | 34.85 | 33.648 | 132.848 | 7.64 | 125.571 | 2033.62 | 26.11 | 54.756 | 6.4 | 1.163 | 3.556 | 7468.46 | 1.154 | 97.3 | 75.4 | 1321 | 27.38 | 4854.5 | 1338.7 | 1766.1 | 2233.5 | 1186.3 | 0.59786 | 4.719
2024-12-09 | 13:56 | Data | 0 | 34.796 | 33.466 | 132.803 | 7.64 | 125.571 | 2031.81 | 26.09 | 54.756 | 6.4 | 1.155 | 3.546 | 7468.46 | 1.33 | 97.3 | 75.4 | 1321 | 27.42 | 4854.5 | 1318.1 | 1749.9 | 2209.7 | 1186.3 | 0.5949 | 4.701
2024-12-09 | 13:56 | Data | 0 | 34.742 | 33.554 | 132.893 | 7.64 | 125.48 | 2031.81 | 26.11 | 54.846 | 6.4 | 1.159 | 3.546 | 7477.5 | 1.323 | 97.3 | 75.4 | 1320 | 27.38 | 4860.4 | 1321.7 | 1765.5 | 2223.2 | 1186.3 | 0.59389 | 4.705
2024-12-09 | 13:56 | Data | 0 | 34.85 | 33.419 | 132.712 | 7.64 | 125.525 | 2031.81 | 26.11 | 54.756 | 6.41 | 1.16 | 3.534 | 7482.02 | 1.208 | 97.3 | 75.3 | 1321 | 27.38 | 4863.3 | 1318.9 | 1765.7 | 2224 | 1186.3 | 0.59071 | 4.693
2024-12-09 | 13:57 | Data | 0 | 34.573 | 33.588 | 132.757 | 7.64 | 125.525 | 2032.72 | 26.11 | 54.756 | 6.41 | 1.16 | 3.535 | 7463.94 | 1.154 | 97.3 | 75.3 | 1322 | 27.38 | 4851.6 | 1336 | 1785.8 | 2249.8 | 1186.3 | 0.59286 | 4.696
2024-12-09 | 13:57 | Data | 0 | 34.965 | 33.696 | 132.803 | 7.63 | 125.525 | 2034.53 | 26.11 | 54.846 | 6.41 | 1.155 | 3.546 | 7495.59 | 1.269 | 97.3 | 75.4 | 1322 | 27.42 | 4872.1 | 1335.1 | 1784.9 | 2248.5 | 1186.3 | 0.59447 | 4.701
2024-12-09 | 13:57 | Data | 0 | 34.796 | 33.412 | 132.757 | 7.64 | 125.525 | 2032.72 | 26.11 | 54.756 | 6.4 | 1.163 | 3.543 | 7495.59 | 1.269 | 97.3 | 75.3 | 1321 | 27.42 | 4872.1 | 1326.3 | 1773.2 | 2234 | 1186.3 | 0.58988 | 4.707
2024-12-09 | 13:57 | Data | 0 | 34.573 | 33.642 | 132.893 | 7.64 | 125.525 | 2031.81 | 26.12 | 54.846 | 6.4 | 1.164 | 3.554 | 7500.11 | 1.141 | 97.3 | 75.3 | 1320 | 27.38 | 4875.1 | 1337.1 | 1760.5 | 2231.4 | 1186.3 | 0.59973 | 4.716
2024-12-09 | 13:57 | Data | 0 | 34.904 | 33.669 | 132.803 | 7.64 | 125.525 | 2030.01 | 26.1 | 54.756 | 6.4 | 1.16 | 3.541 | 7495.59 | 1.242 | 97.3 | 75.3 | 1319 | 27.38 | 4872.1 | 1332.8 | 1769.5 | 2234.2 | 1186.3 | 0.59616 | 4.701
2024-12-09 | 13:57 | Data | 0 | 34.803 | 33.642 | 132.757 | 7.64 | 125.525 | 2029.1 | 26.11 | 54.846 | 6.41 | 1.156 | 3.544 | 7482.02 | 1.154 | 97.3 | 75.4 | 1319 | 27.42 | 4863.3 | 1338.8 | 1769.8 | 2236.3 | 1186.3 | 0.59715 | 4.7
2024-12-09 | 13:57 | Data | 0 | 34.573 | 33.527 | 132.757 | 7.63 | 125.525 | 2027.3 | 26.11 | 54.846 | 6.4 | 1.15 | 3.537 | 7852.85 | 1.262 | 97.3 | 75.4 | 1320 | 27.42 | 5104.3 | 1342.5 | 1755.4 | 2229.6 | 1186.3 | 0.60144 | 4.689
2024-12-09 | 13:57 | Data | 0 | 34.742 | 33.642 | 132.803 | 7.63 | 125.525 | 2029.1 | 26.1 | 54.846 | 6.4 | 1.151 | 3.534 | 7486.55 | 1.154 | 97.3 | 75.4 | 1318 | 27.42 | 4866.3 | 1344.2 | 1783 | 2251.2 | 1186.3 | 0.59523 | 4.685
2024-12-09 | 13:57 | Data | 0 | 34.742 | 33.635 | 132.757 | 7.64 | 125.525 | 2029.1 | 26.1 | 54.846 | 6.4 | 1.153 | 3.53 | 7491.07 | 1.154 | 97.3 | 75.4 | 1320 | 27.42 | 4869.2 | 1341.5 | 1776.4 | 2249 | 1186.3 | 0.5986 | 4.684
2024-12-09 | 13:57 | Data | 0 | 34.573 | 33.615 | 132.622 | 7.64 | 125.48 | 2029.1 | 26.09 | 54.846 | 6.41 | 1.159 | 3.56 | 7477.5 | 1.154 | 97.3 | 75.5 | 1320 | 27.42 | 4860.4 | 1333.9 | 1777.3 | 2242.2 | 1186.3 | 0.59325 | 4.716
2024-12-09 | 13:57 | Data | 0 | 34.796 | 33.864 | 132.803 | 7.64 | 125.525 | 2029.1 | 26.1 | 54.756 | 6.41 | 1.157 | 3.556 | 7509.16 | 1.154 | 97.3 | 75.5 | 1317 | 27.38 | 4881 | 1327.8 | 1754.1 | 2220.8 | 1186.3 | 0.59656 | 4.712
2024-12-09 | 13:57 | Data | 0 | 34.796 | 33.642 | 132.803 | 7.64 | 125.525 | 2030.01 | 26.11 | 54.756 | 6.4 | 1.157 | 3.556 | 7504.64 | 1.154 | 97.3 | 75.5 | 1319 | 27.38 | 4878 | 1334.1 | 1754.6 | 2223.8 | 1186.3 | 0.59878 | 4.712
2024-12-09 | 13:57 | Data | 0 | 34.742 | 33.601 | 132.984 | 7.64 | 125.571 | 2032.72 | 26.1 | 54.846 | 6.4 | 1.159 | 3.548 | 7504.64 | 1.262 | 97.3 | 75.4 | 1321 | 27.42 | 4878 | 1329.7 | 1751.4 | 2217.3 | 1186.3 | 0.59936 | 4.709
2024-12-09 | 13:57 | Data | 0 | 34.405 | 33.588 | 132.757 | 7.64 | 125.525 | 2027.3 | 26.1 | 54.756 | 6.41 | 1.152 | 3.558 | 7504.64 | 1.019 | 97.3 | 75.5 | 1319 | 27.42 | 4878 | 1326.2 | 1761.5 | 2224.1 | 1186.3 | 0.59562 | 4.713
2024-12-09 | 13:57 | Data | 0 | 34.681 | 33.635 | 132.757 | 7.64 | 125.525 | 2030.01 | 26.1 | 54.756 | 6.41 | 1.156 | 3.569 | 7513.68 | 0.965 | 97.3 | 75.5 | 1320 | 27.38 | 4883.9 | 1333.7 | 1779.3 | 2242.8 | 1186.3 | 0.59409 | 4.724
2024-12-09 | 13:57 | Data | 0 | 34.796 | 33.527 | 132.757 | 7.63 | 125.525 | 2021.87 | 26.11 | 54.846 | 6.41 | 1.159 | 3.562 | 7504.64 | 1.154 | 97.3 | 75.4 | 1315 | 27.42 | 4878 | 1320.8 | 1786.1 | 2241.9 | 1186.3 | 0.58753 | 4.72
2024-12-09 | 13:57 | Data | 0 | 34.796 | 33.426 | 132.757 | 7.63 | 125.48 | 2032.72 | 26.11 | 54.665 | 6.41 | 1.152 | 3.537 | 7500.11 | 1.33 | 97.3 | 75.4 | 1321 | 27.38 | 4875.1 | 1334.8 | 1768.5 | 2237.2 | 1186.3 | 0.59557 | 4.691
2024-12-09 | 13:58 | Data | 0 | 34.681 | 33.527 | 132.757 | 7.64 | 125.48 | 2033.62 | 26.11 | 54.485 | 6.4 | 1.161 | 3.525 | 7504.64 | 1.364 | 97.3 | 75.2 | 1322 | 27.24 | 4878 | 1327.9 | 1768.1 | 2232.1 | 1186.3 | 0.59187 | 4.688
2024-12-09 | 13:58 | Data | 0 | 34.796 | 33.642 | 132.803 | 7.64 | 125.525 | 2035.43 | 26.11 | 54.756 | 6.4 | 1.165 | 3.54 | 7644.82 | 1.154 | 97.3 | 75.2 | 1322 | 27.33 | 4969.1 | 1335.7 | 1765.9 | 2223.1 | 1186.3 | 0.59582 | 4.703
2024-12-09 | 13:58 | Data | 0 | 34.742 | 33.419 | 132.622 | 7.64 | 125.435 | 2032.72 | 26.11 | 54.846 | 6.4 | 1.152 | 3.561 | 7676.48 | 1.175 | 97.3 | 75.6 | 1321 | 27.38 | 4989.7 | 1336.3 | 1766.1 | 2234.5 | 1186.3 | 0.59771 | 4.714
2024-12-09 | 13:58 | Data | 0 | 34.742 | 33.466 | 132.757 | 7.63 | 125.435 | 2031.81 | 26.11 | 54.846 | 6.4 | 1.154 | 3.537 | 7671.96 | 1.262 | 97.3 | 75.4 | 1321 | 27.42 | 4986.8 | 1327.7 | 1765.1 | 2227.4 | 1186.3 | 0.59615 | 4.691
2024-12-09 | 13:58 | Data | 0 | 34.769 | 33.642 | 132.757 | 7.64 | 125.525 | 2030.91 | 26.09 | 54.846 | 6.4 | 1.167 | 3.555 | 7681 | 1.148 | 97.3 | 75.3 | 1321 | 27.42 | 4992.7 | 1334 | 1781.9 | 2244.9 | 1186.3 | 0.59316 | 4.72
2024-12-09 | 13:58 | Data | 0 | 34.681 | 33.412 | 132.803 | 7.63 | 125.525 | 2029.1 | 26.11 | 54.756 | 6.4 | 1.161 | 3.564 | 7576.99 | 1.161 | 97.3 | 75.4 | 1319 | 27.38 | 4925 | 1330.8 | 1775.2 | 2236.2 | 1186.3 | 0.59462 | 4.724
2024-12-09 | 13:58 | Data | 0 | 34.789 | 33.466 | 132.712 | 7.63 | 125.48 | 2034.53 | 26.1 | 54.665 | 6.41 | 1.161 | 3.562 | 7504.64 | 1.33 | 97.3 | 75.4 | 1322 | 27.33 | 4878 | 1331.2 | 1774.5 | 2236.3 | 1186.3 | 0.59404 | 4.723
2024-12-09 | 13:58 | Data | 0 | 34.567 | 33.412 | 132.667 | 7.64 | 125.435 | 2030.01 | 26.11 | 54.756 | 6.4 | 1.164 | 3.556 | 7504.64 | 1.154 | 97.3 | 75.3 | 1320 | 27.38 | 4878 | 1341.6 | 1769.9 | 2239.9 | 1186.3 | 0.59849 | 4.719
2024-12-09 | 13:58 | Data | 0 | 34.553 | 33.635 | 132.667 | 7.64 | 125.435 | 2033.62 | 26.1 | 54.846 | 6.4 | 1.166 | 3.527 | 7522.72 | 1.134 | 97.3 | 75.2 | 1323 | 27.42 | 4889.8 | 1335.9 | 1763.9 | 2230.7 | 1186.3 | 0.5984 | 4.692
2024-12-09 | 13:58 | Data | 0 | 34.769 | 33.642 | 132.803 | 7.64 | 125.525 | 2030.91 | 26.09 | 54.665 | 6.41 | 1.159 | 3.531 | 7509.16 | 1.208 | 97.3 | 75.3 | 1320 | 27.42 | 4881 | 1310.8 | 1754.3 | 2211.5 | 1186.3 | 0.59165 | 4.692
2024-12-09 | 13:58 | Data | 0 | 34.641 | 33.419 | 132.757 | 7.64 | 125.48 | 2034.53 | 26.1 | 54.756 | 6.4 | 1.157 | 3.527 | 7509.16 | 1.154 | 97.3 | 75.3 | 1322 | 27.42 | 4881 | 1336.5 | 1758.8 | 2228.4 | 1186.3 | 0.59769 | 4.683
2024-12-09 | 13:58 | Data | 0 | 34.796 | 33.419 | 132.757 | 7.63 | 125.48 | 2035.43 | 26.11 | 54.756 | 6.41 | 1.156 | 3.564 | 7504.64 | 1.154 | 97.3 | 75.5 | 1322 | 27.38 | 4878 | 1331.9 | 1763.4 | 2228.6 | 1186.3 | 0.59574 | 4.72
2024-12-09 | 13:58 | Data | 0 | 34.742 | 33.635 | 132.712 | 7.63 | 125.525 | 2031.81 | 26.09 | 54.756 | 6.41 | 1.157 | 3.548 | 7491.07 | 1.161 | 97.3 | 75.4 | 1323 | 27.42 | 4869.2 | 1334 | 1762.9 | 2228.8 | 1186.3 | 0.59683 | 4.71
2024-12-09 | 13:58 | Data | 0 | 34.567 | 33.615 | 132.667 | 7.63 | 125.48 | 2034.53 | 26.11 | 54.846 | 6.41 | 1.155 | 3.534 | 7495.59 | 1.242 | 97.3 | 75.4 | 1322 | 27.38 | 4872.1 | 1335.8 | 1759.3 | 2226.3 | 1186.3 | 0.59888 | 4.69
2024-12-09 | 13:58 | Data | 0 | 34.904 | 33.432 | 132.757 | 7.63 | 125.525 | 2034.53 | 26.1 | 54.756 | 6.41 | 1.152 | 3.532 | 7477.5 | 1.371 | 97.3 | 75.4 | 1323 | 27.38 | 4860.4 | 1324.2 | 1761.7 | 2221.2 | 1186.3 | 0.59484 | 4.685
2024-12-09 | 13:58 | Data | 0 | 34.567 | 33.412 | 132.667 | 7.63 | 125.435 | 2036.33 | 26.1 | 54.846 | 6.41 | 1.163 | 3.541 | 7486.55 | 1.154 | 97.3 | 75.3 | 1323 | 27.42 | 4866.3 | 1342.5 | 1763.1 | 2231.6 | 1186.3 | 0.59942 | 4.702
2024-12-09 | 13:58 | Data | 0 | 34.769 | 33.655 | 132.667 | 7.64 | 125.39 | 2035.43 | 26.11 | 54.756 | 6.4 | 1.16 | 3.549 | 7482.02 | 1.337 | 97.3 | 75.4 | 1322 | 27.38 | 4863.3 | 1336.1 | 1776.8 | 2241.4 | 1186.3 | 0.59457 | 4.71
2024-12-09 | 13:58 | Data | 0 | 34.58 | 33.412 | 132.667 | 7.64 | 125.435 | 2031.81 | 26.1 | 54.846 | 6.41 | 1.163 | 3.537 | 7482.02 | 1.154 | 97.3 | 75.3 | 1321 | 27.38 | 4863.3 | 1327.4 | 1755.3 | 2219.6 | 1186.3 | 0.59765 | 4.701
2024-12-09 | 13:59 | Data | 0 | 34.823 | 33.642 | 132.848 | 7.63 | 125.48 | 2031.81 | 26.11 | 54.756 | 6.41 | 1.163 | 3.528 | 7486.55 | 1.148 | 97.3 | 75.2 | 1321 | 27.33 | 4866.3 | 1340.8 | 1746.7 | 2220.3 | 1186.3 | 0.60239 | 4.69
2024-12-09 | 13:59 | Data | 0 | 34.567 | 33.412 | 132.622 | 7.64 | 125.39 | 2029.1 | 26.09 | 54.756 | 6.4 | 1.159 | 3.525 | 7482.02 | 1.181 | 97.3 | 75.2 | 1320 | 27.47 | 4863.3 | 1337.4 | 1775.3 | 2242.8 | 1186.3 | 0.59493 | 4.684
2024-12-09 | 13:59 | Data | 0 | 34.769 | 33.635 | 132.757 | 7.64 | 125.48 | 2030.01 | 26.1 | 54.756 | 6.41 | 1.159 | 3.538 | 7491.07 | 1.154 | 97.3 | 75.3 | 1319 | 27.42 | 4869.2 | 1324.2 | 1777.6 | 2236.1 | 1186.3 | 0.59483 | 4.698
2024-12-09 | 13:59 | Data | 0 | 34.594 | 33.615 | 132.712 | 7.64 | 125.525 | 2025.49 | 26.11 | 54.846 | 6.41 | 1.156 | 3.549 | 7495.59 | 1.1 | 97.3 | 75.4 | 1317 | 27.42 | 4872.1 | 1322.2 | 1779.5 | 2236 | 1186.3 | 0.58985 | 4.705
2024-12-09 | 13:59 | Data | 0 | 34.769 | 33.615 | 132.757 | 7.64 | 125.525 | 2025.49 | 26.09 | 54.936 | 6.41 | 1.154 | 3.531 | 7477.5 | 1.067 | 97.3 | 75.4 | 1317 | 27.38 | 4860.4 | 1315.2 | 1761.1 | 2217.6 | 1186.3 | 0.59273 | 4.684
2024-12-09 | 13:59 | Data | 0 | 34.796 | 33.426 | 132.712 | 7.64 | 125.48 | 2030.01 | 26.11 | 54.485 | 6.4 | 1.16 | 3.545 | 7495.59 | 1.357 | 97.3 | 75.3 | 1319 | 27.24 | 4872.1 | 1346.5 | 1775.9 | 2248.4 | 1186.3 | 0.59765 | 4.705
2024-12-09 | 13:59 | Data | 0 | 34.783 | 33.419 | 132.712 | 7.63 | 125.435 | 2033.62 | 26.1 | 54.846 | 6.4 | 1.16 | 3.554 | 7495.59 | 1.364 | 97.3 | 75.4 | 1322 | 27.42 | 4872.1 | 1331.8 | 1771 | 2234.7 | 1186.3 | 0.59405 | 4.715
2024-12-09 | 13:59 | Data | 0 | 34.951 | 33.689 | 132.803 | 7.64 | 125.48 | 2031.81 | 26.11 | 54.575 | 6.4 | 1.168 | 3.546 | 7482.02 | 1.148 | 97.3 | 75.2 | 1320 | 27.29 | 4863.3 | 1335.2 | 1774 | 2239.5 | 1186.3 | 0.59485 | 4.715
2024-12-09 | 13:59 | Data | 0 | 34.681 | 33.432 | 132.667 | 7.64 | 125.435 | 2031.81 | 26.11 | 54.485 | 6.4 | 1.175 | 3.527 | 7482.02 | 1.35 | 97.3 | 75 | 1321 | 27.29 | 4863.3 | 1338.2 | 1766.5 | 2233.3 | 1186.3 | 0.59812 | 4.7
2024-12-09 | 13:59 | Data | 0 | 34.567 | 33.412 | 132.712 | 7.63 | 125.435 | 2033.62 | 26.11 | 54.485 | 6.4 | 1.167 | 3.554 | 7472.98 | 1.161 | 97.3 | 75.3 | 1321 | 27.29 | 4857.4 | 1336.1 | 1751.4 | 2220.9 | 1186.3 | 0.59908 | 4.721
2024-12-09 | 13:59 | Data | 0 | 34.553 | 33.412 | 132.712 | 7.63 | 125.435 | 2030.01 | 26.11 | 54.485 | 6.4 | 1.16 | 3.545 | 7477.5 | 1.323 | 97.3 | 75.3 | 1320 | 27.29 | 4860.4 | 1338.7 | 1757.1 | 2228.1 | 1186.3 | 0.60031 | 4.703
2024-12-09 | 13:59 | Data | 0 | 34.769 | 33.412 | 132.622 | 7.63 | 125.39 | 2024.58 | 26.1 | 54.575 | 6.4 | 1.153 | 3.532 | 7468.46 | 1.249 | 97.3 | 75.4 | 1316 | 27.29 | 4854.5 | 1328 | 1771.7 | 2232.3 | 1186.3 | 0.59318 | 4.685
2024-12-09 | 13:59 | Data | 0 | 34.681 | 33.426 | 132.712 | 7.63 | 125.39 | 2026.39 | 26.11 | 54.575 | 6.41 | 1.159 | 3.537 | 7482.02 | 1.269 | 97.3 | 75.3 | 1317 | 27.2 | 4863.3 | 1331.1 | 1771.5 | 2235.5 | 1186.3 | 0.59402 | 4.696
2024-12-09 | 13:59 | Data | 0 | 34.594 | 33.419 | 132.667 | 7.64 | 125.435 | 2029.1 | 26.1 | 54.485 | 6.4 | 1.159 | 3.527 | 7477.5 | 1.134 | 97.3 | 75.3 | 1319 | 27.24 | 4860.4 | 1324.6 | 1759.3 | 2222.1 | 1186.3 | 0.59417 | 4.685
2024-12-09 | 13:59 | Data | 0 | 34.742 | 33.635 | 132.757 | 7.64 | 125.48 | 2029.1 | 26.11 | 54.575 | 6.41 | 1.164 | 3.543 | 7468.46 | 1.154 | 97.3 | 75.3 | 1318 | 27.24 | 4854.5 | 1323.9 | 1775.3 | 2229.3 | 1186.3 | 0.59435 | 4.707
2024-12-09 | 13:59 | Data | 0 | 34.965 | 33.446 | 132.803 | 7.64 | 125.48 | 2025.49 | 26.11 | 54.485 | 6.41 | 1.159 | 3.529 | 7468.46 | 1.371 | 97.3 | 75.3 | 1317 | 27.24 | 4854.5 | 2561.1 | 2522.5 | 3032.9 | 1186.3 | 0.57247 | 4.688
2024-12-09 | 13:59 | Data | 0 | 34.735 | 33.689 | 132.757 | 7.64 | 125.39 | 2026.39 | 26.1 | 54.485 | 6.41 | 1.148 | 3.537 | 7477.5 | 1.215 | 97.3 | 75.5 | 1316 | 27.29 | 4860.4 | 2413.7 | 2453 | 3593.5 | 1186.3 | 0.6564 | 4.686
2024-12-09 | 13:59 | Data | 0 | 34.796 | 33.412 | 132.712 | 7.63 | 125.435 | 2025.49 | 26.11 | 54.485 | 6.41 | 1.15 | 3.546 | 7482.02 | 1.175 | 97.3 | 75.5 | 1317 | 27.29 | 4863.3 | 2419 | 2452.5 | 3597.5 | 1186.3 | 0.65773 | 4.697
2024-12-09 | 14:00 | Data | 0 | 34.796 | 33.324 | 132.712 | 7.63 | 125.39 | 2025.49 | 26.11 | 54.485 | 6.4 | 1.153 | 3.543 | 7468.46 | 1.283 | 97.3 | 75.4 | 1316 | 27.24 | 4854.5 | 2418.3 | 2442.7 | 3585 | 1186.3 | 0.6591 | 4.696
2024-12-09 | 14:00 | Data | 0 | 34.789 | 33.439 | 132.667 | 7.64 | 125.435 | 2026.39 | 26.11 | 54.485 | 6.4 | 1.16 | 3.541 | 7454.89 | 1.269 | 97.3 | 75.3 | 1317 | 27.24 | 4845.7 | 2420.4 | 2451.3 | 3592.8 | 1186.3 | 0.65767 | 4.701
2024-12-09 | 14:00 | Data | 0 | 34.742 | 33.412 | 132.622 | 7.64 | 125.39 | 2030.01 | 26.11 | 54.575 | 6.41 | 1.159 | 3.527 | 7477.5 | 1.357 | 97.3 | 75.3 | 1319 | 27.24 | 4860.4 | 2417.3 | 2440 | 3581.6 | 1186.3 | 0.65825 | 4.685
2024-12-09 | 14:00 | Data | 0 | 34.594 | 33.297 | 132.667 | 7.63 | 125.435 | 2029.1 | 26.11 | 54.485 | 6.41 | 1.161 | 3.521 | 7468.46 | 1.161 | 97.3 | 75.2 | 1320 | 27.29 | 4854.5 | 2428.2 | 2469 | 3608.7 | 1186.3 | 0.65605 | 4.682
2024-12-09 | 14:00 | Data | 0 | 34.459 | 33.412 | 132.622 | 7.64 | 125.48 | 2030.01 | 26.11 | 54.485 | 6.41 | 1.162 | 3.547 | 7463.94 | 0.986 | 97.3 | 75.3 | 1320 | 27.24 | 4851.6 | 2410.8 | 2442.5 | 3593.9 | 1186.3 | 0.65649 | 4.709
2024-12-09 | 14:00 | Data | 0 | 34.573 | 33.5 | 132.667 | 7.64 | 125.48 | 2031.81 | 26.1 | 54.575 | 6.4 | 1.161 | 3.565 | 7463.94 | 1.046 | 97.3 | 75.4 | 1321 | 27.29 | 4851.6 | 2415.8 | 2434.7 | 3579.7 | 1186.3 | 0.65819 | 4.727
2024-12-09 | 14:00 | Data | 0 | 34.904 | 33.446 | 132.803 | 7.64 | 125.571 | 2031.81 | 26.11 | 54.575 | 6.41 | 1.154 | 3.549 | 7486.55 | 1.181 | 97.3 | 75.5 | 1321 | 27.24 | 4866.3 | 2419.4 | 2417.7 | 3563.5 | 1186.4 | 0.6645 | 4.703
2024-12-09 | 14:00 | Data | 0 | 34.783 | 33.621 | 132.712 | 7.64 | 125.48 | 2031.81 | 26.09 | 54.575 | 6.4 | 1.163 | 3.529 | 7463.94 | 1.235 | 97.3 | 75.2 | 1321 | 27.29 | 4851.6 | 2418.7 | 2435.8 | 3576.7 | 1186.4 | 0.65982 | 4.692
2024-12-09 | 14:00 | Data | 0 | 34.796 | 33.439 | 132.667 | 7.64 | 125.48 | 2031.81 | 26.09 | 54.575 | 6.41 | 1.164 | 3.523 | 7468.46 | 1.181 | 97.3 | 75.2 | 1320 | 27.29 | 4854.5 | 2420.4 | 2421.2 | 3570.7 | 1186.4 | 0.66123 | 4.687
2024-12-09 | 14:00 | Data | 0 | 34.567 | 33.412 | 132.803 | 7.64 | 125.435 | 2031.81 | 26.09 | 54.575 | 6.4 | 1.16 | 3.542 | 7848.32 | 1.154 | 97.3 | 75.3 | 1321 | 27.29 | 5101.4 | 2437.9 | 2432.8 | 3590.7 | 1186.4 | 0.66374 | 4.703
2024-12-09 | 14:00 | Data | 0 | 34.344 | 33.412 | 132.622 | 7.64 | 125.39 | 2036.33 | 26.08 | 54.665 | 6.4 | 1.164 | 3.546 | 7875.46 | 1.127 | 97.3 | 75.3 | 1324 | 27.29 | 5119 | 2413.6 | 2416.7 | 3562.2 | 1186.4 | 0.66013 | 4.709
2024-12-09 | 14:00 | Data | 0 | 34.796 | 33.243 | 132.622 | 7.64 | 125.39 | 2031.81 | 26.08 | 54.846 | 6.41 | 1.166 | 3.543 | 7477.5 | 1.154 | 97.3 | 75.2 | 1321 | 27.42 | 4860.4 | 2418.9 | 2458.7 | 3596.5 | 1186.4 | 0.6572 | 4.709
2024-12-09 | 14:00 | Data | 0 | 34.897 | 33.642 | 132.712 | 7.63 | 125.525 | 2031.81 | 26.08 | 54.846 | 6.4 | 1.163 | 3.556 | 7482.02 | 1.256 | 97.3 | 75.4 | 1321 | 27.42 | 4863.3 | 2432.2 | 2467.5 | 3613.7 | 1186.4 | 0.65781 | 4.719
2024-12-09 | 14:00 | Data | 0 | 34.567 | 33.628 | 132.803 | 7.64 | 125.525 | 2035.43 | 26.08 | 54.394 | 6.4 | 1.153 | 3.55 | 7482.02 | 1.181 | 97.3 | 75.5 | 1322 | 27.2 | 4863.3 | 2398.1 | 2439 | 3574.6 | 1186.4 | 0.65485 | 4.704
2024-12-09 | 14:00 | Data | 0 | 34.783 | 33.594 | 132.667 | 7.63 | 125.48 | 2038.14 | 26.08 | 54.756 | 6.4 | 1.159 | 3.553 | 7468.46 | 1.256 | 97.3 | 75.4 | 1324 | 27.33 | 4854.5 | 2417.3 | 2453.1 | 3588.3 | 1186.4 | 0.65663 | 4.71
2024-12-09 | 14:00 | Data | 0 | 34.783 | 33.635 | 132.757 | 7.63 | 125.48 | 2037.24 | 26.1 | 54.846 | 6.4 | 1.154 | 3.549 | 7482.02 | 1.175 | 97.3 | 75.5 | 1325 | 27.38 | 4863.3 | 2431.8 | 2438.5 | 3592.6 | 1186.4 | 0.66091 | 4.707
2024-12-09 | 14:00 | Data | 0 | 34.789 | 33.426 | 132.667 | 7.64 | 125.48 | 2037.24 | 26.08 | 54.756 | 6.42 | 1.152 | 3.555 | 7491.07 | 1.154 | 97.3 | 75.5 | 1324 | 27.38 | 4869.2 | 2419.5 | 2423.2 | 3574.6 | 1186.4 | 0.66323 | 4.707
2024-12-09 | 14:00 | Data | 0 | 34.796 | 33.527 | 132.712 | 7.63 | 125.525 | 2037.24 | 26.08 | 54.575 | 6.4 | 1.168 | 3.565 | 7477.5 | 1.154 | 97.3 | 75.3 | 1326 | 27.29 | 4860.4 | 2438.4 | 2451.6 | 3600.9 | 1186.4 | 0.66114 | 4.732
2024-12-09 | 14:01 | Data | 0 | 34.675 | 33.412 | 132.757 | 7.64 | 125.48 | 2035.43 | 26.09 | 54.485 | 6.41 | 1.169 | 3.537 | 7495.59 | 1.175 | 97.3 | 75.1 | 1324 | 27.29 | 4872.1 | 2448.1 | 2438.5 | 3604 | 1186.4 | 0.66335 | 4.708
2024-12-09 | 14:01 | Data | 0 | 34.573 | 33.412 | 132.712 | 7.63 | 125.48 | 2031.81 | 26.1 | 54.485 | 6.4 | 1.153 | 3.545 | 7491.07 | 1.161 | 97.3 | 75.5 | 1321 | 27.24 | 4869.2 | 2437.3 | 2446.5 | 3600.5 | 1186.4 | 0.66044 | 4.698
2024-12-09 | 14:01 | Data | 0 | 34.621 | 33.331 | 132.712 | 7.64 | 125.48 | 2031.81 | 26.1 | 54.846 | 6.4 | 1.153 | 3.547 | 7495.59 | 1.323 | 97.3 | 75.4 | 1321 | 27.42 | 4872.1 | 2457.4 | 2452.9 | 3618.2 | 1186.4 | 0.66334 | 4.704
2024-12-09 | 14:01 | Data | 0 | 34.681 | 33.635 | 132.712 | 7.63 | 125.48 | 2032.72 | 26.11 | 54.756 | 6.4 | 1.165 | 3.54 | 7495.59 | 1.148 | 97.3 | 75.2 | 1321 | 27.33 | 4872.1 | 2426.3 | 2440.2 | 3597.9 | 1186.4 | 0.65683 | 4.705
2024-12-09 | 14:01 | Data | 0 | 34.594 | 33.527 | 132.667 | 7.64 | 125.39 | 2029.1 | 26.1 | 54.846 | 6.41 | 1.155 | 3.545 | 7509.16 | 1.188 | 97.3 | 75.4 | 1319 | 27.38 | 4881 | 2431.4 | 2444.5 | 3596.3 | 1186.4 | 0.65837 | 4.7
2024-12-09 | 14:01 | Data | 0 | 34.58 | 33.52 | 132.757 | 7.64 | 125.48 | 2031.81 | 26.11 | 54.846 | 6.4 | 1.156 | 3.549 | 7509.16 | 1.141 | 97.3 | 75.5 | 1321 | 27.47 | 4881 | 2425.4 | 2455.8 | 3599.6 | 1186.4 | 0.65901 | 4.704
2024-12-09 | 14:01 | Data | 0 | 34.567 | 33.588 | 132.712 | 7.64 | 125.39 | 2034.53 | 26.11 | 54.936 | 6.4 | 1.163 | 3.538 | 7509.16 | 1.215 | 97.3 | 75.3 | 1322 | 27.42 | 4881 | 2440.1 | 2450.5 | 3609 | 1186.4 | 0.66149 | 4.704
2024-12-09 | 14:01 | Data | 0 | 34.573 | 33.412 | 132.803 | 7.64 | 125.48 | 2031.81 | 26.1 | 54.756 | 6.4 | 1.157 | 3.551 | 7504.64 | 1.148 | 97.3 | 75.4 | 1321 | 27.42 | 4878 | 2431.7 | 2463.6 | 3613.5 | 1186.4 | 0.65599 | 4.708
2024-12-09 | 14:01 | Data | 0 | 34.371 | 33.527 | 132.712 | 7.64 | 125.435 | 2029.1 | 26.1 | 54.756 | 6.4 | 1.163 | 3.549 | 7509.16 | 0.992 | 97.3 | 75.3 | 1319 | 27.38 | 4881 | 2478.6 | 2415.1 | 3614.6 | 1186.4 | 0.67038 | 4.712
2024-12-09 | 14:01 | Data | 0 | 34.621 | 33.412 | 132.622 | 7.64 | 125.48 | 2027.3 | 26.1 | 54.756 | 6.4 | 1.159 | 3.531 | 7509.16 | 1.161 | 97.3 | 75.3 | 1320 | 27.42 | 4881 | 2465.3 | 2443.3 | 3616.7 | 1186.4 | 0.66529 | 4.691
2024-12-09 | 14:01 | Data | 0 | 34.742 | 33.412 | 132.757 | 7.64 | 125.525 | 2029.1 | 26.11 | 54.846 | 6.41 | 1.151 | 3.545 | 7509.16 | 1.242 | 97.3 | 75.5 | 1319 | 27.42 | 4881 | 2478.1 | 2437.6 | 3623.9 | 1186.4 | 0.66849 | 4.695
2024-12-09 | 14:01 | Data | 0 | 34.803 | 33.426 | 132.803 | 7.63 | 125.571 | 2030.01 | 26.11 | 54.756 | 6.4 | 1.159 | 3.548 | 7504.64 | 1.235 | 97.3 | 75.4 | 1319 | 27.38 | 4878 | 2456.1 | 2458.6 | 3627.3 | 1186.4 | 0.66177 | 4.705
2024-12-09 | 14:01 | Data | 0 | 34.796 | 33.439 | 132.803 | 7.64 | 125.48 | 2026.39 | 26.11 | 54.846 | 6.41 | 1.164 | 3.544 | 7518.2 | 1.242 | 97.3 | 75.3 | 1317 | 27.42 | 4886.8 | 2449.8 | 2421.8 | 3595.8 | 1186.4 | 0.66435 | 4.707
2024-12-09 | 14:01 | Data | 0 | 34.621 | 33.527 | 132.712 | 7.64 | 125.571 | 2030.01 | 26.1 | 54.756 | 6.41 | 1.156 | 3.546 | 7509.16 | 1.161 | 97.3 | 75.4 | 1319 | 27.38 | 4881 | 2466.5 | 2453.2 | 3625.4 | 1186.4 | 0.66471 | 4.701
2024-12-09 | 14:01 | Data | 0 | 34.695 | 33.426 | 132.848 | 7.64 | 125.525 | 2029.1 | 26.1 | 54.846 | 6.4 | 1.155 | 3.548 | 7504.64 | 1.161 | 97.3 | 75.4 | 1319 | 27.42 | 4878 | 2443.2 | 2433.6 | 3596.1 | 1186.4 | 0.66229 | 4.703
2024-12-09 | 14:01 | Data | 0 | 34.783 | 33.844 | 132.757 | 7.64 | 125.525 | 2030.91 | 26.11 | 54.756 | 6.4 | 1.151 | 3.556 | 7509.16 | 1.208 | 97.3 | 75.5 | 1321 | 27.38 | 4881 | 2440 | 2460.1 | 3611.7 | 1186.4 | 0.65892 | 4.707
2024-12-09 | 14:01 | Data | 0 | 34.567 | 33.527 | 132.757 | 7.63 | 125.48 | 2034.53 | 26.1 | 54.846 | 6.41 | 1.155 | 3.537 | 7495.59 | 1.35 | 97.3 | 75.4 | 1322 | 27.42 | 4872.1 | 2450.6 | 2444.4 | 3609.1 | 1186.4 | 0.66437 | 4.693
2024-12-09 | 14:02 | Data | 0 | 34.796 | 33.736 | 132.712 | 7.63 | 125.525 | 2034.53 | 26.11 | 54.756 | 6.41 | 1.16 | 3.544 | 7482.02 | 1.262 | 97.3 | 75.3 | 1323 | 27.38 | 4863.3 | 2440.6 | 2465.2 | 3616 | 1186.4 | 0.65931 | 4.704
2024-12-09 | 14:02 | Data | 0 | 34.378 | 33.412 | 132.667 | 7.64 | 125.435 | 2035.43 | 26.11 | 54.756 | 6.4 | 1.163 | 3.534 | 7495.59 | 1.1 | 97.3 | 75.2 | 1323 | 27.42 | 4872.1 | 2452.3 | 2429.6 | 3604 | 1186.4 | 0.66505 | 4.698
2024-12-09 | 14:02 | Data | 0 | 34.681 | 33.419 | 132.712 | 7.63 | 125.435 | 2033.62 | 26.11 | 54.846 | 6.4 | 1.159 | 3.519 | 7477.5 | 1.148 | 97.3 | 75.2 | 1322 | 27.42 | 4860.4 | 2446.7 | 2443 | 3608.6 | 1186.4 | 0.663 | 4.678
2024-12-09 | 14:02 | Data | 0 | 34.567 | 33.615 | 132.667 | 7.64 | 125.48 | 2032.72 | 26.11 | 54.756 | 6.4 | 1.159 | 3.534 | 7482.02 | 1.215 | 97.3 | 75.3 | 1321 | 27.38 | 4863.3 | 2457.4 | 2434.5 | 3599 | 1186.4 | 0.66196 | 4.692
2024-12-09 | 14:02 | Data | 0 | 34.641 | 33.412 | 132.667 | 7.64 | 125.48 | 2040.85 | 26.11 | 54.756 | 6.41 | 1.159 | 3.536 | 7491.07 | 1.161 | 97.3 | 75.3 | 1327 | 27.38 | 4869.2 | 2435.4 | 2451.2 | 3608 | 1186.4 | 0.66025 | 4.695
2024-12-09 | 14:02 | Data | 0 | 34.796 | 33.81 | 132.757 | 7.64 | 125.48 | 2043.56 | 26.11 | 54.846 | 6.41 | 1.154 | 3.55 | 7495.59 | 1.04 | 97.3 | 75.5 | 1328 | 27.42 | 4872.1 | 2432.5 | 2458.1 | 3612 | 1186.4 | 0.65511 | 4.705
2024-12-09 | 14:02 | Data | 0 | 34.769 | 33.527 | 132.757 | 7.63 | 125.525 | 2042.66 | 26.11 | 54.846 | 6.41 | 1.163 | 3.533 | 7495.59 | 1.262 | 97.3 | 75.2 | 1327 | 27.42 | 4872.1 | 2463.2 | 2456.6 | 3626.1 | 1186.4 | 0.66324 | 4.696
2024-12-09 | 14:02 | Data | 0 | 34.668 | 33.412 | 132.667 | 7.64 | 125.48 | 2041.76 | 26.1 | 54.846 | 6.4 | 1.152 | 3.556 | 7491.07 | 1.181 | 97.3 | 75.5 | 1327 | 27.38 | 4869.2 | 2447.4 | 2437.6 | 3602.5 | 1186.4 | 0.66418 | 4.708
2024-12-09 | 14:02 | Data | 0 | 34.681 | 33.628 | 132.893 | 7.64 | 125.48 | 2042.66 | 26.11 | 54.756 | 6.4 | 1.154 | 3.542 | 7482.02 | 1.141 | 97.3 | 75.4 | 1328 | 27.38 | 4863.3 | 2453.1 | 2448 | 3610.3 | 1186.4 | 0.66048 | 4.697
2024-12-09 | 14:02 | Data | 0 | 34.567 | 33.412 | 132.667 | 7.63 | 125.48 | 2039.95 | 26.1 | 54.756 | 6.4 | 1.16 | 3.537 | 7477.5 | 1.154 | 97.3 | 75.3 | 1326 | 27.42 | 4860.4 | 2407.3 | 2453.1 | 3577.3 | 1186.4 | 0.6566 | 4.697
2024-12-09 | 14:02 | Data | 0 | 34.681 | 33.372 | 132.667 | 7.63 | 125.48 | 2037.24 | 26.11 | 54.846 | 6.4 | 1.159 | 3.55 | 7482.02 | 1.249 | 97.3 | 75.4 | 1324 | 27.42 | 4863.3 | 2379.8 | 2408.9 | 3526.5 | 1186.4 | 0.65945 | 4.71
2024-12-09 | 14:02 | Data | 0 | 34.357 | 33.5 | 132.757 | 7.63 | 125.48 | 2040.85 | 26.11 | 54.756 | 6.4 | 1.167 | 3.552 | 7472.98 | 0.932 | 97.3 | 75.3 | 1326 | 27.38 | 4857.4 | 2372.8 | 2459.8 | 3557.6 | 1186.4 | 0.65134 | 4.719
2024-12-09 | 14:02 | Data | 0 | 34.567 | 33.588 | 132.848 | 7.63 | 125.48 | 2042.66 | 26.1 | 54.846 | 6.41 | 1.164 | 3.551 | 7491.07 | 1.269 | 97.3 | 75.3 | 1327 | 27.42 | 4869.2 | 2372.7 | 2434.9 | 3541.2 | 1186.4 | 0.65501 | 4.716
2024-12-09 | 14:02 | Data | 0 | 34.796 | 33.642 | 132.667 | 7.64 | 125.525 | 2042.66 | 26.11 | 54.756 | 6.41 | 1.164 | 3.532 | 7486.55 | 1.168 | 97.3 | 75.2 | 1328 | 27.38 | 4866.3 | 2377.6 | 2424.6 | 3540.1 | 1186.4 | 0.65398 | 4.695
2024-12-09 | 14:02 | Data | 0 | 34.58 | 33.588 | 132.667 | 7.63 | 125.48 | 2039.05 | 26.11 | 54.936 | 6.4 | 1.154 | 3.558 | 7477.5 | 0.979 | 97.3 | 75.5 | 1325 | 27.38 | 4860.4 | 2395.5 | 2435.3 | 3550.2 | 1186.5 | 0.66116 | 4.712
2024-12-09 | 14:02 | Data | 0 | 34.627 | 33.412 | 132.622 | 7.64 | 125.435 | 2040.85 | 26.11 | 54.665 | 6.4 | 1.152 | 3.561 | 7482.02 | 1.161 | 97.3 | 75.6 | 1325 | 27.42 | 4863.3 | 2348.5 | 2443.8 | 3534 | 1186.5 | 0.64881 | 4.711
2024-12-09 | 14:02 | Data | 0 | 34.573 | 33.419 | 132.712 | 7.63 | 125.48 | 2039.05 | 26.1 | 54.846 | 6.4 | 1.16 | 3.543 | 7482.02 | 1.148 | 97.3 | 75.3 | 1327 | 27.38 | 4863.3 | 2381.2 | 2427.7 | 3542.6 | 1186.5 | 0.65812 | 4.702
2024-12-09 | 14:02 | Data | 0 | 34.486 | 33.412 | 132.712 | 7.64 | 125.48 | 2042.66 | 26.11 | 54.846 | 6.4 | 1.166 | 3.53 | 7491.07 | 1.134 | 97.3 | 75.2 | 1328 | 27.42 | 4869.2 | 2378.6 | 2417.6 | 3533.4 | 1186.5 | 0.65698 | 4.697
2024-12-09 | 14:03 | Data | 0 | 34.884 | 33.439 | 132.848 | 7.64 | 125.525 | 2041.76 | 26.13 | 54.846 | 6.41 | 1.159 | 3.527 | 7477.5 | 1.161 | 97.3 | 75.2 | 1328 | 27.33 | 4860.4 | 2422.9 | 2444.2 | 3590.2 | 1186.5 | 0.65782 | 4.688
2024-12-09 | 14:03 | Data | 0 | 34.58 | 33.419 | 132.622 | 7.64 | 125.435 | 2038.14 | 26.11 | 54.846 | 6.4 | 1.151 | 3.518 | 7482.02 | 1.148 | 97.3 | 75.3 | 1326 | 27.42 | 4863.3 | 2439.7 | 2432.1 | 3595 | 1186.5 | 0.66253 | 4.669
2024-12-09 | 14:03 | Data | 0 | 34.567 | 33.588 | 132.848 | 7.64 | 125.435 | 2037.24 | 26.11 | 54.756 | 6.4 | 1.162 | 3.537 | 7486.55 | 1.154 | 97.3 | 75.3 | 1325 | 27.33 | 4866.3 | 2436.5 | 2439.1 | 3597 | 1186.5 | 0.66303 | 4.699
2024-12-09 | 14:03 | Data | 0 | 34.58 | 33.527 | 132.803 | 7.63 | 125.48 | 2037.24 | 26.09 | 54.756 | 6.4 | 1.162 | 3.542 | 7491.07 | 1.04 | 97.3 | 75.3 | 1324 | 27.42 | 4869.2 | 2431.7 | 2428.2 | 3587.6 | 1186.5 | 0.66074 | 4.704
2024-12-09 | 14:03 | Data | 0 | 34.681 | 33.642 | 132.757 | 7.63 | 125.435 | 2037.24 | 26.11 | 54.846 | 6.4 | 1.154 | 3.536 | 7491.07 | 1.262 | 97.3 | 75.4 | 1325 | 27.38 | 4869.2 | 2441.3 | 2449.8 | 3602.5 | 1186.5 | 0.66142 | 4.69
2024-12-09 | 14:03 | Data | 0 | 34.681 | 33.412 | 132.712 | 7.64 | 125.48 | 2037.24 | 26.09 | 54.756 | 6.4 | 1.153 | 3.529 | 7500.11 | 1.168 | 97.3 | 75.4 | 1324 | 27.42 | 4875.1 | 2408.6 | 2431.1 | 3573.4 | 1186.5 | 0.65934 | 4.682
2024-12-09 | 14:03 | Data | 0 | 34.816 | 33.419 | 132.803 | 7.64 | 125.525 | 2033.62 | 26.08 | 54.846 | 6.41 | 1.159 | 3.534 | 7495.59 | 1.249 | 97.3 | 75.3 | 1323 | 27.42 | 4872.1 | 2449.1 | 2433.1 | 3602.3 | 1186.5 | 0.66557 | 4.693
2024-12-09 | 14:03 | Data | 0 | 34.789 | 33.642 | 132.803 | 7.64 | 125.525 | 2034.53 | 26.11 | 54.665 | 6.41 | 1.155 | 3.551 | 7500.11 | 1.154 | 97.3 | 75.5 | 1322 | 27.38 | 4875.1 | 2419.8 | 2438.3 | 3581.9 | 1186.5 | 0.66036 | 4.706
2024-12-09 | 14:03 | Data | 0 | 34.783 | 33.412 | 132.803 | 7.63 | 125.48 | 2032.72 | 26.09 | 54.846 | 6.4 | 1.156 | 3.547 | 7518.2 | 1.371 | 97.3 | 75.4 | 1321 | 27.42 | 4886.8 | 2411.9 | 2445.3 | 3580.9 | 1186.5 | 0.65762 | 4.707
2024-12-09 | 14:03 | Data | 0 | 34.567 | 33.412 | 132.757 | 7.64 | 125.525 | 2031.81 | 26.09 | 54.846 | 6.41 | 1.153 | 3.53 | 7495.59 | 1.154 | 97.3 | 75.3 | 1321 | 27.51 | 4872.1 | 2431.6 | 2429.4 | 3585 | 1186.5 | 0.66065 | 4.685
2024-12-09 | 14:03 | Data | 0 | 34.58 | 33.426 | 132.803 | 7.64 | 125.48 | 2037.24 | 26.09 | 54.846 | 6.4 | 1.149 | 3.518 | 7486.55 | 1.208 | 97.3 | 75.4 | 1325 | 27.38 | 4866.3 | 2421.6 | 2452.9 | 3594.6 | 1186.5 | 0.66191 | 4.668
2024-12-09 | 14:03 | Data | 0 | 34.567 | 33.412 | 132.712 | 7.64 | 125.48 | 2038.14 | 26.1 | 54.846 | 6.4 | 1.157 | 3.532 | 7491.07 | 1.148 | 97.3 | 75.4 | 1324 | 27.42 | 4869.2 | 2434.8 | 2428.8 | 3583.6 | 1186.5 | 0.66108 | 4.687
2024-12-09 | 14:03 | Data | 0 | 34.567 | 33.412 | 132.712 | 7.64 | 125.39 | 2037.24 | 26.09 | 54.756 | 6.41 | 1.155 | 3.548 | 7472.98 | 1.154 | 97.3 | 75.4 | 1324 | 27.42 | 4857.4 | 2434.7 | 2444.4 | 3595.6 | 1186.5 | 0.66211 | 4.703
2024-12-09 | 14:03 | Data | 0 | 34.357 | 33.52 | 132.893 | 7.63 | 125.48 | 2039.05 | 26.11 | 54.756 | 6.4 | 1.155 | 3.55 | 7477.5 | 0.992 | 97.3 | 75.5 | 1325 | 27.38 | 4860.4 | 2435.9 | 2433.9 | 3590.1 | 1186.5 | 0.66156 | 4.705
2024-12-09 | 14:03 | Data | 0 | 34.783 | 33.419 | 132.712 | 7.64 | 125.48 | 2037.24 | 26.1 | 54.665 | 6.41 | 1.164 | 3.527 | 7477.5 | 1.357 | 97.3 | 75.2 | 1325 | 27.42 | 4860.4 | 2420.7 | 2415.3 | 3564.9 | 1186.5 | 0.66226 | 4.69
2024-12-09 | 14:03 | Data | 0 | 34.486 | 33.412 | 132.667 | 7.64 | 125.435 | 2034.53 | 26.09 | 54.575 | 6.41 | 1.166 | 3.535 | 7482.02 | 1.134 | 97.3 | 75.2 | 1322 | 27.29 | 4863.3 | 2438.5 | 2438.6 | 3596.4 | 1186.5 | 0.66206 | 4.701
2024-12-09 | 14:03 | Data | 0 | 34.479 | 33.608 | 132.757 | 7.63 | 125.435 | 2034.53 | 26.09 | 54.846 | 6.4 | 1.154 | 3.531 | 7486.55 | 1.013 | 97.3 | 75.4 | 1322 | 27.42 | 4866.3 | 2433.4 | 2433.2 | 3585.6 | 1186.5 | 0.66103 | 4.685
2024-12-09 | 14:04 | Data | 0 | 34.769 | 33.466 | 132.757 | 7.64 | 125.48 | 2038.14 | 26.07 | 54.665 | 6.41 | 1.162 | 3.531 | 7491.07 | 1.154 | 97.3 | 75.2 | 1325 | 27.29 | 4869.2 | 2417.6 | 2441.4 | 3580.6 | 1186.5 | 0.6603 | 4.692
2024-12-09 | 14:04 | Data | 0 | 34.567 | 33.412 | 132.622 | 7.64 | 125.435 | 2039.95 | 26.1 | 54.756 | 6.4 | 1.161 | 3.537 | 7653.87 | 1.154 | 97.3 | 75.3 | 1327 | 27.42 | 4975 | 2431.3 | 2417.4 | 3571.9 | 1186.5 | 0.66836 | 4.699
2024-12-09 | 14:04 | Data | 0 | 34.546 | 33.412 | 132.622 | 7.64 | 125.345 | 2039.95 | 26.1 | 54.665 | 6.41 | 1.153 | 3.545 | 7653.87 | 1.154 | 97.3 | 75.5 | 1326 | 27.42 | 4975 | 2392.7 | 2413.6 | 3546.5 | 1186.5 | 0.65794 | 4.697
2024-12-09 | 14:04 | Data | 0 | 34.567 | 33.196 | 132.576 | 7.64 | 125.345 | 2037.24 | 26.08 | 54.756 | 6.4 | 1.159 | 3.545 | 7658.39 | 1.357 | 97.3 | 75.4 | 1325 | 27.42 | 4978 | 2409.1 | 2423.8 | 3568.5 | 1186.5 | 0.65881 | 4.704
2024-12-09 | 14:04 | Data | 0 | 34.796 | 33.243 | 132.667 | 7.64 | 125.48 | 2037.24 | 26.09 | 54.756 | 6.4 | 1.16 | 3.524 | 7658.39 | 1.256 | 97.3 | 75.2 | 1324 | 27.42 | 4978 | 2418.3 | 2412.4 | 3561.5 | 1186.5 | 0.665 | 4.684
2024-12-09 | 14:04 | Data | 0 | 34.465 | 33.527 | 132.712 | 7.63 | 125.435 | 2038.14 | 26.1 | 54.846 | 6.4 | 1.161 | 3.511 | 7486.55 | 1.141 | 97.3 | 75.1 | 1325 | 27.42 | 4866.3 | 2429.1 | 2470.6 | 3609.5 | 1186.5 | 0.65839 | 4.672
2024-12-09 | 14:04 | Data | 0 | 34.459 | 33.237 | 132.576 | 7.63 | 125.48 | 2037.24 | 26.11 | 54.846 | 6.4 | 1.15 | 3.524 | 7472.98 | 1.262 | 97.3 | 75.4 | 1325 | 27.42 | 4857.4 | 2421.9 | 2428.9 | 3576.5 | 1186.5 | 0.66371 | 4.675
2024-12-09 | 14:04 | Data | 0 | 34.567 | 33.405 | 132.712 | 7.64 | 125.435 | 2040.85 | 26.1 | 54.846 | 6.4 | 1.155 | 3.547 | 7463.94 | 1.168 | 97.3 | 75.4 | 1326 | 27.42 | 4851.6 | 2400.3 | 2451.1 | 3581.3 | 1186.5 | 0.65293 | 4.701
2024-12-09 | 14:04 | Data | 0 | 34.796 | 33.223 | 132.757 | 7.64 | 125.435 | 2040.85 | 26.1 | 54.846 | 6.41 | 1.156 | 3.544 | 7472.98 | 1.371 | 97.3 | 75.4 | 1327 | 27.38 | 4857.4 | 2413.9 | 2440.3 | 3576.6 | 1186.5 | 0.66075 | 4.699
2024-12-09 | 14:04 | Data | 0 | 34.897 | 33.426 | 132.848 | 7.63 | 125.48 | 2037.24 | 26.11 | 54.846 | 6.41 | 1.155 | 3.535 | 7477.5 | 1.168 | 97.3 | 75.4 | 1324 | 27.38 | 4860.4 | 2401.9 | 2433.6 | 3568.9 | 1186.5 | 0.65694 | 4.688
2024-12-09 | 14:04 | Data | 0 | 34.567 | 33.412 | 132.576 | 7.64 | 125.435 | 2041.76 | 26.1 | 54.846 | 6.4 | 1.159 | 3.537 | 7486.55 | 1.154 | 97.3 | 75.3 | 1328 | 27.38 | 4866.3 | 2414.8 | 2433.4 | 3573.8 | 1186.5 | 0.65913 | 4.696
2024-12-09 | 14:04 | Data | 0 | 34.432 | 33.608 | 132.712 | 7.64 | 125.48 | 2037.24 | 26.1 | 54.846 | 6.4 | 1.159 | 3.538 | 7477.5 | 1.154 | 97.3 | 75.3 | 1324 | 27.38 | 4860.4 | 2426.8 | 2422.5 | 3572.3 | 1186.5 | 0.66517 | 4.697
2024-12-09 | 14:04 | Data | 0 | 34.357 | 33.385 | 132.667 | 7.64 | 125.48 | 2038.14 | 26.1 | 54.756 | 6.4 | 1.157 | 3.541 | 7482.02 | 1.04 | 97.3 | 75.4 | 1325 | 27.38 | 4863.3 | 2407.3 | 2433.2 | 3570.9 | 1186.5 | 0.65896 | 4.701
2024-12-09 | 14:04 | Data | 0 | 34.573 | 33.392 | 132.712 | 7.64 | 125.435 | 2039.95 | 26.11 | 54.846 | 6.41 | 1.157 | 3.535 | 7477.5 | 1.127 | 97.3 | 75.3 | 1325 | 27.42 | 4860.4 | 2423.3 | 2460.3 | 3594.3 | 1186.5 | 0.6579 | 4.691
2024-12-09 | 14:04 | Data | 0 | 34.789 | 33.243 | 132.667 | 7.64 | 125.435 | 2039.95 | 26.11 | 54.665 | 6.4 | 1.169 | 3.547 | 7477.5 | 1.289 | 97.3 | 75.2 | 1326 | 27.42 | 4860.4 | 2408.2 | 2433.8 | 3575.6 | 1186.5 | 0.66223 | 4.719
2024-12-09 | 14:04 | Data | 0 | 34.681 | 33.453 | 132.757 | 7.63 | 125.435 | 2039.05 | 26.11 | 54.575 | 6.41 | 1.172 | 3.556 | 7491.07 | 1.121 | 97.3 | 75.2 | 1325 | 27.29 | 4869.2 | 2428.9 | 2435.2 | 3583 | 1186.5 | 0.66308 | 4.728
2024-12-09 | 14:04 | Data | 0 | 34.796 | 33.642 | 132.667 | 7.64 | 125.39 | 2031.81 | 26.1 | 54.575 | 6.4 | 1.153 | 3.543 | 7495.59 | 1.161 | 97.3 | 75.4 | 1321 | 27.29 | 4872.1 | 2385.6 | 2438.1 | 3563.3 | 1186.5 | 0.65327 | 4.697
2024-12-09 | 14:04 | Data | 0 | 34.567 | 33.385 | 132.667 | 7.64 | 125.48 | 2037.24 | 26.11 | 54.846 | 6.4 | 1.162 | 3.518 | 7509.16 | 1.208 | 97.3 | 75.2 | 1324 | 27.38 | 4881 | 2413.8 | 2417.2 | 3559.8 | 1186.5 | 0.66293 | 4.678
2024-12-09 | 14:05 | Data | 0 | 34.681 | 33.628 | 132.712 | 7.63 | 125.435 | 2037.24 | 26.1 | 54.846 | 6.4 | 1.151 | 3.537 | 7504.64 | 1.154 | 97.3 | 75.4 | 1324 | 27.42 | 4878 | 2409.1 | 2433.7 | 3567.7 | 1186.5 | 0.6587 | 4.689
2024-12-09 | 14:05 | Data | 0 | 34.567 | 33.426 | 132.667 | 7.63 | 125.48 | 2037.24 | 26.1 | 54.756 | 6.41 | 1.146 | 3.535 | 7500.11 | 1.141 | 97.3 | 75.5 | 1325 | 27.42 | 4875.1 | 2431.9 | 2422.8 | 3580.1 | 1186.5 | 0.66285 | 4.681
2024-12-09 | 14:05 | Data | 0 | 34.789 | 33.21 | 132.667 | 7.63 | 125.435 | 2034.53 | 26.1 | 54.756 | 6.4 | 1.154 | 3.534 | 7486.55 | 1.296 | 97.3 | 75.4 | 1322 | 27.38 | 4866.3 | 2407.8 | 2418.8 | 3558.1 | 1186.5 | 0.66035 | 4.688
2024-12-09 | 14:05 | Data | 0 | 34.789 | 33.642 | 132.712 | 7.64 | 125.48 | 2037.24 | 26.12 | 54.756 | 6.41 | 1.151 | 3.532 | 7491.07 | 1.04 | 97.3 | 75.4 | 1324 | 27.42 | 4869.2 | 2421.5 | 2431.9 | 3578 | 1186.5 | 0.66077 | 4.682
2024-12-09 | 14:05 | Data | 0 | 34.567 | 33.412 | 132.803 | 7.64 | 125.48 | 2037.24 | 26.11 | 54.846 | 6.4 | 1.154 | 3.528 | 7504.64 | 1.154 | 97.3 | 75.4 | 1324 | 27.38 | 4878 | 2401.1 | 2430 | 3567.8 | 1186.5 | 0.65882 | 4.682
2024-12-09 | 14:05 | Data | 0 | 34.627 | 33.412 | 132.667 | 7.63 | 125.48 | 2036.33 | 26.12 | 54.756 | 6.41 | 1.148 | 3.528 | 7500.11 | 1.046 | 97.3 | 75.5 | 1324 | 27.42 | 4875.1 | 2405.2 | 2441.6 | 3572.6 | 1186.6 | 0.65643 | 4.676
2024-12-09 | 14:05 | Data | 0 | 34.621 | 33.412 | 132.622 | 7.64 | 125.435 | 2037.24 | 26.11 | 54.756 | 6.4 | 1.146 | 3.518 | 7482.02 | 1.181 | 97.3 | 75.4 | 1324 | 27.38 | 4863.3 | 2409.2 | 2428.3 | 3562.7 | 1186.6 | 0.66003 | 4.664
2024-12-09 | 14:05 | Data | 0 | 34.553 | 33.581 | 132.757 | 7.64 | 125.435 | 2036.33 | 26.11 | 54.846 | 6.4 | 1.161 | 3.556 | 7482.02 | 1.195 | 97.3 | 75.4 | 1322 | 27.42 | 4863.3 | 2422.7 | 2427 | 3579.6 | 1186.6 | 0.65961 | 4.72
2024-12-09 | 14:05 | Data | 0 | 34.567 | 33.412 | 132.667 | 7.64 | 125.48 | 2032.72 | 26.11 | 54.756 | 6.4 | 1.151 | 3.531 | 7486.55 | 1.154 | 97.3 | 75.4 | 1321 | 27.42 | 4866.3 | 2411.2 | 2435.4 | 3572.2 | 1186.6 | 0.65761 | 4.682
2024-12-09 | 14:05 | Data | 0 | 34.695 | 33.216 | 132.712 | 7.64 | 125.525 | 2029.1 | 26.11 | 54.846 | 6.41 | 1.153 | 3.524 | 7468.46 | 1.283 | 97.3 | 75.3 | 1320 | 27.38 | 4854.5 | 2429.5 | 2410.2 | 3566.3 | 1186.6 | 0.6647 | 4.677
2024-12-09 | 14:05 | Data | 0 | 34.58 | 33.5 | 132.712 | 7.64 | 125.435 | 2031.81 | 26.11 | 54.846 | 6.41 | 1.168 | 3.52 | 7472.98 | 1.35 | 97.3 | 75.1 | 1321 | 27.38 | 4857.4 | 2421.8 | 2414 | 3574.2 | 1186.6 | 0.66588 | 4.688
2024-12-09 | 14:05 | Data | 0 | 34.951 | 33.642 | 132.757 | 7.64 | 125.435 | 2032.72 | 26.11 | 54.756 | 6.4 | 1.153 | 3.551 | 7468.46 | 1.357 | 97.3 | 75.5 | 1321 | 27.38 | 4854.5 | 2438.7 | 2421.8 | 3564.4 | 1186.6 | 0.66262 | 4.704
2024-12-09 | 14:05 | Data | 0 | 34.681 | 33.426 | 132.803 | 7.64 | 125.435 | 2029.1 | 26.1 | 54.846 | 6.41 | 1.154 | 3.58 | 7468.46 | 1.154 | 97.3 | 75.6 | 1320 | 27.42 | 4854.5 | 2416.1 | 2437.6 | 3582.4 | 1186.6 | 0.65935 | 4.735
2024-12-09 | 14:05 | Data | 0 | 34.567 | 33.412 | 132.712 | 7.64 | 125.435 | 2029.1 | 26.11 | 54.665 | 6.41 | 1.159 | 3.547 | 7468.46 | 1.154 | 97.3 | 75.4 | 1319 | 27.38 | 4854.5 | 2400.8 | 2426 | 3561.3 | 1186.6 | 0.65792 | 4.706
2024-12-09 | 14:05 | Data | 0 | 34.567 | 33.412 | 132.667 | 7.64 | 125.48 | 2030.91 | 26.09 | 54.846 | 6.41 | 1.164 | 3.554 | 7459.41 | 0.986 | 97.3 | 75.3 | 1321 | 27.42 | 4848.6 | 2394.6 | 2411.1 | 3548.2 | 1186.6 | 0.65936 | 4.718
2024-12-09 | 14:05 | Data | 0 | 34.459 | 33.304 | 132.757 | 7.64 | 125.48 | 2031.81 | 26.11 | 54.846 | 6.4 | 1.159 | 3.563 | 7463.94 | 1.337 | 97.3 | 75.4 | 1321 | 27.42 | 4851.6 | 2431.5 | 2408.3 | 3559.6 | 1186.6 | 0.66723 | 4.721
2024-12-09 | 14:05 | Data | 0 | 34.951 | 33.729 | 132.848 | 7.64 | 125.435 | 2031.81 | 26.1 | 54.756 | 6.41 | 1.159 | 3.558 | 7463.94 | 1.249 | 97.3 | 75.4 | 1321 | 27.38 | 4851.6 | 2429.2 | 2425.5 | 3579.5 | 1186.6 | 0.66286 | 4.717
2024-12-09 | 14:05 | Data | 0 | 34.681 | 33.635 | 132.712 | 7.64 | 125.435 | 2029.1 | 26.11 | 54.846 | 6.4 | 1.157 | 3.551 | 7468.46 | 1.154 | 97.3 | 75.4 | 1320 | 27.38 | 4854.5 | 2409.2 | 2421.3 | 3563.1 | 1186.6 | 0.65868 | 4.708
2024-12-09 | 14:06 | Data | 0 | 34.627 | 33.412 | 132.803 | 7.64 | 125.48 | 2032.72 | 26.11 | 54.936 | 6.4 | 1.163 | 3.545 | 7463.94 | 1.175 | 97.3 | 75.3 | 1321 | 27.42 | 4851.6 | 2417.8 | 2406.2 | 3555.9 | 1186.6 | 0.66557 | 4.707
2024-12-09 | 14:06 | Data | 0 | 34.796 | 33.203 | 132.757 | 7.63 | 125.435 | 2031.81 | 26.1 | 55.026 | 6.4 | 1.161 | 3.514 | 7468.46 | 1.364 | 97.3 | 75.1 | 1321 | 27.56 | 4854.5 | 2426.5 | 2425.5 | 3574.3 | 1186.6 | 0.66286 | 4.676
2024-12-09 | 14:06 | Data | 0 | 34.796 | 33.426 | 132.803 | 7.64 | 125.525 | 2035.43 | 26.11 | 54.846 | 6.41 | 1.148 | 3.545 | 7468.46 | 1.323 | 97.3 | 75.5 | 1323 | 27.42 | 4854.5 | 2420.3 | 2443 | 3583.2 | 1186.6 | 0.65967 | 4.692
2024-12-09 | 14:06 | Data | 0 | 34.823 | 33.426 | 132.712 | 7.64 | 125.48 | 2034.53 | 26.11 | 54.756 | 6.4 | 1.159 | 3.555 | 7472.98 | 1.161 | 97.3 | 75.4 | 1322 | 27.38 | 4857.4 | 2411.4 | 2436.8 | 3573.6 | 1186.6 | 0.65959 | 4.713
2024-12-09 | 14:06 | Data | 0 | 34.465 | 33.608 | 132.712 | 7.64 | 125.435 | 2033.62 | 26.1 | 54.846 | 6.4 | 1.167 | 3.538 | 7463.94 | 1.073 | 97.3 | 75.2 | 1322 | 27.42 | 4851.6 | 2409 | 2401.8 | 3567.8 | 1186.6 | 0.66231 | 4.706
2024-12-09 | 14:06 | Data | 0 | 34.796 | 33.446 | 132.712 | 7.64 | 125.571 | 2034.53 | 26.11 | 54.756 | 6.4 | 1.153 | 3.536 | 7463.94 | 1.235 | 97.3 | 75.4 | 1322 | 27.42 | 4851.6 | 2434.8 | 2440 | 3587.3 | 1186.6 | 0.66434 | 4.689
2024-12-09 | 14:06 | Data | 0 | 34.567 | 33.628 | 132.803 | 7.64 | 125.525 | 2032.72 | 26.1 | 54.846 | 6.4 | 1.152 | 3.529 | 7477.5 | 1.154 | 97.3 | 75.4 | 1321 | 27.42 | 4860.4 | 2405.9 | 2432.9 | 3568.1 | 1186.6 | 0.65914 | 4.682
2024-12-09 | 14:06 | Data | 0 | 34.621 | 33.588 | 132.757 | 7.64 | 125.571 | 2034.53 | 26.1 | 54.756 | 6.41 | 1.159 | 3.547 | 7459.41 | 0.986 | 97.3 | 75.3 | 1322 | 27.47 | 4848.6 | 2431.6 | 2432.2 | 3586.4 | 1186.6 | 0.66379 | 4.709
2024-12-09 | 14:06 | Data | 0 | 34.567 | 33.635 | 132.712 | 7.64 | 125.525 | 2034.53 | 26.1 | 54.846 | 6.41 | 1.164 | 3.544 | 7454.89 | 0.952 | 97.3 | 75.3 | 1323 | 27.38 | 4845.7 | 2419.4 | 2433.6 | 3574.1 | 1186.6 | 0.66207 | 4.706
2024-12-09 | 14:06 | Data | 0 | 34.796 | 33.75 | 132.893 | 7.64 | 125.571 | 2038.14 | 26.11 | 54.846 | 6.41 | 1.167 | 3.514 | 7459.41 | 1.141 | 97.3 | 75.1 | 1325 | 27.42 | 4848.6 | 2405.5 | 2430 | 3563.9 | 1186.6 | 0.6612 | 4.68
2024-12-09 | 14:06 | Data | 0 | 34.789 | 33.628 | 132.757 | 7.63 | 125.525 | 2039.95 | 26.11 | 54.756 | 6.4 | 1.165 | 3.538 | 7482.02 | 1.208 | 97.3 | 75.2 | 1327 | 27.38 | 4863.3 | 2409.9 | 2417.7 | 3560.4 | 1186.6 | 0.66002 | 4.703
2024-12-09 | 14:06 | Data | 0 | 34.627 | 33.412 | 132.757 | 7.64 | 125.525 | 2041.76 | 26.11 | 54.756 | 6.41 | 1.151 | 3.553 | 7482.02 | 1.161 | 97.3 | 75.5 | 1329 | 27.38 | 4863.3 | 2401.6 | 2416.1 | 3553.9 | 1186.6 | 0.65989 | 4.703
2024-12-09 | 14:06 | Data | 0 | 34.681 | 33.412 | 132.712 | 7.64 | 125.435 | 2042.66 | 26.11 | 54.936 | 6.4 | 1.144 | 3.546 | 7468.46 | 1.357 | 97.3 | 75.6 | 1328 | 27.42 | 4854.5 | 2398.6 | 2423.1 | 3560 | 1186.6 | 0.65689 | 4.69
2024-12-09 | 14:06 | Data | 0 | 34.803 | 33.473 | 132.803 | 7.64 | 125.571 | 2041.76 | 26.1 | 54.846 | 6.4 | 1.164 | 3.538 | 7468.46 | 1.323 | 97.3 | 75.2 | 1327 | 27.42 | 4854.5 | 2428 | 2429.8 | 3575.9 | 1186.6 | 0.66285 | 4.703
2024-12-09 | 14:06 | Data | 0 | 34.6 | 33.52 | 132.893 | 7.63 | 125.571 | 2039.95 | 26.11 | 54.846 | 6.4 | 1.156 | 3.546 | 7463.94 | 1.046 | 97.3 | 75.4 | 1325 | 27.42 | 4851.6 | 2413 | 2436.3 | 3577.4 | 1186.6 | 0.65984 | 4.703
2024-12-09 | 14:06 | Data | 0 | 34.681 | 33.419 | 132.757 | 7.64 | 125.525 | 2041.76 | 26.1 | 54.756 | 6.4 | 1.157 | 3.525 | 7472.98 | 1.303 | 97.3 | 75.3 | 1327 | 27.38 | 4857.4 | 2410.5 | 2419.9 | 3562.5 | 1186.6 | 0.66125 | 4.683
2024-12-09 | 14:06 | Data | 0 | 34.742 | 33.527 | 132.757 | 7.64 | 125.48 | 2042.66 | 26.11 | 54.846 | 6.4 | 1.156 | 3.556 | 7463.94 | 1.148 | 97.3 | 75.5 | 1328 | 27.38 | 4851.6 | 2395.7 | 2436.4 | 3566.5 | 1186.6 | 0.65551 | 4.711
2024-12-09 | 14:06 | Data | 0 | 34.573 | 33.615 | 132.803 | 7.64 | 125.571 | 2042.66 | 26.11 | 54.665 | 6.4 | 1.16 | 3.564 | 7468.46 | 1.154 | 97.3 | 75.4 | 1327 | 27.38 | 4854.5 | 2423.4 | 2395.7 | 3549.9 | 1186.6 | 0.66524 | 4.725
2024-12-09 | 14:07 | Data | 0 | 34.567 | 33.628 | 132.712 | 7.64 | 125.525 | 2043.56 | 26.11 | 54.846 | 6.4 | 1.159 | 3.537 | 7468.46 | 1.127 | 97.3 | 75.3 | 1328 | 27.42 | 4854.5 | 2434.3 | 2443.3 | 3589.2 | 1186.6 | 0.66142 | 4.696
2024-12-09 | 14:07 | Data | 0 | 34.58 | 33.412 | 132.803 | 7.64 | 125.525 | 2039.95 | 26.11 | 54.936 | 6.4 | 1.159 | 3.565 | 7468.46 | 1.154 | 97.3 | 75.4 | 1326 | 27.42 | 4854.5 | 2424.4 | 2457.7 | 3597.6 | 1186.6 | 0.65728 | 4.725
2024-12-09 | 14:07 | Data | 0 | 34.742 | 33.412 | 132.712 | 7.64 | 125.525 | 2034.53 | 26.11 | 54.756 | 6.4 | 1.148 | 3.564 | 7468.46 | 1.168 | 97.3 | 75.6 | 1323 | 27.47 | 4854.5 | 2393.8 | 2452.6 | 3572 | 1186.6 | 0.65374 | 4.711
2024-12-09 | 14:07 | Data | 0 | 34.769 | 33.81 | 132.803 | 7.64 | 125.571 | 2039.95 | 26.11 | 54.846 | 6.4 | 1.149 | 3.552 | 7454.89 | 1.148 | 97.3 | 75.6 | 1326 | 27.42 | 4845.7 | 2422 | 2431.4 | 3582.1 | 1186.6 | 0.66013 | 4.7
2024-12-09 | 14:07 | Data | 0 | 34.769 | 33.615 | 132.938 | 7.64 | 125.525 | 2039.95 | 26.1 | 54.846 | 6.4 | 1.156 | 3.543 | 7454.89 | 1.195 | 97.3 | 75.4 | 1326 | 27.38 | 4845.7 | 2424.5 | 2408.5 | 3557 | 1186.6 | 0.66719 | 4.699
2024-12-09 | 14:07 | Data | 0 | 34.621 | 33.419 | 132.757 | 7.64 | 125.525 | 2036.33 | 26.11 | 54.756 | 6.4 | 1.155 | 3.546 | 7468.46 | 1.168 | 97.3 | 75.4 | 1324 | 27.42 | 4854.5 | 2440.8 | 2410.7 | 3572.1 | 1186.6 | 0.66728 | 4.701
2024-12-09 | 14:07 | Data | 0 | 34.681 | 33.635 | 132.757 | 7.64 | 125.48 | 2037.24 | 26.11 | 54.936 | 6.4 | 1.149 | 3.544 | 7463.94 | 1.317 | 97.3 | 75.5 | 1324 | 27.42 | 4851.6 | 2425.9 | 2436.8 | 3580.3 | 1186.6 | 0.66314 | 4.693
2024-12-09 | 14:07 | Data | 0 | 34.783 | 33.527 | 132.803 | 7.64 | 125.525 | 2037.24 | 26.11 | 54.756 | 6.4 | 1.153 | 3.554 | 7445.85 | 1.269 | 97.3 | 75.5 | 1324 | 27.42 | 4839.8 | 2415.5 | 2424.2 | 3566.6 | 1186.6 | 0.66226 | 4.708
2024-12-09 | 14:07 | Data | 0 | 34.58 | 33.412 | 132.712 | 7.64 | 125.525 | 2036.33 | 26.12 | 54.756 | 6.4 | 1.16 | 3.553 | 7459.41 | 1.154 | 97.3 | 75.4 | 1324 | 27.42 | 4848.6 | 2422.8 | 2428.5 | 3572.3 | 1186.6 | 0.66298 | 4.713
2024-12-09 | 14:07 | Data | 0 | 34.681 | 33.642 | 132.803 | 7.63 | 125.571 | 2034.53 | 26.1 | 54.756 | 6.4 | 1.159 | 3.541 | 7468.46 | 1.317 | 97.3 | 75.3 | 1322 | 27.42 | 4854.5 | 2415.9 | 2431.4 | 3571.2 | 1186.6 | 0.65824 | 4.702
2024-12-09 | 14:07 | Data | 0 | 34.796 | 33.642 | 132.803 | 7.64 | 125.571 | 2034.53 | 26.1 | 54.756 | 6.41 | 1.16 | 3.533 | 7463.94 | 1.154 | 97.3 | 75.3 | 1322 | 27.42 | 4851.6 | 2417 | 2419.2 | 3563.5 | 1186.6 | 0.6632 | 4.693
2024-12-09 | 14:07 | Data | 0 | 34.796 | 33.466 | 132.757 | 7.64 | 125.525 | 2034.53 | 26.11 | 54.756 | 6.41 | 1.157 | 3.533 | 7477.5 | 1.269 | 97.3 | 75.3 | 1323 | 27.42 | 4860.4 | 2434.4 | 2417.3 | 3570.9 | 1186.6 | 0.66381 | 4.69
2024-12-09 | 14:07 | Data | 0 | 34.789 | 33.547 | 132.803 | 7.63 | 125.571 | 2038.14 | 26.09 | 54.846 | 6.4 | 1.156 | 3.553 | 7482.02 | 1.249 | 97.3 | 75.5 | 1323 | 27.42 | 4863.3 | 2413.3 | 2425 | 3572.4 | 1186.6 | 0.66364 | 4.709
2024-12-09 | 14:07 | Data | 0 | 34.796 | 33.527 | 132.848 | 7.63 | 125.571 | 2034.53 | 26.1 | 54.756 | 6.4 | 1.161 | 3.556 | 7472.98 | 1.181 | 97.3 | 75.4 | 1323 | 27.38 | 4857.4 | 2414.6 | 2444.6 | 3578.8 | 1186.7 | 0.65953 | 4.718
2024-12-09 | 14:07 | Data | 0 | 34.85 | 33.648 | 132.803 | 7.64 | 125.525 | 2035.43 | 26.12 | 54.846 | 6.4 | 1.159 | 3.544 | 7472.98 | 1.154 | 97.3 | 75.4 | 1322 | 27.38 | 4857.4 | 2440.7 | 2427.2 | 3580.4 | 1186.7 | 0.66592 | 4.705
2024-12-09 | 14:07 | Data | 0 | 34.58 | 33.588 | 132.712 | 7.64 | 125.48 | 2035.43 | 26.11 | 54.756 | 6.4 | 1.156 | 3.541 | 7477.5 | 1.154 | 97.3 | 75.4 | 1323 | 27.42 | 4860.4 | 2426.3 | 2420.2 | 3572.5 | 1186.7 | 0.66348 | 4.697
2024-12-09 | 14:07 | Data | 0 | 34.587 | 33.527 | 132.848 | 7.64 | 125.525 | 2036.33 | 26.11 | 54.665 | 6.41 | 1.159 | 3.544 | 7472.98 | 1.04 | 97.3 | 75.4 | 1324 | 27.33 | 4857.4 | 2424.4 | 2417.1 | 3567.9 | 1186.7 | 0.66301 | 4.702
2024-12-09 | 14:08 | Data | 0 | 34.573 | 33.588 | 132.712 | 7.64 | 125.525 | 2032.72 | 26.11 | 54.936 | 6.4 | 1.159 | 3.53 | 7472.98 | 1.04 | 97.3 | 75.3 | 1322 | 27.42 | 4857.4 | 2422.5 | 2422.8 | 3575.3 | 1186.7 | 0.66253 | 4.689
2024-12-09 | 14:08 | Data | 0 | 34.81 | 33.466 | 132.803 | 7.64 | 125.571 | 2034.53 | 26.11 | 54.846 | 6.41 | 1.165 | 3.519 | 7459.41 | 1.154 | 97.3 | 75.1 | 1322 | 27.38 | 4848.6 | 2421.5 | 2442.8 | 3589.6 | 1186.7 | 0.66083 | 4.682
2024-12-09 | 14:08 | Data | 0 | 34.573 | 33.527 | 132.757 | 7.64 | 125.525 | 2035.43 | 26.11 | 54.846 | 6.4 | 1.168 | 3.533 | 7454.89 | 1.357 | 97.3 | 75.1 | 1323 | 27.42 | 4845.7 | 2419.5 | 2416.6 | 3568.2 | 1186.7 | 0.6617 | 4.701
2024-12-09 | 14:08 | Data | 0 | 34.823 | 33.642 | 132.757 | 7.63 | 125.571 | 2038.14 | 26.12 | 54.846 | 6.4 | 1.155 | 3.552 | 7436.8 | 0.959 | 97.3 | 75.5 | 1324 | 27.42 | 4833.9 | 2385.9 | 2440.2 | 3562.6 | 1186.7 | 0.65269 | 4.709
2024-12-09 | 14:08 | Data | 0 | 34.891 | 33.554 | 132.848 | 7.63 | 125.616 | 2039.95 | 26.13 | 54.756 | 6.4 | 1.152 | 3.564 | 7445.85 | 1.127 | 97.3 | 75.6 | 1326 | 27.38 | 4839.8 | 2416.3 | 2447.1 | 3583.5 | 1186.7 | 0.65722 | 4.716
2024-12-09 | 14:08 | Data | 0 | 35.019 | 33.642 | 132.893 | 7.64 | 125.571 | 2041.76 | 26.1 | 54.846 | 6.4 | 1.163 | 3.533 | 7468.46 | 1.175 | 97.3 | 75.2 | 1328 | 27.42 | 4854.5 | 2409 | 2427.6 | 3568 | 1186.7 | 0.65766 | 4.697
2024-12-09 | 14:08 | Data | 0 | 34.783 | 33.642 | 132.757 | 7.64 | 125.571 | 2039.95 | 26.11 | 54.756 | 6.4 | 1.165 | 3.509 | 7463.94 | 1.323 | 97.3 | 75.1 | 1326 | 27.33 | 4851.6 | 2428.5 | 2425.1 | 3579.3 | 1186.7 | 0.66284 | 4.675
2024-12-09 | 14:08 | Data | 0 | 34.681 | 33.635 | 132.803 | 7.64 | 125.571 | 2043.56 | 26.11 | 54.846 | 6.41 | 1.157 | 3.546 | 7468.46 | 1.262 | 97.3 | 75.4 | 1328 | 27.38 | 4854.5 | 2408.4 | 2459.3 | 3591.4 | 1186.7 | 0.65469 | 4.702
2024-12-09 | 14:08 | Data | 0 | 34.796 | 33.419 | 132.848 | 7.64 | 125.616 | 2046.28 | 26.12 | 54.846 | 6.4 | 1.159 | 3.53 | 7468.46 | 1.168 | 97.3 | 75.3 | 1330 | 27.38 | 4854.5 | 2407.7 | 2450.7 | 3576.9 | 1186.7 | 0.6573 | 4.688
2024-12-09 | 14:08 | Data | 0 | 34.594 | 33.426 | 132.757 | 7.64 | 125.525 | 2046.28 | 26.1 | 54.846 | 6.4 | 1.161 | 3.542 | 7468.46 | 1.316 | 97.3 | 75.3 | 1330 | 27.38 | 4854.5 | 2420.8 | 2434.6 | 3577.5 | 1186.7 | 0.65963 | 4.704
2024-12-09 | 14:08 | Data | 0 | 34.796 | 33.844 | 132.848 | 7.63 | 125.616 | 2044.47 | 26.13 | 54.846 | 6.41 | 1.159 | 3.529 | 7482.02 | 1.154 | 97.3 | 75.3 | 1329 | 27.42 | 4863.3 | 2420.4 | 2427.8 | 3573.5 | 1186.7 | 0.66328 | 4.69
2024-12-09 | 14:08 | Data | 0 | 34.742 | 33.628 | 132.712 | 7.64 | 125.525 | 2046.28 | 26.12 | 54.665 | 6.4 | 1.16 | 3.54 | 7477.5 | 1.168 | 97.3 | 75.3 | 1329 | 27.38 | 4860.4 | 2435 | 2451.3 | 3600.2 | 1186.7 | 0.65954 | 4.699
2024-12-09 | 14:08 | Data | 0 | 34.769 | 33.858 | 132.803 | 7.64 | 125.48 | 2046.28 | 26.11 | 54.846 | 6.41 | 1.157 | 3.542 | 7477.5 | 1.154 | 97.3 | 75.4 | 1331 | 27.38 | 4860.4 | 2430.1 | 2433.4 | 3582 | 1186.7 | 0.66309 | 4.701
2024-12-09 | 14:08 | Data | 0 | 34.567 | 33.527 | 132.757 | 7.64 | 125.525 | 2046.28 | 26.13 | 54.665 | 6.4 | 1.162 | 3.534 | 7482.02 | 1.269 | 97.3 | 75.3 | 1330 | 27.33 | 4863.3 | 2434.2 | 2452.2 | 3596.9 | 1186.7 | 0.66213 | 4.696
2024-12-09 | 14:08 | Data | 0 | 34.796 | 33.527 | 132.667 | 7.64 | 125.571 | 2042.66 | 26.12 | 54.756 | 6.4 | 1.164 | 3.525 | 7468.46 | 1.154 | 97.3 | 75.2 | 1328 | 27.47 | 4854.5 | 2419.3 | 2424.3 | 3573.5 | 1186.7 | 0.66247 | 4.688
2024-12-09 | 14:08 | Data | 0 | 34.911 | 33.642 | 132.848 | 7.63 | 125.661 | 2046.28 | 26.12 | 54.846 | 6.41 | 1.167 | 3.534 | 7454.89 | 1.195 | 97.3 | 75.2 | 1330 | 27.42 | 4845.7 | 2430.3 | 2437.8 | 3585.8 | 1186.7 | 0.66277 | 4.701
2024-12-09 | 14:08 | Data | 0 | 34.992 | 33.669 | 132.893 | 7.63 | 125.616 | 2046.28 | 26.11 | 54.846 | 6.41 | 1.164 | 3.527 | 7468.46 | 1.269 | 97.3 | 75.2 | 1330 | 27.33 | 4854.5 | 2414.3 | 2450.2 | 3587.2 | 1186.7 | 0.65566 | 4.691
2024-12-09 | 14:08 | Data | 0 | 34.695 | 33.642 | 132.938 | 7.64 | 125.571 | 2043.56 | 26.13 | 54.756 | 6.4 | 1.159 | 3.556 | 7463.94 | 1.141 | 97.3 | 75.4 | 1328 | 27.38 | 4851.6 | 2420.5 | 2459.8 | 3596.9 | 1186.7 | 0.65665 | 4.713
2024-12-09 | 14:09 | Data | 0 | 34.621 | 33.615 | 132.938 | 7.64 | 125.571 | 2044.47 | 26.12 | 54.756 | 6.4 | 1.162 | 3.564 | 7486.55 | 1.06 | 97.3 | 75.4 | 1330 | 27.38 | 4866.3 | 2432.2 | 2448.2 | 3592 | 1186.7 | 0.65939 | 4.727
2024-12-09 | 14:09 | Data | 0 | 34.796 | 33.439 | 132.757 | 7.63 | 125.525 | 2044.47 | 26.12 | 54.756 | 6.4 | 1.16 | 3.516 | 7486.55 | 1.33 | 97.3 | 75.2 | 1330 | 27.42 | 4866.3 | 2433.2 | 2450.1 | 3593.7 | 1186.7 | 0.66121 | 4.676
2024-12-09 | 14:09 | Data | 0 | 34.999 | 33.655 | 132.848 | 7.63 | 125.661 | 2047.18 | 26.12 | 54.846 | 6.4 | 1.151 | 3.541 | 7504.64 | 1.33 | 97.3 | 75.5 | 1331 | 27.38 | 4878 | 2413.2 | 2439.3 | 3584 | 1186.7 | 0.65784 | 4.691
2024-12-09 | 14:09 | Data | 0 | 34.742 | 33.642 | 132.757 | 7.64 | 125.525 | 2046.28 | 26.12 | 54.756 | 6.4 | 1.156 | 3.552 | 7509.16 | 1.269 | 97.3 | 75.4 | 1330 | 27.47 | 4881 | 2418 | 2442.8 | 3587.9 | 1186.7 | 0.65898 | 4.709
2024-12-09 | 14:09 | Data | 0 | 34.796 | 33.642 | 132.938 | 7.64 | 125.661 | 2044.47 | 26.12 | 54.846 | 6.4 | 1.163 | 3.545 | 7509.16 | 1.154 | 97.3 | 75.3 | 1330 | 27.38 | 4881 | 2424.8 | 2412.8 | 3566.5 | 1186.7 | 0.66216 | 4.707
2024-12-09 | 14:09 | Data | 0 | 35.107 | 33.871 | 132.938 | 7.64 | 125.706 | 2042.66 | 26.12 | 54.846 | 6.4 | 1.157 | 3.533 | 7509.16 | 1.323 | 97.3 | 75.4 | 1327 | 27.38 | 4881 | 2419.9 | 2453.1 | 3593.8 | 1186.7 | 0.65791 | 4.688
2024-12-09 | 14:09 | Data | 0 | 34.823 | 33.642 | 132.848 | 7.64 | 125.706 | 2042.66 | 26.12 | 54.756 | 6.41 | 1.155 | 3.528 | 7509.16 | 1.181 | 97.3 | 75.3 | 1328 | 27.38 | 4881 | 2419.7 | 2439.8 | 3577.3 | 1186.7 | 0.66032 | 4.682
2024-12-09 | 14:09 | Data | 0 | 34.573 | 33.635 | 132.803 | 7.64 | 125.571 | 2041.76 | 26.13 | 54.756 | 6.4 | 1.164 | 3.53 | 7500.11 | 0.932 | 97.3 | 75.2 | 1328 | 27.42 | 4875.1 | 2423.5 | 2439.2 | 3581.3 | 1186.7 | 0.66077 | 4.694
2024-12-09 | 14:09 | Data | 0 | 34.796 | 33.844 | 132.848 | 7.64 | 125.616 | 2037.24 | 26.12 | 54.485 | 6.4 | 1.168 | 3.555 | 7509.16 | 1.154 | 97.3 | 75.3 | 1324 | 27.15 | 4881 | 2425.7 | 2462.9 | 3606 | 1186.7 | 0.65587 | 4.724
2024-12-09 | 14:09 | Data | 0 | 34.796 | 33.426 | 132.757 | 7.63 | 125.661 | 2046.28 | 26.11 | 54.846 | 6.4 | 1.161 | 3.544 | 7504.64 | 1.195 | 97.3 | 75.3 | 1329 | 27.42 | 4878 | 2420.6 | 2447.7 | 3590.8 | 1186.7 | 0.65629 | 4.706
2024-12-09 | 14:09 | Data | 0 | 34.911 | 33.642 | 132.848 | 7.63 | 125.661 | 2046.28 | 26.12 | 54.756 | 6.4 | 1.166 | 3.54 | 7504.64 | 1.175 | 97.3 | 75.2 | 1329 | 27.38 | 4878 | 2411.1 | 2467.5 | 3598.2 | 1186.7 | 0.65541 | 4.706
2024-12-09 | 14:09 | Data | 0 | 35.053 | 33.871 | 132.984 | 7.64 | 125.661 | 2046.28 | 26.12 | 54.756 | 6.41 | 1.16 | 3.56 | 7504.64 | 1.154 | 97.3 | 75.4 | 1329 | 27.38 | 4878 | 2437 | 2464.5 | 3605.8 | 1186.7 | 0.66267 | 4.72
2024-12-09 | 14:09 | Data | 0 | 34.965 | 33.642 | 132.848 | 7.64 | 125.616 | 2043.56 | 26.12 | 54.756 | 6.4 | 1.163 | 3.529 | 7504.64 | 1.175 | 97.3 | 75.2 | 1329 | 27.38 | 4878 | 2433.5 | 2428.7 | 3582.6 | 1186.7 | 0.66199 | 4.692
2024-12-09 | 14:09 | Data | 0 | 34.634 | 33.594 | 132.848 | 7.63 | 125.571 | 2048.08 | 26.1 | 54.846 | 6.4 | 1.161 | 3.541 | 7504.64 | 1.033 | 97.3 | 75.3 | 1331 | 27.38 | 4878 | 2388.9 | 2447.6 | 3573.1 | 1186.7 | 0.65344 | 4.702
2024-12-09 | 14:09 | Data | 0 | 34.796 | 33.642 | 132.984 | 7.63 | 125.616 | 2048.08 | 26.12 | 54.846 | 6.4 | 1.161 | 3.546 | 7504.64 | 1.154 | 97.3 | 75.3 | 1331 | 27.42 | 4878 | 2404.2 | 2441.5 | 3577.4 | 1186.7 | 0.65907 | 4.707
2024-12-09 | 14:09 | Data | 0 | 34.742 | 33.419 | 132.848 | 7.63 | 125.571 | 2049.89 | 26.12 | 54.756 | 6.4 | 1.154 | 3.529 | 7509.16 | 1.344 | 97.3 | 75.4 | 1332 | 27.38 | 4881 | 2430 | 2440.5 | 3586.8 | 1186.7 | 0.66285 | 4.683
2024-12-09 | 14:09 | Data | 0 | 34.776 | 33.817 | 132.938 | 7.63 | 125.661 | 2048.99 | 26.11 | 54.846 | 6.41 | 1.165 | 3.556 | 7504.64 | 1.256 | 97.3 | 75.3 | 1332 | 27.42 | 4878 | 2410.6 | 2424.1 | 3565.5 | 1186.7 | 0.66105 | 4.72
2024-12-09 | 14:09 | Data | 0 | 34.796 | 33.642 | 132.893 | 7.64 | 125.661 | 2048.08 | 26.12 | 54.665 | 6.4 | 1.157 | 3.548 | 7522.72 | 1.154 | 97.3 | 75.4 | 1332 | 27.33 | 4889.8 | 2436.5 | 2445.1 | 3593.9 | 1186.7 | 0.66278 | 4.705
2024-12-09 | 14:10 | Data | 0 | 34.965 | 33.925 | 132.938 | 7.64 | 125.616 | 2042.66 | 26.13 | 54.756 | 6.41 | 1.159 | 3.526 | 7509.16 | 1.208 | 97.3 | 75.3 | 1328 | 27.38 | 4881 | 2420.6 | 2429.1 | 3576 | 1186.7 | 0.66105 | 4.684
2024-12-09 | 14:10 | Data | 0 | 34.735 | 33.642 | 132.848 | 7.64 | 125.616 | 2042.66 | 26.12 | 54.756 | 6.41 | 1.162 | 3.542 | 7518.2 | 0.965 | 97.3 | 75.3 | 1327 | 27.38 | 4886.8 | 1538.6 | 1892.2 | 2471.5 | 1186.7 | 0.60638 | 4.704
2024-12-09 | 14:10 | Data | 0 | 34.938 | 33.54 | 132.984 | 7.63 | 125.706 | 2042.66 | 26.11 | 54.756 | 6.4 | 1.16 | 3.553 | 7513.68 | 1.317 | 97.3 | 75.4 | 1328 | 27.42 | 4883.9 | 1347.5 | 1782.8 | 2253.2 | 1186.7 | 0.59724 | 4.713
2024-12-09 | 14:10 | Data | 0 | 34.911 | 33.871 | 132.848 | 7.64 | 125.661 | 2041.76 | 26.12 | 54.846 | 6.4 | 1.161 | 3.558 | 7518.2 | 1.202 | 97.3 | 75.4 | 1329 | 27.42 | 4886.8 | 1330 | 1775.7 | 2237.4 | 1186.7 | 0.59289 | 4.72
2024-12-09 | 14:10 | Data | 0 | 34.85 | 33.446 | 132.938 | 7.64 | 125.661 | 2042.66 | 26.12 | 54.846 | 6.41 | 1.159 | 3.546 | 7522.72 | 1.283 | 97.3 | 75.4 | 1328 | 27.38 | 4889.8 | 1330.6 | 1797.6 | 2256.3 | 1186.7 | 0.58901 | 4.702
2024-12-09 | 14:10 | Data | 0 | 34.85 | 33.642 | 132.893 | 7.64 | 125.661 | 2042.66 | 26.13 | 54.756 | 6.4 | 1.152 | 3.559 | 7513.68 | 1.161 | 97.3 | 75.5 | 1327 | 27.38 | 4883.9 | 1340.8 | 1768.7 | 2237.3 | 1186.7 | 0.59755 | 4.711
2024-12-09 | 14:10 | Data | 0 | 35.053 | 33.655 | 132.938 | 7.64 | 125.661 | 2042.66 | 26.12 | 54.846 | 6.41 | 1.165 | 3.552 | 7504.64 | 1.188 | 97.3 | 75.3 | 1327 | 27.42 | 4878 | 1334.3 | 1801.7 | 2261 | 1186.7 | 0.58833 | 4.716
2024-12-09 | 14:10 | Data | 0 | 34.803 | 33.588 | 132.848 | 7.64 | 125.571 | 2042.66 | 26.12 | 54.756 | 6.4 | 1.16 | 3.528 | 7522.72 | 1.046 | 97.3 | 75.2 | 1328 | 27.38 | 4889.8 | 1343.2 | 1788.3 | 2254.1 | 1186.8 | 0.59521 | 4.689
2024-12-09 | 14:10 | Data | 0 | 34.796 | 33.642 | 132.848 | 7.64 | 125.661 | 2039.95 | 26.11 | 54.846 | 6.4 | 1.161 | 3.537 | 7522.72 | 1.148 | 97.3 | 75.3 | 1325 | 27.42 | 4889.8 | 1344.8 | 1779 | 2247.5 | 1186.8 | 0.59661 | 4.699
2024-12-09 | 14:10 | Data | 0 | 35.019 | 33.642 | 132.848 | 7.64 | 125.661 | 2039.95 | 26.12 | 54.756 | 6.41 | 1.155 | 3.52 | 7518.2 | 1.262 | 97.3 | 75.3 | 1326 | 27.38 | 4886.8 | 1336.5 | 1783.9 | 2247 | 1186.8 | 0.59332 | 4.675
2024-12-09 | 14:10 | Data | 0 | 34.992 | 33.642 | 132.893 | 7.64 | 125.571 | 2038.14 | 26.11 | 54.756 | 6.4 | 1.152 | 3.543 | 7522.72 | 1.262 | 97.3 | 75.5 | 1325 | 27.38 | 4889.8 | 1316.5 | 1799.4 | 2247.5 | 1186.8 | 0.5838 | 4.696
2024-12-09 | 14:10 | Data | 0 | 34.715 | 33.642 | 132.893 | 7.64 | 125.661 | 2042.66 | 26.11 | 54.936 | 6.4 | 1.159 | 3.543 | 7518.2 | 1.141 | 97.3 | 75.4 | 1327 | 27.42 | 4886.8 | 1338.3 | 1788.8 | 2250.5 | 1186.8 | 0.59365 | 4.7
2024-12-09 | 14:10 | Data | 0 | 35.019 | 33.669 | 132.848 | 7.64 | 125.661 | 2039.95 | 26.1 | 54.846 | 6.4 | 1.162 | 3.548 | 7522.72 | 1.161 | 97.3 | 75.3 | 1326 | 27.38 | 4889.8 | 1355.6 | 1795.2 | 2267.8 | 1186.8 | 0.59425 | 4.711
2024-12-09 | 14:10 | Data | 0 | 34.796 | 33.851 | 132.893 | 7.64 | 125.616 | 2039.05 | 26.11 | 54.846 | 6.4 | 1.159 | 3.559 | 7518.2 | 1.181 | 97.3 | 75.4 | 1326 | 27.42 | 4886.8 | 1326.6 | 1783.9 | 2243.2 | 1186.8 | 0.59022 | 4.718
2024-12-09 | 14:10 | Data | 0 | 35.012 | 33.817 | 132.984 | 7.63 | 125.661 | 2039.95 | 26.1 | 54.665 | 6.4 | 1.148 | 3.549 | 7518.2 | 1.262 | 97.3 | 75.6 | 1326 | 27.38 | 4886.8 | 1325.4 | 1759.1 | 2220.6 | 1186.8 | 0.59566 | 4.697
2024-12-09 | 14:10 | Data | 0 | 34.796 | 33.642 | 132.848 | 7.64 | 125.616 | 2039.95 | 26.11 | 54.756 | 6.41 | 1.149 | 3.549 | 7549.86 | 1.154 | 97.3 | 75.6 | 1326 | 27.42 | 4907.4 | 1325.5 | 1777.1 | 2236.2 | 1186.8 | 0.59056 | 4.698
2024-12-09 | 14:10 | Data | 0 | 34.634 | 33.642 | 132.893 | 7.64 | 125.661 | 2039.95 | 26.11 | 54.936 | 6.4 | 1.151 | 3.538 | 7549.86 | 1.134 | 97.3 | 75.4 | 1326 | 27.42 | 4907.4 | 1333.8 | 1794.9 | 2252.3 | 1186.8 | 0.591 | 4.691
2024-12-09 | 14:10 | Data | 0 | 34.796 | 33.642 | 132.848 | 7.63 | 125.661 | 2037.24 | 26.09 | 54.846 | 6.4 | 1.152 | 3.546 | 7527.25 | 1.154 | 97.3 | 75.5 | 1324 | 27.42 | 4892.7 | 1338.8 | 1806.3 | 2262.3 | 1186.8 | 0.5929 | 4.699
2024-12-09 | 14:11 | Data | 0 | 34.904 | 33.851 | 132.893 | 7.64 | 125.616 | 2030.91 | 26.11 | 54.846 | 6.41 | 1.153 | 3.549 | 7549.86 | 1.175 | 97.3 | 75.5 | 1321 | 27.38 | 4907.4 | 1336.7 | 1802.9 | 2263 | 1186.8 | 0.58957 | 4.702
2024-12-09 | 14:11 | Data | 0 | 34.843 | 33.642 | 132.848 | 7.64 | 125.706 | 2037.24 | 26.12 | 54.756 | 6.41 | 1.154 | 3.55 | 7513.68 | 1.161 | 97.3 | 75.5 | 1324 | 27.42 | 4883.9 | 1337.7 | 1797.9 | 2259.8 | 1186.8 | 0.59088 | 4.703
2024-12-09 | 14:11 | Data | 0 | 34.681 | 33.628 | 132.848 | 7.64 | 125.616 | 2036.33 | 26.1 | 54.756 | 6.4 | 1.154 | 3.549 | 7531.77 | 1.168 | 97.3 | 75.4 | 1324 | 27.42 | 4895.6 | 1344.8 | 1790.3 | 2256.4 | 1186.8 | 0.5941 | 4.704
2024-12-09 | 14:11 | Data | 0 | 34.911 | 33.642 | 132.803 | 7.64 | 125.571 | 2039.95 | 26.11 | 54.846 | 6.41 | 1.162 | 3.536 | 7531.77 | 1.371 | 97.3 | 75.3 | 1326 | 27.38 | 4895.6 | 1332.3 | 1772.7 | 2233.9 | 1186.8 | 0.59436 | 4.699
2024-12-09 | 14:11 | Data | 0 | 35.019 | 33.756 | 132.938 | 7.64 | 125.661 | 2044.47 | 26.1 | 54.846 | 6.41 | 1.165 | 3.542 | 7531.77 | 1.269 | 97.3 | 75.3 | 1330 | 27.42 | 4895.6 | 1307.9 | 1783.4 | 2241.5 | 1186.8 | 0.5915 | 4.707
2024-12-09 | 14:11 | Data | 0 | 34.796 | 33.642 | 132.893 | 7.64 | 125.616 | 2042.66 | 26.11 | 54.756 | 6.4 | 1.168 | 3.536 | 7549.86 | 1.269 | 97.3 | 75.2 | 1328 | 27.38 | 4907.4 | 1325.2 | 1786 | 2244.6 | 1186.8 | 0.58963 | 4.704
2024-12-09 | 14:11 | Data | 0 | 34.58 | 33.615 | 132.803 | 7.64 | 125.571 | 2043.56 | 26.11 | 54.665 | 6.4 | 1.163 | 3.542 | 7554.38 | 1.094 | 97.3 | 75.3 | 1328 | 27.33 | 4910.3 | 1328.9 | 1790.2 | 2245.3 | 1186.8 | 0.59091 | 4.705
2024-12-09 | 14:11 | Data | 0 | 34.81 | 33.561 | 132.893 | 7.64 | 125.661 | 2042.66 | 26.1 | 54.846 | 6.42 | 1.152 | 3.532 | 7545.34 | 1.148 | 97.3 | 75.4 | 1327 | 27.42 | 4904.5 | 1324.9 | 1779.5 | 2237.1 | 1186.8 | 0.59098 | 4.684
2024-12-09 | 14:11 | Data | 0 | 34.567 | 33.527 | 132.893 | 7.64 | 125.616 | 2042.66 | 26.1 | 54.665 | 6.41 | 1.149 | 3.546 | 7527.25 | 1.215 | 97.3 | 75.5 | 1328 | 27.42 | 4892.7 | 1322.1 | 1798.6 | 2250.9 | 1186.8 | 0.588 | 4.694
2024-12-09 | 14:11 | Data | 0 | 34.796 | 33.527 | 132.893 | 7.64 | 125.661 | 2042.66 | 26.11 | 54.756 | 6.41 | 1.159 | 3.545 | 7531.77 | 1.154 | 97.3 | 75.4 | 1328 | 27.42 | 4895.6 | 1330 | 1786.1 | 2243.5 | 1186.8 | 0.59099 | 4.704
2024-12-09 | 14:11 | Data | 0 | 34.783 | 33.642 | 132.848 | 7.64 | 125.616 | 2044.47 | 26.11 | 54.756 | 6.41 | 1.16 | 3.53 | 7504.64 | 1.357 | 97.3 | 75.2 | 1330 | 27.38 | 4878 | 1323 | 1767.3 | 2227.8 | 1186.8 | 0.59298 | 4.692
2024-12-09 | 14:11 | Data | 0 | 34.796 | 33.635 | 132.757 | 7.64 | 125.616 | 2046.28 | 26.1 | 54.936 | 6.4 | 1.156 | 3.516 | 7513.68 | 1.161 | 97.3 | 75.3 | 1330 | 27.47 | 4883.9 | 1321.4 | 1757.7 | 2220 | 1186.8 | 0.59414 | 4.672
2024-12-09 | 14:11 | Data | 0 | 34.681 | 33.534 | 132.893 | 7.64 | 125.616 | 2046.28 | 26.1 | 54.846 | 6.4 | 1.159 | 3.555 | 7518.2 | 1.289 | 97.3 | 75.4 | 1329 | 27.42 | 4886.8 | 1327.5 | 1768 | 2229.1 | 1186.8 | 0.5941 | 4.713
2024-12-09 | 14:11 | Data | 0 | 34.81 | 33.419 | 132.848 | 7.64 | 125.661 | 2041.76 | 26.1 | 54.756 | 6.41 | 1.155 | 3.551 | 7500.11 | 1.357 | 97.3 | 75.5 | 1328 | 27.38 | 4875.1 | 1328.3 | 1779.4 | 2240.3 | 1186.8 | 0.59249 | 4.706
2024-12-09 | 14:11 | Data | 0 | 34.594 | 33.615 | 132.803 | 7.64 | 125.571 | 2042.66 | 26.11 | 54.846 | 6.4 | 1.163 | 3.524 | 7491.07 | 0.986 | 97.3 | 75.2 | 1328 | 27.42 | 4869.2 | 1329.3 | 1773.9 | 2238.1 | 1186.8 | 0.59345 | 4.687
2024-12-09 | 14:11 | Data | 0 | 35.12 | 33.655 | 132.893 | 7.64 | 125.661 | 2043.56 | 26.1 | 54.936 | 6.4 | 1.159 | 3.502 | 7491.07 | 1.344 | 97.3 | 75.1 | 1328 | 27.38 | 4869.2 | 1342.6 | 1789.7 | 2256.2 | 1186.8 | 0.5929 | 4.662
2024-12-09 | 14:11 | Data | 0 | 34.796 | 33.466 | 132.848 | 7.64 | 125.616 | 2042.66 | 26.1 | 54.756 | 6.41 | 1.156 | 3.548 | 7482.02 | 1.33 | 97.3 | 75.4 | 1328 | 27.38 | 4863.3 | 1336.8 | 1771.6 | 2238.4 | 1186.8 | 0.59497 | 4.705
2024-12-09 | 14:11 | Data | 0 | 34.999 | 33.75 | 132.893 | 7.64 | 125.571 | 2042.66 | 26.11 | 54.846 | 6.4 | 1.154 | 3.55 | 7482.02 | 1.154 | 97.3 | 75.5 | 1327 | 27.42 | 4863.3 | 1323.6 | 1769.3 | 2226.8 | 1186.8 | 0.59241 | 4.704
2024-12-09 | 14:12 | Data | 0 | 34.911 | 33.642 | 132.848 | 7.64 | 125.661 | 2042.66 | 26.1 | 54.665 | 6.41 | 1.164 | 3.527 | 7468.46 | 1.181 | 97.3 | 75.2 | 1328 | 27.42 | 4854.5 | 1335.1 | 1782.4 | 2246.4 | 1186.8 | 0.59397 | 4.693
2024-12-09 | 14:12 | Data | 0 | 34.783 | 33.419 | 132.848 | 7.64 | 125.571 | 2041.76 | 26.11 | 54.846 | 6.4 | 1.16 | 3.537 | 7482.02 | 1.256 | 97.3 | 75.3 | 1328 | 27.38 | 4863.3 | 1313.6 | 1771.4 | 2225.1 | 1186.8 | 0.58843 | 4.698
2024-12-09 | 14:12 | Data | 0 | 34.567 | 33.527 | 132.757 | 7.63 | 125.571 | 2046.28 | 26.11 | 54.846 | 6.4 | 1.152 | 3.545 | 7491.07 | 1.33 | 97.3 | 75.5 | 1330 | 27.38 | 4869.2 | 1329.3 | 1795 | 2253.8 | 1186.8 | 0.58982 | 4.697
2024-12-09 | 14:12 | Data | 0 | 34.573 | 33.588 | 132.803 | 7.64 | 125.525 | 2048.08 | 26.1 | 54.846 | 6.41 | 1.148 | 3.546 | 7491.07 | 1.04 | 97.3 | 75.5 | 1332 | 27.42 | 4869.2 | 1328.1 | 1777.9 | 2242.5 | 1186.8 | 0.59205 | 4.692
2024-12-09 | 14:12 | Data | 0 | 34.85 | 33.642 | 132.803 | 7.64 | 125.616 | 2048.99 | 26.11 | 54.846 | 6.4 | 1.146 | 3.537 | 7486.55 | 1.053 | 97.3 | 75.6 | 1331 | 27.38 | 4866.3 | 1332.1 | 1795.2 | 2254.7 | 1186.8 | 0.58991 | 4.68
2024-12-09 | 14:12 | Data | 0 | 34.81 | 33.439 | 132.938 | 7.63 | 125.661 | 2048.99 | 26.1 | 54.846 | 6.4 | 1.147 | 3.53 | 7477.5 | 1.154 | 97.3 | 75.5 | 1331 | 27.38 | 4860.4 | 1315.9 | 1771.4 | 2226.8 | 1186.8 | 0.58962 | 4.676
2024-12-09 | 14:12 | Data | 0 | 35.019 | 33.743 | 132.848 | 7.63 | 125.661 | 2047.18 | 26.11 | 54.846 | 6.4 | 1.161 | 3.554 | 7482.02 | 1.283 | 97.3 | 75.4 | 1331 | 27.47 | 4863.3 | 1331.1 | 1798 | 2255.9 | 1186.8 | 0.58887 | 4.716
2024-12-09 | 14:12 | Data | 0 | 34.789 | 33.426 | 132.848 | 7.64 | 125.571 | 2048.08 | 26.11 | 54.665 | 6.4 | 1.153 | 3.561 | 7486.55 | 1.256 | 97.3 | 75.5 | 1331 | 27.38 | 4866.3 | 1344.1 | 1771.9 | 2243.8 | 1186.8 | 0.59742 | 4.714
2024-12-09 | 14:12 | Data | 0 | 34.573 | 33.412 | 132.803 | 7.64 | 125.616 | 2046.28 | 26.1 | 54.756 | 6.4 | 1.154 | 3.55 | 7486.55 | 1.269 | 97.3 | 75.4 | 1330 | 27.42 | 4866.3 | 1322.4 | 1805.2 | 2258.2 | 1186.8 | 0.58362 | 4.707
2024-12-09 | 14:12 | Data | 0 | 34.783 | 33.635 | 132.848 | 7.64 | 125.571 | 2046.28 | 26.11 | 54.846 | 6.41 | 1.159 | 3.527 | 7491.07 | 1.161 | 97.3 | 75.2 | 1330 | 27.42 | 4869.2 | 1346.6 | 1794.6 | 2257 | 1186.8 | 0.5926 | 4.687
2024-12-09 | 14:12 | Data | 0 | 34.884 | 33.642 | 132.848 | 7.63 | 125.616 | 2048.99 | 26.11 | 54.936 | 6.41 | 1.15 | 3.529 | 7495.59 | 1.161 | 97.3 | 75.4 | 1331 | 27.42 | 4872.1 | 1335.7 | 1795.5 | 2255.4 | 1186.8 | 0.58835 | 4.68
2024-12-09 | 14:12 | Data | 0 | 34.789 | 33.642 | 132.757 | 7.64 | 125.571 | 2048.08 | 26.11 | 54.756 | 6.41 | 1.164 | 3.529 | 7500.11 | 1.154 | 97.3 | 75.2 | 1331 | 27.38 | 4875.1 | 1342 | 1799.2 | 2264.2 | 1186.8 | 0.58583 | 4.693
2024-12-09 | 14:12 | Data | 0 | 34.918 | 33.446 | 132.803 | 7.64 | 125.616 | 2048.99 | 26.11 | 54.756 | 6.41 | 1.17 | 3.569 | 7482.02 | 1.215 | 97.3 | 75.3 | 1332 | 27.38 | 4863.3 | 1335.9 | 1798.3 | 2258.8 | 1186.8 | 0.58958 | 4.738
2024-12-09 | 14:12 | Data | 0 | 34.904 | 33.642 | 132.893 | 7.64 | 125.616 | 2047.18 | 26.1 | 54.846 | 6.41 | 1.159 | 3.535 | 7495.59 | 1.208 | 97.3 | 75.3 | 1332 | 27.38 | 4872.1 | 1334 | 1794.5 | 2255.5 | 1186.8 | 0.5901 | 4.694
2024-12-09 | 14:12 | Data | 0 | 34.567 | 33.412 | 132.757 | 7.64 | 125.48 | 2047.18 | 26.1 | 54.936 | 6.41 | 1.157 | 3.537 | 7491.07 | 1.33 | 97.3 | 75.3 | 1330 | 27.47 | 4869.2 | 1336.5 | 1807.7 | 2269.8 | 1186.8 | 0.58701 | 4.695
2024-12-09 | 14:12 | Data | 0 | 34.789 | 33.635 | 132.757 | 7.63 | 125.525 | 2039.95 | 26.1 | 55.026 | 6.4 | 1.16 | 3.558 | 7495.59 | 1.181 | 97.3 | 75.4 | 1327 | 27.51 | 4872.1 | 1341.4 | 1802.5 | 2265.5 | 1186.8 | 0.58917 | 4.719
2024-12-09 | 14:12 | Data | 0 | 34.904 | 33.642 | 132.893 | 7.64 | 125.571 | 2046.28 | 26.11 | 55.117 | 6.4 | 1.165 | 3.554 | 7491.07 | 1.256 | 97.3 | 75.3 | 1330 | 27.56 | 4869.2 | 1318.7 | 1810.3 | 2260.3 | 1186.8 | 0.5832 | 4.718
2024-12-09 | 14:13 | Data | 0 | 34.573 | 33.588 | 132.848 | 7.64 | 125.525 | 2046.28 | 26.11 | 54.936 | 6.41 | 1.156 | 3.555 | 7495.59 | 0.979 | 97.3 | 75.5 | 1330 | 27.47 | 4872.1 | 1326.5 | 1780.5 | 2240.4 | 1186.8 | 0.58998 | 4.709
2024-12-09 | 14:13 | Data | 0 | 34.587 | 33.615 | 132.848 | 7.64 | 125.616 | 2044.47 | 26.11 | 55.026 | 6.41 | 1.159 | 3.543 | 7500.11 | 1.154 | 97.3 | 75.4 | 1329 | 27.56 | 4875.1 | 1359.9 | 1801 | 2274.3 | 1186.8 | 0.59724 | 4.701
2024-12-09 | 14:13 | Data | 0 | 34.911 | 33.669 | 132.803 | 7.64 | 125.571 | 2046.28 | 26.11 | 55.026 | 6.41 | 1.156 | 3.538 | 7495.59 | 1.323 | 97.3 | 75.4 | 1330 | 27.56 | 4872.1 | 1334.2 | 1791.3 | 2253 | 1186.8 | 0.59471 | 4.694
2024-12-09 | 14:13 | Data | 0 | 34.621 | 33.615 | 132.803 | 7.64 | 125.616 | 2046.28 | 26.11 | 55.117 | 6.41 | 1.154 | 3.552 | 7513.68 | 1.134 | 97.3 | 75.4 | 1331 | 27.56 | 4883.9 | 1346.9 | 1815.1 | 2277.6 | 1186.8 | 0.59014 | 4.708
2024-12-09 | 14:13 | Data | 0 | 34.621 | 33.412 | 132.848 | 7.63 | 125.571 | 2046.28 | 26.1 | 55.117 | 6.4 | 1.162 | 3.534 | 7518.2 | 1.161 | 97.3 | 75.3 | 1331 | 27.51 | 4886.8 | 1343.4 | 1801.1 | 2265.4 | 1186.8 | 0.5913 | 4.696
2024-12-09 | 14:13 | Data | 0 | 34.796 | 33.642 | 132.848 | 7.64 | 125.571 | 2044.47 | 26.1 | 55.117 | 6.41 | 1.159 | 3.524 | 7504.64 | 1.154 | 97.3 | 75.3 | 1329 | 27.51 | 4878 | 1324.9 | 1768 | 2227.6 | 1186.8 | 0.59274 | 4.682
2024-12-09 | 14:13 | Data | 0 | 34.519 | 33.412 | 132.803 | 7.64 | 125.525 | 2044.47 | 26.11 | 55.026 | 6.4 | 1.16 | 3.53 | 7522.72 | 1.141 | 97.3 | 75.3 | 1330 | 27.56 | 4889.8 | 1323.3 | 1779.3 | 2236.6 | 1186.8 | 0.59048 | 4.691
2024-12-09 | 14:13 | Data | 0 | 34.796 | 33.642 | 132.803 | 7.64 | 125.616 | 1945.95 | 26.11 | 54.575 | 6.41 | 1.155 | 3.549 | 7491.07 | 1.154 | 97.2 | 75.4 | 1265 | 27.24 | 4869.2 | 1331.3 | 1799.9 | 2259.5 | 1186.8 | 0.58697 | 4.704
2024-12-09 | 14:13 | Data | 0 | 34.634 | 33.419 | 132.712 | 7.64 | 125.525 | 2029.1 | 26.11 | 54.756 | 6.4 | 1.141 | 3.562 | 7491.07 | 1.161 | 97.3 | 75.8 | 1321 | 27.33 | 4869.2 | 1332 | 1794.6 | 2255.9 | 1186.8 | 0.58996 | 4.701
2024-12-09 | 14:13 | Data | 0 | 34.573 | 33.358 | 132.757 | 7.63 | 125.525 | 2044.47 | 26.11 | 55.117 | 6.4 | 1.147 | 3.535 | 7491.07 | 1.262 | 97.3 | 75.5 | 1330 | 27.56 | 4869.2 | 1345.8 | 1793.4 | 2260.6 | 1186.8 | 0.59339 | 4.682
2024-12-09 | 14:13 | Data | 0 | 34.567 | 33.412 | 132.757 | 7.64 | 125.571 | 2046.28 | 26.1 | 55.117 | 6.41 | 1.163 | 3.527 | 7491.07 | 1.154 | 97.3 | 75.2 | 1331 | 27.51 | 4869.2 | 1335.9 | 1782.5 | 2245.8 | 1186.8 | 0.59402 | 4.69
2024-12-09 | 14:13 | Data | 0 | 34.965 | 33.662 | 132.938 | 7.64 | 125.661 | 2046.28 | 26.1 | 54.936 | 6.41 | 1.167 | 3.528 | 7486.55 | 1.283 | 97.3 | 75.2 | 1330 | 27.42 | 4866.3 | 1335 | 1765.2 | 2233.4 | 1186.8 | 0.5955 | 4.696
2024-12-09 | 14:13 | Data | 0 | 34.567 | 33.439 | 132.848 | 7.63 | 125.525 | 2040.85 | 26.1 | 55.117 | 6.4 | 1.156 | 3.547 | 7482.02 | 1.053 | 97.3 | 75.4 | 1327 | 27.51 | 4863.3 | 1324.7 | 1768.5 | 2230.1 | 1186.8 | 0.59324 | 4.701
2024-12-09 | 14:13 | Data | 0 | 34.567 | 33.689 | 132.848 | 7.64 | 125.616 | 2047.18 | 26.1 | 55.117 | 6.41 | 1.157 | 3.544 | 7482.02 | 1.148 | 97.3 | 75.4 | 1331 | 27.51 | 4863.3 | 1337.8 | 1781.6 | 2246.2 | 1186.8 | 0.59506 | 4.7
2024-12-09 | 14:13 | Data | 0 | 34.621 | 33.412 | 132.803 | 7.64 | 125.525 | 2049.89 | 26.11 | 55.026 | 6.41 | 1.156 | 3.531 | 7491.07 | 1.168 | 97.3 | 75.3 | 1333 | 27.47 | 4869.2 | 1337.9 | 1786.1 | 2250.6 | 1186.8 | 0.59314 | 4.687
2024-12-09 | 14:13 | Data | 0 | 34.573 | 33.412 | 132.712 | 7.63 | 125.525 | 2050.8 | 26.1 | 54.846 | 6.41 | 1.155 | 3.51 | 7477.5 | 1.154 | 97.3 | 75.2 | 1334 | 27.38 | 4860.4 | 1324.5 | 1781.3 | 2239 | 1186.8 | 0.59128 | 4.665
2024-12-09 | 14:13 | Data | 0 | 34.567 | 33.412 | 132.712 | 7.64 | 125.525 | 2051.7 | 26.1 | 55.117 | 6.4 | 1.166 | 3.509 | 7482.02 | 1.33 | 97.3 | 75.1 | 1333 | 27.51 | 4863.3 | 1336.5 | 1777.1 | 2242 | 1186.8 | 0.59575 | 4.675
2024-12-09 | 14:13 | Data | 0 | 34.789 | 33.412 | 132.803 | 7.64 | 125.525 | 2051.7 | 26.09 | 55.117 | 6.41 | 1.173 | 3.519 | 7482.02 | 1.181 | 97.3 | 75 | 1333 | 27.47 | 4863.3 | 1317.6 | 1777.4 | 2233.8 | 1186.8 | 0.58991 | 4.692
2024-12-09 | 14:14 | Data | 0 | 34.904 | 33.439 | 132.803 | 7.64 | 125.525 | 2053.51 | 26.11 | 54.756 | 6.41 | 1.164 | 3.532 | 7486.55 | 1.168 | 97.3 | 75.2 | 1335 | 27.38 | 4866.3 | 2415.2 | 2460 | 3595 | 1186.8 | 0.65854 | 4.698
2024-12-09 | 14:14 | Data | 0 | 34.567 | 33.412 | 132.757 | 7.64 | 125.525 | 2059.83 | 26.11 | 54.665 | 6.41 | 1.156 | 3.519 | 7486.55 | 1.154 | 97.3 | 75.3 | 1338 | 27.29 | 4866.3 | 2424.3 | 2464.3 | 3608.2 | 1186.8 | 0.65749 | 4.676
2024-12-09 | 14:14 | Data | 0 | 34.742 | 33.628 | 132.803 | 7.63 | 125.525 | 2052.6 | 26.1 | 54.846 | 6.4 | 1.16 | 3.52 | 7477.5 | 1.168 | 97.3 | 75.2 | 1335 | 27.42 | 4860.4 | 2438.8 | 2455.4 | 3610.9 | 1186.8 | 0.66188 | 4.681
2024-12-09 | 14:14 | Data | 0 | 34.479 | 33.608 | 132.848 | 7.63 | 125.435 | 2054.41 | 26.1 | 54.846 | 6.4 | 1.162 | 3.541 | 7477.5 | 0.972 | 97.3 | 75.3 | 1335 | 27.38 | 4860.4 | 2401.2 | 2461.2 | 3589.9 | 1186.8 | 0.65534 | 4.703
2024-12-09 | 14:14 | Data | 0 | 34.668 | 33.831 | 132.803 | 7.64 | 125.571 | 2058.93 | 26.09 | 54.846 | 6.4 | 1.153 | 3.538 | 7486.55 | 1.121 | 97.3 | 75.4 | 1339 | 27.38 | 4866.3 | 2419.1 | 2452.7 | 3581.7 | 1186.8 | 0.65858 | 4.691
2024-12-09 | 14:14 | Data | 0 | 34.506 | 33.372 | 132.622 | 7.64 | 125.48 | 2053.51 | 26.1 | 54.846 | 6.4 | 1.155 | 3.525 | 7495.59 | 1.026 | 97.3 | 75.3 | 1335 | 27.38 | 4872.1 | 2409.1 | 2455.1 | 3588.6 | 1186.8 | 0.65374 | 4.68
2024-12-09 | 14:14 | Data | 0 | 34.621 | 33.527 | 132.803 | 7.63 | 125.571 | 2054.41 | 26.1 | 54.756 | 6.41 | 1.152 | 3.541 | 7482.02 | 1.154 | 97.3 | 75.4 | 1335 | 27.38 | 4863.3 | 2430.7 | 2453.3 | 3599 | 1186.8 | 0.66018 | 4.694
2024-12-09 | 14:14 | Data | 0 | 34.999 | 33.439 | 132.803 | 7.63 | 125.571 | 2052.6 | 26.11 | 54.846 | 6.4 | 1.16 | 3.536 | 7477.5 | 1.364 | 97.3 | 75.3 | 1335 | 27.38 | 4860.4 | 2434.9 | 2461 | 3605.7 | 1186.8 | 0.65948 | 4.696
2024-12-09 | 14:14 | Data | 0 | 34.681 | 33.412 | 132.712 | 7.63 | 125.525 | 2053.51 | 26.11 | 54.756 | 6.4 | 1.162 | 3.523 | 7477.5 | 1.364 | 97.3 | 75.2 | 1335 | 27.33 | 4860.4 | 2440.5 | 2452 | 3595.2 | 1186.8 | 0.66041 | 4.686
2024-12-09 | 14:14 | Data | 0 | 34.567 | 33.5 | 132.803 | 7.64 | 125.48 | 2053.51 | 26.09 | 54.846 | 6.4 | 1.16 | 3.527 | 7495.59 | 1.04 | 97.3 | 75.2 | 1335 | 27.47 | 4872.1 | 2434.6 | 2453.5 | 3597.5 | 1186.9 | 0.66209 | 4.689
2024-12-09 | 14:14 | Data | 0 | 34.681 | 33.412 | 132.803 | 7.64 | 125.525 | 2057.12 | 26.11 | 54.846 | 6.41 | 1.153 | 3.534 | 7482.02 | 1.168 | 97.3 | 75.4 | 1337 | 27.42 | 4863.3 | 2413.9 | 2462.3 | 3602.8 | 1186.9 | 0.65647 | 4.689
2024-12-09 | 14:14 | Data | 0 | 34.789 | 33.439 | 132.712 | 7.64 | 125.525 | 2056.22 | 26.09 | 54.756 | 6.41 | 1.155 | 3.528 | 7491.07 | 1.215 | 97.3 | 75.3 | 1337 | 27.38 | 4869.2 | 2427.3 | 2460 | 3600.8 | 1186.9 | 0.65748 | 4.683
2024-12-09 | 14:14 | Data | 0 | 34.958 | 33.858 | 132.848 | 7.64 | 125.571 | 2051.7 | 26.08 | 54.756 | 6.41 | 1.162 | 3.547 | 7495.59 | 1.208 | 97.3 | 75.3 | 1334 | 27.38 | 4872.1 | 2411.1 | 2450.8 | 3587.2 | 1186.9 | 0.65911 | 4.709
2024-12-09 | 14:14 | Data | 0 | 34.796 | 33.689 | 132.893 | 7.64 | 125.661 | 2056.22 | 26.1 | 54.756 | 6.4 | 1.152 | 3.545 | 7486.55 | 1.154 | 97.3 | 75.5 | 1337 | 27.42 | 4866.3 | 2432.4 | 2466.8 | 3609.4 | 1186.9 | 0.65753 | 4.697
2024-12-09 | 14:14 | Data | 0 | 34.742 | 33.635 | 132.757 | 7.63 | 125.571 | 2056.22 | 26.09 | 54.756 | 6.41 | 1.151 | 3.536 | 7495.59 | 1.154 | 97.3 | 75.4 | 1337 | 27.42 | 4872.1 | 2421.2 | 2475.6 | 3617.7 | 1186.9 | 0.65513 | 4.687
2024-12-09 | 14:14 | Data | 0 | 34.742 | 33.669 | 132.803 | 7.64 | 125.571 | 2050.8 | 26.08 | 54.846 | 6.4 | 1.149 | 3.516 | 7486.55 | 1.256 | 97.3 | 75.4 | 1334 | 27.38 | 4866.3 | 2407.1 | 2443.3 | 3577.9 | 1186.9 | 0.65768 | 4.666
2024-12-09 | 14:14 | Data | 0 | 34.803 | 33.473 | 132.893 | 7.63 | 125.571 | 2048.99 | 26.08 | 54.756 | 6.41 | 1.153 | 3.521 | 7491.07 | 1.127 | 97.3 | 75.3 | 1332 | 27.42 | 4869.2 | 2411.8 | 2439.5 | 3583 | 1186.9 | 0.65796 | 4.672
2024-12-09 | 14:14 | Data | 0 | 34.6 | 33.615 | 132.803 | 7.64 | 125.525 | 2050.8 | 26.09 | 54.756 | 6.41 | 1.155 | 3.537 | 7491.07 | 1.046 | 97.3 | 75.4 | 1333 | 27.38 | 4869.2 | 2423 | 2446.2 | 3590.9 | 1186.9 | 0.65852 | 4.691
2024-12-09 | 14:15 | Data | 0 | 34.796 | 33.439 | 132.803 | 7.64 | 125.616 | 2051.7 | 26.09 | 54.756 | 6.41 | 1.166 | 3.519 | 7477.5 | 1.357 | 97.3 | 75.1 | 1334 | 27.33 | 4860.4 | 2423.2 | 2428.1 | 3579.6 | 1186.9 | 0.65995 | 4.685
2024-12-09 | 14:15 | Data | 0 | 34.6 | 33.419 | 132.712 | 7.64 | 125.616 | 2051.7 | 26.08 | 54.756 | 6.4 | 1.162 | 3.514 | 7509.16 | 1.154 | 97.3 | 75.1 | 1333 | 27.38 | 4881 | 2416 | 2423.7 | 3567.4 | 1186.9 | 0.66062 | 4.677
2024-12-09 | 14:15 | Data | 0 | 34.708 | 33.75 | 132.848 | 7.64 | 125.525 | 2040.85 | 26.09 | 54.756 | 6.4 | 1.154 | 3.516 | 7486.55 | 1.148 | 97.3 | 75.3 | 1326 | 27.38 | 4866.3 | 2402.2 | 2433.5 | 3570.8 | 1186.9 | 0.6594 | 4.67
2024-12-09 | 14:15 | Data | 0 | 34.796 | 33.642 | 132.848 | 7.64 | 125.571 | 2046.28 | 26.1 | 54.846 | 6.41 | 1.149 | 3.523 | 7482.02 | 1.269 | 97.3 | 75.4 | 1330 | 27.38 | 4863.3 | 2423.9 | 2441.5 | 3590.3 | 1186.9 | 0.66209 | 4.674
2024-12-09 | 14:15 | Data | 0 | 34.992 | 33.642 | 132.848 | 7.64 | 125.661 | 2044.47 | 26.11 | 54.846 | 6.4 | 1.159 | 3.544 | 7495.59 | 1.262 | 97.3 | 75.4 | 1328 | 27.42 | 4872.1 | 2437.9 | 2451.3 | 3600.6 | 1186.9 | 0.66247 | 4.701
2024-12-09 | 14:15 | Data | 0 | 34.58 | 33.615 | 132.712 | 7.63 | 125.48 | 2047.18 | 26.1 | 54.846 | 6.41 | 1.165 | 3.551 | 7495.59 | 1.04 | 97.3 | 75.3 | 1329 | 27.38 | 4872.1 | 2433.6 | 2449.5 | 3599.4 | 1186.9 | 0.66308 | 4.715
2024-12-09 | 14:15 | Data | 0 | 34.796 | 33.642 | 132.712 | 7.64 | 125.571 | 2044.47 | 26.1 | 54.846 | 6.4 | 1.159 | 3.537 | 7477.5 | 1.154 | 97.3 | 75.3 | 1330 | 27.42 | 4860.4 | 2401.3 | 2439.7 | 3571.6 | 1186.9 | 0.65653 | 4.697
2024-12-09 | 14:15 | Data | 0 | 34.567 | 33.635 | 132.893 | 7.64 | 125.571 | 2046.28 | 26.11 | 54.846 | 6.4 | 1.157 | 3.518 | 7477.5 | 1.114 | 97.3 | 75.3 | 1329 | 27.42 | 4860.4 | 2426.6 | 2432.4 | 3580.1 | 1186.9 | 0.66223 | 4.674
2024-12-09 | 14:15 | Data | 0 | 34.695 | 33.52 | 132.803 | 7.64 | 125.571 | 2044.47 | 26.09 | 54.756 | 6.41 | 1.154 | 3.523 | 7482.02 | 1.033 | 97.3 | 75.3 | 1330 | 27.38 | 4863.3 | 2417.4 | 2437.5 | 3578.3 | 1186.9 | 0.66018 | 4.675
2024-12-09 | 14:15 | Data | 0 | 34.783 | 33.419 | 132.848 | 7.63 | 125.571 | 2048.99 | 26.11 | 54.756 | 6.4 | 1.168 | 3.527 | 7491.07 | 1.242 | 97.3 | 75.1 | 1331 | 27.38 | 4869.2 | 2416.7 | 2438.3 | 3580.7 | 1186.9 | 0.65892 | 4.696
2024-12-09 | 14:15 | Data | 0 | 34.789 | 33.642 | 132.848 | 7.64 | 125.616 | 2048.99 | 26.1 | 54.756 | 6.4 | 1.162 | 3.533 | 7482.02 | 1.154 | 97.3 | 75.3 | 1331 | 27.47 | 4863.3 | 2425.1 | 2423.5 | 3576.4 | 1186.9 | 0.65754 | 4.694
2024-12-09 | 14:15 | Data | 0 | 34.796 | 33.642 | 132.803 | 7.64 | 125.616 | 2048.99 | 26.1 | 54.846 | 6.4 | 1.155 | 3.537 | 7509.16 | 1.154 | 97.3 | 75.4 | 1331 | 27.38 | 4881 | 2424.7 | 2425.8 | 3572.3 | 1186.9 | 0.66163 | 4.692
2024-12-09 | 14:15 | Data | 0 | 34.803 | 33.426 | 132.848 | 7.64 | 125.661 | 2051.7 | 26.11 | 54.846 | 6.4 | 1.162 | 3.548 | 7495.59 | 1.202 | 97.3 | 75.3 | 1333 | 27.42 | 4872.1 | 2437.8 | 2439.2 | 3592.3 | 1186.9 | 0.66323 | 4.71
2024-12-09 | 14:15 | Data | 0 | 34.634 | 33.588 | 132.757 | 7.63 | 125.571 | 2047.18 | 26.1 | 54.846 | 6.4 | 1.166 | 3.537 | 7491.07 | 1.188 | 97.3 | 75.2 | 1330 | 27.42 | 4869.2 | 2419.7 | 2440.7 | 3587 | 1186.9 | 0.65855 | 4.702
2024-12-09 | 14:15 | Data | 0 | 34.789 | 33.426 | 132.893 | 7.64 | 125.571 | 2046.28 | 26.11 | 54.846 | 6.4 | 1.169 | 3.545 | 7495.59 | 1.371 | 97.3 | 75.2 | 1329 | 27.42 | 4872.1 | 2417.6 | 2442.8 | 3581.9 | 1186.9 | 0.65897 | 4.714
2024-12-09 | 14:15 | Data | 0 | 34.796 | 33.426 | 132.757 | 7.64 | 125.616 | 2042.66 | 26.09 | 54.846 | 6.4 | 1.16 | 3.524 | 7482.02 | 1.181 | 97.3 | 75.2 | 1328 | 27.42 | 4863.3 | 2415.4 | 2420.6 | 3563.4 | 1186.9 | 0.66393 | 4.682
2024-12-09 | 14:15 | Data | 0 | 34.573 | 33.642 | 132.848 | 7.64 | 125.616 | 2042.66 | 26.1 | 54.756 | 6.4 | 1.166 | 3.516 | 7491.07 | 1.141 | 97.3 | 75.1 | 1328 | 27.38 | 4869.2 | 2418.7 | 2436.9 | 3585.7 | 1186.9 | 0.66157 | 4.682
2024-12-09 | 14:16 | Data | 0 | 34.695 | 33.52 | 132.893 | 7.64 | 125.616 | 2044.47 | 26.11 | 54.665 | 6.41 | 1.161 | 3.536 | 7482.02 | 0.952 | 97.3 | 75.3 | 1330 | 27.38 | 4863.3 | 2430.5 | 2439 | 3605.8 | 1186.9 | 0.65748 | 4.698
2024-12-09 | 14:16 | Data | 0 | 34.486 | 33.412 | 132.848 | 7.64 | 125.706 | 2046.28 | 26.1 | 54.846 | 6.41 | 1.165 | 3.527 | 7482.02 | 1.073 | 97.3 | 75.2 | 1330 | 27.42 | 4863.3 | 2411.9 | 2437.8 | 3579.7 | 1186.9 | 0.6593 | 4.691
2024-12-09 | 14:16 | Data | 0 | 34.965 | 33.554 | 132.893 | 7.64 | 125.616 | 2048.99 | 26.11 | 54.846 | 6.4 | 1.159 | 3.543 | 7495.59 | 1.35 | 97.3 | 75.4 | 1332 | 27.42 | 4872.1 | 2405.9 | 2431.6 | 3573.1 | 1186.9 | 0.65623 | 4.702
2024-12-09 | 14:16 | Data | 0 | 34.789 | 33.466 | 132.803 | 7.64 | 125.525 | 2048.99 | 26.1 | 54.756 | 6.4 | 1.159 | 3.538 | 7477.5 | 1.33 | 97.3 | 75.3 | 1332 | 27.38 | 4860.4 | 2394 | 2416.2 | 3549.6 | 1186.9 | 0.65703 | 4.697
2024-12-09 | 14:16 | Data | 0 | 34.567 | 33.412 | 132.757 | 7.64 | 125.571 | 2048.99 | 26.11 | 54.846 | 6.41 | 1.157 | 3.543 | 7482.02 | 1.33 | 97.3 | 75.4 | 1332 | 27.42 | 4863.3 | 2424.9 | 2451.6 | 3594.9 | 1186.9 | 0.6607 | 4.7
2024-12-09 | 14:16 | Data | 0 | 34.58 | 33.466 | 132.893 | 7.64 | 125.571 | 2048.99 | 26.11 | 54.485 | 6.41 | 1.156 | 3.549 | 7491.07 | 0.932 | 97.3 | 75.4 | 1332 | 27.29 | 4869.2 | 2398.4 | 2433.6 | 3566.3 | 1186.9 | 0.6574 | 4.705
2024-12-09 | 14:16 | Data | 0 | 34.796 | 33.642 | 132.803 | 7.64 | 125.571 | 2050.8 | 26.09 | 54.756 | 6.41 | 1.162 | 3.529 | 7491.07 | 1.161 | 97.3 | 75.2 | 1333 | 27.42 | 4869.2 | 2420.5 | 2436.2 | 3580.9 | 1186.9 | 0.66149 | 4.691
2024-12-09 | 14:16 | Data | 0 | 34.81 | 33.439 | 132.893 | 7.64 | 125.616 | 2051.7 | 26.11 | 54.846 | 6.4 | 1.159 | 3.524 | 7509.16 | 1.154 | 97.3 | 75.3 | 1333 | 27.38 | 4881 | 2419.8 | 2436.9 | 3581.6 | 1186.9 | 0.66015 | 4.681
2024-12-09 | 14:16 | Data | 0 | 34.681 | 33.615 | 132.803 | 7.64 | 125.571 | 2049.89 | 26.1 | 54.846 | 6.39 | 1.15 | 3.523 | 7509.16 | 1.168 | 97.3 | 75.4 | 1332 | 27.38 | 4881 | 2427 | 2437.6 | 3581.8 | 1186.9 | 0.66291 | 4.673
2024-12-09 | 14:16 | Data | 0 | 34.803 | 33.642 | 132.848 | 7.64 | 125.706 | 2048.08 | 26.11 | 54.846 | 6.4 | 1.156 | 3.534 | 7491.07 | 1.154 | 97.3 | 75.4 | 1332 | 27.38 | 4869.2 | 2421 | 2428.4 | 3576.5 | 1186.9 | 0.66283 | 4.69
2024-12-09 | 14:16 | Data | 0 | 34.816 | 33.642 | 132.848 | 7.64 | 125.706 | 2046.28 | 26.1 | 54.756 | 6.4 | 1.157 | 3.51 | 7495.59 | 1.161 | 97.3 | 75.2 | 1330 | 27.38 | 4872.1 | 2431.6 | 2449.8 | 3599.8 | 1186.9 | 0.65954 | 4.667
2024-12-09 | 14:16 | Data | 0 | 34.803 | 33.642 | 132.803 | 7.64 | 125.661 | 2048.08 | 26.12 | 54.756 | 6.4 | 1.161 | 3.532 | 7875.46 | 1.154 | 97.3 | 75.3 | 1331 | 27.38 | 5119 | 2432.7 | 2441.8 | 3591.9 | 1186.9 | 0.66108 | 4.693
2024-12-09 | 14:16 | Data | 0 | 34.796 | 33.621 | 132.893 | 7.63 | 125.661 | 2048.99 | 26.11 | 54.846 | 6.4 | 1.159 | 3.537 | 7531.77 | 1.33 | 97.3 | 75.3 | 1332 | 27.42 | 4895.6 | 2417.2 | 2417.7 | 3564 | 1186.9 | 0.66243 | 4.696
2024-12-09 | 14:16 | Data | 0 | 34.573 | 33.439 | 132.803 | 7.64 | 125.616 | 2042.66 | 26.1 | 54.846 | 6.4 | 1.166 | 3.51 | 7509.16 | 0.932 | 97.3 | 75.1 | 1328 | 27.42 | 4881 | 2428.5 | 2415.4 | 3570.2 | 1186.9 | 0.66501 | 4.677
2024-12-09 | 14:16 | Data | 0 | 34.81 | 33.642 | 132.848 | 7.64 | 125.616 | 2044.47 | 26.11 | 54.756 | 6.4 | 1.153 | 3.518 | 7504.64 | 1.154 | 97.3 | 75.3 | 1329 | 27.42 | 4878 | 2420.2 | 2428.9 | 3575.9 | 1186.9 | 0.65806 | 4.671
2024-12-09 | 14:16 | Data | 0 | 34.756 | 33.621 | 132.848 | 7.64 | 125.661 | 2046.28 | 26.1 | 54.846 | 6.4 | 1.153 | 3.561 | 7491.07 | 1.175 | 97.3 | 75.5 | 1329 | 27.42 | 4869.2 | 2425.6 | 2433.8 | 3578 | 1186.9 | 0.66249 | 4.714
2024-12-09 | 14:16 | Data | 0 | 34.823 | 33.642 | 132.938 | 7.64 | 125.661 | 2046.28 | 26.11 | 54.756 | 6.41 | 1.159 | 3.516 | 7509.16 | 0.959 | 97.3 | 75.2 | 1329 | 27.42 | 4881 | 2434.4 | 2430.7 | 3584 | 1186.9 | 0.66283 | 4.675
2024-12-09 | 14:16 | Data | 0 | 34.85 | 33.642 | 132.893 | 7.64 | 125.661 | 2046.28 | 26.11 | 54.665 | 6.4 | 1.157 | 3.509 | 7500.11 | 1.053 | 97.3 | 75.2 | 1330 | 27.38 | 4875.1 | 2432.2 | 2438.6 | 3590.5 | 1186.9 | 0.66102 | 4.665
2024-12-09 | 14:17 | Data | 0 | 34.884 | 33.858 | 132.893 | 7.63 | 125.661 | 2043.56 | 26.1 | 54.846 | 6.4 | 1.165 | 3.523 | 7513.68 | 1.269 | 97.3 | 75.2 | 1330 | 27.42 | 4883.9 | 2429.6 | 2452.2 | 3593 | 1187 | 0.65981 | 4.688
2024-12-09 | 14:17 | Data | 0 | 34.742 | 33.621 | 132.893 | 7.64 | 125.661 | 2042.66 | 26.11 | 54.846 | 6.41 | 1.164 | 3.529 | 7504.64 | 1.283 | 97.3 | 75.2 | 1328 | 27.42 | 4878 | 2423.7 | 2430.8 | 3571.9 | 1187 | 0.66189 | 4.692
2024-12-09 | 14:17 | Data | 0 | 34.796 | 33.601 | 132.848 | 7.64 | 125.616 | 2048.08 | 26.1 | 54.756 | 6.4 | 1.157 | 3.512 | 7518.2 | 1.242 | 97.3 | 75.2 | 1332 | 27.42 | 4886.8 | 2402.6 | 2439 | 3582.4 | 1187 | 0.65948 | 4.669
2024-12-09 | 14:17 | Data | 0 | 34.783 | 33.412 | 132.803 | 7.64 | 125.616 | 2048.08 | 26.11 | 54.756 | 6.41 | 1.153 | 3.512 | 7527.25 | 1.256 | 97.3 | 75.3 | 1332 | 27.38 | 4892.7 | 2404.9 | 2436 | 3577.1 | 1187 | 0.65672 | 4.666
2024-12-09 | 14:17 | Data | 0 | 34.857 | 33.736 | 132.893 | 7.64 | 125.616 | 2046.28 | 26.11 | 54.756 | 6.4 | 1.155 | 3.52 | 7518.2 | 1.323 | 97.3 | 75.3 | 1330 | 27.38 | 4886.8 | 2433.1 | 2445.2 | 3592.6 | 1187 | 0.66279 | 4.675
2024-12-09 | 14:17 | Data | 0 | 34.58 | 33.412 | 132.803 | 7.64 | 125.571 | 2046.28 | 26.11 | 54.846 | 6.4 | 1.165 | 3.527 | 7504.64 | 1.161 | 97.3 | 75.2 | 1331 | 27.42 | 4878 | 2425.4 | 2439.9 | 3584.2 | 1187 | 0.66325 | 4.691
2024-12-09 | 14:17 | Data | 0 | 34.992 | 33.642 | 132.893 | 7.64 | 125.661 | 2046.28 | 26.11 | 54.846 | 6.4 | 1.161 | 3.53 | 7491.07 | 1.208 | 97.3 | 75.3 | 1330 | 27.42 | 4869.2 | 2415.5 | 2440 | 3581.3 | 1187 | 0.65895 | 4.691
2024-12-09 | 14:17 | Data | 0 | 35.019 | 33.655 | 132.848 | 7.63 | 125.661 | 2046.28 | 26.1 | 54.756 | 6.4 | 1.163 | 3.546 | 7491.07 | 1.154 | 97.3 | 75.3 | 1330 | 27.42 | 4869.2 | 2423.5 | 2427 | 3575.6 | 1187 | 0.66179 | 4.71
2024-12-09 | 14:17 | Data | 0 | 34.911 | 33.655 | 132.848 | 7.64 | 125.661 | 2047.18 | 26.11 | 54.756 | 6.4 | 1.16 | 3.562 | 7491.07 | 1.141 | 97.3 | 75.4 | 1331 | 27.38 | 4869.2 | 2400.9 | 2443.8 | 3571.7 | 1187 | 0.65799 | 4.722
2024-12-09 | 14:17 | Data | 0 | 34.823 | 33.419 | 132.848 | 7.64 | 125.706 | 2048.99 | 26.12 | 54.665 | 6.4 | 1.164 | 3.551 | 7495.59 | 1.181 | 97.3 | 75.3 | 1332 | 27.33 | 4872.1 | 2435.4 | 2441.1 | 3594.3 | 1187 | 0.66288 | 4.715
2024-12-09 | 14:17 | Data | 0 | 34.742 | 33.588 | 132.757 | 7.64 | 125.616 | 2049.89 | 26.11 | 54.846 | 6.4 | 1.15 | 3.544 | 7504.64 | 1.262 | 97.3 | 75.5 | 1332 | 27.42 | 4878 | 2412.1 | 2439.1 | 3579.3 | 1187 | 0.65914 | 4.695
2024-12-09 | 14:17 | Data | 0 | 34.796 | 33.642 | 132.984 | 7.64 | 125.661 | 2051.7 | 26.1 | 54.846 | 6.41 | 1.149 | 3.556 | 7504.64 | 1.154 | 97.3 | 75.6 | 1334 | 27.38 | 4878 | 2418.5 | 2448.1 | 3591.1 | 1187 | 0.65715 | 4.704
2024-12-09 | 14:17 | Data | 0 | 34.641 | 33.615 | 132.893 | 7.64 | 125.616 | 2051.7 | 26.1 | 54.936 | 6.4 | 1.156 | 3.546 | 7504.64 | 0.986 | 97.3 | 75.4 | 1334 | 27.51 | 4878 | 2443.7 | 2436.5 | 3593.1 | 1187 | 0.66593 | 4.702
2024-12-09 | 14:17 | Data | 0 | 34.796 | 33.561 | 132.848 | 7.64 | 125.616 | 2052.6 | 26.12 | 54.846 | 6.41 | 1.155 | 3.546 | 7504.64 | 1.262 | 97.3 | 75.4 | 1334 | 27.42 | 4878 | 2412.3 | 2432.3 | 3575 | 1187 | 0.65757 | 4.7
2024-12-09 | 14:17 | Data | 0 | 34.58 | 33.837 | 132.848 | 7.64 | 125.661 | 2050.8 | 26.11 | 54.846 | 6.41 | 1.16 | 3.53 | 7495.59 | 1.114 | 97.3 | 75.3 | 1334 | 27.42 | 4872.1 | 2445.4 | 2447.7 | 3601.6 | 1187 | 0.66123 | 4.691
2024-12-09 | 14:17 | Data | 0 | 34.823 | 33.473 | 132.893 | 7.64 | 125.706 | 2051.7 | 26.11 | 54.846 | 6.41 | 1.16 | 3.525 | 7500.11 | 0.959 | 97.3 | 75.2 | 1332 | 27.42 | 4875.1 | 2432.2 | 2446.7 | 3595.1 | 1187 | 0.66075 | 4.686
2024-12-09 | 14:17 | Data | 0 | 34.749 | 33.628 | 132.893 | 7.64 | 125.661 | 2051.7 | 26.1 | 54.756 | 6.4 | 1.167 | 3.54 | 7509.16 | 1.168 | 97.3 | 75.2 | 1334 | 27.38 | 4881 | 2428.1 | 2446.1 | 3592.9 | 1187 | 0.65718 | 4.707
2024-12-09 | 14:17 | Data | 0 | 34.85 | 33.642 | 132.938 | 7.63 | 125.797 | 2058.93 | 26.09 | 54.846 | 6.4 | 1.165 | 3.513 | 7500.11 | 1.175 | 97.3 | 75.1 | 1338 | 27.42 | 4875.1 | 2427 | 2442.2 | 3588.5 | 1187 | 0.66079 | 4.678
2024-12-09 | 14:18 | Data | 0 | 34.783 | 33.642 | 132.893 | 7.63 | 125.616 | 2054.41 | 26.11 | 55.388 | 6.4 | 1.162 | 3.518 | 7509.16 | 1.208 | 97.3 | 75.2 | 1335 | 27.65 | 4881 | 2412.8 | 2453.9 | 3587.6 | 1187 | 0.65734 | 4.681
2024-12-09 | 14:18 | Data | 0 | 34.627 | 33.527 | 132.938 | 7.64 | 125.706 | 2054.41 | 26.11 | 54.846 | 6.4 | 1.146 | 3.523 | 7518.2 | 1.269 | 97.3 | 75.5 | 1335 | 27.38 | 4886.8 | 2411 | 2456.7 | 3584.1 | 1187 | 0.65843 | 4.669
2024-12-09 | 14:18 | Data | 0 | 34.803 | 33.642 | 132.893 | 7.64 | 125.661 | 2053.51 | 26.11 | 54.756 | 6.4 | 1.148 | 3.523 | 7509.16 | 1.154 | 97.3 | 75.4 | 1335 | 27.38 | 4881 | 2436.9 | 2443.5 | 3596.4 | 1187 | 0.66183 | 4.672
2024-12-09 | 14:18 | Data | 0 | 34.695 | 33.635 | 132.757 | 7.64 | 125.571 | 2053.51 | 26.11 | 54.756 | 6.4 | 1.155 | 3.533 | 7509.16 | 1.168 | 97.3 | 75.4 | 1335 | 27.38 | 4881 | 2440.2 | 2461.2 | 3606.4 | 1187 | 0.66148 | 4.688
2024-12-09 | 14:18 | Data | 0 | 34.796 | 33.642 | 132.848 | 7.64 | 125.706 | 2052.6 | 26.1 | 54.846 | 6.4 | 1.159 | 3.543 | 7504.64 | 1.256 | 97.3 | 75.3 | 1335 | 27.38 | 4878 | 2415.1 | 2436.8 | 3580.3 | 1187 | 0.6596 | 4.702
2024-12-09 | 14:18 | Data | 0 | 34.796 | 33.642 | 132.893 | 7.64 | 125.661 | 2050.8 | 26.1 | 54.756 | 6.4 | 1.161 | 3.524 | 7491.07 | 1.161 | 97.3 | 75.2 | 1334 | 27.42 | 4869.2 | 2398.5 | 2448.1 | 3578.1 | 1187 | 0.65374 | 4.686
2024-12-09 | 14:18 | Data | 0 | 34.85 | 33.642 | 132.803 | 7.64 | 125.616 | 2051.7 | 26.1 | 54.756 | 6.41 | 1.159 | 3.502 | 7495.59 | 1.161 | 97.3 | 75.1 | 1333 | 27.42 | 4872.1 | 2413.8 | 2433.4 | 3574.1 | 1187 | 0.65824 | 4.661
2024-12-09 | 14:18 | Data | 0 | 34.789 | 33.642 | 132.848 | 7.64 | 125.661 | 2050.8 | 26.1 | 54.846 | 6.41 | 1.154 | 3.519 | 7504.64 | 1.154 | 97.3 | 75.3 | 1334 | 27.42 | 4878 | 2435.1 | 2441 | 3590 | 1187 | 0.66136 | 4.674
2024-12-09 | 14:18 | Data | 0 | 34.621 | 33.588 | 132.803 | 7.64 | 125.616 | 2051.7 | 26.11 | 54.756 | 6.41 | 1.155 | 3.52 | 7522.72 | 1.222 | 97.3 | 75.3 | 1334 | 27.38 | 4889.8 | 2424.9 | 2446.1 | 3587.3 | 1187 | 0.66091 | 4.675
2024-12-09 | 14:18 | Data | 0 | 34.573 | 33.642 | 132.803 | 7.64 | 125.661 | 2050.8 | 26.11 | 54.846 | 6.4 | 1.151 | 3.527 | 7518.2 | 1.134 | 97.3 | 75.4 | 1332 | 27.42 | 4886.8 | 2417.8 | 2442.2 | 3584.8 | 1187 | 0.66132 | 4.678
2024-12-09 | 14:18 | Data | 0 | 34.796 | 33.756 | 132.938 | 7.64 | 125.797 | 2048.99 | 26.11 | 54.756 | 6.4 | 1.164 | 3.518 | 7522.72 | 1.04 | 97.3 | 75.1 | 1331 | 27.38 | 4889.8 | 2411.6 | 2479.9 | 3607.9 | 1187 | 0.65185 | 4.682
2024-12-09 | 14:18 | Data | 0 | 34.796 | 33.642 | 132.938 | 7.63 | 125.706 | 2048.99 | 26.1 | 54.846 | 6.4 | 1.163 | 3.544 | 7513.68 | 1.154 | 97.3 | 75.3 | 1332 | 27.42 | 4883.9 | 2414.6 | 2442.1 | 3580.7 | 1187 | 0.65943 | 4.705
2024-12-09 | 14:18 | Data | 0 | 34.594 | 33.615 | 132.848 | 7.64 | 125.616 | 2048.99 | 26.1 | 54.846 | 6.4 | 1.152 | 3.546 | 7495.59 | 1.053 | 97.3 | 75.5 | 1332 | 27.38 | 4872.1 | 2404.8 | 2443.6 | 3575 | 1187 | 0.65739 | 4.699
2024-12-09 | 14:18 | Data | 0 | 34.972 | 33.932 | 133.074 | 7.63 | 125.797 | 2048.99 | 26.1 | 54.846 | 6.41 | 1.147 | 3.551 | 7491.07 | 1.262 | 97.3 | 75.6 | 1332 | 27.42 | 4869.2 | 2421.6 | 2446 | 3591.5 | 1187 | 0.65971 | 4.697
2024-12-09 | 14:18 | Data | 0 | 34.796 | 33.682 | 132.938 | 7.64 | 125.706 | 2048.99 | 26.11 | 54.846 | 6.4 | 1.159 | 3.529 | 7509.16 | 1.289 | 97.3 | 75.3 | 1331 | 27.38 | 4881 | 2443.4 | 2444.6 | 3592.4 | 1187 | 0.66484 | 4.686
2024-12-09 | 14:18 | Data | 0 | 35.019 | 33.648 | 132.984 | 7.64 | 125.797 | 2046.28 | 26.11 | 54.575 | 6.41 | 1.161 | 3.526 | 7509.16 | 1.256 | 97.3 | 75.2 | 1329 | 27.33 | 4881 | 2415.7 | 2431.1 | 3575.9 | 1187 | 0.66192 | 4.689
2024-12-09 | 14:18 | Data | 0 | 34.796 | 33.736 | 132.938 | 7.64 | 125.661 | 2044.47 | 26.11 | 54.756 | 6.4 | 1.161 | 3.537 | 7518.2 | 1.175 | 97.3 | 75.3 | 1330 | 27.38 | 4886.8 | 1329.4 | 1777.5 | 2238.5 | 1187 | 0.59402 | 4.699
2024-12-09 | 14:19 | Data | 0 | 35.019 | 33.871 | 133.074 | 7.64 | 125.797 | 2046.28 | 26.11 | 54.936 | 6.41 | 1.168 | 3.541 | 7522.72 | 1.154 | 97.3 | 75.2 | 1330 | 27.47 | 4889.8 | 1332.6 | 1795 | 2254.5 | 1187 | 0.59001 | 4.708
2024-12-09 | 14:19 | Data | 0 | 34.911 | 33.864 | 133.074 | 7.64 | 125.706 | 2046.28 | 26.1 | 54.846 | 6.4 | 1.161 | 3.526 | 7504.64 | 1.195 | 97.3 | 75.2 | 1330 | 27.42 | 4878 | 1327.4 | 1783.7 | 2241.9 | 1187 | 0.59082 | 4.686
2024-12-09 | 14:19 | Data | 0 | 34.891 | 33.642 | 132.938 | 7.64 | 125.661 | 2048.08 | 26.1 | 54.846 | 6.4 | 1.159 | 3.527 | 7513.68 | 1.181 | 97.3 | 75.3 | 1331 | 27.42 | 4883.9 | 1337.2 | 1789.7 | 2253.1 | 1187 | 0.58708 | 4.685
2024-12-09 | 14:19 | Data | 0 | 34.708 | 33.642 | 132.893 | 7.64 | 125.661 | 2048.99 | 26.11 | 54.756 | 6.41 | 1.157 | 3.542 | 7522.72 | 1.141 | 97.3 | 75.4 | 1332 | 27.38 | 4889.8 | 1338.6 | 1791.9 | 2255.3 | 1187 | 0.59263 | 4.699
2024-12-09 | 14:19 | Data | 0 | 34.999 | 33.453 | 132.938 | 7.64 | 125.797 | 2048.08 | 26.12 | 54.756 | 6.4 | 1.159 | 3.527 | 7509.16 | 1.33 | 97.3 | 75.3 | 1331 | 27.42 | 4881 | 1327.3 | 1770 | 2232.4 | 1187 | 0.59297 | 4.685
2024-12-09 | 14:19 | Data | 0 | 34.627 | 33.527 | 132.848 | 7.64 | 125.661 | 2047.18 | 26.11 | 54.756 | 6.41 | 1.153 | 3.51 | 7509.16 | 1.161 | 97.3 | 75.3 | 1331 | 27.42 | 4881 | 1351.2 | 1799.8 | 2268 | 1187 | 0.59554 | 4.663
2024-12-09 | 14:19 | Data | 0 | 34.972 | 33.75 | 132.984 | 7.64 | 125.706 | 2044.47 | 26.12 | 54.846 | 6.4 | 1.157 | 3.556 | 7486.55 | 1.161 | 97.3 | 75.5 | 1329 | 27.38 | 4866.3 | 1320.9 | 1784.8 | 2239.1 | 1187 | 0.58812 | 4.712
2024-12-09 | 14:19 | Data | 0 | 35.039 | 33.446 | 132.938 | 7.64 | 125.706 | 2046.28 | 26.11 | 55.026 | 6.4 | 1.154 | 3.53 | 7495.59 | 1.154 | 97.3 | 75.4 | 1329 | 27.56 | 4872.1 | 1344.4 | 1773.9 | 2242.6 | 1187 | 0.59891 | 4.684
2024-12-09 | 14:19 | Data | 0 | 35.046 | 33.669 | 132.893 | 7.64 | 125.661 | 2047.18 | 26.11 | 55.026 | 6.4 | 1.168 | 3.506 | 7486.55 | 1.289 | 97.3 | 75 | 1331 | 27.47 | 4866.3 | 1329 | 1786 | 2245.8 | 1187 | 0.59022 | 4.672
2024-12-09 | 14:19 | Data | 0 | 34.796 | 33.844 | 132.938 | 7.63 | 125.661 | 2044.47 | 26.11 | 55.117 | 6.41 | 1.179 | 3.518 | 7491.07 | 1.154 | 97.3 | 74.9 | 1329 | 27.56 | 4869.2 | 1334.9 | 1803.7 | 2262.9 | 1187 | 0.58842 | 4.697
2024-12-09 | 14:19 | Data | 0 | 34.796 | 33.756 | 132.938 | 7.64 | 125.706 | 2048.08 | 26.11 | 55.026 | 6.4 | 1.159 | 3.509 | 7500.11 | 1.269 | 97.3 | 75.2 | 1331 | 27.6 | 4875.1 | 1330.4 | 1789.7 | 2248.4 | 1187 | 0.59137 | 4.669
2024-12-09 | 14:19 | Data | 0 | 34.621 | 33.756 | 132.803 | 7.64 | 125.706 | 2051.7 | 26.11 | 55.026 | 6.41 | 1.159 | 3.513 | 7509.16 | 1.114 | 97.3 | 75.2 | 1334 | 27.51 | 4881 | 1321.3 | 1785.4 | 2241.4 | 1187 | 0.58839 | 4.671
2024-12-09 | 14:19 | Data | 0 | 34.789 | 33.554 | 132.803 | 7.64 | 125.661 | 2051.7 | 26.11 | 55.026 | 6.4 | 1.16 | 3.535 | 7504.64 | 1.269 | 97.3 | 75.3 | 1334 | 27.51 | 4878 | 1325.8 | 1767.3 | 2228.4 | 1187 | 0.59384 | 4.695
2024-12-09 | 14:19 | Data | 0 | 34.81 | 33.527 | 133.074 | 7.64 | 125.706 | 2053.51 | 26.11 | 55.117 | 6.4 | 1.16 | 3.529 | 7509.16 | 1.154 | 97.3 | 75.3 | 1334 | 27.56 | 4881 | 1326.2 | 1779.7 | 2231 | 1187 | 0.59036 | 4.689
2024-12-09 | 14:19 | Data | 0 | 34.789 | 33.642 | 132.893 | 7.64 | 125.661 | 2052.6 | 26.1 | 54.846 | 6.4 | 1.155 | 3.525 | 7504.64 | 1.154 | 97.3 | 75.3 | 1334 | 27.42 | 4878 | 1310.1 | 1781.1 | 2231.3 | 1187 | 0.59289 | 4.679
2024-12-09 | 14:19 | Data | 0 | 35.107 | 33.527 | 132.893 | 7.64 | 125.706 | 2050.8 | 26.1 | 55.026 | 6.4 | 1.16 | 3.532 | 7500.11 | 1.161 | 97.3 | 75.3 | 1333 | 27.6 | 4875.1 | 1342.7 | 1794.5 | 2257.9 | 1187 | 0.59345 | 4.692
2024-12-09 | 14:19 | Data | 0 | 34.992 | 33.642 | 132.848 | 7.64 | 125.706 | 2049.89 | 26.1 | 54.846 | 6.4 | 1.164 | 3.52 | 7522.72 | 1.256 | 97.3 | 75.1 | 1334 | 27.42 | 4889.8 | 1312.6 | 1784.5 | 2239.6 | 1187 | 0.58771 | 4.683
2024-12-09 | 14:19 | Data | 0 | 34.823 | 33.642 | 132.938 | 7.64 | 125.706 | 2044.47 | 26.11 | 54.756 | 6.4 | 1.165 | 3.542 | 7504.64 | 1.168 | 97.3 | 75.2 | 1330 | 27.42 | 4878 | 1328.4 | 1772.2 | 2235.5 | 1187.1 | 0.59251 | 4.709
2024-12-09 | 14:20 | Data | 0 | 34.823 | 33.588 | 132.984 | 7.63 | 125.706 | 2050.8 | 26.1 | 54.756 | 6.4 | 1.161 | 3.531 | 7518.2 | 1.154 | 97.3 | 75.3 | 1334 | 27.38 | 4886.8 | 1335.2 | 1779.5 | 2246.1 | 1187.1 | 0.59307 | 4.692
2024-12-09 | 14:20 | Data | 0 | 34.796 | 33.642 | 132.803 | 7.64 | 125.706 | 2047.18 | 26.11 | 55.026 | 6.41 | 1.161 | 3.535 | 7518.2 | 1.269 | 97.3 | 75.3 | 1331 | 27.51 | 4886.8 | 1346.7 | 1774.9 | 2247.3 | 1187.1 | 0.59864 | 4.694
2024-12-09 | 14:20 | Data | 0 | 34.776 | 33.621 | 132.984 | 7.64 | 125.661 | 2055.31 | 26.11 | 54.936 | 6.4 | 1.157 | 3.545 | 7504.64 | 1.188 | 97.3 | 75.4 | 1335 | 27.56 | 4878 | 1317 | 1764.7 | 2222.1 | 1187.1 | 0.59014 | 4.702
2024-12-09 | 14:20 | Data | 0 | 34.688 | 33.513 | 132.848 | 7.64 | 125.616 | 2053.51 | 26.1 | 55.117 | 6.41 | 1.155 | 3.534 | 7522.72 | 1.276 | 97.3 | 75.4 | 1335 | 27.56 | 4889.8 | 1337.2 | 1780.5 | 2245.2 | 1187.1 | 0.59403 | 4.689
2024-12-09 | 14:20 | Data | 0 | 34.796 | 33.642 | 132.893 | 7.64 | 125.616 | 2048.99 | 26.1 | 54.936 | 6.4 | 1.153 | 3.523 | 7509.16 | 1.33 | 97.3 | 75.3 | 1332 | 27.51 | 4881 | 1324.7 | 1779.2 | 2238.3 | 1187.1 | 0.59017 | 4.676
2024-12-09 | 14:20 | Data | 0 | 34.796 | 33.588 | 132.848 | 7.64 | 125.616 | 2053.51 | 26.1 | 55.026 | 6.4 | 1.154 | 3.551 | 7522.72 | 1.175 | 97.3 | 75.5 | 1335 | 27.56 | 4889.8 | 1333.3 | 1793.7 | 2253.9 | 1187.1 | 0.59472 | 4.705
2024-12-09 | 14:20 | Data | 0 | 34.769 | 33.642 | 132.803 | 7.64 | 125.616 | 2053.51 | 26.11 | 55.026 | 6.4 | 1.15 | 3.54 | 7513.68 | 1.148 | 97.3 | 75.5 | 1335 | 27.51 | 4883.9 | 1325.2 | 1784.9 | 2240.5 | 1187.1 | 0.58918 | 4.691
2024-12-09 | 14:20 | Data | 0 | 34.783 | 33.419 | 132.938 | 7.64 | 125.616 | 2053.51 | 26.09 | 55.026 | 6.4 | 1.155 | 3.542 | 7518.2 | 1.377 | 97.3 | 75.4 | 1335 | 27.56 | 4886.8 | 1337.3 | 1782.2 | 2246.2 | 1187.1 | 0.59411 | 4.698
2024-12-09 | 14:20 | Data | 0 | 34.796 | 33.628 | 132.803 | 7.64 | 125.661 | 2053.51 | 26.1 | 55.026 | 6.41 | 1.16 | 3.551 | 7531.77 | 1.175 | 97.3 | 75.4 | 1335 | 27.56 | 4895.6 | 1331 | 1790.4 | 2250.9 | 1187.1 | 0.58931 | 4.711
2024-12-09 | 14:20 | Data | 0 | 34.958 | 33.439 | 132.848 | 7.64 | 125.661 | 2054.41 | 26.11 | 55.026 | 6.4 | 1.165 | 3.53 | 7518.2 | 1.377 | 97.3 | 75.2 | 1335 | 27.56 | 4886.8 | 1333.4 | 1795.8 | 2253 | 1187.1 | 0.59073 | 4.695
2024-12-09 | 14:20 | Data | 0 | 34.769 | 33.642 | 132.803 | 7.64 | 125.616 | 2054.41 | 26.1 | 55.117 | 6.41 | 1.167 | 3.528 | 7518.2 | 1.148 | 97.3 | 75.2 | 1335 | 27.51 | 4886.8 | 1334.1 | 1805.6 | 2263 | 1187.1 | 0.58874 | 4.695
2024-12-09 | 14:20 | Data | 0 | 34.621 | 33.743 | 132.938 | 7.63 | 125.616 | 2054.41 | 26.1 | 55.117 | 6.4 | 1.159 | 3.506 | 7531.77 | 1.168 | 97.3 | 75.1 | 1335 | 27.56 | 4895.6 | 1320 | 1770.2 | 2228.4 | 1187.1 | 0.58702 | 4.665
2024-12-09 | 14:20 | Data | 0 | 34.742 | 33.527 | 132.848 | 7.63 | 125.661 | 2053.51 | 26.11 | 55.026 | 6.41 | 1.157 | 3.526 | 7531.77 | 1.256 | 97.3 | 75.3 | 1335 | 27.56 | 4895.6 | 1340.1 | 1778.1 | 2245.3 | 1187.1 | 0.59538 | 4.682
2024-12-09 | 14:20 | Data | 0 | 34.594 | 33.628 | 132.848 | 7.64 | 125.661 | 2050.8 | 26.11 | 55.117 | 6.4 | 1.163 | 3.524 | 7518.2 | 1.1 | 97.3 | 75.2 | 1333 | 27.56 | 4886.8 | 1334.8 | 1792.2 | 2253.5 | 1187.1 | 0.59071 | 4.688
2024-12-09 | 14:20 | Data | 0 | 34.573 | 33.743 | 132.893 | 7.63 | 125.661 | 2051.7 | 26.1 | 55.117 | 6.4 | 1.166 | 3.527 | 7513.68 | 0.999 | 97.3 | 75.2 | 1333 | 27.51 | 4883.9 | 1332.4 | 1780.3 | 2243.8 | 1187.1 | 0.59188 | 4.693
2024-12-09 | 14:20 | Data | 0 | 34.573 | 33.642 | 132.938 | 7.64 | 125.706 | 2051.7 | 26.1 | 55.026 | 6.41 | 1.162 | 3.531 | 7509.16 | 1.249 | 97.3 | 75.2 | 1334 | 27.56 | 4881 | 1347.1 | 1777.4 | 2247.4 | 1187.1 | 0.59765 | 4.692
2024-12-09 | 14:20 | Data | 0 | 34.911 | 33.642 | 132.938 | 7.64 | 125.706 | 2052.6 | 26.11 | 55.026 | 6.41 | 1.164 | 3.532 | 7491.07 | 0.999 | 97.3 | 75.2 | 1333 | 27.51 | 4869.2 | 1316 | 1768.2 | 2224.7 | 1187.1 | 0.58992 | 4.695
2024-12-09 | 14:20 | Data | 0 | 34.783 | 33.642 | 132.848 | 7.64 | 125.616 | 2053.51 | 26.1 | 55.026 | 6.41 | 1.164 | 3.529 | 7495.59 | 1.154 | 97.3 | 75.2 | 1335 | 27.51 | 4872.1 | 1327.2 | 1787.9 | 2256.8 | 1187.1 | 0.58895 | 4.694
2024-12-09 | 14:21 | Data | 0 | 34.58 | 33.412 | 132.803 | 7.64 | 125.661 | 2054.41 | 26.11 | 55.117 | 6.4 | 1.157 | 3.518 | 7495.59 | 1.269 | 97.3 | 75.3 | 1335 | 27.56 | 4872.1 | 1343.1 | 1793.5 | 2257.1 | 1187.1 | 0.59564 | 4.674
2024-12-09 | 14:21 | Data | 0 | 34.796 | 33.642 | 132.848 | 7.64 | 125.616 | 2053.51 | 26.1 | 55.297 | 6.4 | 1.159 | 3.527 | 7504.64 | 1.154 | 97.3 | 75.3 | 1335 | 27.65 | 4878 | 1321.2 | 1788.1 | 2243 | 1187.1 | 0.58512 | 4.686
2024-12-09 | 14:21 | Data | 0 | 34.796 | 33.642 | 132.848 | 7.64 | 125.616 | 2059.83 | 26.1 | 55.117 | 6.4 | 1.154 | 3.526 | 7292.09 | 1.154 | 97.3 | 75.3 | 1338 | 27.51 | 4739.9 | 1315.2 | 1781.2 | 2233.9 | 1187.1 | 0.58632 | 4.679
2024-12-09 | 14:21 | Data | 0 | 34.796 | 33.635 | 132.757 | 7.64 | 125.661 | 2053.51 | 26.11 | 55.026 | 6.4 | 1.164 | 3.53 | 7283.05 | 1.168 | 97.3 | 75.2 | 1335 | 27.56 | 4734 | 1342.6 | 1804.8 | 2267.2 | 1187.1 | 0.59017 | 4.693
2024-12-09 | 14:21 | Data | 0 | 34.688 | 33.642 | 132.803 | 7.63 | 125.661 | 2054.41 | 26.1 | 55.117 | 6.4 | 1.166 | 3.529 | 7486.55 | 1.107 | 97.3 | 75.2 | 1335 | 27.51 | 4866.3 | 1324.6 | 1786.1 | 2243.3 | 1187.1 | 0.58913 | 4.695
2024-12-09 | 14:21 | Data | 0 | 34.965 | 33.81 | 132.893 | 7.64 | 125.616 | 2053.51 | 26.11 | 55.117 | 6.41 | 1.157 | 3.528 | 7482.02 | 1.256 | 97.3 | 75.3 | 1335 | 27.51 | 4863.3 | 1322.7 | 1799.3 | 2251.6 | 1187.1 | 0.58621 | 4.687
2024-12-09 | 14:21 | Data | 0 | 34.513 | 33.635 | 132.893 | 7.63 | 125.616 | 2054.41 | 26.11 | 55.026 | 6.4 | 1.16 | 3.552 | 7468.46 | 1.148 | 97.3 | 75.4 | 1335 | 27.51 | 4854.5 | 1337.4 | 1774.6 | 2243.4 | 1187.1 | 0.59548 | 4.713
2024-12-09 | 14:21 | Data | 0 | 34.796 | 33.615 | 132.893 | 7.63 | 125.616 | 2053.51 | 26.1 | 55.026 | 6.4 | 1.155 | 3.544 | 7536.29 | 1.087 | 97.3 | 75.4 | 1335 | 27.51 | 4898.6 | 1337.2 | 1774.7 | 2239.5 | 1187.1 | 0.59547 | 4.699
2024-12-09 | 14:21 | Data | 0 | 34.6 | 33.412 | 132.803 | 7.64 | 125.661 | 2053.51 | 26.11 | 55.117 | 6.4 | 1.151 | 3.537 | 7531.77 | 1.154 | 97.3 | 75.4 | 1335 | 27.51 | 4895.6 | 1339.6 | 1802.5 | 2264.6 | 1187.1 | 0.58972 | 4.688
2024-12-09 | 14:21 | Data | 0 | 34.81 | 33.426 | 132.803 | 7.64 | 125.706 | 2052.6 | 26.11 | 54.936 | 6.4 | 1.15 | 3.512 | 7518.2 | 1.188 | 97.3 | 75.3 | 1335 | 27.51 | 4886.8 | 1313.2 | 1800.4 | 2247.6 | 1187.1 | 0.5825 | 4.663
2024-12-09 | 14:21 | Data | 0 | 34.796 | 33.426 | 132.893 | 7.64 | 125.616 | 2055.31 | 26.11 | 55.026 | 6.4 | 1.153 | 3.511 | 7509.16 | 1.215 | 97.3 | 75.3 | 1335 | 27.56 | 4881 | 1330.4 | 1804.4 | 2261 | 1187.1 | 0.58761 | 4.665
2024-12-09 | 14:21 | Data | 0 | 34.742 | 33.439 | 132.803 | 7.63 | 125.661 | 2051.7 | 26.1 | 55.026 | 6.4 | 1.154 | 3.534 | 7518.2 | 1.35 | 97.3 | 75.4 | 1334 | 27.51 | 4886.8 | 1324.2 | 1775.7 | 2233.4 | 1187.1 | 0.59151 | 4.687
2024-12-09 | 14:21 | Data | 0 | 34.837 | 33.864 | 132.938 | 7.64 | 125.661 | 2050.8 | 26.11 | 55.026 | 6.4 | 1.167 | 3.532 | 7518.2 | 1.141 | 97.3 | 75.2 | 1332 | 27.51 | 4886.8 | 1336.6 | 1802.3 | 2262.4 | 1187.1 | 0.59013 | 4.699
2024-12-09 | 14:21 | Data | 0 | 34.567 | 33.527 | 132.893 | 7.64 | 125.616 | 2048.99 | 26.11 | 55.026 | 6.4 | 1.167 | 3.513 | 7504.64 | 1.154 | 97.3 | 75.1 | 1332 | 27.51 | 4878 | 1339 | 1786.6 | 2251.9 | 1187.1 | 0.59213 | 4.679
2024-12-09 | 14:21 | Data | 0 | 34.573 | 33.412 | 132.757 | 7.64 | 125.525 | 2048.99 | 26.1 | 55.207 | 6.4 | 1.166 | 3.509 | 7509.16 | 1.154 | 97.3 | 75.1 | 1332 | 27.56 | 4881 | 1330.3 | 1792.1 | 2253.5 | 1187.1 | 0.58904 | 4.674
2024-12-09 | 14:21 | Data | 0 | 34.553 | 33.628 | 132.803 | 7.64 | 125.571 | 2048.99 | 26.1 | 55.026 | 6.4 | 1.163 | 3.533 | 7518.2 | 1.094 | 97.3 | 75.2 | 1332 | 27.51 | 4886.8 | 1337.3 | 1775.2 | 2240.5 | 1187.1 | 0.59459 | 4.694
2024-12-09 | 14:21 | Data | 0 | 34.796 | 33.419 | 132.938 | 7.64 | 125.661 | 2050.8 | 26.11 | 55.207 | 6.4 | 1.161 | 3.52 | 7518.2 | 1.168 | 97.3 | 75.2 | 1333 | 27.56 | 4886.8 | 1324.8 | 1787.5 | 2251.2 | 1187.1 | 0.59078 | 4.682
2024-12-09 | 14:22 | Data | 0 | 34.783 | 33.426 | 132.757 | 7.64 | 125.661 | 2051.7 | 26.11 | 55.117 | 6.41 | 1.151 | 3.506 | 7522.72 | 1.269 | 97.3 | 75.3 | 1333 | 27.56 | 4889.8 | 1334.9 | 1785 | 2253.1 | 1187.1 | 0.59681 | 4.658
2024-12-09 | 14:22 | Data | 0 | 34.796 | 33.635 | 132.848 | 7.64 | 125.571 | 2051.7 | 26.1 | 55.117 | 6.4 | 1.16 | 3.535 | 7522.72 | 1.208 | 97.3 | 75.3 | 1333 | 27.51 | 4889.8 | 1327 | 1773.8 | 2235.4 | 1187.1 | 0.59221 | 4.695
2024-12-09 | 14:22 | Data | 0 | 34.789 | 33.466 | 132.848 | 7.64 | 125.616 | 2051.7 | 26.11 | 55.026 | 6.4 | 1.156 | 3.535 | 7509.16 | 1.154 | 97.3 | 75.4 | 1334 | 27.51 | 4881 | 1341 | 1775.4 | 2244 | 1187.1 | 0.5954 | 4.691
2024-12-09 | 14:22 | Data | 0 | 34.573 | 33.628 | 132.893 | 7.63 | 125.661 | 2051.7 | 26.11 | 55.207 | 6.4 | 1.156 | 3.566 | 7504.64 | 1.154 | 97.3 | 75.5 | 1334 | 27.51 | 4878 | 1307.6 | 1766.1 | 2216.4 | 1187.1 | 0.58953 | 4.722
2024-12-09 | 14:22 | Data | 0 | 34.735 | 33.52 | 132.803 | 7.64 | 125.571 | 2050.8 | 26.1 | 55.117 | 6.4 | 1.152 | 3.547 | 7504.64 | 1.141 | 97.3 | 75.5 | 1333 | 27.56 | 4878 | 1345.1 | 1769.7 | 2226 | 1187.1 | 0.59696 | 4.699
2024-12-09 | 14:22 | Data | 0 | 34.789 | 33.412 | 132.803 | 7.63 | 125.616 | 2050.8 | 26.11 | 54.575 | 6.4 | 1.153 | 3.528 | 7522.72 | 1.175 | 97.3 | 75.4 | 1333 | 27.33 | 4889.8 | 1331.6 | 1784.7 | 2246.6 | 1187.1 | 0.59114 | 4.682
2024-12-09 | 14:22 | Data | 0 | 34.681 | 33.642 | 132.757 | 7.64 | 125.571 | 2051.7 | 26.11 | 55.026 | 6.4 | 1.149 | 3.531 | 7531.77 | 1.141 | 97.3 | 75.5 | 1334 | 27.51 | 4895.6 | 1327.8 | 1782.4 | 2241.5 | 1187.1 | 0.59061 | 4.681
2024-12-09 | 14:22 | Data | 0 | 34.573 | 33.412 | 132.757 | 7.64 | 125.525 | 2051.7 | 26.1 | 55.026 | 6.41 | 1.15 | 3.535 | 7549.86 | 1.154 | 97.3 | 75.4 | 1333 | 27.51 | 4907.4 | 1351.2 | 1790.6 | 2252.8 | 1187.1 | 0.59778 | 4.685
2024-12-09 | 14:22 | Data | 0 | 34.681 | 33.419 | 132.893 | 7.63 | 125.616 | 2051.7 | 26.11 | 55.117 | 6.41 | 1.151 | 3.509 | 7549.86 | 1.148 | 97.3 | 75.3 | 1334 | 27.51 | 4907.4 | 1337.2 | 1770.2 | 2236.2 | 1187.1 | 0.59071 | 4.661
2024-12-09 | 14:22 | Data | 0 | 34.769 | 33.588 | 132.757 | 7.63 | 125.525 | 2051.7 | 26.1 | 54.936 | 6.4 | 1.159 | 3.538 | 7549.86 | 1.377 | 97.3 | 75.3 | 1334 | 27.47 | 4907.4 | 1331.1 | 1772.8 | 2237.4 | 1187.1 | 0.59336 | 4.696
2024-12-09 | 14:22 | Data | 0 | 34.567 | 33.412 | 132.803 | 7.64 | 125.571 | 2050.8 | 26.1 | 54.846 | 6.4 | 1.152 | 3.521 | 7527.25 | 1.154 | 97.3 | 75.3 | 1334 | 27.47 | 4892.7 | 1333.1 | 1775.9 | 2238.5 | 1187.1 | 0.5944 | 4.673
2024-12-09 | 14:22 | Data | 0 | 34.789 | 33.412 | 132.712 | 7.64 | 125.571 | 2054.41 | 26.11 | 54.756 | 6.4 | 1.153 | 3.532 | 7518.2 | 1.175 | 97.3 | 75.4 | 1335 | 27.38 | 4886.8 | 1320.7 | 1794.4 | 2247.4 | 1187.1 | 0.58628 | 4.686
2024-12-09 | 14:22 | Data | 0 | 34.567 | 33.527 | 132.803 | 7.64 | 125.525 | 2050.8 | 26.11 | 54.846 | 6.4 | 1.155 | 3.53 | 7536.29 | 1.154 | 97.3 | 75.4 | 1334 | 27.42 | 4898.6 | 1352 | 1792.7 | 2264.1 | 1187.1 | 0.59608 | 4.686
2024-12-09 | 14:22 | Data | 0 | 34.553 | 33.635 | 132.848 | 7.64 | 125.571 | 2050.8 | 26.11 | 54.756 | 6.4 | 1.156 | 3.537 | 7536.29 | 1.269 | 97.3 | 75.4 | 1334 | 27.38 | 4898.6 | 1339.8 | 1798.2 | 2260.8 | 1187.1 | 0.59098 | 4.693
2024-12-09 | 14:22 | Data | 0 | 34.789 | 33.642 | 132.803 | 7.64 | 125.616 | 2054.41 | 26.1 | 54.756 | 6.4 | 1.155 | 3.548 | 7549.86 | 1.161 | 97.3 | 75.4 | 1334 | 27.42 | 4907.4 | 1337.3 | 1795.3 | 2259.2 | 1187.1 | 0.59051 | 4.704
2024-12-09 | 14:22 | Data | 0 | 34.411 | 33.392 | 132.712 | 7.64 | 125.616 | 2054.41 | 26.1 | 54.846 | 6.41 | 1.163 | 3.52 | 7536.29 | 0.972 | 97.3 | 75.2 | 1335 | 27.42 | 4898.6 | 1341.2 | 1785.7 | 2253.4 | 1187.1 | 0.59411 | 4.682
2024-12-09 | 14:22 | Data | 0 | 34.742 | 33.426 | 132.757 | 7.64 | 125.616 | 2054.41 | 26.11 | 54.846 | 6.41 | 1.162 | 3.534 | 7536.29 | 1.344 | 97.3 | 75.3 | 1335 | 27.42 | 4898.6 | 1334.7 | 1808 | 2264.3 | 1187.1 | 0.58906 | 4.696
2024-12-09 | 14:22 | Data | 0 | 34.789 | 33.615 | 132.893 | 7.64 | 125.525 | 2055.31 | 26.11 | 54.846 | 6.4 | 1.163 | 3.537 | 7522.72 | 1.181 | 97.3 | 75.3 | 1336 | 27.42 | 4889.8 | 1328 | 1811.3 | 2263.9 | 1187.1 | 0.58527 | 4.701
2024-12-09 | 14:23 | Data | 0 | 34.567 | 33.527 | 132.803 | 7.64 | 125.571 | 2155.64 | 26.11 | 54.756 | 6.4 | 1.155 | 3.53 | 7545.34 | 1.148 | 97.5 | 75.3 | 1401 | 27.38 | 4904.5 | 2421 | 2471.6 | 3610.8 | 1187.1 | 0.65351 | 4.685
2024-12-09 | 14:23 | Data | 0 | 34.769 | 33.588 | 132.803 | 7.64 | 125.616 | 2052.6 | 26.11 | 54.846 | 6.41 | 1.159 | 3.52 | 7549.86 | 1.371 | 97.3 | 75.3 | 1334 | 27.38 | 4907.4 | 2435.4 | 2470.1 | 3613.4 | 1187.1 | 0.65756 | 4.677
2024-12-09 | 14:23 | Data | 0 | 34.951 | 33.696 | 132.848 | 7.63 | 125.661 | 2050.8 | 26.11 | 54.846 | 6.41 | 1.162 | 3.541 | 7549.86 | 1.269 | 97.3 | 75.3 | 1333 | 27.42 | 4907.4 | 2409.9 | 2473.2 | 3606 | 1187.1 | 0.65135 | 4.703
2024-12-09 | 14:23 | Data | 0 | 34.567 | 33.615 | 132.803 | 7.64 | 125.616 | 2051.7 | 26.1 | 54.846 | 6.41 | 1.16 | 3.556 | 7549.86 | 1.154 | 97.3 | 75.4 | 1333 | 27.42 | 4907.4 | 2417.4 | 2470 | 3602.5 | 1187.1 | 0.655 | 4.717
2024-12-09 | 14:23 | Data | 0 | 34.789 | 33.426 | 132.757 | 7.63 | 125.571 | 2050.8 | 26.1 | 54.846 | 6.4 | 1.159 | 3.542 | 7554.38 | 1.242 | 97.3 | 75.3 | 1333 | 27.42 | 4910.3 | 2418.6 | 2475.1 | 3611 | 1187.1 | 0.65302 | 4.701
2024-12-09 | 14:23 | Data | 0 | 34.56 | 33.419 | 132.848 | 7.64 | 125.525 | 2051.7 | 26.11 | 54.756 | 6.41 | 1.155 | 3.536 | 7558.9 | 1.127 | 97.3 | 75.4 | 1334 | 27.33 | 4913.3 | 2418.8 | 2441.3 | 3585.2 | 1187.1 | 0.65741 | 4.689
2024-12-09 | 14:23 | Data | 0 | 34.56 | 33.527 | 132.712 | 7.64 | 125.571 | 2050.8 | 26.1 | 54.756 | 6.4 | 1.159 | 3.536 | 7563.42 | 1.323 | 97.3 | 75.3 | 1332 | 27.42 | 4916.2 | 2409.3 | 2453.5 | 3589.1 | 1187.1 | 0.65494 | 4.691
2024-12-09 | 14:23 | Data | 0 | 34.843 | 33.466 | 132.893 | 7.63 | 125.661 | 2050.8 | 26.11 | 54.665 | 6.41 | 1.152 | 3.528 | 7545.34 | 1.046 | 97.3 | 75.4 | 1333 | 27.24 | 4904.5 | 2426.4 | 2465.3 | 3597 | 1187.1 | 0.65715 | 4.681
2024-12-09 | 14:23 | Data | 0 | 34.567 | 33.412 | 132.757 | 7.63 | 125.525 | 2051.7 | 26.1 | 54.846 | 6.4 | 1.138 | 3.532 | 7549.86 | 1.154 | 97.3 | 75.7 | 1334 | 27.42 | 4907.4 | 2407.8 | 2438.9 | 3575.6 | 1187.1 | 0.65926 | 4.67
2024-12-09 | 14:23 | Data | 0 | 34.675 | 33.628 | 132.803 | 7.64 | 125.571 | 2051.7 | 26.08 | 54.846 | 6.4 | 1.155 | 3.517 | 7527.25 | 1.141 | 97.3 | 75.3 | 1334 | 27.42 | 4892.7 | 2421 | 2445.7 | 3588.2 | 1187.1 | 0.65984 | 4.672
2024-12-09 | 14:23 | Data | 0 | 34.742 | 33.615 | 132.848 | 7.64 | 125.616 | 2051.7 | 26.08 | 54.846 | 6.4 | 1.161 | 3.536 | 7531.77 | 1.202 | 97.3 | 75.3 | 1334 | 27.33 | 4895.6 | 2405.7 | 2461.5 | 3594.8 | 1187.1 | 0.65389 | 4.696
2024-12-09 | 14:23 | Data | 0 | 34.708 | 33.412 | 132.803 | 7.64 | 125.661 | 2050.8 | 26.08 | 54.846 | 6.4 | 1.154 | 3.561 | 7527.25 | 0.986 | 97.3 | 75.5 | 1333 | 27.38 | 4892.7 | 2414 | 2464.4 | 3595.9 | 1187.1 | 0.65487 | 4.715
2024-12-09 | 14:23 | Data | 0 | 34.789 | 33.527 | 132.848 | 7.64 | 125.616 | 2052.6 | 26.08 | 54.756 | 6.4 | 1.165 | 3.534 | 7536.29 | 1.154 | 97.3 | 75.2 | 1335 | 27.47 | 4898.6 | 2397.1 | 2460.7 | 3587.1 | 1187.1 | 0.65234 | 4.7
2024-12-09 | 14:23 | Data | 0 | 34.796 | 33.642 | 132.893 | 7.64 | 125.661 | 2055.31 | 26.08 | 54.846 | 6.4 | 1.157 | 3.514 | 7536.29 | 1.154 | 97.3 | 75.2 | 1336 | 27.38 | 4898.6 | 2419.2 | 2467 | 3604.4 | 1187.1 | 0.65792 | 4.67
2024-12-09 | 14:23 | Data | 0 | 34.567 | 33.432 | 132.712 | 7.63 | 125.571 | 2059.83 | 26.06 | 54.846 | 6.41 | 1.159 | 3.542 | 7549.86 | 1.289 | 97.3 | 75.3 | 1338 | 27.38 | 4907.4 | 2425.1 | 2466 | 3611 | 1187.2 | 0.65409 | 4.7
2024-12-09 | 14:23 | Data | 0 | 34.58 | 33.412 | 132.757 | 7.64 | 125.571 | 2059.83 | 26.06 | 54.846 | 6.41 | 1.159 | 3.535 | 7567.95 | 1.161 | 97.3 | 75.3 | 1339 | 27.42 | 4919.2 | 2415.7 | 2455.2 | 3593.7 | 1187.2 | 0.65637 | 4.691
2024-12-09 | 14:23 | Data | 0 | 34.702 | 33.426 | 132.848 | 7.64 | 125.616 | 2053.51 | 26.07 | 54.756 | 6.41 | 1.149 | 3.542 | 7545.34 | 1.161 | 97.3 | 75.5 | 1335 | 27.42 | 4904.5 | 2421.7 | 2443 | 3588.4 | 1187.2 | 0.65994 | 4.691
2024-12-09 | 14:23 | Data | 0 | 34.708 | 33.412 | 132.803 | 7.64 | 125.616 | 2058.93 | 26.07 | 54.756 | 6.4 | 1.151 | 3.55 | 7549.86 | 1.215 | 97.3 | 75.5 | 1339 | 27.38 | 4907.4 | 2401.7 | 2451.6 | 3588.1 | 1187.2 | 0.65568 | 4.701
2024-12-09 | 14:24 | Data | 0 | 34.567 | 33.412 | 132.757 | 7.64 | 125.571 | 2058.93 | 26.08 | 54.846 | 6.41 | 1.159 | 3.546 | 7558.9 | 1.154 | 97.3 | 75.4 | 1338 | 27.42 | 4913.3 | 2448.4 | 2455.1 | 3617.1 | 1187.2 | 0.66256 | 4.705
2024-12-09 | 14:24 | Data | 0 | 34.816 | 33.473 | 132.848 | 7.63 | 125.616 | 2058.93 | 26.08 | 54.756 | 6.41 | 1.152 | 3.529 | 7567.95 | 1.168 | 97.3 | 75.4 | 1338 | 27.38 | 4919.2 | 2465.7 | 2483 | 3647.5 | 1187.2 | 0.6581 | 4.682
2024-12-09 | 14:24 | Data | 0 | 34.594 | 33.588 | 132.757 | 7.63 | 125.616 | 2059.83 | 26.07 | 54.846 | 6.41 | 1.156 | 3.521 | 7558.9 | 1.168 | 97.3 | 75.3 | 1339 | 27.38 | 4913.3 | 2449 | 2444.1 | 3608.2 | 1187.2 | 0.66231 | 4.676
2024-12-09 | 14:24 | Data | 0 | 34.789 | 33.594 | 132.848 | 7.64 | 125.661 | 2058.93 | 26.08 | 54.756 | 6.41 | 1.159 | 3.521 | 7567.95 | 1.357 | 97.3 | 75.3 | 1338 | 27.42 | 4919.2 | 2440.9 | 2443.6 | 3606.5 | 1187.2 | 0.65914 | 4.682
2024-12-09 | 14:24 | Data | 0 | 34.965 | 33.689 | 132.984 | 7.64 | 125.661 | 2058.93 | 26.08 | 54.756 | 6.41 | 1.156 | 3.53 | 7563.42 | 1.154 | 97.3 | 75.3 | 1338 | 27.33 | 4916.2 | 2451.4 | 2447.7 | 3610.5 | 1187.2 | 0.66225 | 4.686
2024-12-09 | 14:24 | Data | 0 | 34.567 | 33.527 | 132.803 | 7.63 | 125.571 | 2057.12 | 26.08 | 54.756 | 6.4 | 1.161 | 3.534 | 7554.38 | 1.154 | 97.3 | 75.3 | 1338 | 27.42 | 4910.3 | 2421.5 | 2462.9 | 3603.5 | 1187.2 | 0.65664 | 4.697
2024-12-09 | 14:24 | Data | 0 | 34.681 | 33.459 | 132.803 | 7.63 | 125.616 | 2058.93 | 26.08 | 54.575 | 6.4 | 1.153 | 3.53 | 7572.47 | 1.154 | 97.3 | 75.4 | 1338 | 27.33 | 4922.1 | 2466 | 2478.8 | 3643.9 | 1187.2 | 0.66088 | 4.684
2024-12-09 | 14:24 | Data | 0 | 34.567 | 33.412 | 132.893 | 7.64 | 125.661 | 2058.03 | 26.08 | 54.846 | 6.4 | 1.157 | 3.532 | 7531.77 | 1.154 | 97.3 | 75.3 | 1338 | 27.42 | 4895.6 | 2439.1 | 2442.8 | 3603 | 1187.2 | 0.6598 | 4.688
2024-12-09 | 14:24 | Data | 0 | 34.843 | 33.669 | 132.893 | 7.63 | 125.661 | 2059.83 | 26.08 | 55.026 | 6.4 | 1.149 | 3.526 | 7531.77 | 1.269 | 97.3 | 75.4 | 1338 | 27.56 | 4895.6 | 2450.5 | 2445.2 | 3607.6 | 1187.2 | 0.66481 | 4.674
2024-12-09 | 14:24 | Data | 0 | 34.567 | 33.628 | 132.938 | 7.64 | 125.571 | 2059.83 | 26.08 | 54.846 | 6.4 | 1.144 | 3.501 | 7531.77 | 1.127 | 97.3 | 75.4 | 1338 | 27.42 | 4895.6 | 2444.9 | 2452.9 | 3613.1 | 1187.2 | 0.66132 | 4.645
2024-12-09 | 14:24 | Data | 0 | 34.789 | 33.311 | 132.803 | 7.63 | 125.661 | 2058.03 | 26.08 | 54.936 | 6.41 | 1.162 | 3.517 | 7549.86 | 1.215 | 97.3 | 75.2 | 1339 | 27.47 | 4907.4 | 2457 | 2453.3 | 3619.3 | 1187.2 | 0.66273 | 4.679
2024-12-09 | 14:24 | Data | 0 | 34.681 | 33.534 | 132.803 | 7.64 | 125.616 | 2062.55 | 26.1 | 54.756 | 6.4 | 1.161 | 3.513 | 7527.25 | 1.161 | 97.3 | 75.2 | 1340 | 27.38 | 4892.7 | 2456.3 | 2443.9 | 3619.5 | 1187.2 | 0.66241 | 4.672
2024-12-09 | 14:24 | Data | 0 | 34.769 | 33.466 | 132.848 | 7.64 | 125.616 | 2060.74 | 26.09 | 54.936 | 6.4 | 1.156 | 3.535 | 7536.29 | 1.161 | 97.3 | 75.4 | 1340 | 27.42 | 4898.6 | 2455.2 | 2465.2 | 3623.6 | 1187.2 | 0.66184 | 4.691
2024-12-09 | 14:24 | Data | 0 | 34.769 | 33.615 | 132.803 | 7.64 | 125.616 | 2058.93 | 26.09 | 54.846 | 6.41 | 1.147 | 3.546 | 7554.38 | 1.208 | 97.3 | 75.6 | 1338 | 27.38 | 4910.3 | 2457 | 2468.6 | 3628.3 | 1187.2 | 0.66041 | 4.692
2024-12-09 | 14:24 | Data | 0 | 34.769 | 33.628 | 132.893 | 7.63 | 125.616 | 2061.64 | 26.09 | 54.936 | 6.4 | 1.149 | 3.523 | 7554.38 | 1.161 | 97.3 | 75.4 | 1339 | 27.38 | 4910.3 | 2452.9 | 2470.6 | 3633.2 | 1187.2 | 0.65913 | 4.672
2024-12-09 | 14:24 | Data | 0 | 34.796 | 33.419 | 132.757 | 7.64 | 125.571 | 2061.64 | 26.09 | 54.846 | 6.4 | 1.16 | 3.537 | 7563.42 | 1.195 | 97.3 | 75.3 | 1341 | 27.42 | 4916.2 | 2466.5 | 2453 | 3625.2 | 1187.2 | 0.66546 | 4.697
2024-12-09 | 14:24 | Data | 0 | 34.992 | 33.642 | 132.893 | 7.64 | 125.616 | 2062.55 | 26.09 | 54.846 | 6.41 | 1.153 | 3.53 | 7549.86 | 1.262 | 97.3 | 75.4 | 1341 | 27.42 | 4907.4 | 2451.1 | 2477 | 3634.4 | 1187.2 | 0.65846 | 4.683
2024-12-09 | 14:24 | Data | 0 | 34.567 | 33.412 | 132.757 | 7.63 | 125.661 | 2058.03 | 26.09 | 55.026 | 6.4 | 1.164 | 3.527 | 7545.34 | 1.269 | 97.3 | 75.2 | 1338 | 27.56 | 4904.5 | 2465.1 | 2471.2 | 3635.8 | 1187.2 | 0.66358 | 4.691
2024-12-09 | 14:25 | Data | 0 | 34.553 | 33.412 | 132.757 | 7.64 | 125.571 | 2058.93 | 26.09 | 54.756 | 6.4 | 1.169 | 3.529 | 7545.34 | 1.323 | 97.3 | 75.1 | 1338 | 27.38 | 4904.5 | 2459.3 | 2453.4 | 3622.2 | 1187.2 | 0.66475 | 4.7
2024-12-09 | 14:25 | Data | 0 | 34.567 | 33.412 | 132.803 | 7.64 | 125.571 | 2058.93 | 26.09 | 54.846 | 6.4 | 1.163 | 3.518 | 7549.86 | 1.154 | 97.3 | 75.2 | 1338 | 27.38 | 4907.4 | 2435 | 2462.4 | 3616.4 | 1187.2 | 0.66377 | 4.681
2024-12-09 | 14:25 | Data | 0 | 34.992 | 33.655 | 132.848 | 7.63 | 125.706 | 2065.26 | 26.09 | 54.756 | 6.4 | 1.156 | 3.537 | 7527.25 | 1.242 | 97.3 | 75.4 | 1342 | 27.38 | 4892.7 | 2447.4 | 2456.5 | 3620.3 | 1187.2 | 0.66083 | 4.693
2024-12-09 | 14:25 | Data | 0 | 34.783 | 33.635 | 132.848 | 7.64 | 125.616 | 2059.83 | 26.08 | 54.846 | 6.41 | 1.157 | 3.531 | 7531.77 | 1.168 | 97.3 | 75.3 | 1339 | 27.38 | 4895.6 | 2448.8 | 2447.3 | 3610.5 | 1187.2 | 0.66216 | 4.688
2024-12-09 | 14:25 | Data | 0 | 34.708 | 33.466 | 132.803 | 7.64 | 125.616 | 2061.64 | 26.09 | 54.846 | 6.4 | 1.154 | 3.523 | 7531.77 | 1.127 | 97.3 | 75.3 | 1340 | 27.42 | 4895.6 | 2458.6 | 2453.5 | 3623.1 | 1187.2 | 0.66276 | 4.677
2024-12-09 | 14:25 | Data | 0 | 34.357 | 33.392 | 132.757 | 7.64 | 125.616 | 2059.83 | 26.08 | 54.756 | 6.4 | 1.161 | 3.512 | 7536.29 | 1.141 | 97.3 | 75.2 | 1339 | 27.38 | 4898.6 | 2451.5 | 2462.2 | 3618.2 | 1187.2 | 0.66388 | 4.672
2024-12-09 | 14:25 | Data | 0 | 34.58 | 33.412 | 132.803 | 7.64 | 125.616 | 2058.93 | 26.08 | 54.846 | 6.4 | 1.16 | 3.531 | 7527.25 | 1.114 | 97.3 | 75.3 | 1338 | 27.38 | 4892.7 | 2469.9 | 2473.8 | 3641.5 | 1187.2 | 0.66435 | 4.692
2024-12-09 | 14:25 | Data | 0 | 34.783 | 33.642 | 132.893 | 7.64 | 125.616 | 2056.22 | 26.09 | 54.756 | 6.4 | 1.153 | 3.541 | 7531.77 | 1.154 | 97.3 | 75.4 | 1336 | 27.38 | 4895.6 | 2442 | 2454.3 | 3616.2 | 1187.2 | 0.65839 | 4.694
2024-12-09 | 14:25 | Data | 0 | 34.796 | 33.837 | 132.803 | 7.64 | 125.661 | 2057.12 | 26.09 | 54.756 | 6.4 | 1.159 | 3.533 | 7518.2 | 1.168 | 97.3 | 75.3 | 1337 | 27.38 | 4886.8 | 2459 | 2461.6 | 3626.2 | 1187.2 | 0.66202 | 4.692
2024-12-09 | 14:25 | Data | 0 | 34.742 | 33.419 | 132.803 | 7.64 | 125.616 | 2059.83 | 26.08 | 54.846 | 6.4 | 1.161 | 3.54 | 7518.2 | 1.364 | 97.3 | 75.3 | 1339 | 27.42 | 4886.8 | 2388.2 | 2439.7 | 3553.1 | 1187.2 | 0.65708 | 4.702
2024-12-09 | 14:25 | Data | 0 | 34.681 | 33.304 | 132.803 | 7.63 | 125.616 | 2058.93 | 26.1 | 54.846 | 6.4 | 1.16 | 3.514 | 7527.25 | 1.154 | 97.3 | 75.2 | 1338 | 27.47 | 4892.7 | 2393.3 | 2460.2 | 3574.7 | 1187.2 | 0.65563 | 4.674
2024-12-09 | 14:25 | Data | 0 | 34.594 | 33.412 | 132.757 | 7.63 | 125.571 | 2058.03 | 26.08 | 54.936 | 6.4 | 1.155 | 3.546 | 7531.77 | 1.161 | 97.3 | 75.4 | 1338 | 27.42 | 4895.6 | 2399.5 | 2475.2 | 3588.3 | 1187.2 | 0.65209 | 4.702
2024-12-09 | 14:25 | Data | 0 | 34.58 | 33.635 | 132.757 | 7.64 | 125.525 | 2058.93 | 26.09 | 55.026 | 6.41 | 1.156 | 3.527 | 7522.72 | 1.114 | 97.3 | 75.3 | 1338 | 27.51 | 4889.8 | 2367.3 | 2440.2 | 3545.5 | 1187.2 | 0.65202 | 4.683
2024-12-09 | 14:25 | Data | 0 | 34.526 | 33.588 | 132.938 | 7.64 | 125.571 | 2055.31 | 26.08 | 54.756 | 6.4 | 1.163 | 3.546 | 7509.16 | 1.141 | 97.3 | 75.3 | 1336 | 27.38 | 4881 | 2385.5 | 2466.9 | 3577.6 | 1187.2 | 0.6513 | 4.709
2024-12-09 | 14:25 | Data | 0 | 34.742 | 33.635 | 132.848 | 7.63 | 125.661 | 2050.8 | 26.09 | 54.846 | 6.4 | 1.166 | 3.513 | 7500.11 | 1.141 | 97.3 | 75.1 | 1333 | 27.47 | 4875.1 | 2379.4 | 2480.5 | 3578.1 | 1187.2 | 0.65032 | 4.68
2024-12-09 | 14:25 | Data | 0 | 34.796 | 33.419 | 132.848 | 7.63 | 125.571 | 2050.8 | 26.08 | 54.936 | 6.4 | 1.163 | 3.516 | 7518.2 | 1.175 | 97.3 | 75.1 | 1334 | 27.51 | 4886.8 | 2359.3 | 2468 | 3562.8 | 1187.2 | 0.64631 | 4.679
2024-12-09 | 14:25 | Data | 0 | 34.479 | 33.412 | 132.848 | 7.64 | 125.571 | 2048.08 | 26.09 | 55.117 | 6.4 | 1.159 | 3.519 | 7518.2 | 1.141 | 97.3 | 75.2 | 1331 | 27.56 | 4886.8 | 2366 | 2418.7 | 3527.7 | 1187.2 | 0.65701 | 4.679
2024-12-09 | 14:26 | Data | 0 | 34.567 | 33.588 | 132.848 | 7.63 | 125.616 | 2048.99 | 26.08 | 55.026 | 6.4 | 1.16 | 3.503 | 7522.72 | 1.154 | 97.3 | 75.1 | 1332 | 27.56 | 4889.8 | 2377.7 | 2455.5 | 3560.7 | 1187.2 | 0.648 | 4.665
2024-12-09 | 14:26 | Data | 0 | 34.594 | 33.527 | 132.848 | 7.64 | 125.616 | 2048.08 | 26.08 | 55.117 | 6.41 | 1.159 | 3.518 | 7518.2 | 1.154 | 97.3 | 75.2 | 1331 | 27.6 | 4886.8 | 2421 | 2479.3 | 3616.3 | 1187.2 | 0.65196 | 4.678
2024-12-09 | 14:26 | Data | 0 | 34.992 | 33.642 | 132.803 | 7.64 | 125.661 | 2046.28 | 26.08 | 55.117 | 6.4 | 1.167 | 3.535 | 7518.2 | 1.067 | 97.3 | 75.2 | 1330 | 27.51 | 4886.8 | 2427.4 | 2458.7 | 3600.2 | 1187.2 | 0.65795 | 4.702
2024-12-09 | 14:26 | Data | 0 | 34.553 | 33.412 | 132.757 | 7.64 | 125.571 | 2039.95 | 26.09 | 55.117 | 6.4 | 1.163 | 3.537 | 7518.2 | 1.161 | 97.3 | 75.3 | 1326 | 27.51 | 4886.8 | 2437.5 | 2476.2 | 3623.9 | 1187.2 | 0.65657 | 4.7
2024-12-09 | 14:26 | Data | 0 | 34.573 | 33.412 | 132.757 | 7.64 | 125.616 | 2044.47 | 26.08 | 55.026 | 6.41 | 1.16 | 3.521 | 7518.2 | 1.154 | 97.3 | 75.2 | 1328 | 27.51 | 4886.8 | 2435.6 | 2461.8 | 3611.4 | 1187.3 | 0.65845 | 4.683
2024-12-09 | 14:26 | Data | 0 | 34.459 | 33.412 | 132.803 | 7.64 | 125.661 | 2046.28 | 26.08 | 54.936 | 6.4 | 1.167 | 3.541 | 7531.77 | 0.952 | 97.3 | 75.2 | 1330 | 27.51 | 4895.6 | 2438.5 | 2451.7 | 3604.9 | 1187.3 | 0.65799 | 4.708
2024-12-09 | 14:26 | Data | 0 | 34.567 | 33.615 | 132.848 | 7.64 | 125.661 | 2041.76 | 26.09 | 55.026 | 6.4 | 1.169 | 3.555 | 7518.2 | 1.154 | 97.3 | 75.2 | 1327 | 27.51 | 4886.8 | 2424.8 | 2465.3 | 3604.1 | 1187.3 | 0.65863 | 4.724
2024-12-09 | 14:26 | Data | 0 | 34.567 | 33.237 | 132.622 | 7.63 | 125.525 | 2041.76 | 26.09 | 55.117 | 6.41 | 1.16 | 3.558 | 7527.25 | 1.154 | 97.3 | 75.4 | 1328 | 27.6 | 4892.7 | 2441.1 | 2456.1 | 3609.6 | 1187.3 | 0.6606 | 4.719
2024-12-09 | 14:26 | Data | 0 | 34.594 | 33.324 | 132.803 | 7.64 | 125.616 | 2039.95 | 26.08 | 55.117 | 6.4 | 1.149 | 3.537 | 7527.25 | 1.06 | 97.3 | 75.5 | 1326 | 27.51 | 4892.7 | 2438.5 | 2480.6 | 3625.7 | 1187.3 | 0.65685 | 4.687
2024-12-09 | 14:26 | Data | 0 | 34.567 | 33.412 | 132.803 | 7.64 | 125.571 | 2041.76 | 26.08 | 55.117 | 6.41 | 1.168 | 3.521 | 7531.77 | 1.154 | 97.3 | 75.1 | 1328 | 27.56 | 4895.6 | 2449.4 | 2468.7 | 3621.7 | 1187.3 | 0.66065 | 4.689
2024-12-09 | 14:26 | Data | 0 | 34.681 | 33.52 | 132.848 | 7.64 | 125.571 | 1942.34 | 26.09 | 55.117 | 6.4 | 1.168 | 3.54 | 7531.77 | 1.134 | 97.2 | 75.2 | 1263 | 27.56 | 4895.6 | 2433.4 | 2459.4 | 3607.3 | 1187.3 | 0.65972 | 4.709
2024-12-09 | 14:26 | Data | 0 | 34.594 | 33.392 | 132.757 | 7.64 | 125.571 | 2033.62 | 26.08 | 55.117 | 6.4 | 1.159 | 3.52 | 7549.86 | 1.249 | 97.3 | 75.2 | 1322 | 27.56 | 4907.4 | 2415.2 | 2481.4 | 3611.7 | 1187.3 | 0.65191 | 4.679
2024-12-09 | 14:26 | Data | 0 | 34.762 | 33.216 | 132.757 | 7.64 | 125.571 | 2033.62 | 26.08 | 55.117 | 6.4 | 1.164 | 3.518 | 7531.77 | 1.431 | 97.3 | 75.1 | 1322 | 27.51 | 4895.6 | 2417 | 2474.7 | 3612.2 | 1187.3 | 0.65251 | 4.682
2024-12-09 | 14:26 | Data | 0 | 34.344 | 33.453 | 132.712 | 7.63 | 125.616 | 2037.24 | 26.07 | 55.117 | 6.4 | 1.164 | 3.508 | 7531.77 | 1.019 | 97.3 | 75.1 | 1324 | 27.51 | 4895.6 | 2438.2 | 2464.3 | 3613.9 | 1187.3 | 0.65813 | 4.672
2024-12-09 | 14:26 | Data | 0 | 34.567 | 33.412 | 132.803 | 7.64 | 125.571 | 2049.89 | 26.08 | 55.026 | 6.4 | 1.157 | 3.535 | 7545.34 | 1.154 | 97.3 | 75.3 | 1334 | 27.51 | 4904.5 | 2421.4 | 2485.7 | 3620.1 | 1187.3 | 0.65153 | 4.692
2024-12-09 | 14:26 | Data | 0 | 34.546 | 33.412 | 132.893 | 7.64 | 125.616 | 2057.12 | 26.09 | 55.026 | 6.4 | 1.149 | 3.551 | 7554.38 | 1.262 | 97.3 | 75.5 | 1337 | 27.56 | 4910.3 | 2435.2 | 2450.9 | 3616.3 | 1187.3 | 0.65851 | 4.701
2024-12-09 | 14:26 | Data | 0 | 34.837 | 33.439 | 132.803 | 7.64 | 125.571 | 2056.22 | 26.08 | 55.026 | 6.41 | 1.155 | 3.53 | 7567.95 | 1.229 | 97.3 | 75.4 | 1337 | 27.56 | 4919.2 | 2447.6 | 2451.3 | 3608.5 | 1187.3 | 0.6609 | 4.684
2024-12-09 | 14:26 | Data | 0 | 34.627 | 33.419 | 132.757 | 7.64 | 125.571 | 2060.74 | 26.08 | 55.207 | 6.4 | 1.165 | 3.531 | 7563.42 | 1.175 | 97.3 | 75.2 | 1340 | 27.56 | 4916.2 | 2434.8 | 2449.3 | 3597.6 | 1187.3 | 0.66194 | 4.695
2024-12-09 | 14:27 | Data | 0 | 34.573 | 33.412 | 132.757 | 7.64 | 125.571 | 2051.7 | 26.08 | 55.117 | 6.41 | 1.152 | 3.547 | 7572.47 | 1.154 | 97.3 | 75.5 | 1334 | 27.51 | 4922.1 | 2437.7 | 2444.1 | 3598 | 1187.3 | 0.66288 | 4.7
2024-12-09 | 14:27 | Data | 0 | 34.337 | 33.385 | 132.622 | 7.64 | 125.48 | 2050.8 | 26.08 | 55.026 | 6.41 | 1.149 | 3.527 | 7563.42 | 1.215 | 97.3 | 75.4 | 1332 | 27.51 | 4916.2 | 2435.5 | 2456.4 | 3601.3 | 1187.3 | 0.65989 | 4.678
2024-12-09 | 14:27 | Data | 0 | 34.344 | 33.399 | 132.757 | 7.64 | 125.525 | 2051.7 | 26.08 | 55.026 | 6.4 | 1.162 | 3.519 | 7576.99 | 1.127 | 97.3 | 75.2 | 1334 | 27.51 | 4925 | 2402.9 | 2451.7 | 3579.9 | 1187.3 | 0.6544 | 4.682
2024-12-09 | 14:27 | Data | 0 | 34.681 | 33.412 | 132.757 | 7.63 | 125.48 | 2050.8 | 26.08 | 55.117 | 6.4 | 1.15 | 3.531 | 7576.99 | 1.181 | 97.3 | 75.4 | 1333 | 27.51 | 4925 | 2416.4 | 2456.8 | 3596.2 | 1187.3 | 0.6568 | 4.682
2024-12-09 | 14:27 | Data | 0 | 34.364 | 33.527 | 132.803 | 7.63 | 125.571 | 2054.41 | 26.08 | 54.936 | 6.4 | 1.16 | 3.549 | 7572.47 | 1.1 | 97.3 | 75.4 | 1335 | 27.56 | 4922.1 | 2416.8 | 2465.1 | 3599.9 | 1187.3 | 0.6565 | 4.709
2024-12-09 | 14:27 | Data | 0 | 34.567 | 33.399 | 132.712 | 7.64 | 125.571 | 2053.51 | 26.08 | 54.846 | 6.41 | 1.151 | 3.536 | 7590.56 | 1.202 | 97.3 | 75.4 | 1335 | 27.42 | 4933.9 | 2419.9 | 2465.7 | 3598.2 | 1187.3 | 0.65675 | 4.687
2024-12-09 | 14:27 | Data | 0 | 34.789 | 33.426 | 132.803 | 7.64 | 125.616 | 2056.22 | 26.1 | 55.026 | 6.41 | 1.149 | 3.531 | 7572.47 | 1.181 | 97.3 | 75.4 | 1337 | 27.56 | 4922.1 | 2432.3 | 2470.3 | 3614.6 | 1187.3 | 0.65859 | 4.682
2024-12-09 | 14:27 | Data | 0 | 34.567 | 33.412 | 132.803 | 7.64 | 125.571 | 2056.22 | 26.11 | 55.026 | 6.41 | 1.16 | 3.541 | 7558.9 | 1.154 | 97.3 | 75.3 | 1337 | 27.51 | 4913.3 | 2397.6 | 2458.5 | 3581.7 | 1187.3 | 0.65268 | 4.701
2024-12-09 | 14:27 | Data | 0 | 34.735 | 33.412 | 132.803 | 7.64 | 125.525 | 2055.31 | 26.11 | 55.117 | 6.41 | 1.16 | 3.52 | 7558.9 | 1.371 | 97.3 | 75.2 | 1337 | 27.51 | 4913.3 | 2419.6 | 2438.9 | 3576.4 | 1187.3 | 0.66222 | 4.681
2024-12-09 | 14:27 | Data | 0 | 34.567 | 33.412 | 132.848 | 7.63 | 125.525 | 2065.26 | 26.1 | 54.936 | 6.4 | 1.159 | 3.527 | 7563.42 | 1.154 | 97.3 | 75.3 | 1342 | 27.51 | 4916.2 | 2443.7 | 2436.8 | 3591.2 | 1187.3 | 0.66593 | 4.684
2024-12-09 | 14:27 | Data | 0 | 34.567 | 33.412 | 132.803 | 7.64 | 125.571 | 2054.41 | 26.11 | 55.026 | 6.41 | 1.156 | 3.525 | 7563.42 | 1.154 | 97.3 | 75.3 | 1336 | 27.51 | 4916.2 | 2430.2 | 2441.5 | 3588.4 | 1187.3 | 0.66189 | 4.68
2024-12-09 | 14:27 | Data | 0 | 34.796 | 33.439 | 132.893 | 7.64 | 125.616 | 2058.93 | 26.1 | 55.117 | 6.41 | 1.154 | 3.528 | 7572.47 | 1.215 | 97.3 | 75.4 | 1338 | 27.6 | 4922.1 | 2421.1 | 2447.9 | 3587.4 | 1187.3 | 0.6591 | 4.682
2024-12-09 | 14:27 | Data | 0 | 34.573 | 33.412 | 132.757 | 7.64 | 125.571 | 2058.93 | 26.1 | 55.026 | 6.41 | 1.152 | 3.53 | 7554.38 | 1.154 | 97.3 | 75.4 | 1338 | 27.51 | 4910.3 | 2423.9 | 2441.7 | 3586.4 | 1187.3 | 0.66039 | 4.682
2024-12-09 | 14:27 | Data | 0 | 34.573 | 33.412 | 132.757 | 7.64 | 125.571 | 2059.83 | 26.1 | 54.846 | 6.4 | 1.146 | 3.529 | 7531.77 | 1.154 | 97.3 | 75.5 | 1338 | 27.42 | 4895.6 | 2432.2 | 2446.6 | 3593.4 | 1187.3 | 0.66043 | 4.676
2024-12-09 | 14:27 | Data | 0 | 34.627 | 33.419 | 132.893 | 7.64 | 125.616 | 2058.93 | 26.11 | 55.026 | 6.41 | 1.153 | 3.538 | 7531.77 | 1.154 | 97.3 | 75.4 | 1338 | 27.47 | 4895.6 | 2425.1 | 2444.1 | 3587.4 | 1187.3 | 0.66003 | 4.691
2024-12-09 | 14:27 | Data | 0 | 34.56 | 33.412 | 132.757 | 7.63 | 125.616 | 2058.03 | 26.1 | 55.117 | 6.41 | 1.159 | 3.502 | 7531.77 | 1.154 | 97.3 | 75.1 | 1339 | 27.51 | 4895.6 | 2420.5 | 2419.2 | 3579.5 | 1187.3 | 0.66062 | 4.661
2024-12-09 | 14:27 | Data | 0 | 34.675 | 33.588 | 132.803 | 7.63 | 125.571 | 2059.83 | 26.1 | 55.117 | 6.41 | 1.167 | 3.504 | 7518.2 | 1.046 | 97.3 | 75 | 1338 | 27.56 | 4886.8 | 2414.2 | 2453 | 3581.8 | 1187.3 | 0.65666 | 4.671
2024-12-09 | 14:27 | Data | 0 | 34.465 | 33.412 | 132.848 | 7.63 | 125.661 | 2061.64 | 26.09 | 55.117 | 6.41 | 1.154 | 3.503 | 7518.2 | 0.938 | 97.3 | 75.2 | 1341 | 27.51 | 4886.8 | 2416.8 | 2443.6 | 3583.6 | 1187.3 | 0.6617 | 4.656
2024-12-09 | 14:28 | Data | 0 | 34.479 | 33.412 | 132.803 | 7.64 | 125.661 | 2062.55 | 26.11 | 55.117 | 6.41 | 1.161 | 3.534 | 7527.25 | 0.992 | 97.3 | 75.2 | 1340 | 27.51 | 4892.7 | 2404.7 | 2440.9 | 3574.1 | 1187.3 | 0.65786 | 4.698
2024-12-09 | 14:28 | Data | 0 | 34.783 | 33.48 | 132.803 | 7.64 | 125.661 | 2061.64 | 26.11 | 55.026 | 6.41 | 1.16 | 3.538 | 7522.72 | 1.033 | 97.3 | 75.3 | 1340 | 27.51 | 4889.8 | 2426.8 | 2434.3 | 3583.4 | 1187.3 | 0.66174 | 4.701
2024-12-09 | 14:28 | Data | 0 | 34.796 | 33.527 | 132.848 | 7.64 | 125.616 | 2060.74 | 26.11 | 55.117 | 6.4 | 1.168 | 3.532 | 7513.68 | 1.154 | 97.3 | 75.2 | 1339 | 27.56 | 4883.9 | 2404.9 | 2459.5 | 3588.4 | 1187.3 | 0.65864 | 4.701
2024-12-09 | 14:28 | Data | 0 | 34.357 | 33.426 | 132.803 | 7.64 | 125.616 | 2062.55 | 26.11 | 55.026 | 6.4 | 1.166 | 3.519 | 7500.11 | 1.04 | 97.3 | 75.1 | 1340 | 27.51 | 4875.1 | 2425.9 | 2442 | 3590 | 1187.3 | 0.66005 | 4.686
2024-12-09 | 14:28 | Data | 0 | 34.621 | 33.21 | 132.803 | 7.64 | 125.616 | 2062.55 | 26.1 | 55.117 | 6.4 | 1.16 | 3.516 | 7509.16 | 1.364 | 97.3 | 75.2 | 1340 | 27.51 | 4881 | 2391.1 | 2452.8 | 3572.3 | 1187.3 | 0.65348 | 4.676
2024-12-09 | 14:28 | Data | 0 | 34.567 | 33.412 | 132.803 | 7.64 | 125.571 | 2062.55 | 26.1 | 55.117 | 6.4 | 1.16 | 3.534 | 7513.68 | 1.175 | 97.3 | 75.3 | 1341 | 27.56 | 4883.9 | 2435.7 | 2443 | 3593.3 | 1187.3 | 0.66147 | 4.693
2024-12-09 | 14:28 | Data | 0 | 34.567 | 33.412 | 132.712 | 7.64 | 125.571 | 2058.93 | 26.11 | 55.117 | 6.4 | 1.151 | 3.509 | 7509.16 | 1.154 | 97.3 | 75.3 | 1338 | 27.56 | 4881 | 2425.5 | 2448.3 | 3592.9 | 1187.3 | 0.65911 | 4.662
2024-12-09 | 14:28 | Data | 0 | 34.681 | 33.432 | 132.757 | 7.64 | 125.571 | 2058.93 | 26.11 | 55.026 | 6.4 | 1.149 | 3.513 | 7522.72 | 1.249 | 97.3 | 75.3 | 1338 | 27.56 | 4889.8 | 2417.5 | 2440.1 | 3578 | 1187.3 | 0.65899 | 4.662
2024-12-09 | 14:28 | Data | 0 | 34.567 | 33.642 | 132.757 | 7.64 | 125.616 | 2058.93 | 26.11 | 54.936 | 6.41 | 1.161 | 3.538 | 7518.2 | 1.148 | 97.3 | 75.3 | 1338 | 27.47 | 4886.8 | 2418.2 | 2454.8 | 3591.3 | 1187.3 | 0.65833 | 4.698
2024-12-09 | 14:28 | Data | 0 | 34.567 | 33.635 | 132.803 | 7.64 | 125.571 | 2061.64 | 26.11 | 55.026 | 6.4 | 1.16 | 3.531 | 7518.2 | 0.986 | 97.3 | 75.3 | 1339 | 27.51 | 4886.8 | 2427 | 2422 | 3576.7 | 1187.3 | 0.66229 | 4.693
2024-12-09 | 14:28 | Data | 0 | 34.621 | 33.615 | 132.893 | 7.64 | 125.616 | 2066.16 | 26.1 | 55.297 | 6.4 | 1.159 | 3.546 | 7513.68 | 1.161 | 97.3 | 75.4 | 1343 | 27.56 | 4883.9 | 2410.4 | 2434.1 | 3566.3 | 1187.3 | 0.65964 | 4.703
2024-12-09 | 14:28 | Data | 0 | 34.796 | 33.642 | 132.893 | 7.64 | 125.661 | 2058.93 | 26.09 | 55.117 | 6.4 | 1.154 | 3.55 | 7509.16 | 1.154 | 97.3 | 75.5 | 1339 | 27.56 | 4881 | 2425.8 | 2401.7 | 3558.1 | 1187.3 | 0.66351 | 4.705
2024-12-09 | 14:28 | Data | 0 | 34.769 | 33.419 | 132.848 | 7.64 | 125.661 | 2059.83 | 26.1 | 55.026 | 6.4 | 1.159 | 3.546 | 7522.72 | 1.202 | 97.3 | 75.4 | 1338 | 27.51 | 4889.8 | 2436.9 | 2432.6 | 3586.6 | 1187.4 | 0.66342 | 4.704
2024-12-09 | 14:28 | Data | 0 | 34.567 | 33.412 | 132.757 | 7.64 | 125.571 | 2059.83 | 26.12 | 55.026 | 6.4 | 1.168 | 3.512 | 7509.16 | 1.269 | 97.3 | 75 | 1339 | 27.56 | 4881 | 2417.1 | 2459.9 | 3596.6 | 1187.4 | 0.65448 | 4.68
2024-12-09 | 14:28 | Data | 0 | 34.573 | 33.412 | 132.848 | 7.64 | 125.616 | 2058.03 | 26.11 | 55.026 | 6.4 | 1.16 | 3.541 | 7513.68 | 1.154 | 97.3 | 75.3 | 1338 | 27.51 | 4883.9 | 2414.9 | 2439.4 | 3582.8 | 1187.4 | 0.65856 | 4.702
2024-12-09 | 14:28 | Data | 0 | 34.567 | 33.419 | 132.757 | 7.64 | 125.571 | 2061.64 | 26.11 | 55.117 | 6.4 | 1.159 | 3.525 | 7504.64 | 1.148 | 97.3 | 75.3 | 1339 | 27.47 | 4878 | 2413.1 | 2424.2 | 3567.7 | 1187.4 | 0.66092 | 4.685
2024-12-09 | 14:28 | Data | 0 | 34.681 | 33.628 | 132.803 | 7.64 | 125.571 | 2062.55 | 26.1 | 55.026 | 6.4 | 1.159 | 3.526 | 7495.59 | 1.154 | 97.3 | 75.3 | 1340 | 27.56 | 4872.1 | 2395.6 | 2432.1 | 3561.1 | 1187.4 | 0.65599 | 4.683
2024-12-09 | 14:28 | Data | 0 | 34.58 | 33.412 | 132.848 | 7.63 | 125.661 | 2064.35 | 26.1 | 55.026 | 6.41 | 1.151 | 3.529 | 7500.11 | 1.161 | 97.3 | 75.4 | 1341 | 27.51 | 4875.1 | 2429.3 | 2424.3 | 3575.9 | 1187.4 | 0.66206 | 4.682
2024-12-09 | 14:29 | Data | 0 | 34.58 | 33.412 | 132.848 | 7.64 | 125.706 | 2059.83 | 26.1 | 55.658 | 6.41 | 1.153 | 3.518 | 7495.59 | 1.148 | 97.3 | 75.3 | 1339 | 27.87 | 4872.1 | 2430.5 | 2454.1 | 3596.4 | 1187.4 | 0.65871 | 4.672
2024-12-09 | 14:29 | Data | 0 | 34.742 | 33.628 | 132.893 | 7.64 | 125.616 | 2058.03 | 26.11 | 55.117 | 6.41 | 1.166 | 3.537 | 7491.07 | 1.161 | 97.3 | 75.2 | 1338 | 27.56 | 4869.2 | 2427.9 | 2432.6 | 3585.3 | 1187.4 | 0.66131 | 4.702
2024-12-09 | 14:29 | Data | 0 | 34.681 | 33.621 | 132.893 | 7.64 | 125.706 | 2058.93 | 26.11 | 55.117 | 6.41 | 1.161 | 3.538 | 7491.07 | 0.959 | 97.3 | 75.3 | 1338 | 27.51 | 4869.2 | 2427.2 | 2420.9 | 3572.5 | 1187.4 | 0.66502 | 4.7
2024-12-09 | 14:29 | Data | 0 | 34.769 | 33.642 | 132.848 | 7.64 | 125.661 | 2058.93 | 26.1 | 55.026 | 6.41 | 1.165 | 3.525 | 7495.59 | 1.154 | 97.3 | 75.2 | 1339 | 27.47 | 4872.1 | 2416.8 | 2424.8 | 3571.5 | 1187.4 | 0.65961 | 4.691
2024-12-09 | 14:29 | Data | 0 | 34.58 | 33.412 | 132.803 | 7.64 | 125.661 | 2059.83 | 26.11 | 55.026 | 6.4 | 1.163 | 3.518 | 7500.11 | 1.148 | 97.3 | 75.2 | 1339 | 27.51 | 4875.1 | 2434.1 | 2429.7 | 3589 | 1187.4 | 0.6636 | 4.682
2024-12-09 | 14:29 | Data | 0 | 34.573 | 33.412 | 132.757 | 7.64 | 125.616 | 2058.93 | 26.09 | 55.117 | 6.4 | 1.151 | 3.518 | 7500.11 | 1.148 | 97.3 | 75.4 | 1338 | 27.51 | 4875.1 | 2417.8 | 2403.5 | 3558.1 | 1187.4 | 0.66317 | 4.671
2024-12-09 | 14:29 | Data | 0 | 34.567 | 33.304 | 132.712 | 7.64 | 125.616 | 2061.64 | 26.1 | 55.297 | 6.4 | 1.162 | 3.518 | 7491.07 | 1.141 | 97.3 | 75.2 | 1340 | 27.69 | 4869.2 | 2402.5 | 2425.2 | 3588.1 | 1187.4 | 0.65703 | 4.679
2024-12-09 | 14:29 | Data | 0 | 34.769 | 33.588 | 132.893 | 7.64 | 125.661 | 2062.55 | 26.09 | 55.297 | 6.4 | 1.159 | 3.541 | 7504.64 | 1.377 | 97.3 | 75.3 | 1340 | 27.65 | 4878 | 2422.8 | 2426.9 | 3571.6 | 1187.4 | 0.665 | 4.701
2024-12-09 | 14:29 | Data | 0 | 34.594 | 33.365 | 132.803 | 7.64 | 125.616 | 2064.35 | 26.11 | 55.297 | 6.41 | 1.163 | 3.51 | 7486.55 | 1.08 | 97.3 | 75.1 | 1342 | 27.6 | 4866.3 | 2410.6 | 2420.8 | 3562 | 1187.4 | 0.66041 | 4.672
2024-12-09 | 14:29 | Data | 0 | 34.85 | 33.473 | 132.984 | 7.64 | 125.661 | 2065.26 | 26.12 | 55.297 | 6.41 | 1.162 | 3.556 | 7495.59 | 1.215 | 97.3 | 75.4 | 1342 | 27.65 | 4872.1 | 2406.2 | 2425.4 | 3556.9 | 1187.4 | 0.65975 | 4.719
2024-12-09 | 14:29 | Data | 0 | 34.796 | 33.669 | 132.803 | 7.64 | 125.661 | 2065.26 | 26.1 | 55.297 | 6.4 | 1.159 | 3.548 | 7491.07 | 1.269 | 97.3 | 75.4 | 1342 | 27.65 | 4869.2 | 2416.7 | 2451.4 | 3587.7 | 1187.4 | 0.65784 | 4.708
2024-12-09 | 14:29 | Data | 0 | 34.6 | 33.628 | 132.938 | 7.64 | 125.661 | 2065.26 | 26.1 | 55.388 | 6.4 | 1.159 | 3.543 | 7486.55 | 0.986 | 97.3 | 75.3 | 1342 | 27.65 | 4866.3 | 2422.6 | 2419.3 | 3569.3 | 1187.4 | 0.66314 | 4.701
2024-12-09 | 14:29 | Data | 0 | 34.567 | 33.635 | 132.803 | 7.64 | 125.661 | 2064.35 | 26.09 | 55.297 | 6.41 | 1.156 | 3.519 | 7477.5 | 1.107 | 97.3 | 75.3 | 1342 | 27.65 | 4860.4 | 2404.7 | 2442.1 | 3570.5 | 1187.4 | 0.65538 | 4.675
2024-12-09 | 14:29 | Data | 0 | 34.789 | 33.419 | 132.893 | 7.63 | 125.661 | 2064.35 | 26.11 | 55.388 | 6.4 | 1.152 | 3.527 | 7504.64 | 1.195 | 97.3 | 75.4 | 1341 | 27.65 | 4878 | 2421.5 | 2446 | 3585.3 | 1187.4 | 0.65811 | 4.68
2024-12-09 | 14:29 | Data | 0 | 34.573 | 33.412 | 132.938 | 7.64 | 125.706 | 2065.26 | 26.1 | 54.665 | 6.4 | 1.15 | 3.529 | 7504.64 | 1.154 | 97.3 | 75.4 | 1342 | 27.38 | 4878 | 2397.6 | 2428.6 | 3558.2 | 1187.4 | 0.65665 | 4.68
2024-12-09 | 14:29 | Data | 0 | 34.58 | 33.743 | 132.803 | 7.64 | 125.616 | 2064.35 | 26.1 | 55.026 | 6.41 | 1.159 | 3.543 | 7491.07 | 1.094 | 97.3 | 75.4 | 1342 | 27.56 | 4869.2 | 2404.5 | 2445.9 | 3578.5 | 1187.4 | 0.65838 | 4.7
2024-12-09 | 14:29 | Data | 0 | 34.911 | 33.655 | 132.984 | 7.64 | 125.661 | 2065.26 | 26.11 | 55.658 | 6.4 | 1.159 | 3.536 | 7504.64 | 1.222 | 97.3 | 75.3 | 1342 | 27.87 | 4878 | 2416.4 | 2440.7 | 3580.2 | 1187.4 | 0.6582 | 4.695
2024-12-09 | 14:30 | Data | 0 | 34.783 | 33.412 | 132.757 | 7.64 | 125.616 | 2065.26 | 26.09 | 55.297 | 6.4 | 1.156 | 3.532 | 7500.11 | 1.256 | 97.3 | 75.3 | 1342 | 27.69 | 4875.1 | 2408.5 | 2459.2 | 3583 | 1187.4 | 0.65645 | 4.687
2024-12-09 | 14:30 | Data | 0 | 34.567 | 33.797 | 132.893 | 7.64 | 125.661 | 2062.55 | 26.1 | 55.388 | 6.41 | 1.152 | 3.537 | 7495.59 | 1.181 | 97.3 | 75.4 | 1340 | 27.69 | 4872.1 | 2409.4 | 2448.2 | 3576.7 | 1187.4 | 0.65723 | 4.689
2024-12-09 | 14:30 | Data | 0 | 34.796 | 33.642 | 132.848 | 7.64 | 125.706 | 2061.64 | 26.1 | 55.297 | 6.4 | 1.15 | 3.527 | 7504.64 | 1.154 | 97.3 | 75.4 | 1340 | 27.69 | 4878 | 2405.1 | 2447.8 | 3573.5 | 1187.4 | 0.65706 | 4.678
2024-12-09 | 14:30 | Data | 0 | 34.789 | 33.426 | 132.757 | 7.64 | 125.616 | 2060.74 | 26.11 | 55.297 | 6.4 | 1.16 | 3.527 | 7504.64 | 1.357 | 97.3 | 75.2 | 1339 | 27.65 | 4878 | 2428.1 | 2438.5 | 3581 | 1187.4 | 0.6616 | 4.687
2024-12-09 | 14:30 | Data | 0 | 35.012 | 33.655 | 132.938 | 7.64 | 125.797 | 2065.26 | 26.1 | 55.297 | 6.4 | 1.166 | 3.523 | 7509.16 | 1.33 | 97.3 | 75.1 | 1342 | 27.65 | 4881 | 2418.8 | 2428.4 | 3581.1 | 1187.4 | 0.66248 | 4.687
2024-12-09 | 14:30 | Data | 0 | 34.972 | 33.648 | 133.074 | 7.63 | 125.887 | 2065.26 | 26.12 | 55.297 | 6.41 | 1.17 | 3.511 | 7495.59 | 1.175 | 97.3 | 75 | 1342 | 27.65 | 4872.1 | 2418.4 | 2441.2 | 3601.8 | 1187.4 | 0.66315 | 4.682
2024-12-09 | 14:30 | Data | 0 | 34.911 | 33.439 | 132.803 | 7.63 | 125.706 | 2062.55 | 26.11 | 55.388 | 6.4 | 1.155 | 3.532 | 7522.72 | 1.337 | 97.3 | 75.4 | 1343 | 27.65 | 4889.8 | 2431.3 | 2452.9 | 3594.1 | 1187.4 | 0.66082 | 4.685
2024-12-09 | 14:30 | Data | 0 | 34.796 | 33.642 | 132.938 | 7.64 | 125.706 | 2065.26 | 26.11 | 55.388 | 6.4 | 1.154 | 3.53 | 7518.2 | 1.154 | 97.3 | 75.3 | 1343 | 27.6 | 4886.8 | 2419.7 | 2431.9 | 3575.4 | 1187.4 | 0.66163 | 4.685
2024-12-09 | 14:30 | Data | 0 | 34.594 | 33.412 | 132.848 | 7.64 | 125.706 | 2064.35 | 26.1 | 55.297 | 6.4 | 1.149 | 3.498 | 7509.16 | 1.161 | 97.3 | 75.3 | 1342 | 27.65 | 4881 | 2416.4 | 2445.4 | 3585.1 | 1187.4 | 0.65811 | 4.647
2024-12-09 | 14:30 | Data | 0 | 34.567 | 33.743 | 132.893 | 7.64 | 125.661 | 2067.97 | 26.11 | 55.658 | 6.4 | 1.148 | 3.517 | 7513.68 | 1.154 | 97.3 | 75.4 | 1344 | 27.65 | 4883.9 | 2405.3 | 2458.4 | 3590.8 | 1187.4 | 0.65447 | 4.664
2024-12-09 | 14:30 | Data | 0 | 34.789 | 33.588 | 132.848 | 7.63 | 125.616 | 2059.83 | 26.1 | 55.388 | 6.41 | 1.151 | 3.538 | 7522.72 | 1.371 | 97.3 | 75.5 | 1339 | 27.65 | 4889.8 | 2425.6 | 2447.2 | 3586.4 | 1187.4 | 0.65736 | 4.69
2024-12-09 | 14:30 | Data | 0 | 34.796 | 33.419 | 132.893 | 7.64 | 125.616 | 2066.16 | 26.11 | 55.297 | 6.4 | 1.15 | 3.514 | 7522.72 | 1.175 | 97.3 | 75.4 | 1342 | 27.65 | 4889.8 | 2395.7 | 2433.9 | 3562.8 | 1187.4 | 0.65588 | 4.663
2024-12-09 | 14:30 | Data | 0 | 34.796 | 33.642 | 132.984 | 7.64 | 125.706 | 2065.26 | 26.1 | 55.297 | 6.41 | 1.149 | 3.496 | 7527.25 | 1.04 | 97.3 | 75.3 | 1342 | 27.6 | 4892.7 | 2412.9 | 2430.7 | 3572.5 | 1187.4 | 0.66116 | 4.644
2024-12-09 | 14:30 | Data | 0 | 34.769 | 33.628 | 132.848 | 7.64 | 125.661 | 2065.26 | 26.1 | 55.297 | 6.41 | 1.146 | 3.526 | 7509.16 | 1.154 | 97.3 | 75.5 | 1342 | 27.69 | 4881 | 2423.8 | 2444.2 | 3584.5 | 1187.4 | 0.66121 | 4.672
2024-12-09 | 14:30 | Data | 0 | 34.85 | 33.419 | 132.893 | 7.64 | 125.706 | 2065.26 | 26.11 | 55.388 | 6.4 | 1.152 | 3.521 | 7518.2 | 1.168 | 97.3 | 75.4 | 1342 | 27.69 | 4886.8 | 2411.9 | 2429.4 | 3568.9 | 1187.4 | 0.66053 | 4.675
2024-12-09 | 14:30 | Data | 0 | 34.58 | 33.513 | 132.803 | 7.64 | 125.661 | 2065.26 | 26.1 | 55.388 | 6.41 | 1.159 | 3.52 | 7518.2 | 1.175 | 97.3 | 75.2 | 1342 | 27.69 | 4886.8 | 2415.4 | 2420.1 | 3565.7 | 1187.4 | 0.66056 | 4.679
2024-12-09 | 14:30 | Data | 0 | 34.783 | 33.426 | 132.803 | 7.64 | 125.661 | 2065.26 | 26.11 | 55.388 | 6.41 | 1.159 | 3.54 | 7509.16 | 1.256 | 97.3 | 75.4 | 1343 | 27.69 | 4881 | 2401.8 | 2432.7 | 3566.4 | 1187.4 | 0.65926 | 4.697
2024-12-09 | 14:30 | Data | 0 | 34.567 | 33.527 | 132.893 | 7.64 | 125.661 | 2065.26 | 26.09 | 55.297 | 6.4 | 1.168 | 3.546 | 7509.16 | 1.242 | 97.3 | 75.2 | 1342 | 27.65 | 4881 | 2407 | 2445.9 | 3580.6 | 1187.4 | 0.65499 | 4.713
2024-12-09 | 14:31 | Data | 0 | 34.742 | 33.588 | 132.893 | 7.63 | 125.661 | 2060.74 | 26.11 | 55.388 | 6.4 | 1.164 | 3.525 | 7504.64 | 1.35 | 97.3 | 75.2 | 1339 | 27.69 | 4878 | 2418.8 | 2433.4 | 3573.4 | 1187.4 | 0.65928 | 4.689
2024-12-09 | 14:31 | Data | 0 | 34.573 | 33.439 | 132.803 | 7.64 | 125.706 | 2065.26 | 26.1 | 55.388 | 6.4 | 1.159 | 3.515 | 7509.16 | 1.33 | 97.3 | 75.2 | 1342 | 27.74 | 4881 | 2418.9 | 2446 | 3589.7 | 1187.4 | 0.66222 | 4.673
2024-12-09 | 14:31 | Data | 0 | 34.573 | 33.588 | 132.893 | 7.64 | 125.706 | 2064.35 | 26.12 | 55.297 | 6.41 | 1.161 | 3.518 | 7522.72 | 1.33 | 97.3 | 75.2 | 1342 | 27.69 | 4889.8 | 2429.1 | 2429.3 | 3577.6 | 1187.4 | 0.66302 | 4.679
2024-12-09 | 14:31 | Data | 0 | 34.796 | 33.642 | 132.938 | 7.64 | 125.661 | 2059.83 | 26.11 | 55.026 | 6.41 | 1.163 | 3.498 | 7522.72 | 1.154 | 97.3 | 75 | 1339 | 27.56 | 4889.8 | 2423.9 | 2431.4 | 3576.6 | 1187.5 | 0.66051 | 4.662
2024-12-09 | 14:31 | Data | 0 | 34.58 | 33.729 | 132.803 | 7.64 | 125.661 | 2066.16 | 26.09 | 55.026 | 6.4 | 1.166 | 3.534 | 7518.2 | 1.013 | 97.3 | 75.2 | 1343 | 27.47 | 4886.8 | 2415.1 | 2441.6 | 3587.8 | 1187.5 | 0.66187 | 4.7
2024-12-09 | 14:31 | Data | 0 | 34.58 | 33.635 | 132.893 | 7.64 | 125.661 | 2062.55 | 26.11 | 55.117 | 6.41 | 1.164 | 3.544 | 7518.2 | 0.986 | 97.3 | 75.3 | 1342 | 27.56 | 4886.8 | 2407 | 2442.8 | 3577.3 | 1187.5 | 0.65719 | 4.708
2024-12-09 | 14:31 | Data | 0 | 34.789 | 33.642 | 132.984 | 7.64 | 125.706 | 2061.64 | 26.1 | 55.117 | 6.4 | 1.164 | 3.518 | 7518.2 | 1.154 | 97.3 | 75.1 | 1340 | 27.51 | 4886.8 | 2414.7 | 2437.2 | 3580.5 | 1187.5 | 0.66194 | 4.681
2024-12-09 | 14:31 | Data | 0 | 34.715 | 33.412 | 132.984 | 7.64 | 125.661 | 2061.64 | 26.1 | 55.026 | 6.4 | 1.159 | 3.507 | 7504.64 | 0.992 | 97.3 | 75.2 | 1339 | 27.51 | 4878 | 2406.1 | 2425.5 | 3563.3 | 1187.5 | 0.65855 | 4.665
2024-12-09 | 14:31 | Data | 0 | 34.823 | 33.534 | 132.938 | 7.63 | 125.661 | 2062.55 | 26.1 | 54.936 | 6.4 | 1.15 | 3.525 | 7513.68 | 1.202 | 97.3 | 75.4 | 1340 | 27.47 | 4883.9 | 2422.1 | 2446.2 | 3585.7 | 1187.5 | 0.65742 | 4.675
2024-12-09 | 14:31 | Data | 0 | 34.783 | 33.81 | 132.893 | 7.64 | 125.661 | 2062.55 | 26.1 | 55.117 | 6.41 | 1.16 | 3.528 | 7504.64 | 1.269 | 97.3 | 75.3 | 1340 | 27.56 | 4878 | 2427.8 | 2421 | 3570.6 | 1187.5 | 0.66269 | 4.689
2024-12-09 | 14:31 | Data | 0 | 35.019 | 33.655 | 132.984 | 7.64 | 125.842 | 2061.64 | 26.1 | 55.026 | 6.39 | 1.165 | 3.514 | 7518.2 | 1.195 | 97.3 | 75.1 | 1341 | 27.51 | 4886.8 | 2415.9 | 2441.1 | 3576.7 | 1187.5 | 0.65962 | 4.678
2024-12-09 | 14:31 | Data | 0 | 34.641 | 33.419 | 132.893 | 7.63 | 125.706 | 2061.64 | 26.1 | 55.207 | 6.4 | 1.168 | 3.54 | 7518.2 | 1.127 | 97.3 | 75.2 | 1340 | 27.51 | 4886.8 | 2420.6 | 2433.9 | 3575.7 | 1187.5 | 0.66052 | 4.71
2024-12-09 | 14:31 | Data | 0 | 34.594 | 33.642 | 132.938 | 7.64 | 125.706 | 2061.64 | 26.11 | 55.026 | 6.42 | 1.157 | 3.519 | 7518.2 | 0.932 | 97.3 | 75.3 | 1341 | 27.51 | 4886.8 | 2409.3 | 2436.5 | 3574.3 | 1187.5 | 0.65727 | 4.676
2024-12-09 | 14:31 | Data | 0 | 34.573 | 33.419 | 132.893 | 7.63 | 125.706 | 2061.64 | 26.11 | 55.117 | 6.41 | 1.16 | 3.516 | 7522.72 | 1.344 | 97.3 | 75.2 | 1340 | 27.47 | 4889.8 | 2418.2 | 2458.8 | 3593.4 | 1187.5 | 0.65928 | 4.678
2024-12-09 | 14:31 | Data | 0 | 34.621 | 33.419 | 132.848 | 7.64 | 125.661 | 2061.64 | 26.1 | 55.026 | 6.4 | 1.152 | 3.536 | 7504.64 | 1.161 | 97.3 | 75.4 | 1339 | 27.51 | 4878 | 2412.8 | 2466.2 | 3591.7 | 1187.5 | 0.65665 | 4.688
2024-12-09 | 14:31 | Data | 0 | 34.796 | 33.642 | 132.938 | 7.64 | 125.797 | 2062.55 | 26.11 | 55.117 | 6.4 | 1.162 | 3.538 | 7518.2 | 1.154 | 97.3 | 75.3 | 1340 | 27.51 | 4886.8 | 2448.6 | 2438 | 3596.4 | 1187.5 | 0.66352 | 4.701
2024-12-09 | 14:31 | Data | 0 | 34.573 | 33.642 | 132.893 | 7.63 | 125.797 | 2065.26 | 26.11 | 54.846 | 6.4 | 1.153 | 3.51 | 7531.77 | 1.127 | 97.3 | 75.3 | 1342 | 27.42 | 4895.6 | 2430.5 | 2451.3 | 3594.8 | 1187.5 | 0.65956 | 4.664
2024-12-09 | 14:31 | Data | 0 | 34.796 | 33.635 | 132.938 | 7.64 | 125.706 | 2064.35 | 26.11 | 55.117 | 6.41 | 1.161 | 3.528 | 7536.29 | 1.161 | 97.3 | 75.2 | 1342 | 27.56 | 4898.6 | 2410.8 | 2421 | 3559.1 | 1187.5 | 0.66168 | 4.69
2024-12-09 | 14:32 | Data | 0 | 35.019 | 33.534 | 133.074 | 7.63 | 125.797 | 2061.64 | 26.1 | 55.026 | 6.41 | 1.161 | 3.538 | 7549.86 | 1.181 | 97.3 | 75.3 | 1340 | 27.47 | 4907.4 | 2405.8 | 2445.6 | 3567.8 | 1187.5 | 0.65585 | 4.698
2024-12-09 | 14:32 | Data | 0 | 34.904 | 33.844 | 133.074 | 7.64 | 125.842 | 2060.74 | 26.1 | 55.026 | 6.41 | 1.164 | 3.538 | 7527.25 | 1.053 | 97.3 | 75.2 | 1338 | 27.56 | 4892.7 | 2430.5 | 2418.6 | 3576 | 1187.5 | 0.66431 | 4.702
2024-12-09 | 14:32 | Data | 0 | 34.796 | 33.426 | 132.938 | 7.64 | 125.797 | 2065.26 | 26.11 | 55.026 | 6.4 | 1.152 | 3.527 | 7549.86 | 1.202 | 97.3 | 75.4 | 1343 | 27.51 | 4907.4 | 2420.2 | 2453.5 | 3591 | 1187.5 | 0.65728 | 4.679
2024-12-09 | 14:32 | Data | 0 | 34.789 | 33.601 | 132.893 | 7.64 | 125.706 | 2065.26 | 26.09 | 55.117 | 6.41 | 1.149 | 3.524 | 7545.34 | 1.242 | 97.3 | 75.4 | 1342 | 27.51 | 4904.5 | 2410.8 | 2426.3 | 3566.5 | 1187.5 | 0.66106 | 4.672
2024-12-09 | 14:32 | Data | 0 | 34.6 | 33.642 | 132.893 | 7.64 | 125.842 | 2065.26 | 26.11 | 55.117 | 6.41 | 1.157 | 3.516 | 7554.38 | 1.053 | 97.3 | 75.2 | 1342 | 27.56 | 4910.3 | 2402.3 | 2421.5 | 3557.7 | 1187.5 | 0.65908 | 4.672
2024-12-09 | 14:32 | Data | 0 | 34.756 | 33.642 | 132.848 | 7.64 | 125.706 | 2062.55 | 26.1 | 55.117 | 6.41 | 1.159 | 3.524 | 7558.9 | 1.148 | 97.3 | 75.3 | 1340 | 27.56 | 4913.3 | 2426.1 | 2436.5 | 3580.5 | 1187.5 | 0.66094 | 4.682
2024-12-09 | 14:32 | Data | 0 | 34.911 | 33.419 | 132.938 | 7.64 | 125.797 | 2060.74 | 26.1 | 55.117 | 6.4 | 1.16 | 3.54 | 7545.34 | 1.154 | 97.3 | 75.3 | 1340 | 27.51 | 4904.5 | 2415.2 | 2435.5 | 3578.5 | 1187.5 | 0.65942 | 4.701
2024-12-09 | 14:32 | Data | 0 | 34.911 | 33.601 | 132.984 | 7.63 | 125.797 | 2062.55 | 26.11 | 55.026 | 6.4 | 1.151 | 3.526 | 7554.38 | 1.283 | 97.3 | 75.4 | 1340 | 27.51 | 4910.3 | 2422.4 | 2419.7 | 3571.9 | 1187.5 | 0.66421 | 4.677
2024-12-09 | 14:32 | Data | 0 | 34.796 | 33.642 | 132.984 | 7.64 | 125.842 | 2061.64 | 26.11 | 55.117 | 6.4 | 1.159 | 3.526 | 7563.42 | 1.154 | 97.3 | 75.3 | 1340 | 27.51 | 4916.2 | 2427.7 | 2469.4 | 3606.6 | 1187.5 | 0.65728 | 4.685
2024-12-09 | 14:32 | Data | 0 | 34.911 | 33.858 | 132.938 | 7.64 | 125.706 | 2061.64 | 26.11 | 55.026 | 6.41 | 1.16 | 3.513 | 7567.95 | 1.256 | 97.3 | 75.1 | 1339 | 27.51 | 4919.2 | 2449.9 | 2440.2 | 3599.6 | 1187.5 | 0.66399 | 4.673
2024-12-09 | 14:32 | Data | 0 | 35.019 | 33.858 | 132.984 | 7.63 | 125.797 | 2065.26 | 26.11 | 55.388 | 6.41 | 1.159 | 3.525 | 7572.47 | 1.208 | 97.3 | 75.3 | 1342 | 27.69 | 4922.1 | 2411.2 | 2444.4 | 3583.4 | 1187.5 | 0.65792 | 4.683
2024-12-09 | 14:32 | Data | 0 | 34.796 | 33.615 | 132.893 | 7.64 | 125.706 | 2064.35 | 26.1 | 55.297 | 6.4 | 1.163 | 3.516 | 7563.42 | 1.141 | 97.3 | 75.1 | 1342 | 27.69 | 4916.2 | 2415.8 | 2436.2 | 3573 | 1187.5 | 0.66056 | 4.677
2024-12-09 | 14:32 | Data | 0 | 35.08 | 33.756 | 133.074 | 7.64 | 125.797 | 2066.16 | 26.1 | 55.207 | 6.41 | 1.168 | 3.526 | 7567.95 | 1.256 | 97.3 | 75.1 | 1343 | 27.69 | 4919.2 | 2414.9 | 2446.5 | 3573.8 | 1187.5 | 0.65761 | 4.696
2024-12-09 | 14:32 | Data | 0 | 34.587 | 33.628 | 132.893 | 7.64 | 125.797 | 2064.35 | 26.1 | 55.388 | 6.41 | 1.163 | 3.54 | 7572.47 | 0.986 | 97.3 | 75.3 | 1342 | 27.69 | 4922.1 | 2419.3 | 2455.4 | 3586.2 | 1187.5 | 0.6588 | 4.703
2024-12-09 | 14:32 | Data | 0 | 34.938 | 33.642 | 132.984 | 7.64 | 125.797 | 2061.64 | 26.11 | 55.297 | 6.4 | 1.159 | 3.55 | 7590.56 | 1.364 | 97.3 | 75.4 | 1340 | 27.65 | 4933.9 | 2416.6 | 2437.5 | 3577.3 | 1187.5 | 0.6609 | 4.71
2024-12-09 | 14:32 | Data | 0 | 34.796 | 33.952 | 132.938 | 7.64 | 125.797 | 2062.55 | 26.09 | 55.478 | 6.4 | 1.159 | 3.521 | 7576.99 | 1.04 | 97.3 | 75.2 | 1341 | 27.69 | 4925 | 2423.2 | 2465 | 3595.6 | 1187.5 | 0.65582 | 4.68
2024-12-09 | 14:32 | Data | 0 | 34.796 | 33.864 | 133.074 | 7.63 | 125.706 | 2061.64 | 26.1 | 55.749 | 6.41 | 1.166 | 3.537 | 7576.99 | 1.154 | 97.3 | 75.2 | 1340 | 27.87 | 4925 | 2428.9 | 2468.7 | 3605.3 | 1187.5 | 0.65984 | 4.702
2024-12-09 | 14:32 | Data | 0 | 35.019 | 33.642 | 132.984 | 7.63 | 125.842 | 2061.64 | 26.1 | 55.658 | 6.41 | 1.165 | 3.533 | 7567.95 | 1.262 | 97.3 | 75.2 | 1340 | 27.83 | 4919.2 | 2422.1 | 2442.9 | 3580.8 | 1187.5 | 0.65978 | 4.697
2024-12-09 | 14:33 | Data | 0 | 34.742 | 33.534 | 132.893 | 7.64 | 125.706 | 2014.64 | 26.11 | 55.388 | 6.41 | 1.167 | 3.537 | 7572.47 | 1.35 | 97.3 | 75.2 | 1309 | 27.69 | 4922.1 | 2392.1 | 2432.2 | 3555.4 | 1187.5 | 0.65782 | 4.703
2024-12-09 | 14:33 | Data | 0 | 34.681 | 33.642 | 132.938 | 7.63 | 125.706 | 2009.22 | 26.1 | 55.658 | 6.41 | 1.166 | 3.517 | 7572.47 | 0.986 | 97.2 | 75.1 | 1307 | 27.87 | 4922.1 | 2410.5 | 2435.6 | 3573.3 | 1187.5 | 0.65821 | 4.684
2024-12-09 | 14:33 | Data | 0 | 34.999 | 33.756 | 133.074 | 7.64 | 125.842 | 2007.41 | 26.11 | 55.658 | 6.41 | 1.168 | 3.537 | 7590.56 | 1.256 | 97.2 | 75.2 | 1305 | 27.92 | 4933.9 | 2393.8 | 2442.5 | 3564.2 | 1187.5 | 0.65635 | 4.705
2024-12-09 | 14:33 | Data | 0 | 34.796 | 33.642 | 132.938 | 7.63 | 125.797 | 2007.41 | 26.11 | 55.658 | 6.4 | 1.167 | 3.521 | 7572.47 | 1.154 | 97.2 | 75.1 | 1305 | 27.83 | 4922.1 | 1779.4 | 2053.6 | 2768.7 | 1187.5 | 0.62172 | 4.691
2024-12-09 | 14:33 | Data | 0 | 34.783 | 33.642 | 132.893 | 7.64 | 125.842 | 2054.41 | 26.11 | 55.478 | 6.4 | 1.156 | 3.503 | 7590.56 | 1.181 | 97.3 | 75.2 | 1335 | 27.74 | 4933.9 | 1332.7 | 1794.5 | 2254 | 1187.5 | 0.59033 | 4.659
2024-12-09 | 14:33 | Data | 0 | 35.026 | 33.696 | 133.074 | 7.64 | 125.887 | 2058.93 | 26.11 | 55.658 | 6.41 | 1.166 | 3.517 | 7576.99 | 1.269 | 97.3 | 75.1 | 1338 | 27.83 | 4925 | 1342.8 | 1793.7 | 2259.3 | 1187.5 | 0.59164 | 4.683
2024-12-09 | 14:33 | Data | 0 | 34.796 | 33.662 | 132.984 | 7.64 | 125.797 | 2058.93 | 26.11 | 55.658 | 6.4 | 1.164 | 3.491 | 7581.51 | 1.067 | 97.3 | 75 | 1338 | 27.83 | 4928 | 1327.7 | 1787.5 | 2243.7 | 1187.5 | 0.59076 | 4.656
2024-12-09 | 14:33 | Data | 0 | 34.715 | 33.642 | 133.074 | 7.64 | 125.797 | 2061.64 | 26.09 | 55.749 | 6.41 | 1.162 | 3.51 | 7590.56 | 1.134 | 97.3 | 75.1 | 1340 | 27.83 | 4933.9 | 1334.6 | 1788.6 | 2249.5 | 1187.5 | 0.59125 | 4.673
2024-12-09 | 14:33 | Data | 0 | 34.796 | 33.642 | 132.938 | 7.64 | 125.706 | 2061.64 | 26.1 | 55.658 | 6.4 | 1.154 | 3.524 | 7576.99 | 1.154 | 97.3 | 75.3 | 1340 | 27.83 | 4925 | 1327.5 | 1780.6 | 2238.4 | 1187.5 | 0.5893 | 4.677
2024-12-09 | 14:33 | Data | 0 | 34.972 | 33.648 | 133.119 | 7.64 | 125.842 | 2059.83 | 26.12 | 55.478 | 6.4 | 1.159 | 3.521 | 7581.51 | 1.222 | 97.3 | 75.2 | 1338 | 27.83 | 4928 | 1320.7 | 1781.3 | 2236.8 | 1187.5 | 0.58933 | 4.68
2024-12-09 | 14:33 | Data | 0 | 34.81 | 33.642 | 132.893 | 7.64 | 125.706 | 1957.7 | 26.11 | 55.658 | 6.41 | 1.156 | 3.518 | 7586.04 | 1.154 | 97.2 | 75.3 | 1273 | 27.83 | 4930.9 | 1344.5 | 1775 | 2245.2 | 1187.5 | 0.5968 | 4.673
2024-12-09 | 14:33 | Data | 0 | 34.83 | 33.642 | 133.074 | 7.64 | 125.842 | 2051.7 | 26.1 | 55.658 | 6.41 | 1.159 | 3.508 | 7563.42 | 1.168 | 97.3 | 75.2 | 1334 | 27.83 | 4916.2 | 1334.9 | 1802.1 | 2259.9 | 1187.5 | 0.58985 | 4.667
2024-12-09 | 14:33 | Data | 0 | 34.796 | 33.642 | 132.984 | 7.63 | 125.797 | 2058.03 | 26.11 | 55.658 | 6.41 | 1.164 | 3.518 | 7563.42 | 1.154 | 97.3 | 75.2 | 1338 | 27.87 | 4916.2 | 1329.6 | 1785.6 | 2246.2 | 1187.5 | 0.59024 | 4.682
2024-12-09 | 14:33 | Data | 0 | 34.796 | 33.756 | 133.164 | 7.64 | 125.887 | 2061.64 | 26.1 | 55.388 | 6.41 | 1.153 | 3.543 | 7572.47 | 1.04 | 97.3 | 75.5 | 1340 | 27.69 | 4922.1 | 1343.5 | 1795.7 | 2260.5 | 1187.5 | 0.59287 | 4.695
2024-12-09 | 14:33 | Data | 0 | 34.911 | 33.54 | 133.164 | 7.63 | 125.842 | 2061.64 | 26.1 | 55.388 | 6.4 | 1.16 | 3.542 | 7563.42 | 1.317 | 97.3 | 75.3 | 1340 | 27.65 | 4916.2 | 1334.4 | 1783.1 | 2254.7 | 1187.5 | 0.59279 | 4.701
2024-12-09 | 14:33 | Data | 0 | 34.735 | 33.628 | 132.984 | 7.64 | 125.797 | 2055.31 | 26.11 | 55.297 | 6.41 | 1.163 | 3.544 | 7581.51 | 1.073 | 97.3 | 75.3 | 1335 | 27.65 | 4928 | 1336.7 | 1777 | 2243.6 | 1187.5 | 0.59971 | 4.707
2024-12-09 | 14:33 | Data | 0 | 34.796 | 33.851 | 133.074 | 7.64 | 125.887 | 2060.74 | 26.11 | 55.297 | 6.41 | 1.168 | 3.529 | 7549.86 | 1.073 | 97.3 | 75.1 | 1340 | 27.6 | 4907.4 | 1335.4 | 1787.6 | 2249.6 | 1187.5 | 0.59207 | 4.698
2024-12-09 | 14:34 | Data | 0 | 34.823 | 33.615 | 132.984 | 7.64 | 125.797 | 2061.64 | 26.11 | 55.297 | 6.41 | 1.164 | 3.523 | 7549.86 | 1.08 | 97.3 | 75.2 | 1340 | 27.65 | 4907.4 | 1319.7 | 1803.2 | 2253 | 1187.5 | 0.58498 | 4.687
2024-12-09 | 14:34 | Data | 0 | 34.789 | 33.642 | 132.984 | 7.64 | 125.797 | 2059.83 | 26.11 | 55.388 | 6.41 | 1.152 | 3.526 | 7554.38 | 1.154 | 97.3 | 75.4 | 1339 | 27.65 | 4910.3 | 1325.8 | 1808.3 | 2262 | 1187.6 | 0.58552 | 4.677
2024-12-09 | 14:34 | Data | 0 | 34.688 | 33.837 | 132.984 | 7.64 | 125.842 | 2062.55 | 26.09 | 55.388 | 6.41 | 1.156 | 3.531 | 7549.86 | 1.127 | 97.3 | 75.3 | 1340 | 27.69 | 4907.4 | 1325.2 | 1792.6 | 2247.5 | 1187.6 | 0.59084 | 4.687
2024-12-09 | 14:34 | Data | 0 | 34.789 | 33.601 | 132.938 | 7.63 | 125.797 | 2058.03 | 26.11 | 55.297 | 6.41 | 1.154 | 3.537 | 7576.99 | 1.242 | 97.3 | 75.4 | 1338 | 27.65 | 4925 | 1332.2 | 1795.7 | 2258.3 | 1187.6 | 0.58809 | 4.691
2024-12-09 | 14:34 | Data | 0 | 34.796 | 33.534 | 132.984 | 7.64 | 125.797 | 2058.93 | 26.1 | 55.297 | 6.4 | 1.159 | 3.534 | 7549.86 | 1.377 | 97.3 | 75.3 | 1339 | 27.74 | 4907.4 | 1336.9 | 1816.1 | 2274.8 | 1187.6 | 0.58632 | 4.692
2024-12-09 | 14:34 | Data | 0 | 34.85 | 33.426 | 132.984 | 7.64 | 125.706 | 2059.83 | 26.09 | 55.207 | 6.4 | 1.153 | 3.529 | 7554.38 | 1.222 | 97.3 | 75.4 | 1339 | 27.6 | 4910.3 | 1333.7 | 1796.6 | 2257.2 | 1187.6 | 0.58914 | 4.682
2024-12-09 | 14:34 | Data | 0 | 35.019 | 33.642 | 132.984 | 7.64 | 125.797 | 2058.93 | 26.1 | 55.297 | 6.4 | 1.148 | 3.53 | 7545.34 | 1.262 | 97.3 | 75.5 | 1338 | 27.65 | 4904.5 | 1321.7 | 1803.3 | 2255.7 | 1187.6 | 0.58414 | 4.678
2024-12-09 | 14:34 | Data | 0 | 34.783 | 33.642 | 132.984 | 7.64 | 125.842 | 2058.93 | 26.11 | 55.297 | 6.4 | 1.162 | 3.537 | 7549.86 | 1.154 | 97.3 | 75.3 | 1338 | 27.65 | 4907.4 | 1350.7 | 1800.2 | 2269.4 | 1187.6 | 0.59379 | 4.698
2024-12-09 | 14:34 | Data | 0 | 34.796 | 33.419 | 132.893 | 7.64 | 125.706 | 2058.93 | 26.11 | 55.388 | 6.41 | 1.16 | 3.524 | 7549.86 | 1.161 | 97.3 | 75.2 | 1338 | 27.69 | 4907.4 | 1325.6 | 1802.8 | 2259 | 1187.6 | 0.58448 | 4.685
2024-12-09 | 14:34 | Data | 0 | 34.884 | 33.75 | 132.984 | 7.63 | 125.842 | 2058.93 | 26.1 | 55.297 | 6.41 | 1.157 | 3.502 | 7558.9 | 1.1 | 97.3 | 75.2 | 1339 | 27.65 | 4913.3 | 1329.5 | 1803.1 | 2259.2 | 1187.6 | 0.58516 | 4.656
2024-12-09 | 14:34 | Data | 0 | 34.965 | 33.75 | 133.074 | 7.64 | 125.842 | 2058.93 | 26.11 | 55.297 | 6.4 | 1.157 | 3.523 | 7554.38 | 1.154 | 97.3 | 75.3 | 1338 | 27.65 | 4910.3 | 1351.9 | 1823.2 | 2287.6 | 1187.6 | 0.5902 | 4.681
2024-12-09 | 14:34 | Data | 0 | 34.627 | 33.419 | 133.074 | 7.64 | 125.842 | 2057.12 | 26.12 | 55.388 | 6.4 | 1.151 | 3.542 | 7567.95 | 1.154 | 97.3 | 75.5 | 1338 | 27.65 | 4919.2 | 1338.3 | 1825.7 | 2276.2 | 1187.6 | 0.58492 | 4.692
2024-12-09 | 14:34 | Data | 0 | 34.796 | 33.642 | 132.893 | 7.63 | 125.797 | 2161.06 | 26.1 | 55.388 | 6.41 | 1.147 | 3.541 | 7567.95 | 1.154 | 97.4 | 75.5 | 1405 | 27.65 | 4919.2 | 1340.8 | 1799.2 | 2259.3 | 1187.6 | 0.58735 | 4.688
2024-12-09 | 14:34 | Data | 0 | 34.567 | 33.412 | 132.938 | 7.64 | 125.797 | 2086.04 | 26.11 | 55.297 | 6.41 | 1.162 | 3.516 | 7563.42 | 1.33 | 97.3 | 75.2 | 1354 | 27.69 | 4916.2 | 1334.8 | 1807.5 | 2267.1 | 1187.6 | 0.58753 | 4.678
2024-12-09 | 14:34 | Data | 0 | 34.573 | 33.588 | 133.074 | 7.64 | 125.706 | 2061.64 | 26.1 | 55.388 | 6.41 | 1.166 | 3.518 | 7549.86 | 1.04 | 97.3 | 75.1 | 1340 | 27.69 | 4907.4 | 1344.4 | 1807.1 | 2269.1 | 1187.6 | 0.59153 | 4.684
2024-12-09 | 14:34 | Data | 0 | 34.681 | 33.615 | 132.938 | 7.63 | 125.661 | 2061.64 | 26.1 | 55.297 | 6.41 | 1.159 | 3.547 | 7531.77 | 1.195 | 97.3 | 75.4 | 1340 | 27.65 | 4895.6 | 1331.5 | 1800 | 2257.9 | 1187.6 | 0.589 | 4.707
2024-12-09 | 14:34 | Data | 0 | 34.999 | 33.756 | 133.074 | 7.64 | 125.842 | 2060.74 | 26.11 | 55.388 | 6.41 | 1.153 | 3.542 | 7536.29 | 1.154 | 97.3 | 75.4 | 1339 | 27.69 | 4898.6 | 1335.2 | 1800.2 | 2259 | 1187.6 | 0.58964 | 4.697
2024-12-09 | 14:35 | Data | 0 | 34.796 | 33.817 | 132.984 | 7.64 | 125.842 | 2061.64 | 26.1 | 55.388 | 6.41 | 1.161 | 3.535 | 7531.77 | 1.094 | 97.3 | 75.3 | 1340 | 27.65 | 4895.6 | 1331.5 | 1802.2 | 2259.6 | 1187.6 | 0.58774 | 4.697
2024-12-09 | 14:35 | Data | 0 | 34.735 | 33.642 | 132.893 | 7.64 | 125.661 | 2067.97 | 26.11 | 55.297 | 6.41 | 1.159 | 3.526 | 7545.34 | 1.242 | 97.3 | 75.3 | 1344 | 27.65 | 4904.5 | 1340.8 | 1790.8 | 2254.9 | 1187.6 | 0.59351 | 4.685
2024-12-09 | 14:35 | Data | 0 | 34.796 | 33.527 | 132.893 | 7.64 | 125.797 | 2061.64 | 26.11 | 55.297 | 6.4 | 1.155 | 3.528 | 7531.77 | 1.154 | 97.3 | 75.3 | 1340 | 27.69 | 4895.6 | 1348.3 | 1788.4 | 2258.2 | 1187.6 | 0.59565 | 4.683
2024-12-09 | 14:35 | Data | 0 | 34.573 | 33.419 | 132.893 | 7.63 | 125.842 | 2061.64 | 26.1 | 55.297 | 6.4 | 1.151 | 3.523 | 7531.77 | 1.148 | 97.3 | 75.4 | 1340 | 27.69 | 4895.6 | 1320.6 | 1796.6 | 2249.7 | 1187.6 | 0.58425 | 4.675
2024-12-09 | 14:35 | Data | 0 | 34.384 | 33.615 | 132.893 | 7.63 | 125.706 | 2061.64 | 26.1 | 55.297 | 6.41 | 1.151 | 3.555 | 7531.77 | 0.898 | 97.3 | 75.5 | 1340 | 27.65 | 4895.6 | 1323.2 | 1771.3 | 2232.2 | 1187.6 | 0.59062 | 4.705
2024-12-09 | 14:35 | Data | 0 | 34.999 | 33.689 | 132.938 | 7.63 | 125.797 | 2061.64 | 26.1 | 55.388 | 6.4 | 1.159 | 3.504 | 7531.77 | 1.161 | 97.3 | 75.2 | 1340 | 27.65 | 4895.6 | 1329.4 | 1788 | 2248.7 | 1187.6 | 0.58911 | 4.663
2024-12-09 | 14:35 | Data | 0 | 34.567 | 33.608 | 132.893 | 7.64 | 125.661 | 2056.22 | 26.11 | 55.297 | 6.41 | 1.154 | 3.51 | 7536.29 | 1.06 | 97.3 | 75.3 | 1337 | 27.65 | 4898.6 | 1345.6 | 1785.1 | 2252.1 | 1187.6 | 0.59538 | 4.664
2024-12-09 | 14:35 | Data | 0 | 34.769 | 33.439 | 132.984 | 7.64 | 125.706 | 2061.64 | 26.11 | 55.297 | 6.41 | 1.161 | 3.529 | 7531.77 | 1.148 | 97.3 | 75.2 | 1340 | 27.65 | 4895.6 | 1333 | 1796.7 | 2257.3 | 1187.6 | 0.58973 | 4.69
2024-12-09 | 14:35 | Data | 0 | 34.573 | 33.588 | 132.893 | 7.64 | 125.706 | 2060.74 | 26.11 | 55.478 | 6.41 | 1.157 | 3.528 | 7536.29 | 1.269 | 97.3 | 75.3 | 1340 | 27.69 | 4898.6 | 1321.7 | 1792.7 | 2247.1 | 1187.6 | 0.59154 | 4.686
2024-12-09 | 14:35 | Data | 0 | 34.681 | 33.412 | 132.938 | 7.64 | 125.661 | 2060.74 | 26.1 | 55.297 | 6.41 | 1.146 | 3.537 | 7527.25 | 1.161 | 97.3 | 75.5 | 1341 | 27.65 | 4892.7 | 1316.4 | 1785.3 | 2238.2 | 1187.6 | 0.5861 | 4.684
2024-12-09 | 14:35 | Data | 0 | 34.573 | 33.635 | 132.938 | 7.64 | 125.661 | 2065.26 | 26.1 | 55.297 | 6.41 | 1.153 | 3.527 | 7549.86 | 1.08 | 97.3 | 75.4 | 1343 | 27.65 | 4907.4 | 1333.8 | 1789.3 | 2249.9 | 1187.6 | 0.59147 | 4.679
2024-12-09 | 14:35 | Data | 0 | 34.594 | 33.588 | 132.848 | 7.63 | 125.797 | 2064.35 | 26.1 | 55.297 | 6.4 | 1.167 | 3.531 | 7549.86 | 1.215 | 97.3 | 75.2 | 1342 | 27.69 | 4907.4 | 1341.6 | 1772.1 | 2241.1 | 1187.6 | 0.5973 | 4.697
2024-12-09 | 14:35 | Data | 0 | 34.486 | 33.527 | 132.848 | 7.64 | 125.661 | 2064.35 | 26.12 | 55.026 | 6.4 | 1.166 | 3.543 | 7527.25 | 1.141 | 97.3 | 75.2 | 1342 | 27.51 | 4892.7 | 1339.3 | 1771.5 | 2238.4 | 1187.6 | 0.59543 | 4.709
2024-12-09 | 14:35 | Data | 0 | 34.621 | 33.432 | 132.893 | 7.63 | 125.706 | 2061.64 | 26.1 | 55.207 | 6.41 | 1.161 | 3.564 | 7531.77 | 1.323 | 97.3 | 75.4 | 1341 | 27.56 | 4895.6 | 1347.3 | 1795.6 | 2263 | 1187.6 | 0.59734 | 4.724
2024-12-09 | 14:35 | Data | 0 | 34.519 | 33.412 | 132.938 | 7.64 | 125.797 | 2065.26 | 26.11 | 55.026 | 6.41 | 1.159 | 3.544 | 7513.68 | 1.242 | 97.3 | 75.4 | 1342 | 27.51 | 4883.9 | 1336.6 | 1794.4 | 2255.6 | 1187.6 | 0.59086 | 4.702
2024-12-09 | 14:35 | Data | 0 | 34.479 | 33.412 | 132.848 | 7.64 | 125.616 | 2060.74 | 26.11 | 55.026 | 6.41 | 1.163 | 3.502 | 7531.77 | 1.262 | 97.3 | 75.1 | 1340 | 27.56 | 4895.6 | 1328.5 | 1810.8 | 2267 | 1187.6 | 0.58456 | 4.665
2024-12-09 | 14:35 | Data | 0 | 34.567 | 33.729 | 132.938 | 7.64 | 125.706 | 2061.64 | 26.11 | 55.388 | 6.41 | 1.168 | 3.514 | 7527.25 | 1.154 | 97.3 | 75 | 1340 | 27.69 | 4892.7 | 1344.5 | 1802.8 | 2269 | 1187.6 | 0.5921 | 4.683
2024-12-09 | 14:36 | Data | 0 | 34.783 | 33.338 | 132.938 | 7.64 | 125.706 | 2061.64 | 26.11 | 54.936 | 6.4 | 1.172 | 3.529 | 7531.77 | 1.229 | 97.3 | 75.1 | 1340 | 27.51 | 4895.6 | 1331.5 | 1804.5 | 2261.3 | 1187.6 | 0.5878 | 4.701
2024-12-09 | 14:36 | Data | 0 | 34.567 | 33.797 | 132.893 | 7.64 | 125.661 | 2060.74 | 26.11 | 55.026 | 6.41 | 1.169 | 3.531 | 7549.86 | 1.04 | 97.3 | 75.1 | 1339 | 27.51 | 4907.4 | 1333.2 | 1801.3 | 2261.2 | 1187.6 | 0.58834 | 4.701
2024-12-09 | 14:36 | Data | 0 | 34.681 | 33.52 | 132.938 | 7.64 | 125.797 | 2060.74 | 26.11 | 55.207 | 6.41 | 1.16 | 3.534 | 7567.95 | 1.134 | 97.3 | 75.3 | 1339 | 27.65 | 4919.2 | 1342.6 | 1810.1 | 2271.4 | 1187.6 | 0.58918 | 4.694
2024-12-09 | 14:36 | Data | 0 | 34.796 | 33.426 | 132.848 | 7.63 | 125.706 | 2061.64 | 26.1 | 55.117 | 6.4 | 1.154 | 3.517 | 7563.42 | 1.215 | 97.3 | 75.3 | 1340 | 27.56 | 4916.2 | 1326.3 | 1791.1 | 2237.6 | 1187.6 | 0.59063 | 4.671
2024-12-09 | 14:36 | Data | 0 | 34.837 | 33.426 | 132.893 | 7.64 | 125.706 | 2062.55 | 26.1 | 55.388 | 6.41 | 1.15 | 3.523 | 7554.38 | 1.188 | 97.3 | 75.4 | 1342 | 27.65 | 4910.3 | 1345 | 1800.5 | 2264.2 | 1187.6 | 0.59205 | 4.672
2024-12-09 | 14:36 | Data | 0 | 34.796 | 33.588 | 132.893 | 7.63 | 125.706 | 2061.64 | 26.1 | 55.026 | 6.41 | 1.16 | 3.527 | 7576.99 | 1.033 | 97.3 | 75.2 | 1340 | 27.51 | 4925 | 1336.2 | 1800.7 | 2260.3 | 1187.6 | 0.58882 | 4.687
2024-12-09 | 14:36 | Data | 0 | 34.229 | 32.73 | 143.161 | 7.64 | 135.016 | 2062.55 | 26.11 | 55.117 | 6.4 | 1.159 | 3.533 | 7567.95 | 1.371 | 97.3 | 75.3 | 1340 | 27.51 | 4919.2 | 1392.3 | 1826 | 2315.5 | 1187.6 | 0.59926 | 4.691
2024-12-09 | 14:36 | Data | 0 | 33.297 | 31.988 | 160.802 | 7.64 | 151.015 | 2058.93 | 26.11 | 55.297 | 6.4 | 1.189 | 3.789 | 7576.99 | 1.614 | 97.3 | 76.1 | 1338 | 27.69 | 4925 | 1551.3 | 1984.3 | 2552.9 | 1187.6 | 0.61328 | 4.976
2024-12-09 | 14:36 | Data | 0 | 32.838 | 30.705 | 176.361 | 7.63 | 165.296 | 2058.93 | 26.1 | 55.929 | 6.41 | 1.256 | 4.206 | 7576.99 | 1.985 | 97.3 | 77 | 1338 | 27.96 | 4925 | 1702.5 | 2101.8 | 2719 | 1187.6 | 0.6267 | 5.458
2024-12-09 | 14:36 | Data | 0 | 32.028 | 29.76 | 189.117 | 7.63 | 177.001 | 2059.83 | 26.11 | 55.749 | 6.4 | 1.308 | 4.543 | 7545.34 | 2.174 | 97.3 | 77.6 | 1339 | 27.87 | 4904.5 | 1855.6 | 2242.9 | 2922.5 | 1187.6 | 0.63334 | 5.851
2024-12-09 | 14:36 | Data | 0 | 31.745 | 29.321 | 200.018 | 7.64 | 187.079 | 2058.93 | 26.1 | 54.485 | 6.4 | 1.352 | 4.841 | 7536.29 | 2.302 | 97.3 | 78.2 | 1338 | 27.29 | 4898.6 | 1947.9 | 2365.1 | 3078.5 | 1187.6 | 0.62608 | 6.193
2024-12-09 | 14:36 | Data | 0 | 31.542 | 28.889 | 208.748 | 7.64 | 194.852 | 2058.93 | 26.09 | 52.769 | 6.39 | 1.389 | 5.071 | 7563.42 | 2.599 | 97.4 | 78.5 | 1338 | 26.34 | 4916.2 | 2052.3 | 2455.5 | 3212.5 | 1187.6 | 0.63468 | 6.459
2024-12-09 | 14:36 | Data | 0 | 31.333 | 28.133 | 215.533 | 7.63 | 201.18 | 2057.12 | 26.08 | 50.603 | 6.37 | 1.41 | 5.271 | 7608.65 | 2.511 | 97.5 | 78.9 | 1337 | 25.26 | 4945.6 | 2153.3 | 2567.5 | 3360.6 | 1187.6 | 0.63791 | 6.679
2024-12-09 | 14:36 | Data | 0 | 31.319 | 28.139 | 220.78 | 7.64 | 206.06 | 2054.41 | 26.05 | 48.436 | 6.34 | 1.428 | 5.44 | 7671.96 | 2.788 | 97.6 | 79.2 | 1335 | 24.17 | 4986.8 | 2194.1 | 2644.9 | 3446.8 | 1187.6 | 0.6357 | 6.868
2024-12-09 | 14:36 | Data | 0 | 30.928 | 27.694 | 224.851 | 7.64 | 209.676 | 2050.8 | 26.07 | 46.721 | 6.33 | 1.453 | 5.535 | 7762.4 | 2.991 | 97.7 | 79.2 | 1334 | 23.36 | 5045.6 | 2251.2 | 2700.7 | 3509 | 1187.6 | 0.63171 | 6.99
2024-12-09 | 14:36 | Data | 0 | 30.428 | 27.606 | 228.153 | 7.64 | 212.84 | 2048.99 | 26.02 | 45.366 | 6.31 | 1.463 | 5.573 | 7861.89 | 2.869 | 97.8 | 79.2 | 1332 | 22.68 | 5110.2 | 2280.6 | 2757.3 | 3587.2 | 1187.6 | 0.63397 | 7.036
2024-12-09 | 14:36 | Data | 0 | 29.982 | 27.194 | 231.138 | 7.64 | 215.325 | 2049.89 | 26.02 | 44.283 | 6.3 | 1.46 | 5.678 | 7943.29 | 2.755 | 97.8 | 79.6 | 1333 | 22.05 | 5163.1 | 2324.9 | 2814 | 3658.9 | 1187.6 | 0.63366 | 7.136
2024-12-09 | 14:36 | Data | 0 | 30.516 | 27.856 | 232.993 | 7.64 | 217.314 | 2051.7 | 26.02 | 43.109 | 6.28 | 1.468 | 5.757 | 8020.17 | 2.856 | 97.9 | 79.7 | 1334 | 21.6 | 5213.1 | 3431.6 | 3336.5 | 4886.4 | 1187.6 | 0.68755 | 7.225
2024-12-09 | 14:37 | Data | 0 | 30.361 | 27.268 | 234.35 | 7.64 | 218.579 | 2050.8 | 26.02 | 42.477 | 6.27 | 1.478 | 5.751 | 8083.48 | 2.822 | 97.9 | 79.6 | 1333 | 21.28 | 5254.3 | 3457.2 | 3353 | 4916.3 | 1187.6 | 0.68879 | 7.229
2024-12-09 | 14:37 | Data | 0 | 30.192 | 27.167 | 235.797 | 7.64 | 219.799 | 2050.8 | 26.02 | 41.936 | 6.27 | 1.479 | 5.778 | 8155.84 | 3.099 | 98 | 79.6 | 1333 | 20.97 | 5301.3 | 3478 | 3348.6 | 4926.9 | 1187.6 | 0.69103 | 7.257
2024-12-09 | 14:37 | Data | 0 | 30.084 | 26.971 | 236.43 | 7.64 | 220.522 | 2053.51 | 26.02 | 41.575 | 6.26 | 1.484 | 5.822 | 8205.58 | 2.998 | 98 | 79.7 | 1335 | 20.79 | 5333.6 | 3454.5 | 3367.2 | 4926.8 | 1187.6 | 0.68564 | 7.307
2024-12-09 | 14:37 | Data | 0 | 29.989 | 26.965 | 236.385 | 7.64 | 220.432 | 2053.51 | 26.02 | 41.304 | 6.26 | 1.487 | 5.84 | 8300.55 | 3.011 | 98 | 79.7 | 1334 | 20.65 | 5395.4 | 3483.7 | 3382.7 | 4950.9 | 1187.6 | 0.68913 | 7.327
2024-12-09 | 14:37 | Data | 0 | 30.401 | 27.106 | 236.475 | 7.64 | 220.568 | 2051.7 | 26.02 | 41.033 | 6.25 | 1.492 | 5.832 | 8354.81 | 3.133 | 98 | 79.7 | 1334 | 20.47 | 5430.6 | 3484.4 | 3390.5 | 4959.5 | 1187.6 | 0.68836 | 7.322
2024-12-09 | 14:37 | Data | 0 | 30.097 | 27.187 | 236.43 | 7.63 | 220.522 | 2056.22 | 26.01 | 41.033 | 6.25 | 1.481 | 5.826 | 8395.51 | 2.849 | 98 | 79.7 | 1337 | 20.47 | 5457.1 | 3489.7 | 3380.7 | 4954.5 | 1187.6 | 0.68893 | 7.307
2024-12-09 | 14:37 | Data | 0 | 29.982 | 26.796 | 236.475 | 7.64 | 220.522 | 2057.12 | 26.01 | 41.033 | 6.25 | 1.493 | 5.854 | 8463.35 | 2.977 | 98 | 79.7 | 1337 | 20.43 | 5501.2 | 3473.1 | 3408.5 | 4965 | 1187.6 | 0.6838 | 7.347
2024-12-09 | 14:37 | Data | 0 | 30.3 | 27.154 | 236.34 | 7.64 | 220.477 | 2056.22 | 26 | 40.762 | 6.25 | 1.487 | 5.825 | 8495 | 2.944 | 98 | 79.7 | 1337 | 20.38 | 5521.8 | 3477.8 | 3379.6 | 4949.5 | 1187.7 | 0.68715 | 7.312
2024-12-09 | 14:37 | Data | 0 | 30.063 | 27.349 | 236.475 | 7.63 | 220.432 | 2058.93 | 26 | 40.762 | 6.24 | 1.489 | 5.833 | 8549.27 | 2.89 | 98 | 79.7 | 1338 | 20.38 | 5557 | 3489.6 | 3390.9 | 4960.9 | 1187.7 | 0.68726 | 7.321
2024-12-09 | 14:37 | Data | 0 | 30.03 | 27.181 | 236.43 | 7.63 | 220.477 | 2059.83 | 25.99 | 41.033 | 6.24 | 1.486 | 5.846 | 8585.45 | 2.822 | 98 | 79.7 | 1338 | 20.52 | 5580.5 | 3464.4 | 3395.7 | 4949.9 | 1187.7 | 0.68452 | 7.333
2024-12-09 | 14:37 | Data | 0 | 30.455 | 27.086 | 236.611 | 7.64 | 220.522 | 2061.64 | 26 | 40.943 | 6.25 | 1.486 | 5.829 | 8608.06 | 3.058 | 98 | 79.7 | 1339 | 20.52 | 5595.2 | 3466 | 3402.6 | 4951.4 | 1187.7 | 0.68485 | 7.315
2024-12-09 | 14:37 | Data | 0 | 30.178 | 26.971 | 236.385 | 7.63 | 220.477 | 2061.64 | 26.01 | 40.943 | 6.25 | 1.481 | 5.805 | 8608.06 | 3.207 | 98 | 79.7 | 1340 | 20.47 | 5595.2 | 3457.3 | 3387.5 | 4934.2 | 1187.7 | 0.68585 | 7.286
2024-12-09 | 14:37 | Data | 0 | 30.036 | 26.951 | 236.34 | 7.64 | 220.522 | 2060.74 | 26 | 41.033 | 6.25 | 1.494 | 5.838 | 8635.19 | 2.842 | 98 | 79.6 | 1339 | 20.47 | 5612.9 | 3487.4 | 3385 | 4957.1 | 1187.7 | 0.68814 | 7.333
2024-12-09 | 14:37 | Data | 0 | 29.861 | 27.187 | 236.521 | 7.64 | 220.613 | 2061.64 | 26 | 40.852 | 6.24 | 1.49 | 5.812 | 8648.76 | 2.93 | 98 | 79.6 | 1340 | 20.47 | 5621.7 | 3469.6 | 3382.2 | 4948 | 1187.7 | 0.68631 | 7.301
2024-12-09 | 14:37 | Data | 0 | 30.293 | 27.194 | 236.566 | 7.63 | 220.522 | 2062.55 | 26 | 41.213 | 6.24 | 1.501 | 5.807 | 8666.85 | 2.998 | 98 | 79.4 | 1341 | 20.7 | 5633.5 | 3480.7 | 3365.8 | 4943.9 | 1187.7 | 0.6894 | 7.309
2024-12-09 | 14:37 | Data | 0 | 29.841 | 26.857 | 236.702 | 7.63 | 220.432 | 2062.55 | 26 | 41.213 | 6.25 | 1.5 | 5.81 | 8716.59 | 3.011 | 98 | 79.5 | 1342 | 20.61 | 5665.8 | 3464.9 | 3373.6 | 4936.6 | 1187.7 | 0.68908 | 7.309
2024-12-09 | 14:37 | Data | 0 | 30.124 | 26.971 | 237.471 | 7.63 | 221.381 | 2066.16 | 26.01 | 41.213 | 6.24 | 1.491 | 5.773 | 8725.64 | 3.018 | 98 | 79.5 | 1343 | 20.65 | 5671.7 | 3495.9 | 3375.6 | 4954.4 | 1187.7 | 0.69172 | 7.264
2024-12-09 | 14:38 | Data | 0 | 30.462 | 27.329 | 237.968 | 7.64 | 221.743 | 2064.35 | 26 | 41.213 | 6.24 | 1.493 | 5.834 | 8784.42 | 3.025 | 98 | 79.6 | 1342 | 20.65 | 5709.9 | 3494.2 | 3423.1 | 4972.7 | 1187.7 | 0.68531 | 7.328
2024-12-09 | 14:38 | Data | 0 | 30.009 | 26.965 | 237.832 | 7.64 | 221.743 | 2065.26 | 26 | 41.213 | 6.25 | 1.495 | 5.858 | 8788.95 | 2.998 | 98 | 79.7 | 1342 | 20.56 | 5712.8 | 3499.3 | 3406.1 | 4974.7 | 1187.7 | 0.68703 | 7.352
2024-12-09 | 14:38 | Data | 0 | 30.07 | 27.079 | 237.787 | 7.64 | 221.878 | 2065.26 | 26.03 | 41.123 | 6.25 | 1.498 | 5.857 | 8834.17 | 2.984 | 98 | 79.6 | 1342 | 20.61 | 5742.2 | 3501.6 | 3418 | 4990.2 | 1187.7 | 0.68711 | 7.355
2024-12-09 | 14:38 | Data | 0 | 30.32 | 26.978 | 237.787 | 7.63 | 221.833 | 2067.97 | 26 | 41.394 | 6.25 | 1.497 | 5.828 | 8865.83 | 3.254 | 98 | 79.6 | 1344 | 20.7 | 5762.8 | 3496.4 | 3436.6 | 5002.8 | 1187.7 | 0.68423 | 7.324
2024-12-09 | 14:38 | Data | 0 | 30.009 | 26.971 | 237.878 | 7.63 | 221.743 | 2067.97 | 26 | 41.304 | 6.24 | 1.505 | 5.849 | 8879.39 | 2.863 | 98 | 79.5 | 1344 | 20.65 | 5771.6 | 3480.9 | 3452.7 | 4999.8 | 1187.7 | 0.68131 | 7.354
2024-12-09 | 14:38 | Data | 0 | 29.881 | 26.789 | 237.923 | 7.64 | 221.833 | 2065.26 | 26 | 41.304 | 6.25 | 1.487 | 5.855 | 8902 | 2.896 | 98 | 79.8 | 1342 | 20.65 | 5786.3 | 3478.6 | 3438.3 | 4987.4 | 1187.7 | 0.68231 | 7.342
2024-12-09 | 14:38 | Data | 0 | 30.239 | 26.857 | 237.968 | 7.64 | 221.878 | 2061.64 | 26.01 | 41.304 | 6.25 | 1.485 | 5.826 | 8883.91 | 3.052 | 98 | 79.7 | 1340 | 20.61 | 5774.5 | 3488.7 | 3440.5 | 4995.1 | 1187.7 | 0.68407 | 7.31
2024-12-09 | 14:38 | Data | 0 | 30.34 | 27.309 | 237.832 | 7.63 | 221.878 | 2060.74 | 26.01 | 41.304 | 6.24 | 1.498 | 5.842 | 8874.87 | 2.971 | 98 | 79.6 | 1341 | 20.7 | 5768.7 | 3500.8 | 3423.2 | 4992.1 | 1187.7 | 0.68689 | 7.336
2024-12-09 | 14:38 | Data | 0 | 30.394 | 27.194 | 237.878 | 7.63 | 221.878 | 2058.93 | 26.01 | 41.304 | 6.24 | 1.484 | 5.847 | 8883.91 | 3.214 | 98 | 79.8 | 1338 | 20.65 | 5774.5 | 3496.8 | 3437.6 | 4998.7 | 1187.7 | 0.68497 | 7.329
2024-12-09 | 14:38 | Data | 0 | 30.07 | 27.302 | 237.878 | 7.63 | 221.743 | 2056.22 | 26 | 41.213 | 6.24 | 1.49 | 5.838 | 8883.91 | 2.964 | 98 | 79.7 | 1337 | 20.65 | 5774.5 | 3477.3 | 3407.8 | 4968.8 | 1187.7 | 0.68656 | 7.328
2024-12-09 | 14:38 | Data | 0 | 29.955 | 27.187 | 237.878 | 7.63 | 221.652 | 2057.12 | 26 | 41.304 | 6.24 | 1.5 | 5.815 | 8897.48 | 2.991 | 98 | 79.5 | 1337 | 20.65 | 5783.4 | 3483.7 | 3408 | 4971.7 | 1187.7 | 0.68597 | 7.314
2024-12-09 | 14:38 | Data | 0 | 29.955 | 27.214 | 237.832 | 7.64 | 221.743 | 2056.22 | 26 | 41.484 | 6.24 | 1.498 | 5.818 | 8897.48 | 2.876 | 98 | 79.5 | 1337 | 20.74 | 5783.4 | 3471 | 3409.5 | 4964.3 | 1187.7 | 0.68389 | 7.317
2024-12-09 | 14:38 | Data | 0 | 30.198 | 27.39 | 237.968 | 7.63 | 221.969 | 2057.12 | 26 | 41.484 | 6.24 | 1.5 | 5.833 | 8892.96 | 2.91 | 98 | 79.5 | 1337 | 20.74 | 5780.4 | 3485.3 | 3414.5 | 4978.6 | 1187.7 | 0.68431 | 7.333
2024-12-09 | 14:38 | Data | 0 | 29.955 | 26.735 | 237.787 | 7.63 | 221.697 | 2057.12 | 26.01 | 41.304 | 6.25 | 1.499 | 5.8 | 8883.91 | 3.173 | 98 | 79.5 | 1337 | 20.61 | 5774.5 | 3498.4 | 3415.4 | 4982.9 | 1187.7 | 0.68687 | 7.3
2024-12-09 | 14:38 | Data | 0 | 30.171 | 26.965 | 238.42 | 7.63 | 222.421 | 2056.22 | 26 | 41.213 | 6.24 | 1.495 | 5.826 | 8888.44 | 3.038 | 98 | 79.6 | 1337 | 20.65 | 5777.5 | 3494.5 | 3450.9 | 5004.5 | 1187.7 | 0.6833 | 7.32
2024-12-09 | 14:38 | Data | 0 | 30.3 | 26.998 | 238.782 | 7.63 | 222.647 | 2056.22 | 26.01 | 41.213 | 6.24 | 1.484 | 5.865 | 8888.44 | 3.099 | 98 | 79.8 | 1337 | 20.65 | 5777.5 | 3498.8 | 3491 | 5037.9 | 1187.7 | 0.68006 | 7.349
2024-12-09 | 14:38 | Data | 0 | 30.293 | 26.762 | 238.692 | 7.63 | 222.375 | 2057.12 | 26.01 | 41.213 | 6.24 | 1.481 | 5.848 | 8911.05 | 2.89 | 98 | 79.8 | 1337 | 20.65 | 5792.2 | 3479.7 | 3448.8 | 4995.5 | 1187.7 | 0.68191 | 7.328
2024-12-09 | 14:38 | Data | 0 | 29.982 | 27.167 | 238.511 | 7.63 | 222.421 | 2055.31 | 26 | 41.304 | 6.24 | 1.497 | 5.853 | 8911.05 | 2.991 | 98 | 79.6 | 1337 | 20.65 | 5792.2 | 3507.2 | 3435 | 5005.4 | 1187.7 | 0.68581 | 7.35
2024-12-09 | 14:39 | Data | 0 | 30.104 | 27.1 | 238.692 | 7.63 | 222.466 | 2058.03 | 26 | 41.304 | 6.24 | 1.499 | 5.834 | 8911.05 | 2.876 | 98 | 79.6 | 1338 | 20.61 | 5792.2 | 3517.6 | 3436.6 | 5009.6 | 1187.7 | 0.68676 | 7.332
2024-12-09 | 14:39 | Data | 0 | 29.901 | 26.951 | 238.33 | 7.63 | 222.375 | 2058.93 | 25.99 | 41.304 | 6.24 | 1.505 | 5.872 | 8892.96 | 3.038 | 98 | 79.6 | 1338 | 20.61 | 5780.4 | 3487.8 | 3401.1 | 4967.3 | 1187.7 | 0.68875 | 7.376
2024-12-09 | 14:39 | Data | 0 | 30.185 | 26.971 | 238.737 | 7.63 | 222.511 | 2058.93 | 26.01 | 41.213 | 6.24 | 1.505 | 5.857 | 8879.39 | 3.207 | 98 | 79.6 | 1338 | 20.65 | 5771.6 | 3511.2 | 3410.9 | 4994.1 | 1187.7 | 0.69095 | 7.362
2024-12-09 | 14:39 | Data | 0 | 30.212 | 27.194 | 238.873 | 7.63 | 222.466 | 2056.22 | 26.01 | 41.213 | 6.25 | 1.497 | 5.855 | 8870.35 | 2.991 | 98 | 79.6 | 1337 | 20.65 | 5765.7 | 3493.1 | 3398.2 | 4971.3 | 1187.8 | 0.68738 | 7.352
2024-12-09 | 14:39 | Data | 0 | 30.158 | 27.019 | 238.782 | 7.63 | 222.466 | 2061.64 | 26 | 41.304 | 6.25 | 1.49 | 5.855 | 8861.3 | 2.991 | 98 | 79.7 | 1340 | 20.65 | 5759.8 | 3495.1 | 3423.8 | 4987.2 | 1187.8 | 0.68592 | 7.347
2024-12-09 | 14:39 | Data | 0 | 30.178 | 26.877 | 238.556 | 7.63 | 222.511 | 2062.55 | 26 | 41.304 | 6.24 | 1.498 | 5.866 | 8856.78 | 3.193 | 98 | 79.7 | 1340 | 20.56 | 5756.9 | 3505.4 | 3466.8 | 5026.5 | 1187.8 | 0.68312 | 7.363
2024-12-09 | 14:39 | Data | 0 | 30.225 | 27.093 | 238.375 | 7.63 | 222.285 | 2060.74 | 26 | 41.304 | 6.24 | 1.492 | 5.884 | 8847.74 | 3.207 | 98 | 79.8 | 1340 | 20.65 | 5751 | 3503.1 | 3487.9 | 5040.1 | 1187.8 | 0.68007 | 7.376
2024-12-09 | 14:39 | Data | 0 | 30.185 | 27.167 | 238.647 | 7.63 | 222.421 | 2062.55 | 26 | 41.213 | 6.25 | 1.494 | 5.855 | 8847.74 | 3.038 | 98 | 79.7 | 1340 | 20.56 | 5751 | 3503.4 | 3469.9 | 5025.7 | 1187.8 | 0.68154 | 7.348
2024-12-09 | 14:39 | Data | 0 | 30.043 | 27.295 | 238.556 | 7.63 | 222.466 | 2065.26 | 25.99 | 41.213 | 6.24 | 1.49 | 5.812 | 8838.69 | 3.106 | 98 | 79.6 | 1343 | 20.65 | 5745.1 | 3510.4 | 3492.3 | 5048.1 | 1187.8 | 0.67993 | 7.301
2024-12-09 | 14:39 | Data | 0 | 29.847 | 27.376 | 238.466 | 7.63 | 222.511 | 2067.97 | 26.02 | 41.213 | 6.25 | 1.5 | 5.829 | 8883.91 | 2.964 | 98 | 79.5 | 1344 | 20.61 | 5774.5 | 3501.9 | 3478.9 | 5034 | 1187.8 | 0.68078 | 7.329
2024-12-09 | 14:39 | Data | 0 | 30.192 | 27.322 | 238.647 | 7.63 | 222.601 | 2070.68 | 25.99 | 41.304 | 6.24 | 1.492 | 5.834 | 8883.91 | 2.944 | 98 | 79.6 | 1345 | 20.7 | 5774.5 | 3506.8 | 3468.9 | 5029.6 | 1187.8 | 0.68236 | 7.329
2024-12-09 | 14:39 | Data | 0 | 30.077 | 27.019 | 238.556 | 7.63 | 222.511 | 2070.68 | 26.01 | 41.304 | 6.24 | 1.485 | 5.859 | 8897.48 | 2.89 | 98 | 79.8 | 1346 | 20.65 | 5783.4 | 3502.7 | 3466.9 | 5025.3 | 1187.8 | 0.68177 | 7.343
2024-12-09 | 14:39 | Data | 0 | 29.577 | 26.735 | 238.601 | 7.63 | 222.466 | 2070.68 | 26.02 | 41.304 | 6.25 | 1.496 | 5.873 | 8476.91 | 2.768 | 98 | 79.7 | 1345 | 20.65 | 5510 | 3518.4 | 3436.7 | 5015.1 | 1187.8 | 0.68683 | 7.368
2024-12-09 | 14:39 | Data | 0 | 29.901 | 27.376 | 238.556 | 7.63 | 222.511 | 2069.78 | 26 | 41.304 | 6.25 | 1.49 | 5.858 | 8816.08 | 3.119 | 98 | 79.7 | 1345 | 20.65 | 5730.5 | 3503 | 3431.1 | 5000.4 | 1187.8 | 0.68514 | 7.35
2024-12-09 | 14:39 | Data | 0 | 30.496 | 27.201 | 238.511 | 7.63 | 222.601 | 2067.97 | 26.01 | 41.304 | 6.25 | 1.494 | 5.868 | 8825.13 | 2.991 | 98 | 79.7 | 1344 | 20.65 | 5736.3 | 3510.6 | 3414.7 | 4995.4 | 1187.8 | 0.68773 | 7.361
2024-12-09 | 14:39 | Data | 0 | 30.212 | 27.221 | 238.556 | 7.63 | 222.375 | 2067.97 | 26.05 | 41.304 | 6.24 | 1.489 | 5.881 | 8829.65 | 2.95 | 98 | 79.8 | 1344 | 20.56 | 5739.3 | 3499.1 | 3440.5 | 4998.4 | 1187.8 | 0.68611 | 7.366
2024-12-09 | 14:39 | Data | 0 | 30.057 | 26.965 | 238.466 | 7.63 | 222.421 | 2065.26 | 26.01 | 41.213 | 6.24 | 1.491 | 5.861 | 8820.6 | 3.153 | 98 | 79.7 | 1342 | 20.65 | 5733.4 | 3510.5 | 3465 | 5023.4 | 1187.8 | 0.68247 | 7.353
2024-12-09 | 14:39 | Data | 0 | 30.043 | 27.194 | 238.692 | 7.63 | 222.601 | 2065.26 | 26 | 41.304 | 6.24 | 1.495 | 5.839 | 8843.21 | 2.782 | 98 | 79.6 | 1342 | 20.65 | 5748.1 | 3519.4 | 3460.9 | 5032.8 | 1187.8 | 0.68372 | 7.333
2024-12-09 | 14:40 | Data | 0 | 29.955 | 26.789 | 238.466 | 7.63 | 222.421 | 2067.97 | 26 | 41.304 | 6.25 | 1.49 | 5.857 | 8843.21 | 3.112 | 98 | 79.7 | 1344 | 20.65 | 5748.1 | 3505.7 | 3470.7 | 5024.4 | 1187.8 | 0.68286 | 7.345
2024-12-09 | 14:40 | Data | 0 | 30.07 | 27.363 | 238.647 | 7.63 | 222.421 | 2067.06 | 26 | 41.304 | 6.24 | 1.491 | 5.873 | 8838.69 | 2.998 | 98 | 79.7 | 1344 | 20.61 | 5745.1 | 3506.2 | 3475.6 | 5036.5 | 1187.8 | 0.68039 | 7.365
2024-12-09 | 14:40 | Data | 0 | 29.969 | 27.167 | 238.556 | 7.63 | 222.601 | 2067.97 | 26 | 41.304 | 6.24 | 1.485 | 5.841 | 8856.78 | 2.964 | 98 | 79.7 | 1344 | 20.65 | 5756.9 | 3515.9 | 3449.5 | 5023.8 | 1187.8 | 0.68485 | 7.326
2024-12-09 | 14:40 | Data | 0 | 30.556 | 27.052 | 238.647 | 7.63 | 222.466 | 2067.97 | 26.01 | 41.304 | 6.25 | 1.497 | 5.826 | 8847.74 | 3.031 | 98 | 79.6 | 1344 | 20.65 | 5751 | 3498.7 | 3444 | 5004.8 | 1187.8 | 0.68408 | 7.323
2024-12-09 | 14:40 | Data | 0 | 29.76 | 26.735 | 238.466 | 7.63 | 222.421 | 2065.26 | 26.01 | 41.213 | 6.25 | 1.497 | 5.838 | 8861.3 | 3.166 | 98 | 79.6 | 1342 | 20.61 | 5759.8 | 3492.7 | 3419.1 | 4983.3 | 1187.8 | 0.68659 | 7.334
2024-12-09 | 14:40 | Data | 0 | 29.962 | 26.992 | 238.692 | 7.63 | 222.375 | 2067.06 | 26.02 | 41.213 | 6.24 | 1.492 | 5.848 | 8843.21 | 3.146 | 98 | 79.7 | 1345 | 20.61 | 5748.1 | 3473.4 | 3382.9 | 4947.5 | 1187.8 | 0.68711 | 7.34
2024-12-09 | 14:40 | Data | 0 | 29.969 | 26.965 | 238.647 | 7.63 | 222.375 | 2065.26 | 26.02 | 41.213 | 6.24 | 1.507 | 5.837 | 8856.78 | 2.998 | 98 | 79.5 | 1343 | 20.7 | 5756.9 | 3500.7 | 3405.5 | 4980.1 | 1187.8 | 0.68879 | 7.339
2024-12-09 | 14:40 | Data | 0 | 30.07 | 27.295 | 238.692 | 7.63 | 222.692 | 2058.93 | 26.01 | 41.304 | 6.24 | 1.501 | 5.848 | 8838.69 | 2.795 | 98 | 79.6 | 1338 | 20.65 | 5745.1 | 3491 | 3418.2 | 4980.6 | 1187.8 | 0.68641 | 7.348
2024-12-09 | 14:40 | Data | 0 | 30.124 | 27.032 | 238.601 | 7.63 | 222.556 | 2055.31 | 26.02 | 41.304 | 6.24 | 1.487 | 5.84 | 8861.3 | 2.971 | 98 | 79.7 | 1335 | 20.65 | 5759.8 | 3510.5 | 3445.6 | 5014.7 | 1187.8 | 0.68613 | 7.326
2024-12-09 | 14:40 | Data | 0 | 29.841 | 26.742 | 238.33 | 7.63 | 222.33 | 2058.93 | 26.01 | 41.213 | 6.24 | 1.486 | 5.848 | 8856.78 | 2.998 | 98 | 79.7 | 1338 | 20.61 | 5756.9 | 3509.2 | 3447.7 | 5014 | 1187.8 | 0.6855 | 7.333
2024-12-09 | 14:40 | Data | 0 | 29.733 | 26.951 | 238.511 | 7.63 | 222.421 | 2061.64 | 26.01 | 41.304 | 6.24 | 1.505 | 5.855 | 8861.3 | 2.95 | 98 | 79.5 | 1340 | 20.61 | 5759.8 | 3507.1 | 3433.3 | 5004.5 | 1187.8 | 0.68627 | 7.361
2024-12-09 | 14:40 | Data | 0 | 30.185 | 26.992 | 238.556 | 7.63 | 222.601 | 2061.64 | 26.02 | 40.852 | 6.24 | 1.504 | 5.871 | 8874.87 | 3.058 | 98 | 79.6 | 1341 | 20.38 | 5768.7 | 3511.5 | 3416.3 | 4993.1 | 1187.8 | 0.68869 | 7.376
2024-12-09 | 14:40 | Data | 0 | 30.124 | 27.019 | 238.556 | 7.63 | 222.511 | 2061.64 | 26.01 | 41.304 | 6.24 | 1.504 | 5.859 | 8911.05 | 2.991 | 98 | 79.6 | 1340 | 20.65 | 5792.2 | 3512 | 3412.8 | 4996.7 | 1187.8 | 0.69009 | 7.363
2024-12-09 | 14:40 | Data | 0 | 30.131 | 26.796 | 238.33 | 7.63 | 222.375 | 2067.06 | 26.01 | 41.304 | 6.24 | 1.493 | 5.81 | 8911.05 | 3.315 | 98 | 79.5 | 1343 | 20.65 | 5792.2 | 3509.8 | 3415.8 | 4992.9 | 1187.8 | 0.68842 | 7.304
2024-12-09 | 14:40 | Data | 0 | 29.901 | 26.965 | 238.466 | 7.63 | 222.421 | 2061.64 | 26.03 | 41.304 | 6.24 | 1.496 | 5.845 | 8911.05 | 3.153 | 98 | 79.6 | 1341 | 20.61 | 5792.2 | 3523.3 | 3387.2 | 4981.4 | 1187.8 | 0.69304 | 7.341
2024-12-09 | 14:40 | Data | 0 | 30.286 | 27.241 | 238.692 | 7.63 | 222.421 | 2061.64 | 26.02 | 41.304 | 6.24 | 1.486 | 5.82 | 8915.57 | 2.984 | 98 | 79.7 | 1340 | 20.65 | 5795.1 | 3521.3 | 3401.5 | 4989.2 | 1187.9 | 0.69111 | 7.305
2024-12-09 | 14:40 | Data | 0 | 29.726 | 27.37 | 238.601 | 7.63 | 222.466 | 2061.64 | 26.01 | 40.943 | 6.25 | 1.48 | 5.823 | 8865.83 | 3.045 | 98 | 79.7 | 1340 | 20.52 | 5762.8 | 3494.4 | 3384.9 | 4959.4 | 1187.9 | 0.68939 | 7.302
2024-12-09 | 14:40 | Data | 0 | 30.293 | 27.106 | 238.828 | 7.63 | 222.647 | 2065.26 | 26.01 | 41.213 | 6.25 | 1.5 | 5.828 | 8865.83 | 3.099 | 98 | 79.5 | 1342 | 20.56 | 5762.8 | 3494.7 | 3390.4 | 4966.4 | 1187.9 | 0.69 | 7.327
2024-12-09 | 14:41 | Data | 0 | 29.962 | 27.295 | 238.556 | 7.63 | 222.511 | 2062.55 | 26.02 | 41.123 | 6.25 | 1.494 | 5.836 | 8865.83 | 2.903 | 98 | 79.6 | 1340 | 20.56 | 5762.8 | 3505.1 | 3410.5 | 4986.5 | 1187.9 | 0.68747 | 7.329
2024-12-09 | 14:41 | Data | 0 | 30.117 | 27.194 | 238.647 | 7.63 | 222.511 | 2065.26 | 25.99 | 41.304 | 6.25 | 1.492 | 5.889 | 8870.35 | 3.045 | 98 | 79.8 | 1343 | 20.7 | 5765.7 | 3485.8 | 3430.5 | 4986.3 | 1187.9 | 0.68403 | 7.382
2024-12-09 | 14:41 | Data | 0 | 30.428 | 26.884 | 238.782 | 7.63 | 222.556 | 2065.26 | 26.01 | 41.123 | 6.25 | 1.497 | 5.856 | 8802.51 | 3.025 | 98 | 79.6 | 1342 | 20.52 | 5721.6 | 3503.5 | 3462.3 | 5022.7 | 1187.9 | 0.68239 | 7.352
2024-12-09 | 14:41 | Data | 0 | 29.78 | 27.079 | 238.647 | 7.63 | 222.556 | 2065.26 | 26.01 | 41.304 | 6.25 | 1.495 | 5.846 | 8802.51 | 2.788 | 98 | 79.6 | 1342 | 20.65 | 5721.6 | 3494.1 | 3462.3 | 5014.8 | 1187.9 | 0.6824 | 7.341
2024-12-09 | 14:41 | Data | 0 | 30.07 | 27.012 | 238.375 | 7.63 | 222.421 | 2066.16 | 26.01 | 41.213 | 6.24 | 1.495 | 5.842 | 8811.56 | 2.957 | 98 | 79.6 | 1343 | 20.65 | 5727.5 | 3499.1 | 3451.8 | 5011.9 | 1187.9 | 0.68365 | 7.337
2024-12-09 | 14:41 | Data | 0 | 29.82 | 26.762 | 238.375 | 7.63 | 222.466 | 2069.78 | 26.03 | 41.304 | 6.24 | 1.498 | 5.873 | 8797.99 | 2.923 | 98 | 79.7 | 1346 | 20.61 | 5718.7 | 3522.2 | 3424.9 | 5008.6 | 1187.9 | 0.68763 | 7.371
2024-12-09 | 14:41 | Data | 0 | 30.28 | 26.971 | 238.647 | 7.63 | 222.511 | 2065.26 | 26.02 | 41.304 | 6.24 | 1.499 | 5.846 | 8883.91 | 3.052 | 98 | 79.6 | 1343 | 20.65 | 5774.5 | 3498.9 | 3444.9 | 5005.5 | 1187.9 | 0.68457 | 7.344
2024-12-09 | 14:41 | Data | 0 | 30.205 | 27.397 | 238.692 | 7.63 | 222.692 | 2070.68 | 26.02 | 41.304 | 6.24 | 1.487 | 5.83 | 8883.91 | 2.876 | 98 | 79.7 | 1345 | 20.61 | 5774.5 | 3511.3 | 3421.9 | 5000.6 | 1187.9 | 0.68767 | 7.317
2024-12-09 | 14:41 | Data | 0 | 30.266 | 27.39 | 238.737 | 7.63 | 222.511 | 2065.26 | 26.02 | 41.213 | 6.25 | 1.496 | 5.834 | 8870.35 | 3.058 | 98 | 79.6 | 1342 | 20.61 | 5765.7 | 3497.9 | 3382.1 | 4961 | 1187.9 | 0.69007 | 7.33
2024-12-09 | 14:41 | Data | 0 | 30.489 | 27.417 | 238.601 | 7.63 | 222.647 | 2067.97 | 26.02 | 41.304 | 6.25 | 1.495 | 5.842 | 8902 | 3.187 | 98 | 79.6 | 1344 | 20.65 | 5786.3 | 3500.4 | 3418.2 | 4988.4 | 1187.9 | 0.68718 | 7.337
2024-12-09 | 14:41 | Data | 0 | 30.07 | 27.187 | 238.647 | 7.64 | 222.421 | 2070.68 | 26.02 | 41.304 | 6.24 | 1.491 | 5.861 | 8879.39 | 2.971 | 98 | 79.7 | 1346 | 20.61 | 5771.6 | 3494.9 | 3411.8 | 4975.4 | 1187.9 | 0.68843 | 7.352
2024-12-09 | 14:41 | Data | 0 | 30.502 | 27.147 | 238.466 | 7.63 | 222.421 | 2069.78 | 26.02 | 41.213 | 6.25 | 1.488 | 5.84 | 8883.91 | 3.308 | 98 | 79.7 | 1345 | 20.61 | 5774.5 | 3485.4 | 3433.2 | 4991 | 1187.9 | 0.68297 | 7.328
2024-12-09 | 14:41 | Data | 0 | 30.604 | 27.046 | 238.466 | 7.63 | 222.511 | 2070.68 | 26.02 | 41.304 | 6.24 | 1.49 | 5.846 | 8874.87 | 3.301 | 98 | 79.7 | 1346 | 20.61 | 5768.7 | 3517.5 | 3454 | 5021.2 | 1187.9 | 0.68561 | 7.335
2024-12-09 | 14:41 | Data | 0 | 30.239 | 26.884 | 238.601 | 7.63 | 222.556 | 2073.39 | 26.02 | 41.304 | 6.24 | 1.495 | 5.838 | 8888.44 | 2.991 | 98 | 79.6 | 1348 | 20.65 | 5777.5 | 3507 | 3476.8 | 5034.1 | 1187.9 | 0.68206 | 7.332
2024-12-09 | 14:41 | Data | 0 | 30.556 | 27.538 | 238.647 | 7.63 | 222.556 | 2072.49 | 26 | 41.304 | 6.25 | 1.498 | 5.838 | 8883.91 | 3.058 | 98 | 79.6 | 1347 | 20.65 | 5774.5 | 3499.9 | 3464 | 5021.4 | 1187.9 | 0.68192 | 7.335
2024-12-09 | 14:41 | Data | 0 | 30.225 | 27.106 | 238.647 | 7.63 | 222.466 | 2072.49 | 26.01 | 41.304 | 6.25 | 1.504 | 5.877 | 8883.91 | 3.214 | 98 | 79.6 | 1348 | 20.61 | 5774.5 | 3492.1 | 3479.6 | 5024.4 | 1187.9 | 0.68056 | 7.38
2024-12-09 | 14:41 | Data | 0 | 30.401 | 27.505 | 238.873 | 7.63 | 222.647 | 2072.49 | 26.02 | 41.213 | 6.24 | 1.493 | 5.848 | 8883.91 | 2.903 | 98 | 79.7 | 1348 | 20.61 | 5774.5 | 3500.3 | 3428.9 | 4995 | 1187.9 | 0.68549 | 7.342
2024-12-09 | 14:42 | Data | 0 | 30.381 | 27.208 | 238.647 | 7.63 | 222.511 | 2073.39 | 26.02 | 41.304 | 6.24 | 1.49 | 5.857 | 8897.48 | 3.031 | 98 | 79.7 | 1347 | 20.61 | 5783.4 | 3505 | 3385.3 | 4971.8 | 1187.9 | 0.68742 | 7.347
2024-12-09 | 14:42 | Data | 0 | 29.753 | 26.735 | 238.511 | 7.63 | 222.466 | 2073.39 | 26.02 | 41.213 | 6.24 | 1.499 | 5.854 | 8920.09 | 3.112 | 98 | 79.6 | 1348 | 20.61 | 5798.1 | 3504.8 | 3405.7 | 4981.8 | 1187.9 | 0.68933 | 7.352
2024-12-09 | 14:42 | Data | 0 | 30.185 | 26.971 | 238.556 | 7.63 | 222.466 | 2072.49 | 26.02 | 41.213 | 6.24 | 1.505 | 5.85 | 8924.61 | 3.193 | 98 | 79.5 | 1347 | 20.65 | 5801 | 3500.4 | 3417.3 | 4984.4 | 1187.9 | 0.6871 | 7.357
2024-12-09 | 14:42 | Data | 0 | 30.016 | 27.289 | 238.647 | 7.63 | 222.601 | 2073.39 | 26.02 | 41.213 | 6.25 | 1.496 | 5.812 | 8924.61 | 2.937 | 98 | 79.5 | 1348 | 20.56 | 5801 | 3502.2 | 3418.6 | 4987.5 | 1187.9 | 0.68752 | 7.308
2024-12-09 | 14:42 | Data | 0 | 29.982 | 26.965 | 238.375 | 7.63 | 222.421 | 2075.2 | 26.02 | 41.304 | 6.25 | 1.487 | 5.842 | 8924.61 | 2.998 | 98 | 79.7 | 1349 | 20.61 | 5801 | 3512.3 | 3432.5 | 5006.1 | 1187.9 | 0.68665 | 7.331
2024-12-09 | 14:42 | Data | 0 | 29.962 | 26.965 | 238.466 | 7.63 | 222.375 | 2075.2 | 26.02 | 41.213 | 6.25 | 1.504 | 5.845 | 8920.09 | 2.991 | 98 | 79.5 | 1350 | 20.65 | 5798.1 | 3499.5 | 3437.4 | 5000.2 | 1187.9 | 0.68467 | 7.348
2024-12-09 | 14:42 | Data | 0 | 30.185 | 26.965 | 238.556 | 7.63 | 222.511 | 2076.1 | 26.02 | 41.304 | 6.25 | 1.5 | 5.819 | 8897.48 | 3.22 | 98 | 79.5 | 1349 | 20.65 | 5783.4 | 3507.1 | 3471 | 5026.5 | 1187.9 | 0.68174 | 7.318
2024-12-09 | 14:42 | Data | 0 | 30.158 | 27.14 | 238.556 | 7.63 | 222.466 | 2075.2 | 26.02 | 41.304 | 6.25 | 1.504 | 5.838 | 8892.96 | 3.214 | 98 | 79.5 | 1349 | 20.61 | 5780.4 | 3503.9 | 3485.8 | 5040.3 | 1187.9 | 0.68166 | 7.342
2024-12-09 | 14:42 | Data | 0 | 29.955 | 26.971 | 238.647 | 7.63 | 222.601 | 2073.39 | 26.01 | 41.123 | 6.24 | 1.498 | 5.861 | 8902 | 3.079 | 98 | 79.6 | 1347 | 20.61 | 5786.3 | 3508.8 | 3474.4 | 5029.5 | 1187.9 | 0.6836 | 7.359
2024-12-09 | 14:42 | Data | 0 | 29.908 | 27.14 | 238.601 | 7.63 | 222.556 | 2077.01 | 26 | 41.304 | 6.25 | 1.494 | 5.816 | 8915.57 | 2.964 | 98 | 79.6 | 1349 | 20.61 | 5795.1 | 3502.7 | 3459.6 | 5015.3 | 1187.9 | 0.68334 | 7.31
2024-12-09 | 14:42 | Data | 0 | 30.381 | 27.471 | 238.647 | 7.63 | 222.647 | 2081.53 | 26.02 | 41.213 | 6.24 | 1.487 | 5.841 | 8870.35 | 3.072 | 98 | 79.7 | 1353 | 20.61 | 5765.7 | 3513.4 | 3490.8 | 5050.5 | 1187.9 | 0.68036 | 7.328
2024-12-09 | 14:42 | Data | 0 | 30.077 | 27.41 | 238.601 | 7.63 | 222.647 | 2075.2 | 26.02 | 41.304 | 6.24 | 1.481 | 5.868 | 9309 | 2.917 | 98 | 79.9 | 1349 | 20.7 | 6050.9 | 3526.9 | 3471.1 | 5039.3 | 1188 | 0.68543 | 7.349
2024-12-09 | 14:42 | Data | 0 | 30.144 | 27.005 | 238.692 | 7.63 | 222.511 | 2076.1 | 26.02 | 41.213 | 6.25 | 1.492 | 5.844 | 8865.83 | 3.16 | 98 | 79.7 | 1349 | 20.65 | 5762.8 | 3510.6 | 3462.4 | 5022.9 | 1188 | 0.68408 | 7.337
2024-12-09 | 14:42 | Data | 0 | 30.502 | 26.998 | 238.692 | 7.63 | 222.556 | 2070.68 | 26.01 | 41.123 | 6.25 | 1.491 | 5.851 | 8856.78 | 3.227 | 98 | 79.7 | 1347 | 20.61 | 5756.9 | 3505.4 | 3427.3 | 5002.1 | 1188 | 0.68776 | 7.342
2024-12-09 | 14:42 | Data | 0 | 29.969 | 27.14 | 238.556 | 7.63 | 222.511 | 2074.29 | 26.02 | 41.213 | 6.25 | 1.494 | 5.859 | 8883.91 | 2.991 | 98 | 79.7 | 1348 | 20.65 | 5774.5 | 3498.3 | 3427.7 | 4995.5 | 1188 | 0.68563 | 7.353
2024-12-09 | 14:42 | Data | 0 | 30.178 | 26.965 | 238.511 | 7.63 | 222.466 | 2072.49 | 26.03 | 41.304 | 6.25 | 1.49 | 5.859 | 8883.91 | 3.22 | 98 | 79.7 | 1348 | 20.61 | 5774.5 | 3502.5 | 3418.9 | 4992.1 | 1188 | 0.68766 | 7.35
2024-12-09 | 14:42 | Data | 0 | 29.955 | 27.167 | 238.556 | 7.63 | 222.556 | 2070.68 | 26.02 | 41.213 | 6.25 | 1.494 | 5.867 | 8883.91 | 2.991 | 98 | 79.7 | 1346 | 20.61 | 5774.5 | 3496.4 | 3391.9 | 4965 | 1188 | 0.69089 | 7.361
2024-12-09 | 14:42 | Data | 0 | 29.854 | 26.749 | 238.511 | 7.63 | 222.511 | 2071.58 | 26.02 | 41.394 | 6.24 | 1.497 | 5.855 | 8897.48 | 2.957 | 98 | 79.7 | 1346 | 20.61 | 5783.4 | 3508.5 | 3417.4 | 4991.6 | 1188 | 0.68785 | 7.352
2024-12-09 | 14:43 | Data | 0 | 30.577 | 27.309 | 238.692 | 7.63 | 222.556 | 2070.68 | 26.02 | 41.213 | 6.25 | 1.498 | 5.86 | 8843.21 | 3.2 | 98 | 79.6 | 1346 | 20.61 | 5748.1 | 3511.3 | 3431.8 | 5003.2 | 1188 | 0.68669 | 7.358
2024-12-09 | 14:43 | Data | 0 | 30.185 | 26.971 | 238.601 | 7.63 | 222.421 | 2071.58 | 26.01 | 41.304 | 6.24 | 1.498 | 5.839 | 8843.21 | 3.119 | 98 | 79.6 | 1347 | 20.65 | 5748.1 | 3516.4 | 3450.5 | 5023.3 | 1188 | 0.6845 | 7.337
2024-12-09 | 14:43 | Data | 0 | 30.131 | 27.073 | 238.42 | 7.63 | 222.556 | 2072.49 | 26.02 | 41.123 | 6.25 | 1.495 | 5.833 | 8847.74 | 2.883 | 98 | 79.6 | 1347 | 20.61 | 5751 | 3514.8 | 3453.2 | 5020.4 | 1188 | 0.68563 | 7.328
2024-12-09 | 14:43 | Data | 0 | 30.185 | 27.066 | 238.466 | 7.63 | 222.33 | 2072.49 | 26.02 | 41.304 | 6.25 | 1.491 | 5.854 | 8838.69 | 2.795 | 98 | 79.7 | 1347 | 20.61 | 5745.1 | 3489.7 | 3459.8 | 5006.6 | 1188 | 0.68292 | 7.345
2024-12-09 | 14:43 | Data | 0 | 29.861 | 26.924 | 238.601 | 7.63 | 222.601 | 2072.49 | 26.02 | 41.213 | 6.25 | 1.487 | 5.862 | 8834.17 | 2.991 | 98 | 79.8 | 1347 | 20.61 | 5742.2 | 3510 | 3457.4 | 5020.4 | 1188 | 0.68492 | 7.35
2024-12-09 | 14:43 | Data | 0 | 29.955 | 26.877 | 238.42 | 7.63 | 222.33 | 2075.2 | 26.02 | 41.304 | 6.25 | 1.494 | 5.83 | 8829.65 | 2.991 | 98 | 79.6 | 1349 | 20.7 | 5739.3 | 3506.8 | 3477.4 | 5034 | 1188 | 0.68115 | 7.324
2024-12-09 | 14:43 | Data | 0 | 29.955 | 27.012 | 238.556 | 7.63 | 222.511 | 2073.39 | 26.01 | 41.304 | 6.24 | 1.492 | 5.837 | 8847.74 | 2.795 | 98 | 79.6 | 1347 | 20.65 | 5751 | 3491 | 3506.7 | 5047.8 | 1188 | 0.67611 | 7.328
2024-12-09 | 14:43 | Data | 0 | 30.178 | 27.025 | 238.692 | 7.63 | 222.601 | 2073.39 | 26.02 | 41.123 | 6.25 | 1.491 | 5.849 | 8843.21 | 2.984 | 98 | 79.7 | 1348 | 20.61 | 5748.1 | 3509.8 | 3500.5 | 5051.5 | 1188 | 0.68047 | 7.339
2024-12-09 | 14:43 | Data | 0 | 29.955 | 27.349 | 238.511 | 7.64 | 222.556 | 2072.49 | 26.02 | 41.213 | 6.24 | 1.484 | 5.862 | 8856.78 | 2.923 | 98 | 79.8 | 1347 | 20.65 | 5756.9 | 3485.7 | 3455.6 | 5006.2 | 1188 | 0.68078 | 7.346
2024-12-09 | 14:43 | Data | 0 | 30.455 | 27.336 | 238.782 | 7.63 | 222.692 | 2073.39 | 26.02 | 41.123 | 6.24 | 1.484 | 5.85 | 8861.3 | 3.126 | 98 | 79.8 | 1347 | 20.61 | 5759.8 | 3488.7 | 3417.7 | 4979.4 | 1188 | 0.68576 | 7.333
2024-12-09 | 14:43 | Data | 0 | 29.753 | 27.12 | 238.511 | 7.63 | 222.511 | 2073.39 | 26.02 | 41.213 | 6.25 | 1.491 | 5.865 | 8838.69 | 2.849 | 98 | 79.7 | 1347 | 20.61 | 5745.1 | 3507.6 | 3444.4 | 5007.4 | 1188 | 0.68581 | 7.354
2024-12-09 | 14:43 | Data | 0 | 29.733 | 26.755 | 238.466 | 7.63 | 222.421 | 2070.68 | 26.02 | 41.304 | 6.25 | 1.493 | 5.848 | 8856.78 | 3.119 | 98 | 79.7 | 1346 | 20.65 | 5756.9 | 3505.4 | 3435.4 | 5007.1 | 1188 | 0.68684 | 7.342
2024-12-09 | 14:43 | Data | 0 | 30.178 | 27.194 | 238.42 | 7.63 | 222.466 | 2071.58 | 26.02 | 41.213 | 6.24 | 1.502 | 5.807 | 8825.13 | 3.16 | 98 | 79.5 | 1347 | 20.56 | 5736.3 | 3498.6 | 3448.1 | 5009 | 1188 | 0.68436 | 7.308
2024-12-09 | 14:43 | Data | 0 | 30.185 | 27.079 | 238.556 | 7.63 | 222.511 | 2070.68 | 26.02 | 41.304 | 6.25 | 1.494 | 5.857 | 8865.83 | 2.876 | 98 | 79.7 | 1346 | 20.65 | 5762.8 | 3504.4 | 3426.6 | 4997.6 | 1188 | 0.68608 | 7.351
2024-12-09 | 14:43 | Data | 0 | 30.3 | 27.208 | 238.737 | 7.63 | 222.692 | 2070.68 | 26.02 | 41.213 | 6.24 | 1.493 | 5.86 | 8838.69 | 2.984 | 98 | 79.7 | 1346 | 20.61 | 5745.1 | 3493.4 | 3405.5 | 4975.6 | 1188 | 0.68966 | 7.353
2024-12-09 | 14:43 | Data | 0 | 30.185 | 26.965 | 238.647 | 7.63 | 222.466 | 2069.78 | 26.03 | 41.213 | 6.25 | 1.491 | 5.823 | 8816.08 | 3.22 | 98 | 79.6 | 1345 | 20.65 | 5730.5 | 3514.3 | 3431 | 5006.6 | 1188 | 0.6877 | 7.314
2024-12-09 | 14:43 | Data | 0 | 30.05 | 26.965 | 238.782 | 7.63 | 222.556 | 2070.68 | 26.02 | 41.213 | 6.24 | 1.497 | 5.859 | 8892.96 | 2.977 | 98 | 79.7 | 1345 | 20.65 | 5780.4 | 3493.4 | 3405.9 | 4975.1 | 1188 | 0.68787 | 7.356
2024-12-09 | 14:43 | Data | 0 | 30.496 | 27.417 | 238.511 | 7.63 | 222.647 | 2073.39 | 26.01 | 41.213 | 6.25 | 1.499 | 5.824 | 8911.05 | 3.099 | 98 | 79.5 | 1348 | 20.65 | 5792.2 | 3511.1 | 3427.3 | 4999.5 | 1188 | 0.68746 | 7.323
2024-12-09 | 14:44 | Data | 0 | 30.097 | 26.971 | 238.647 | 7.63 | 222.511 | 2072.49 | 26.02 | 41.213 | 6.24 | 1.51 | 5.85 | 8924.61 | 2.998 | 98 | 79.5 | 1347 | 20.56 | 5801 | 3501.9 | 3422.9 | 4990.2 | 1188 | 0.68493 | 7.36
2024-12-09 | 14:44 | Data | 0 | 30.246 | 26.985 | 238.601 | 7.63 | 222.692 | 2073.39 | 26.02 | 41.213 | 6.25 | 1.506 | 5.86 | 8924.61 | 3.018 | 98 | 79.6 | 1348 | 20.61 | 5801 | 3499.5 | 3417.1 | 4986.9 | 1188 | 0.68728 | 7.366
2024-12-09 | 14:44 | Data | 0 | 30.016 | 27.559 | 238.647 | 7.63 | 222.601 | 2071.58 | 26.01 | 41.213 | 6.25 | 1.506 | 5.853 | 8879.39 | 2.944 | 98 | 79.5 | 1347 | 20.65 | 5771.6 | 3494.1 | 3403.7 | 4977.1 | 1188 | 0.6876 | 7.358
2024-12-09 | 14:44 | Data | 0 | 30.273 | 26.998 | 238.692 | 7.63 | 222.556 | 2072.49 | 26.02 | 41.304 | 6.25 | 1.503 | 5.853 | 8892.96 | 3.2 | 98 | 79.6 | 1348 | 20.61 | 5780.4 | 3520.7 | 3413.6 | 4998.6 | 1188 | 0.68705 | 7.357
2024-12-09 | 14:44 | Data | 0 | 29.874 | 26.965 | 238.737 | 7.63 | 222.601 | 2070.68 | 26.03 | 41.304 | 6.25 | 1.493 | 5.829 | 8892.96 | 2.802 | 98 | 79.6 | 1345 | 20.61 | 5780.4 | 3507.3 | 3408 | 4984.8 | 1188 | 0.68878 | 7.322
2024-12-09 | 14:44 | Data | 0 | 30.273 | 27.363 | 238.692 | 7.63 | 222.601 | 2067.97 | 26.02 | 41.213 | 6.24 | 1.491 | 5.851 | 8897.48 | 3.079 | 98 | 79.7 | 1344 | 20.61 | 5783.4 | 3514.3 | 3403 | 4986.9 | 1188.1 | 0.68991 | 7.342
2024-12-09 | 14:44 | Data | 0 | 29.976 | 26.992 | 238.692 | 7.63 | 222.647 | 2067.97 | 26.01 | 41.213 | 6.25 | 1.497 | 5.827 | 8902 | 2.775 | 98 | 79.6 | 1344 | 20.7 | 5786.3 | 3502.3 | 3394.9 | 4975.9 | 1188.1 | 0.68932 | 7.321
2024-12-09 | 14:44 | Data | 0 | 30.185 | 27.262 | 238.601 | 7.63 | 222.647 | 2061.64 | 26.02 | 41.213 | 6.24 | 1.501 | 5.838 | 8924.61 | 3.092 | 98 | 79.5 | 1340 | 20.61 | 5801 | 3491.4 | 3400.6 | 4970.4 | 1188.1 | 0.68857 | 7.339
2024-12-09 | 14:44 | Data | 0 | 29.955 | 27.133 | 238.556 | 7.63 | 222.466 | 2067.97 | 26.02 | 41.123 | 6.24 | 1.502 | 5.849 | 8883.91 | 2.937 | 98 | 79.6 | 1345 | 20.56 | 5774.5 | 3514.4 | 3372.1 | 4958.6 | 1188.1 | 0.69226 | 7.351
2024-12-09 | 14:44 | Data | 0 | 30.097 | 26.965 | 238.737 | 7.63 | 222.601 | 2058.93 | 26.01 | 41.304 | 6.24 | 1.494 | 5.838 | 8911.05 | 2.998 | 98 | 79.6 | 1339 | 20.65 | 5792.2 | 3509.5 | 3388.3 | 4975.7 | 1188.1 | 0.69102 | 7.333
2024-12-09 | 14:44 | Data | 0 | 30.246 | 27.444 | 238.601 | 7.63 | 222.692 | 2065.26 | 26.02 | 41.213 | 6.25 | 1.491 | 5.84 | 8897.48 | 3.126 | 98 | 79.6 | 1342 | 20.61 | 5783.4 | 3509.8 | 3401.7 | 4984.3 | 1188.1 | 0.68939 | 7.333
2024-12-09 | 14:44 | Data | 0 | 30.003 | 27.282 | 238.782 | 7.63 | 222.511 | 2065.26 | 26.02 | 41.213 | 6.25 | 1.489 | 5.848 | 8883.91 | 2.795 | 98 | 79.7 | 1342 | 20.56 | 5774.5 | 3488.5 | 3398.2 | 4968.8 | 1188.1 | 0.68822 | 7.337
2024-12-09 | 14:44 | Data | 0 | 30.482 | 27.032 | 238.647 | 7.63 | 222.692 | 2065.26 | 26.02 | 41.213 | 6.24 | 1.496 | 5.844 | 8883.91 | 3.207 | 98 | 79.6 | 1343 | 20.65 | 5774.5 | 3498.8 | 3395.4 | 4967.6 | 1188.1 | 0.6908 | 7.34
2024-12-09 | 14:44 | Data | 0 | 29.955 | 27.181 | 238.466 | 7.63 | 222.466 | 2067.97 | 26.02 | 41.213 | 6.24 | 1.497 | 5.849 | 8883.91 | 2.775 | 98 | 79.6 | 1344 | 20.65 | 5774.5 | 3503.6 | 3402.5 | 4978.6 | 1188.1 | 0.68903 | 7.347
2024-12-09 | 14:44 | Data | 0 | 30.009 | 26.965 | 238.511 | 7.63 | 222.556 | 2067.97 | 26.01 | 41.304 | 6.24 | 1.484 | 5.837 | 8883.91 | 2.998 | 98 | 79.7 | 1345 | 20.65 | 5774.5 | 3504 | 3407.7 | 4983 | 1188.1 | 0.68897 | 7.323
2024-12-09 | 14:44 | Data | 0 | 30.212 | 27.289 | 238.647 | 7.63 | 222.647 | 2067.97 | 26.02 | 41.213 | 6.25 | 1.494 | 5.836 | 8870.35 | 2.836 | 98 | 79.6 | 1344 | 20.61 | 5765.7 | 3488.4 | 3409.3 | 4978.2 | 1188.1 | 0.68606 | 7.33
2024-12-09 | 14:44 | Data | 0 | 30.442 | 27.208 | 238.647 | 7.63 | 222.647 | 2067.97 | 26.01 | 41.304 | 6.24 | 1.492 | 5.851 | 8870.35 | 3.052 | 98 | 79.7 | 1344 | 20.61 | 5765.7 | 3510.9 | 3414.9 | 4992 | 1188.1 | 0.68864 | 7.344
2024-12-09 | 14:44 | Data | 0 | 29.962 | 27.356 | 238.782 | 7.63 | 222.692 | 2067.06 | 26.02 | 41.213 | 6.25 | 1.496 | 5.857 | 8883.91 | 2.917 | 98 | 79.7 | 1344 | 20.61 | 5774.5 | 3502.6 | 3374.1 | 4959.2 | 1188.1 | 0.69137 | 7.353
2024-12-09 | 14:45 | Data | 0 | 30.246 | 27.295 | 238.466 | 7.63 | 222.647 | 2067.97 | 26.02 | 41.304 | 6.24 | 1.496 | 5.825 | 8870.35 | 2.971 | 98 | 79.6 | 1344 | 20.65 | 5765.7 | 3500.8 | 3392.4 | 4967.3 | 1188.1 | 0.6912 | 7.322
2024-12-09 | 14:45 | Data | 0 | 30.097 | 26.992 | 238.511 | 7.63 | 222.556 | 2067.97 | 26.02 | 41.394 | 6.24 | 1.495 | 5.81 | 8879.39 | 2.998 | 98 | 79.5 | 1345 | 20.65 | 5771.6 | 3515.8 | 3409.9 | 4990.1 | 1188.1 | 0.69019 | 7.305
2024-12-09 | 14:45 | Data | 0 | 30.185 | 27.613 | 238.647 | 7.63 | 222.556 | 2068.87 | 26.02 | 41.304 | 6.25 | 1.5 | 5.831 | 8892.96 | 3.025 | 98 | 79.5 | 1344 | 20.61 | 5780.4 | 3506.9 | 3416 | 4990.8 | 1188.1 | 0.68829 | 7.331
2024-12-09 | 14:45 | Data | 0 | 29.982 | 26.978 | 238.556 | 7.63 | 222.556 | 2068.87 | 26.01 | 41.304 | 6.25 | 1.495 | 5.84 | 8897.48 | 2.984 | 98 | 79.6 | 1345 | 20.61 | 5783.4 | 3485.8 | 3432 | 4992 | 1188.1 | 0.68509 | 7.335
2024-12-09 | 14:45 | Data | 0 | 30.273 | 27.417 | 238.647 | 7.63 | 222.466 | 2069.78 | 26.02 | 41.304 | 6.25 | 1.495 | 5.851 | 8883.91 | 3.106 | 98 | 79.6 | 1345 | 20.65 | 5774.5 | 3505.2 | 3426.3 | 5005.4 | 1188.1 | 0.6888 | 7.346
2024-12-09 | 14:45 | Data | 0 | 30.07 | 26.735 | 238.466 | 7.63 | 222.511 | 2070.68 | 26.03 | 41.213 | 6.25 | 1.499 | 5.839 | 8870.35 | 3.227 | 98 | 79.6 | 1345 | 20.61 | 5765.7 | 3495.6 | 3383.1 | 4959.5 | 1188.1 | 0.6908 | 7.337
2024-12-09 | 14:45 | Data | 0 | 30.266 | 26.978 | 238.601 | 7.63 | 222.511 | 2067.97 | 26.02 | 41.213 | 6.25 | 1.499 | 5.84 | 8874.87 | 3.038 | 98 | 79.6 | 1344 | 20.65 | 5768.7 | 3494.6 | 3428.4 | 4991.9 | 1188.1 | 0.68505 | 7.34
2024-12-09 | 14:45 | Data | 0 | 29.989 | 27.282 | 238.601 | 7.63 | 222.601 | 2073.39 | 26.02 | 41.123 | 6.25 | 1.489 | 5.829 | 8888.44 | 2.795 | 98 | 79.7 | 1348 | 20.61 | 5777.5 | 3501.2 | 3401.6 | 4976.4 | 1188.1 | 0.68879 | 7.317
2024-12-09 | 14:45 | Data | 0 | 30.509 | 27.133 | 238.692 | 7.63 | 222.647 | 2075.2 | 26.01 | 41.213 | 6.24 | 1.493 | 5.86 | 8883.91 | 3.038 | 98 | 79.7 | 1349 | 20.61 | 5774.5 | 3494.9 | 3394.8 | 4968.3 | 1188.1 | 0.68692 | 7.354
2024-12-09 | 14:45 | Data | 0 | 29.955 | 27.14 | 238.737 | 7.63 | 222.511 | 2075.2 | 26.02 | 41.304 | 6.24 | 1.495 | 5.851 | 8897.48 | 3.018 | 98 | 79.7 | 1349 | 20.65 | 5783.4 | 3485.6 | 3371.4 | 4946.4 | 1188.1 | 0.69007 | 7.346
2024-12-09 | 14:45 | Data | 0 | 30.144 | 27.397 | 238.737 | 7.63 | 222.737 | 2077.91 | 26.01 | 41.213 | 6.25 | 1.492 | 5.81 | 8911.05 | 2.971 | 98 | 79.6 | 1351 | 20.65 | 5792.2 | 3506.1 | 3392.6 | 4971.1 | 1188.1 | 0.69115 | 7.304
2024-12-09 | 14:45 | Data | 0 | 30.442 | 27.093 | 238.556 | 7.63 | 222.601 | 2077.91 | 26.01 | 41.304 | 6.24 | 1.499 | 5.826 | 8906.53 | 3.099 | 98 | 79.5 | 1351 | 20.61 | 5789.2 | 3512.1 | 3380 | 4967.8 | 1188.1 | 0.69254 | 7.324
2024-12-09 | 14:45 | Data | 0 | 30.415 | 27.248 | 238.873 | 7.63 | 222.692 | 2082.43 | 26.02 | 41.213 | 6.25 | 1.501 | 5.808 | 8924.61 | 2.998 | 98 | 79.4 | 1354 | 20.52 | 5801 | 3512.2 | 3388.5 | 4973.1 | 1188.1 | 0.69153 | 7.309
2024-12-09 | 14:45 | Data | 0 | 30.043 | 27.066 | 238.556 | 7.63 | 222.556 | 2081.53 | 26.02 | 41.304 | 6.25 | 1.498 | 5.819 | 8906.53 | 3.099 | 98 | 79.5 | 1353 | 20.65 | 5789.2 | 3494.3 | 3423 | 4983.5 | 1188.1 | 0.6863 | 7.316
2024-12-09 | 14:45 | Data | 0 | 30.178 | 27.079 | 238.466 | 7.63 | 222.421 | 2082.43 | 26.02 | 41.304 | 6.25 | 1.489 | 5.831 | 8911.05 | 2.998 | 98 | 79.7 | 1354 | 20.65 | 5792.2 | 3495 | 3434.5 | 4996.6 | 1188.1 | 0.68476 | 7.319
2024-12-09 | 14:45 | Data | 0 | 30.354 | 27.464 | 238.601 | 7.63 | 222.601 | 2082.43 | 26.01 | 41.304 | 6.24 | 1.493 | 5.836 | 8892.96 | 2.883 | 98 | 79.6 | 1354 | 20.65 | 5780.4 | 3505.2 | 3444.6 | 5008.7 | 1188.1 | 0.68585 | 7.329
2024-12-09 | 14:45 | Data | 0 | 30.3 | 27.214 | 238.737 | 7.63 | 222.511 | 2081.53 | 26.01 | 41.304 | 6.25 | 1.497 | 5.831 | 8920.09 | 3.166 | 98 | 79.6 | 1354 | 20.65 | 5798.1 | 3487.8 | 3453.8 | 5001.8 | 1188.1 | 0.68579 | 7.328
2024-12-09 | 14:46 | Data | 0 | 29.8 | 26.971 | 238.782 | 7.63 | 222.601 | 2081.53 | 26.03 | 41.213 | 6.24 | 1.487 | 5.838 | 8951.75 | 2.937 | 98 | 79.7 | 1353 | 20.61 | 5818.6 | 3502.1 | 3400.5 | 4978.5 | 1188.2 | 0.68847 | 7.326
2024-12-09 | 14:46 | Data | 0 | 30.185 | 27.194 | 238.42 | 7.63 | 222.511 | 2079.72 | 26.01 | 41.304 | 6.25 | 1.489 | 5.839 | 8933.66 | 2.991 | 98 | 79.7 | 1351 | 20.61 | 5806.9 | 3501.6 | 3376.6 | 4959.7 | 1188.2 | 0.69163 | 7.329
2024-12-09 | 14:46 | Data | 0 | 29.955 | 27.14 | 238.556 | 7.63 | 222.511 | 2079.72 | 26.02 | 41.213 | 6.24 | 1.5 | 5.838 | 8929.14 | 2.991 | 98 | 79.6 | 1352 | 20.65 | 5803.9 | 3498.8 | 3361.8 | 4946.4 | 1188.2 | 0.69359 | 7.336
2024-12-09 | 14:46 | Data | 0 | 30.003 | 26.85 | 238.556 | 7.63 | 222.511 | 2078.81 | 26.02 | 41.123 | 6.25 | 1.5 | 5.838 | 8933.66 | 2.883 | 98 | 79.6 | 1353 | 20.61 | 5806.9 | 3502.4 | 3355.2 | 4945.2 | 1188.2 | 0.69358 | 7.338
2024-12-09 | 14:46 | Data | 0 | 30.158 | 27.511 | 238.782 | 7.63 | 222.647 | 2084.24 | 26.02 | 41.394 | 6.24 | 1.501 | 5.843 | 8947.23 | 2.734 | 98 | 79.6 | 1354 | 20.65 | 5815.7 | 3482.7 | 3372.5 | 4943.9 | 1188.2 | 0.69005 | 7.344
2024-12-09 | 14:46 | Data | 0 | 30.225 | 26.971 | 238.601 | 7.63 | 222.511 | 2085.14 | 26.02 | 41.213 | 6.25 | 1.505 | 5.848 | 8947.23 | 3.038 | 98 | 79.5 | 1355 | 20.65 | 5815.7 | 3500.3 | 3362.2 | 4949.5 | 1188.2 | 0.69324 | 7.352
2024-12-09 | 14:46 | Data | 0 | 30.246 | 27.14 | 238.511 | 7.63 | 222.601 | 2082.43 | 26.01 | 41.304 | 6.25 | 1.498 | 5.857 | 8956.27 | 3.193 | 98 | 79.6 | 1352 | 20.65 | 5821.6 | 3498.9 | 3382.4 | 4961.2 | 1188.2 | 0.69134 | 7.355
2024-12-09 | 14:46 | Data | 0 | 30.057 | 26.965 | 238.647 | 7.63 | 222.556 | 2073.39 | 26.02 | 41.213 | 6.25 | 1.494 | 5.854 | 8915.57 | 3.187 | 98 | 79.6 | 1348 | 20.56 | 5795.1 | 3486.9 | 3425.4 | 4985.3 | 1188.2 | 0.68416 | 7.35
2024-12-09 | 14:46 | Data | 0 | 30.165 | 27.187 | 238.556 | 7.63 | 222.511 | 2085.14 | 26.01 | 41.304 | 6.24 | 1.493 | 5.842 | 8956.27 | 2.998 | 98 | 79.7 | 1354 | 20.65 | 5821.6 | 3485.8 | 3443.3 | 4994.9 | 1188.2 | 0.68397 | 7.334
2024-12-09 | 14:46 | Data | 0 | 30.178 | 26.796 | 238.466 | 7.63 | 222.556 | 2084.24 | 26.02 | 41.213 | 6.24 | 1.496 | 5.846 | 8924.61 | 3.389 | 98 | 79.6 | 1355 | 20.61 | 5801 | 3505.3 | 3426.8 | 4997.2 | 1188.2 | 0.68641 | 7.342
2024-12-09 | 14:46 | Data | 0 | 30.415 | 27.505 | 238.737 | 7.63 | 222.692 | 2085.14 | 26.02 | 41.213 | 6.25 | 1.487 | 5.853 | 8924.61 | 2.89 | 98 | 79.7 | 1355 | 20.61 | 5801 | 3492 | 3411.8 | 4977.7 | 1188.2 | 0.6867 | 7.341
2024-12-09 | 14:46 | Data | 0 | 30.07 | 27.248 | 238.601 | 7.63 | 222.556 | 2083.33 | 26.02 | 41.304 | 6.24 | 1.498 | 5.81 | 8911.05 | 3.079 | 98 | 79.5 | 1355 | 20.65 | 5792.2 | 3489.6 | 3429.5 | 4988.4 | 1188.2 | 0.68473 | 7.308
2024-12-09 | 14:46 | Data | 0 | 30.212 | 26.992 | 238.737 | 7.63 | 222.647 | 2078.81 | 26.02 | 41.304 | 6.25 | 1.496 | 5.821 | 8911.05 | 2.998 | 98 | 79.6 | 1351 | 20.65 | 5792.2 | 3507.8 | 3397.3 | 4978 | 1188.2 | 0.68824 | 7.317
2024-12-09 | 14:46 | Data | 0 | 30.185 | 26.965 | 238.828 | 7.63 | 222.692 | 2079.72 | 26.01 | 41.304 | 6.25 | 1.485 | 5.845 | 8897.48 | 3.214 | 98 | 79.7 | 1351 | 20.65 | 5783.4 | 3474.1 | 3427.6 | 4978.9 | 1188.2 | 0.68358 | 7.33
2024-12-09 | 14:46 | Data | 0 | 30.212 | 27.086 | 238.782 | 7.63 | 222.647 | 2084.24 | 26.02 | 41.304 | 6.24 | 1.492 | 5.834 | 8888.44 | 3.085 | 98 | 79.6 | 1355 | 20.61 | 5777.5 | 3503.1 | 3405.4 | 4980.9 | 1188.2 | 0.68849 | 7.326
2024-12-09 | 14:46 | Data | 0 | 29.733 | 26.735 | 238.466 | 7.63 | 222.511 | 2081.53 | 26.01 | 41.304 | 6.24 | 1.495 | 5.851 | 8874.87 | 3.099 | 98 | 79.6 | 1354 | 20.65 | 5768.7 | 3496.6 | 3383.3 | 4963.4 | 1188.2 | 0.69141 | 7.346
2024-12-09 | 14:46 | Data | 0 | 30.273 | 26.998 | 238.511 | 7.63 | 222.647 | 2081.53 | 26.03 | 41.304 | 6.25 | 1.493 | 5.822 | 8870.35 | 3.247 | 98 | 79.6 | 1353 | 20.61 | 5765.7 | 3514.4 | 3376.9 | 4966.2 | 1188.2 | 0.69315 | 7.315
2024-12-09 | 14:46 | Data | 0 | 30.34 | 27.079 | 238.556 | 7.63 | 222.601 | 2079.72 | 26.01 | 41.304 | 6.25 | 1.492 | 5.819 | 8820.6 | 3.038 | 98 | 79.6 | 1353 | 20.61 | 5733.4 | 3496.2 | 3394.5 | 4968.3 | 1188.2 | 0.68901 | 7.31
2024-12-09 | 14:47 | Data | 0 | 30.036 | 27.383 | 238.556 | 7.63 | 222.601 | 2083.33 | 26.02 | 41.213 | 6.25 | 1.482 | 5.828 | 8829.65 | 3.2 | 98 | 79.7 | 1355 | 20.65 | 5739.3 | 3503.9 | 3420 | 4993.7 | 1188.2 | 0.68887 | 7.311
2024-12-09 | 14:47 | Data | 0 | 29.989 | 27.167 | 238.692 | 7.63 | 222.737 | 2084.24 | 26.02 | 41.304 | 6.25 | 1.501 | 5.814 | 8820.6 | 2.822 | 98 | 79.5 | 1355 | 20.61 | 5733.4 | 3516 | 3414.6 | 5003.2 | 1188.2 | 0.68773 | 7.316
2024-12-09 | 14:47 | Data | 0 | 30.516 | 27.093 | 238.556 | 7.63 | 222.692 | 2085.14 | 26.01 | 41.304 | 6.25 | 1.507 | 5.804 | 8820.6 | 3.018 | 98 | 79.4 | 1355 | 20.65 | 5733.4 | 3525.5 | 3424.9 | 5011.9 | 1188.2 | 0.6884 | 7.311
2024-12-09 | 14:47 | Data | 0 | 30.185 | 26.938 | 238.647 | 7.63 | 222.601 | 2086.95 | 26.02 | 41.213 | 6.25 | 1.49 | 5.818 | 8829.65 | 3.045 | 98 | 79.6 | 1357 | 20.65 | 5739.3 | 3519.8 | 3429.4 | 5014 | 1188.2 | 0.68693 | 7.308
2024-12-09 | 14:47 | Data | 0 | 30.185 | 27.167 | 238.556 | 7.63 | 222.511 | 2086.04 | 26.02 | 41.213 | 6.24 | 1.491 | 5.844 | 8843.21 | 3.106 | 98 | 79.7 | 1356 | 20.61 | 5748.1 | 3524.8 | 3445.9 | 5025.4 | 1188.2 | 0.68514 | 7.333
2024-12-09 | 14:47 | Data | 0 | 29.955 | 27.012 | 238.692 | 7.63 | 222.556 | 2083.33 | 26.02 | 41.213 | 6.25 | 1.49 | 5.845 | 8838.69 | 2.788 | 98 | 79.7 | 1354 | 20.65 | 5745.1 | 3490.3 | 3431.6 | 4993.2 | 1188.2 | 0.68389 | 7.337
2024-12-09 | 14:47 | Data | 0 | 30.063 | 27.187 | 238.511 | 7.63 | 222.511 | 2082.43 | 26.02 | 41.123 | 6.25 | 1.504 | 5.823 | 8838.69 | 2.991 | 98 | 79.5 | 1354 | 20.61 | 5745.1 | 3511.1 | 3438.9 | 5012.3 | 1188.2 | 0.68552 | 7.33
2024-12-09 | 14:47 | Data | 0 | 30.185 | 27.194 | 238.647 | 7.63 | 222.601 | 2082.43 | 26.02 | 41.213 | 6.25 | 1.5 | 5.812 | 8838.69 | 2.998 | 98 | 79.5 | 1354 | 20.65 | 5745.1 | 3525.9 | 3419.7 | 5008.7 | 1188.2 | 0.68885 | 7.313
2024-12-09 | 14:47 | Data | 0 | 29.989 | 26.965 | 238.556 | 7.63 | 222.556 | 2081.53 | 26.02 | 41.213 | 6.25 | 1.495 | 5.814 | 8838.69 | 2.998 | 98 | 79.5 | 1353 | 20.65 | 5745.1 | 3524.8 | 3408.6 | 4999.2 | 1188.2 | 0.69 | 7.31
2024-12-09 | 14:47 | Data | 0 | 30.07 | 26.742 | 238.42 | 7.63 | 222.556 | 2084.24 | 26.02 | 41.304 | 6.25 | 1.498 | 5.808 | 8856.78 | 3.22 | 98 | 79.5 | 1355 | 20.65 | 5756.9 | 3527 | 3441.6 | 5023.8 | 1188.2 | 0.6875 | 7.305
2024-12-09 | 14:47 | Data | 0 | 30.198 | 27.187 | 238.647 | 7.63 | 222.737 | 2077.91 | 26.02 | 41.213 | 6.25 | 1.503 | 5.841 | 8856.78 | 3.025 | 98 | 79.5 | 1351 | 20.65 | 5756.9 | 3523.9 | 3418.7 | 5005.3 | 1188.2 | 0.68905 | 7.345
2024-12-09 | 14:47 | Data | 0 | 30.354 | 27.302 | 238.647 | 7.63 | 222.647 | 2077.91 | 26.02 | 41.213 | 6.24 | 1.5 | 5.874 | 8897.48 | 3.2 | 98 | 79.7 | 1351 | 20.61 | 5783.4 | 3500.2 | 3423.3 | 4997.6 | 1188.2 | 0.68506 | 7.373
2024-12-09 | 14:47 | Data | 0 | 30.178 | 27.336 | 238.601 | 7.63 | 222.556 | 2077.91 | 26.02 | 41.304 | 6.24 | 1.494 | 5.858 | 8892.96 | 2.93 | 98 | 79.7 | 1350 | 20.61 | 5780.4 | 3520.5 | 3414.6 | 4997.9 | 1188.2 | 0.68919 | 7.352
2024-12-09 | 14:47 | Data | 0 | 30.131 | 27.187 | 238.647 | 7.63 | 222.601 | 2078.81 | 26.02 | 41.304 | 6.25 | 1.495 | 5.823 | 8897.48 | 2.991 | 98 | 79.6 | 1351 | 20.7 | 5783.4 | 3538.7 | 3447.1 | 5037.1 | 1188.3 | 0.68858 | 7.319
2024-12-09 | 14:47 | Data | 0 | 29.955 | 26.965 | 238.601 | 7.63 | 222.601 | 2078.81 | 26 | 41.394 | 6.25 | 1.491 | 5.81 | 8902 | 2.991 | 98 | 79.6 | 1351 | 20.65 | 5786.3 | 3519.7 | 3436.3 | 5018.9 | 1188.3 | 0.68587 | 7.302
2024-12-09 | 14:47 | Data | 0 | 30.3 | 27.505 | 238.647 | 7.63 | 222.647 | 2077.91 | 26.02 | 41.213 | 6.25 | 1.488 | 5.826 | 8874.87 | 3.072 | 98 | 79.7 | 1351 | 20.61 | 5768.7 | 3535 | 3463.2 | 5042.7 | 1188.3 | 0.68591 | 7.313
2024-12-09 | 14:47 | Data | 0 | 30.07 | 27.444 | 238.556 | 7.63 | 222.647 | 2078.81 | 26.02 | 41.213 | 6.25 | 1.497 | 5.856 | 8883.91 | 2.842 | 98 | 79.6 | 1351 | 20.61 | 5774.5 | 3538.7 | 3463.1 | 5042.2 | 1188.3 | 0.6875 | 7.352
2024-12-09 | 14:48 | Data | 0 | 30.435 | 26.971 | 238.873 | 7.63 | 222.782 | 2077.01 | 26.02 | 41.304 | 6.25 | 1.5 | 5.855 | 8892.96 | 3.045 | 98 | 79.6 | 1350 | 20.65 | 5780.4 | 3528.3 | 3447.9 | 5026.7 | 1188.3 | 0.68719 | 7.355
2024-12-09 | 14:48 | Data | 0 | 30.185 | 27.235 | 238.466 | 7.63 | 222.601 | 2075.2 | 26.02 | 41.304 | 6.24 | 1.5 | 5.865 | 8883.91 | 2.822 | 98 | 79.6 | 1349 | 20.61 | 5774.5 | 3522.6 | 3436.8 | 5020 | 1188.3 | 0.68672 | 7.365
2024-12-09 | 14:48 | Data | 0 | 30.185 | 27.491 | 238.601 | 7.63 | 222.601 | 2072.49 | 26.02 | 41.213 | 6.25 | 1.497 | 5.854 | 8911.05 | 3.011 | 98 | 79.6 | 1347 | 20.61 | 5792.2 | 3518.5 | 3415.7 | 5001.9 | 1188.3 | 0.68771 | 7.351
2024-12-09 | 14:48 | Data | 0 | 30.171 | 27.363 | 238.692 | 7.63 | 222.647 | 2070.68 | 26.01 | 41.304 | 6.24 | 1.49 | 5.843 | 8911.05 | 3.072 | 98 | 79.7 | 1346 | 20.7 | 5792.2 | 3529 | 3437.3 | 5023.1 | 1188.3 | 0.68811 | 7.333
2024-12-09 | 14:48 | Data | 0 | 29.874 | 26.965 | 238.692 | 7.63 | 222.601 | 2076.1 | 26.01 | 41.304 | 6.25 | 1.497 | 5.838 | 8920.09 | 2.788 | 98 | 79.6 | 1349 | 20.61 | 5798.1 | 3539.4 | 3427.7 | 5024.9 | 1188.3 | 0.68995 | 7.333
2024-12-09 | 14:48 | Data | 0 | 30.07 | 26.965 | 238.601 | 7.63 | 222.511 | 2075.2 | 26.02 | 41.213 | 6.24 | 1.498 | 5.846 | 8920.09 | 3.004 | 98 | 79.6 | 1349 | 20.65 | 5798.1 | 3519.2 | 3408.3 | 4998.8 | 1188.3 | 0.68928 | 7.342
2024-12-09 | 14:48 | Data | 0 | 29.962 | 26.911 | 238.466 | 7.63 | 222.511 | 2075.2 | 26.02 | 40.943 | 6.25 | 1.5 | 5.826 | 8924.61 | 3.045 | 98 | 79.5 | 1349 | 20.47 | 5801 | 3528.2 | 3422.2 | 5011.9 | 1188.3 | 0.68958 | 7.327
2024-12-09 | 14:48 | Data | 0 | 30.097 | 27.079 | 238.692 | 7.63 | 222.692 | 2073.39 | 26.01 | 41.304 | 6.25 | 1.497 | 5.844 | 8933.66 | 2.829 | 98 | 79.6 | 1348 | 20.65 | 5806.9 | 3503.7 | 3418.1 | 4995.9 | 1188.3 | 0.68617 | 7.341
2024-12-09 | 14:48 | Data | 0 | 30.185 | 26.971 | 238.556 | 7.63 | 222.601 | 2072.49 | 26.02 | 41.123 | 6.25 | 1.496 | 5.846 | 8933.66 | 3.038 | 98 | 79.6 | 1348 | 20.56 | 5806.9 | 3521.2 | 3426.8 | 5014.4 | 1188.3 | 0.6865 | 7.342
2024-12-09 | 14:48 | Data | 0 | 30.171 | 27.019 | 238.647 | 7.63 | 222.556 | 2076.1 | 26.02 | 41.123 | 6.25 | 1.484 | 5.846 | 8915.57 | 3.166 | 98 | 79.7 | 1349 | 20.61 | 5795.1 | 3541.1 | 3434.5 | 5032.4 | 1188.3 | 0.68882 | 7.331
2024-12-09 | 14:48 | Data | 0 | 29.733 | 27.268 | 238.466 | 7.63 | 222.511 | 2076.1 | 26.02 | 41.304 | 6.25 | 1.483 | 5.846 | 8938.18 | 2.775 | 98 | 79.8 | 1349 | 20.61 | 5809.8 | 3458.6 | 3423.7 | 4968.9 | 1188.3 | 0.68466 | 7.33
2024-12-09 | 14:48 | Data | 0 | 29.962 | 27.444 | 238.737 | 7.63 | 222.601 | 2077.91 | 26.05 | 41.123 | 6.25 | 1.491 | 5.837 | 8906.53 | 2.89 | 98 | 79.6 | 1351 | 20.56 | 5789.2 | 3461.5 | 3438 | 4969 | 1188.3 | 0.68256 | 7.331
2024-12-09 | 14:48 | Data | 0 | 29.733 | 26.965 | 238.647 | 7.63 | 222.601 | 2076.1 | 26.02 | 41.304 | 6.25 | 1.499 | 5.853 | 8915.57 | 2.964 | 98 | 79.6 | 1351 | 20.65 | 5795.1 | 3448.4 | 3441.1 | 4966.2 | 1188.3 | 0.68022 | 7.352
2024-12-09 | 14:48 | Data | 0 | 29.753 | 26.85 | 238.556 | 7.63 | 222.511 | 2077.91 | 26.03 | 41.304 | 6.25 | 1.495 | 5.838 | 8906.53 | 3.119 | 98 | 79.6 | 1351 | 20.56 | 5789.2 | 3443.9 | 3431.6 | 4956.3 | 1188.3 | 0.68034 | 7.333
2024-12-09 | 14:48 | Data | 0 | 29.955 | 27.181 | 238.601 | 7.63 | 222.511 | 2077.91 | 26.01 | 41.213 | 6.25 | 1.489 | 5.825 | 8906.53 | 2.89 | 98 | 79.6 | 1351 | 20.65 | 5789.2 | 3456.5 | 3420.5 | 4956.8 | 1188.3 | 0.68482 | 7.314
2024-12-09 | 14:48 | Data | 0 | 30.489 | 27.356 | 238.601 | 7.63 | 222.556 | 2078.81 | 26.02 | 41.213 | 6.25 | 1.491 | 5.82 | 8883.91 | 3.099 | 98 | 79.6 | 1352 | 20.65 | 5774.5 | 3475.2 | 3401.3 | 4952.4 | 1188.3 | 0.68717 | 7.312
2024-12-09 | 14:48 | Data | 0 | 29.645 | 26.938 | 238.556 | 7.63 | 222.647 | 2078.81 | 26.02 | 41.213 | 6.24 | 1.494 | 5.836 | 8920.09 | 2.95 | 98 | 79.6 | 1351 | 20.61 | 5798.1 | 3457.8 | 3410.4 | 4945.6 | 1188.3 | 0.68201 | 7.33
2024-12-09 | 14:48 | Data | 0 | 29.969 | 27.181 | 238.375 | 7.63 | 222.556 | 2081.53 | 26.02 | 41.213 | 6.25 | 1.502 | 5.845 | 8883.91 | 2.795 | 98 | 79.5 | 1353 | 20.61 | 5774.5 | 3451 | 3400.7 | 4924.9 | 1188.3 | 0.68418 | 7.345
2024-12-09 | 14:48 | Data | 0 | 29.955 | 26.965 | 238.42 | 7.63 | 222.511 | 2081.53 | 26.02 | 41.304 | 6.25 | 1.505 | 5.867 | 8897.48 | 3.106 | 98 | 79.6 | 1353 | 20.61 | 5783.4 | 3454.7 | 3442.1 | 4972 | 1188.3 | 0.6803 | 7.371
2024-12-09 | 14:49 | Data | 0 | 30.583 | 27.093 | 238.466 | 7.63 | 222.601 | 2081.53 | 26.02 | 41.304 | 6.25 | 1.495 | 5.834 | 8883.91 | 3.153 | 98 | 79.6 | 1353 | 20.65 | 5774.5 | 3502 | 3433.5 | 5001.5 | 1188.3 | 0.68486 | 7.329
2024-12-09 | 14:49 | Data | 0 | 29.847 | 26.735 | 238.601 | 7.63 | 222.556 | 2081.53 | 26.01 | 41.304 | 6.25 | 1.488 | 5.84 | 8883.91 | 3.18 | 98 | 79.7 | 1354 | 20.65 | 5774.5 | 3527.1 | 3446.1 | 5029.2 | 1188.3 | 0.686 | 7.328
2024-12-09 | 14:49 | Data | 0 | 30.354 | 27.451 | 238.647 | 7.63 | 222.692 | 2081.53 | 26.01 | 41.213 | 6.25 | 1.503 | 5.838 | 8883.91 | 3.045 | 98 | 79.5 | 1353 | 20.61 | 5774.5 | 3513.5 | 3470 | 5033 | 1188.3 | 0.68324 | 7.342
2024-12-09 | 14:49 | Data | 0 | 30.185 | 27.309 | 238.556 | 7.63 | 222.647 | 2081.53 | 26.02 | 41.394 | 6.25 | 1.494 | 5.851 | 8883.91 | 3.106 | 98 | 79.7 | 1353 | 20.7 | 5774.5 | 3519.4 | 3459.1 | 5028.4 | 1188.3 | 0.68521 | 7.344
2024-12-09 | 14:49 | Data | 0 | 30.388 | 26.809 | 238.601 | 7.63 | 222.647 | 2081.53 | 26.02 | 41.033 | 6.25 | 1.487 | 5.813 | 8897.48 | 3.045 | 98 | 79.6 | 1354 | 20.47 | 5783.4 | 3493.2 | 3419.2 | 4986.4 | 1188.3 | 0.68581 | 7.301
2024-12-09 | 14:49 | Data | 0 | 30.239 | 26.985 | 238.466 | 7.63 | 222.647 | 2075.2 | 26.02 | 40.943 | 6.25 | 1.494 | 5.812 | 8892.96 | 3.004 | 98 | 79.6 | 1349 | 20.52 | 5780.4 | 3506.7 | 3413.2 | 4997.4 | 1188.3 | 0.68878 | 7.306
2024-12-09 | 14:49 | Data | 0 | 30.266 | 27.079 | 238.647 | 7.63 | 222.556 | 2077.01 | 26.02 | 41.033 | 6.25 | 1.489 | 5.83 | 8883.91 | 3.038 | 98 | 79.7 | 1349 | 20.47 | 5774.5 | 3499.8 | 3397.4 | 4973.4 | 1188.3 | 0.68863 | 7.32
2024-12-09 | 14:49 | Data | 0 | 29.726 | 26.728 | 238.556 | 7.63 | 222.556 | 2076.1 | 26.01 | 41.304 | 6.26 | 1.487 | 5.855 | 8888.44 | 2.998 | 98 | 79.7 | 1349 | 20.65 | 5777.5 | 3506 | 3393.9 | 4979.2 | 1188.4 | 0.69004 | 7.342
2024-12-09 | 14:49 | Data | 0 | 30.232 | 26.971 | 238.782 | 7.63 | 222.601 | 2076.1 | 26.02 | 41.304 | 6.25 | 1.492 | 5.81 | 8892.96 | 3.2 | 98 | 79.6 | 1349 | 20.65 | 5780.4 | 3514.3 | 3406.4 | 4979.8 | 1188.4 | 0.68817 | 7.304
2024-12-09 | 14:49 | Data | 0 | 29.996 | 26.843 | 238.42 | 7.63 | 222.556 | 2074.29 | 26.02 | 41.123 | 6.25 | 1.495 | 5.815 | 8897.48 | 3.004 | 98 | 79.6 | 1348 | 20.61 | 5783.4 | 3516.3 | 3421.3 | 4999.4 | 1188.4 | 0.68833 | 7.308
2024-12-09 | 14:49 | Data | 0 | 29.955 | 26.951 | 238.601 | 7.63 | 222.511 | 2076.1 | 26.02 | 41.394 | 6.25 | 1.494 | 5.828 | 8883.91 | 3.018 | 98 | 79.6 | 1349 | 20.65 | 5774.5 | 3499.3 | 3434 | 5001.8 | 1188.4 | 0.68597 | 7.322
2024-12-09 | 14:49 | Data | 0 | 30.023 | 26.823 | 238.466 | 7.63 | 222.601 | 2067.97 | 26.02 | 41.123 | 6.25 | 1.5 | 5.833 | 8874.87 | 2.883 | 98 | 79.5 | 1344 | 20.56 | 5768.7 | 3516.5 | 3424.7 | 5008.7 | 1188.4 | 0.68708 | 7.333
2024-12-09 | 14:49 | Data | 0 | 30.131 | 26.978 | 238.601 | 7.63 | 222.647 | 2072.49 | 26.01 | 41.213 | 6.25 | 1.499 | 5.847 | 8911.05 | 2.984 | 98 | 79.6 | 1347 | 20.65 | 5792.2 | 3503.8 | 3401.9 | 4981 | 1188.4 | 0.68852 | 7.346
2024-12-09 | 14:49 | Data | 0 | 30.225 | 26.965 | 238.601 | 7.63 | 222.601 | 2020.97 | 26.02 | 41.213 | 6.25 | 1.496 | 5.829 | 8888.44 | 2.937 | 98 | 79.6 | 1314 | 20.61 | 5777.5 | 3514 | 3424.5 | 4985.2 | 1188.4 | 0.68801 | 7.326
2024-12-09 | 14:49 | Data | 0 | 30.293 | 27.093 | 238.692 | 7.63 | 222.737 | 2020.97 | 26.02 | 41.213 | 6.25 | 1.489 | 5.824 | 8897.48 | 3.22 | 98 | 79.7 | 1314 | 20.56 | 5783.4 | 3503.2 | 3397.9 | 4976.3 | 1188.4 | 0.68967 | 7.315
2024-12-09 | 14:49 | Data | 0 | 30.158 | 27.086 | 238.511 | 7.63 | 222.647 | 2020.07 | 26.02 | 41.304 | 6.25 | 1.494 | 5.81 | 8906.53 | 3.052 | 98 | 79.5 | 1313 | 20.65 | 5789.2 | 3500.4 | 3393.2 | 4976.5 | 1188.4 | 0.68964 | 7.304
2024-12-09 | 14:49 | Data | 0 | 30.455 | 27.221 | 238.647 | 7.62 | 222.421 | 2020.97 | 26.02 | 41.213 | 6.25 | 1.5 | 5.813 | 8888.44 | 3.227 | 98 | 79.5 | 1314 | 20.65 | 5777.5 | 3519.7 | 3386.5 | 4977.3 | 1188.4 | 0.69307 | 7.313
2024-12-09 | 14:50 | Data | 0 | 29.888 | 26.728 | 238.42 | 7.63 | 222.466 | 2073.39 | 26.01 | 41.304 | 6.25 | 1.497 | 5.814 | 8883.91 | 3.214 | 98 | 79.5 | 1347 | 20.65 | 5774.5 | 3493.1 | 3374.5 | 4952.2 | 1188.4 | 0.69068 | 7.31
2024-12-09 | 14:50 | Data | 0 | 29.969 | 27.14 | 238.42 | 7.63 | 222.511 | 2067.97 | 26.02 | 41.213 | 6.25 | 1.498 | 5.847 | 8906.53 | 2.815 | 98 | 79.6 | 1344 | 20.61 | 5789.2 | 3492.7 | 3400.1 | 4966.4 | 1188.4 | 0.68903 | 7.345
2024-12-09 | 14:50 | Data | 0 | 29.847 | 27.127 | 238.285 | 7.63 | 222.556 | 2071.58 | 26.02 | 41.213 | 6.25 | 1.502 | 5.848 | 8902 | 2.991 | 98 | 79.6 | 1346 | 20.61 | 5786.3 | 3497.2 | 3420.6 | 4984.4 | 1188.4 | 0.68753 | 7.352
2024-12-09 | 14:50 | Data | 0 | 30.185 | 26.971 | 238.556 | 7.63 | 222.601 | 2070.68 | 26.02 | 41.123 | 6.24 | 1.5 | 5.803 | 8883.91 | 3.085 | 98 | 79.5 | 1345 | 20.56 | 5774.5 | 3514.5 | 3431.6 | 5005.6 | 1188.4 | 0.68724 | 7.304
2024-12-09 | 14:50 | Data | 0 | 29.463 | 27.1 | 238.511 | 7.63 | 222.511 | 2073.39 | 26.02 | 41.213 | 6.24 | 1.492 | 5.81 | 8897.48 | 2.883 | 98 | 79.6 | 1347 | 20.61 | 5783.4 | 3508.5 | 3445.7 | 5011.2 | 1188.4 | 0.68587 | 7.303
2024-12-09 | 14:50 | Data | 0 | 29.733 | 26.789 | 238.375 | 7.63 | 222.421 | 2069.78 | 26.02 | 41.304 | 6.25 | 1.491 | 5.825 | 8892.96 | 3.22 | 98 | 79.6 | 1346 | 20.65 | 5780.4 | 3503.9 | 3455.6 | 5011.2 | 1188.4 | 0.68366 | 7.314
2024-12-09 | 14:50 | Data | 0 | 30.273 | 27.248 | 238.647 | 7.63 | 222.647 | 2073.39 | 26.02 | 41.304 | 6.25 | 1.496 | 5.836 | 8879.39 | 3.146 | 98 | 79.6 | 1348 | 20.65 | 5771.6 | 3503.7 | 3446.2 | 5007.2 | 1188.4 | 0.6844 | 7.332
2024-12-09 | 14:50 | Data | 0 | 29.746 | 27.052 | 238.33 | 7.63 | 222.375 | 2072.49 | 26.01 | 41.304 | 6.25 | 1.494 | 5.847 | 8902 | 2.761 | 98 | 79.7 | 1348 | 20.61 | 5786.3 | 3496.3 | 3476.5 | 5023.9 | 1188.4 | 0.68179 | 7.34
2024-12-09 | 14:50 | Data | 0 | 29.955 | 27.133 | 238.511 | 7.63 | 222.511 | 2072.49 | 26.02 | 41.213 | 6.25 | 1.489 | 5.84 | 8892.96 | 2.883 | 98 | 79.7 | 1347 | 20.65 | 5780.4 | 3488.6 | 3443.7 | 5003.8 | 1188.4 | 0.68283 | 7.329
2024-12-09 | 14:50 | Data | 0 | 29.955 | 26.863 | 238.466 | 7.63 | 222.601 | 2076.1 | 26.02 | 41.213 | 6.25 | 1.5 | 5.831 | 8911.05 | 3.193 | 98 | 79.5 | 1349 | 20.61 | 5792.2 | 3491 | 3451 | 5001.7 | 1188.4 | 0.68366 | 7.332
2024-12-09 | 14:50 | Data | 0 | 30.036 | 26.958 | 238.375 | 7.63 | 222.647 | 2075.2 | 26.02 | 41.213 | 6.25 | 1.491 | 5.826 | 8951.75 | 3.173 | 98 | 79.6 | 1349 | 20.61 | 5818.6 | 3485.9 | 3438.8 | 4992.5 | 1188.4 | 0.6837 | 7.317
2024-12-09 | 14:50 | Data | 0 | 29.942 | 26.951 | 238.511 | 7.63 | 222.511 | 2076.1 | 26.02 | 41.304 | 6.25 | 1.482 | 5.873 | 8924.61 | 3.011 | 98 | 79.8 | 1349 | 20.61 | 5801 | 3505.1 | 3454.6 | 5018.5 | 1188.4 | 0.68362 | 7.354
2024-12-09 | 14:50 | Data | 0 | 30.394 | 26.985 | 238.511 | 7.63 | 222.601 | 2075.2 | 26.02 | 41.213 | 6.25 | 1.493 | 5.819 | 8906.53 | 3.254 | 98 | 79.6 | 1349 | 20.65 | 5789.2 | 3497.4 | 3477.7 | 5025.3 | 1188.4 | 0.68073 | 7.313
2024-12-09 | 14:50 | Data | 0 | 30.124 | 27.343 | 238.511 | 7.63 | 222.556 | 2077.91 | 26.01 | 41.304 | 6.25 | 1.499 | 5.838 | 8920.09 | 3.018 | 98 | 79.6 | 1351 | 20.7 | 5798.1 | 3477.5 | 3473.4 | 5011.5 | 1188.4 | 0.67872 | 7.336
2024-12-09 | 14:50 | Data | 0 | 29.726 | 26.85 | 238.194 | 7.63 | 222.33 | 2078.81 | 26.01 | 41.123 | 6.25 | 1.492 | 5.838 | 8951.75 | 3.112 | 98 | 79.7 | 1351 | 20.65 | 5818.6 | 3490.7 | 3455.7 | 5004.2 | 1188.4 | 0.68271 | 7.329
2024-12-09 | 14:50 | Data | 0 | 29.733 | 26.728 | 238.42 | 7.63 | 222.511 | 2077.91 | 26.02 | 41.304 | 6.25 | 1.492 | 5.806 | 8938.18 | 3.004 | 98 | 79.6 | 1351 | 20.65 | 5809.8 | 3489 | 3478.1 | 5020.1 | 1188.4 | 0.67968 | 7.298
2024-12-09 | 14:50 | Data | 0 | 29.901 | 27.1 | 238.511 | 7.63 | 222.511 | 2076.1 | 26.03 | 41.304 | 6.25 | 1.494 | 5.809 | 9091.94 | 3.106 | 98 | 79.5 | 1349 | 20.61 | 5909.8 | 3499.7 | 3473.9 | 5023.5 | 1188.4 | 0.68218 | 7.303
2024-12-09 | 14:50 | Data | 0 | 29.841 | 27.133 | 238.556 | 7.63 | 222.511 | 2072.49 | 26.01 | 41.213 | 6.25 | 1.495 | 5.814 | 9069.33 | 2.971 | 98 | 79.5 | 1347 | 20.65 | 5895.1 | 3516.2 | 3467.8 | 5032.5 | 1188.4 | 0.68164 | 7.309
2024-12-09 | 14:51 | Data | 0 | 29.955 | 26.863 | 238.466 | 7.63 | 222.421 | 2075.2 | 26.02 | 41.304 | 6.25 | 1.491 | 5.828 | 9078.37 | 2.998 | 98 | 79.6 | 1349 | 20.61 | 5900.9 | 3490.5 | 3495.9 | 5032.3 | 1188.4 | 0.67911 | 7.319
2024-12-09 | 14:51 | Data | 0 | 30.178 | 26.992 | 238.556 | 7.63 | 222.556 | 2073.39 | 26.03 | 41.213 | 6.25 | 1.486 | 5.831 | 9069.33 | 3.193 | 98 | 79.7 | 1348 | 20.61 | 5895.1 | 3489.5 | 3484.3 | 5025.6 | 1188.4 | 0.67943 | 7.316
2024-12-09 | 14:51 | Data | 0 | 29.834 | 27.268 | 238.511 | 7.63 | 222.601 | 2072.49 | 26.02 | 41.304 | 6.25 | 1.497 | 5.837 | 8879.39 | 3.025 | 98 | 79.6 | 1348 | 20.61 | 5771.6 | 3489.3 | 3463.4 | 5011.1 | 1188.5 | 0.68128 | 7.335
2024-12-09 | 14:51 | Data | 0 | 29.955 | 27.187 | 238.375 | 7.63 | 222.556 | 2076.1 | 26.02 | 41.213 | 6.25 | 1.493 | 5.851 | 8865.83 | 2.964 | 98 | 79.7 | 1349 | 20.65 | 5762.8 | 3515.7 | 3492.8 | 5047.5 | 1188.5 | 0.68106 | 7.344
2024-12-09 | 14:51 | Data | 0 | 29.962 | 26.803 | 238.601 | 7.63 | 222.601 | 2073.39 | 26.01 | 41.304 | 6.25 | 1.486 | 5.845 | 8843.21 | 2.937 | 98 | 79.7 | 1348 | 20.65 | 5748.1 | 3499.2 | 3485.5 | 5030.4 | 1188.5 | 0.68241 | 7.332
2024-12-09 | 14:51 | Data | 0 | 30.016 | 27.194 | 238.511 | 7.63 | 222.466 | 2065.26 | 26.02 | 41.213 | 6.24 | 1.492 | 5.838 | 8870.35 | 3.187 | 98 | 79.6 | 1342 | 20.61 | 5765.7 | 3490.2 | 3442.5 | 5001.5 | 1188.5 | 0.68374 | 7.329
2024-12-09 | 14:51 | Data | 0 | 30.117 | 27.511 | 238.692 | 7.63 | 222.692 | 2076.1 | 26.03 | 41.213 | 6.25 | 1.489 | 5.8 | 8883.91 | 2.998 | 98 | 79.6 | 1349 | 20.61 | 5774.5 | 3488.6 | 3443.2 | 4997.4 | 1188.5 | 0.68356 | 7.29
2024-12-09 | 14:51 | Data | 0 | 29.949 | 26.965 | 238.963 | 7.63 | 222.827 | 2071.58 | 26.02 | 41.394 | 6.26 | 1.492 | 5.819 | 8915.57 | 2.991 | 98 | 79.6 | 1348 | 20.65 | 5795.1 | 3498.5 | 3434.9 | 4999.2 | 1188.5 | 0.68446 | 7.313
2024-12-09 | 14:51 | Data | 0 | 29.679 | 27.1 | 239.008 | 7.63 | 222.963 | 2072.49 | 26.01 | 41.213 | 6.25 | 1.494 | 5.834 | 8902 | 2.937 | 98 | 79.6 | 1348 | 20.61 | 5786.3 | 3511.2 | 3490 | 5047.5 | 1188.5 | 0.68002 | 7.328
2024-12-09 | 14:51 | Data | 0 | 30.327 | 27.133 | 238.828 | 7.63 | 223.053 | 2074.29 | 26.01 | 41.213 | 6.25 | 1.496 | 5.831 | 8906.53 | 3.106 | 98 | 79.6 | 1348 | 20.7 | 5789.2 | 3505.2 | 3527.3 | 5067.1 | 1188.5 | 0.67716 | 7.329
2024-12-09 | 14:51 | Data | 0 | 29.739 | 26.735 | 238.873 | 7.63 | 222.737 | 2071.58 | 26.03 | 41.304 | 6.26 | 1.495 | 5.84 | 8883.91 | 2.991 | 98 | 79.6 | 1348 | 20.7 | 5774.5 | 3515.5 | 3478.9 | 5038.8 | 1188.5 | 0.68269 | 7.337
2024-12-09 | 14:51 | Data | 0 | 30.009 | 27.079 | 238.873 | 7.63 | 222.827 | 2073.39 | 26 | 41.304 | 6.25 | 1.496 | 5.849 | 8892.96 | 2.883 | 98 | 79.6 | 1348 | 20.65 | 5780.4 | 3501.3 | 3498.1 | 5044.5 | 1188.5 | 0.67966 | 7.344
2024-12-09 | 14:51 | Data | 0 | 29.814 | 27.16 | 238.828 | 7.63 | 222.782 | 2074.29 | 26.02 | 41.304 | 6.25 | 1.487 | 5.834 | 8870.35 | 2.984 | 98 | 79.7 | 1349 | 20.7 | 5765.7 | 3515.5 | 3518.7 | 5065.1 | 1188.5 | 0.67668 | 7.321
2024-12-09 | 14:51 | Data | 0 | 29.847 | 27.275 | 238.828 | 7.63 | 222.963 | 2076.1 | 26.02 | 41.213 | 6.25 | 1.492 | 5.847 | 8883.91 | 2.984 | 98 | 79.7 | 1349 | 20.61 | 5774.5 | 3517.8 | 3555 | 5086.5 | 1188.5 | 0.67492 | 7.34
2024-12-09 | 14:51 | Data | 0 | 29.901 | 26.951 | 238.828 | 7.63 | 222.963 | 2073.39 | 26.01 | 41.304 | 6.25 | 1.498 | 5.842 | 8883.91 | 3.004 | 98 | 79.6 | 1348 | 20.65 | 5774.5 | 3487.4 | 3513.7 | 5050.4 | 1188.5 | 0.67514 | 7.34
2024-12-09 | 14:51 | Data | 0 | 30.394 | 26.971 | 238.873 | 7.63 | 223.098 | 2076.1 | 26.02 | 41.213 | 6.26 | 1.489 | 5.838 | 8879.39 | 2.93 | 98 | 79.7 | 1349 | 20.61 | 5771.6 | 3471.5 | 3536.6 | 5059.3 | 1188.5 | 0.67309 | 7.325
2024-12-09 | 14:51 | Data | 0 | 30.307 | 26.776 | 238.828 | 7.63 | 222.963 | 2075.2 | 26.02 | 41.033 | 6.26 | 1.494 | 5.837 | 8879.39 | 3.22 | 98 | 79.6 | 1348 | 20.52 | 5771.6 | 3499.7 | 3465.5 | 5023.2 | 1188.5 | 0.6823 | 7.331
2024-12-09 | 14:52 | Data | 0 | 30.07 | 26.978 | 239.054 | 7.63 | 223.008 | 2077.91 | 26.02 | 41.304 | 6.25 | 1.5 | 5.838 | 8888.44 | 3.153 | 98 | 79.6 | 1351 | 20.65 | 5777.5 | 3482.6 | 3472.4 | 5015.8 | 1188.5 | 0.67869 | 7.338
2024-12-09 | 14:52 | Data | 0 | 30.198 | 26.796 | 238.873 | 7.63 | 223.008 | 2081.53 | 26.01 | 41.213 | 6.25 | 1.488 | 5.861 | 8861.3 | 2.991 | 98 | 79.8 | 1353 | 20.61 | 5759.8 | 3497.8 | 3496.8 | 5041.3 | 1188.5 | 0.6784 | 7.349
2024-12-09 | 14:52 | Data | 0 | 30.28 | 26.742 | 238.963 | 7.63 | 222.873 | 2075.2 | 26.03 | 41.213 | 6.25 | 1.49 | 5.867 | 8838.69 | 3.436 | 98 | 79.8 | 1349 | 20.65 | 5745.1 | 3502.2 | 3512.4 | 5050.3 | 1188.5 | 0.67937 | 7.356
2024-12-09 | 14:52 | Data | 0 | 30.32 | 26.85 | 238.828 | 7.63 | 223.008 | 2084.24 | 26.02 | 41.033 | 6.26 | 1.492 | 5.827 | 8856.78 | 2.91 | 98 | 79.6 | 1355 | 20.47 | 5756.9 | 3515.7 | 3530.4 | 5076.6 | 1188.5 | 0.67713 | 7.319
2024-12-09 | 14:52 | Data | 0 | 29.928 | 26.965 | 238.782 | 7.64 | 222.782 | 2086.04 | 26.01 | 41.033 | 6.26 | 1.495 | 5.849 | 8861.3 | 3.16 | 98 | 79.6 | 1357 | 20.52 | 5759.8 | 3492.4 | 3544.8 | 5076.2 | 1188.5 | 0.67312 | 7.345
2024-12-09 | 14:52 | Data | 0 | 29.901 | 27.073 | 238.963 | 7.63 | 222.873 | 2092.37 | 26.02 | 41.033 | 6.26 | 1.496 | 5.828 | 8843.21 | 2.876 | 98 | 79.6 | 1361 | 20.52 | 5748.1 | 3511.1 | 3562.6 | 5094.2 | 1188.5 | 0.67491 | 7.323
2024-12-09 | 14:52 | Data | 0 | 29.672 | 26.728 | 238.828 | 7.63 | 222.827 | 2084.24 | 26.02 | 40.852 | 6.26 | 1.49 | 5.837 | 8897.48 | 3.146 | 98 | 79.7 | 1355 | 20.38 | 5783.4 | 3515.8 | 3569.9 | 5103.4 | 1188.5 | 0.67435 | 7.326
2024-12-09 | 14:52 | Data | 0 | 29.901 | 27.174 | 238.828 | 7.63 | 222.963 | 2083.33 | 26.02 | 40.943 | 6.26 | 1.491 | 5.844 | 8897.48 | 3.106 | 98 | 79.7 | 1354 | 20.52 | 5783.4 | 3506 | 3562.3 | 5093.8 | 1188.5 | 0.67341 | 7.335
2024-12-09 | 14:52 | Data | 0 | 29.726 | 26.924 | 238.737 | 7.63 | 222.782 | 2083.33 | 26.02 | 43.29 | 6.25 | 1.489 | 5.83 | 8911.05 | 2.964 | 97.9 | 79.7 | 1355 | 21.64 | 5792.2 | 3507.1 | 3584.1 | 5116.5 | 1188.5 | 0.67217 | 7.319
2024-12-09 | 14:52 | Data | 0 | 30.097 | 27.235 | 239.008 | 7.63 | 222.963 | 2078.81 | 26.01 | 43.2 | 6.25 | 1.5 | 5.812 | 8911.05 | 3.025 | 97.9 | 79.5 | 1351 | 21.6 | 5792.2 | 3491.5 | 3573 | 5090.1 | 1188.5 | 0.67008 | 7.313
2024-12-09 | 14:52 | Data | 0 | 29.874 | 26.965 | 238.873 | 7.63 | 222.873 | 2076.1 | 26.02 | 41.484 | 6.26 | 1.498 | 5.824 | 8897.48 | 2.788 | 98 | 79.5 | 1349 | 20.74 | 5783.4 | 3507.6 | 3539.6 | 5077.1 | 1188.5 | 0.67613 | 7.322
2024-12-09 | 14:52 | Data | 0 | 29.928 | 26.965 | 239.054 | 7.63 | 223.053 | 2078.81 | 26.02 | 41.304 | 6.25 | 1.494 | 5.834 | 8883.91 | 2.984 | 98 | 79.6 | 1351 | 20.7 | 5774.5 | 3516.1 | 3548.4 | 5092.9 | 1188.5 | 0.67516 | 7.328
2024-12-09 | 14:52 | Data | 0 | 30.03 | 26.796 | 238.782 | 7.63 | 223.008 | 2077.91 | 26.02 | 41.304 | 6.26 | 1.492 | 5.838 | 8902 | 2.937 | 98 | 79.6 | 1351 | 20.61 | 5786.3 | 3516 | 3563.7 | 5099.1 | 1188.5 | 0.67444 | 7.331
2024-12-09 | 14:52 | Data | 0 | 30.34 | 27.079 | 239.054 | 7.63 | 223.008 | 2078.81 | 26.02 | 41.213 | 6.26 | 1.492 | 5.829 | 8499.53 | 3.092 | 98 | 79.6 | 1351 | 20.61 | 5524.7 | 3487.7 | 3575.8 | 5091.8 | 1188.5 | 0.66944 | 7.321
2024-12-09 | 14:52 | Data | 0 | 30.063 | 26.755 | 239.054 | 7.63 | 223.098 | 2077.01 | 26.02 | 41.213 | 6.25 | 1.496 | 5.848 | 8874.87 | 3.079 | 98 | 79.6 | 1351 | 20.61 | 5768.7 | 3488.5 | 3596.1 | 5103.5 | 1188.5 | 0.66898 | 7.344
2024-12-09 | 14:52 | Data | 0 | 30.225 | 27.012 | 238.873 | 7.63 | 222.873 | 2077.91 | 26.02 | 41.213 | 6.26 | 1.498 | 5.836 | 8883.91 | 3.308 | 98 | 79.6 | 1351 | 20.61 | 5774.5 | 3509.6 | 3597.5 | 5119.2 | 1188.5 | 0.67038 | 7.333
2024-12-09 | 14:52 | Data | 0 | 29.726 | 26.742 | 238.828 | 7.63 | 222.827 | 2073.39 | 26.02 | 41.304 | 6.26 | 1.503 | 5.848 | 8865.83 | 3.146 | 98 | 79.6 | 1348 | 20.65 | 5762.8 | 3502.7 | 3598.2 | 5115.2 | 1188.6 | 0.66964 | 7.352
2024-12-09 | 14:52 | Data | 0 | 29.949 | 27.174 | 238.873 | 7.63 | 222.873 | 2078.81 | 26.01 | 41.304 | 6.26 | 1.501 | 5.825 | 8865.83 | 2.964 | 98 | 79.5 | 1352 | 20.65 | 5762.8 | 3515.5 | 3621.8 | 5140.8 | 1188.6 | 0.66979 | 7.327
2024-12-09 | 14:52 | Data | 0 | 29.746 | 27.079 | 238.782 | 7.63 | 222.963 | 2078.81 | 26.02 | 41.304 | 6.26 | 1.514 | 5.838 | 8874.87 | 2.768 | 98 | 79.4 | 1352 | 20.65 | 5768.7 | 3504.2 | 3590.7 | 5110 | 1188.6 | 0.6707 | 7.351
2024-12-09 | 14:53 | Data | 0 | 29.726 | 27.073 | 238.873 | 7.63 | 222.827 | 2081.53 | 26.02 | 41.213 | 6.25 | 1.503 | 5.867 | 8874.87 | 3.099 | 98 | 79.6 | 1353 | 20.61 | 5768.7 | 3511.7 | 3597.9 | 5119.1 | 1188.6 | 0.67158 | 7.37
2024-12-09 | 14:53 | Data | 0 | 30.009 | 26.965 | 238.873 | 7.63 | 222.827 | 2077.91 | 26.02 | 41.213 | 6.25 | 1.497 | 5.85 | 8883.91 | 2.89 | 98 | 79.6 | 1351 | 20.61 | 5774.5 | 3504 | 3581.9 | 5102.5 | 1188.6 | 0.67201 | 7.347
2024-12-09 | 14:53 | Data | 0 | 29.955 | 26.924 | 239.099 | 7.63 | 222.963 | 2082.43 | 26.01 | 41.304 | 6.25 | 1.5 | 5.844 | 8883.91 | 3.16 | 98 | 79.6 | 1353 | 20.61 | 5774.5 | 3495.7 | 3581.4 | 5107.9 | 1188.6 | 0.67204 | 7.344
2024-12-09 | 14:53 | Data | 0 | 30.232 | 26.755 | 239.054 | 7.63 | 223.053 | 2077.91 | 26.02 | 41.304 | 6.25 | 1.499 | 5.848 | 8861.3 | 3.045 | 98 | 79.6 | 1351 | 20.61 | 5759.8 | 3508 | 3588.9 | 5109.6 | 1188.6 | 0.67164 | 7.345
2024-12-09 | 14:53 | Data | 0 | 30.185 | 27.39 | 239.144 | 7.63 | 223.144 | 2076.1 | 26.01 | 41.213 | 6.25 | 1.499 | 5.843 | 8870.35 | 2.903 | 98 | 79.6 | 1349 | 20.61 | 5765.7 | 3490.7 | 3578.6 | 5095 | 1188.6 | 0.67006 | 7.342
2024-12-09 | 14:53 | Data | 0 | 30.185 | 27.133 | 239.235 | 7.63 | 223.053 | 2072.49 | 26.02 | 41.575 | 6.25 | 1.5 | 5.831 | 8874.87 | 2.977 | 98 | 79.5 | 1347 | 20.79 | 5768.7 | 3498.3 | 3579.7 | 5100.4 | 1188.6 | 0.67362 | 7.332
2024-12-09 | 14:53 | Data | 0 | 29.982 | 26.789 | 238.692 | 7.63 | 222.647 | 2070.68 | 26.02 | 41.213 | 6.26 | 1.484 | 5.84 | 8888.44 | 2.971 | 98 | 79.7 | 1346 | 20.65 | 5777.5 | 3503.9 | 3562.2 | 5094.4 | 1188.6 | 0.67178 | 7.327
2024-12-09 | 14:53 | Data | 0 | 29.982 | 27.268 | 239.008 | 7.63 | 222.963 | 2069.78 | 26.02 | 41.304 | 6.26 | 1.494 | 5.824 | 8879.39 | 2.802 | 98 | 79.6 | 1347 | 20.7 | 5771.6 | 3511 | 3614.6 | 5131.7 | 1188.6 | 0.66972 | 7.318
2024-12-09 | 14:53 | Data | 0 | 30.28 | 27.14 | 239.008 | 7.63 | 223.008 | 2069.78 | 26.02 | 41.213 | 6.25 | 1.49 | 5.844 | 8897.48 | 3.112 | 98 | 79.7 | 1345 | 20.61 | 5783.4 | 3513.2 | 3580.3 | 5108.8 | 1188.6 | 0.67231 | 7.333
2024-12-09 | 14:53 | Data | 0 | 29.969 | 27.302 | 238.873 | 7.63 | 222.963 | 2071.58 | 26.01 | 41.213 | 6.25 | 1.491 | 5.847 | 8874.87 | 2.971 | 98 | 79.7 | 1347 | 20.65 | 5768.7 | 3502.6 | 3622.2 | 5131.5 | 1188.6 | 0.66869 | 7.339
2024-12-09 | 14:53 | Data | 0 | 29.733 | 26.951 | 238.828 | 7.63 | 222.782 | 2070.68 | 26.02 | 41.213 | 6.25 | 1.502 | 5.844 | 8883.91 | 2.991 | 98 | 79.6 | 1347 | 20.65 | 5774.5 | 3499 | 3619.1 | 5127.5 | 1188.6 | 0.66757 | 7.346
2024-12-09 | 14:53 | Data | 0 | 29.955 | 26.728 | 238.782 | 7.63 | 222.963 | 2073.39 | 26 | 41.213 | 6.26 | 1.501 | 5.831 | 8915.57 | 3.025 | 98 | 79.5 | 1347 | 20.65 | 5795.1 | 3502.4 | 3639.5 | 5144.8 | 1188.6 | 0.66478 | 7.333
2024-12-09 | 14:53 | Data | 0 | 30.212 | 27.079 | 239.144 | 7.63 | 223.008 | 2073.39 | 26.02 | 41.213 | 6.25 | 1.496 | 5.812 | 8915.57 | 3.18 | 98 | 79.5 | 1347 | 20.65 | 5795.1 | 3517 | 3641.6 | 5153.7 | 1188.6 | 0.66727 | 7.306
2024-12-09 | 14:53 | Data | 0 | 29.706 | 26.904 | 238.963 | 7.63 | 222.873 | 2073.39 | 26.02 | 41.304 | 6.25 | 1.481 | 5.83 | 8897.48 | 2.788 | 98 | 79.7 | 1347 | 20.61 | 5783.4 | 3507.5 | 3626.5 | 5142.2 | 1188.6 | 0.66599 | 7.311
2024-12-09 | 14:53 | Data | 0 | 29.928 | 26.958 | 238.873 | 7.63 | 222.827 | 2072.49 | 26.03 | 41.213 | 6.25 | 1.485 | 5.84 | 8902 | 2.991 | 98 | 79.7 | 1348 | 20.61 | 5786.3 | 3517.9 | 3593.4 | 5121.5 | 1188.6 | 0.67248 | 7.325
2024-12-09 | 14:53 | Data | 0 | 29.955 | 26.965 | 238.828 | 7.63 | 222.963 | 2073.39 | 26.02 | 41.304 | 6.25 | 1.493 | 5.855 | 8888.44 | 2.991 | 98 | 79.7 | 1347 | 20.65 | 5777.5 | 3532.6 | 3581.8 | 5115.2 | 1188.6 | 0.67339 | 7.349
2024-12-09 | 14:53 | Data | 0 | 29.982 | 27.187 | 239.008 | 7.63 | 222.963 | 2076.1 | 26.02 | 41.213 | 6.25 | 1.5 | 5.84 | 8861.3 | 2.782 | 98 | 79.6 | 1350 | 20.61 | 5759.8 | 3510.6 | 3581.2 | 5109.3 | 1188.6 | 0.67199 | 7.339
2024-12-09 | 14:54 | Data | 0 | 29.955 | 27.106 | 239.099 | 7.63 | 223.144 | 2073.39 | 26.02 | 41.304 | 6.25 | 1.503 | 5.844 | 8856.78 | 2.957 | 98 | 79.5 | 1347 | 20.65 | 5756.9 | 3505.5 | 3569 | 5097 | 1188.6 | 0.67263 | 7.349
2024-12-09 | 14:54 | Data | 0 | 29.861 | 26.789 | 239.099 | 7.63 | 222.963 | 2073.39 | 26.03 | 41.213 | 6.25 | 1.501 | 5.841 | 8888.44 | 2.815 | 98 | 79.6 | 1348 | 20.61 | 5777.5 | 3484.5 | 3603 | 5106.3 | 1188.6 | 0.66749 | 7.342
2024-12-09 | 14:54 | Data | 0 | 29.726 | 26.728 | 238.828 | 7.63 | 222.827 | 2073.39 | 26.02 | 41.304 | 6.25 | 1.499 | 5.845 | 8865.83 | 2.998 | 98 | 79.6 | 1347 | 20.65 | 5762.8 | 3516.8 | 3641.4 | 5156.2 | 1188.6 | 0.66655 | 7.343
2024-12-09 | 14:54 | Data | 0 | 29.726 | 26.904 | 239.054 | 7.63 | 222.963 | 2072.49 | 26.02 | 41.304 | 6.25 | 1.487 | 5.847 | 8843.21 | 2.998 | 98 | 79.7 | 1347 | 20.61 | 5748.1 | 3509.1 | 3585.9 | 5109.5 | 1188.6 | 0.67201 | 7.333
2024-12-09 | 14:54 | Data | 0 | 29.949 | 26.782 | 238.873 | 7.63 | 223.053 | 2073.39 | 26.01 | 41.213 | 6.26 | 1.492 | 5.863 | 8838.69 | 3.004 | 98 | 79.7 | 1347 | 20.65 | 5745.1 | 3480.2 | 3601.3 | 5099.1 | 1188.6 | 0.66757 | 7.356
2024-12-09 | 14:54 | Data | 0 | 29.935 | 26.951 | 238.828 | 7.63 | 222.782 | 2072.49 | 26.02 | 41.304 | 6.26 | 1.488 | 5.807 | 8838.69 | 2.998 | 98 | 79.6 | 1348 | 20.65 | 5745.1 | 3513.6 | 3631.1 | 5147.2 | 1188.6 | 0.6675 | 7.295
2024-12-09 | 14:54 | Data | 0 | 29.949 | 26.728 | 239.008 | 7.63 | 223.053 | 2076.1 | 26.02 | 41.123 | 6.26 | 1.505 | 5.822 | 8834.17 | 3.004 | 98 | 79.5 | 1349 | 20.61 | 5742.2 | 3508.5 | 3600.6 | 5119.1 | 1188.6 | 0.66927 | 7.327
2024-12-09 | 14:54 | Data | 0 | 30.293 | 27.025 | 239.054 | 7.63 | 223.008 | 2074.29 | 26.01 | 41.213 | 6.26 | 1.502 | 5.85 | 8870.35 | 2.991 | 98 | 79.6 | 1350 | 20.65 | 5765.7 | 3502.6 | 3618.4 | 5133.4 | 1188.6 | 0.66665 | 7.353
2024-12-09 | 14:54 | Data | 0 | 30.205 | 27.019 | 238.963 | 7.63 | 222.963 | 2081.53 | 26.02 | 41.123 | 6.26 | 1.495 | 5.841 | 8874.87 | 2.822 | 98 | 79.6 | 1353 | 20.61 | 5768.7 | 3518.2 | 3584.1 | 5115.2 | 1188.6 | 0.67291 | 7.337
2024-12-09 | 14:54 | Data | 0 | 30.023 | 27.181 | 238.828 | 7.63 | 222.873 | 2082.43 | 26.02 | 41.213 | 6.26 | 1.495 | 5.818 | 8870.35 | 3.153 | 98 | 79.5 | 1353 | 20.61 | 5765.7 | 3499.8 | 3590.7 | 5119.2 | 1188.6 | 0.66913 | 7.314
2024-12-09 | 14:54 | Data | 0 | 29.955 | 26.965 | 238.963 | 7.63 | 222.963 | 2077.91 | 26.03 | 41.304 | 6.26 | 1.5 | 5.859 | 8856.78 | 2.977 | 98 | 79.6 | 1351 | 20.65 | 5756.9 | 3502.8 | 3605.9 | 5122 | 1188.7 | 0.66932 | 7.359
2024-12-09 | 14:54 | Data | 0 | 30.212 | 27.356 | 239.144 | 7.63 | 223.098 | 2082.43 | 26.02 | 41.213 | 6.25 | 1.496 | 5.858 | 8883.91 | 2.809 | 98 | 79.6 | 1353 | 20.61 | 5774.5 | 3512.3 | 3624.6 | 5138.2 | 1188.7 | 0.66975 | 7.355
2024-12-09 | 14:54 | Data | 0 | 30.239 | 27.039 | 238.873 | 7.63 | 222.827 | 2083.33 | 26.02 | 41.213 | 6.25 | 1.497 | 5.823 | 8865.83 | 2.944 | 98 | 79.6 | 1355 | 20.61 | 5762.8 | 3488.5 | 3602.9 | 5112.8 | 1188.7 | 0.66618 | 7.32
2024-12-09 | 14:54 | Data | 0 | 30.131 | 27.187 | 239.054 | 7.63 | 223.053 | 2082.43 | 26.02 | 41.304 | 6.25 | 1.507 | 5.84 | 8888.44 | 2.991 | 98 | 79.5 | 1353 | 20.61 | 5777.5 | 3503.1 | 3599.4 | 5112.8 | 1188.7 | 0.67039 | 7.348
2024-12-09 | 14:54 | Data | 0 | 30.34 | 26.998 | 239.054 | 7.63 | 223.144 | 2081.53 | 26.02 | 41.304 | 6.25 | 1.498 | 5.865 | 8888.44 | 3.247 | 98 | 79.7 | 1351 | 20.65 | 5777.5 | 3513.1 | 3622.7 | 5147 | 1188.7 | 0.6685 | 7.362
2024-12-09 | 14:54 | Data | 0 | 30.158 | 27.14 | 239.189 | 7.63 | 223.098 | 2078.81 | 26.02 | 41.304 | 6.25 | 1.484 | 5.834 | 8874.87 | 3.207 | 98 | 79.7 | 1351 | 20.7 | 5768.7 | 3507.2 | 3645.4 | 5151 | 1188.7 | 0.66636 | 7.321
2024-12-09 | 14:54 | Data | 0 | 30.185 | 27.025 | 238.963 | 7.63 | 223.008 | 2078.81 | 26.02 | 41.213 | 6.26 | 1.495 | 5.825 | 8856.78 | 2.984 | 98 | 79.6 | 1351 | 20.61 | 5756.9 | 3512.4 | 3646.4 | 5135.7 | 1188.7 | 0.66582 | 7.32
2024-12-09 | 14:54 | Data | 0 | 29.76 | 27.079 | 238.963 | 7.63 | 223.008 | 2078.81 | 26.01 | 41.213 | 6.25 | 1.491 | 5.85 | 8874.87 | 2.782 | 98 | 79.7 | 1351 | 20.61 | 5768.7 | 3497.4 | 3655.3 | 5156 | 1188.7 | 0.66522 | 7.342
2024-12-09 | 14:55 | Data | 0 | 29.841 | 26.951 | 238.963 | 7.63 | 222.737 | 2078.81 | 26.01 | 41.304 | 6.25 | 1.5 | 5.83 | 8874.87 | 2.998 | 98 | 79.5 | 1351 | 20.65 | 5768.7 | 3520.9 | 3680.2 | 5181.1 | 1188.7 | 0.66439 | 7.33
2024-12-09 | 14:55 | Data | 0 | 29.955 | 26.965 | 239.054 | 7.63 | 222.873 | 2077.91 | 26.01 | 40.762 | 6.26 | 1.49 | 5.841 | 8951.75 | 2.991 | 98 | 79.7 | 1351 | 20.43 | 5818.6 | 3502.1 | 3718 | 5198.4 | 1188.7 | 0.65848 | 7.329
2024-12-09 | 14:55 | Data | 0 | 30.354 | 26.823 | 239.008 | 7.63 | 223.098 | 2078.81 | 26.02 | 41.394 | 6.25 | 1.495 | 5.837 | 8951.75 | 3.187 | 98 | 79.6 | 1351 | 20.65 | 5818.6 | 3503.3 | 3737.6 | 5212.8 | 1188.7 | 0.65732 | 7.331
2024-12-09 | 14:55 | Data | 0 | 29.962 | 26.85 | 238.873 | 7.63 | 223.053 | 2078.81 | 26.01 | 41.213 | 6.26 | 1.509 | 5.841 | 8956.27 | 2.991 | 98 | 79.5 | 1351 | 20.65 | 5821.6 | 3512.4 | 3763.7 | 5229.6 | 1188.7 | 0.65687 | 7.35
2024-12-09 | 14:55 | Data | 0 | 29.888 | 26.735 | 239.008 | 7.63 | 222.963 | 2077.91 | 26.03 | 41.304 | 6.25 | 1.5 | 5.834 | 8947.23 | 2.903 | 98 | 79.6 | 1351 | 20.65 | 5815.7 | 3502.6 | 3743 | 5216.8 | 1188.7 | 0.65627 | 7.335
2024-12-09 | 14:55 | Data | 0 | 29.854 | 27.349 | 239.054 | 7.63 | 223.144 | 2078.81 | 26.02 | 41.304 | 6.25 | 1.487 | 5.829 | 9399.45 | 2.95 | 98 | 79.7 | 1351 | 20.61 | 6109.6 | 3528 | 3760.9 | 5242.9 | 1188.7 | 0.65724 | 7.316
2024-12-09 | 14:55 | Data | 0 | 29.949 | 26.897 | 238.963 | 7.63 | 222.873 | 2078.81 | 26.02 | 41.304 | 6.25 | 1.496 | 5.851 | 9381.36 | 3.119 | 98 | 79.6 | 1351 | 20.65 | 6097.9 | 3512.8 | 3728.2 | 5213.2 | 1188.7 | 0.65753 | 7.347
2024-12-09 | 14:55 | Data | 0 | 29.841 | 26.965 | 239.008 | 7.63 | 222.827 | 2078.81 | 26.02 | 41.213 | 6.25 | 1.489 | 5.85 | 8929.14 | 2.937 | 98 | 79.7 | 1351 | 20.65 | 5803.9 | 3513.9 | 3738.5 | 5221.8 | 1188.7 | 0.65817 | 7.339
2024-12-09 | 14:55 | Data | 0 | 29.726 | 26.755 | 238.647 | 7.63 | 222.782 | 2078.81 | 26.01 | 41.304 | 6.25 | 1.491 | 5.847 | 8915.57 | 3.058 | 98 | 79.7 | 1352 | 20.61 | 5795.1 | 3505.4 | 3766.4 | 5235.5 | 1188.7 | 0.65382 | 7.339
2024-12-09 | 14:55 | Data | 0 | 29.955 | 26.965 | 238.873 | 7.63 | 222.873 | 2077.91 | 26.02 | 41.213 | 6.26 | 1.501 | 5.838 | 8897.48 | 2.991 | 98 | 79.5 | 1351 | 20.61 | 5783.4 | 3514 | 3757 | 5236.8 | 1188.7 | 0.65583 | 7.339
2024-12-09 | 14:55 | Data | 0 | 30.415 | 27.019 | 239.054 | 7.63 | 223.098 | 2077.91 | 26.03 | 41.213 | 6.25 | 1.497 | 5.82 | 8883.91 | 3.018 | 98 | 79.6 | 1351 | 20.61 | 5774.5 | 3508 | 3756.7 | 5229.2 | 1188.7 | 0.65536 | 7.317
2024-12-09 | 14:55 | Data | 0 | 29.989 | 27.14 | 239.008 | 7.63 | 223.189 | 2077.91 | 26.02 | 41.304 | 6.25 | 1.493 | 5.819 | 8897.48 | 2.991 | 98 | 79.6 | 1351 | 20.65 | 5783.4 | 3499.3 | 3744.9 | 5216 | 1188.7 | 0.65577 | 7.312
2024-12-09 | 14:55 | Data | 0 | 29.76 | 27.106 | 238.873 | 7.63 | 223.053 | 2077.91 | 26.01 | 41.213 | 6.25 | 1.508 | 5.838 | 8902 | 2.795 | 98 | 79.5 | 1351 | 20.61 | 5786.3 | 3494.4 | 3761.7 | 5225.5 | 1188.7 | 0.65317 | 7.346
2024-12-09 | 14:55 | Data | 0 | 29.976 | 26.965 | 238.963 | 7.63 | 222.873 | 2082.43 | 26.01 | 41.213 | 6.25 | 1.504 | 5.825 | 8915.57 | 2.991 | 98 | 79.5 | 1354 | 20.61 | 5795.1 | 3493.7 | 3738.8 | 5209 | 1188.7 | 0.65484 | 7.329
2024-12-09 | 14:55 | Data | 0 | 29.901 | 26.836 | 239.551 | 7.63 | 223.596 | 2079.72 | 26.02 | 41.304 | 6.26 | 1.507 | 5.795 | 8911.05 | 3.112 | 98 | 79.4 | 1353 | 20.61 | 5792.2 | 3516.4 | 3739.2 | 5224.6 | 1188.7 | 0.65707 | 7.303
2024-12-09 | 14:55 | Data | 0 | 29.962 | 27.066 | 239.687 | 7.63 | 223.596 | 2082.43 | 26.03 | 41.394 | 6.26 | 1.499 | 5.855 | 8906.53 | 3.011 | 98 | 79.6 | 1354 | 20.65 | 5789.2 | 3496.7 | 3757.1 | 5221.8 | 1188.7 | 0.6545 | 7.354
2024-12-09 | 14:55 | Data | 0 | 29.976 | 26.735 | 239.597 | 7.63 | 223.686 | 2083.33 | 26.02 | 41.304 | 6.25 | 1.492 | 5.831 | 8911.05 | 3.2 | 98 | 79.6 | 1355 | 20.61 | 5792.2 | 3542.3 | 3744.1 | 5238.3 | 1188.7 | 0.6585 | 7.324
2024-12-09 | 14:55 | Data | 0 | 30.063 | 27.133 | 239.732 | 7.63 | 223.596 | 2087.85 | 26.02 | 41.213 | 6.26 | 1.492 | 5.829 | 8902 | 3.207 | 98 | 79.6 | 1357 | 20.61 | 5786.3 | 3528.5 | 3756.4 | 5248 | 1188.7 | 0.65702 | 7.318
2024-12-09 | 14:56 | Data | 0 | 30.063 | 26.85 | 239.777 | 7.63 | 223.596 | 2079.72 | 26.02 | 41.213 | 6.26 | 1.5 | 5.868 | 8915.57 | 3.052 | 98 | 79.6 | 1351 | 20.61 | 5795.1 | 3530.2 | 3771.1 | 5254.6 | 1188.7 | 0.65643 | 7.368
2024-12-09 | 14:56 | Data | 0 | 29.996 | 26.742 | 239.732 | 7.63 | 223.641 | 2084.24 | 26.02 | 40.943 | 6.26 | 1.5 | 5.863 | 8906.53 | 3.193 | 98 | 79.6 | 1355 | 20.47 | 5789.2 | 3514.6 | 3746.8 | 5227.9 | 1188.7 | 0.65703 | 7.363
2024-12-09 | 14:56 | Data | 0 | 29.726 | 26.681 | 239.642 | 7.63 | 223.686 | 2084.24 | 26.03 | 40.852 | 6.25 | 1.499 | 5.877 | 8915.57 | 3.099 | 98 | 79.7 | 1356 | 20.52 | 5795.1 | 3522.4 | 3770.3 | 5250.7 | 1188.7 | 0.65556 | 7.376
2024-12-09 | 14:56 | Data | 0 | 29.78 | 26.85 | 239.597 | 7.63 | 223.641 | 2085.14 | 26.02 | 41.033 | 6.26 | 1.499 | 5.876 | 8906.53 | 3.025 | 98 | 79.7 | 1355 | 20.52 | 5789.2 | 3510 | 3788.2 | 5257.8 | 1188.7 | 0.65194 | 7.374
2024-12-09 | 14:56 | Data | 0 | 29.928 | 26.843 | 239.551 | 7.63 | 223.55 | 2085.14 | 26.02 | 41.033 | 6.26 | 1.494 | 5.862 | 8888.44 | 3.112 | 98 | 79.7 | 1355 | 20.47 | 5777.5 | 3510.9 | 3780.2 | 5256.7 | 1188.8 | 0.65207 | 7.356
2024-12-09 | 14:56 | Data | 0 | 29.942 | 26.965 | 239.642 | 7.63 | 223.641 | 2084.24 | 26.02 | 41.033 | 6.26 | 1.502 | 5.849 | 8897.48 | 2.991 | 98 | 79.6 | 1355 | 20.52 | 5783.4 | 3507.9 | 3786.8 | 5249.9 | 1188.8 | 0.65314 | 7.352
2024-12-09 | 14:56 | Data | 0 | 30.131 | 26.965 | 239.777 | 7.63 | 223.596 | 1983.01 | 26.02 | 41.033 | 6.25 | 1.501 | 5.829 | 8902 | 3.214 | 97.9 | 79.5 | 1288 | 20.56 | 5786.3 | 3527.2 | 3767.2 | 5249.7 | 1188.8 | 0.65694 | 7.331
2024-12-09 | 14:56 | Data | 0 | 30.198 | 26.749 | 239.687 | 7.63 | 223.822 | 2082.43 | 26.01 | 41.213 | 6.25 | 1.495 | 5.825 | 8924.61 | 3.106 | 98 | 79.6 | 1354 | 20.65 | 5801 | 3501.2 | 3734.8 | 5212.3 | 1188.8 | 0.65612 | 7.321
2024-12-09 | 14:56 | Data | 0 | 30.34 | 27.073 | 239.777 | 7.63 | 223.596 | 2086.04 | 26.03 | 41.213 | 6.25 | 1.486 | 5.839 | 8897.48 | 3.085 | 98 | 79.7 | 1356 | 20.61 | 5783.4 | 3526 | 3750.7 | 5241.7 | 1188.8 | 0.6568 | 7.325
2024-12-09 | 14:56 | Data | 0 | 30.063 | 26.735 | 239.597 | 7.63 | 223.686 | 2086.95 | 26.02 | 41.213 | 6.25 | 1.5 | 5.858 | 8897.48 | 3.058 | 98 | 79.6 | 1357 | 20.61 | 5783.4 | 3526.8 | 3746.2 | 5235.5 | 1188.8 | 0.65827 | 7.358
2024-12-09 | 14:56 | Data | 0 | 29.955 | 26.735 | 239.597 | 7.63 | 223.641 | 2084.24 | 26.02 | 41.304 | 6.26 | 1.504 | 5.866 | 8897.48 | 3.085 | 98 | 79.6 | 1354 | 20.65 | 5783.4 | 3523.8 | 3750.4 | 5240.2 | 1188.8 | 0.65671 | 7.368
2024-12-09 | 14:56 | Data | 0 | 30.232 | 27.019 | 239.777 | 7.63 | 223.867 | 2085.14 | 26.02 | 41.213 | 6.26 | 1.495 | 5.863 | 8906.53 | 3.011 | 98 | 79.7 | 1355 | 20.61 | 5789.2 | 3530 | 3762.6 | 5254.6 | 1188.8 | 0.65533 | 7.359
2024-12-09 | 14:56 | Data | 0 | 29.962 | 27.14 | 239.777 | 7.63 | 223.731 | 2084.24 | 26.02 | 41.213 | 6.25 | 1.5 | 5.855 | 8974.36 | 2.998 | 98 | 79.6 | 1355 | 20.65 | 5833.3 | 3533.2 | 3764.8 | 5254 | 1188.8 | 0.65447 | 7.353
2024-12-09 | 14:56 | Data | 0 | 30.185 | 26.978 | 239.597 | 7.63 | 223.641 | 2086.95 | 26.03 | 41.304 | 6.26 | 1.513 | 5.867 | 8978.88 | 3.106 | 98 | 79.5 | 1357 | 20.61 | 5836.3 | 3509 | 3766.3 | 5240.6 | 1188.8 | 0.65471 | 7.383
2024-12-09 | 14:56 | Data | 0 | 29.739 | 26.85 | 239.732 | 7.63 | 223.867 | 2087.85 | 26 | 41.304 | 6.25 | 1.499 | 5.848 | 8978.88 | 2.991 | 98 | 79.6 | 1357 | 20.61 | 5836.3 | 3515.4 | 3751.3 | 5232.3 | 1188.8 | 0.65634 | 7.348
2024-12-09 | 14:56 | Data | 0 | 30.117 | 26.62 | 239.732 | 7.63 | 223.686 | 2086.04 | 26.02 | 41.304 | 6.26 | 1.507 | 5.857 | 8983.4 | 3.072 | 98 | 79.5 | 1357 | 20.61 | 5839.2 | 3504.8 | 3729 | 5208.8 | 1188.8 | 0.65505 | 7.362
2024-12-09 | 14:56 | Data | 0 | 29.726 | 26.789 | 239.687 | 7.63 | 223.641 | 2085.14 | 26.02 | 41.213 | 6.26 | 1.506 | 5.848 | 8965.31 | 2.971 | 98 | 79.5 | 1355 | 20.65 | 5827.5 | 3496.1 | 3726.5 | 5204.3 | 1188.8 | 0.65572 | 7.356
2024-12-09 | 14:57 | Data | 0 | 30.063 | 27.336 | 239.687 | 7.63 | 223.686 | 2083.33 | 26.02 | 41.304 | 6.25 | 1.509 | 5.831 | 8965.31 | 3.16 | 98 | 79.4 | 1355 | 20.65 | 5827.5 | 3515 | 3712.9 | 5204.8 | 1188.8 | 0.65989 | 7.34
2024-12-09 | 14:57 | Data | 0 | 30.185 | 27.194 | 239.868 | 7.63 | 223.867 | 2081.53 | 26.02 | 41.304 | 6.26 | 1.505 | 5.825 | 8965.31 | 2.991 | 98 | 79.5 | 1353 | 20.65 | 5827.5 | 3528.3 | 3720.7 | 5217.2 | 1188.8 | 0.66117 | 7.33
2024-12-09 | 14:57 | Data | 0 | 29.726 | 27.262 | 239.732 | 7.63 | 223.731 | 2088.76 | 26.02 | 41.213 | 6.26 | 1.493 | 5.861 | 8965.31 | 3.018 | 98 | 79.7 | 1357 | 20.65 | 5827.5 | 3523.6 | 3710.7 | 5206.4 | 1188.8 | 0.66118 | 7.354
2024-12-09 | 14:57 | Data | 0 | 29.847 | 26.803 | 239.913 | 7.63 | 223.822 | 2086.95 | 26.02 | 41.213 | 6.26 | 1.496 | 5.867 | 8978.88 | 3.112 | 98 | 79.7 | 1357 | 20.65 | 5836.3 | 3518.4 | 3725.7 | 5214.4 | 1188.8 | 0.65899 | 7.363
2024-12-09 | 14:57 | Data | 0 | 30.043 | 27.187 | 239.777 | 7.63 | 223.912 | 2085.14 | 26.02 | 41.213 | 6.26 | 1.497 | 5.831 | 8969.84 | 3.085 | 98 | 79.6 | 1355 | 20.65 | 5830.4 | 3502 | 3717.4 | 5200.7 | 1188.8 | 0.65836 | 7.329
2024-12-09 | 14:57 | Data | 0 | 29.908 | 26.735 | 239.913 | 7.63 | 223.822 | 2086.95 | 26.02 | 41.304 | 6.26 | 1.506 | 5.846 | 8992.45 | 2.896 | 98 | 79.5 | 1356 | 20.65 | 5845.1 | 3515.5 | 3711.5 | 5204.5 | 1188.8 | 0.65947 | 7.351
2024-12-09 | 14:57 | Data | 0 | 29.746 | 26.728 | 239.777 | 7.63 | 223.686 | 2086.95 | 26.02 | 41.213 | 6.25 | 1.504 | 5.838 | 8974.36 | 2.998 | 98 | 79.5 | 1357 | 20.7 | 5833.3 | 3503.1 | 3715.2 | 5194.2 | 1188.8 | 0.65951 | 7.342
2024-12-09 | 14:57 | Data | 0 | 29.895 | 26.56 | 239.551 | 7.63 | 223.596 | 2086.95 | 26.01 | 41.213 | 6.26 | 1.497 | 5.836 | 8996.97 | 3.214 | 98 | 79.6 | 1357 | 20.61 | 5848 | 3521.7 | 3709.7 | 5200.4 | 1188.8 | 0.66288 | 7.33
2024-12-09 | 14:57 | Data | 0 | 29.523 | 27.052 | 239.777 | 7.63 | 223.641 | 2087.85 | 26.02 | 41.304 | 6.26 | 1.493 | 5.849 | 8956.27 | 2.822 | 98 | 79.6 | 1357 | 20.61 | 5821.6 | 3511.4 | 3716 | 5203.3 | 1188.8 | 0.65907 | 7.345
2024-12-09 | 14:57 | Data | 0 | 30.3 | 27.086 | 239.913 | 7.63 | 223.731 | 2086.95 | 26.02 | 41.304 | 6.25 | 1.5 | 5.868 | 8978.88 | 2.822 | 98 | 79.6 | 1357 | 20.65 | 5836.3 | 3514.5 | 3714.8 | 5203.5 | 1188.8 | 0.65991 | 7.367
2024-12-09 | 14:57 | Data | 0 | 30.043 | 27.127 | 239.958 | 7.63 | 223.867 | 2086.95 | 26.02 | 41.304 | 6.25 | 1.503 | 5.857 | 8992.45 | 2.849 | 98 | 79.6 | 1357 | 20.65 | 5845.1 | 3496.4 | 3733.4 | 5207.1 | 1188.8 | 0.65671 | 7.361
2024-12-09 | 14:57 | Data | 0 | 29.726 | 26.728 | 239.777 | 7.63 | 223.686 | 2086.95 | 26.01 | 40.852 | 6.25 | 1.499 | 5.842 | 9010.54 | 3.2 | 98 | 79.6 | 1357 | 20.47 | 5856.8 | 3507.9 | 3707.1 | 5192.8 | 1188.8 | 0.66023 | 7.341
2024-12-09 | 14:57 | Data | 0 | 29.955 | 26.755 | 239.868 | 7.63 | 223.686 | 2086.95 | 26.02 | 41.033 | 6.26 | 1.507 | 5.843 | 8992.45 | 3.2 | 98 | 79.5 | 1355 | 20.52 | 5845.1 | 3499.5 | 3726.7 | 5202.2 | 1188.8 | 0.65776 | 7.35
2024-12-09 | 14:57 | Data | 0 | 30.07 | 26.965 | 239.868 | 7.63 | 223.686 | 2087.85 | 26.02 | 40.943 | 6.26 | 1.492 | 5.826 | 9001.49 | 3.207 | 98 | 79.6 | 1357 | 20.52 | 5851 | 3532.8 | 3722.6 | 5217.4 | 1188.8 | 0.66062 | 7.318
2024-12-09 | 14:57 | Data | 0 | 30.043 | 27.383 | 239.777 | 7.63 | 223.822 | 2089.66 | 26.02 | 41.033 | 6.26 | 1.495 | 5.827 | 8992.45 | 3.004 | 98 | 79.6 | 1358 | 20.56 | 5845.1 | 3518.1 | 3728.2 | 5219 | 1188.8 | 0.65854 | 7.323
2024-12-09 | 14:57 | Data | 0 | 30.144 | 27.032 | 240.049 | 7.63 | 223.822 | 2085.14 | 26.02 | 41.033 | 6.26 | 1.499 | 5.84 | 8965.31 | 2.923 | 98 | 79.6 | 1355 | 20.52 | 5827.5 | 3533.1 | 3710.7 | 5214.2 | 1188.8 | 0.66281 | 7.34
2024-12-09 | 14:57 | Data | 0 | 29.672 | 27.12 | 239.732 | 7.63 | 223.686 | 2085.14 | 26.02 | 40.943 | 6.26 | 1.5 | 5.845 | 8965.31 | 2.984 | 98 | 79.6 | 1355 | 20.47 | 5827.5 | 3502.7 | 3700.7 | 5187.8 | 1188.8 | 0.66003 | 7.342
2024-12-09 | 14:57 | Data | 0 | 30.489 | 27.032 | 239.913 | 7.63 | 223.822 | 2084.24 | 26.02 | 41.033 | 6.26 | 1.508 | 5.846 | 8938.18 | 3.207 | 98 | 79.5 | 1355 | 20.47 | 5809.8 | 3515.3 | 3673.4 | 5175.3 | 1188.8 | 0.66422 | 7.352
2024-12-09 | 14:58 | Data | 0 | 29.841 | 27.005 | 239.597 | 7.63 | 223.55 | 2084.24 | 26.02 | 41.123 | 6.25 | 1.501 | 5.848 | 8951.75 | 2.998 | 98 | 79.6 | 1355 | 20.56 | 5818.6 | 3498.1 | 3655.2 | 5153.4 | 1188.9 | 0.66403 | 7.349
2024-12-09 | 14:58 | Data | 0 | 29.955 | 27.289 | 239.642 | 7.63 | 223.822 | 2085.14 | 26.01 | 41.033 | 6.26 | 1.503 | 5.858 | 8965.31 | 2.937 | 98 | 79.6 | 1355 | 20.47 | 5827.5 | 3506.6 | 3670.9 | 5167.8 | 1188.9 | 0.66565 | 7.361
2024-12-09 | 14:58 | Data | 0 | 30.131 | 26.965 | 239.868 | 7.63 | 223.731 | 2086.04 | 26.01 | 41.033 | 6.25 | 1.495 | 5.855 | 8969.84 | 3.011 | 98 | 79.7 | 1357 | 20.52 | 5830.4 | 3515.5 | 3683.1 | 5183.6 | 1188.9 | 0.66281 | 7.35
2024-12-09 | 14:58 | Data | 0 | 29.766 | 26.951 | 239.777 | 7.63 | 223.686 | 2086.95 | 26.02 | 40.943 | 6.26 | 1.501 | 5.86 | 8978.88 | 2.822 | 98 | 79.6 | 1357 | 20.52 | 5836.3 | 3521.1 | 3671.2 | 5180.1 | 1188.9 | 0.66346 | 7.361
2024-12-09 | 14:58 | Data | 0 | 29.76 | 26.911 | 239.732 | 7.63 | 223.731 | 2086.04 | 26.03 | 41.033 | 6.25 | 1.497 | 5.829 | 8960.79 | 2.896 | 98 | 79.6 | 1356 | 20.52 | 5824.5 | 3532.4 | 3672.3 | 5186 | 1188.9 | 0.6661 | 7.325
2024-12-09 | 14:58 | Data | 0 | 29.888 | 27.133 | 239.687 | 7.63 | 223.55 | 2084.24 | 26.02 | 41.033 | 6.26 | 1.497 | 5.829 | 8956.27 | 3.085 | 98 | 79.6 | 1355 | 20.47 | 5821.6 | 3519.1 | 3647.9 | 5152.8 | 1188.9 | 0.66832 | 7.325
2024-12-09 | 14:58 | Data | 0 | 30.023 | 27.228 | 239.777 | 7.63 | 223.822 | 2084.24 | 26.01 | 41.033 | 6.26 | 1.492 | 5.859 | 8951.75 | 2.707 | 98 | 79.7 | 1355 | 20.52 | 5818.6 | 3520.6 | 3620.1 | 5142.1 | 1188.9 | 0.66849 | 7.352
2024-12-09 | 14:58 | Data | 0 | 29.733 | 26.742 | 239.687 | 7.63 | 223.596 | 2085.14 | 26.02 | 41.033 | 6.26 | 1.498 | 5.838 | 8960.79 | 3.085 | 98 | 79.6 | 1355 | 20.52 | 5824.5 | 3520.9 | 3690.5 | 5189.9 | 1188.9 | 0.66351 | 7.334
2024-12-09 | 14:58 | Data | 0 | 29.996 | 26.735 | 239.868 | 7.63 | 223.731 | 2078.81 | 26 | 40.943 | 6.26 | 1.505 | 5.846 | 8951.75 | 3.106 | 98 | 79.5 | 1351 | 20.47 | 5818.6 | 3511.7 | 3675.2 | 5177.1 | 1188.9 | 0.66275 | 7.349
2024-12-09 | 14:58 | Data | 0 | 29.901 | 27.187 | 239.732 | 7.63 | 223.731 | 2084.24 | 26.02 | 40.943 | 6.26 | 1.515 | 5.857 | 8938.18 | 3.133 | 98 | 79.4 | 1355 | 20.47 | 5809.8 | 3500.6 | 3678.2 | 5167.2 | 1188.9 | 0.66305 | 7.371
2024-12-09 | 14:58 | Data | 0 | 29.854 | 26.958 | 239.868 | 7.63 | 223.686 | 2086.95 | 26.02 | 40.943 | 6.26 | 1.509 | 5.859 | 8951.75 | 2.998 | 98 | 79.5 | 1357 | 20.47 | 5818.6 | 3529 | 3661.7 | 5174.9 | 1188.9 | 0.66707 | 7.371
2024-12-09 | 14:58 | Data | 0 | 30.266 | 26.803 | 239.551 | 7.63 | 223.686 | 2083.33 | 26.03 | 40.943 | 6.26 | 1.507 | 5.854 | 8947.23 | 3.092 | 98 | 79.5 | 1355 | 20.47 | 5815.7 | 3496.2 | 3695.6 | 5177.9 | 1188.9 | 0.66059 | 7.361
2024-12-09 | 14:58 | Data | 0 | 29.969 | 26.938 | 239.732 | 7.63 | 223.641 | 2086.95 | 26.02 | 41.033 | 6.26 | 1.51 | 5.851 | 8933.66 | 3.038 | 98 | 79.5 | 1357 | 20.52 | 5806.9 | 3496.4 | 3668.1 | 5161.6 | 1188.9 | 0.66037 | 7.361
2024-12-09 | 14:58 | Data | 0 | 30.023 | 27.181 | 239.958 | 7.63 | 223.822 | 2086.95 | 26.02 | 41.123 | 6.26 | 1.498 | 5.87 | 8920.09 | 2.849 | 98 | 79.7 | 1357 | 20.52 | 5798.1 | 3511.1 | 3669.4 | 5168.9 | 1188.9 | 0.66424 | 7.368
2024-12-09 | 14:58 | Data | 0 | 29.746 | 26.904 | 239.777 | 7.63 | 223.867 | 2084.24 | 26.01 | 41.033 | 6.27 | 1.496 | 5.848 | 8897.48 | 2.998 | 98 | 79.6 | 1355 | 20.52 | 5783.4 | 3516.8 | 3659 | 5165.8 | 1188.9 | 0.66362 | 7.344
2024-12-09 | 14:58 | Data | 0 | 29.739 | 26.904 | 239.732 | 7.63 | 223.731 | 2082.43 | 26.02 | 40.943 | 6.25 | 1.498 | 5.855 | 8883.91 | 2.998 | 98 | 79.6 | 1353 | 20.52 | 5774.5 | 3521.6 | 3669.4 | 5176.7 | 1188.9 | 0.6654 | 7.352
2024-12-09 | 14:58 | Data | 0 | 30.07 | 26.803 | 239.732 | 7.63 | 223.822 | 2081.53 | 26.02 | 41.033 | 6.27 | 1.512 | 5.842 | 8879.39 | 3.18 | 98 | 79.4 | 1352 | 20.52 | 5771.6 | 3529.2 | 3660.1 | 5174.8 | 1188.9 | 0.66723 | 7.355
2024-12-09 | 14:58 | Data | 0 | 29.733 | 27.012 | 239.687 | 7.63 | 223.686 | 2081.53 | 26.03 | 40.943 | 6.26 | 1.495 | 5.847 | 8888.44 | 2.775 | 98 | 79.6 | 1354 | 20.52 | 5777.5 | 3517.8 | 3662.4 | 5165.7 | 1188.9 | 0.6667 | 7.342
2024-12-09 | 14:59 | Data | 0 | 30.097 | 26.789 | 239.913 | 7.63 | 223.867 | 2078.81 | 26.01 | 41.033 | 6.26 | 1.493 | 5.844 | 8965.31 | 2.829 | 98 | 79.6 | 1352 | 20.52 | 5827.5 | 3511.3 | 3665.8 | 5167.2 | 1188.9 | 0.66522 | 7.338
2024-12-09 | 14:59 | Data | 0 | 29.78 | 26.728 | 239.597 | 7.63 | 223.596 | 2085.14 | 26.01 | 41.033 | 6.26 | 1.502 | 5.842 | 8951.75 | 3.018 | 98 | 79.5 | 1355 | 20.47 | 5818.6 | 3504.9 | 3642.7 | 5147.9 | 1188.9 | 0.66566 | 7.343
2024-12-09 | 14:59 | Data | 0 | 30.171 | 26.87 | 239.777 | 7.63 | 223.822 | 2081.53 | 26.01 | 41.033 | 6.26 | 1.496 | 5.865 | 8947.23 | 3.106 | 98 | 79.7 | 1352 | 20.47 | 5815.7 | 3519.5 | 3652.6 | 5160.9 | 1188.9 | 0.66757 | 7.36
2024-12-09 | 14:59 | Data | 0 | 29.618 | 26.533 | 239.551 | 7.63 | 223.596 | 2085.14 | 26.02 | 41.033 | 6.26 | 1.502 | 5.865 | 8951.75 | 3.139 | 98 | 79.6 | 1355 | 20.47 | 5818.6 | 3484 | 3647.8 | 5135.8 | 1188.9 | 0.66401 | 7.366
2024-12-09 | 14:59 | Data | 0 | 29.8 | 26.85 | 239.597 | 7.63 | 223.686 | 2084.24 | 26.01 | 40.852 | 6.26 | 1.5 | 5.866 | 8834.17 | 3.011 | 98 | 79.6 | 1355 | 20.43 | 5742.2 | 3497.9 | 3650.9 | 5146.3 | 1188.9 | 0.66518 | 7.367
2024-12-09 | 14:59 | Data | 0 | 30.124 | 27.073 | 239.732 | 7.63 | 223.596 | 2084.24 | 26.03 | 41.033 | 6.26 | 1.499 | 5.856 | 8838.69 | 3.106 | 98 | 79.6 | 1355 | 20.52 | 5745.1 | 3496.2 | 3652.4 | 5149.5 | 1188.9 | 0.66397 | 7.355
2024-12-09 | 14:59 | Data | 0 | 30.158 | 26.735 | 239.732 | 7.63 | 223.686 | 2076.1 | 26.02 | 40.943 | 6.26 | 1.497 | 5.838 | 8838.69 | 3.058 | 98 | 79.6 | 1350 | 20.47 | 5745.1 | 3513.3 | 3636.3 | 5144 | 1188.9 | 0.66755 | 7.335
2024-12-09 | 14:59 | Data | 0 | 29.982 | 26.742 | 239.732 | 7.63 | 223.641 | 2085.14 | 26.01 | 40.943 | 6.26 | 1.497 | 5.828 | 8834.17 | 3.018 | 98 | 79.6 | 1355 | 20.52 | 5742.2 | 3487 | 3653.4 | 5142.1 | 1188.9 | 0.66375 | 7.323
2024-12-09 | 14:59 | Data | 0 | 29.733 | 27.181 | 239.958 | 7.63 | 223.731 | 2084.24 | 26.02 | 41.033 | 6.25 | 1.496 | 5.853 | 8856.78 | 3.133 | 98 | 79.6 | 1355 | 20.52 | 5756.9 | 3501.4 | 3636 | 5141.6 | 1188.9 | 0.66558 | 7.35
2024-12-09 | 14:59 | Data | 0 | 30.124 | 26.992 | 239.732 | 7.63 | 223.731 | 2085.14 | 26.02 | 41.033 | 6.26 | 1.501 | 5.841 | 8870.35 | 3.16 | 98 | 79.6 | 1355 | 20.52 | 5765.7 | 3531.1 | 3631.4 | 5157.6 | 1188.9 | 0.6698 | 7.342
2024-12-09 | 14:59 | Data | 0 | 29.51 | 26.904 | 240.004 | 7.63 | 223.686 | 2084.24 | 26 | 41.033 | 6.26 | 1.503 | 5.854 | 9345.18 | 2.883 | 98 | 79.6 | 1355 | 20.52 | 6074.4 | 3512.5 | 3669.2 | 5174.3 | 1188.9 | 0.66611 | 7.357
2024-12-09 | 14:59 | Data | 0 | 29.955 | 26.965 | 239.642 | 7.63 | 223.641 | 2086.95 | 26.02 | 40.943 | 6.26 | 1.506 | 5.825 | 8915.57 | 2.991 | 98 | 79.5 | 1356 | 20.43 | 5795.1 | 3509.2 | 3648.5 | 5156.4 | 1188.9 | 0.66609 | 7.332
2024-12-09 | 14:59 | Data | 0 | 30.543 | 27.154 | 239.777 | 7.63 | 223.822 | 2086.95 | 26.03 | 41.033 | 6.26 | 1.497 | 5.836 | 8924.61 | 3.43 | 98 | 79.6 | 1357 | 20.52 | 5801 | 3466.2 | 3635.7 | 5119.2 | 1189 | 0.66211 | 7.333
2024-12-09 | 14:59 | Data | 0 | 30.097 | 26.965 | 239.687 | 7.63 | 223.641 | 2130.33 | 26.02 | 41.033 | 6.26 | 1.5 | 5.828 | 8911.05 | 3.207 | 98.1 | 79.5 | 1385 | 20.52 | 5792.2 | 3520.2 | 3640.6 | 5151.3 | 1189 | 0.66809 | 7.328
2024-12-09 | 14:59 | Data | 0 | 29.773 | 26.85 | 239.913 | 7.63 | 223.686 | 2131.24 | 26.02 | 40.943 | 6.26 | 1.5 | 5.862 | 8920.09 | 2.883 | 98.1 | 79.6 | 1385 | 20.52 | 5798.1 | 3505.9 | 3669.2 | 5162.9 | 1189 | 0.66423 | 7.362
2024-12-09 | 14:59 | Data | 0 | 30.009 | 26.735 | 239.642 | 7.63 | 223.686 | 2129.43 | 26.02 | 40.943 | 6.26 | 1.498 | 5.87 | 8920.09 | 3.112 | 98.1 | 79.7 | 1385 | 20.52 | 5798.1 | 3488.7 | 3679.9 | 5163.4 | 1189 | 0.66094 | 7.368
2024-12-09 | 14:59 | Data | 0 | 30.117 | 27.187 | 239.687 | 7.63 | 223.686 | 2131.24 | 26.02 | 41.213 | 6.26 | 1.495 | 5.848 | 8956.27 | 2.991 | 98.1 | 79.6 | 1385 | 20.65 | 5821.6 | 3511.5 | 3680.2 | 5177.7 | 1189 | 0.66332 | 7.343
2024-12-09 | 15:00 | Data | 0 | 30.232 | 26.816 | 239.868 | 7.63 | 223.822 | 2087.85 | 26.02 | 41.033 | 6.26 | 1.493 | 5.831 | 8956.27 | 3.173 | 98 | 79.6 | 1357 | 20.52 | 5821.6 | 3501.9 | 3684.7 | 5176.7 | 1189 | 0.66111 | 7.323
2024-12-09 | 15:00 | Data | 0 | 29.901 | 26.742 | 239.687 | 7.63 | 223.641 | 2086.95 | 26.02 | 41.033 | 6.26 | 1.511 | 5.838 | 8969.84 | 2.991 | 98 | 79.4 | 1357 | 20.47 | 5830.4 | 3510.1 | 3682.4 | 5181 | 1189 | 0.66225 | 7.349
2024-12-09 | 15:00 | Data | 0 | 30.057 | 26.985 | 239.687 | 7.63 | 223.641 | 2086.95 | 26.02 | 40.943 | 6.26 | 1.509 | 5.846 | 8965.31 | 3.146 | 98 | 79.5 | 1357 | 20.43 | 5827.5 | 3500 | 3665.5 | 5158 | 1189 | 0.66288 | 7.354
2024-12-09 | 15:00 | Data | 0 | 29.881 | 26.965 | 239.958 | 7.63 | 223.912 | 2087.85 | 26.01 | 41.033 | 6.26 | 1.501 | 5.855 | 8938.18 | 2.782 | 98 | 79.6 | 1358 | 20.52 | 5809.8 | 3525.1 | 3684.5 | 5195 | 1189 | 0.66574 | 7.357
2024-12-09 | 15:00 | Data | 0 | 29.942 | 26.965 | 239.687 | 7.63 | 223.686 | 2084.24 | 26.02 | 40.943 | 6.26 | 1.504 | 5.847 | 8947.23 | 2.984 | 98 | 79.5 | 1355 | 20.47 | 5815.7 | 3499.4 | 3668.1 | 5160.5 | 1189 | 0.66295 | 7.351
2024-12-09 | 15:00 | Data | 0 | 30.192 | 27.14 | 240.049 | 7.63 | 223.867 | 2082.43 | 26.01 | 41.033 | 6.26 | 1.495 | 5.855 | 8938.18 | 3.22 | 98 | 79.7 | 1353 | 20.52 | 5809.8 | 3511.7 | 3677.2 | 5178.2 | 1189 | 0.6629 | 7.351
2024-12-09 | 15:00 | Data | 0 | 30.381 | 27.133 | 239.913 | 7.63 | 223.867 | 2081.53 | 26.02 | 41.033 | 6.26 | 1.498 | 5.837 | 8924.61 | 3.16 | 98 | 79.6 | 1353 | 20.52 | 5801 | 3497.2 | 3685.5 | 5173.8 | 1189 | 0.661 | 7.335
2024-12-09 | 15:00 | Data | 0 | 30.043 | 26.742 | 239.687 | 7.63 | 223.731 | 2081.53 | 26.03 | 40.852 | 6.26 | 1.5 | 5.858 | 8920.09 | 3.106 | 98 | 79.6 | 1354 | 20.47 | 5798.1 | 3509 | 3670.2 | 5171.4 | 1189 | 0.66353 | 7.358
2024-12-09 | 15:00 | Data | 0 | 29.841 | 26.958 | 239.551 | 7.63 | 223.641 | 2081.53 | 26.03 | 41.304 | 6.26 | 1.494 | 5.833 | 8879.39 | 2.842 | 98 | 79.6 | 1352 | 20.65 | 5771.6 | 3525.1 | 3692.2 | 5192.9 | 1189 | 0.66389 | 7.327
2024-12-09 | 15:00 | Data | 0 | 29.982 | 26.857 | 240.004 | 7.63 | 223.731 | 2086.95 | 26.03 | 41.304 | 6.26 | 1.493 | 5.847 | 8892.96 | 3.22 | 98 | 79.7 | 1357 | 20.65 | 5780.4 | 3493.3 | 3679.2 | 5160.1 | 1189 | 0.66242 | 7.34
2024-12-09 | 15:00 | Data | 0 | 30.158 | 27.194 | 239.687 | 7.63 | 223.731 | 2086.95 | 26.02 | 41.213 | 6.26 | 1.498 | 5.841 | 8883.91 | 2.984 | 98 | 79.6 | 1357 | 20.61 | 5774.5 | 3502.3 | 3675.6 | 5167.6 | 1189 | 0.66357 | 7.339
2024-12-09 | 15:00 | Data | 0 | 29.949 | 26.641 | 239.732 | 7.63 | 223.686 | 2086.95 | 26.02 | 41.304 | 6.26 | 1.501 | 5.848 | 8897.48 | 3.214 | 98 | 79.6 | 1357 | 20.7 | 5783.4 | 3498.1 | 3689.7 | 5181.2 | 1189 | 0.66002 | 7.349
2024-12-09 | 15:00 | Data | 0 | 30.097 | 26.965 | 239.777 | 7.63 | 223.731 | 2087.85 | 26.01 | 41.304 | 6.26 | 1.495 | 5.88 | 8911.05 | 2.829 | 98 | 79.7 | 1357 | 20.65 | 5792.2 | 3495.4 | 3665.7 | 5153.4 | 1189 | 0.66396 | 7.374
2024-12-09 | 15:00 | Data | 0 | 30.212 | 26.978 | 239.868 | 7.63 | 223.957 | 2086.95 | 26.02 | 41.304 | 6.26 | 1.485 | 5.87 | 8920.09 | 3.193 | 98 | 79.8 | 1357 | 20.65 | 5798.1 | 3497.4 | 3643.5 | 5139.9 | 1189 | 0.66578 | 7.355
2024-12-09 | 15:00 | Data | 0 | 29.969 | 26.843 | 239.777 | 7.63 | 223.686 | 2086.95 | 26.02 | 41.304 | 6.26 | 1.499 | 5.879 | 8911.05 | 2.89 | 98 | 79.7 | 1357 | 20.61 | 5792.2 | 3521 | 3653.2 | 5164.1 | 1189 | 0.66464 | 7.378
2024-12-09 | 15:00 | Data | 0 | 29.625 | 26.728 | 239.551 | 7.63 | 223.731 | 2087.85 | 26.02 | 41.304 | 6.26 | 1.493 | 5.838 | 8897.48 | 2.971 | 98 | 79.6 | 1357 | 20.61 | 5783.4 | 3508.8 | 3635.6 | 5141 | 1189 | 0.66804 | 7.332
2024-12-09 | 15:00 | Data | 0 | 29.942 | 26.776 | 239.642 | 7.63 | 223.641 | 2089.66 | 26.02 | 41.213 | 6.26 | 1.499 | 5.848 | 8965.31 | 3.065 | 98 | 79.6 | 1358 | 20.61 | 5827.5 | 3521.7 | 3656.4 | 5164 | 1189 | 0.6673 | 7.347
2024-12-09 | 15:00 | Data | 0 | 30.178 | 26.992 | 240.049 | 7.63 | 223.867 | 2092.37 | 26.02 | 41.394 | 6.26 | 1.493 | 5.853 | 8933.66 | 2.91 | 98 | 79.7 | 1361 | 20.65 | 5806.9 | 3520.7 | 3639.4 | 5150.1 | 1189 | 0.66826 | 7.346
2024-12-09 | 15:01 | Data | 0 | 29.787 | 26.965 | 239.913 | 7.63 | 223.731 | 2089.66 | 26.02 | 41.304 | 6.26 | 1.498 | 5.851 | 8938.18 | 2.883 | 98 | 79.6 | 1358 | 20.61 | 5809.8 | 3487.1 | 3618.4 | 5115.8 | 1189 | 0.66617 | 7.348
2024-12-09 | 15:01 | Data | 0 | 29.685 | 26.728 | 239.777 | 7.63 | 223.686 | 2089.66 | 26.01 | 41.213 | 6.26 | 1.511 | 5.857 | 8956.27 | 3.099 | 98 | 79.5 | 1358 | 20.65 | 5821.6 | 3504.8 | 3641.3 | 5147.1 | 1189 | 0.66375 | 7.368
2024-12-09 | 15:01 | Data | 0 | 29.807 | 26.958 | 239.642 | 7.63 | 223.641 | 2087.85 | 26.02 | 41.033 | 6.26 | 1.502 | 5.846 | 8920.09 | 2.633 | 98 | 79.6 | 1357 | 20.52 | 5798.1 | 3487.5 | 3659.9 | 5147.9 | 1189 | 0.66255 | 7.348
2024-12-09 | 15:01 | Data | 0 | 29.733 | 26.938 | 239.597 | 7.63 | 223.822 | 2085.14 | 26.03 | 41.033 | 6.25 | 1.488 | 5.865 | 8938.18 | 2.903 | 98 | 79.8 | 1355 | 20.47 | 5809.8 | 3494.6 | 3638 | 5132.2 | 1189 | 0.66633 | 7.351
2024-12-09 | 15:01 | Data | 0 | 30.131 | 27.046 | 239.958 | 7.63 | 223.957 | 2085.14 | 26.01 | 41.033 | 6.26 | 1.489 | 5.847 | 8915.57 | 3.18 | 98 | 79.7 | 1355 | 20.52 | 5795.1 | 3491.3 | 3621.5 | 5120.2 | 1189 | 0.66554 | 7.335
2024-12-09 | 15:01 | Data | 0 | 30.374 | 27.032 | 239.868 | 7.63 | 223.822 | 2086.04 | 26.02 | 40.943 | 6.27 | 1.504 | 5.871 | 8924.61 | 3.052 | 98 | 79.6 | 1356 | 20.52 | 5801 | 3495.3 | 3628.7 | 5127.6 | 1189 | 0.66777 | 7.374
2024-12-09 | 15:01 | Data | 0 | 29.793 | 26.728 | 239.732 | 7.63 | 223.731 | 2086.95 | 26.01 | 40.852 | 6.26 | 1.497 | 5.847 | 8947.23 | 3.025 | 98 | 79.6 | 1357 | 20.52 | 5815.7 | 3505.3 | 3613.1 | 5123.2 | 1189 | 0.66937 | 7.344
2024-12-09 | 15:01 | Data | 0 | 30.158 | 27.133 | 240.004 | 7.63 | 223.731 | 2087.85 | 26.02 | 40.943 | 6.26 | 1.494 | 5.829 | 8951.75 | 2.971 | 98 | 79.6 | 1357 | 20.52 | 5818.6 | 3504.6 | 3604.1 | 5116 | 1189.1 | 0.6686 | 7.323
2024-12-09 | 15:01 | Data | 0 | 30.185 | 26.803 | 239.732 | 7.63 | 223.731 | 2089.66 | 26.02 | 40.943 | 6.26 | 1.491 | 5.866 | 8951.75 | 3.038 | 98 | 79.8 | 1358 | 20.47 | 5818.6 | 3485.9 | 3610.2 | 5110.3 | 1189.1 | 0.66744 | 7.353
2024-12-09 | 15:01 | Data | 0 | 29.942 | 26.971 | 239.958 | 7.63 | 223.912 | 2089.66 | 26.02 | 41.033 | 6.26 | 1.5 | 5.857 | 8933.66 | 3.153 | 98 | 79.6 | 1358 | 20.52 | 5806.9 | 3492.2 | 3593.1 | 5103.8 | 1189.1 | 0.66925 | 7.358
2024-12-09 | 15:01 | Data | 0 | 29.753 | 26.83 | 239.687 | 7.63 | 223.596 | 2089.66 | 26.02 | 40.943 | 6.26 | 1.507 | 5.843 | 8965.31 | 2.998 | 98 | 79.5 | 1358 | 20.52 | 5827.5 | 3505.4 | 3607.2 | 5122.6 | 1189.1 | 0.66939 | 7.351
2024-12-09 | 15:01 | Data | 0 | 29.733 | 26.728 | 239.732 | 7.63 | 223.731 | 2089.66 | 26.03 | 40.943 | 6.26 | 1.503 | 5.863 | 8956.27 | 2.998 | 98 | 79.6 | 1358 | 20.47 | 5821.6 | 3506.5 | 3631.1 | 5138.8 | 1189.1 | 0.66766 | 7.368
2024-12-09 | 15:01 | Data | 0 | 29.753 | 26.958 | 239.732 | 7.63 | 223.641 | 2083.33 | 26.02 | 41.033 | 6.26 | 1.499 | 5.866 | 8951.75 | 2.91 | 98 | 79.7 | 1355 | 20.56 | 5818.6 | 3522.3 | 3625 | 5148.1 | 1189.1 | 0.66945 | 7.365
2024-12-09 | 15:01 | Data | 0 | 30.232 | 27.201 | 239.958 | 7.63 | 223.822 | 2081.53 | 26.01 | 41.033 | 6.25 | 1.49 | 5.866 | 8951.75 | 3.004 | 98 | 79.8 | 1354 | 20.52 | 5818.6 | 3526.8 | 3614 | 5138.3 | 1189.1 | 0.67303 | 7.356
2024-12-09 | 15:01 | Data | 0 | 30.063 | 26.884 | 239.777 | 7.63 | 223.912 | 2079.72 | 26.01 | 41.033 | 6.26 | 1.498 | 5.844 | 8915.57 | 3.085 | 98 | 79.6 | 1353 | 20.47 | 5795.1 | 3501.1 | 3588.5 | 5103.3 | 1189.1 | 0.67159 | 7.342
2024-12-09 | 15:01 | Data | 0 | 30.171 | 27.079 | 239.732 | 7.63 | 223.822 | 2085.14 | 26.03 | 41.033 | 6.26 | 1.5 | 5.844 | 8933.66 | 3.133 | 98 | 79.6 | 1355 | 20.47 | 5806.9 | 3494.2 | 3601.8 | 5110.7 | 1189.1 | 0.66871 | 7.343
2024-12-09 | 15:01 | Data | 0 | 29.841 | 26.85 | 239.777 | 7.63 | 223.731 | 2084.24 | 26.02 | 41.033 | 6.26 | 1.49 | 5.857 | 8920.09 | 3.173 | 98 | 79.7 | 1355 | 20.52 | 5798.1 | 3507.6 | 3629.9 | 5134.9 | 1189.1 | 0.66693 | 7.346
2024-12-09 | 15:01 | Data | 0 | 29.726 | 26.931 | 239.642 | 7.63 | 223.641 | 2083.33 | 26.02 | 40.943 | 6.26 | 1.485 | 5.853 | 8924.61 | 2.883 | 98 | 79.8 | 1355 | 20.52 | 5801 | 3509.5 | 3604.8 | 5120.6 | 1189.1 | 0.67026 | 7.336
2024-12-09 | 15:02 | Data | 0 | 30.185 | 27.309 | 240.185 | 7.63 | 224.002 | 1987.53 | 26.02 | 40.943 | 6.26 | 1.503 | 5.838 | 8956.27 | 2.991 | 97.9 | 79.5 | 1292 | 20.52 | 5821.6 | 3503.3 | 3586.1 | 5103.4 | 1189.1 | 0.67084 | 7.341
2024-12-09 | 15:02 | Data | 0 | 30.124 | 27.019 | 239.642 | 7.63 | 223.731 | 2143.89 | 26.02 | 41.033 | 6.27 | 1.496 | 5.857 | 8965.31 | 3.099 | 98.1 | 79.7 | 1394 | 20.52 | 5827.5 | 3495.1 | 3591.6 | 5104.3 | 1189.1 | 0.66947 | 7.353
2024-12-09 | 15:02 | Data | 0 | 29.955 | 26.958 | 239.642 | 7.63 | 223.731 | 2142.08 | 26.02 | 40.852 | 6.26 | 1.486 | 5.868 | 8974.36 | 2.998 | 98.1 | 79.8 | 1392 | 20.47 | 5833.3 | 3506.1 | 3588 | 5108.5 | 1189.1 | 0.67134 | 7.354
2024-12-09 | 15:02 | Data | 0 | 29.746 | 26.951 | 239.642 | 7.63 | 223.641 | 2139.37 | 26.01 | 41.033 | 6.26 | 1.492 | 5.858 | 8978.88 | 2.937 | 98.1 | 79.7 | 1391 | 20.52 | 5836.3 | 3501.1 | 3616.7 | 5126.5 | 1189.1 | 0.66831 | 7.351
2024-12-09 | 15:02 | Data | 0 | 29.955 | 26.728 | 239.687 | 7.63 | 223.686 | 2136.66 | 26.02 | 41.033 | 6.27 | 1.492 | 5.819 | 8960.79 | 3.112 | 98.1 | 79.6 | 1390 | 20.61 | 5824.5 | 3517.7 | 3605.9 | 5130.3 | 1189.1 | 0.67405 | 7.31
2024-12-09 | 15:02 | Data | 0 | 30.124 | 27.181 | 239.958 | 7.63 | 223.731 | 2134.85 | 26.01 | 41.033 | 6.26 | 1.5 | 5.822 | 8951.75 | 3.011 | 98.1 | 79.5 | 1388 | 20.52 | 5818.6 | 3483.3 | 3586.7 | 5092 | 1189.1 | 0.66924 | 7.322
2024-12-09 | 15:02 | Data | 0 | 30.117 | 27.167 | 239.777 | 7.63 | 223.686 | 2129.43 | 26.03 | 40.943 | 6.26 | 1.506 | 5.823 | 8947.23 | 3.187 | 98.1 | 79.5 | 1385 | 20.47 | 5815.7 | 3511.8 | 3586.1 | 5108.5 | 1189.1 | 0.67392 | 7.33
2024-12-09 | 15:02 | Data | 0 | 29.517 | 26.836 | 239.642 | 7.63 | 223.731 | 2128.52 | 26.02 | 41.033 | 6.26 | 1.514 | 5.823 | 8956.27 | 3.106 | 98.1 | 79.4 | 1384 | 20.52 | 5821.6 | 3528 | 3566.8 | 5103.7 | 1189.1 | 0.6769 | 7.337
2024-12-09 | 15:02 | Data | 0 | 30.34 | 27.093 | 239.958 | 7.63 | 223.867 | 2128.52 | 26.01 | 41.033 | 6.26 | 1.508 | 5.814 | 8969.84 | 3.146 | 98.1 | 79.4 | 1383 | 20.52 | 5830.4 | 3485.8 | 3566.8 | 5085.6 | 1189.1 | 0.67182 | 7.321
2024-12-09 | 15:02 | Data | 0 | 30.07 | 27.019 | 239.732 | 7.63 | 223.912 | 2125.81 | 26.02 | 40.943 | 6.27 | 1.501 | 5.837 | 8965.31 | 2.964 | 98.1 | 79.5 | 1381 | 20.52 | 5827.5 | 3489.9 | 3573.5 | 5087.4 | 1189.1 | 0.67112 | 7.338
2024-12-09 | 15:02 | Data | 0 | 29.881 | 26.965 | 239.868 | 7.63 | 223.731 | 2044.47 | 26.01 | 40.943 | 6.27 | 1.497 | 5.84 | 8956.27 | 2.842 | 98 | 79.6 | 1330 | 20.52 | 5821.6 | 3491.7 | 3589.8 | 5097.3 | 1189.1 | 0.67041 | 7.336
2024-12-09 | 15:02 | Data | 0 | 30.043 | 27.127 | 239.777 | 7.63 | 223.867 | 2041.76 | 26.02 | 41.033 | 6.26 | 1.507 | 5.865 | 8965.31 | 3.2 | 98 | 79.6 | 1328 | 20.52 | 5827.5 | 3492.1 | 3586.8 | 5096 | 1189.1 | 0.67042 | 7.371
2024-12-09 | 15:02 | Data | 0 | 29.962 | 26.789 | 239.913 | 7.63 | 223.822 | 2044.47 | 26.02 | 40.943 | 6.25 | 1.509 | 5.836 | 8978.88 | 2.991 | 98 | 79.4 | 1329 | 20.47 | 5836.3 | 3503.9 | 3552.8 | 5081.7 | 1189.1 | 0.67518 | 7.345
2024-12-09 | 15:02 | Data | 0 | 29.841 | 26.749 | 239.687 | 7.63 | 223.686 | 2048.08 | 26.03 | 41.033 | 6.26 | 1.507 | 5.855 | 8996.97 | 2.971 | 98 | 79.5 | 1331 | 20.52 | 5848 | 3489 | 3538.6 | 5060.8 | 1189.1 | 0.67442 | 7.362
2024-12-09 | 15:02 | Data | 0 | 29.982 | 27.322 | 239.958 | 7.63 | 223.822 | 2129.43 | 26.03 | 40.943 | 6.26 | 1.504 | 5.85 | 9033.15 | 2.849 | 98.1 | 79.6 | 1385 | 20.43 | 5871.5 | 3512 | 3574.2 | 5107.4 | 1189.1 | 0.67445 | 7.354
2024-12-09 | 15:02 | Data | 0 | 29.928 | 27.16 | 239.868 | 7.63 | 223.686 | 2136.66 | 26.02 | 41.033 | 6.26 | 1.499 | 5.842 | 9019.58 | 3.166 | 98.1 | 79.6 | 1389 | 20.52 | 5862.7 | 3502.8 | 3568.1 | 5089.5 | 1189.1 | 0.67205 | 7.342
2024-12-09 | 15:02 | Data | 0 | 30.3 | 26.803 | 239.687 | 7.63 | 223.686 | 2134.85 | 26.02 | 41.033 | 6.26 | 1.503 | 5.831 | 9019.58 | 3.065 | 98.1 | 79.5 | 1387 | 20.52 | 5862.7 | 3487 | 3570.1 | 5082.1 | 1189.1 | 0.67243 | 7.333
2024-12-09 | 15:03 | Data | 0 | 29.746 | 27.066 | 240.185 | 7.63 | 223.822 | 2123.1 | 26.03 | 40.943 | 6.27 | 1.503 | 5.843 | 9037.67 | 2.977 | 98.1 | 79.5 | 1379 | 20.47 | 5874.5 | 3503.3 | 3578.2 | 5098.1 | 1189.1 | 0.67239 | 7.346
2024-12-09 | 15:03 | Data | 0 | 30.178 | 26.965 | 239.732 | 7.63 | 223.731 | 2059.83 | 26.02 | 40.943 | 6.26 | 1.501 | 5.856 | 9019.58 | 3.214 | 98 | 79.6 | 1337 | 20.52 | 5862.7 | 3494 | 3575.4 | 5090.6 | 1189.1 | 0.67165 | 7.357
2024-12-09 | 15:03 | Data | 0 | 29.847 | 26.985 | 239.732 | 7.63 | 223.822 | 2041.76 | 26.02 | 40.943 | 6.26 | 1.485 | 5.838 | 9015.06 | 3.072 | 98 | 79.7 | 1328 | 20.43 | 5859.8 | 3501.3 | 3573.6 | 5093.4 | 1189.1 | 0.67273 | 7.323
2024-12-09 | 15:03 | Data | 0 | 29.915 | 26.87 | 239.777 | 7.63 | 223.731 | 2043.56 | 26.01 | 41.033 | 6.26 | 1.478 | 5.857 | 9024.1 | 3.112 | 98 | 79.8 | 1328 | 20.52 | 5865.7 | 3517.1 | 3586.6 | 5111.1 | 1189.2 | 0.67251 | 7.334
2024-12-09 | 15:03 | Data | 0 | 29.942 | 26.843 | 239.777 | 7.63 | 223.686 | 2072.49 | 26.01 | 41.123 | 6.26 | 1.489 | 5.846 | 9444.67 | 3.112 | 98 | 79.7 | 1356 | 20.52 | 6139 | 3480.5 | 3555.2 | 5065.3 | 1189.2 | 0.6723 | 7.334
2024-12-09 | 15:03 | Data | 0 | 29.955 | 26.992 | 239.732 | 7.63 | 223.731 | 2143.89 | 26.01 | 41.033 | 6.26 | 1.49 | 5.822 | 8983.4 | 2.883 | 98.1 | 79.6 | 1394 | 20.52 | 5839.2 | 3506.4 | 3561.4 | 5089.6 | 1189.2 | 0.67417 | 7.311
2024-12-09 | 15:03 | Data | 0 | 30.286 | 27.241 | 239.868 | 7.63 | 223.912 | 2142.08 | 26.01 | 41.033 | 6.26 | 1.496 | 5.831 | 8978.88 | 3.018 | 98.1 | 79.6 | 1392 | 20.47 | 5836.3 | 3514.2 | 3536 | 5077.8 | 1189.2 | 0.6776 | 7.326
2024-12-09 | 15:03 | Data | 0 | 29.746 | 26.742 | 239.687 | 7.63 | 223.731 | 2139.37 | 26.03 | 40.943 | 6.27 | 1.486 | 5.832 | 8992.45 | 2.977 | 98.1 | 79.7 | 1391 | 20.43 | 5845.1 | 3508 | 3543.2 | 5067.7 | 1189.2 | 0.67561 | 7.318
2024-12-09 | 15:03 | Data | 0 | 29.949 | 26.728 | 239.913 | 7.63 | 223.867 | 2137.56 | 26.02 | 41.033 | 6.26 | 1.497 | 5.839 | 8938.18 | 3.22 | 98.1 | 79.6 | 1389 | 20.47 | 5809.8 | 3511.4 | 3541.9 | 5084.3 | 1189.2 | 0.67743 | 7.337
2024-12-09 | 15:03 | Data | 0 | 29.787 | 26.755 | 239.687 | 7.63 | 223.912 | 2128.52 | 26.02 | 40.943 | 6.26 | 1.5 | 5.824 | 8513.09 | 3.018 | 98.1 | 79.5 | 1383 | 20.52 | 5533.5 | 3505.4 | 3531.8 | 5066.1 | 1189.2 | 0.67694 | 7.325
2024-12-09 | 15:03 | Data | 0 | 29.739 | 26.728 | 239.687 | 7.63 | 223.641 | 2040.85 | 26.01 | 40.943 | 6.27 | 1.492 | 5.833 | 8911.05 | 2.998 | 98 | 79.6 | 1327 | 20.52 | 5792.2 | 3496.4 | 3536.6 | 5066.8 | 1189.2 | 0.67504 | 7.325
2024-12-09 | 15:03 | Data | 0 | 30.05 | 26.857 | 239.732 | 7.63 | 223.686 | 2042.66 | 26.02 | 41.033 | 6.26 | 1.491 | 5.881 | 8906.53 | 3.119 | 98 | 79.8 | 1328 | 20.52 | 5789.2 | 3518.2 | 3540.9 | 5079.9 | 1189.2 | 0.67814 | 7.372
2024-12-09 | 15:03 | Data | 0 | 30.016 | 27.383 | 239.958 | 7.63 | 223.867 | 2047.18 | 26.02 | 40.943 | 6.26 | 1.504 | 5.861 | 8883.91 | 2.917 | 98 | 79.6 | 1331 | 20.47 | 5774.5 | 3498.6 | 3545.9 | 5053.1 | 1189.2 | 0.67532 | 7.366
2024-12-09 | 15:03 | Data | 0 | 29.82 | 27.181 | 239.777 | 7.63 | 223.731 | 2038.14 | 26.02 | 41.033 | 6.26 | 1.506 | 5.844 | 8879.39 | 2.849 | 98 | 79.5 | 1324 | 20.52 | 5771.6 | 3521 | 3553.9 | 5085.6 | 1189.2 | 0.67752 | 7.35
2024-12-09 | 15:03 | Data | 0 | 29.901 | 27.012 | 239.732 | 7.63 | 223.731 | 2039.95 | 26.02 | 40.943 | 6.26 | 1.504 | 5.853 | 8888.44 | 3.106 | 98 | 79.6 | 1326 | 20.47 | 5777.5 | 3501.9 | 3548.7 | 5075.6 | 1189.2 | 0.67536 | 7.357
2024-12-09 | 15:03 | Data | 0 | 30.32 | 26.998 | 239.913 | 7.63 | 223.912 | 2043.56 | 26.01 | 41.033 | 6.26 | 1.504 | 5.841 | 8481.44 | 2.917 | 98 | 79.5 | 1328 | 20.52 | 5512.9 | 3494.3 | 3577.5 | 5090.3 | 1189.2 | 0.67404 | 7.344
2024-12-09 | 15:03 | Data | 0 | 29.814 | 26.742 | 239.777 | 7.63 | 223.822 | 2042.66 | 26.02 | 40.943 | 6.26 | 1.501 | 5.813 | 9082.89 | 2.984 | 98 | 79.5 | 1328 | 20.56 | 5903.9 | 3481.5 | 3558.5 | 5073.2 | 1189.2 | 0.67456 | 7.313
2024-12-09 | 15:03 | Data | 0 | 29.854 | 26.647 | 239.642 | 7.63 | 223.731 | 2046.28 | 26.01 | 40.943 | 6.26 | 1.5 | 5.855 | 9100.98 | 3.092 | 98 | 79.6 | 1330 | 20.56 | 5915.6 | 3507.2 | 3559.6 | 5087.2 | 1189.2 | 0.67481 | 7.354
2024-12-09 | 15:04 | Data | 0 | 30.158 | 26.762 | 239.732 | 7.63 | 223.641 | 2048.08 | 26.01 | 41.033 | 6.26 | 1.502 | 5.854 | 9132.64 | 3.133 | 98 | 79.6 | 1332 | 20.47 | 5936.2 | 3480.6 | 3557.4 | 5068 | 1189.2 | 0.67209 | 7.356
2024-12-09 | 15:04 | Data | 0 | 30.171 | 27.1 | 239.958 | 7.63 | 223.867 | 2048.99 | 26.02 | 40.762 | 6.26 | 1.506 | 5.827 | 9137.16 | 3.085 | 98 | 79.5 | 1332 | 20.43 | 5939.2 | 3511.5 | 3568.6 | 5096.6 | 1189.2 | 0.67514 | 7.332
2024-12-09 | 15:04 | Data | 0 | 30.394 | 26.769 | 239.777 | 7.63 | 223.686 | 2050.8 | 26.02 | 41.033 | 6.26 | 1.497 | 5.829 | 9006.01 | 3.227 | 98 | 79.6 | 1333 | 20.52 | 5853.9 | 3508.4 | 3547.8 | 5076.2 | 1189.2 | 0.67666 | 7.325
2024-12-09 | 15:04 | Data | 0 | 30.401 | 26.769 | 239.958 | 7.63 | 223.912 | 2053.51 | 26.02 | 41.213 | 6.26 | 1.504 | 5.808 | 8960.79 | 3.146 | 98 | 79.4 | 1335 | 20.52 | 5824.5 | 3492.3 | 3524.9 | 5051 | 1189.2 | 0.67612 | 7.312
2024-12-09 | 15:04 | Data | 0 | 30.381 | 27.032 | 239.868 | 7.63 | 223.867 | 2055.31 | 26.01 | 41.123 | 6.26 | 1.502 | 5.824 | 8951.75 | 3.065 | 98 | 79.5 | 1337 | 20.56 | 5818.6 | 3516.4 | 3525.5 | 5093.9 | 1189.2 | 0.67781 | 7.326
2024-12-09 | 15:04 | Data | 0 | 30.097 | 26.971 | 239.958 | 7.63 | 223.867 | 2059.83 | 26.02 | 41.033 | 6.26 | 1.498 | 5.841 | 8951.75 | 3.004 | 98 | 79.6 | 1339 | 20.52 | 5818.6 | 3496.6 | 3547.5 | 5074.7 | 1189.2 | 0.67358 | 7.338
2024-12-09 | 15:04 | Data | 0 | 29.847 | 27.174 | 239.732 | 7.63 | 223.867 | 2062.55 | 26.02 | 40.943 | 6.26 | 1.495 | 5.853 | 8879.39 | 2.89 | 98 | 79.7 | 1341 | 20.47 | 5771.6 | 3500.7 | 3531.4 | 5064.6 | 1189.2 | 0.67602 | 7.348
2024-12-09 | 15:04 | Data | 0 | 30.171 | 27.019 | 239.687 | 7.63 | 223.822 | 2065.26 | 26.02 | 40.943 | 6.27 | 1.493 | 5.839 | 8576.4 | 2.991 | 98 | 79.6 | 1342 | 20.52 | 5574.7 | 3503 | 3545.5 | 5076.4 | 1189.2 | 0.67534 | 7.333
2024-12-09 | 15:04 | Data | 0 | 29.962 | 27.349 | 239.913 | 7.63 | 223.912 | 2069.78 | 26.01 | 41.033 | 6.26 | 1.502 | 5.841 | 8965.31 | 2.923 | 98 | 79.5 | 1346 | 20.47 | 5827.5 | 3521.4 | 3551.8 | 5093.5 | 1189.2 | 0.67613 | 7.344
2024-12-09 | 15:04 | Data | 0 | 29.733 | 26.843 | 239.687 | 7.63 | 223.686 | 2073.39 | 26.01 | 41.033 | 6.26 | 1.496 | 5.843 | 8956.27 | 2.775 | 98 | 79.6 | 1348 | 20.52 | 5821.6 | 3519.9 | 3548 | 5087.5 | 1189.2 | 0.67615 | 7.339
2024-12-09 | 15:04 | Data | 0 | 29.962 | 27.14 | 239.642 | 7.63 | 223.686 | 2076.1 | 26.01 | 41.033 | 6.26 | 1.494 | 5.838 | 8969.84 | 2.991 | 98 | 79.6 | 1349 | 20.47 | 5830.4 | 3494.1 | 3545.1 | 5068.8 | 1189.2 | 0.67452 | 7.333
2024-12-09 | 15:04 | Data | 0 | 29.685 | 26.85 | 239.732 | 7.63 | 223.822 | 2075.2 | 26.01 | 40.943 | 6.26 | 1.491 | 5.854 | 8924.61 | 3.099 | 98 | 79.7 | 1349 | 20.52 | 5801 | 3497.2 | 3537.2 | 5062.4 | 1189.2 | 0.67704 | 7.347
2024-12-09 | 15:04 | Data | 0 | 30.246 | 27.046 | 239.868 | 7.63 | 223.867 | 2075.2 | 26.02 | 41.123 | 6.26 | 1.49 | 5.85 | 8924.61 | 2.977 | 98 | 79.7 | 1349 | 20.52 | 5801 | 3495.3 | 3539.8 | 5068.2 | 1189.2 | 0.67495 | 7.339
2024-12-09 | 15:04 | Data | 0 | 29.942 | 26.836 | 239.687 | 7.63 | 223.641 | 2082.43 | 26.02 | 40.943 | 6.26 | 1.504 | 5.844 | 8920.09 | 3.038 | 98 | 79.5 | 1353 | 20.52 | 5798.1 | 3491.9 | 3558.3 | 5079.1 | 1189.2 | 0.67195 | 7.349
2024-12-09 | 15:04 | Data | 0 | 30.192 | 26.762 | 239.597 | 7.63 | 223.731 | 2084.24 | 26.02 | 41.033 | 6.26 | 1.507 | 5.839 | 8924.61 | 3.106 | 98 | 79.5 | 1355 | 20.52 | 5801 | 3509.5 | 3521 | 5061.6 | 1189.2 | 0.67816 | 7.345
2024-12-09 | 15:04 | Data | 0 | 30.016 | 26.762 | 239.868 | 7.63 | 223.912 | 2081.53 | 26.03 | 41.033 | 6.27 | 1.49 | 5.832 | 8983.4 | 3.106 | 98 | 79.6 | 1353 | 20.52 | 5839.2 | 3518.2 | 3532.9 | 5076.4 | 1189.3 | 0.67807 | 7.323
2024-12-09 | 15:04 | Data | 0 | 29.982 | 27.16 | 239.913 | 7.63 | 223.867 | 2089.66 | 26.02 | 41.033 | 6.26 | 1.498 | 5.843 | 8965.31 | 2.95 | 98 | 79.6 | 1358 | 20.47 | 5827.5 | 3501.2 | 3548.9 | 5079.6 | 1189.3 | 0.67474 | 7.341
2024-12-09 | 15:04 | Data | 0 | 29.949 | 26.965 | 239.642 | 7.63 | 223.731 | 2089.66 | 26.02 | 41.033 | 6.26 | 1.499 | 5.843 | 8965.31 | 3.106 | 98 | 79.6 | 1358 | 20.52 | 5827.5 | 3502.8 | 3535 | 5067.4 | 1189.3 | 0.67617 | 7.342
2024-12-09 | 15:05 | Data | 0 | 29.955 | 26.917 | 239.777 | 7.63 | 223.867 | 2091.47 | 26.03 | 40.852 | 6.26 | 1.508 | 5.846 | 8987.93 | 2.964 | 98 | 79.5 | 1359 | 20.43 | 5842.2 | 3506.8 | 3535.7 | 5072.3 | 1189.3 | 0.67649 | 7.352
2024-12-09 | 15:05 | Data | 0 | 30.185 | 26.863 | 239.913 | 7.63 | 223.822 | 2091.47 | 26.01 | 41.033 | 6.26 | 1.509 | 5.827 | 8938.18 | 3.079 | 98 | 79.4 | 1359 | 20.52 | 5809.8 | 3517.2 | 3537.6 | 5068.4 | 1189.3 | 0.67528 | 7.336
2024-12-09 | 15:05 | Data | 0 | 30.151 | 27.295 | 239.913 | 7.63 | 223.822 | 2096.89 | 26.02 | 41.033 | 6.26 | 1.503 | 5.828 | 8938.18 | 2.883 | 98 | 79.5 | 1363 | 20.47 | 5809.8 | 3501.9 | 3562.8 | 5085.2 | 1189.3 | 0.67451 | 7.332
2024-12-09 | 15:05 | Data | 0 | 29.969 | 27.248 | 239.687 | 7.63 | 223.822 | 2099.6 | 26.02 | 40.943 | 6.26 | 1.505 | 5.837 | 8938.18 | 2.998 | 98 | 79.5 | 1365 | 20.52 | 5809.8 | 3512.2 | 3529.9 | 5069.1 | 1189.3 | 0.67824 | 7.341
2024-12-09 | 15:05 | Data | 0 | 30.171 | 27.187 | 239.732 | 7.63 | 223.912 | 2100.51 | 26.02 | 40.943 | 6.26 | 1.5 | 5.855 | 8947.23 | 2.883 | 98 | 79.6 | 1365 | 20.52 | 5815.7 | 3505.4 | 3555.8 | 5087.7 | 1189.3 | 0.67376 | 7.357
2024-12-09 | 15:05 | Data | 0 | 29.739 | 27.073 | 239.777 | 7.63 | 223.686 | 2101.41 | 26.02 | 41.033 | 6.26 | 1.498 | 5.86 | 8911.05 | 2.896 | 98.1 | 79.6 | 1367 | 20.47 | 5792.2 | 3489.6 | 3544.6 | 5086.9 | 1189.3 | 0.67571 | 7.357
2024-12-09 | 15:05 | Data | 0 | 29.949 | 26.728 | 239.597 | 7.63 | 223.686 | 2101.41 | 26.01 | 41.033 | 6.26 | 1.5 | 5.858 | 8911.05 | 3.052 | 98 | 79.6 | 1367 | 20.52 | 5792.2 | 3490.6 | 3542.9 | 5066.9 | 1189.3 | 0.67436 | 7.36
2024-12-09 | 15:05 | Data | 0 | 29.928 | 26.755 | 239.597 | 7.63 | 223.686 | 2101.41 | 26.02 | 40.943 | 6.26 | 1.493 | 5.837 | 8902 | 3.173 | 98 | 79.6 | 1366 | 20.52 | 5786.3 | 3508.3 | 3521 | 5072.3 | 1189.3 | 0.67742 | 7.33
2024-12-09 | 15:05 | Data | 0 | 29.82 | 26.735 | 239.777 | 7.63 | 223.686 | 2100.51 | 26.01 | 41.033 | 6.26 | 1.493 | 5.86 | 8906.53 | 2.883 | 98.1 | 79.7 | 1365 | 20.52 | 5789.2 | 3516.4 | 3500.3 | 5053.1 | 1189.3 | 0.68083 | 7.352
2024-12-09 | 15:05 | Data | 0 | 29.739 | 26.728 | 239.732 | 7.63 | 223.686 | 2101.41 | 26.02 | 41.033 | 6.26 | 1.5 | 5.863 | 8920.09 | 2.998 | 98.1 | 79.6 | 1366 | 20.52 | 5798.1 | 3510.6 | 3492.7 | 5043 | 1189.3 | 0.68205 | 7.362
2024-12-09 | 15:05 | Data | 0 | 29.827 | 27.106 | 239.687 | 7.63 | 223.822 | 2100.51 | 26.05 | 40.943 | 6.26 | 1.494 | 5.848 | 8911.05 | 3.038 | 98.1 | 79.7 | 1365 | 20.43 | 5792.2 | 3507.9 | 3492.5 | 5038.9 | 1189.3 | 0.68127 | 7.341
2024-12-09 | 15:05 | Data | 0 | 30.158 | 27.073 | 239.913 | 7.63 | 223.867 | 2101.41 | 26.02 | 41.033 | 6.27 | 1.503 | 5.857 | 8924.61 | 3.106 | 98 | 79.6 | 1365 | 20.52 | 5801 | 3499.2 | 3501.3 | 5041.5 | 1189.3 | 0.67953 | 7.359
2024-12-09 | 15:05 | Data | 0 | 30.07 | 27.181 | 239.958 | 7.63 | 223.912 | 2100.51 | 26.02 | 40.943 | 6.27 | 1.498 | 5.834 | 8933.66 | 2.991 | 98 | 79.6 | 1365 | 20.47 | 5806.9 | 3510.6 | 3502.1 | 5049.1 | 1189.3 | 0.68026 | 7.332
2024-12-09 | 15:05 | Data | 0 | 29.928 | 26.742 | 239.687 | 7.63 | 223.686 | 2101.41 | 26.01 | 40.943 | 6.26 | 1.5 | 5.824 | 8938.18 | 3.079 | 98 | 79.5 | 1367 | 20.52 | 5809.8 | 3512.5 | 3538.5 | 5075.1 | 1189.3 | 0.67772 | 7.326
2024-12-09 | 15:05 | Data | 0 | 30.009 | 26.857 | 239.732 | 7.63 | 223.822 | 2096.89 | 26 | 41.033 | 6.26 | 1.499 | 5.848 | 8960.79 | 3.241 | 98 | 79.6 | 1362 | 20.47 | 5824.5 | 3495.9 | 3512.5 | 5045.6 | 1189.3 | 0.67831 | 7.346
2024-12-09 | 15:05 | Data | 0 | 30.185 | 26.742 | 239.913 | 7.63 | 223.957 | 2096.89 | 26.02 | 41.033 | 6.26 | 1.49 | 5.853 | 8965.31 | 3.187 | 98 | 79.7 | 1364 | 20.52 | 5827.5 | 3506.8 | 3495.8 | 5042.1 | 1189.3 | 0.68017 | 7.342
2024-12-09 | 15:06 | Data | 0 | 29.726 | 26.735 | 239.642 | 7.63 | 223.686 | 2098.7 | 26 | 41.033 | 6.26 | 1.488 | 5.84 | 8978.88 | 2.984 | 98 | 79.7 | 1364 | 20.47 | 5836.3 | 3486.7 | 3482.7 | 5020.6 | 1189.3 | 0.68059 | 7.328
2024-12-09 | 15:06 | Data | 0 | 29.739 | 26.728 | 239.777 | 7.63 | 223.822 | 2096.89 | 26.02 | 41.033 | 6.26 | 1.482 | 5.839 | 8947.23 | 3.004 | 98 | 79.7 | 1362 | 20.52 | 5815.7 | 3488 | 3496 | 5031.5 | 1189.3 | 0.67831 | 7.323
2024-12-09 | 15:06 | Data | 0 | 30.151 | 27.194 | 239.732 | 7.63 | 223.867 | 2095.08 | 26.02 | 41.033 | 6.26 | 1.491 | 5.843 | 8951.75 | 3.193 | 98 | 79.7 | 1362 | 20.52 | 5818.6 | 3490.2 | 3490.2 | 5026.5 | 1189.3 | 0.67928 | 7.334
2024-12-09 | 15:06 | Data | 0 | 30.516 | 27.039 | 240.049 | 7.63 | 223.912 | 2093.28 | 26.02 | 41.033 | 6.26 | 1.49 | 5.834 | 8969.84 | 3.045 | 98 | 79.7 | 1362 | 20.52 | 5830.4 | 3510.3 | 3487.7 | 5042.5 | 1189.3 | 0.68157 | 7.323
2024-12-09 | 15:06 | Data | 0 | 30.367 | 26.762 | 239.777 | 7.63 | 223.822 | 2098.7 | 26.02 | 41.123 | 6.27 | 1.493 | 5.846 | 8897.48 | 3.106 | 98 | 79.7 | 1364 | 20.52 | 5783.4 | 3496.4 | 3501.5 | 5040.7 | 1189.3 | 0.67803 | 7.339
2024-12-09 | 15:06 | Data | 0 | 29.787 | 26.85 | 239.732 | 7.63 | 223.731 | 2098.7 | 26.02 | 40.943 | 6.26 | 1.499 | 5.829 | 8897.48 | 2.883 | 98 | 79.5 | 1364 | 20.56 | 5783.4 | 3475 | 3492.3 | 5020.5 | 1189.3 | 0.67761 | 7.329
2024-12-09 | 15:06 | Data | 0 | 29.733 | 27.295 | 239.868 | 7.63 | 223.731 | 2091.47 | 26.02 | 40.943 | 6.26 | 1.499 | 5.836 | 8897.48 | 2.89 | 98 | 79.6 | 1359 | 20.52 | 5783.4 | 3483.6 | 3500.7 | 5034.2 | 1189.3 | 0.67722 | 7.334
2024-12-09 | 15:06 | Data | 0 | 29.949 | 26.965 | 239.732 | 7.63 | 223.731 | 2091.47 | 26.02 | 40.943 | 6.26 | 1.5 | 5.858 | 8897.48 | 2.991 | 98 | 79.6 | 1360 | 20.52 | 5783.4 | 3506.4 | 3489.8 | 5043.4 | 1189.3 | 0.68047 | 7.357
2024-12-09 | 15:06 | Data | 0 | 30.043 | 26.978 | 239.777 | 7.63 | 223.822 | 2091.47 | 26.02 | 40.943 | 6.26 | 1.491 | 5.843 | 8911.05 | 3.18 | 98 | 79.7 | 1359 | 20.52 | 5792.2 | 3512.4 | 3500.5 | 5051.2 | 1189.3 | 0.68108 | 7.335
2024-12-09 | 15:06 | Data | 0 | 30.185 | 26.931 | 240.004 | 7.63 | 224.002 | 2086.95 | 26.02 | 41.033 | 6.27 | 1.499 | 5.85 | 8924.61 | 2.896 | 98 | 79.6 | 1357 | 20.52 | 5801 | 3502.9 | 3476.6 | 5030.3 | 1189.3 | 0.68078 | 7.35
2024-12-09 | 15:06 | Data | 0 | 29.517 | 26.728 | 239.597 | 7.63 | 223.686 | 2088.76 | 26.01 | 41.033 | 6.26 | 1.503 | 5.884 | 8906.53 | 2.944 | 98 | 79.7 | 1358 | 20.52 | 5789.2 | 3507.4 | 3451 | 5013.8 | 1189.4 | 0.68415 | 7.386
2024-12-09 | 15:06 | Data | 0 | 30.266 | 26.978 | 240.004 | 7.63 | 223.822 | 2086.95 | 26.02 | 41.033 | 6.26 | 1.503 | 5.84 | 8915.57 | 2.883 | 98 | 79.5 | 1357 | 20.52 | 5795.1 | 3506.6 | 3442.4 | 5008.5 | 1189.4 | 0.68513 | 7.343
2024-12-09 | 15:06 | Data | 0 | 29.955 | 26.742 | 239.958 | 7.63 | 223.867 | 2087.85 | 26 | 41.033 | 6.27 | 1.503 | 5.831 | 8920.09 | 3.166 | 98 | 79.5 | 1357 | 20.52 | 5798.1 | 3490.7 | 3452.1 | 5004 | 1189.4 | 0.68316 | 7.335
2024-12-09 | 15:06 | Data | 0 | 29.908 | 26.965 | 239.732 | 7.63 | 223.867 | 2086.95 | 26.02 | 40.943 | 6.26 | 1.507 | 5.844 | 8920.09 | 2.971 | 98 | 79.5 | 1356 | 20.47 | 5798.1 | 3495.4 | 3458 | 5010.5 | 1189.4 | 0.68368 | 7.351
2024-12-09 | 15:06 | Data | 0 | 29.996 | 26.735 | 239.597 | 7.63 | 223.596 | 2084.24 | 26.02 | 40.943 | 6.26 | 1.496 | 5.864 | 8924.61 | 3.025 | 98 | 79.7 | 1354 | 20.43 | 5801 | 3496.2 | 3431.2 | 4990.9 | 1189.4 | 0.68632 | 7.359
2024-12-09 | 15:06 | Data | 0 | 29.955 | 26.938 | 239.687 | 7.63 | 223.686 | 2086.95 | 26.01 | 41.123 | 6.27 | 1.494 | 5.844 | 8929.14 | 3.106 | 98 | 79.6 | 1357 | 20.52 | 5803.9 | 3491.8 | 3455.1 | 5009.6 | 1189.4 | 0.68184 | 7.338
2024-12-09 | 15:06 | Data | 0 | 29.726 | 26.728 | 239.913 | 7.63 | 223.731 | 2084.24 | 26.01 | 41.033 | 6.27 | 1.5 | 5.841 | 8947.23 | 3.106 | 98 | 79.6 | 1355 | 20.52 | 5815.7 | 3506.5 | 3462.4 | 5022.8 | 1189.4 | 0.68217 | 7.341
2024-12-09 | 15:06 | Data | 0 | 30.28 | 27.241 | 240.004 | 7.63 | 224.002 | 2089.66 | 26.01 | 41.033 | 6.26 | 1.497 | 5.871 | 8960.79 | 3.16 | 98 | 79.7 | 1358 | 20.52 | 5824.5 | 3507.8 | 3481.5 | 5048.2 | 1189.4 | 0.68165 | 7.367
2024-12-09 | 15:07 | Data | 0 | 29.955 | 27.309 | 239.913 | 7.63 | 224.002 | 2086.95 | 26.02 | 41.033 | 6.27 | 1.501 | 5.856 | 8960.79 | 3.092 | 98 | 79.6 | 1356 | 20.52 | 5824.5 | 3513.8 | 3504.8 | 5056.1 | 1189.4 | 0.6816 | 7.358
2024-12-09 | 15:07 | Data | 0 | 30.185 | 27.046 | 240.004 | 7.63 | 223.912 | 2087.85 | 26.02 | 40.943 | 6.27 | 1.496 | 5.862 | 8951.75 | 2.896 | 98 | 79.7 | 1357 | 20.47 | 5818.6 | 3478 | 3501.5 | 5028.7 | 1189.4 | 0.67692 | 7.358
2024-12-09 | 15:07 | Data | 0 | 30.293 | 27.241 | 240.094 | 7.63 | 223.912 | 2084.24 | 26.02 | 41.033 | 6.27 | 1.502 | 5.839 | 8938.18 | 2.964 | 98 | 79.5 | 1354 | 20.52 | 5809.8 | 3495.9 | 3504.5 | 5042.8 | 1189.4 | 0.67874 | 7.342
2024-12-09 | 15:07 | Data | 0 | 30.036 | 26.944 | 239.913 | 7.63 | 223.867 | 2085.14 | 26.02 | 41.484 | 6.26 | 1.502 | 5.829 | 8965.31 | 2.883 | 98 | 79.5 | 1355 | 20.79 | 5827.5 | 3496.4 | 3490.2 | 5034.1 | 1189.4 | 0.67966 | 7.331
2024-12-09 | 15:07 | Data | 0 | 29.739 | 26.755 | 239.687 | 7.63 | 223.822 | 2086.04 | 26.01 | 41.033 | 6.27 | 1.506 | 5.838 | 8974.36 | 3.058 | 98 | 79.5 | 1355 | 20.52 | 5833.3 | 3506.1 | 3469.9 | 5025.8 | 1189.4 | 0.68282 | 7.343
2024-12-09 | 15:07 | Data | 0 | 30.273 | 26.877 | 239.777 | 7.63 | 223.867 | 2084.24 | 26.02 | 41.033 | 6.27 | 1.502 | 5.882 | 8969.84 | 2.991 | 98 | 79.7 | 1355 | 20.52 | 5830.4 | 3499.6 | 3442.7 | 5004.1 | 1189.4 | 0.68383 | 7.383
2024-12-09 | 15:07 | Data | 0 | 30.07 | 26.971 | 239.958 | 7.63 | 223.912 | 2081.53 | 26.02 | 40.943 | 6.26 | 1.49 | 5.851 | 8978.88 | 3.011 | 98 | 79.7 | 1353 | 20.52 | 5836.3 | 3527.1 | 3423.7 | 5005.1 | 1189.4 | 0.68979 | 7.339
2024-12-09 | 15:07 | Data | 0 | 29.82 | 26.749 | 239.597 | 7.63 | 223.686 | 2081.53 | 26.03 | 40.943 | 6.26 | 1.484 | 5.828 | 8951.75 | 2.883 | 98 | 79.7 | 1352 | 20.52 | 5818.6 | 3511 | 3432.4 | 5003.6 | 1189.4 | 0.68733 | 7.314
2024-12-09 | 15:07 | Data | 0 | 29.733 | 26.755 | 239.597 | 7.63 | 223.686 | 2084.24 | 26.02 | 40.943 | 6.26 | 1.496 | 5.837 | 8987.93 | 3.085 | 98 | 79.6 | 1355 | 20.52 | 5842.2 | 3492.8 | 3426.2 | 4986.1 | 1189.4 | 0.68568 | 7.333
2024-12-09 | 15:07 | Data | 0 | 30.063 | 27.268 | 239.913 | 7.63 | 223.822 | 2086.95 | 26.01 | 40.852 | 6.26 | 1.5 | 5.838 | 8965.31 | 2.991 | 98 | 79.6 | 1357 | 20.47 | 5827.5 | 3499.6 | 3464.7 | 5022.3 | 1189.4 | 0.68177 | 7.338
2024-12-09 | 15:07 | Data | 0 | 29.901 | 26.85 | 239.868 | 7.63 | 223.822 | 2089.66 | 26.02 | 41.033 | 6.26 | 1.507 | 5.857 | 8978.88 | 3.025 | 98 | 79.5 | 1358 | 20.52 | 5836.3 | 3494.1 | 3465.7 | 5015.8 | 1189.4 | 0.68255 | 7.364
2024-12-09 | 15:07 | Data | 0 | 29.672 | 26.904 | 239.642 | 7.63 | 223.912 | 2091.47 | 26.02 | 41.123 | 6.26 | 1.5 | 5.85 | 9024.1 | 3.247 | 98 | 79.6 | 1359 | 20.56 | 5865.7 | 3487.1 | 3480.6 | 5016.5 | 1189.4 | 0.68075 | 7.347
2024-12-09 | 15:07 | Data | 0 | 29.955 | 27.079 | 239.777 | 7.63 | 223.641 | 2094.18 | 26.02 | 41.304 | 6.26 | 1.497 | 5.848 | 9015.06 | 3.106 | 98 | 79.6 | 1361 | 20.65 | 5859.8 | 3511.9 | 3470.4 | 5026.7 | 1189.4 | 0.68396 | 7.343
2024-12-09 | 15:07 | Data | 0 | 30.185 | 26.911 | 239.868 | 7.63 | 223.867 | 2095.08 | 26.02 | 41.123 | 6.26 | 1.5 | 5.836 | 9037.67 | 3.22 | 98 | 79.5 | 1362 | 20.52 | 5874.5 | 3513.9 | 3487.1 | 5034.9 | 1189.4 | 0.68116 | 7.336
2024-12-09 | 15:07 | Data | 0 | 30.212 | 26.749 | 239.868 | 7.63 | 223.822 | 2094.18 | 26.03 | 41.304 | 6.27 | 1.494 | 5.858 | 9037.67 | 3.112 | 98 | 79.7 | 1361 | 20.61 | 5874.5 | 3496.2 | 3519.1 | 5044.7 | 1189.4 | 0.6766 | 7.353
2024-12-09 | 15:07 | Data | 0 | 29.672 | 26.951 | 239.777 | 7.63 | 223.912 | 2095.08 | 26.02 | 41.033 | 6.27 | 1.494 | 5.857 | 9006.01 | 2.95 | 98 | 79.7 | 1361 | 20.52 | 5853.9 | 3500.7 | 3486.4 | 5049.3 | 1189.4 | 0.68173 | 7.352
2024-12-09 | 15:07 | Data | 0 | 30.05 | 26.951 | 239.732 | 7.63 | 223.641 | 2095.99 | 26.02 | 41.304 | 6.27 | 1.499 | 5.853 | 8992.45 | 3.214 | 98 | 79.6 | 1362 | 20.61 | 5845.1 | 3500 | 3494.3 | 5037.4 | 1189.4 | 0.68033 | 7.352
2024-12-09 | 15:07 | Data | 0 | 30.347 | 27.1 | 239.732 | 7.63 | 223.822 | 2099.6 | 26.02 | 41.033 | 6.26 | 1.488 | 5.873 | 9001.49 | 2.998 | 98 | 79.8 | 1364 | 20.52 | 5851 | 3498 | 3499.9 | 5044.3 | 1189.4 | 0.67863 | 7.361
2024-12-09 | 15:08 | Data | 0 | 30.408 | 27.079 | 239.913 | 7.63 | 223.912 | 2096.89 | 26.02 | 41.213 | 6.26 | 1.494 | 5.85 | 8992.45 | 3.018 | 98 | 79.7 | 1364 | 20.61 | 5845.1 | 3485.2 | 3479.8 | 5017.9 | 1189.4 | 0.68007 | 7.344
2024-12-09 | 15:08 | Data | 0 | 30.171 | 27.16 | 239.777 | 7.63 | 223.822 | 2096.89 | 26.02 | 41.213 | 6.26 | 1.486 | 5.861 | 8965.31 | 3.112 | 98 | 79.8 | 1364 | 20.65 | 5827.5 | 3490.4 | 3482.8 | 5025.6 | 1189.4 | 0.6801 | 7.347
2024-12-09 | 15:08 | Data | 0 | 29.928 | 26.735 | 239.777 | 7.63 | 223.822 | 2095.99 | 26.02 | 41.484 | 6.27 | 1.487 | 5.877 | 8956.27 | 2.761 | 98 | 79.8 | 1362 | 20.7 | 5821.6 | 3515.6 | 3505.9 | 5055.3 | 1189.4 | 0.68031 | 7.365
2024-12-09 | 15:08 | Data | 0 | 29.982 | 26.755 | 239.777 | 7.63 | 223.686 | 2098.7 | 26.03 | 41.123 | 6.27 | 1.488 | 5.828 | 8951.75 | 2.971 | 98 | 79.7 | 1364 | 20.65 | 5818.6 | 3514.9 | 3495.7 | 5051.4 | 1189.4 | 0.68089 | 7.316
2024-12-09 | 15:08 | Data | 0 | 30.185 | 26.965 | 239.913 | 7.63 | 223.822 | 2096.89 | 26.02 | 41.304 | 6.26 | 1.487 | 5.819 | 8938.18 | 2.849 | 98 | 79.7 | 1363 | 20.65 | 5809.8 | 3503.2 | 3503.7 | 5061.1 | 1189.5 | 0.6788 | 7.304
2024-12-09 | 15:08 | Data | 0 | 30.03 | 26.971 | 239.958 | 7.63 | 223.912 | 2095.08 | 26.02 | 41.123 | 6.26 | 1.502 | 5.843 | 9444.67 | 2.998 | 98 | 79.5 | 1362 | 20.52 | 6139 | 3516.9 | 3501.2 | 5055.1 | 1189.5 | 0.68135 | 7.344
2024-12-09 | 15:08 | Data | 0 | 29.854 | 27.14 | 239.868 | 7.63 | 223.822 | 2092.37 | 26.01 | 41.304 | 6.27 | 1.507 | 5.834 | 9010.54 | 2.775 | 98 | 79.5 | 1359 | 20.65 | 5856.8 | 3483.3 | 3506.3 | 5035.1 | 1189.5 | 0.67707 | 7.339
2024-12-09 | 15:08 | Data | 0 | 30.408 | 26.796 | 239.642 | 7.63 | 223.867 | 2090.56 | 26.02 | 41.213 | 6.26 | 1.496 | 5.846 | 8992.45 | 2.93 | 98 | 79.6 | 1358 | 20.61 | 5845.1 | 3514.4 | 3513.4 | 5059.9 | 1189.5 | 0.68034 | 7.342
2024-12-09 | 15:08 | Data | 0 | 30.171 | 27.181 | 239.868 | 7.63 | 223.912 | 2089.66 | 26.02 | 41.123 | 6.27 | 1.5 | 5.858 | 9019.58 | 3.018 | 98 | 79.6 | 1358 | 20.65 | 5862.7 | 3479.1 | 3496.6 | 5024.8 | 1189.5 | 0.67833 | 7.357
2024-12-09 | 15:08 | Data | 0 | 29.739 | 26.958 | 239.687 | 7.63 | 223.686 | 2090.56 | 26.02 | 41.304 | 6.26 | 1.496 | 5.842 | 8933.66 | 2.944 | 98 | 79.6 | 1359 | 20.65 | 5806.9 | 3490.3 | 3481.1 | 5027.3 | 1189.5 | 0.68008 | 7.338
2024-12-09 | 15:08 | Data | 0 | 29.726 | 26.85 | 239.868 | 7.63 | 223.822 | 2089.66 | 26.02 | 40.943 | 6.26 | 1.494 | 5.848 | 8920.09 | 3.166 | 98 | 79.6 | 1358 | 20.52 | 5798.1 | 3499.9 | 3478.3 | 5030.5 | 1189.5 | 0.68258 | 7.342
2024-12-09 | 15:08 | Data | 0 | 30.185 | 26.809 | 239.913 | 7.63 | 223.912 | 2089.66 | 26.02 | 41.213 | 6.27 | 1.495 | 5.842 | 8902 | 3.058 | 98 | 79.6 | 1357 | 20.61 | 5786.3 | 3489.7 | 3462.8 | 5010.9 | 1189.5 | 0.68189 | 7.337
2024-12-09 | 15:08 | Data | 0 | 29.766 | 27.16 | 239.777 | 7.63 | 223.867 | 2090.56 | 26.02 | 41.213 | 6.27 | 1.49 | 5.815 | 8911.05 | 2.829 | 98 | 79.6 | 1359 | 20.7 | 5792.2 | 3482.1 | 3491.8 | 5024.8 | 1189.5 | 0.67827 | 7.305
2024-12-09 | 15:08 | Data | 0 | 30.057 | 26.965 | 239.777 | 7.63 | 223.867 | 2087.85 | 26.02 | 41.033 | 6.26 | 1.499 | 5.847 | 8978.88 | 3.004 | 98 | 79.6 | 1357 | 20.52 | 5836.3 | 3503.6 | 3446.7 | 5008.7 | 1189.5 | 0.68473 | 7.344
2024-12-09 | 15:08 | Data | 0 | 30.124 | 27.187 | 239.868 | 7.63 | 223.822 | 2086.04 | 26.02 | 40.943 | 6.26 | 1.503 | 5.841 | 8974.36 | 2.991 | 98 | 79.5 | 1357 | 20.52 | 5833.3 | 3515.2 | 3475.9 | 5037.7 | 1189.5 | 0.68285 | 7.344
2024-12-09 | 15:08 | Data | 0 | 29.982 | 26.789 | 239.958 | 7.63 | 223.867 | 2086.04 | 26.02 | 40.943 | 6.27 | 1.505 | 5.84 | 8983.4 | 2.998 | 98 | 79.5 | 1357 | 20.52 | 5839.2 | 3517.2 | 3457.4 | 5025.4 | 1189.5 | 0.68393 | 7.345
2024-12-09 | 15:08 | Data | 0 | 30.111 | 27.356 | 239.777 | 7.63 | 223.822 | 2091.47 | 26.01 | 41.033 | 6.26 | 1.494 | 5.857 | 8974.36 | 3.2 | 98 | 79.7 | 1359 | 20.52 | 5833.3 | 3490 | 3482.3 | 5023.4 | 1189.5 | 0.68045 | 7.351
2024-12-09 | 15:08 | Data | 0 | 30.111 | 27.282 | 239.958 | 7.63 | 223.731 | 2086.95 | 26.02 | 41.033 | 6.27 | 1.496 | 5.847 | 8960.79 | 2.944 | 98 | 79.6 | 1357 | 20.52 | 5824.5 | 3503 | 3486.7 | 5034.8 | 1189.5 | 0.68111 | 7.342
2024-12-09 | 15:09 | Data | 0 | 30.003 | 26.789 | 239.597 | 7.63 | 223.731 | 2087.85 | 26.02 | 41.033 | 6.26 | 1.499 | 5.824 | 8938.18 | 2.944 | 98 | 79.5 | 1357 | 20.52 | 5809.8 | 3499 | 3483.4 | 5026.6 | 1189.5 | 0.68231 | 7.322
2024-12-09 | 15:09 | Data | 0 | 30.232 | 26.789 | 239.868 | 7.63 | 223.957 | 2086.95 | 26.02 | 41.033 | 6.27 | 1.499 | 5.865 | 8947.23 | 3.045 | 98 | 79.6 | 1357 | 20.52 | 5815.7 | 3497.5 | 3513.3 | 5053.8 | 1189.5 | 0.67817 | 7.364
2024-12-09 | 15:09 | Data | 0 | 29.982 | 26.924 | 240.049 | 7.63 | 223.912 | 2086.95 | 26.02 | 41.033 | 6.26 | 1.499 | 5.858 | 8951.75 | 3.16 | 98 | 79.6 | 1357 | 20.52 | 5818.6 | 3508.8 | 3506.8 | 5052.6 | 1189.5 | 0.67988 | 7.358
2024-12-09 | 15:09 | Data | 0 | 29.915 | 26.742 | 239.777 | 7.63 | 223.867 | 2087.85 | 26.03 | 40.943 | 6.27 | 1.496 | 5.825 | 8938.18 | 3.004 | 98 | 79.6 | 1357 | 20.52 | 5809.8 | 3506.3 | 3455.5 | 5011.9 | 1189.5 | 0.68581 | 7.321
2024-12-09 | 15:09 | Data | 0 | 30.286 | 27.019 | 239.732 | 7.63 | 223.867 | 2090.56 | 26.01 | 41.123 | 6.27 | 1.495 | 5.85 | 9006.01 | 2.971 | 98 | 79.7 | 1358 | 20.52 | 5853.9 | 3499.3 | 3417.3 | 4982.2 | 1189.5 | 0.68785 | 7.343
2024-12-09 | 15:09 | Data | 0 | 29.942 | 26.742 | 239.687 | 7.63 | 223.822 | 2089.66 | 26.02 | 41.033 | 6.27 | 1.507 | 5.847 | 9010.54 | 3.166 | 98 | 79.5 | 1359 | 20.52 | 5856.8 | 3494 | 3392.3 | 4962.3 | 1189.5 | 0.6895 | 7.353
2024-12-09 | 15:09 | Data | 0 | 29.989 | 27.167 | 239.868 | 7.63 | 223.867 | 2085.14 | 26.03 | 41.033 | 6.27 | 1.503 | 5.821 | 9010.54 | 2.883 | 98 | 79.5 | 1355 | 20.52 | 5856.8 | 3531.7 | 3440.1 | 5023.3 | 1189.5 | 0.68866 | 7.323
2024-12-09 | 15:09 | Data | 0 | 30.225 | 26.803 | 239.732 | 7.63 | 223.912 | 2092.37 | 26.02 | 41.033 | 6.27 | 1.502 | 5.821 | 9010.54 | 3.328 | 98 | 79.5 | 1360 | 20.52 | 5856.8 | 3510.8 | 3461.4 | 5021.2 | 1189.5 | 0.68529 | 7.324
2024-12-09 | 15:09 | Data | 0 | 30.185 | 27.167 | 240.004 | 7.63 | 223.867 | 2092.37 | 26.02 | 41.033 | 6.27 | 1.499 | 5.843 | 8924.61 | 2.903 | 98 | 79.6 | 1360 | 20.47 | 5801 | 3510.2 | 3452 | 5016 | 1189.5 | 0.68609 | 7.342
2024-12-09 | 15:09 | Data | 0 | 29.969 | 26.965 | 239.732 | 7.63 | 223.731 | 2092.37 | 26.01 | 41.033 | 6.27 | 1.506 | 5.829 | 8956.27 | 2.991 | 98 | 79.5 | 1360 | 20.56 | 5821.6 | 3520.6 | 3470.3 | 5034.5 | 1189.5 | 0.68597 | 7.334
2024-12-09 | 15:09 | Data | 0 | 30.34 | 27.019 | 239.777 | 7.63 | 223.957 | 2089.66 | 26.02 | 40.943 | 6.27 | 1.507 | 5.83 | 8938.18 | 3.092 | 98 | 79.5 | 1358 | 20.47 | 5809.8 | 3494.9 | 3453.5 | 5007.1 | 1189.5 | 0.68296 | 7.336
2024-12-09 | 15:09 | Data | 0 | 30.313 | 26.985 | 239.732 | 7.63 | 223.957 | 2090.56 | 26.02 | 41.033 | 6.27 | 1.501 | 5.843 | 8938.18 | 3.025 | 98 | 79.6 | 1359 | 20.38 | 5809.8 | 3493 | 3500.1 | 5040.7 | 1189.5 | 0.67827 | 7.346
2024-12-09 | 15:09 | Data | 0 | 29.78 | 26.938 | 239.732 | 7.63 | 223.731 | 2093.28 | 26.02 | 41.033 | 6.28 | 1.495 | 5.85 | 8911.05 | 3.065 | 98 | 79.6 | 1359 | 20.47 | 5792.2 | 3487.1 | 3493.7 | 5032.3 | 1189.5 | 0.6784 | 7.345
2024-12-09 | 15:09 | Data | 0 | 29.807 | 26.938 | 240.004 | 7.63 | 223.912 | 2086.04 | 26.02 | 41.033 | 6.27 | 1.503 | 5.872 | 8929.14 | 2.883 | 98 | 79.6 | 1356 | 20.52 | 5803.9 | 3485.3 | 3499.9 | 5033 | 1189.5 | 0.67916 | 7.375
2024-12-09 | 15:09 | Data | 0 | 29.739 | 26.728 | 239.913 | 7.63 | 223.912 | 2086.95 | 26 | 40.943 | 6.27 | 1.502 | 5.848 | 8929.14 | 3.004 | 98 | 79.6 | 1357 | 20.47 | 5803.9 | 3491.9 | 3480.5 | 5024.2 | 1189.5 | 0.68074 | 7.351
2024-12-09 | 15:09 | Data | 0 | 30.057 | 27.329 | 239.913 | 7.63 | 223.731 | 2086.04 | 26.01 | 41.033 | 6.26 | 1.508 | 5.847 | 8929.14 | 2.917 | 98 | 79.5 | 1357 | 20.52 | 5803.9 | 3485.5 | 3451.7 | 5000.6 | 1189.5 | 0.68252 | 7.353
2024-12-09 | 15:09 | Data | 0 | 30.185 | 27.194 | 240.094 | 7.63 | 223.867 | 2092.37 | 26.02 | 41.033 | 6.27 | 1.503 | 5.805 | 8938.18 | 2.991 | 98 | 79.4 | 1360 | 20.61 | 5809.8 | 3494 | 3480.7 | 5022.5 | 1189.5 | 0.6815 | 7.311
2024-12-09 | 15:10 | Data | 0 | 30.084 | 26.877 | 239.868 | 7.63 | 223.912 | 2088.76 | 26.02 | 41.033 | 6.26 | 1.505 | 5.829 | 8951.75 | 3.092 | 98 | 79.5 | 1358 | 20.52 | 5818.6 | 3488.3 | 3446 | 4999.6 | 1189.6 | 0.68257 | 7.335
2024-12-09 | 15:10 | Data | 0 | 29.76 | 26.904 | 239.868 | 7.63 | 223.822 | 2089.66 | 26.03 | 40.943 | 6.27 | 1.5 | 5.824 | 8956.27 | 2.883 | 98 | 79.5 | 1357 | 20.52 | 5821.6 | 3531 | 3462.3 | 5037.3 | 1189.6 | 0.68557 | 7.324
2024-12-09 | 15:10 | Data | 0 | 30.32 | 27.032 | 240.139 | 7.63 | 224.228 | 2089.66 | 26.02 | 41.033 | 6.26 | 1.495 | 5.806 | 9390.4 | 3.16 | 98 | 79.5 | 1358 | 20.52 | 6103.8 | 3519 | 3532.6 | 5080.3 | 1189.6 | 0.67779 | 7.3
2024-12-09 | 15:10 | Data | 0 | 29.969 | 27.248 | 240.23 | 7.63 | 224.274 | 2090.56 | 26.02 | 41.033 | 6.26 | 1.499 | 5.833 | 8969.84 | 2.944 | 98 | 79.6 | 1358 | 20.52 | 5830.4 | 3517 | 3544 | 5085 | 1189.6 | 0.6768 | 7.331
2024-12-09 | 15:10 | Data | 0 | 30.286 | 27.289 | 240.185 | 7.63 | 224.138 | 2089.66 | 26.02 | 40.943 | 6.27 | 1.499 | 5.865 | 8951.75 | 3.106 | 98 | 79.6 | 1359 | 20.52 | 5818.6 | 3513.3 | 3580.2 | 5109.4 | 1189.6 | 0.67276 | 7.365
2024-12-09 | 15:10 | Data | 0 | 30.009 | 26.843 | 240.004 | 7.63 | 224.048 | 2089.66 | 26.03 | 40.943 | 6.27 | 1.502 | 5.846 | 8951.75 | 3.031 | 98 | 79.6 | 1358 | 20.52 | 5818.6 | 3535.6 | 3575.9 | 5122.8 | 1189.6 | 0.67606 | 7.35
2024-12-09 | 15:10 | Data | 0 | 29.928 | 27.187 | 239.958 | 7.63 | 224.093 | 2089.66 | 26.03 | 40.943 | 6.26 | 1.512 | 5.838 | 8956.27 | 2.998 | 98 | 79.4 | 1358 | 20.52 | 5821.6 | 3544 | 3577.7 | 5125.4 | 1189.6 | 0.67715 | 7.351
2024-12-09 | 15:10 | Data | 0 | 30.455 | 26.998 | 240.004 | 7.63 | 224.093 | 2091.47 | 26.01 | 40.943 | 6.27 | 1.504 | 5.854 | 8902 | 3.011 | 98 | 79.6 | 1361 | 20.47 | 5786.3 | 3518.4 | 3556 | 5094.9 | 1189.6 | 0.67571 | 7.359
2024-12-09 | 15:10 | Data | 0 | 29.955 | 27.268 | 240.139 | 7.63 | 224.093 | 2085.14 | 26.02 | 41.033 | 6.26 | 1.503 | 5.848 | 8911.05 | 2.964 | 98 | 79.6 | 1355 | 20.52 | 5792.2 | 3534.4 | 3554.1 | 5104.2 | 1189.6 | 0.67841 | 7.35
2024-12-09 | 15:10 | Data | 0 | 29.679 | 27.262 | 240.049 | 7.63 | 224.048 | 2088.76 | 26.02 | 41.033 | 6.27 | 1.506 | 5.85 | 8879.39 | 3.025 | 98 | 79.5 | 1358 | 20.52 | 5771.6 | 3556.3 | 3534.2 | 5119.3 | 1189.6 | 0.68019 | 7.354
2024-12-09 | 15:10 | Data | 0 | 29.962 | 27.282 | 240.049 | 7.63 | 224.138 | 2083.33 | 26.02 | 41.033 | 6.26 | 1.506 | 5.879 | 8911.05 | 2.991 | 98 | 79.6 | 1355 | 20.52 | 5792.2 | 3522.7 | 3544 | 5090.2 | 1189.6 | 0.67645 | 7.387
2024-12-09 | 15:10 | Data | 0 | 30.259 | 27.019 | 240.094 | 7.63 | 224.138 | 2084.24 | 26.02 | 40.852 | 6.27 | 1.504 | 5.861 | 8933.66 | 3.274 | 98 | 79.6 | 1355 | 20.52 | 5806.9 | 3543 | 3548.2 | 5110.7 | 1189.6 | 0.67766 | 7.366
2024-12-09 | 15:10 | Data | 0 | 29.726 | 26.85 | 240.094 | 7.63 | 224.183 | 2081.53 | 26.02 | 41.033 | 6.27 | 1.492 | 5.838 | 8956.27 | 3.166 | 98 | 79.6 | 1354 | 20.47 | 5821.6 | 3541.5 | 3546.9 | 5108.6 | 1189.6 | 0.67881 | 7.33
2024-12-09 | 15:10 | Data | 0 | 30.408 | 27.133 | 240.275 | 7.63 | 224.093 | 2084.24 | 26.02 | 41.033 | 6.27 | 1.499 | 5.831 | 8951.75 | 3.106 | 98 | 79.6 | 1355 | 20.52 | 5818.6 | 3555.4 | 3561.7 | 5125.7 | 1189.6 | 0.67943 | 7.33
2024-12-09 | 15:10 | Data | 0 | 29.733 | 26.749 | 239.958 | 7.63 | 223.912 | 2081.53 | 26.02 | 41.033 | 6.27 | 1.503 | 5.832 | 8956.27 | 2.95 | 98 | 79.5 | 1353 | 20.52 | 5821.6 | 3519.1 | 3557 | 5098.2 | 1189.6 | 0.67524 | 7.335
2024-12-09 | 15:10 | Data | 0 | 29.733 | 26.823 | 240.094 | 7.63 | 224.002 | 2081.53 | 26.02 | 41.033 | 6.27 | 1.507 | 5.849 | 8956.27 | 3.106 | 98 | 79.5 | 1353 | 20.52 | 5821.6 | 3537.9 | 3564.7 | 5114.4 | 1189.6 | 0.67693 | 7.357
2024-12-09 | 15:10 | Data | 0 | 29.571 | 26.904 | 240.139 | 7.63 | 224.048 | 2082.43 | 26.02 | 40.943 | 6.27 | 1.5 | 5.847 | 8947.23 | 2.917 | 98 | 79.6 | 1354 | 20.47 | 5815.7 | 3510.6 | 3574.8 | 5108.5 | 1189.6 | 0.67305 | 7.348
2024-12-09 | 15:10 | Data | 0 | 30.131 | 26.749 | 240.004 | 7.63 | 224.093 | 2084.24 | 26.02 | 41.033 | 6.26 | 1.503 | 5.842 | 8960.79 | 3.092 | 98 | 79.5 | 1355 | 20.52 | 5824.5 | 3520 | 3571.2 | 5111 | 1189.6 | 0.67354 | 7.345
2024-12-09 | 15:11 | Data | 0 | 30.212 | 26.823 | 240.23 | 7.63 | 224.319 | 2084.24 | 26.02 | 40.943 | 6.27 | 1.511 | 5.863 | 8933.66 | 3.099 | 98 | 79.5 | 1355 | 20.47 | 5806.9 | 3532.1 | 3564.9 | 5112.3 | 1189.6 | 0.67522 | 7.374
2024-12-09 | 15:11 | Data | 0 | 30.185 | 27.1 | 240.049 | 7.63 | 224.093 | 2085.14 | 26.01 | 41.123 | 6.26 | 1.506 | 5.847 | 8956.27 | 2.896 | 98 | 79.5 | 1355 | 20.52 | 5821.6 | 3535.6 | 3545 | 5100.4 | 1189.6 | 0.67793 | 7.352
2024-12-09 | 15:11 | Data | 0 | 30.111 | 27.268 | 240.049 | 7.63 | 224.183 | 2087.85 | 26.02 | 40.943 | 6.26 | 1.506 | 5.868 | 8951.75 | 3.065 | 98 | 79.6 | 1357 | 20.47 | 5818.6 | 3551.2 | 3524.6 | 5098 | 1189.6 | 0.68227 | 7.376
2024-12-09 | 15:11 | Data | 0 | 30.138 | 27.167 | 240.23 | 7.63 | 224.183 | 2085.14 | 26.02 | 40.943 | 6.26 | 1.494 | 5.88 | 8951.75 | 3.038 | 98 | 79.7 | 1355 | 20.47 | 5818.6 | 3545.9 | 3523.5 | 5092.9 | 1189.6 | 0.68167 | 7.374
2024-12-09 | 15:11 | Data | 0 | 29.955 | 27.16 | 240.049 | 7.63 | 223.867 | 2086.95 | 26.02 | 41.123 | 6.27 | 1.5 | 5.876 | 8969.84 | 2.836 | 98 | 79.7 | 1356 | 20.52 | 5830.4 | 3535.4 | 3546.8 | 5102.1 | 1189.6 | 0.67742 | 7.374
2024-12-09 | 15:11 | Data | 0 | 29.766 | 26.958 | 240.139 | 7.63 | 224.183 | 2087.85 | 26.02 | 41.033 | 6.27 | 1.501 | 5.849 | 8956.27 | 2.775 | 98 | 79.6 | 1357 | 20.52 | 5821.6 | 3539.4 | 3534.8 | 5094.6 | 1189.6 | 0.68001 | 7.351
2024-12-09 | 15:11 | Data | 0 | 29.854 | 26.735 | 240.094 | 7.63 | 224.093 | 2084.24 | 26.01 | 41.033 | 6.26 | 1.497 | 5.834 | 8969.84 | 3.052 | 98 | 79.6 | 1355 | 20.47 | 5830.4 | 3531.7 | 3553.9 | 5104.5 | 1189.6 | 0.67754 | 7.33
2024-12-09 | 15:11 | Data | 0 | 29.841 | 26.728 | 240.049 | 7.63 | 224.093 | 2085.14 | 26.03 | 41.033 | 6.27 | 1.5 | 5.85 | 8960.79 | 3.2 | 98 | 79.6 | 1355 | 20.47 | 5824.5 | 3542.9 | 3506.1 | 5079.2 | 1189.6 | 0.68266 | 7.35
2024-12-09 | 15:11 | Data | 0 | 30.273 | 27.403 | 240.23 | 7.63 | 224.048 | 2085.14 | 26.02 | 40.943 | 6.27 | 1.498 | 5.858 | 8974.36 | 3.004 | 98 | 79.6 | 1355 | 20.47 | 5833.3 | 3533.9 | 3549.8 | 5102.6 | 1189.6 | 0.67818 | 7.358
2024-12-09 | 15:11 | Data | 0 | 29.949 | 27.167 | 239.958 | 7.63 | 224.048 | 2086.04 | 26.02 | 41.033 | 6.27 | 1.49 | 5.829 | 8965.31 | 3.16 | 98 | 79.7 | 1357 | 20.52 | 5827.5 | 3457.3 | 3531.7 | 5032.7 | 1189.6 | 0.67123 | 7.319
2024-12-09 | 15:11 | Data | 0 | 30.158 | 27.073 | 240.139 | 7.63 | 224.138 | 2088.76 | 26.02 | 40.943 | 6.27 | 1.499 | 5.851 | 8938.18 | 3.011 | 98 | 79.6 | 1358 | 20.47 | 5809.8 | 3462.8 | 3550 | 5047.5 | 1189.6 | 0.67217 | 7.351
2024-12-09 | 15:11 | Data | 0 | 29.726 | 26.951 | 240.049 | 7.63 | 224.093 | 2090.56 | 26.02 | 41.123 | 6.27 | 1.495 | 5.848 | 8938.18 | 2.788 | 98 | 79.6 | 1358 | 20.56 | 5809.8 | 3470.4 | 3544.7 | 5048.3 | 1189.6 | 0.67111 | 7.344
2024-12-09 | 15:11 | Data | 0 | 30.34 | 26.87 | 240.139 | 7.63 | 224.093 | 2090.56 | 26.02 | 41.033 | 6.27 | 1.504 | 5.848 | 8929.14 | 3.193 | 98 | 79.5 | 1358 | 20.56 | 5803.9 | 3462.8 | 3526.4 | 5034.2 | 1189.7 | 0.67414 | 7.353
2024-12-09 | 15:11 | Data | 0 | 29.928 | 27.174 | 240.049 | 7.63 | 223.912 | 2090.56 | 26.06 | 41.033 | 6.27 | 1.497 | 5.826 | 8929.14 | 2.998 | 98 | 79.6 | 1359 | 20.47 | 5803.9 | 3445.5 | 3524.7 | 5019.1 | 1189.7 | 0.67156 | 7.324
2024-12-09 | 15:11 | Data | 0 | 29.726 | 26.728 | 239.958 | 7.63 | 224.002 | 2089.66 | 26.02 | 41.033 | 6.26 | 1.506 | 5.85 | 8933.66 | 2.998 | 98 | 79.5 | 1359 | 20.47 | 5806.9 | 3468.2 | 3527.8 | 5037.7 | 1189.7 | 0.67387 | 7.356
2024-12-09 | 15:11 | Data | 0 | 29.928 | 26.958 | 239.777 | 7.63 | 224.002 | 2092.37 | 26.02 | 40.943 | 6.27 | 1.506 | 5.828 | 8938.18 | 3.126 | 98 | 79.5 | 1360 | 20.47 | 5809.8 | 3461.1 | 3513.8 | 5022.4 | 1189.7 | 0.6748 | 7.333
2024-12-09 | 15:11 | Data | 0 | 29.881 | 26.735 | 240.094 | 7.63 | 224.048 | 2087.85 | 26.02 | 41.033 | 6.26 | 1.498 | 5.842 | 8933.66 | 2.809 | 98 | 79.6 | 1357 | 20.47 | 5806.9 | 3462.4 | 3512.9 | 5025.4 | 1189.7 | 0.67455 | 7.341
2024-12-09 | 15:12 | Data | 0 | 30.225 | 27.039 | 240.185 | 7.63 | 224.048 | 2095.08 | 26.02 | 41.033 | 6.26 | 1.502 | 5.851 | 8933.66 | 3.126 | 98 | 79.6 | 1362 | 20.52 | 5806.9 | 3453 | 3524.6 | 5023.3 | 1189.7 | 0.67376 | 7.353
2024-12-09 | 15:12 | Data | 0 | 29.962 | 26.755 | 240.049 | 7.63 | 224.048 | 2095.08 | 26.01 | 41.033 | 6.27 | 1.502 | 5.848 | 8965.31 | 2.991 | 98 | 79.6 | 1362 | 20.52 | 5827.5 | 3512.2 | 3514.9 | 5062.5 | 1189.7 | 0.67967 | 7.352
2024-12-09 | 15:12 | Data | 0 | 29.841 | 26.715 | 239.913 | 7.63 | 223.867 | 2092.37 | 26.02 | 41.033 | 6.26 | 1.491 | 5.824 | 9444.67 | 3.011 | 98 | 79.6 | 1360 | 20.52 | 6139 | 3493.1 | 3505.8 | 5046.3 | 1189.7 | 0.6772 | 7.315
2024-12-09 | 15:12 | Data | 0 | 29.949 | 27.336 | 240.185 | 7.63 | 224.048 | 2092.37 | 26.02 | 40.943 | 6.27 | 1.494 | 5.823 | 8983.4 | 2.998 | 98 | 79.6 | 1360 | 20.52 | 5839.2 | 3518.6 | 3536.8 | 5080.6 | 1189.7 | 0.67817 | 7.318
2024-12-09 | 15:12 | Data | 0 | 29.631 | 26.533 | 239.868 | 7.63 | 223.912 | 2086.95 | 26.02 | 41.213 | 6.26 | 1.492 | 5.847 | 8974.36 | 2.944 | 98 | 79.7 | 1357 | 20.65 | 5833.3 | 3519.4 | 3519.2 | 5070.9 | 1189.7 | 0.67915 | 7.338
2024-12-09 | 15:12 | Data | 0 | 30.151 | 26.965 | 239.777 | 7.63 | 223.822 | 2092.37 | 26.03 | 41.213 | 6.27 | 1.48 | 5.851 | 8956.27 | 3.031 | 98 | 79.8 | 1360 | 20.61 | 5821.6 | 3524.1 | 3498.7 | 5055.4 | 1189.7 | 0.68163 | 7.331
2024-12-09 | 15:12 | Data | 0 | 29.726 | 26.722 | 239.777 | 7.63 | 223.912 | 2095.08 | 26.02 | 41.484 | 6.26 | 1.503 | 5.876 | 8933.66 | 3.025 | 98 | 79.6 | 1361 | 20.74 | 5806.9 | 3498.8 | 3501.5 | 5044.5 | 1189.7 | 0.67845 | 7.38
2024-12-09 | 15:12 | Data | 0 | 30.273 | 26.971 | 239.868 | 7.63 | 224.093 | 2093.28 | 26.02 | 41.123 | 6.27 | 1.513 | 5.858 | 8938.18 | 3.234 | 98 | 79.5 | 1361 | 20.52 | 5809.8 | 3524.6 | 3480.4 | 5041.4 | 1189.7 | 0.68337 | 7.371
2024-12-09 | 15:12 | Data | 0 | 30.117 | 27.403 | 240.049 | 7.63 | 224.093 | 2095.99 | 26.01 | 41.033 | 6.27 | 1.486 | 5.838 | 8920.09 | 2.977 | 98 | 79.7 | 1362 | 20.47 | 5798.1 | 3519.5 | 3483.6 | 5047.9 | 1189.7 | 0.68194 | 7.323
2024-12-09 | 15:12 | Data | 0 | 29.746 | 26.985 | 240.004 | 7.63 | 224.093 | 2095.99 | 26.02 | 41.033 | 6.27 | 1.497 | 5.818 | 8960.79 | 2.822 | 98 | 79.5 | 1361 | 20.52 | 5824.5 | 3512.2 | 3498.8 | 5051.6 | 1189.7 | 0.68006 | 7.313
2024-12-09 | 15:12 | Data | 0 | 29.935 | 26.519 | 240.049 | 7.63 | 224.002 | 2095.08 | 26.02 | 40.943 | 6.26 | 1.486 | 5.842 | 8978.88 | 3.038 | 98 | 79.7 | 1361 | 20.47 | 5836.3 | 3533.9 | 3488.5 | 5060 | 1189.7 | 0.68288 | 7.327
2024-12-09 | 15:12 | Data | 0 | 29.544 | 26.587 | 239.958 | 7.63 | 224.002 | 2098.7 | 26.02 | 41.033 | 6.26 | 1.487 | 5.836 | 8969.84 | 2.91 | 98 | 79.7 | 1363 | 20.47 | 5830.4 | 3523.4 | 3462.8 | 5033.3 | 1189.7 | 0.68568 | 7.323
2024-12-09 | 15:12 | Data | 0 | 29.712 | 26.728 | 240.049 | 7.63 | 224.002 | 2095.99 | 26.02 | 40.943 | 6.26 | 1.49 | 5.838 | 8969.84 | 3.106 | 98 | 79.7 | 1362 | 20.52 | 5830.4 | 3515.9 | 3472.9 | 5036.9 | 1189.7 | 0.68261 | 7.328
2024-12-09 | 15:12 | Data | 0 | 30.286 | 26.6 | 240.32 | 7.63 | 224.093 | 2096.89 | 26.02 | 41.033 | 6.26 | 1.493 | 5.856 | 8947.23 | 2.998 | 98 | 79.7 | 1362 | 20.56 | 5815.7 | 3508.8 | 3468.7 | 5033.6 | 1189.7 | 0.68076 | 7.351
2024-12-09 | 15:12 | Data | 0 | 30.151 | 26.87 | 240.004 | 7.63 | 224.048 | 2096.89 | 26.01 | 41.033 | 6.27 | 1.504 | 5.846 | 8933.66 | 3.166 | 98 | 79.5 | 1363 | 20.52 | 5806.9 | 3510.9 | 3488.7 | 5043.2 | 1189.7 | 0.68175 | 7.352
2024-12-09 | 15:12 | Data | 0 | 29.739 | 26.627 | 240.049 | 7.63 | 223.957 | 2098.7 | 26.02 | 40.943 | 6.26 | 1.481 | 5.826 | 8924.61 | 2.896 | 98 | 79.7 | 1364 | 20.52 | 5801 | 3511.8 | 3493.7 | 5055.9 | 1189.7 | 0.68108 | 7.306
2024-12-09 | 15:12 | Data | 0 | 29.577 | 26.728 | 240.004 | 7.63 | 223.957 | 2094.18 | 26.02 | 40.943 | 6.27 | 1.49 | 5.865 | 8929.14 | 2.775 | 98 | 79.7 | 1362 | 20.56 | 5803.9 | 3505.9 | 3502.9 | 5051.7 | 1189.7 | 0.67905 | 7.353
2024-12-09 | 15:12 | Data | 0 | 29.442 | 26.674 | 239.777 | 7.63 | 223.867 | 2095.99 | 26.03 | 40.943 | 6.27 | 1.5 | 5.819 | 8956.27 | 3.079 | 98 | 79.5 | 1362 | 20.52 | 5821.6 | 3507.2 | 3505.9 | 5042.7 | 1189.7 | 0.68104 | 7.32
2024-12-09 | 15:13 | Data | 0 | 29.841 | 26.904 | 239.868 | 7.63 | 223.912 | 2094.18 | 26.02 | 40.852 | 6.27 | 1.502 | 5.832 | 9001.49 | 3.166 | 98 | 79.5 | 1362 | 20.47 | 5851 | 3518.5 | 3482.6 | 5048.6 | 1189.7 | 0.68272 | 7.334
2024-12-09 | 15:13 | Data | 0 | 29.496 | 26.499 | 239.732 | 7.63 | 223.957 | 2095.08 | 26.02 | 41.033 | 6.27 | 1.498 | 5.845 | 9006.01 | 2.991 | 98 | 79.6 | 1362 | 20.52 | 5853.9 | 3500.8 | 3420.2 | 4990.7 | 1189.7 | 0.68762 | 7.342
2024-12-09 | 15:13 | Data | 0 | 28.457 | 25.574 | 238.873 | 7.63 | 223.008 | 2095.99 | 26.01 | 41.033 | 6.27 | 1.5 | 5.851 | 9001.49 | 2.984 | 98 | 79.6 | 1362 | 20.47 | 5851 | 3493.9 | 3441.5 | 4998.1 | 1189.7 | 0.68467 | 7.352
2024-12-09 | 15:13 | Data | 0 | 27.079 | 23.778 | 237.878 | 7.63 | 222.104 | 2094.18 | 26.03 | 41.033 | 6.26 | 1.511 | 5.829 | 8992.45 | 3.166 | 98 | 79.4 | 1362 | 20.52 | 5845.1 | 3525.1 | 3424.3 | 5003.6 | 1189.7 | 0.69021 | 7.342
2024-12-09 | 15:13 | Data | 0 | 26.742 | 23.913 | 237.516 | 7.63 | 221.833 | 2095.08 | 26.01 | 40.943 | 6.27 | 1.5 | 5.798 | 8915.57 | 2.937 | 98 | 79.4 | 1362 | 20.47 | 5795.1 | 3503 | 3455.4 | 5019 | 1189.7 | 0.68249 | 7.299
2024-12-09 | 15:13 | Data | 0 | 26.256 | 23.272 | 238.285 | 7.63 | 222.421 | 2095.08 | 26.03 | 41.033 | 6.27 | 1.49 | 5.795 | 8924.61 | 2.998 | 98 | 79.6 | 1361 | 20.52 | 5801 | 3539.6 | 3488.1 | 5063.5 | 1189.7 | 0.68483 | 7.286
2024-12-09 | 15:13 | Data | 0 | 26.492 | 23.089 | 239.189 | 7.63 | 223.189 | 2095.08 | 26.03 | 41.033 | 6.27 | 1.491 | 5.807 | 8920.09 | 3.153 | 98 | 79.6 | 1362 | 20.47 | 5798.1 | 3521.4 | 3532.9 | 5081.5 | 1189.7 | 0.6784 | 7.299
2024-12-09 | 15:13 | Data | 0 | 26.269 | 23.272 | 239.235 | 7.63 | 223.234 | 2095.08 | 26.06 | 41.304 | 6.27 | 1.49 | 5.833 | 8920.09 | 2.998 | 98 | 79.7 | 1362 | 20.65 | 5798.1 | 3522.3 | 3557.7 | 5100.3 | 1189.8 | 0.67598 | 7.323
2024-12-09 | 15:13 | Data | 0 | 26.283 | 23.494 | 239.325 | 7.63 | 223.46 | 2094.18 | 26.06 | 41.033 | 6.27 | 1.487 | 5.845 | 8938.18 | 2.95 | 98 | 79.7 | 1361 | 20.52 | 5809.8 | 3517.5 | 3528.5 | 5072.4 | 1189.8 | 0.67875 | 7.332
2024-12-09 | 15:13 | Data | 0 | 25.844 | 23.062 | 239.28 | 7.63 | 223.324 | 2095.08 | 26.06 | 40.943 | 6.27 | 1.505 | 5.794 | 8911.05 | 3.058 | 98 | 79.4 | 1361 | 20.52 | 5792.2 | 3542.9 | 3520.5 | 5084.8 | 1189.8 | 0.6827 | 7.299
2024-12-09 | 15:13 | Data | 0 | 26.492 | 23.508 | 240.049 | 7.63 | 224.093 | 2092.37 | 26.06 | 40.943 | 6.27 | 1.504 | 5.827 | 8920.09 | 2.998 | 98 | 79.5 | 1360 | 20.52 | 5798.1 | 3529.3 | 3499.3 | 5065.5 | 1189.8 | 0.68533 | 7.331
2024-12-09 | 15:13 | Data | 0 | 27.052 | 23.683 | 240.32 | 7.63 | 224.409 | 2092.37 | 26.07 | 40.943 | 6.27 | 1.5 | 5.803 | 8924.61 | 3.119 | 98 | 79.5 | 1360 | 20.47 | 5801 | 3599 | 3521.4 | 5121.4 | 1189.8 | 0.68907 | 7.302
2024-12-09 | 15:13 | Data | 0 | 26.276 | 23.272 | 240.275 | 7.63 | 224.319 | 2095.08 | 26.07 | 40.943 | 6.27 | 1.503 | 5.845 | 8978.88 | 3.004 | 98 | 79.5 | 1362 | 20.52 | 5836.3 | 3544.2 | 3515.2 | 5085.5 | 1189.8 | 0.68217 | 7.348
2024-12-09 | 15:13 | Data | 0 | 26.262 | 23.056 | 240.139 | 7.63 | 224.183 | 2089.66 | 26.06 | 40.943 | 6.27 | 1.5 | 5.875 | 8965.31 | 3.065 | 98 | 79.7 | 1358 | 20.52 | 5827.5 | 3551.7 | 3470.2 | 5060.5 | 1189.8 | 0.6873 | 7.375
2024-12-09 | 15:13 | Data | 0 | 26.715 | 23.461 | 240.411 | 7.64 | 224.454 | 2089.66 | 26.03 | 40.943 | 6.27 | 1.505 | 5.879 | 8987.93 | 3.207 | 98 | 79.6 | 1358 | 20.52 | 5842.2 | 3550.9 | 3494 | 5072 | 1189.8 | 0.68615 | 7.385
2024-12-09 | 15:13 | Data | 0 | 26.661 | 23.245 | 240.456 | 7.63 | 224.499 | 2087.85 | 26.05 | 40.943 | 6.27 | 1.5 | 5.854 | 8996.97 | 3.308 | 98 | 79.6 | 1357 | 20.52 | 5848 | 3562.2 | 3490.3 | 5077.9 | 1189.8 | 0.68565 | 7.352
2024-12-09 | 15:13 | Data | 0 | 27.255 | 24.143 | 240.999 | 7.64 | 224.951 | 2088.76 | 26.07 | 40.943 | 6.27 | 1.511 | 5.873 | 8983.4 | 3.227 | 98 | 79.5 | 1358 | 20.47 | 5839.2 | 3528.4 | 3555 | 5104.9 | 1189.8 | 0.67578 | 7.384
2024-12-09 | 15:13 | Data | 0 | 27.302 | 24.264 | 241.134 | 7.63 | 225.042 | 2088.76 | 26.06 | 41.033 | 6.27 | 1.505 | 5.862 | 8965.31 | 3.214 | 98 | 79.6 | 1359 | 20.52 | 5827.5 | 3541.7 | 3555.2 | 5108.7 | 1189.8 | 0.67904 | 7.368
2024-12-09 | 15:14 | Data | 0 | 26.269 | 23.069 | 240.185 | 7.63 | 224.364 | 2086.95 | 26.06 | 40.943 | 6.27 | 1.496 | 5.872 | 8974.36 | 3.011 | 98 | 79.7 | 1357 | 20.52 | 5833.3 | 3544.8 | 3558.6 | 5112.7 | 1189.8 | 0.6792 | 7.368
2024-12-09 | 15:14 | Data | 0 | 26.904 | 23.846 | 240.863 | 7.63 | 224.771 | 2089.66 | 26.06 | 40.943 | 6.27 | 1.49 | 5.856 | 8965.31 | 2.984 | 98 | 79.7 | 1359 | 20.52 | 5827.5 | 3565 | 3555.7 | 5129.8 | 1189.8 | 0.68038 | 7.345
2024-12-09 | 15:14 | Data | 0 | 26.499 | 23.501 | 240.411 | 7.63 | 224.409 | 2090.56 | 26.07 | 40.491 | 6.27 | 1.499 | 5.837 | 8974.36 | 3.004 | 98.1 | 79.6 | 1358 | 20.2 | 5833.3 | 3556 | 3563.2 | 5127.3 | 1189.8 | 0.67777 | 7.335
2024-12-09 | 15:14 | Data | 0 | 27.194 | 23.744 | 240.863 | 7.63 | 224.816 | 2090.56 | 26.07 | 41.033 | 6.27 | 1.508 | 5.858 | 8960.79 | 3.241 | 98 | 79.5 | 1358 | 20.52 | 5824.5 | 3536.9 | 3541.2 | 5104.9 | 1189.8 | 0.67908 | 7.366
2024-12-09 | 15:14 | Data | 0 | 27.194 | 23.967 | 240.954 | 7.64 | 224.816 | 2084.24 | 26.06 | 41.033 | 6.27 | 1.501 | 5.85 | 8965.31 | 3.227 | 98 | 79.6 | 1355 | 20.52 | 5827.5 | 3555.7 | 3501.7 | 5082.5 | 1189.8 | 0.68412 | 7.352
2024-12-09 | 15:14 | Data | 0 | 26.506 | 23.319 | 240.411 | 7.63 | 224.499 | 2089.66 | 26.07 | 41.033 | 6.27 | 1.512 | 5.845 | 8951.75 | 3.18 | 98 | 79.4 | 1358 | 20.47 | 5818.6 | 3534.7 | 3476.9 | 5053.1 | 1189.8 | 0.68522 | 7.357
2024-12-09 | 15:14 | Data | 0 | 25.716 | 22.698 | 240.049 | 7.63 | 224.138 | 2089.66 | 26.08 | 41.033 | 6.27 | 1.511 | 5.84 | 8947.23 | 2.93 | 98 | 79.5 | 1358 | 20.52 | 5815.7 | 3540.6 | 3469.5 | 5061.3 | 1189.8 | 0.68532 | 7.347
2024-12-09 | 15:14 | Data | 0 | 26.472 | 23.17 | 240.32 | 7.63 | 224.183 | 2088.76 | 26.07 | 40.581 | 6.28 | 1.501 | 5.828 | 8915.57 | 3.166 | 98.1 | 79.5 | 1358 | 20.29 | 5795.1 | 3556 | 3469.6 | 5059 | 1189.8 | 0.6888 | 7.329
2024-12-09 | 15:14 | Data | 0 | 26.958 | 23.575 | 240.546 | 7.63 | 224.59 | 2084.24 | 26.07 | 41.033 | 6.27 | 1.493 | 5.836 | 8911.05 | 3.119 | 98 | 79.6 | 1355 | 20.47 | 5792.2 | 3552.6 | 3477.5 | 5064.9 | 1189.8 | 0.68764 | 7.326
2024-12-09 | 15:14 | Data | 0 | 26.742 | 23.629 | 240.773 | 7.63 | 224.635 | 2089.66 | 26.06 | 40.943 | 6.27 | 1.503 | 5.856 | 8924.61 | 3.207 | 98 | 79.6 | 1358 | 20.52 | 5801 | 3545.6 | 3498.7 | 5070.9 | 1189.8 | 0.68497 | 7.359
2024-12-09 | 15:14 | Data | 0 | 26.965 | 23.744 | 240.592 | 7.63 | 224.771 | 2090.56 | 26.07 | 41.213 | 6.27 | 1.502 | 5.853 | 8924.61 | 3.22 | 98 | 79.6 | 1358 | 20.56 | 5801 | 3546.5 | 3507.9 | 5080.7 | 1189.8 | 0.6852 | 7.355
2024-12-09 | 15:14 | Data | 0 | 27.424 | 24.224 | 241.134 | 7.63 | 225.087 | 2089.66 | 26.06 | 40.943 | 6.27 | 1.5 | 5.837 | 8929.14 | 3.173 | 98 | 79.6 | 1358 | 20.52 | 5803.9 | 3544.6 | 3530.9 | 5094.5 | 1189.8 | 0.68176 | 7.337
2024-12-09 | 15:14 | Data | 0 | 26.269 | 23.177 | 240.365 | 7.63 | 224.319 | 2089.66 | 26.07 | 41.033 | 6.26 | 1.495 | 5.85 | 8911.05 | 3.018 | 98 | 79.6 | 1359 | 20.52 | 5792.2 | 3549 | 3557.4 | 5118 | 1189.8 | 0.67917 | 7.345
2024-12-09 | 15:14 | Data | 0 | 26.472 | 23.11 | 240.275 | 7.63 | 224.319 | 2092.37 | 26.07 | 40.943 | 6.27 | 1.49 | 5.857 | 8920.09 | 3.166 | 98 | 79.7 | 1360 | 20.47 | 5798.1 | 3550.7 | 3503.2 | 5070.1 | 1189.8 | 0.68439 | 7.346
2024-12-09 | 15:14 | Data | 0 | 26.641 | 23.711 | 240.546 | 7.63 | 224.454 | 2092.37 | 26.07 | 40.943 | 6.27 | 1.501 | 5.823 | 8947.23 | 2.998 | 98 | 79.5 | 1360 | 20.47 | 5815.7 | 3540 | 3508.4 | 5077.6 | 1189.8 | 0.68351 | 7.324
2024-12-09 | 15:14 | Data | 0 | 26.519 | 23.359 | 240.637 | 7.64 | 224.59 | 2093.28 | 26.07 | 41.123 | 6.26 | 1.5 | 5.846 | 8938.18 | 2.849 | 98 | 79.6 | 1361 | 20.43 | 5809.8 | 3547.8 | 3457.4 | 5044.6 | 1189.8 | 0.68873 | 7.347
2024-12-09 | 15:14 | Data | 0 | 26.269 | 23.076 | 240.411 | 7.63 | 224.409 | 2091.47 | 26.06 | 41.033 | 6.27 | 1.509 | 5.87 | 9340.66 | 3.092 | 98 | 79.6 | 1360 | 20.52 | 6071.4 | 3543.7 | 3469.5 | 5056.5 | 1189.8 | 0.68585 | 7.376
2024-12-09 | 15:14 | Data | 0 | 26.728 | 23.629 | 240.727 | 7.63 | 224.635 | 2092.37 | 26.06 | 41.033 | 6.27 | 1.496 | 5.845 | 9299.96 | 3.214 | 98 | 79.6 | 1360 | 20.52 | 6045 | 3554.4 | 3456.4 | 5037.2 | 1189.8 | 0.69125 | 7.342
2024-12-09 | 15:15 | Data | 0 | 27.052 | 23.771 | 240.818 | 7.64 | 224.771 | 2095.08 | 26.06 | 40.943 | 6.26 | 1.49 | 5.844 | 8996.97 | 3.2 | 98 | 79.7 | 1361 | 20.43 | 5848 | 3530.5 | 3450.8 | 5035 | 1189.8 | 0.68825 | 7.332
2024-12-09 | 15:15 | Data | 0 | 26.789 | 23.697 | 240.592 | 7.64 | 224.59 | 2094.18 | 26.06 | 40.943 | 6.26 | 1.498 | 5.861 | 8983.4 | 3.085 | 98 | 79.6 | 1361 | 20.52 | 5839.2 | 3569.7 | 3468.5 | 5053.6 | 1189.9 | 0.68981 | 7.358
2024-12-09 | 15:15 | Data | 0 | 27.451 | 24.426 | 241.225 | 7.63 | 224.997 | 2095.08 | 26.07 | 40.943 | 6.27 | 1.503 | 5.867 | 9019.58 | 3.004 | 98.1 | 79.6 | 1362 | 20.43 | 5862.7 | 3546.7 | 3475.9 | 5059.9 | 1189.9 | 0.68614 | 7.37
2024-12-09 | 15:15 | Data | 0 | 27.755 | 24.48 | 241.18 | 7.64 | 225.042 | 2094.18 | 26.08 | 40.943 | 6.27 | 1.5 | 5.872 | 9399.45 | 3.085 | 98.1 | 79.6 | 1362 | 20.43 | 6109.6 | 3538.1 | 3494 | 5070 | 1189.9 | 0.68286 | 7.372
2024-12-09 | 15:15 | Data | 0 | 27.194 | 24.089 | 240.908 | 7.64 | 224.861 | 2095.08 | 26.07 | 40.943 | 6.27 | 1.502 | 5.86 | 8965.31 | 3.22 | 98 | 79.6 | 1361 | 20.47 | 5827.5 | 3547.1 | 3490.4 | 5069.8 | 1189.9 | 0.68522 | 7.363
2024-12-09 | 15:15 | Data | 0 | 26.85 | 23.832 | 240.637 | 7.63 | 224.59 | 2095.08 | 26.06 | 41.033 | 6.27 | 1.504 | 5.865 | 8992.45 | 3.119 | 98 | 79.6 | 1362 | 20.52 | 5845.1 | 3536.5 | 3494.3 | 5063.8 | 1189.9 | 0.68451 | 7.369
2024-12-09 | 15:15 | Data | 0 | 27.059 | 23.629 | 240.501 | 7.64 | 224.545 | 2095.08 | 26.06 | 41.033 | 6.27 | 1.495 | 5.831 | 9444.67 | 3.025 | 98 | 79.6 | 1362 | 20.52 | 6139 | 3556.6 | 3491.4 | 5074 | 1189.9 | 0.68619 | 7.329
2024-12-09 | 15:15 | Data | 0 | 26.654 | 23.535 | 240.546 | 7.64 | 224.499 | 2095.08 | 26.06 | 41.033 | 6.27 | 1.504 | 5.825 | 8992.45 | 3.16 | 98 | 79.5 | 1362 | 20.47 | 5845.1 | 3542.1 | 3511.2 | 5081.4 | 1189.9 | 0.68431 | 7.329
2024-12-09 | 15:15 | Data | 0 | 26.735 | 23.738 | 240.727 | 7.64 | 224.725 | 2090.56 | 26.06 | 41.033 | 6.27 | 1.495 | 5.857 | 8983.4 | 2.991 | 98 | 79.7 | 1360 | 20.52 | 5839.2 | 3554.6 | 3478.8 | 5065.7 | 1189.9 | 0.68702 | 7.351
2024-12-09 | 15:15 | Data | 0 | 27.451 | 23.913 | 240.999 | 7.64 | 225.132 | 2092.37 | 26.06 | 41.123 | 6.27 | 1.498 | 5.848 | 9033.15 | 3.112 | 98 | 79.6 | 1361 | 20.47 | 5871.5 | 3559.9 | 3472.4 | 5066 | 1189.9 | 0.68892 | 7.348
2024-12-09 | 15:15 | Data | 0 | 27.424 | 24.257 | 241.225 | 7.64 | 225.087 | 2090.56 | 26.06 | 41.033 | 6.27 | 1.502 | 5.843 | 9006.01 | 3.106 | 98 | 79.6 | 1358 | 20.52 | 5853.9 | 3539.7 | 3453.8 | 5037 | 1189.9 | 0.68869 | 7.344
2024-12-09 | 15:15 | Data | 0 | 26.971 | 24.224 | 240.863 | 7.63 | 224.861 | 2088.76 | 26.07 | 41.033 | 6.27 | 1.491 | 5.877 | 8996.97 | 2.917 | 98 | 79.8 | 1358 | 20.52 | 5848 | 3549.1 | 3480.2 | 5063.5 | 1189.9 | 0.68679 | 7.369
2024-12-09 | 15:15 | Data | 0 | 26.728 | 23.569 | 240.637 | 7.64 | 224.545 | 2085.14 | 26.07 | 41.033 | 6.26 | 1.493 | 5.876 | 8992.45 | 3.349 | 98 | 79.7 | 1355 | 20.47 | 5845.1 | 3535 | 3462.1 | 5039.6 | 1189.9 | 0.68697 | 7.368
2024-12-09 | 15:15 | Data | 0 | 26.728 | 23.508 | 240.592 | 7.63 | 224.59 | 2089.66 | 26.06 | 41.033 | 6.27 | 1.5 | 5.864 | 9006.01 | 3.018 | 98 | 79.6 | 1358 | 20.47 | 5853.9 | 3550.9 | 3462.4 | 5054.2 | 1189.9 | 0.68918 | 7.363
2024-12-09 | 15:15 | Data | 0 | 26.269 | 23.272 | 240.32 | 7.63 | 224.364 | 2090.56 | 26.06 | 40.401 | 6.27 | 1.498 | 5.883 | 9024.1 | 3.112 | 98.1 | 79.7 | 1359 | 20.29 | 5865.7 | 3535.6 | 3461.8 | 5042.6 | 1189.9 | 0.68696 | 7.38
2024-12-09 | 15:15 | Data | 0 | 26.013 | 22.988 | 240.094 | 7.64 | 224.093 | 2089.66 | 26.06 | 40.943 | 6.27 | 1.502 | 5.83 | 9015.06 | 3.052 | 98 | 79.5 | 1358 | 20.52 | 5859.8 | 3570.6 | 3492.3 | 5088.2 | 1189.9 | 0.68692 | 7.333
2024-12-09 | 15:15 | Data | 0 | 27.194 | 23.92 | 241.044 | 7.63 | 224.997 | 2088.76 | 26.06 | 40.943 | 6.27 | 1.5 | 5.838 | 9010.54 | 3.322 | 98 | 79.6 | 1359 | 20.52 | 5856.8 | 3549.5 | 3452 | 5043.2 | 1189.9 | 0.6887 | 7.337
2024-12-09 | 15:16 | Data | 0 | 26.742 | 23.738 | 240.818 | 7.64 | 224.771 | 2090.56 | 26.06 | 41.033 | 6.28 | 1.505 | 5.854 | 9015.06 | 3.2 | 98 | 79.5 | 1358 | 20.47 | 5859.8 | 3552.3 | 3481.1 | 5067.9 | 1189.9 | 0.68662 | 7.359
2024-12-09 | 15:16 | Data | 0 | 26.728 | 23.508 | 240.637 | 7.63 | 224.545 | 2086.95 | 26.06 | 40.943 | 6.27 | 1.502 | 5.895 | 9006.01 | 3.214 | 98 | 79.7 | 1357 | 20.52 | 5853.9 | 3552.6 | 3496.6 | 5080.9 | 1189.9 | 0.68558 | 7.398
2024-12-09 | 15:16 | Data | 0 | 26.776 | 23.292 | 240.727 | 7.64 | 224.725 | 2087.85 | 26.07 | 41.033 | 6.28 | 1.497 | 5.91 | 9006.01 | 3.22 | 98 | 79.8 | 1357 | 20.52 | 5853.9 | 3532 | 3477.8 | 5051.3 | 1189.9 | 0.68402 | 7.408
2024-12-09 | 15:16 | Data | 0 | 26.978 | 23.751 | 240.954 | 7.64 | 224.771 | 2086.95 | 26.07 | 40.943 | 6.28 | 1.508 | 5.866 | 9024.1 | 3.085 | 98 | 79.6 | 1355 | 20.52 | 5865.7 | 3547.3 | 3514.3 | 5087 | 1189.9 | 0.68313 | 7.373
2024-12-09 | 15:16 | Data | 0 | 26.715 | 23.501 | 240.456 | 7.64 | 224.364 | 2085.14 | 26.06 | 41.033 | 6.27 | 1.502 | 5.853 | 8965.31 | 3.025 | 98 | 79.6 | 1355 | 20.56 | 5827.5 | 3570.8 | 3535 | 5117.2 | 1189.9 | 0.68308 | 7.356
2024-12-09 | 15:16 | Data | 0 | 26.472 | 23.285 | 240.592 | 7.64 | 224.454 | 2081.53 | 26.06 | 40.943 | 6.28 | 1.5 | 5.855 | 8983.4 | 3.207 | 98 | 79.6 | 1354 | 20.47 | 5839.2 | 3549.2 | 3518.1 | 5088.2 | 1189.9 | 0.68355 | 7.355
2024-12-09 | 15:16 | Data | 0 | 27.329 | 23.906 | 240.727 | 7.63 | 224.771 | 2086.95 | 26.07 | 41.033 | 6.27 | 1.493 | 5.888 | 8974.36 | 3.214 | 98 | 79.8 | 1357 | 20.52 | 5833.3 | 3532.9 | 3516.5 | 5076.9 | 1189.9 | 0.68109 | 7.382
2024-12-09 | 15:16 | Data | 0 | 26.735 | 23.738 | 240.773 | 7.63 | 224.816 | 2086.95 | 26.06 | 41.033 | 6.27 | 1.5 | 5.873 | 8965.31 | 2.991 | 98 | 79.7 | 1357 | 20.56 | 5827.5 | 3538.4 | 3515.6 | 5078.9 | 1189.9 | 0.68216 | 7.373
2024-12-09 | 15:16 | Data | 0 | 27.127 | 24.183 | 241.044 | 7.63 | 224.725 | 2087.85 | 26.07 | 40.943 | 6.26 | 1.496 | 5.89 | 8969.84 | 3.133 | 98 | 79.7 | 1357 | 20.52 | 5830.4 | 3538.3 | 3505.2 | 5071.4 | 1189.9 | 0.683 | 7.386
2024-12-09 | 15:16 | Data | 0 | 27.525 | 24.325 | 241.225 | 7.64 | 225.087 | 2087.85 | 26.06 | 41.123 | 6.27 | 1.501 | 5.877 | 8965.31 | 3.139 | 98 | 79.7 | 1357 | 20.52 | 5827.5 | 3548.5 | 3521 | 5092.2 | 1189.9 | 0.68209 | 7.379
2024-12-09 | 15:16 | Data | 0 | 27.633 | 24.203 | 241.225 | 7.63 | 225.042 | 2089.66 | 26.07 | 40.943 | 6.27 | 1.5 | 5.85 | 8965.31 | 3.247 | 98 | 79.6 | 1358 | 20.47 | 5827.5 | 3531.7 | 3473.6 | 5044.5 | 1189.9 | 0.68604 | 7.352
2024-12-09 | 15:16 | Data | 0 | 26.971 | 24.028 | 241.044 | 7.64 | 224.951 | 2092.37 | 26.07 | 41.033 | 6.27 | 1.5 | 5.854 | 8960.79 | 3.22 | 98 | 79.6 | 1360 | 20.47 | 5824.5 | 3539.8 | 3489.3 | 5066.2 | 1189.9 | 0.68529 | 7.354
2024-12-09 | 15:16 | Data | 0 | 26.965 | 23.859 | 240.908 | 7.63 | 224.816 | 2092.37 | 26.03 | 40.943 | 6.27 | 1.491 | 5.876 | 8960.79 | 3.2 | 98 | 79.8 | 1359 | 20.47 | 5824.5 | 3546.8 | 3473.2 | 5056 | 1189.9 | 0.68686 | 7.363
2024-12-09 | 15:16 | Data | 0 | 27.869 | 24.966 | 241.722 | 7.64 | 225.403 | 2093.28 | 26.06 | 40.943 | 6.27 | 1.509 | 5.897 | 8947.23 | 3.079 | 98 | 79.6 | 1362 | 20.52 | 5815.7 | 3539.9 | 3495.4 | 5067.4 | 1189.9 | 0.68412 | 7.408
2024-12-09 | 15:16 | Data | 0 | 27.91 | 24.487 | 241.632 | 7.64 | 225.494 | 1996.57 | 26.06 | 40.852 | 6.27 | 1.508 | 5.878 | 8951.75 | 3.079 | 97.9 | 79.6 | 1298 | 20.47 | 5818.6 | 3522.8 | 3503.8 | 5063.5 | 1190 | 0.68103 | 7.386
2024-12-09 | 15:16 | Data | 0 | 28.396 | 25.351 | 242.084 | 7.64 | 225.765 | 2094.18 | 26.06 | 40.943 | 6.27 | 1.5 | 5.872 | 8956.27 | 2.998 | 98 | 79.7 | 1363 | 20.52 | 5821.6 | 3544.3 | 3510.2 | 5076.8 | 1190 | 0.68413 | 7.37
2024-12-09 | 15:16 | Data | 0 | 28.484 | 25.257 | 241.813 | 7.63 | 225.81 | 2095.08 | 26.07 | 41.033 | 6.27 | 1.5 | 5.879 | 8960.79 | 3.119 | 98 | 79.7 | 1361 | 20.52 | 5824.5 | 3536.3 | 3493.7 | 5063.7 | 1190 | 0.68234 | 7.379
2024-12-09 | 15:16 | Data | 0 | 28.187 | 25.236 | 242.084 | 7.63 | 225.81 | 2095.99 | 26.07 | 40.852 | 6.27 | 1.513 | 5.885 | 8951.75 | 3.025 | 98.1 | 79.5 | 1362 | 20.47 | 5818.6 | 3553.3 | 3496.8 | 5079.1 | 1190 | 0.68596 | 7.399
2024-12-09 | 15:17 | Data | 0 | 29.139 | 26.04 | 242.401 | 7.63 | 225.991 | 2094.18 | 26.06 | 41.033 | 6.28 | 1.5 | 5.864 | 8933.66 | 3.011 | 98 | 79.6 | 1361 | 20.47 | 5806.9 | 3530.4 | 3486.7 | 5055.1 | 1190 | 0.68346 | 7.363
2024-12-09 | 15:17 | Data | 0 | 28.835 | 25.614 | 242.175 | 7.64 | 226.081 | 2095.08 | 26.06 | 41.123 | 6.27 | 1.5 | 5.864 | 8924.61 | 3.045 | 98 | 79.6 | 1362 | 20.47 | 5801 | 3534.3 | 3487.9 | 5058 | 1190 | 0.68406 | 7.361
2024-12-09 | 15:17 | Data | 0 | 28.922 | 25.803 | 242.22 | 7.64 | 226.081 | 2091.47 | 26.07 | 41.033 | 6.27 | 1.503 | 5.881 | 8951.75 | 3.045 | 98 | 79.6 | 1359 | 20.47 | 5818.6 | 3533.9 | 3470.9 | 5045.7 | 1190 | 0.68529 | 7.385
2024-12-09 | 15:17 | Data | 0 | 28.355 | 25.162 | 242.084 | 7.64 | 225.9 | 2089.66 | 26.06 | 40.943 | 6.27 | 1.507 | 5.886 | 8902 | 3.112 | 98 | 79.6 | 1359 | 20.56 | 5786.3 | 3551.1 | 3482.4 | 5064.1 | 1190 | 0.68593 | 7.395
2024-12-09 | 15:17 | Data | 0 | 27.674 | 24.656 | 241.451 | 7.64 | 225.358 | 2089.66 | 26.03 | 40.491 | 6.27 | 1.5 | 5.87 | 8911.05 | 3.011 | 98.1 | 79.6 | 1358 | 20.29 | 5792.2 | 3538.8 | 3485.2 | 5058.9 | 1190 | 0.68517 | 7.371
2024-12-09 | 15:17 | Data | 0 | 27.14 | 23.744 | 240.954 | 7.63 | 224.771 | 2089.66 | 26.03 | 41.033 | 6.27 | 1.496 | 5.866 | 8911.05 | 3.072 | 98 | 79.7 | 1358 | 20.52 | 5792.2 | 3552.3 | 3479.3 | 5062.3 | 1190 | 0.68738 | 7.362
2024-12-09 | 15:17 | Data | 0 | 27.856 | 24.271 | 241.225 | 7.63 | 225.268 | 2092.37 | 26.06 | 40.943 | 6.27 | 1.493 | 5.855 | 8897.48 | 3.214 | 98 | 79.7 | 1361 | 20.47 | 5783.4 | 3544.8 | 3474.8 | 5054.3 | 1190 | 0.68594 | 7.348
2024-12-09 | 15:17 | Data | 0 | 27.262 | 24.318 | 241.18 | 7.64 | 225.042 | 2095.08 | 26.05 | 41.033 | 6.27 | 1.5 | 5.864 | 8951.75 | 3.018 | 98 | 79.6 | 1361 | 20.47 | 5818.6 | 3549.6 | 3491.9 | 5071.1 | 1190 | 0.68563 | 7.362
2024-12-09 | 15:17 | Data | 0 | 27.424 | 24.487 | 241.225 | 7.64 | 225.177 | 2095.08 | 26.06 | 41.033 | 6.28 | 1.508 | 5.857 | 8951.75 | 3.227 | 98 | 79.5 | 1361 | 20.47 | 5818.6 | 3544.9 | 3500.9 | 5072.1 | 1190 | 0.68505 | 7.364
2024-12-09 | 15:17 | Data | 0 | 27.728 | 24.237 | 241.406 | 7.64 | 225.313 | 2095.99 | 26.06 | 41.033 | 6.27 | 1.502 | 5.877 | 8951.75 | 3.072 | 98 | 79.7 | 1362 | 20.52 | 5818.6 | 3526.3 | 3514.4 | 5060.6 | 1190 | 0.68045 | 7.38
2024-12-09 | 15:17 | Data | 0 | 28.423 | 25.236 | 241.722 | 7.63 | 225.629 | 2095.99 | 26.06 | 41.033 | 6.27 | 1.507 | 5.862 | 8933.66 | 3.22 | 98 | 79.5 | 1362 | 20.52 | 5806.9 | 3564.9 | 3509.8 | 5093.8 | 1190 | 0.68481 | 7.37
2024-12-09 | 15:17 | Data | 0 | 28.342 | 25.29 | 241.858 | 7.64 | 225.675 | 2095.08 | 26.07 | 40.943 | 6.27 | 1.5 | 5.863 | 8938.18 | 3.22 | 98 | 79.6 | 1362 | 20.47 | 5809.8 | 3535.7 | 3524.9 | 5082.2 | 1190 | 0.68154 | 7.364
2024-12-09 | 15:17 | Data | 0 | 28.72 | 25.392 | 241.994 | 7.64 | 225.855 | 2092.37 | 26.06 | 40.943 | 6.27 | 4.992 | 5.87 | 8920.09 | 3.126 | 98 | 53.6 | 1360 | 20.47 | 5798.1 | 3538.7 | 3501.1 | 5072 | 1190 | 0.6827 | 10.951
2024-12-09 | 15:17 | Data | 0 | 28.794 | 25.641 | 242.31 | 7.63 | 225.9 | 2092.37 | 26.06 | 41.033 | 6.27 | 1.505 | 5.867 | 8924.61 | 3.099 | 98 | 79.6 | 1360 | 20.47 | 5801 | 3547.8 | 3500.7 | 5069.2 | 1190 | 0.6862 | 7.373
2024-12-09 | 15:17 | Data | 0 | 28.922 | 25.81 | 242.175 | 7.64 | 225.855 | 2092.37 | 26.05 | 40.852 | 6.27 | 1.51 | 5.885 | 8920.09 | 3.004 | 98 | 79.6 | 1361 | 20.47 | 5798.1 | 3536.2 | 3445.5 | 5023.6 | 1190 | 0.69034 | 7.396
2024-12-09 | 15:17 | Data | 0 | 28.517 | 25.493 | 241.813 | 7.64 | 225.72 | 2092.37 | 26.07 | 41.033 | 6.27 | 1.527 | 5.892 | 8933.66 | 3.376 | 98 | 79.4 | 1360 | 20.52 | 5806.9 | 3546.8 | 3453.1 | 5041.1 | 1190 | 0.68937 | 7.42
2024-12-09 | 15:17 | Data | 0 | 28.808 | 25.466 | 242.13 | 7.64 | 225.946 | 2092.37 | 26.05 | 41.123 | 6.27 | 1.528 | 5.905 | 8929.14 | 3.133 | 98 | 79.4 | 1360 | 20.56 | 5803.9 | 3550.2 | 3453.5 | 5037.1 | 1190 | 0.69065 | 7.433
2024-12-09 | 15:17 | Data | 0 | 28.544 | 25.351 | 241.813 | 7.63 | 225.629 | 2091.47 | 26.03 | 40.762 | 6.27 | 1.515 | 5.881 | 8933.66 | 3.092 | 98.1 | 79.5 | 1360 | 20.38 | 5806.9 | 3518.7 | 3489.1 | 5048 | 1190 | 0.68181 | 7.396
2024-12-09 | 15:18 | Data | 0 | 28.112 | 24.993 | 241.451 | 7.64 | 225.358 | 2084.24 | 26.05 | 42.748 | 6.27 | 1.512 | 5.886 | 8911.05 | 3.011 | 97.9 | 79.6 | 1355 | 21.42 | 5792.2 | 3550.1 | 3518.6 | 5078.4 | 1190 | 0.68447 | 7.399
2024-12-09 | 15:18 | Data | 0 | 26.965 | 24.082 | 241.044 | 7.64 | 224.816 | 2094.18 | 26.03 | 40.672 | 6.27 | 1.515 | 5.868 | 8965.31 | 3.052 | 98.1 | 79.5 | 1362 | 20.38 | 5827.5 | 3552.1 | 3551.5 | 5125.9 | 1190 | 0.68172 | 7.384
2024-12-09 | 15:18 | Data | 0 | 27.309 | 24.635 | 241.044 | 7.63 | 224.997 | 2092.37 | 26.05 | 41.845 | 6.27 | 1.518 | 5.838 | 8978.88 | 3.092 | 98 | 79.4 | 1361 | 20.88 | 5836.3 | 3522.8 | 3568.4 | 5104.2 | 1190 | 0.67561 | 7.355
2024-12-09 | 15:18 | Data | 0 | 28.342 | 24.75 | 241.587 | 7.64 | 225.403 | 2092.37 | 26.05 | 41.936 | 6.27 | 1.518 | 5.863 | 8992.45 | 3.119 | 98 | 79.4 | 1360 | 20.97 | 5845.1 | 3535 | 3537.9 | 5090.6 | 1190 | 0.68086 | 7.38
2024-12-09 | 15:18 | Data | 0 | 28.058 | 25.034 | 241.632 | 7.63 | 225.449 | 2091.47 | 26.06 | 41.845 | 6.28 | 1.51 | 5.838 | 8965.31 | 3.187 | 98 | 79.4 | 1360 | 20.92 | 5827.5 | 3552.2 | 3529.9 | 5100.5 | 1190 | 0.68113 | 7.35
2024-12-09 | 15:18 | Data | 0 | 27.309 | 24.554 | 241.089 | 7.64 | 224.951 | 2095.08 | 26.06 | 41.936 | 6.28 | 1.518 | 5.831 | 8956.27 | 3.025 | 98 | 79.3 | 1362 | 20.97 | 5821.6 | 3548.1 | 3504.5 | 5079.2 | 1190 | 0.68423 | 7.349
2024-12-09 | 15:18 | Data | 0 | 26.978 | 24.305 | 241.089 | 7.64 | 224.861 | 2105.03 | 26.06 | 40.762 | 6.27 | 1.519 | 5.859 | 8960.79 | 2.944 | 98.1 | 79.4 | 1368 | 20.38 | 5824.5 | 3544.3 | 3456.6 | 5040.3 | 1190 | 0.6889 | 7.379
2024-12-09 | 15:18 | Data | 0 | 27.397 | 24.784 | 241.134 | 7.64 | 224.997 | 2104.12 | 26.06 | 40.672 | 6.27 | 1.512 | 5.859 | 8933.66 | 3.112 | 98.1 | 79.5 | 1367 | 20.25 | 5806.9 | 3549 | 3456.7 | 5034.4 | 1190 | 0.68781 | 7.371
2024-12-09 | 15:18 | Data | 0 | 26.965 | 24.467 | 240.908 | 7.63 | 224.816 | 2103.22 | 26.06 | 40.672 | 6.28 | 1.511 | 5.866 | 8947.23 | 3.018 | 98.1 | 79.5 | 1367 | 20.34 | 5815.7 | 3542.3 | 3458.8 | 5046 | 1190.1 | 0.68752 | 7.378
2024-12-09 | 15:18 | Data | 0 | 27.221 | 24.028 | 241.315 | 7.64 | 225.087 | 2101.41 | 26.06 | 40.762 | 6.27 | 1.514 | 5.851 | 8938.18 | 2.998 | 98.1 | 79.4 | 1365 | 20.38 | 5809.8 | 3532.2 | 3474.5 | 5047.4 | 1190.1 | 0.6854 | 7.363
2024-12-09 | 15:18 | Data | 0 | 28.342 | 24.959 | 241.722 | 7.64 | 225.449 | 2100.51 | 26.06 | 40.672 | 6.27 | 1.515 | 5.871 | 8933.66 | 3.112 | 98.1 | 79.5 | 1365 | 20.34 | 5806.9 | 3541.1 | 3505.7 | 5074.3 | 1190.1 | 0.68429 | 7.386
2024-12-09 | 15:18 | Data | 0 | 28.342 | 25.169 | 241.768 | 7.64 | 225.675 | 2100.51 | 26.06 | 40.762 | 6.27 | 1.514 | 5.838 | 8938.18 | 3.126 | 98.1 | 79.4 | 1365 | 20.38 | 5809.8 | 3543.1 | 3509 | 5081.8 | 1190.1 | 0.68275 | 7.352
2024-12-09 | 15:18 | Data | 0 | 28.112 | 25.061 | 241.722 | 7.64 | 225.403 | 2101.41 | 26.07 | 40.581 | 6.27 | 1.523 | 5.836 | 8933.66 | 3.106 | 98.1 | 79.3 | 1367 | 20.34 | 5806.9 | 3542.7 | 3531.3 | 5091.7 | 1190.1 | 0.68121 | 7.357
2024-12-09 | 15:18 | Data | 0 | 28.099 | 25.432 | 241.722 | 7.63 | 225.494 | 2099.6 | 26.07 | 40.491 | 6.28 | 1.517 | 5.866 | 8938.18 | 3.207 | 98.1 | 79.5 | 1365 | 20.2 | 5809.8 | 3545.1 | 3543.1 | 5105.9 | 1190.1 | 0.68032 | 7.383
2024-12-09 | 15:18 | Data | 0 | 28.106 | 25.061 | 241.587 | 7.63 | 225.358 | 2096.89 | 26.07 | 40.762 | 6.28 | 1.509 | 5.876 | 8947.23 | 3.112 | 98.1 | 79.6 | 1363 | 20.34 | 5815.7 | 3520 | 3496.8 | 5052 | 1190.1 | 0.68253 | 7.386
2024-12-09 | 15:18 | Data | 0 | 27.376 | 24.541 | 241.27 | 7.64 | 225.132 | 2109.54 | 26.06 | 40.762 | 6.28 | 1.518 | 5.878 | 8947.23 | 3.092 | 98.1 | 79.5 | 1371 | 20.43 | 5815.7 | 3540.1 | 3497.1 | 5065.7 | 1190.1 | 0.68391 | 7.397
2024-12-09 | 15:19 | Data | 0 | 27.991 | 24.878 | 241.406 | 7.64 | 225.042 | 2102.31 | 26.06 | 40.852 | 6.28 | 1.514 | 5.871 | 8933.66 | 3.025 | 98.1 | 79.5 | 1366 | 20.38 | 5806.9 | 3543.2 | 3486 | 5059.8 | 1190.1 | 0.68632 | 7.385
2024-12-09 | 15:19 | Data | 0 | 27.424 | 24.109 | 240.954 | 7.63 | 224.906 | 2102.31 | 26.06 | 40.672 | 6.27 | 1.518 | 5.866 | 8938.18 | 2.998 | 98.1 | 79.4 | 1368 | 20.38 | 5809.8 | 3559 | 3461.9 | 5056.7 | 1190.1 | 0.68996 | 7.385
2024-12-09 | 15:19 | Data | 0 | 27.768 | 24.48 | 241.225 | 7.64 | 225.177 | 2101.41 | 26.05 | 40.672 | 6.27 | 1.512 | 5.867 | 8956.27 | 3.038 | 98.1 | 79.5 | 1366 | 20.38 | 5821.6 | 3520.2 | 3463.4 | 5031.2 | 1190.1 | 0.68528 | 7.38
2024-12-09 | 15:19 | Data | 0 | 28.342 | 25.02 | 241.406 | 7.64 | 225.358 | 2104.12 | 26.05 | 40.762 | 6.28 | 1.514 | 5.876 | 8938.18 | 3.065 | 98.1 | 79.5 | 1367 | 20.34 | 5809.8 | 3534.7 | 3470.8 | 5048.3 | 1190.1 | 0.68474 | 7.386
2024-12-09 | 15:19 | Data | 0 | 28.558 | 25.351 | 241.768 | 7.64 | 225.629 | 2106.83 | 26.06 | 40.943 | 6.27 | 1.51 | 5.851 | 8924.61 | 3.193 | 98.1 | 79.5 | 1369 | 20.47 | 5801 | 3539.5 | 3504.7 | 5072.8 | 1190.1 | 0.68513 | 7.361
2024-12-09 | 15:19 | Data | 0 | 28.335 | 25.115 | 241.722 | 7.64 | 225.494 | 2105.93 | 26.06 | 40.672 | 6.28 | 1.512 | 5.845 | 8924.61 | 3.22 | 98.1 | 79.4 | 1369 | 20.38 | 5801 | 3527.9 | 3493.7 | 5061.4 | 1190.1 | 0.6849 | 7.358
2024-12-09 | 15:19 | Data | 0 | 26.978 | 24.332 | 240.954 | 7.63 | 224.906 | 2105.93 | 26.07 | 40.852 | 6.28 | 1.515 | 5.868 | 8920.09 | 3.004 | 98.1 | 79.5 | 1369 | 20.43 | 5798.1 | 3554.3 | 3510.9 | 5090.3 | 1190.1 | 0.68348 | 7.384
2024-12-09 | 15:19 | Data | 0 | 26.83 | 23.94 | 240.954 | 7.64 | 224.816 | 2105.93 | 26.06 | 40.762 | 6.28 | 1.516 | 5.875 | 8897.48 | 2.971 | 98.1 | 79.5 | 1369 | 20.38 | 5783.4 | 3538.4 | 3529.6 | 5088.4 | 1190.1 | 0.68107 | 7.39
2024-12-09 | 15:19 | Data | 0 | 27.201 | 24.237 | 240.999 | 7.64 | 224.906 | 2105.93 | 26.07 | 40.491 | 6.28 | 1.518 | 5.856 | 8951.75 | 2.957 | 98.1 | 79.4 | 1368 | 20.29 | 5818.6 | 3530.6 | 3514.5 | 5077.8 | 1190.1 | 0.68212 | 7.373
2024-12-09 | 15:19 | Data | 0 | 26.971 | 23.954 | 240.954 | 7.64 | 224.771 | 2103.22 | 26.07 | 40.491 | 6.28 | 1.507 | 5.861 | 8956.27 | 3.085 | 98.1 | 79.5 | 1367 | 20.16 | 5821.6 | 3554.6 | 3497.3 | 5073.7 | 1190.1 | 0.68694 | 7.368
2024-12-09 | 15:19 | Data | 0 | 27.316 | 24.413 | 240.908 | 7.63 | 224.861 | 2103.22 | 26.06 | 40.762 | 6.28 | 1.506 | 5.842 | 8965.31 | 3.112 | 98.1 | 79.5 | 1367 | 20.43 | 5827.5 | 3536.2 | 3482 | 5055.7 | 1190.1 | 0.68474 | 7.348
2024-12-09 | 15:19 | Data | 0 | 27.775 | 24.716 | 241.27 | 7.64 | 224.951 | 2098.7 | 26.07 | 40.762 | 6.27 | 1.522 | 5.862 | 8956.27 | 3.126 | 98 | 79.4 | 1364 | 20.43 | 5821.6 | 3551.6 | 3482.2 | 5064.2 | 1190.1 | 0.68664 | 7.385
2024-12-09 | 15:19 | Data | 0 | 27.775 | 24.575 | 241.27 | 7.64 | 225.268 | 2104.12 | 26.06 | 40.762 | 6.27 | 1.52 | 5.842 | 8938.18 | 3.173 | 98.1 | 79.4 | 1368 | 20.34 | 5809.8 | 3554.9 | 3459.1 | 5047.1 | 1190.1 | 0.69012 | 7.363
2024-12-09 | 15:19 | Data | 0 | 27.795 | 24.44 | 241.361 | 7.63 | 225.223 | 2104.12 | 26.06 | 40.762 | 6.27 | 1.515 | 5.858 | 8920.09 | 3.112 | 98.1 | 79.5 | 1367 | 20.34 | 5798.1 | 3521.6 | 3500.1 | 5057.7 | 1190.1 | 0.68301 | 7.373
2024-12-09 | 15:19 | Data | 0 | 28.187 | 25.176 | 241.677 | 7.63 | 225.358 | 2106.83 | 26.07 | 40.581 | 6.28 | 1.523 | 5.871 | 8938.18 | 3.301 | 98.1 | 79.4 | 1369 | 20.29 | 5809.8 | 3532.7 | 3476.9 | 5056.2 | 1190.1 | 0.68596 | 7.394
2024-12-09 | 15:19 | Data | 0 | 28.396 | 25.149 | 241.768 | 7.64 | 225.675 | 2105.93 | 26.07 | 40.762 | 6.28 | 1.522 | 5.867 | 8920.09 | 2.964 | 98.1 | 79.4 | 1369 | 20.38 | 5798.1 | 3538.2 | 3469 | 5045.9 | 1190.1 | 0.68716 | 7.39
2024-12-09 | 15:19 | Data | 0 | 28.369 | 25.122 | 241.632 | 7.64 | 225.494 | 2110.45 | 26.06 | 40.762 | 6.27 | 1.521 | 5.883 | 8938.18 | 3.22 | 98.1 | 79.5 | 1372 | 20.38 | 5809.8 | 3528.1 | 3496.2 | 5064 | 1190.1 | 0.68228 | 7.405
2024-12-09 | 15:19 | Data | 0 | 27.194 | 24.284 | 241.18 | 7.64 | 224.997 | 2106.83 | 26.06 | 40.852 | 6.28 | 1.51 | 5.889 | 8951.75 | 3.106 | 98.1 | 79.6 | 1369 | 20.38 | 5818.6 | 3545.3 | 3509.8 | 5076.5 | 1190.1 | 0.68571 | 7.399
2024-12-09 | 15:20 | Data | 0 | 27.559 | 24.102 | 241.18 | 7.63 | 224.997 | 2001.99 | 26.07 | 40.762 | 6.28 | 1.515 | 5.879 | 8938.18 | 2.998 | 98 | 79.5 | 1301 | 20.34 | 5809.8 | 3529.5 | 3504.3 | 5076.8 | 1190.1 | 0.68186 | 7.395
2024-12-09 | 15:20 | Data | 0 | 28.065 | 24.797 | 241.406 | 7.63 | 225.177 | 2103.22 | 26.07 | 40.672 | 6.28 | 1.523 | 5.851 | 8951.75 | 3.308 | 98.1 | 79.3 | 1368 | 20.34 | 5818.6 | 3531.4 | 3495.2 | 5058.6 | 1190.1 | 0.68354 | 7.375
2024-12-09 | 15:20 | Data | 0 | 27.653 | 24.453 | 241.27 | 7.63 | 225.132 | 2105.93 | 26.06 | 40.762 | 6.27 | 1.515 | 5.838 | 8947.23 | 3.166 | 98.1 | 79.4 | 1369 | 20.34 | 5815.7 | 3558.6 | 3515 | 5097.4 | 1190.1 | 0.68405 | 7.355
2024-12-09 | 15:20 | Data | 0 | 27.721 | 24.662 | 241.315 | 7.64 | 225.177 | 2105.93 | 26.07 | 40.672 | 6.27 | 1.51 | 5.819 | 8956.27 | 2.903 | 98.1 | 79.4 | 1369 | 20.34 | 5821.6 | 3533.6 | 3484.5 | 5046.2 | 1190.2 | 0.68399 | 7.328
2024-12-09 | 15:20 | Data | 0 | 27.471 | 24.521 | 241.089 | 7.64 | 225.132 | 2105.03 | 26.05 | 40.491 | 6.27 | 1.516 | 5.843 | 8938.18 | 3.092 | 98.1 | 79.4 | 1369 | 20.2 | 5809.8 | 3545.7 | 3485.2 | 5070.9 | 1190.2 | 0.68365 | 7.36
2024-12-09 | 15:20 | Data | 0 | 27.478 | 24.433 | 241.089 | 7.63 | 224.906 | 2103.22 | 26.07 | 40.762 | 6.28 | 1.515 | 5.855 | 8951.75 | 3.112 | 98.1 | 79.5 | 1368 | 20.38 | 5818.6 | 3545.1 | 3463.5 | 5049.9 | 1190.2 | 0.68881 | 7.369
2024-12-09 | 15:20 | Data | 0 | 27.788 | 24.743 | 241.225 | 7.63 | 225.177 | 2104.12 | 26.05 | 40.762 | 6.28 | 1.505 | 5.88 | 8965.31 | 3.058 | 98.1 | 79.6 | 1367 | 20.38 | 5827.5 | 3533.1 | 3462.7 | 5040.4 | 1190.2 | 0.68672 | 7.385
2024-12-09 | 15:20 | Data | 0 | 27.565 | 24.635 | 241.18 | 7.63 | 224.951 | 2103.22 | 26.07 | 40.762 | 6.27 | 1.511 | 5.877 | 8965.31 | 3.146 | 98.1 | 79.5 | 1367 | 20.38 | 5827.5 | 3553.3 | 3450.6 | 5046.4 | 1190.2 | 0.68996 | 7.389
2024-12-09 | 15:20 | Data | 0 | 27.701 | 24.433 | 241.18 | 7.64 | 224.951 | 2104.12 | 26.06 | 40.762 | 6.28 | 1.512 | 5.857 | 8965.31 | 3.004 | 98.1 | 79.5 | 1367 | 20.34 | 5827.5 | 3557.5 | 3478.1 | 5053.9 | 1190.2 | 0.68729 | 7.368
2024-12-09 | 15:20 | Data | 0 | 26.992 | 23.758 | 241.044 | 7.64 | 224.951 | 2103.22 | 26.06 | 40.672 | 6.27 | 1.514 | 5.872 | 8960.79 | 3.2 | 98.1 | 79.5 | 1367 | 20.34 | 5824.5 | 3536.6 | 3524.5 | 5087.7 | 1190.2 | 0.68111 | 7.386
2024-12-09 | 15:20 | Data | 0 | 27.086 | 23.548 | 241.044 | 7.63 | 224.861 | 2104.12 | 26.07 | 40.762 | 6.27 | 1.513 | 5.874 | 8969.84 | 3.139 | 98.1 | 79.5 | 1368 | 20.29 | 5830.4 | 3542.4 | 3493.6 | 5080.9 | 1190.2 | 0.68403 | 7.388
2024-12-09 | 15:20 | Data | 0 | 27.41 | 24.197 | 240.908 | 7.64 | 224.906 | 2105.93 | 26.06 | 40.852 | 6.28 | 1.508 | 5.844 | 8965.31 | 3.052 | 98.1 | 79.5 | 1369 | 20.43 | 5827.5 | 3544 | 3534.9 | 5098 | 1190.2 | 0.68038 | 7.353
2024-12-09 | 15:20 | Data | 0 | 28.126 | 25.176 | 241.406 | 7.64 | 225.087 | 2101.41 | 26.05 | 40.762 | 6.28 | 1.507 | 5.865 | 8956.27 | 3.106 | 98.1 | 79.6 | 1366 | 20.34 | 5821.6 | 3529.9 | 3519.5 | 5074.6 | 1190.2 | 0.68116 | 7.375
2024-12-09 | 15:20 | Data | 0 | 27.383 | 24.203 | 241.18 | 7.64 | 225.042 | 2107.74 | 26.07 | 40.852 | 6.27 | 1.516 | 5.874 | 8951.75 | 3.058 | 98.1 | 79.5 | 1369 | 20.38 | 5818.6 | 3538.1 | 3500.5 | 5067.1 | 1190.2 | 0.68357 | 7.389
2024-12-09 | 15:20 | Data | 0 | 27.424 | 24.541 | 241.406 | 7.64 | 225.087 | 2105.93 | 26.07 | 40.762 | 6.27 | 1.523 | 5.866 | 8983.4 | 3.173 | 98.1 | 79.4 | 1369 | 20.34 | 5839.2 | 3528.2 | 3491.4 | 5061.9 | 1190.2 | 0.68335 | 7.39
2024-12-09 | 15:20 | Data | 0 | 28.335 | 25.115 | 241.451 | 7.64 | 225.403 | 2105.93 | 26.07 | 40.762 | 6.28 | 1.521 | 5.874 | 8965.31 | 3.227 | 98.1 | 79.4 | 1369 | 20.43 | 5827.5 | 3529.1 | 3482.7 | 5048.8 | 1190.2 | 0.68419 | 7.394
2024-12-09 | 15:20 | Data | 0 | 27.883 | 25.169 | 241.587 | 7.64 | 225.313 | 2104.12 | 26.05 | 40.762 | 6.27 | 1.519 | 5.868 | 8969.84 | 3.079 | 98.1 | 79.4 | 1367 | 20.38 | 5830.4 | 3540.6 | 3469.8 | 5049.3 | 1190.2 | 0.68644 | 7.387
2024-12-09 | 15:20 | Data | 0 | 28.166 | 24.98 | 241.677 | 7.63 | 225.449 | 2105.93 | 26.07 | 40.762 | 6.28 | 1.511 | 5.848 | 8983.4 | 3.079 | 98.1 | 79.4 | 1369 | 20.38 | 5839.2 | 3546.4 | 3455.1 | 5040.4 | 1190.2 | 0.68939 | 7.361
2024-12-09 | 15:21 | Data | 0 | 28.139 | 25.115 | 241.587 | 7.64 | 225.358 | 2105.93 | 26.07 | 40.672 | 6.28 | 1.509 | 5.856 | 8969.84 | 3.004 | 98.1 | 79.5 | 1369 | 20.34 | 5830.4 | 3542.1 | 3453.8 | 5038.6 | 1190.2 | 0.6861 | 7.363
2024-12-09 | 15:21 | Data | 0 | 28.315 | 25.459 | 241.677 | 7.64 | 225.494 | 2100.51 | 26.07 | 40.762 | 6.27 | 1.514 | 5.862 | 8969.84 | 3.011 | 98.1 | 79.5 | 1365 | 20.38 | 5830.4 | 3547 | 3487.9 | 5068 | 1190.2 | 0.68534 | 7.376
2024-12-09 | 15:21 | Data | 0 | 28.119 | 25.115 | 241.722 | 7.64 | 225.629 | 2105.03 | 26.07 | 40.762 | 6.28 | 1.518 | 5.876 | 8960.79 | 3.173 | 98.1 | 79.5 | 1368 | 20.29 | 5824.5 | 3536.1 | 3521.2 | 5082.1 | 1190.2 | 0.68086 | 7.395
2024-12-09 | 15:21 | Data | 0 | 28.349 | 25.351 | 241.858 | 7.63 | 225.72 | 2105.03 | 26.06 | 40.672 | 6.27 | 1.511 | 5.881 | 8969.84 | 2.991 | 98.1 | 79.6 | 1367 | 20.38 | 5830.4 | 3533.7 | 3518 | 5078.2 | 1190.2 | 0.68146 | 7.393
2024-12-09 | 15:21 | Data | 0 | 28.808 | 25.722 | 242.265 | 7.64 | 225.991 | 2104.12 | 26.06 | 40.762 | 6.27 | 1.518 | 5.87 | 8969.84 | 3.092 | 98.1 | 79.4 | 1368 | 20.38 | 5830.4 | 3532.6 | 3520.8 | 5077.8 | 1190.2 | 0.68116 | 7.387
2024-12-09 | 15:21 | Data | 0 | 29.017 | 25.925 | 242.31 | 7.64 | 225.946 | 2101.41 | 26.05 | 40.762 | 6.28 | 1.508 | 5.874 | 8992.45 | 3.22 | 98.1 | 79.6 | 1366 | 20.43 | 5845.1 | 3531.1 | 3510.9 | 5070.9 | 1190.2 | 0.6814 | 7.381
2024-12-09 | 15:21 | Data | 0 | 29.267 | 25.857 | 242.401 | 7.64 | 226.081 | 2096.89 | 26.06 | 40.672 | 6.27 | 1.508 | 5.876 | 8978.88 | 3.193 | 98.1 | 79.6 | 1364 | 20.34 | 5836.3 | 3552.4 | 3431.7 | 5031.4 | 1190.2 | 0.69205 | 7.383
2024-12-09 | 15:21 | Data | 0 | 29.267 | 26.046 | 242.627 | 7.63 | 226.172 | 2101.41 | 26.07 | 40.672 | 6.28 | 1.516 | 5.883 | 8992.45 | 3.2 | 98.1 | 79.5 | 1365 | 20.34 | 5845.1 | 3542.2 | 3488.4 | 5057.4 | 1190.2 | 0.68574 | 7.398
2024-12-09 | 15:21 | Data | 0 | 29.213 | 26.067 | 242.491 | 7.64 | 226.262 | 2102.31 | 26.06 | 40.672 | 6.27 | 1.511 | 5.885 | 8969.84 | 3.106 | 98.1 | 79.6 | 1368 | 20.34 | 5830.4 | 3536.3 | 3498.7 | 5065.3 | 1190.2 | 0.68319 | 7.396
2024-12-09 | 15:21 | Data | 0 | 29.328 | 26.094 | 242.356 | 7.63 | 226.262 | 2103.22 | 26.05 | 40.672 | 6.27 | 1.518 | 5.886 | 8983.4 | 3.214 | 98.1 | 79.5 | 1367 | 20.43 | 5839.2 | 3538.6 | 3449.1 | 5033.2 | 1190.2 | 0.68847 | 7.403
2024-12-09 | 15:21 | Data | 0 | 29.267 | 26.269 | 242.582 | 7.63 | 226.307 | 2102.31 | 26.02 | 40.672 | 6.27 | 1.521 | 5.882 | 8987.93 | 3.207 | 98.1 | 79.5 | 1367 | 20.38 | 5842.2 | 3547.3 | 3443.5 | 5036.1 | 1190.2 | 0.69022 | 7.403
2024-12-09 | 15:21 | Data | 0 | 29.436 | 26.472 | 242.627 | 7.64 | 226.217 | 2101.41 | 26.02 | 40.762 | 6.27 | 1.529 | 5.871 | 8996.97 | 3.193 | 98.1 | 79.3 | 1366 | 20.38 | 5848 | 3534.8 | 3472.3 | 5044.7 | 1190.2 | 0.6869 | 7.401
2024-12-09 | 15:21 | Data | 0 | 29.611 | 26.506 | 242.898 | 7.64 | 226.624 | 2103.22 | 26.06 | 40.672 | 6.27 | 1.516 | 5.878 | 9001.49 | 3.025 | 98.1 | 79.5 | 1368 | 20.34 | 5851 | 3544.9 | 3488.3 | 5063.6 | 1190.2 | 0.68586 | 7.394
2024-12-09 | 15:21 | Data | 0 | 29.78 | 26.506 | 242.853 | 7.64 | 226.669 | 2105.93 | 26.02 | 40.762 | 6.27 | 1.517 | 5.899 | 8983.4 | 3.22 | 98.1 | 79.5 | 1367 | 20.34 | 5839.2 | 3535.6 | 3493.1 | 5060.9 | 1190.2 | 0.6845 | 7.415
2024-12-09 | 15:21 | Data | 0 | 29.719 | 26.499 | 242.763 | 7.64 | 226.488 | 2100.51 | 26.05 | 40.672 | 6.27 | 1.516 | 5.884 | 8965.31 | 3.025 | 98.1 | 79.5 | 1366 | 20.34 | 5827.5 | 3546.7 | 3500.2 | 5072.7 | 1190.2 | 0.68458 | 7.399
2024-12-09 | 15:21 | Data | 0 | 29.726 | 26.715 | 242.627 | 7.64 | 226.443 | 2103.22 | 26.03 | 40.672 | 6.27 | 1.507 | 5.895 | 8978.88 | 2.896 | 98.1 | 79.6 | 1367 | 20.38 | 5836.3 | 3539.9 | 3488.2 | 5063 | 1190.3 | 0.68447 | 7.402
2024-12-09 | 15:21 | Data | 0 | 29.496 | 26.323 | 242.718 | 7.64 | 226.533 | 2096.89 | 26.03 | 40.491 | 6.28 | 1.508 | 5.905 | 8978.88 | 3.004 | 98.1 | 79.7 | 1364 | 20.29 | 5836.3 | 3535.6 | 3513.6 | 5079.2 | 1190.3 | 0.68105 | 7.413
2024-12-09 | 15:22 | Data | 0 | 29.469 | 26.587 | 242.582 | 7.63 | 226.443 | 2102.31 | 26.02 | 40.581 | 6.27 | 1.525 | 5.894 | 9010.54 | 3.22 | 98.1 | 79.5 | 1367 | 20.25 | 5856.8 | 3543 | 3516 | 5081.9 | 1190.3 | 0.68304 | 7.418
2024-12-09 | 15:22 | Data | 0 | 29.78 | 26.296 | 242.672 | 7.64 | 226.533 | 2103.22 | 26.05 | 40.672 | 6.27 | 1.507 | 5.862 | 9015.06 | 3.234 | 98.1 | 79.6 | 1367 | 20.38 | 5859.8 | 3536.9 | 3516.3 | 5078.1 | 1190.3 | 0.68209 | 7.367
2024-12-09 | 15:22 | Data | 0 | 29.712 | 26.728 | 242.763 | 7.64 | 226.533 | 2104.12 | 26.05 | 40.491 | 6.27 | 1.5 | 5.88 | 9019.58 | 3.112 | 98.1 | 79.7 | 1367 | 20.25 | 5862.7 | 3530.5 | 3491.3 | 5072.8 | 1190.3 | 0.68278 | 7.381
2024-12-09 | 15:22 | Data | 0 | 29.955 | 26.506 | 242.763 | 7.64 | 226.533 | 2102.31 | 26.05 | 40.401 | 6.27 | 1.515 | 5.86 | 9019.58 | 3.234 | 98.1 | 79.5 | 1367 | 20.2 | 5862.7 | 3536 | 3479.6 | 5055.4 | 1190.3 | 0.68455 | 7.375
2024-12-09 | 15:22 | Data | 0 | 29.814 | 26.843 | 242.898 | 7.63 | 226.578 | 2104.12 | 26.05 | 40.491 | 6.27 | 1.511 | 5.885 | 9019.58 | 3.193 | 98.1 | 79.6 | 1368 | 20.25 | 5862.7 | 3528.8 | 3456.1 | 5031.7 | 1190.3 | 0.68647 | 7.397
2024-12-09 | 15:22 | Data | 0 | 29.51 | 26.391 | 242.853 | 7.63 | 226.488 | 2101.41 | 26.05 | 40.491 | 6.28 | 1.519 | 5.88 | 9019.58 | 3.22 | 98.1 | 79.5 | 1366 | 20.25 | 5862.7 | 3540.6 | 3465.3 | 5047.2 | 1190.3 | 0.68672 | 7.398
2024-12-09 | 15:22 | Data | 0 | 29.861 | 26.512 | 242.898 | 7.63 | 226.533 | 2100.51 | 26.05 | 40.491 | 6.27 | 1.523 | 5.881 | 8978.88 | 3.025 | 98.1 | 79.4 | 1366 | 20.25 | 5836.3 | 3540.1 | 3463.1 | 5046.6 | 1190.3 | 0.68715 | 7.404
2024-12-09 | 15:22 | Data | 0 | 29.726 | 26.782 | 242.718 | 7.63 | 226.624 | 2101.41 | 26.05 | 40.491 | 6.27 | 1.517 | 5.914 | 8978.88 | 3.025 | 98.1 | 79.6 | 1366 | 20.29 | 5836.3 | 3534.6 | 3471.8 | 5068.3 | 1190.3 | 0.68262 | 7.433
2024-12-09 | 15:22 | Data | 0 | 29.949 | 26.512 | 242.627 | 7.64 | 226.443 | 2096.89 | 26.05 | 40.491 | 6.27 | 1.519 | 5.885 | 9015.06 | 3.112 | 98.1 | 79.5 | 1364 | 20.2 | 5859.8 | 3531 | 3495.2 | 5060.6 | 1190.3 | 0.68328 | 7.405
2024-12-09 | 15:22 | Data | 0 | 29.503 | 26.472 | 242.763 | 7.64 | 226.578 | 2100.51 | 26.05 | 40.491 | 6.27 | 1.518 | 5.878 | 8992.45 | 3.025 | 98.1 | 79.5 | 1365 | 20.25 | 5845.1 | 3537.3 | 3510.7 | 5076.8 | 1190.3 | 0.68235 | 7.396
2024-12-09 | 15:22 | Data | 0 | 29.679 | 26.674 | 242.672 | 7.63 | 226.533 | 2100.51 | 26.01 | 40.401 | 6.27 | 1.506 | 5.898 | 8978.88 | 3.227 | 98.1 | 79.7 | 1365 | 20.25 | 5836.3 | 3543.9 | 3516.3 | 5086.1 | 1190.3 | 0.68271 | 7.404
2024-12-09 | 15:22 | Data | 0 | 29.456 | 26.674 | 242.898 | 7.63 | 226.533 | 2100.51 | 26.03 | 40.491 | 6.28 | 1.514 | 5.883 | 8978.88 | 3.092 | 98.1 | 79.5 | 1365 | 20.25 | 5836.3 | 3537.5 | 3516.2 | 5076.3 | 1190.3 | 0.68192 | 7.396
2024-12-09 | 15:22 | Data | 0 | 29.618 | 26.701 | 242.853 | 7.63 | 226.533 | 2104.12 | 26.01 | 40.491 | 6.27 | 1.523 | 5.899 | 8974.36 | 2.937 | 98.1 | 79.5 | 1368 | 20.25 | 5833.3 | 3541.9 | 3520.1 | 5084.8 | 1190.3 | 0.68278 | 7.422
2024-12-09 | 15:22 | Data | 0 | 29.726 | 26.398 | 242.672 | 7.64 | 226.488 | 2101.41 | 26.05 | 40.491 | 6.27 | 1.511 | 5.91 | 8924.61 | 3.173 | 98.1 | 79.6 | 1366 | 20.25 | 5801 | 3540 | 3513.6 | 5075.1 | 1190.3 | 0.68432 | 7.421
2024-12-09 | 15:22 | Data | 0 | 29.699 | 26.519 | 242.853 | 7.63 | 226.578 | 2100.51 | 26.02 | 40.401 | 6.27 | 1.511 | 5.892 | 8924.61 | 3.247 | 98.1 | 79.6 | 1365 | 20.2 | 5801 | 3525.8 | 3498 | 5061.8 | 1190.3 | 0.68243 | 7.403
2024-12-09 | 15:22 | Data | 0 | 29.827 | 26.944 | 242.989 | 7.64 | 226.578 | 2100.51 | 26.01 | 40.491 | 6.28 | 1.512 | 5.896 | 8938.18 | 3.166 | 98.1 | 79.6 | 1366 | 20.25 | 5809.8 | 3546.6 | 3502.5 | 5076.5 | 1190.3 | 0.68372 | 7.41
2024-12-09 | 15:22 | Data | 0 | 30.09 | 26.728 | 242.853 | 7.64 | 226.624 | 2096.89 | 26.02 | 40.401 | 6.28 | 1.518 | 5.92 | 8911.05 | 3.247 | 98.1 | 79.6 | 1364 | 20.25 | 5792.2 | 3538.8 | 3502.1 | 5067.8 | 1190.3 | 0.6826 | 7.437
2024-12-09 | 15:22 | Data | 0 | 29.726 | 26.452 | 242.853 | 7.63 | 226.578 | 2095.08 | 26.03 | 40.401 | 6.27 | 1.516 | 5.912 | 8911.05 | 3.274 | 98.1 | 79.6 | 1362 | 20.25 | 5792.2 | 3542.6 | 3506.3 | 5076.8 | 1190.3 | 0.68345 | 7.428
2024-12-09 | 15:23 | Data | 0 | 29.118 | 26.587 | 242.898 | 7.64 | 226.578 | 2100.51 | 26.02 | 40.491 | 6.28 | 1.516 | 5.88 | 8906.53 | 2.95 | 98.1 | 79.5 | 1365 | 20.29 | 5789.2 | 3517.5 | 3475.8 | 5039.8 | 1190.3 | 0.68312 | 7.396
2024-12-09 | 15:23 | Data | 0 | 29.955 | 26.418 | 242.898 | 7.64 | 226.669 | 2101.41 | 26.03 | 40.491 | 6.27 | 1.508 | 5.901 | 8911.05 | 3.099 | 98.1 | 79.7 | 1366 | 20.25 | 5792.2 | 3525.3 | 3487.3 | 5051.9 | 1190.3 | 0.68232 | 7.408
2024-12-09 | 15:23 | Data | 0 | 29.922 | 27.147 | 242.898 | 7.64 | 226.533 | 2101.41 | 26.02 | 40.762 | 6.28 | 1.519 | 5.894 | 8911.05 | 3.031 | 98.1 | 79.5 | 1365 | 20.38 | 5792.2 | 3552.5 | 3497.2 | 5076.4 | 1190.3 | 0.68544 | 7.412
2024-12-09 | 15:23 | Data | 0 | 29.726 | 26.458 | 242.898 | 7.64 | 226.669 | 2104.12 | 26.05 | 40.762 | 6.27 | 1.524 | 5.88 | 8960.79 | 3.308 | 98.1 | 79.4 | 1367 | 20.34 | 5824.5 | 3542.4 | 3528 | 5090.7 | 1190.3 | 0.682 | 7.404
2024-12-09 | 15:23 | Data | 0 | 29.348 | 26.445 | 242.808 | 7.63 | 226.533 | 2104.12 | 26.03 | 40.762 | 6.27 | 1.515 | 5.9 | 8960.79 | 2.998 | 98.1 | 79.6 | 1368 | 20.34 | 5824.5 | 3532.1 | 3513.3 | 5074.4 | 1190.3 | 0.68125 | 7.415
2024-12-09 | 15:23 | Data | 0 | 29.591 | 26.425 | 242.853 | 7.64 | 226.578 | 2096.89 | 26.03 | 40.762 | 6.27 | 1.521 | 5.894 | 8992.45 | 3.004 | 98.1 | 79.5 | 1364 | 20.38 | 5845.1 | 3535.8 | 3541.6 | 5098.4 | 1190.3 | 0.67887 | 7.416
2024-12-09 | 15:23 | Data | 0 | 29.928 | 26.398 | 242.763 | 7.64 | 226.624 | 2104.12 | 26.05 | 40.581 | 6.27 | 1.524 | 5.885 | 8983.4 | 3.166 | 98.1 | 79.4 | 1367 | 20.29 | 5839.2 | 3541.1 | 3521.3 | 5083.7 | 1190.3 | 0.68144 | 7.409
2024-12-09 | 15:23 | Data | 0 | 29.942 | 26.641 | 243.034 | 7.64 | 226.669 | 2104.12 | 26.02 | 40.762 | 6.28 | 1.522 | 5.866 | 9006.01 | 3.166 | 98.1 | 79.4 | 1367 | 20.38 | 5853.9 | 3537.6 | 3490.8 | 5060.9 | 1190.3 | 0.68793 | 7.389
2024-12-09 | 15:23 | Data | 0 | 29.915 | 26.728 | 242.853 | 7.64 | 226.533 | 2105.03 | 26.05 | 40.762 | 6.27 | 1.519 | 5.881 | 9010.54 | 3.22 | 98.1 | 79.5 | 1368 | 20.34 | 5856.8 | 3542.4 | 3480.5 | 5058.1 | 1190.3 | 0.68602 | 7.4
2024-12-09 | 15:23 | Data | 0 | 30.036 | 26.742 | 242.808 | 7.64 | 226.669 | 2103.22 | 26.02 | 40.311 | 6.27 | 1.514 | 5.894 | 8992.45 | 3.22 | 98.1 | 79.6 | 1368 | 20.16 | 5845.1 | 3544.4 | 3492.5 | 5070.8 | 1190.3 | 0.6843 | 7.408
2024-12-09 | 15:23 | Data | 0 | 29.841 | 26.512 | 242.718 | 7.64 | 226.624 | 2103.22 | 26.02 | 40.672 | 6.27 | 1.513 | 5.89 | 8992.45 | 3.227 | 98.1 | 79.6 | 1367 | 20.38 | 5845.1 | 3559.9 | 3491.5 | 5078.1 | 1190.4 | 0.68708 | 7.403
2024-12-09 | 15:23 | Data | 0 | 29.814 | 26.776 | 242.763 | 7.63 | 226.624 | 2103.22 | 26.03 | 40.581 | 6.27 | 1.523 | 5.878 | 8969.84 | 3.227 | 98.1 | 79.4 | 1368 | 20.29 | 5830.4 | 3523.4 | 3489.6 | 5054.2 | 1190.4 | 0.68309 | 7.4
2024-12-09 | 15:23 | Data | 0 | 29.564 | 26.283 | 242.853 | 7.64 | 226.488 | 2101.41 | 26.03 | 40.762 | 6.27 | 1.514 | 5.908 | 8969.84 | 3.038 | 98.1 | 79.6 | 1365 | 20.38 | 5830.4 | 3540.9 | 3510.4 | 5075.8 | 1190.4 | 0.68319 | 7.423
2024-12-09 | 15:23 | Data | 0 | 30.009 | 26.965 | 243.125 | 7.63 | 226.759 | 2099.6 | 26.05 | 40.762 | 6.27 | 1.516 | 5.914 | 8969.84 | 3.004 | 98.1 | 79.6 | 1365 | 20.38 | 5830.4 | 3528.7 | 3520.9 | 5077.7 | 1190.4 | 0.67977 | 7.43
2024-12-09 | 15:23 | Data | 0 | 29.51 | 26.668 | 242.718 | 7.64 | 226.578 | 2096.89 | 26.06 | 40.943 | 6.27 | 1.517 | 5.868 | 8965.31 | 2.944 | 98.1 | 79.5 | 1362 | 20.43 | 5827.5 | 3551.3 | 3539.4 | 5105.8 | 1190.4 | 0.68102 | 7.385
2024-12-09 | 15:23 | Data | 0 | 29.726 | 26.553 | 242.718 | 7.64 | 226.624 | 2101.41 | 26.03 | 40.762 | 6.27 | 1.516 | 5.849 | 8978.88 | 3.112 | 98.1 | 79.4 | 1365 | 20.34 | 5836.3 | 3539 | 3537.5 | 5096.1 | 1190.4 | 0.68016 | 7.364
2024-12-09 | 15:23 | Data | 0 | 29.739 | 26.384 | 242.672 | 7.64 | 226.533 | 2101.41 | 26.03 | 40.672 | 6.28 | 1.515 | 5.89 | 8987.93 | 3.031 | 98.1 | 79.5 | 1366 | 20.34 | 5842.2 | 3518.4 | 3530.4 | 5080.8 | 1190.4 | 0.67796 | 7.405
2024-12-09 | 15:23 | Data | 0 | 29.942 | 26.985 | 242.763 | 7.64 | 226.533 | 2100.51 | 26.06 | 40.672 | 6.28 | 1.514 | 5.895 | 8992.45 | 3.052 | 98.1 | 79.6 | 1366 | 20.34 | 5845.1 | 3548.1 | 3539.8 | 5099.4 | 1190.4 | 0.68159 | 7.41
2024-12-09 | 15:24 | Data | 0 | 29.618 | 26.715 | 242.763 | 7.64 | 226.578 | 2101.41 | 26.02 | 40.672 | 6.28 | 1.509 | 5.89 | 8996.97 | 3.112 | 98.1 | 79.6 | 1366 | 20.34 | 5848 | 3534.2 | 3534 | 5086.9 | 1190.4 | 0.67966 | 7.397
2024-12-09 | 15:24 | Data | 0 | 29.739 | 26.722 | 242.718 | 7.64 | 226.578 | 2102.31 | 26.03 | 40.672 | 6.28 | 1.508 | 5.906 | 8996.97 | 3.018 | 98.1 | 79.7 | 1365 | 20.29 | 5848 | 3545.9 | 3506.9 | 5078.3 | 1190.4 | 0.68491 | 7.414
2024-12-09 | 15:24 | Data | 0 | 29.523 | 26.674 | 242.898 | 7.64 | 226.578 | 2103.22 | 26.03 | 40.762 | 6.27 | 1.512 | 5.892 | 8933.66 | 3.004 | 98.1 | 79.6 | 1366 | 20.38 | 5806.9 | 3537.5 | 3511.6 | 5078.2 | 1190.4 | 0.68262 | 7.403
2024-12-09 | 15:24 | Data | 0 | 29.834 | 27.093 | 242.853 | 7.63 | 226.669 | 2002.89 | 26.02 | 40.762 | 6.27 | 1.525 | 5.895 | 8920.09 | 2.937 | 98 | 79.4 | 1302 | 20.34 | 5798.1 | 3552.3 | 3519.4 | 5093.8 | 1190.4 | 0.68314 | 7.419
2024-12-09 | 15:24 | Data | 0 | 29.726 | 26.931 | 242.808 | 7.64 | 226.624 | 2102.31 | 26.03 | 40.762 | 6.27 | 1.515 | 5.881 | 8933.66 | 3.031 | 98.1 | 79.5 | 1367 | 20.38 | 5806.9 | 3549.2 | 3515.3 | 5094.6 | 1190.4 | 0.68439 | 7.396
2024-12-09 | 15:24 | Data | 0 | 29.949 | 26.519 | 242.944 | 7.64 | 226.804 | 2103.22 | 26.02 | 40.672 | 6.27 | 1.525 | 5.881 | 8915.57 | 3.214 | 98.1 | 79.4 | 1367 | 20.34 | 5795.1 | 3549.6 | 3536.6 | 5102.1 | 1190.4 | 0.6813 | 7.406
2024-12-09 | 15:24 | Data | 0 | 29.584 | 26.614 | 242.808 | 7.63 | 226.714 | 2103.22 | 26.05 | 40.762 | 6.28 | 1.509 | 5.872 | 8929.14 | 3.011 | 98.1 | 79.6 | 1367 | 20.34 | 5803.9 | 3530.3 | 3523.8 | 5077.6 | 1190.4 | 0.68015 | 7.382
2024-12-09 | 15:24 | Data | 0 | 29.496 | 26.708 | 242.808 | 7.64 | 226.624 | 2101.41 | 26.03 | 40.762 | 6.27 | 1.519 | 5.88 | 8920.09 | 3.025 | 98.1 | 79.5 | 1366 | 20.43 | 5798.1 | 3541.5 | 3545.7 | 5102.8 | 1190.4 | 0.67941 | 7.4
2024-12-09 | 15:24 | Data | 0 | 29.442 | 26.668 | 242.853 | 7.64 | 226.533 | 2105.93 | 26.03 | 40.311 | 6.27 | 1.511 | 5.884 | 8911.05 | 3.106 | 98.1 | 79.6 | 1369 | 20.16 | 5792.2 | 3531.2 | 3542.6 | 5094.3 | 1190.4 | 0.67736 | 7.395
2024-12-09 | 15:24 | Data | 0 | 29.652 | 26.728 | 242.989 | 7.63 | 226.578 | 2106.83 | 26.05 | 40.762 | 6.27 | 1.512 | 5.89 | 8924.61 | 2.903 | 98.1 | 79.6 | 1369 | 20.43 | 5801 | 3530.3 | 3569.8 | 5110.8 | 1190.4 | 0.67659 | 7.402
2024-12-09 | 15:24 | Data | 0 | 29.503 | 26.998 | 242.763 | 7.64 | 226.624 | 2105.93 | 26.03 | 40.581 | 6.28 | 1.503 | 5.895 | 8965.31 | 2.829 | 98.1 | 79.7 | 1369 | 20.29 | 5827.5 | 3521.1 | 3549.3 | 5093.2 | 1190.4 | 0.67577 | 7.398
2024-12-09 | 15:24 | Data | 0 | 30.111 | 26.843 | 242.944 | 7.63 | 226.714 | 2106.83 | 26.05 | 40.762 | 6.27 | 1.502 | 5.88 | 8978.88 | 3.22 | 98.1 | 79.7 | 1369 | 20.38 | 5836.3 | 3547.4 | 3550.8 | 5109.2 | 1190.4 | 0.6795 | 7.383
2024-12-09 | 15:24 | Data | 0 | 29.679 | 26.843 | 242.898 | 7.63 | 226.624 | 2105.93 | 26.03 | 40.762 | 6.27 | 1.506 | 5.877 | 8974.36 | 2.815 | 98.1 | 79.6 | 1369 | 20.38 | 5833.3 | 3537.7 | 3569.6 | 5117.3 | 1190.4 | 0.67723 | 7.383
2024-12-09 | 15:24 | Data | 0 | 29.719 | 26.553 | 242.763 | 7.63 | 226.488 | 2106.83 | 26.02 | 40.762 | 6.27 | 1.518 | 5.876 | 8978.88 | 3.112 | 98.1 | 79.4 | 1369 | 20.43 | 5836.3 | 3547.1 | 3545.9 | 5106.9 | 1190.4 | 0.68046 | 7.397
2024-12-09 | 15:24 | Data | 0 | 29.949 | 26.512 | 242.808 | 7.63 | 226.578 | 2104.12 | 26.02 | 40.672 | 6.28 | 1.518 | 5.881 | 8933.66 | 3.396 | 98.1 | 79.5 | 1368 | 20.38 | 5806.9 | 3537.2 | 3551.9 | 5104.2 | 1190.4 | 0.67832 | 7.399
2024-12-09 | 15:24 | Data | 0 | 29.746 | 26.121 | 242.763 | 7.63 | 226.624 | 2101.41 | 26.03 | 40.672 | 6.27 | 1.519 | 5.876 | 8951.75 | 3.355 | 98.1 | 79.5 | 1366 | 20.34 | 5818.6 | 3541.9 | 3512.6 | 5079.6 | 1190.4 | 0.68152 | 7.395
2024-12-09 | 15:24 | Data | 0 | 30.03 | 26.56 | 242.989 | 7.63 | 226.669 | 2102.31 | 26.05 | 40.762 | 6.28 | 1.505 | 5.871 | 8956.27 | 3.119 | 98.1 | 79.6 | 1367 | 20.38 | 5821.6 | 3535 | 3491.9 | 5061.7 | 1190.4 | 0.68348 | 7.376
2024-12-09 | 15:24 | Data | 0 | 29.638 | 26.506 | 242.989 | 7.64 | 226.669 | 2104.12 | 26.02 | 40.491 | 6.27 | 1.511 | 5.863 | 8969.84 | 3.025 | 98.1 | 79.5 | 1368 | 20.29 | 5830.4 | 3553.9 | 3465.3 | 5055.7 | 1190.4 | 0.68854 | 7.372
2024-12-09 | 15:25 | Data | 0 | 29.679 | 26.627 | 242.989 | 7.64 | 226.669 | 2103.22 | 26.01 | 40.762 | 6.28 | 1.509 | 5.866 | 8951.75 | 3.052 | 98.1 | 79.5 | 1368 | 20.34 | 5818.6 | 3544.2 | 3490.3 | 5065.4 | 1190.4 | 0.68512 | 7.376
2024-12-09 | 15:25 | Data | 0 | 29.496 | 26.458 | 242.627 | 7.64 | 226.488 | 2103.22 | 26.02 | 40.672 | 6.27 | 1.514 | 5.876 | 8965.31 | 3.112 | 98.1 | 79.5 | 1368 | 20.34 | 5827.5 | 3545.1 | 3496.5 | 5069.7 | 1190.4 | 0.68502 | 7.391
2024-12-09 | 15:25 | Data | 0 | 29.361 | 26.526 | 242.808 | 7.64 | 226.443 | 2103.22 | 26.02 | 40.672 | 6.28 | 1.518 | 5.908 | 8969.84 | 3.18 | 98.1 | 79.6 | 1368 | 20.43 | 5830.4 | 3538.9 | 3520 | 5097.9 | 1190.4 | 0.68185 | 7.427
2024-12-09 | 15:25 | Data | 0 | 29.496 | 26.472 | 242.763 | 7.64 | 226.578 | 2103.22 | 26.05 | 40.762 | 6.28 | 1.528 | 5.899 | 8965.31 | 3.052 | 98.1 | 79.4 | 1367 | 20.38 | 5827.5 | 3546.9 | 3548.6 | 5109 | 1190.4 | 0.68015 | 7.426
2024-12-09 | 15:25 | Data | 0 | 29.469 | 26.384 | 242.718 | 7.64 | 226.488 | 2100.51 | 26.02 | 40.762 | 6.27 | 1.523 | 5.906 | 8938.18 | 3.214 | 98.1 | 79.5 | 1366 | 20.38 | 5809.8 | 3550 | 3543.2 | 5106.4 | 1190.5 | 0.68042 | 7.43
2024-12-09 | 15:25 | Data | 0 | 30.003 | 26.782 | 242.944 | 7.64 | 226.669 | 2101.41 | 26.02 | 40.672 | 6.28 | 1.518 | 5.893 | 8951.75 | 3.328 | 98.1 | 79.5 | 1365 | 20.38 | 5818.6 | 3544.4 | 3572.5 | 5124.2 | 1190.5 | 0.67696 | 7.409
2024-12-09 | 15:25 | Data | 0 | 29.719 | 27.1 | 242.989 | 7.63 | 226.624 | 2101.41 | 26.01 | 40.672 | 6.28 | 1.518 | 5.895 | 8951.75 | 3.166 | 98.1 | 79.5 | 1366 | 20.34 | 5818.6 | 3531.4 | 3576.4 | 5118.8 | 1190.5 | 0.67517 | 7.411
2024-12-09 | 15:25 | Data | 0 | 29.793 | 26.512 | 243.034 | 7.64 | 226.624 | 2100.51 | 26.02 | 40.943 | 6.28 | 1.52 | 5.892 | 8965.31 | 3.018 | 98.1 | 79.5 | 1366 | 20.34 | 5827.5 | 3528.8 | 3552.9 | 5087.2 | 1190.5 | 0.6766 | 7.413
2024-12-09 | 15:25 | Data | 0 | 30.003 | 26.843 | 242.853 | 7.63 | 226.669 | 2095.08 | 26.03 | 40.762 | 6.28 | 1.517 | 5.906 | 9155.25 | 3.146 | 98.1 | 79.6 | 1362 | 20.38 | 5950.9 | 3532.6 | 3534.6 | 5087.9 | 1190.5 | 0.67979 | 7.422
2024-12-09 | 15:25 | Data | 0 | 30.131 | 26.654 | 242.944 | 7.64 | 226.804 | 2092.37 | 26.03 | 40.581 | 6.28 | 1.516 | 5.889 | 9141.68 | 3.092 | 98.1 | 79.5 | 1360 | 20.34 | 5942.1 | 3546.7 | 3562.7 | 5117.5 | 1190.5 | 0.67825 | 7.405
2024-12-09 | 15:25 | Data | 0 | 29.793 | 26.519 | 242.989 | 7.64 | 226.714 | 2099.6 | 26.01 | 40.762 | 6.28 | 1.51 | 5.889 | 9155.25 | 3.187 | 98.1 | 79.6 | 1365 | 20.34 | 5950.9 | 3545.9 | 3540.1 | 5100 | 1190.5 | 0.6812 | 7.399
2024-12-09 | 15:25 | Data | 0 | 29.881 | 26.289 | 243.034 | 7.64 | 226.533 | 2098.7 | 26.02 | 40.852 | 6.27 | 1.505 | 5.908 | 9146.2 | 3.207 | 98.1 | 79.7 | 1364 | 20.38 | 5945 | 3532.6 | 3559.5 | 5109.8 | 1190.5 | 0.67662 | 7.411
2024-12-09 | 15:25 | Data | 0 | 29.564 | 26.506 | 242.853 | 7.63 | 226.624 | 2100.51 | 26.01 | 40.762 | 6.27 | 1.513 | 5.884 | 9001.49 | 3.112 | 98.1 | 79.5 | 1364 | 20.34 | 5851 | 3545.9 | 3579.6 | 5129.9 | 1190.5 | 0.67636 | 7.398
2024-12-09 | 15:25 | Data | 0 | 29.469 | 26.472 | 242.763 | 7.64 | 226.443 | 2095.08 | 26.02 | 40.762 | 6.27 | 1.527 | 5.889 | 8987.93 | 3.045 | 98.1 | 79.4 | 1362 | 20.38 | 5842.2 | 3540.5 | 3578.5 | 5125.7 | 1190.5 | 0.67737 | 7.416
2024-12-09 | 15:25 | Data | 0 | 29.719 | 26.701 | 242.808 | 7.64 | 226.669 | 2098.7 | 26.01 | 40.672 | 6.27 | 1.527 | 5.864 | 8974.36 | 3.112 | 98.1 | 79.3 | 1364 | 20.34 | 5833.3 | 3538.9 | 3548.5 | 5100.9 | 1190.5 | 0.67932 | 7.39
2024-12-09 | 15:25 | Data | 0 | 30.165 | 26.62 | 242.944 | 7.63 | 226.714 | 2098.7 | 26.02 | 40.762 | 6.27 | 1.525 | 5.89 | 8996.97 | 3.274 | 98.1 | 79.4 | 1365 | 20.38 | 5848 | 3546.8 | 3570.9 | 5123.6 | 1190.5 | 0.67757 | 7.415
2024-12-09 | 15:25 | Data | 0 | 29.611 | 26.499 | 242.898 | 7.64 | 226.669 | 2096.89 | 26.02 | 40.672 | 6.27 | 1.507 | 5.92 | 8987.93 | 3.052 | 98.1 | 79.7 | 1363 | 20.38 | 5842.2 | 3542.2 | 3572.1 | 5122.8 | 1190.5 | 0.67717 | 7.427
2024-12-09 | 15:26 | Data | 0 | 29.672 | 26.607 | 242.808 | 7.63 | 226.578 | 2095.99 | 26.01 | 40.762 | 6.27 | 1.513 | 5.888 | 8974.36 | 3.214 | 98.1 | 79.5 | 1362 | 20.38 | 5833.3 | 3535 | 3578.3 | 5123.6 | 1190.5 | 0.675 | 7.402
2024-12-09 | 15:26 | Data | 0 | 29.712 | 26.472 | 242.763 | 7.64 | 226.578 | 2101.41 | 26.02 | 40.852 | 6.27 | 1.508 | 5.848 | 8996.97 | 3.099 | 98.1 | 79.5 | 1366 | 20.43 | 5848 | 3541.5 | 3571 | 5120.8 | 1190.5 | 0.67696 | 7.354
2024-12-09 | 15:26 | Data | 0 | 29.814 | 26.836 | 242.989 | 7.63 | 226.669 | 2098.7 | 26.02 | 40.762 | 6.28 | 1.505 | 5.85 | 8987.93 | 3.106 | 98.1 | 79.5 | 1364 | 20.38 | 5842.2 | 3552.6 | 3558.4 | 5119.3 | 1190.5 | 0.67958 | 7.354
2024-12-09 | 15:26 | Data | 0 | 29.618 | 26.526 | 242.763 | 7.63 | 226.488 | 2098.7 | 26.03 | 40.762 | 6.28 | 1.515 | 5.908 | 8987.93 | 2.971 | 98.1 | 79.6 | 1363 | 20.38 | 5842.2 | 3542.5 | 3543.5 | 5103.7 | 1190.5 | 0.67942 | 7.424
2024-12-09 | 15:26 | Data | 0 | 30.009 | 26.701 | 242.989 | 7.64 | 226.669 | 2092.37 | 26 | 40.672 | 6.28 | 1.51 | 5.898 | 8974.36 | 3.079 | 98.1 | 79.6 | 1361 | 20.38 | 5833.3 | 3544.1 | 3587.9 | 5135.1 | 1190.5 | 0.67582 | 7.409
2024-12-09 | 15:26 | Data | 0 | 29.949 | 26.83 | 242.989 | 7.64 | 226.714 | 2094.18 | 26.05 | 40.672 | 6.28 | 1.516 | 5.857 | 8978.88 | 3.112 | 98.1 | 79.4 | 1362 | 20.34 | 5836.3 | 3548.9 | 3549.9 | 5110.2 | 1190.5 | 0.67986 | 7.372
2024-12-09 | 15:26 | Data | 0 | 29.496 | 26.499 | 242.718 | 7.63 | 226.443 | 2095.08 | 26.03 | 40.762 | 6.28 | 1.522 | 5.868 | 9006.01 | 3.193 | 98.1 | 79.4 | 1362 | 20.34 | 5853.9 | 3534.5 | 3582 | 5122.6 | 1190.5 | 0.67527 | 7.391
2024-12-09 | 15:26 | Data | 0 | 29.733 | 26.553 | 242.808 | 7.63 | 226.669 | 2098.7 | 26.02 | 40.762 | 6.27 | 1.51 | 5.873 | 8996.97 | 2.998 | 98.1 | 79.5 | 1364 | 20.34 | 5848 | 3528.6 | 3568.7 | 5110.3 | 1190.5 | 0.6756 | 7.383
2024-12-09 | 15:26 | Data | 0 | 29.922 | 26.337 | 242.808 | 7.64 | 226.578 | 2093.28 | 26.05 | 40.762 | 6.28 | 1.505 | 5.894 | 9001.49 | 3.133 | 98.1 | 79.7 | 1360 | 20.43 | 5851 | 3525.8 | 3559.4 | 5104.5 | 1190.5 | 0.67679 | 7.398
2024-12-09 | 15:26 | Data | 0 | 29.537 | 26.553 | 242.898 | 7.64 | 226.669 | 2101.41 | 26.02 | 40.762 | 6.26 | 1.513 | 5.9 | 8992.45 | 2.977 | 98.1 | 79.6 | 1366 | 20.34 | 5845.1 | 3528.7 | 3571.8 | 5112.5 | 1190.5 | 0.67543 | 7.414
2024-12-09 | 15:26 | Data | 0 | 29.841 | 26.782 | 242.989 | 7.63 | 226.624 | 2100.51 | 26.02 | 40.672 | 6.27 | 1.517 | 5.899 | 8996.97 | 3.16 | 98.1 | 79.5 | 1365 | 20.38 | 5848 | 3546.8 | 3571.5 | 5132.1 | 1190.5 | 0.67892 | 7.416
2024-12-09 | 15:26 | Data | 0 | 29.739 | 26.836 | 242.808 | 7.64 | 226.624 | 2100.51 | 26.03 | 40.762 | 6.27 | 1.523 | 5.915 | 8992.45 | 3.058 | 98.1 | 79.5 | 1366 | 20.38 | 5845.1 | 3535.3 | 3596 | 5136.6 | 1190.5 | 0.67313 | 7.439
2024-12-09 | 15:26 | Data | 0 | 29.827 | 26.958 | 242.944 | 7.63 | 226.714 | 2105.03 | 26.01 | 40.762 | 6.28 | 1.515 | 5.913 | 8933.66 | 3.207 | 98.1 | 79.6 | 1369 | 20.34 | 5806.9 | 3554.9 | 3577.6 | 5134.5 | 1190.5 | 0.678 | 7.428
2024-12-09 | 15:26 | Data | 0 | 29.949 | 26.398 | 242.763 | 7.64 | 226.624 | 2106.83 | 26.02 | 40.762 | 6.27 | 1.521 | 5.907 | 8951.75 | 3.058 | 98.1 | 79.5 | 1369 | 20.38 | 5818.6 | 3549.4 | 3595.3 | 5139.8 | 1190.5 | 0.67553 | 7.429
2024-12-09 | 15:26 | Data | 0 | 29.888 | 26.965 | 242.808 | 7.63 | 226.624 | 2106.83 | 26.01 | 40.762 | 6.27 | 1.52 | 5.911 | 8965.31 | 3.092 | 98.1 | 79.5 | 1369 | 20.43 | 5827.5 | 3535.5 | 3574.7 | 5122.9 | 1190.5 | 0.67507 | 7.43
2024-12-09 | 15:26 | Data | 0 | 29.895 | 26.931 | 242.853 | 7.63 | 226.624 | 2104.12 | 26.03 | 40.762 | 6.28 | 1.518 | 5.884 | 8947.23 | 3.166 | 98.1 | 79.5 | 1368 | 20.38 | 5815.7 | 3531.1 | 3612.6 | 5142 | 1190.5 | 0.67277 | 7.401
2024-12-09 | 15:26 | Data | 0 | 29.787 | 26.573 | 242.898 | 7.63 | 226.624 | 2106.83 | 26.03 | 40.762 | 6.27 | 1.529 | 5.855 | 8978.88 | 3.416 | 98.1 | 79.3 | 1370 | 20.38 | 5836.3 | 3532.5 | 3607.8 | 5139.4 | 1190.5 | 0.67158 | 7.383
2024-12-09 | 15:26 | Data | 0 | 29.503 | 26.323 | 242.763 | 7.64 | 226.533 | 2105.93 | 26.03 | 40.491 | 6.28 | 1.519 | 5.873 | 8938.18 | 2.998 | 98.1 | 79.4 | 1369 | 20.29 | 5809.8 | 3555.7 | 3562.4 | 5126.8 | 1190.6 | 0.67897 | 7.391
2024-12-09 | 15:27 | Data | 0 | 29.726 | 26.614 | 242.853 | 7.63 | 226.669 | 2105.93 | 26.02 | 40.581 | 6.27 | 1.52 | 5.886 | 8938.18 | 2.998 | 98.1 | 79.5 | 1369 | 20.34 | 5809.8 | 3544.4 | 3577.6 | 5123.2 | 1190.6 | 0.67786 | 7.407
2024-12-09 | 15:27 | Data | 0 | 29.503 | 26.614 | 242.898 | 7.63 | 226.714 | 2107.74 | 26.01 | 40.852 | 6.27 | 1.512 | 5.836 | 8956.27 | 3.119 | 98.1 | 79.4 | 1369 | 20.38 | 5821.6 | 3532.7 | 3568.2 | 5109.4 | 1190.6 | 0.67831 | 7.349
2024-12-09 | 15:27 | Data | 0 | 29.571 | 26.614 | 242.853 | 7.63 | 226.669 | 2106.83 | 26.03 | 40.943 | 6.28 | 1.516 | 5.848 | 8947.23 | 3.018 | 98.1 | 79.4 | 1369 | 20.52 | 5815.7 | 3523.6 | 3529 | 5081.3 | 1190.6 | 0.68057 | 7.362
2024-12-09 | 15:27 | Data | 0 | 29.307 | 26.499 | 242.944 | 7.64 | 226.533 | 2104.12 | 26.02 | 40.762 | 6.27 | 1.517 | 5.857 | 8956.27 | 2.896 | 98.1 | 79.4 | 1367 | 20.38 | 5821.6 | 3548.9 | 3507.5 | 5076.4 | 1190.6 | 0.68426 | 7.374
2024-12-09 | 15:27 | Data | 0 | 29.652 | 26.445 | 242.989 | 7.64 | 226.714 | 2102.31 | 26.02 | 40.762 | 6.28 | 1.518 | 5.873 | 8938.18 | 3.119 | 98.1 | 79.5 | 1367 | 20.38 | 5809.8 | 3522.4 | 3478.8 | 5041.5 | 1190.6 | 0.68452 | 7.39
2024-12-09 | 15:27 | Data | 0 | 29.881 | 26.931 | 242.853 | 7.63 | 226.624 | 2105.93 | 26.02 | 40.672 | 6.27 | 1.518 | 5.885 | 8920.09 | 3.214 | 98.1 | 79.5 | 1369 | 20.29 | 5798.1 | 3537.9 | 3492.5 | 5052.7 | 1190.6 | 0.68339 | 7.403
2024-12-09 | 15:27 | Data | 0 | 29.908 | 26.668 | 243.034 | 7.64 | 226.714 | 2105.93 | 26.02 | 40.672 | 6.27 | 1.523 | 5.867 | 8915.57 | 2.984 | 98.1 | 79.4 | 1369 | 20.34 | 5795.1 | 3536.3 | 3539.1 | 5095 | 1190.6 | 0.68139 | 7.39
2024-12-09 | 15:27 | Data | 0 | 29.503 | 26.323 | 242.763 | 7.64 | 226.624 | 2105.93 | 26.02 | 40.852 | 6.28 | 1.52 | 5.874 | 8906.53 | 2.998 | 98.1 | 79.4 | 1369 | 20.38 | 5789.2 | 3526.3 | 3526.5 | 5075.6 | 1190.6 | 0.67964 | 7.394
2024-12-09 | 15:27 | Data | 0 | 29.719 | 26.499 | 242.808 | 7.63 | 226.624 | 2108.64 | 26.01 | 40.762 | 6.27 | 1.522 | 5.874 | 8897.48 | 3.227 | 98.1 | 79.4 | 1371 | 20.38 | 5783.4 | 3570.4 | 3553.7 | 5123.6 | 1190.6 | 0.68294 | 7.395
2024-12-09 | 15:27 | Data | 0 | 29.753 | 26.506 | 242.944 | 7.63 | 226.624 | 2108.64 | 26.02 | 40.762 | 6.27 | 1.518 | 5.902 | 8906.53 | 3.025 | 98.1 | 79.5 | 1371 | 20.43 | 5789.2 | 3549.7 | 3560.6 | 5115.2 | 1190.6 | 0.67945 | 7.421
2024-12-09 | 15:27 | Data | 0 | 29.496 | 26.499 | 242.808 | 7.63 | 226.488 | 2109.54 | 26.05 | 40.672 | 6.27 | 1.512 | 5.894 | 8956.27 | 3.112 | 98.1 | 79.6 | 1371 | 20.34 | 5821.6 | 3527.7 | 3544.2 | 5090.7 | 1190.6 | 0.67845 | 7.407
2024-12-09 | 15:27 | Data | 0 | 29.895 | 26.728 | 242.718 | 7.63 | 226.669 | 2107.74 | 26.02 | 40.762 | 6.28 | 1.519 | 5.884 | 8960.79 | 3.22 | 98.1 | 79.5 | 1371 | 20.38 | 5824.5 | 3530.4 | 3510.1 | 5060.9 | 1190.6 | 0.68175 | 7.403
2024-12-09 | 15:27 | Data | 0 | 29.557 | 26.458 | 242.808 | 7.63 | 226.578 | 2105.03 | 26.02 | 40.762 | 6.27 | 1.521 | 5.9 | 8933.66 | 3.254 | 98.1 | 79.5 | 1368 | 20.34 | 5806.9 | 3532.6 | 3508.5 | 5073.1 | 1190.6 | 0.68154 | 7.422
2024-12-09 | 15:27 | Data | 0 | 29.382 | 26.269 | 242.718 | 7.64 | 226.578 | 2111.35 | 26 | 40.672 | 6.28 | 1.513 | 5.866 | 8965.31 | 3.2 | 98.1 | 79.5 | 1372 | 20.29 | 5827.5 | 3531.4 | 3494.3 | 5057.1 | 1190.6 | 0.6842 | 7.378
2024-12-09 | 15:27 | Data | 0 | 29.496 | 26.674 | 242.853 | 7.64 | 226.533 | 2106.83 | 26.02 | 40.762 | 6.27 | 1.513 | 5.895 | 8956.27 | 3.085 | 98.1 | 79.6 | 1369 | 20.43 | 5821.6 | 3540.3 | 3509.9 | 5076.3 | 1190.6 | 0.68276 | 7.409
2024-12-09 | 15:27 | Data | 0 | 29.753 | 26.722 | 242.718 | 7.63 | 226.669 | 2105.93 | 26.03 | 40.762 | 6.28 | 1.514 | 5.883 | 8938.18 | 3.025 | 98.1 | 79.5 | 1369 | 20.34 | 5809.8 | 3543.7 | 3523.8 | 5087.9 | 1190.6 | 0.68234 | 7.396
2024-12-09 | 15:27 | Data | 0 | 29.814 | 26.722 | 242.898 | 7.63 | 226.759 | 2106.83 | 26.05 | 40.672 | 6.27 | 1.511 | 5.864 | 8956.27 | 3.214 | 98.1 | 79.5 | 1368 | 20.34 | 5821.6 | 3522 | 3505.1 | 5059.2 | 1190.6 | 0.68171 | 7.376
2024-12-09 | 15:28 | Data | 0 | 29.53 | 26.526 | 242.853 | 7.64 | 226.669 | 2105.93 | 26.02 | 40.672 | 6.28 | 1.507 | 5.88 | 8965.31 | 2.91 | 98.1 | 79.6 | 1369 | 20.34 | 5827.5 | 3540.1 | 3506.8 | 5073.2 | 1190.6 | 0.68335 | 7.388
2024-12-09 | 15:28 | Data | 0 | 29.874 | 26.728 | 242.808 | 7.63 | 226.578 | 2106.83 | 26.01 | 40.672 | 6.28 | 1.511 | 5.901 | 8920.09 | 3.052 | 98.1 | 79.6 | 1369 | 20.29 | 5798.1 | 3535.9 | 3511.2 | 5076 | 1190.6 | 0.68173 | 7.412
2024-12-09 | 15:28 | Data | 0 | 29.442 | 26.674 | 242.718 | 7.64 | 226.669 | 2108.64 | 26.02 | 40.762 | 6.28 | 1.529 | 5.866 | 8906.53 | 3.052 | 98.1 | 79.3 | 1371 | 20.38 | 5789.2 | 3531.5 | 3520.3 | 5079.6 | 1190.6 | 0.68104 | 7.396
2024-12-09 | 15:28 | Data | 0 | 29.679 | 26.526 | 242.944 | 7.63 | 226.714 | 2112.26 | 26.05 | 40.762 | 6.28 | 1.518 | 5.891 | 8915.57 | 2.991 | 98.1 | 79.5 | 1372 | 20.38 | 5795.1 | 3542.8 | 3524.5 | 5088.5 | 1190.6 | 0.68182 | 7.409
2024-12-09 | 15:28 | Data | 0 | 29.618 | 26.674 | 242.898 | 7.63 | 226.669 | 2112.26 | 26.03 | 40.762 | 6.28 | 1.51 | 5.879 | 8920.09 | 3.166 | 98.1 | 79.6 | 1373 | 20.38 | 5798.1 | 3528.3 | 3539.4 | 5095.7 | 1190.6 | 0.6808 | 7.389
2024-12-09 | 15:28 | Data | 0 | 29.274 | 26.492 | 242.944 | 7.64 | 226.624 | 2111.35 | 26.02 | 40.672 | 6.27 | 1.515 | 5.874 | 8915.57 | 3.146 | 98.1 | 79.5 | 1373 | 20.34 | 5795.1 | 3531 | 3512.7 | 5071.7 | 1190.6 | 0.68148 | 7.388
2024-12-09 | 15:28 | Data | 0 | 29.49 | 26.445 | 242.718 | 7.63 | 226.578 | 2108.64 | 26.05 | 40.762 | 6.27 | 1.515 | 5.857 | 8933.66 | 3.214 | 98.1 | 79.5 | 1371 | 20.34 | 5806.9 | 3517.7 | 3522.8 | 5071.5 | 1190.6 | 0.67925 | 7.372
2024-12-09 | 15:28 | Data | 0 | 29.854 | 26.87 | 242.944 | 7.64 | 226.759 | 2108.64 | 26.03 | 40.762 | 6.28 | 1.508 | 5.86 | 8924.61 | 2.998 | 98.1 | 79.5 | 1371 | 20.34 | 5801 | 3546.3 | 3545.7 | 5099.7 | 1190.6 | 0.68333 | 7.368
2024-12-09 | 15:28 | Data | 0 | 29.51 | 26.816 | 242.853 | 7.63 | 226.578 | 2108.64 | 26.02 | 40.762 | 6.28 | 1.518 | 5.872 | 8906.53 | 2.998 | 98.1 | 79.5 | 1371 | 20.38 | 5789.2 | 3524.8 | 3542.1 | 5084.4 | 1190.6 | 0.67888 | 7.39
2024-12-09 | 15:28 | Data | 0 | 30.111 | 26.627 | 242.898 | 7.63 | 226.759 | 2105.93 | 26.02 | 40.311 | 6.27 | 1.519 | 5.881 | 8920.09 | 3.261 | 98.1 | 79.5 | 1369 | 20.16 | 5798.1 | 3552.3 | 3548.3 | 5109.8 | 1190.6 | 0.68097 | 7.4
2024-12-09 | 15:28 | Data | 0 | 29.712 | 26.728 | 242.989 | 7.63 | 226.714 | 2106.83 | 26.02 | 40.762 | 6.28 | 1.513 | 5.873 | 8920.09 | 3.004 | 98.1 | 79.5 | 1369 | 20.34 | 5798.1 | 3514 | 3541.1 | 5079 | 1190.6 | 0.67731 | 7.386
2024-12-09 | 15:28 | Data | 0 | 29.949 | 26.742 | 242.898 | 7.63 | 226.578 | 2011.93 | 26.02 | 40.762 | 6.27 | 1.519 | 5.89 | 8938.18 | 3.038 | 98 | 79.5 | 1306 | 20.38 | 5809.8 | 3538.9 | 3542 | 5095.6 | 1190.6 | 0.68033 | 7.409
2024-12-09 | 15:28 | Data | 0 | 29.571 | 26.499 | 242.853 | 7.63 | 226.759 | 2095.08 | 26.02 | 40.672 | 6.28 | 1.514 | 5.897 | 8920.09 | 2.917 | 98.1 | 79.6 | 1364 | 20.34 | 5798.1 | 3540.3 | 3537.4 | 5092.9 | 1190.7 | 0.68093 | 7.411
2024-12-09 | 15:28 | Data | 0 | 29.766 | 26.83 | 242.898 | 7.63 | 226.669 | 2106.83 | 26.02 | 40.762 | 6.28 | 1.516 | 5.905 | 8920.09 | 3.214 | 98.1 | 79.6 | 1369 | 20.38 | 5798.1 | 3550.1 | 3553.6 | 5109.5 | 1190.7 | 0.68112 | 7.421
2024-12-09 | 15:28 | Data | 0 | 29.55 | 26.445 | 242.898 | 7.64 | 226.669 | 2103.22 | 26.02 | 40.762 | 6.27 | 1.521 | 5.918 | 8956.27 | 3.227 | 98.1 | 79.5 | 1367 | 20.38 | 5821.6 | 3520.3 | 3564.3 | 5102.3 | 1190.7 | 0.67483 | 7.44
2024-12-09 | 15:28 | Data | 0 | 29.496 | 26.458 | 242.853 | 7.63 | 226.533 | 2105.03 | 26.02 | 40.762 | 6.27 | 1.519 | 5.897 | 8947.23 | 3.261 | 98.1 | 79.5 | 1369 | 20.29 | 5815.7 | 3544.4 | 3567.7 | 5115.4 | 1190.7 | 0.67841 | 7.417
2024-12-09 | 15:28 | Data | 0 | 29.611 | 26.499 | 242.853 | 7.63 | 226.533 | 2105.03 | 26.01 | 40.852 | 6.27 | 1.522 | 5.909 | 8965.31 | 3.025 | 98.1 | 79.5 | 1368 | 20.43 | 5827.5 | 3539.1 | 3566.5 | 5116.2 | 1190.7 | 0.67746 | 7.431
2024-12-09 | 15:28 | Data | 0 | 30.036 | 26.735 | 242.944 | 7.63 | 226.669 | 2105.93 | 26.03 | 40.762 | 6.28 | 1.512 | 5.885 | 8974.36 | 3.227 | 98.1 | 79.6 | 1368 | 20.38 | 5833.3 | 3531.2 | 3537.7 | 5088.6 | 1190.7 | 0.67893 | 7.398
2024-12-09 | 15:29 | Data | 0 | 29.51 | 26.499 | 242.944 | 7.63 | 226.578 | 2106.83 | 26.01 | 40.762 | 6.29 | 1.52 | 5.87 | 8983.4 | 3.004 | 98.1 | 79.4 | 1369 | 20.38 | 5839.2 | 3540.5 | 3545 | 5101.2 | 1190.7 | 0.67936 | 7.39
2024-12-09 | 15:29 | Data | 0 | 29.584 | 26.296 | 242.808 | 7.63 | 226.488 | 2106.83 | 26.03 | 40.762 | 6.27 | 1.515 | 5.888 | 9453.71 | 3.187 | 98.1 | 79.5 | 1369 | 20.38 | 6144.9 | 3547.6 | 3510.9 | 5080.7 | 1190.7 | 0.68334 | 7.403
2024-12-09 | 15:29 | Data | 0 | 29.699 | 26.722 | 243.034 | 7.64 | 226.759 | 2103.22 | 26.02 | 40.762 | 6.27 | 1.512 | 5.88 | 9431.1 | 3.011 | 98.1 | 79.5 | 1367 | 20.38 | 6130.2 | 3557.8 | 3524 | 5111.6 | 1190.7 | 0.68175 | 7.392
2024-12-09 | 15:29 | Data | 0 | 29.503 | 26.614 | 242.763 | 7.64 | 226.578 | 2103.22 | 26.02 | 40.762 | 6.27 | 1.513 | 5.87 | 8784.42 | 2.998 | 98.1 | 79.5 | 1367 | 20.38 | 5709.9 | 3521.6 | 3538 | 5086.3 | 1190.7 | 0.6784 | 7.383
2024-12-09 | 15:29 | Data | 0 | 30.104 | 26.755 | 242.989 | 7.64 | 226.714 | 2101.41 | 26.02 | 40.762 | 6.28 | 1.511 | 5.9 | 8757.29 | 3.18 | 98.1 | 79.6 | 1366 | 20.34 | 5692.2 | 3519.9 | 3543.3 | 5087.3 | 1190.7 | 0.67742 | 7.411
2024-12-09 | 15:29 | Data | 0 | 29.611 | 26.553 | 242.853 | 7.63 | 226.714 | 2103.22 | 26.01 | 40.943 | 6.27 | 1.517 | 5.914 | 8784.42 | 3.2 | 98 | 79.6 | 1367 | 20.47 | 5709.9 | 3544 | 3524.8 | 5086.7 | 1190.7 | 0.68092 | 7.431
2024-12-09 | 15:29 | Data | 0 | 29.611 | 26.789 | 242.989 | 7.63 | 226.669 | 2099.6 | 26.01 | 40.672 | 6.27 | 1.506 | 5.881 | 8784.42 | 3.153 | 98.1 | 79.6 | 1364 | 20.38 | 5709.9 | 3533.8 | 3520.4 | 5079.2 | 1190.7 | 0.68082 | 7.388
2024-12-09 | 15:29 | Data | 0 | 29.746 | 26.809 | 242.989 | 7.63 | 226.759 | 2104.12 | 26.02 | 40.672 | 6.28 | 1.508 | 5.879 | 8802.51 | 3.018 | 98.1 | 79.6 | 1368 | 20.34 | 5721.6 | 3522.2 | 3527.2 | 5080.4 | 1190.7 | 0.67889 | 7.388
2024-12-09 | 15:29 | Data | 0 | 29.712 | 26.404 | 242.763 | 7.63 | 226.714 | 2098.7 | 26.02 | 40.762 | 6.28 | 1.514 | 5.879 | 8793.47 | 3.133 | 98.1 | 79.5 | 1363 | 20.38 | 5715.8 | 3546.6 | 3526.7 | 5100.7 | 1190.7 | 0.68202 | 7.392
2024-12-09 | 15:29 | Data | 0 | 29.591 | 26.506 | 242.763 | 7.63 | 226.714 | 2101.41 | 26.02 | 40.672 | 6.27 | 1.53 | 5.854 | 9177.86 | 2.829 | 98.1 | 79.3 | 1366 | 20.38 | 5965.6 | 3533 | 3526.2 | 5084.4 | 1190.7 | 0.68131 | 7.383
2024-12-09 | 15:29 | Data | 0 | 30.063 | 26.573 | 243.125 | 7.63 | 226.804 | 2100.51 | 26.01 | 40.672 | 6.28 | 1.518 | 5.853 | 9186.9 | 3.22 | 98.1 | 79.4 | 1365 | 20.38 | 5971.5 | 3535.3 | 3526.4 | 5081.3 | 1190.7 | 0.68163 | 7.371
2024-12-09 | 15:29 | Data | 0 | 29.523 | 26.472 | 242.898 | 7.63 | 226.669 | 2095.08 | 26.03 | 40.762 | 6.28 | 1.521 | 5.83 | 9155.25 | 2.856 | 98.1 | 79.3 | 1362 | 20.43 | 5950.9 | 3524.4 | 3501.8 | 5063.7 | 1190.7 | 0.68099 | 7.352
2024-12-09 | 15:29 | Data | 0 | 29.719 | 27.093 | 242.944 | 7.63 | 226.714 | 2100.51 | 26.03 | 40.672 | 6.28 | 1.531 | 5.879 | 9159.77 | 3.112 | 98.1 | 79.3 | 1366 | 20.38 | 5953.9 | 3548.3 | 3486.2 | 5062.6 | 1190.7 | 0.68359 | 7.411
2024-12-09 | 15:29 | Data | 0 | 29.814 | 26.931 | 242.989 | 7.63 | 226.669 | 2100.51 | 26.02 | 40.762 | 6.27 | 1.521 | 5.865 | 9173.34 | 3.16 | 98.1 | 79.4 | 1366 | 20.38 | 5962.7 | 3565.1 | 3478.1 | 5070.8 | 1190.7 | 0.68895 | 7.386
2024-12-09 | 15:29 | Data | 0 | 29.719 | 26.499 | 242.853 | 7.63 | 226.624 | 2104.12 | 26.03 | 40.672 | 6.27 | 1.517 | 5.873 | 9173.34 | 3.227 | 98.1 | 79.5 | 1367 | 20.34 | 5962.7 | 3563.6 | 3486.4 | 5073.3 | 1190.7 | 0.68763 | 7.389
2024-12-09 | 15:29 | Data | 0 | 29.733 | 26.499 | 243.17 | 7.63 | 226.759 | 2103.22 | 26.02 | 40.852 | 6.28 | 1.507 | 5.897 | 9155.25 | 3.22 | 98.1 | 79.6 | 1368 | 20.43 | 5950.9 | 3530.9 | 3470.6 | 5041.9 | 1190.7 | 0.685 | 7.403
2024-12-09 | 15:29 | Data | 0 | 29.503 | 26.614 | 242.989 | 7.63 | 226.533 | 2104.12 | 26.03 | 40.762 | 6.28 | 1.518 | 5.9 | 9146.2 | 3.2 | 98.1 | 79.5 | 1367 | 20.43 | 5945 | 3516.7 | 3510.5 | 5080.7 | 1190.7 | 0.6804 | 7.419
2024-12-09 | 15:29 | Data | 0 | 29.645 | 26.56 | 242.898 | 7.63 | 226.714 | 2103.22 | 26.01 | 40.762 | 6.28 | 1.524 | 5.871 | 9141.68 | 2.917 | 98.1 | 79.4 | 1367 | 20.38 | 5942.1 | 3537.6 | 3527.8 | 5085.3 | 1190.7 | 0.68085 | 7.395
2024-12-09 | 15:30 | Data | 0 | 30.077 | 26.62 | 242.898 | 7.64 | 226.804 | 2103.22 | 26.05 | 40.762 | 6.28 | 1.516 | 5.865 | 9128.11 | 2.977 | 98.1 | 79.5 | 1367 | 20.38 | 5933.3 | 3541.3 | 3540.2 | 5099.8 | 1190.7 | 0.68019 | 7.381
2024-12-09 | 15:30 | Data | 0 | 29.726 | 26.303 | 242.944 | 7.64 | 226.714 | 2104.12 | 26.03 | 40.672 | 6.28 | 1.516 | 5.876 | 9132.64 | 3.2 | 98.1 | 79.5 | 1368 | 20.34 | 5936.2 | 3547.7 | 3575.6 | 5121 | 1190.7 | 0.67712 | 7.392
2024-12-09 | 15:30 | Data | 0 | 29.726 | 26.904 | 242.763 | 7.64 | 226.533 | 2103.22 | 26.02 | 40.762 | 6.28 | 1.522 | 5.913 | 9119.07 | 2.937 | 98.1 | 79.5 | 1367 | 20.38 | 5927.4 | 3555.1 | 3561.6 | 5123.2 | 1190.7 | 0.67965 | 7.434
2024-12-09 | 15:30 | Data | 0 | 29.928 | 26.755 | 242.989 | 7.63 | 226.759 | 2104.12 | 26.02 | 40.852 | 6.27 | 1.517 | 5.885 | 9064.8 | 3.112 | 98.1 | 79.5 | 1367 | 20.38 | 5892.1 | 3558.4 | 3587.8 | 5142.5 | 1190.7 | 0.6772 | 7.403
2024-12-09 | 15:30 | Data | 0 | 29.537 | 26.499 | 242.808 | 7.64 | 226.669 | 2107.74 | 26.01 | 40.672 | 6.28 | 1.517 | 5.88 | 9051.24 | 3.004 | 98.1 | 79.5 | 1369 | 20.34 | 5883.3 | 3546.6 | 3546 | 5107.3 | 1190.7 | 0.67966 | 7.398
2024-12-09 | 15:30 | Data | 0 | 29.793 | 26.519 | 242.989 | 7.63 | 226.804 | 2106.83 | 26.02 | 40.762 | 6.27 | 1.522 | 5.886 | 9042.19 | 3.018 | 98.1 | 79.5 | 1369 | 20.34 | 5877.4 | 3520.6 | 3524.4 | 5077.5 | 1190.7 | 0.67957 | 7.409
2024-12-09 | 15:30 | Data | 0 | 29.618 | 26.674 | 242.672 | 7.63 | 226.804 | 2108.64 | 26.02 | 40.943 | 6.27 | 1.525 | 5.899 | 9042.19 | 3.011 | 98.1 | 79.5 | 1371 | 20.47 | 5877.4 | 3552 | 3475.4 | 5059.8 | 1190.8 | 0.68814 | 7.424
2024-12-09 | 15:30 | Data | 0 | 30.003 | 26.728 | 242.853 | 7.63 | 226.714 | 2107.74 | 26.02 | 40.762 | 6.28 | 1.511 | 5.882 | 9060.28 | 2.917 | 98.1 | 79.6 | 1371 | 20.43 | 5889.2 | 3536.6 | 3488.4 | 5060.2 | 1190.8 | 0.68451 | 7.393
2024-12-09 | 15:30 | Data | 0 | 30.057 | 26.965 | 242.989 | 7.63 | 226.759 | 2108.64 | 26.02 | 40.762 | 6.28 | 1.514 | 5.876 | 9051.24 | 3.214 | 98.1 | 79.5 | 1371 | 20.34 | 5883.3 | 3541.8 | 3491.2 | 5064.9 | 1190.8 | 0.68507 | 7.389
2024-12-09 | 15:30 | Data | 0 | 29.739 | 26.506 | 242.898 | 7.63 | 226.759 | 2108.64 | 26.02 | 40.762 | 6.28 | 1.515 | 5.876 | 9019.58 | 3.085 | 98.1 | 79.5 | 1371 | 20.38 | 5862.7 | 3516.4 | 3488.8 | 5043.7 | 1190.8 | 0.68299 | 7.39
2024-12-09 | 15:30 | Data | 0 | 29.76 | 26.998 | 243.079 | 7.64 | 226.85 | 2116.78 | 26.03 | 40.762 | 6.28 | 1.51 | 5.911 | 9042.19 | 3.018 | 98.1 | 79.6 | 1376 | 20.43 | 5877.4 | 3556 | 3533.4 | 5084 | 1190.8 | 0.6828 | 7.421
2024-12-09 | 15:30 | Data | 0 | 29.328 | 26.269 | 242.808 | 7.63 | 226.624 | 2111.35 | 26.02 | 40.672 | 6.28 | 1.522 | 5.909 | 9006.01 | 3.187 | 98.1 | 79.5 | 1372 | 20.38 | 5853.9 | 3536.8 | 3570.1 | 5114.2 | 1190.8 | 0.67764 | 7.434
2024-12-09 | 15:30 | Data | 0 | 29.672 | 26.836 | 243.034 | 7.63 | 226.714 | 2111.35 | 26.02 | 40.762 | 6.28 | 1.525 | 5.904 | 8965.31 | 3.025 | 98.1 | 79.5 | 1372 | 20.38 | 5827.5 | 3538.4 | 3582.9 | 5124.5 | 1190.8 | 0.67573 | 7.428
2024-12-09 | 15:30 | Data | 0 | 29.847 | 26.728 | 242.944 | 7.63 | 226.714 | 2112.26 | 26.03 | 40.672 | 6.28 | 1.519 | 5.874 | 8969.84 | 3.018 | 98.1 | 79.5 | 1373 | 20.34 | 5830.4 | 3527.4 | 3574.3 | 5113.2 | 1190.8 | 0.67532 | 7.392
2024-12-09 | 15:30 | Data | 0 | 30.165 | 26.634 | 242.853 | 7.63 | 226.714 | 2111.35 | 26.02 | 40.762 | 6.28 | 1.512 | 5.881 | 8969.84 | 3.274 | 98.1 | 79.5 | 1372 | 20.38 | 5830.4 | 3557.3 | 3548.5 | 5112.6 | 1190.8 | 0.67971 | 7.394
2024-12-09 | 15:30 | Data | 0 | 29.699 | 26.701 | 242.808 | 7.63 | 226.578 | 2108.64 | 26.02 | 40.762 | 6.28 | 1.514 | 5.881 | 9006.01 | 3.045 | 98.1 | 79.5 | 1370 | 20.29 | 5853.9 | 3518.9 | 3567.6 | 5104.1 | 1190.8 | 0.67513 | 7.396
2024-12-09 | 15:30 | Data | 0 | 29.672 | 27.052 | 243.079 | 7.63 | 226.804 | 2112.26 | 26.02 | 40.672 | 6.28 | 1.508 | 5.883 | 8992.45 | 2.998 | 98.1 | 79.6 | 1372 | 20.38 | 5845.1 | 3537.5 | 3538.6 | 5095.1 | 1190.8 | 0.68007 | 7.39
2024-12-09 | 15:30 | Data | 0 | 29.922 | 26.728 | 242.989 | 7.63 | 226.759 | 2111.35 | 26.02 | 40.762 | 6.28 | 1.512 | 5.905 | 9006.01 | 3.308 | 98.1 | 79.6 | 1372 | 20.38 | 5853.9 | 3537.3 | 3505.1 | 5073.9 | 1190.8 | 0.68272 | 7.416
2024-12-09 | 15:31 | Data | 0 | 29.841 | 27.1 | 242.989 | 7.63 | 226.624 | 2111.35 | 26.03 | 40.672 | 6.27 | 1.519 | 5.898 | 8992.45 | 3.038 | 98.1 | 79.5 | 1372 | 20.34 | 5845.1 | 3539.4 | 3484.8 | 5060.2 | 1190.8 | 0.68478 | 7.418
2024-12-09 | 15:31 | Data | 0 | 30.07 | 26.985 | 242.898 | 7.63 | 226.759 | 2114.06 | 26.02 | 40.672 | 6.27 | 1.518 | 5.889 | 9006.01 | 3.085 | 98.1 | 79.5 | 1374 | 20.43 | 5853.9 | 3541.9 | 3489 | 5060.3 | 1190.8 | 0.68549 | 7.408
2024-12-09 | 15:31 | Data | 0 | 29.739 | 26.62 | 242.989 | 7.64 | 226.624 | 2119.49 | 26.02 | 40.672 | 6.27 | 1.514 | 5.878 | 8987.93 | 2.991 | 98.1 | 79.5 | 1378 | 20.34 | 5842.2 | 3547.2 | 3491.3 | 5067.6 | 1190.8 | 0.68569 | 7.391
2024-12-09 | 15:31 | Data | 0 | 30.151 | 26.56 | 242.853 | 7.63 | 226.759 | 2121.29 | 26 | 40.581 | 6.28 | 1.51 | 5.88 | 8992.45 | 3.153 | 98.1 | 79.6 | 1378 | 20.38 | 5845.1 | 3541 | 3521.3 | 5092.2 | 1190.8 | 0.68191 | 7.39
2024-12-09 | 15:31 | Data | 0 | 30.178 | 26.965 | 243.125 | 7.63 | 226.669 | 2120.39 | 26.02 | 40.762 | 6.28 | 1.517 | 5.883 | 8996.97 | 3.214 | 98.1 | 79.5 | 1379 | 20.38 | 5848 | 3540.2 | 3537.4 | 5095.5 | 1190.8 | 0.67967 | 7.399
2024-12-09 | 15:31 | Data | 0 | 29.726 | 26.492 | 242.763 | 7.63 | 226.624 | 2118.58 | 26.02 | 40.672 | 6.27 | 1.513 | 5.874 | 8965.31 | 3.247 | 98.1 | 79.5 | 1377 | 20.34 | 5827.5 | 3525.8 | 3559.7 | 5115 | 1190.8 | 0.67768 | 7.387
2024-12-09 | 15:31 | Data | 0 | 29.503 | 26.499 | 242.808 | 7.64 | 226.669 | 2117.68 | 26.02 | 40.311 | 6.27 | 1.516 | 5.892 | 8978.88 | 3.112 | 98.1 | 79.5 | 1376 | 20.11 | 5836.3 | 3545.1 | 3566.1 | 5117.8 | 1190.8 | 0.67932 | 7.406
2024-12-09 | 15:31 | Data | 0 | 29.618 | 26.681 | 242.853 | 7.63 | 226.759 | 2114.06 | 26.02 | 40.672 | 6.28 | 1.515 | 5.886 | 8992.45 | 3.133 | 98.1 | 79.5 | 1374 | 20.29 | 5845.1 | 3566.5 | 3577.9 | 5142 | 1190.8 | 0.6792 | 7.401
2024-12-09 | 15:31 | Data | 0 | 29.537 | 26.722 | 242.853 | 7.63 | 226.714 | 2114.06 | 26.01 | 40.762 | 6.28 | 1.53 | 5.858 | 8992.45 | 3.092 | 98.1 | 79.3 | 1374 | 20.38 | 5845.1 | 3523.9 | 3571.2 | 5111 | 1190.8 | 0.67511 | 7.389
2024-12-09 | 15:31 | Data | 0 | 29.726 | 26.674 | 242.853 | 7.63 | 226.669 | 2120.39 | 26.02 | 40.672 | 6.28 | 1.51 | 5.846 | 9037.67 | 3.227 | 98.1 | 79.5 | 1378 | 20.47 | 5874.5 | 3539.8 | 3535.7 | 5094.5 | 1190.8 | 0.68072 | 7.358
2024-12-09 | 15:31 | Data | 0 | 29.469 | 26.6 | 242.808 | 7.63 | 226.578 | 2111.35 | 26.02 | 40.672 | 6.28 | 1.513 | 5.884 | 9037.67 | 3.153 | 98.1 | 79.5 | 1372 | 20.38 | 5874.5 | 3532.9 | 3539.1 | 5091.5 | 1190.8 | 0.67933 | 7.397
2024-12-09 | 15:31 | Data | 0 | 29.517 | 26.499 | 242.898 | 7.63 | 226.759 | 2112.26 | 26.02 | 40.672 | 6.28 | 1.525 | 5.908 | 9046.71 | 2.998 | 98.1 | 79.5 | 1372 | 20.38 | 5880.4 | 3531.9 | 3524.6 | 5083.3 | 1190.8 | 0.68018 | 7.432
2024-12-09 | 15:31 | Data | 0 | 29.618 | 26.674 | 242.853 | 7.63 | 226.669 | 2111.35 | 26.02 | 40.672 | 6.27 | 1.507 | 5.911 | 9042.19 | 3.173 | 98.1 | 79.7 | 1372 | 20.34 | 5877.4 | 3534.8 | 3539.5 | 5092.9 | 1190.8 | 0.67953 | 7.418
2024-12-09 | 15:31 | Data | 0 | 30.205 | 26.735 | 243.079 | 7.63 | 226.759 | 2113.16 | 26.02 | 40.762 | 6.27 | 1.507 | 5.882 | 9024.1 | 3.072 | 98.1 | 79.6 | 1374 | 20.38 | 5865.7 | 3534.9 | 3511.2 | 5077.1 | 1190.8 | 0.68124 | 7.389
2024-12-09 | 15:31 | Data | 0 | 29.949 | 26.553 | 242.944 | 7.63 | 226.759 | 2114.06 | 26.02 | 40.762 | 6.28 | 1.513 | 5.895 | 9024.1 | 3.085 | 98.1 | 79.6 | 1374 | 20.29 | 5865.7 | 3526.9 | 3511.4 | 5066.8 | 1190.8 | 0.68176 | 7.409
2024-12-09 | 15:31 | Data | 0 | 29.348 | 26.384 | 243.034 | 7.63 | 226.714 | 2114.06 | 26.02 | 40.762 | 6.27 | 1.508 | 5.876 | 9033.15 | 2.977 | 98.1 | 79.6 | 1374 | 20.43 | 5871.5 | 3539.8 | 3542.6 | 5106.7 | 1190.8 | 0.68091 | 7.383
2024-12-09 | 15:31 | Data | 0 | 29.868 | 26.728 | 242.989 | 7.63 | 226.804 | 2114.97 | 26.02 | 40.762 | 6.28 | 1.504 | 5.895 | 9019.58 | 3.214 | 98.1 | 79.7 | 1374 | 20.38 | 5862.7 | 3542.2 | 3552.1 | 5109.2 | 1190.8 | 0.67885 | 7.399
2024-12-09 | 15:32 | Data | 0 | 29.787 | 26.56 | 242.944 | 7.63 | 226.714 | 2111.35 | 26.02 | 40.762 | 6.27 | 1.508 | 5.899 | 8983.4 | 3.173 | 98.1 | 79.7 | 1372 | 20.38 | 5839.2 | 3544.9 | 3563 | 5119.3 | 1190.8 | 0.67826 | 7.406
2024-12-09 | 15:32 | Data | 0 | 29.928 | 26.749 | 242.898 | 7.63 | 226.714 | 2113.16 | 26.02 | 40.762 | 6.27 | 1.512 | 5.886 | 8960.79 | 3.173 | 98.1 | 79.6 | 1373 | 20.38 | 5824.5 | 3549.8 | 3574.4 | 5128.5 | 1190.9 | 0.67788 | 7.4
2024-12-09 | 15:32 | Data | 0 | 29.726 | 26.587 | 242.898 | 7.63 | 226.624 | 2112.26 | 26.02 | 40.672 | 6.27 | 1.515 | 5.901 | 8947.23 | 3.112 | 98.1 | 79.6 | 1373 | 20.29 | 5815.7 | 3533 | 3552.4 | 5102.8 | 1190.9 | 0.6777 | 7.416
2024-12-09 | 15:32 | Data | 0 | 29.726 | 26.499 | 243.034 | 7.63 | 226.759 | 2109.54 | 26.02 | 40.762 | 6.28 | 1.516 | 5.884 | 8951.75 | 3.227 | 98.1 | 79.5 | 1371 | 20.38 | 5818.6 | 3539 | 3548.5 | 5105.5 | 1190.9 | 0.67839 | 7.399
2024-12-09 | 15:32 | Data | 0 | 29.699 | 26.836 | 242.944 | 7.63 | 226.714 | 2106.83 | 26.02 | 40.762 | 6.28 | 1.511 | 5.87 | 8938.18 | 3.058 | 98.1 | 79.5 | 1369 | 20.34 | 5809.8 | 3525.4 | 3540.2 | 5087.4 | 1190.9 | 0.67846 | 7.38
2024-12-09 | 15:32 | Data | 0 | 29.827 | 26.728 | 242.989 | 7.63 | 226.714 | 2103.22 | 26 | 40.762 | 6.27 | 1.513 | 5.886 | 8987.93 | 3.214 | 98.1 | 79.5 | 1368 | 20.38 | 5842.2 | 3518.6 | 3527.9 | 5076.7 | 1190.9 | 0.67866 | 7.4
2024-12-09 | 15:32 | Data | 0 | 29.672 | 26.985 | 243.125 | 7.63 | 226.669 | 2100.51 | 26.03 | 40.762 | 6.28 | 1.51 | 5.903 | 8992.45 | 3.22 | 98.1 | 79.6 | 1365 | 20.38 | 5845.1 | 3534 | 3493.9 | 5063.9 | 1190.9 | 0.68303 | 7.412
2024-12-09 | 15:32 | Data | 0 | 29.503 | 26.722 | 242.989 | 7.63 | 226.759 | 2101.41 | 26.02 | 40.762 | 6.28 | 1.508 | 5.912 | 8983.4 | 2.957 | 98.1 | 79.7 | 1366 | 20.38 | 5839.2 | 3540.2 | 3468.6 | 5050.8 | 1190.9 | 0.68567 | 7.419
2024-12-09 | 15:32 | Data | 0 | 29.895 | 27.005 | 242.989 | 7.63 | 226.759 | 2099.6 | 26.02 | 40.672 | 6.29 | 1.518 | 5.858 | 9006.01 | 3.106 | 98.1 | 79.4 | 1365 | 20.38 | 5853.9 | 3557.1 | 3497.4 | 5079.1 | 1190.9 | 0.68649 | 7.376
2024-12-09 | 15:32 | Data | 0 | 29.699 | 26.546 | 242.763 | 7.63 | 226.624 | 2101.41 | 26.02 | 40.672 | 6.28 | 1.522 | 5.862 | 8956.27 | 3.018 | 98.1 | 79.4 | 1366 | 20.34 | 5821.6 | 3520.2 | 3522.9 | 5074.4 | 1190.9 | 0.68014 | 7.385
2024-12-09 | 15:32 | Data | 0 | 29.719 | 26.668 | 242.944 | 7.63 | 226.669 | 2105.03 | 26.02 | 40.762 | 6.28 | 1.513 | 5.893 | 8960.79 | 3.227 | 98.1 | 79.6 | 1369 | 20.43 | 5824.5 | 3520.5 | 3532.1 | 5074.6 | 1190.9 | 0.67897 | 7.407
2024-12-09 | 15:32 | Data | 0 | 29.989 | 26.674 | 243.215 | 7.63 | 226.985 | 2105.93 | 26.01 | 40.762 | 6.27 | 1.508 | 5.872 | 8933.66 | 3.011 | 98.1 | 79.6 | 1369 | 20.38 | 5806.9 | 3527 | 3559.8 | 5100.4 | 1190.9 | 0.67748 | 7.381
2024-12-09 | 15:32 | Data | 0 | 30.09 | 26.958 | 242.808 | 7.63 | 226.759 | 2105.93 | 26.02 | 40.672 | 6.28 | 1.509 | 5.867 | 8951.75 | 3.207 | 98.1 | 79.5 | 1369 | 20.34 | 5818.6 | 3517.3 | 3569.1 | 5102.8 | 1190.9 | 0.67461 | 7.377
2024-12-09 | 15:32 | Data | 0 | 29.928 | 27.127 | 242.989 | 7.64 | 226.759 | 2105.93 | 26.02 | 40.491 | 6.28 | 1.518 | 5.878 | 8933.66 | 2.998 | 98.1 | 79.5 | 1369 | 20.25 | 5806.9 | 3529.7 | 3558.1 | 5100.1 | 1190.9 | 0.67759 | 7.396
2024-12-09 | 15:32 | Data | 0 | 29.503 | 26.499 | 242.898 | 7.63 | 226.624 | 2105.93 | 26.03 | 40.581 | 6.28 | 1.529 | 5.867 | 8920.09 | 2.998 | 98.1 | 79.3 | 1369 | 20.25 | 5798.1 | 3533.9 | 3558.9 | 5107.5 | 1190.9 | 0.67709 | 7.398
2024-12-09 | 15:32 | Data | 0 | 29.814 | 26.715 | 242.989 | 7.63 | 226.804 | 2105.93 | 26.03 | 40.401 | 6.28 | 1.516 | 5.862 | 8938.18 | 3.22 | 98.1 | 79.5 | 1369 | 20.2 | 5809.8 | 3538.6 | 3559.2 | 5109.3 | 1190.9 | 0.67842 | 7.378
2024-12-09 | 15:32 | Data | 0 | 29.699 | 26.688 | 242.853 | 7.63 | 226.804 | 2105.03 | 26.01 | 40.672 | 6.28 | 1.518 | 5.866 | 8956.27 | 3.274 | 98.1 | 79.4 | 1368 | 20.34 | 5821.6 | 3540.8 | 3510.9 | 5076.5 | 1190.9 | 0.68284 | 7.384
2024-12-09 | 15:32 | Data | 0 | 29.503 | 26.499 | 242.627 | 7.63 | 226.533 | 2104.12 | 26 | 40.401 | 6.27 | 1.521 | 5.88 | 8978.88 | 3.004 | 98.1 | 79.4 | 1368 | 20.25 | 5836.3 | 3536 | 3546.1 | 5099.1 | 1190.9 | 0.679 | 7.401
2024-12-09 | 15:33 | Data | 0 | 29.53 | 26.701 | 243.034 | 7.63 | 226.669 | 2100.51 | 26.02 | 40.762 | 6.27 | 1.511 | 5.881 | 8978.88 | 2.829 | 98.1 | 79.6 | 1365 | 20.43 | 5836.3 | 3545.9 | 3534.2 | 5102.3 | 1190.9 | 0.68172 | 7.392
2024-12-09 | 15:33 | Data | 0 | 29.76 | 26.526 | 242.989 | 7.63 | 226.759 | 2101.41 | 26.01 | 40.581 | 6.28 | 1.523 | 5.895 | 9001.49 | 3.119 | 98.1 | 79.5 | 1366 | 20.38 | 5851 | 3552.8 | 3526.9 | 5102.5 | 1190.9 | 0.6802 | 7.418
2024-12-09 | 15:33 | Data | 0 | 29.503 | 26.499 | 242.853 | 7.63 | 226.714 | 2103.22 | 26.02 | 40.762 | 6.27 | 1.52 | 5.872 | 9015.06 | 3.004 | 98.1 | 79.4 | 1367 | 20.38 | 5859.8 | 3555.1 | 3553.6 | 5122.5 | 1190.9 | 0.68277 | 7.392
2024-12-09 | 15:33 | Data | 0 | 29.618 | 26.506 | 242.944 | 7.64 | 226.669 | 2101.41 | 26.02 | 40.581 | 6.27 | 1.507 | 5.878 | 8969.84 | 3.011 | 98.1 | 79.6 | 1365 | 20.34 | 5830.4 | 3553.9 | 3560 | 5120.1 | 1190.9 | 0.67925 | 7.386
2024-12-09 | 15:33 | Data | 0 | 30.009 | 26.789 | 242.944 | 7.63 | 226.85 | 2100.51 | 26.01 | 40.672 | 6.28 | 1.504 | 5.885 | 8974.36 | 2.903 | 98.1 | 79.6 | 1366 | 20.38 | 5833.3 | 3561.5 | 3578.8 | 5138.9 | 1190.9 | 0.6785 | 7.39
2024-12-09 | 15:33 | Data | 0 | 29.611 | 26.499 | 242.898 | 7.64 | 226.624 | 2104.12 | 26.01 | 40.852 | 6.28 | 1.513 | 5.878 | 8992.45 | 3.011 | 98.1 | 79.5 | 1368 | 20.38 | 5845.1 | 3550.7 | 3576.9 | 5130.8 | 1190.9 | 0.67684 | 7.391
2024-12-09 | 15:33 | Data | 0 | 29.955 | 26.573 | 243.034 | 7.63 | 226.714 | 2105.93 | 26.01 | 40.762 | 6.28 | 1.522 | 5.876 | 8965.31 | 3.2 | 98.1 | 79.4 | 1369 | 20.34 | 5827.5 | 3562.1 | 3585.1 | 5137.8 | 1190.9 | 0.67829 | 7.399
2024-12-09 | 15:33 | Data | 0 | 29.726 | 26.722 | 242.898 | 7.63 | 226.669 | 2105.93 | 26.02 | 40.762 | 6.27 | 1.51 | 5.866 | 9037.67 | 3.011 | 98.1 | 79.5 | 1368 | 20.38 | 5874.5 | 3567.8 | 3577.7 | 5145.2 | 1190.9 | 0.67863 | 7.375
2024-12-09 | 15:33 | Data | 0 | 29.53 | 26.303 | 242.718 | 7.63 | 226.669 | 2108.64 | 26.02 | 40.762 | 6.28 | 1.507 | 5.867 | 9051.24 | 2.998 | 98.1 | 79.6 | 1371 | 20.47 | 5883.3 | 3555.7 | 3564.8 | 5127.2 | 1190.9 | 0.67922 | 7.374
2024-12-09 | 15:33 | Data | 0 | 30.009 | 26.789 | 242.944 | 7.64 | 226.895 | 2106.83 | 26.02 | 40.762 | 6.28 | 1.517 | 5.867 | 9037.67 | 3.119 | 98.1 | 79.5 | 1369 | 20.34 | 5874.5 | 3626.4 | 3564.6 | 5180.1 | 1190.9 | 0.68508 | 7.385
2024-12-09 | 15:33 | Data | 0 | 29.773 | 26.728 | 243.125 | 7.63 | 226.804 | 2105.93 | 26.02 | 40.762 | 6.28 | 1.515 | 5.858 | 9046.71 | 3.004 | 98.1 | 79.5 | 1369 | 20.38 | 5880.4 | 3559.1 | 3571.4 | 5134.9 | 1190.9 | 0.67869 | 7.372
2024-12-09 | 15:33 | Data | 0 | 29.672 | 26.83 | 243.079 | 7.63 | 226.759 | 2106.83 | 26.02 | 40.762 | 6.28 | 1.521 | 5.88 | 8974.36 | 2.998 | 98.1 | 79.4 | 1369 | 20.38 | 5833.3 | 3572.7 | 3557.7 | 5135.6 | 1190.9 | 0.67904 | 7.401
2024-12-09 | 15:33 | Data | 0 | 29.868 | 26.506 | 242.853 | 7.63 | 226.85 | 2102.31 | 26.02 | 40.762 | 6.28 | 1.515 | 5.873 | 8974.36 | 3.031 | 98.1 | 79.5 | 1366 | 20.38 | 5833.3 | 3561.6 | 3570.1 | 5134.1 | 1190.9 | 0.68002 | 7.389
2024-12-09 | 15:33 | Data | 0 | 29.834 | 26.587 | 242.898 | 7.64 | 226.804 | 2106.83 | 26.02 | 40.672 | 6.27 | 1.505 | 5.878 | 8969.84 | 3.335 | 98.1 | 79.6 | 1369 | 20.34 | 5830.4 | 3572.7 | 3588 | 5157.5 | 1191 | 0.67791 | 7.385
2024-12-09 | 15:33 | Data | 0 | 29.517 | 26.674 | 242.944 | 7.63 | 226.714 | 2105.93 | 26.02 | 40.672 | 6.28 | 1.508 | 5.879 | 8969.84 | 2.937 | 98.1 | 79.6 | 1368 | 20.38 | 5830.4 | 3555.7 | 3587.5 | 5144.3 | 1191 | 0.6766 | 7.389
2024-12-09 | 15:33 | Data | 0 | 29.726 | 26.674 | 242.989 | 7.63 | 226.759 | 2105.93 | 26.02 | 40.672 | 6.27 | 1.521 | 5.894 | 9006.01 | 3.106 | 98.1 | 79.5 | 1369 | 20.34 | 5853.9 | 3565.4 | 3571.2 | 5139.2 | 1191 | 0.6784 | 7.414
2024-12-09 | 15:33 | Data | 0 | 29.712 | 26.728 | 243.034 | 7.63 | 226.714 | 2105.93 | 26.01 | 40.672 | 6.28 | 1.515 | 5.881 | 9033.15 | 3.119 | 98.1 | 79.5 | 1369 | 20.38 | 5871.5 | 3569 | 3560.1 | 5137.6 | 1191 | 0.67932 | 7.395
2024-12-09 | 15:33 | Data | 0 | 29.868 | 26.539 | 243.079 | 7.63 | 226.804 | 2105.03 | 26.02 | 40.762 | 6.28 | 1.52 | 5.874 | 9019.58 | 3.146 | 98.1 | 79.4 | 1369 | 20.38 | 5862.7 | 3547 | 3546.3 | 5112 | 1191 | 0.6779 | 7.395
2024-12-09 | 15:34 | Data | 0 | 29.915 | 26.728 | 243.17 | 7.63 | 226.669 | 2106.83 | 26.03 | 40.672 | 6.28 | 1.517 | 5.891 | 9037.67 | 3.214 | 98.1 | 79.5 | 1369 | 20.38 | 5874.5 | 3574.2 | 3563.1 | 5145.3 | 1191 | 0.67973 | 7.409
2024-12-09 | 15:34 | Data | 0 | 30.185 | 26.796 | 243.079 | 7.63 | 226.94 | 2106.83 | 26.02 | 40.762 | 6.27 | 1.525 | 5.894 | 9019.58 | 3.153 | 98.1 | 79.4 | 1369 | 20.38 | 5862.7 | 3563.6 | 3549.2 | 5125.4 | 1191 | 0.68013 | 7.418
2024-12-09 | 15:34 | Data | 0 | 29.503 | 26.283 | 242.898 | 7.63 | 226.804 | 2104.12 | 26.02 | 40.672 | 6.28 | 1.51 | 5.884 | 8992.45 | 3.214 | 98.1 | 79.6 | 1367 | 20.38 | 5845.1 | 3578.3 | 3541.2 | 5129.5 | 1191 | 0.68267 | 7.394
2024-12-09 | 15:34 | Data | 0 | 29.658 | 26.499 | 242.989 | 7.63 | 226.804 | 2104.12 | 26.01 | 40.762 | 6.27 | 1.517 | 5.873 | 9006.01 | 3.106 | 98.1 | 79.5 | 1367 | 20.34 | 5853.9 | 3574.9 | 3551.5 | 5131.5 | 1191 | 0.68291 | 7.39
2024-12-09 | 15:34 | Data | 0 | 30.111 | 26.796 | 242.989 | 7.63 | 226.759 | 2103.22 | 26.03 | 41.033 | 6.28 | 1.514 | 5.871 | 8996.97 | 3.058 | 98 | 79.5 | 1367 | 20.52 | 5848 | 3549.9 | 3593.3 | 5145.8 | 1191 | 0.67503 | 7.385
2024-12-09 | 15:34 | Data | 0 | 29.51 | 26.499 | 242.718 | 7.63 | 226.624 | 2103.22 | 26.02 | 40.852 | 6.28 | 1.518 | 5.872 | 9006.01 | 2.998 | 98.1 | 79.5 | 1368 | 20.34 | 5853.9 | 3558.3 | 3583.5 | 5147.8 | 1191 | 0.67585 | 7.389
2024-12-09 | 15:34 | Data | 0 | 29.996 | 26.587 | 242.989 | 7.63 | 226.714 | 2103.22 | 26.01 | 41.033 | 6.28 | 1.518 | 5.867 | 8987.93 | 3.274 | 98 | 79.4 | 1368 | 20.52 | 5842.2 | 3567.8 | 3585.4 | 5156.7 | 1191 | 0.67868 | 7.384
2024-12-09 | 15:34 | Data | 0 | 29.719 | 26.499 | 242.853 | 7.63 | 226.669 | 2104.12 | 26.02 | 40.762 | 6.28 | 1.515 | 5.873 | 8978.88 | 3.052 | 98.1 | 79.5 | 1367 | 20.38 | 5836.3 | 3561.8 | 3595.6 | 5155.8 | 1191 | 0.67612 | 7.388
2024-12-09 | 15:34 | Data | 0 | 29.942 | 26.566 | 242.944 | 7.63 | 226.759 | 2106.83 | 26.01 | 40.672 | 6.28 | 1.513 | 5.883 | 8983.4 | 3.065 | 98.1 | 79.5 | 1369 | 20.38 | 5839.2 | 3564.5 | 3594.8 | 5155.2 | 1191 | 0.67637 | 7.396
2024-12-09 | 15:34 | Data | 0 | 29.719 | 26.506 | 242.808 | 7.63 | 226.669 | 2103.22 | 26.03 | 40.762 | 6.28 | 1.513 | 5.892 | 8983.4 | 3.058 | 98.1 | 79.6 | 1368 | 20.38 | 5839.2 | 3491.8 | 3564.6 | 5079.6 | 1191 | 0.67332 | 7.405
2024-12-09 | 15:34 | Data | 0 | 29.739 | 26.688 | 242.898 | 7.63 | 226.624 | 2101.41 | 26.02 | 40.762 | 6.28 | 1.516 | 5.916 | 8965.31 | 3.153 | 98.1 | 79.6 | 1366 | 20.34 | 5827.5 | 3505.1 | 3534.8 | 5065.1 | 1191 | 0.67816 | 7.432
2024-12-09 | 15:34 | Data | 0 | 29.814 | 26.722 | 242.763 | 7.63 | 226.759 | 2099.6 | 26.03 | 40.762 | 6.27 | 1.519 | 5.866 | 8978.88 | 3.166 | 98.1 | 79.4 | 1365 | 20.38 | 5836.3 | 3488.7 | 3542.6 | 5057.7 | 1191 | 0.67244 | 7.386
2024-12-09 | 15:34 | Data | 0 | 30.171 | 26.519 | 242.853 | 7.63 | 226.85 | 2101.41 | 26.01 | 40.672 | 6.28 | 1.52 | 5.873 | 8978.88 | 3.227 | 98.1 | 79.4 | 1366 | 20.34 | 5836.3 | 3503.6 | 3552.8 | 5078.6 | 1191 | 0.67557 | 7.393
2024-12-09 | 15:34 | Data | 0 | 29.955 | 26.735 | 243.125 | 7.64 | 226.804 | 2101.41 | 26.01 | 40.762 | 6.27 | 1.51 | 5.898 | 9006.01 | 3.214 | 98.1 | 79.6 | 1366 | 20.38 | 5853.9 | 3508.2 | 3566.8 | 5091.6 | 1191 | 0.67488 | 7.408
2024-12-09 | 15:34 | Data | 0 | 29.922 | 26.519 | 243.079 | 7.63 | 226.85 | 2101.41 | 26.02 | 40.852 | 6.28 | 1.512 | 5.9 | 9033.15 | 3.011 | 98.1 | 79.6 | 1366 | 20.43 | 5871.5 | 3496.5 | 3544.7 | 5071 | 1191 | 0.67473 | 7.412
2024-12-09 | 15:34 | Data | 0 | 29.685 | 26.391 | 242.989 | 7.63 | 226.804 | 2104.12 | 26.02 | 40.672 | 6.28 | 1.512 | 5.863 | 9019.58 | 3.403 | 98.1 | 79.5 | 1367 | 20.34 | 5862.7 | 3496.2 | 3541.4 | 5074.7 | 1191 | 0.67627 | 7.374
2024-12-09 | 15:34 | Data | 0 | 29.503 | 26.715 | 242.944 | 7.64 | 226.669 | 2104.12 | 26.02 | 40.762 | 6.28 | 1.504 | 5.876 | 9019.58 | 2.782 | 98.1 | 79.6 | 1367 | 20.34 | 5862.7 | 3472.7 | 3555.7 | 5059.1 | 1191 | 0.6719 | 7.38
2024-12-09 | 15:34 | Data | 0 | 30.144 | 26.573 | 243.079 | 7.64 | 226.759 | 2100.51 | 26.02 | 40.762 | 6.27 | 1.52 | 5.848 | 9024.1 | 3.22 | 98.1 | 79.4 | 1366 | 20.34 | 5865.7 | 3487.7 | 3570.8 | 5075.4 | 1191 | 0.67133 | 7.371
2024-12-09 | 15:35 | Data | 0 | 29.706 | 26.843 | 242.989 | 7.63 | 226.714 | 2104.12 | 26.01 | 40.762 | 6.28 | 1.524 | 5.879 | 9001.49 | 3.2 | 98.1 | 79.4 | 1368 | 20.38 | 5851 | 3555.2 | 3590.5 | 5146.9 | 1191 | 0.67715 | 7.402
2024-12-09 | 15:35 | Data | 0 | 29.604 | 26.654 | 242.808 | 7.64 | 226.714 | 2104.12 | 26.02 | 40.672 | 6.28 | 1.521 | 5.885 | 8992.45 | 3.22 | 98.1 | 79.5 | 1368 | 20.34 | 5845.1 | 3559.2 | 3579.2 | 5138 | 1191 | 0.67829 | 7.407
2024-12-09 | 15:35 | Data | 0 | 29.814 | 26.722 | 243.079 | 7.63 | 226.759 | 2104.12 | 26.02 | 40.762 | 6.28 | 1.52 | 5.892 | 8996.97 | 3.173 | 98.1 | 79.5 | 1368 | 20.38 | 5848 | 3558.8 | 3582.4 | 5142.5 | 1191 | 0.67687 | 7.412
2024-12-09 | 15:35 | Data | 0 | 29.652 | 26.492 | 242.808 | 7.63 | 226.624 | 2104.12 | 26.02 | 40.672 | 6.28 | 1.512 | 5.888 | 9001.49 | 3.227 | 98.1 | 79.6 | 1368 | 20.38 | 5851 | 3550.2 | 3555.2 | 5122.1 | 1191 | 0.68008 | 7.401
2024-12-09 | 15:35 | Data | 0 | 29.793 | 26.614 | 242.944 | 7.63 | 226.759 | 2103.22 | 26.01 | 40.672 | 6.28 | 1.518 | 5.879 | 8996.97 | 3.004 | 98.1 | 79.5 | 1367 | 20.38 | 5848 | 3538.9 | 3564.4 | 5117.6 | 1191 | 0.67948 | 7.397
2024-12-09 | 15:35 | Data | 0 | 29.422 | 26.384 | 242.763 | 7.63 | 226.578 | 2104.12 | 26.02 | 40.762 | 6.28 | 1.505 | 5.914 | 9010.54 | 3.011 | 98.1 | 79.7 | 1367 | 20.38 | 5856.8 | 3545.7 | 3561 | 5116.9 | 1191 | 0.67832 | 7.418
2024-12-09 | 15:35 | Data | 0 | 29.584 | 26.816 | 242.944 | 7.64 | 226.669 | 2104.12 | 26.02 | 40.581 | 6.27 | 1.511 | 5.911 | 9006.01 | 3.207 | 98.1 | 79.6 | 1368 | 20.38 | 5853.9 | 3560 | 3570.4 | 5136.3 | 1191 | 0.67856 | 7.422
2024-12-09 | 15:35 | Data | 0 | 29.49 | 26.384 | 242.718 | 7.63 | 226.488 | 2098.7 | 26.02 | 40.672 | 6.27 | 1.52 | 5.893 | 8996.97 | 3.22 | 98.1 | 79.5 | 1364 | 20.34 | 5848 | 3549.5 | 3566.5 | 5128.6 | 1191.1 | 0.67802 | 7.413
2024-12-09 | 15:35 | Data | 0 | 29.726 | 26.843 | 242.853 | 7.63 | 226.759 | 2103.22 | 26.02 | 40.852 | 6.28 | 1.519 | 5.879 | 9001.49 | 3.085 | 98.1 | 79.5 | 1367 | 20.38 | 5851 | 3544.4 | 3539.7 | 5101.8 | 1191.1 | 0.68156 | 7.399
2024-12-09 | 15:35 | Data | 0 | 29.517 | 26.607 | 242.898 | 7.64 | 226.714 | 2098.7 | 26.01 | 40.762 | 6.27 | 1.518 | 5.879 | 9006.01 | 2.829 | 98.1 | 79.5 | 1364 | 20.43 | 5853.9 | 3526.5 | 3560.3 | 5103.3 | 1191.1 | 0.67624 | 7.399
2024-12-09 | 15:35 | Data | 0 | 29.881 | 26.634 | 242.944 | 7.64 | 226.624 | 2096.89 | 26.02 | 40.672 | 6.28 | 1.516 | 5.873 | 9006.01 | 3.052 | 98.1 | 79.5 | 1363 | 20.43 | 5853.9 | 3532.9 | 3562.2 | 5108.2 | 1191.1 | 0.67646 | 7.39
2024-12-09 | 15:35 | Data | 0 | 30.003 | 26.782 | 242.944 | 7.63 | 226.804 | 2099.6 | 26.02 | 40.852 | 6.27 | 1.515 | 5.873 | 8996.97 | 3.018 | 98.1 | 79.5 | 1365 | 20.34 | 5848 | 3549.5 | 3579.5 | 5132.4 | 1191.1 | 0.67744 | 7.389
2024-12-09 | 15:35 | Data | 0 | 29.287 | 26.6 | 242.808 | 7.64 | 226.669 | 2098.7 | 26.03 | 40.672 | 6.27 | 1.518 | 5.866 | 9033.15 | 2.91 | 98.1 | 79.4 | 1364 | 20.34 | 5871.5 | 3556.4 | 3567 | 5128.9 | 1191.1 | 0.67848 | 7.386
2024-12-09 | 15:35 | Data | 0 | 29.496 | 26.269 | 242.898 | 7.64 | 226.624 | 2100.51 | 26.02 | 40.762 | 6.28 | 1.52 | 5.846 | 9051.24 | 3.227 | 98.1 | 79.4 | 1366 | 20.38 | 5883.3 | 3549.6 | 3568.9 | 5129.2 | 1191.1 | 0.67693 | 7.365
2024-12-09 | 15:35 | Data | 0 | 29.712 | 26.526 | 242.898 | 7.63 | 226.669 | 2099.6 | 26.03 | 40.672 | 6.28 | 1.523 | 5.863 | 9037.67 | 3.106 | 98.1 | 79.4 | 1365 | 20.38 | 5874.5 | 3545.5 | 3556.2 | 5113.3 | 1191.1 | 0.67888 | 7.384
2024-12-09 | 15:35 | Data | 0 | 29.564 | 26.499 | 243.034 | 7.64 | 226.624 | 2099.6 | 26.02 | 40.762 | 6.27 | 1.515 | 5.885 | 9051.24 | 2.809 | 98.1 | 79.5 | 1365 | 20.38 | 5883.3 | 3563.9 | 3568.7 | 5136 | 1191.1 | 0.67858 | 7.399
2024-12-09 | 15:35 | Data | 0 | 29.382 | 26.384 | 242.944 | 7.63 | 226.488 | 2101.41 | 26.02 | 40.762 | 6.28 | 1.524 | 5.876 | 9024.1 | 3.335 | 98.1 | 79.4 | 1366 | 20.38 | 5865.7 | 3560.5 | 3565.8 | 5124.8 | 1191.1 | 0.6775 | 7.401
2024-12-09 | 15:36 | Data | 0 | 29.773 | 26.418 | 242.808 | 7.63 | 226.759 | 2099.6 | 26.02 | 40.762 | 6.28 | 1.524 | 5.868 | 8992.45 | 3.139 | 98.1 | 79.4 | 1365 | 20.38 | 5845.1 | 3551.8 | 3571.9 | 5129.8 | 1191.1 | 0.67804 | 7.391
2024-12-09 | 15:36 | Data | 0 | 29.172 | 26.411 | 242.898 | 7.63 | 226.669 | 2100.51 | 26.02 | 40.762 | 6.27 | 1.515 | 5.864 | 9006.01 | 3.018 | 98.1 | 79.5 | 1366 | 20.43 | 5853.9 | 3548.9 | 3554.3 | 5090.1 | 1191.1 | 0.68037 | 7.38
2024-12-09 | 15:36 | Data | 0 | 28.639 | 25.601 | 242.31 | 7.63 | 226.126 | 2101.41 | 26.02 | 40.762 | 6.28 | 1.524 | 5.894 | 9001.49 | 2.977 | 98.1 | 79.4 | 1365 | 20.34 | 5851 | 3532.3 | 3559.9 | 5108.1 | 1191.1 | 0.67747 | 7.418
2024-12-09 | 15:36 | Data | 0 | 28.767 | 25.155 | 241.994 | 7.64 | 225.855 | 2098.7 | 26.03 | 40.672 | 6.28 | 1.522 | 5.89 | 9006.01 | 3.052 | 98.1 | 79.5 | 1363 | 20.38 | 5853.9 | 3543.6 | 3533 | 5089.4 | 1191.1 | 0.6804 | 7.411
2024-12-09 | 15:36 | Data | 0 | 28.848 | 25.587 | 242.084 | 7.64 | 226.036 | 2101.41 | 26.02 | 40.762 | 6.28 | 1.52 | 5.873 | 9033.15 | 3.241 | 98.1 | 79.4 | 1365 | 20.43 | 5871.5 | 3538 | 3572.5 | 5119.8 | 1191.1 | 0.67841 | 7.393
2024-12-09 | 15:36 | Data | 0 | 28.457 | 25.358 | 242.084 | 7.64 | 225.855 | 2101.41 | 26.01 | 40.762 | 6.28 | 1.511 | 5.867 | 9033.15 | 3.18 | 98.1 | 79.5 | 1365 | 20.38 | 5871.5 | 3542.6 | 3553 | 5109.2 | 1191.1 | 0.67906 | 7.379
2024-12-09 | 15:36 | Data | 0 | 28.349 | 25.668 | 236.249 | 7.64 | 220.703 | 2102.31 | 26.02 | 40.762 | 6.28 | 1.515 | 5.848 | 9037.67 | 2.876 | 98.1 | 79.4 | 1367 | 20.34 | 5874.5 | 3492.7 | 3503.1 | 5040.8 | 1191.1 | 0.67735 | 7.362
2024-12-09 | 15:36 | Data | 0 | 28.517 | 25.83 | 225.213 | 7.64 | 210.489 | 2100.51 | 26.05 | 40.672 | 6.27 | 1.493 | 5.745 | 9033.15 | 2.667 | 98.1 | 79.4 | 1366 | 20.34 | 5871.5 | 3363.9 | 3373.1 | 4862.5 | 1191.1 | 0.67569 | 7.239
2024-12-09 | 15:36 | Data | 0 | 29.199 | 26.323 | 216.076 | 7.64 | 202.309 | 2104.12 | 26.07 | 40.491 | 6.28 | 1.464 | 5.504 | 9015.06 | 2.647 | 98.1 | 79 | 1368 | 20.2 | 5859.8 | 3254.3 | 3257 | 4712.3 | 1191.1 | 0.67587 | 6.97
2024-12-09 | 15:36 | Data | 0 | 28.875 | 26.465 | 209.426 | 7.64 | 196.253 | 2104.12 | 26.06 | 40.762 | 6.28 | 1.446 | 5.307 | 9019.58 | 2.484 | 98.1 | 78.6 | 1367 | 20.34 | 5862.7 | 3180.5 | 3210.5 | 4626.5 | 1191.1 | 0.66888 | 6.752
2024-12-09 | 15:36 | Data | 0 | 29.604 | 26.823 | 204.496 | 7.64 | 191.508 | 2103.22 | 26.07 | 40.943 | 6.29 | 1.419 | 5.172 | 9006.01 | 2.451 | 98 | 78.5 | 1368 | 20.52 | 5853.9 | 3123.8 | 3154.8 | 4548 | 1191.1 | 0.66806 | 6.59
2024-12-09 | 15:36 | Data | 0 | 29.854 | 27.322 | 200.832 | 7.64 | 188.299 | 2106.83 | 26.06 | 41.755 | 6.29 | 1.406 | 5.088 | 8992.45 | 2.248 | 98 | 78.3 | 1369 | 20.88 | 5845.1 | 3062.9 | 3122.7 | 4494.2 | 1191.1 | 0.66753 | 6.495
2024-12-09 | 15:36 | Data | 0 | 29.726 | 27.046 | 197.168 | 7.64 | 184.955 | 2108.64 | 26.06 | 42.026 | 6.3 | 1.391 | 4.977 | 8969.84 | 2.43 | 98 | 78.2 | 1370 | 21.06 | 5830.4 | 3043.4 | 3081 | 4439.1 | 1191.1 | 0.66856 | 6.368
2024-12-09 | 15:36 | Data | 0 | 28.45 | 26.08 | 194.228 | 7.64 | 182.334 | 2109.54 | 26.06 | 42.929 | 6.3 | 1.386 | 4.891 | 8929.14 | 2.194 | 98 | 77.9 | 1371 | 21.42 | 5803.9 | 3007.9 | 3037 | 4386.9 | 1191.1 | 0.66984 | 6.279
2024-12-09 | 15:36 | Data | 0 | 28.99 | 26.951 | 193.007 | 7.64 | 181.294 | 2111.35 | 26.07 | 43.29 | 6.31 | 1.377 | 4.865 | 8902 | 2.093 | 98 | 78 | 1373 | 21.64 | 5786.3 | 2985.3 | 3005.8 | 4352.9 | 1191.1 | 0.6694 | 6.241
2024-12-09 | 15:36 | Data | 0 | 30.07 | 27.883 | 192.057 | 7.65 | 180.39 | 2113.16 | 26.07 | 43.922 | 6.31 | 1.372 | 4.87 | 8856.78 | 2.289 | 97.9 | 78 | 1374 | 21.92 | 5756.9 | 2984.9 | 3007.9 | 4349.3 | 1191.1 | 0.66837 | 6.242
2024-12-09 | 15:36 | Data | 0 | 30.063 | 27.775 | 190.881 | 7.64 | 179.215 | 2112.26 | 26.08 | 44.102 | 6.32 | 1.366 | 4.813 | 8838.69 | 2.295 | 97.9 | 77.9 | 1373 | 22.05 | 5745.1 | 2970 | 2973.6 | 4319.2 | 1191.1 | 0.67055 | 6.179
2024-12-09 | 15:36 | Data | 0 | 29.037 | 26.938 | 189.796 | 7.64 | 178.221 | 2112.26 | 26.08 | 44.734 | 6.32 | 1.355 | 4.768 | 8816.08 | 2.174 | 97.9 | 77.9 | 1372 | 22.41 | 5730.5 | 2992.6 | 2951.3 | 4317 | 1191.1 | 0.67565 | 6.123
2024-12-09 | 15:37 | Data | 0 | 29.557 | 27.538 | 190.338 | 7.64 | 178.718 | 2111.35 | 26.08 | 45.186 | 6.33 | 1.358 | 4.745 | 8797.99 | 2.194 | 97.9 | 77.8 | 1372 | 22.46 | 5718.7 | 2964.1 | 2962.9 | 4302.6 | 1191.1 | 0.67066 | 6.102
2024-12-09 | 15:37 | Data | 0 | 30.117 | 27.93 | 190.564 | 7.64 | 178.899 | 2112.26 | 26.08 | 45.186 | 6.34 | 1.358 | 4.746 | 8761.81 | 2.079 | 97.9 | 77.8 | 1373 | 22.64 | 5695.2 | 2982 | 2972 | 4322.8 | 1191.1 | 0.67244 | 6.104
2024-12-09 | 15:37 | Data | 0 | 30.32 | 27.802 | 190.881 | 7.65 | 179.08 | 2116.78 | 26.08 | 45.457 | 6.34 | 1.352 | 4.744 | 8743.73 | 2.309 | 97.9 | 77.8 | 1376 | 22.73 | 5683.4 | 2957.7 | 2982.1 | 4314.9 | 1191.1 | 0.66821 | 6.097
2024-12-09 | 15:37 | Data | 0 | 30.259 | 28.112 | 190.745 | 7.65 | 179.215 | 2117.68 | 26.08 | 45.727 | 6.33 | 1.356 | 4.787 | 8730.16 | 1.998 | 97.8 | 77.9 | 1377 | 22.86 | 5674.6 | 2974.8 | 2972.7 | 4312.8 | 1191.1 | 0.66891 | 6.143
2024-12-09 | 15:37 | Data | 0 | 30.671 | 28.349 | 190.926 | 7.65 | 179.261 | 2116.78 | 26.08 | 45.727 | 6.34 | 1.369 | 4.776 | 8730.16 | 2.093 | 97.8 | 77.7 | 1375 | 22.86 | 5674.6 | 2944.5 | 2977.6 | 4297.3 | 1191.2 | 0.66999 | 6.146
2024-12-09 | 15:37 | Data | 0 | 30.651 | 28.457 | 190.7 | 7.64 | 178.989 | 2117.68 | 26.08 | 45.637 | 6.34 | 1.376 | 4.815 | 8707.55 | 2.079 | 97.8 | 77.8 | 1376 | 22.82 | 5659.9 | 2969.1 | 2988.9 | 4325.3 | 1191.2 | 0.66806 | 6.189
2024-12-09 | 15:37 | Data | 0 | 30.462 | 28.349 | 190.022 | 7.65 | 178.447 | 2113.16 | 26.08 | 45.998 | 6.35 | 1.36 | 4.785 | 8639.71 | 2.066 | 97.8 | 77.9 | 1373 | 23 | 5615.8 | 2942.6 | 2983 | 4304.8 | 1191.2 | 0.66546 | 6.146
2024-12-09 | 15:37 | Data | 0 | 30.759 | 28.673 | 189.886 | 7.65 | 178.312 | 2117.68 | 26.08 | 45.998 | 6.35 | 1.353 | 4.771 | 8621.63 | 2.194 | 97.8 | 77.9 | 1376 | 22.95 | 5604.1 | 2954.8 | 2990.1 | 4319.1 | 1191.2 | 0.66775 | 6.124
2024-12-09 | 15:37 | Data | 0 | 30.55 | 28.544 | 189.886 | 7.65 | 178.357 | 2118.58 | 26.08 | 45.998 | 6.35 | 1.36 | 4.782 | 8608.06 | 2.16 | 97.8 | 77.9 | 1377 | 23 | 5595.2 | 2964.2 | 2964.2 | 4304.2 | 1191.2 | 0.66785 | 6.142
2024-12-09 | 15:37 | Data | 0 | 31.083 | 28.693 | 190.203 | 7.65 | 178.538 | 2116.78 | 26.08 | 45.998 | 6.34 | 1.358 | 4.768 | 8594.49 | 2.289 | 97.8 | 77.8 | 1376 | 23.04 | 5586.4 | 2958 | 2939.8 | 4280.5 | 1191.2 | 0.67461 | 6.124
2024-12-09 | 15:37 | Data | 0 | 30.826 | 28.781 | 190.112 | 7.65 | 178.447 | 2118.58 | 26.08 | 46.179 | 6.35 | 1.364 | 4.775 | 8580.93 | 2.133 | 97.8 | 77.8 | 1376 | 22.95 | 5577.6 | 2944 | 2947.6 | 4280.5 | 1191.2 | 0.66995 | 6.138
2024-12-09 | 15:37 | Data | 0 | 30.995 | 28.814 | 190.157 | 7.65 | 178.583 | 2117.68 | 26.08 | 45.908 | 6.35 | 1.357 | 4.791 | 8567.36 | 2.093 | 97.8 | 77.9 | 1376 | 23 | 5568.8 | 2934 | 2942.3 | 4271 | 1191.2 | 0.66933 | 6.149
2024-12-09 | 15:37 | Data | 0 | 30.198 | 28.288 | 189.705 | 7.65 | 178.176 | 2117.68 | 26.08 | 46.089 | 6.35 | 1.36 | 4.776 | 8562.84 | 2.282 | 97.8 | 77.8 | 1376 | 23 | 5565.8 | 2946.5 | 2952.2 | 4285 | 1191.2 | 0.67061 | 6.137
2024-12-09 | 15:37 | Data | 0 | 30.469 | 28.328 | 189.976 | 7.65 | 178.221 | 2117.68 | 26.07 | 46.089 | 6.35 | 1.363 | 4.751 | 8553.79 | 2.1 | 97.8 | 77.7 | 1376 | 23.04 | 5560 | 2937.2 | 2937.3 | 4267.3 | 1191.2 | 0.67099 | 6.113
2024-12-09 | 15:37 | Data | 0 | 30.658 | 28.342 | 190.067 | 7.65 | 178.402 | 2120.39 | 26.08 | 45.998 | 6.35 | 1.355 | 4.771 | 8585.45 | 2.1 | 97.8 | 77.9 | 1378 | 23 | 5580.5 | 2948.6 | 2956.1 | 4288.5 | 1191.2 | 0.67014 | 6.126
2024-12-09 | 15:37 | Data | 0 | 30.185 | 28.288 | 189.796 | 7.65 | 178.086 | 2114.97 | 26.08 | 45.818 | 6.35 | 1.346 | 4.78 | 8562.84 | 2.073 | 97.8 | 78 | 1375 | 22.91 | 5565.8 | 2939.5 | 2944.2 | 4278.2 | 1191.2 | 0.66902 | 6.126
2024-12-09 | 15:37 | Data | 0 | 30.307 | 28.619 | 190.022 | 7.65 | 178.176 | 2118.58 | 26.08 | 45.998 | 6.35 | 1.356 | 4.788 | 8567.36 | 2.147 | 97.8 | 77.9 | 1378 | 22.95 | 5568.8 | 2952.1 | 2962.9 | 4294.7 | 1191.2 | 0.66962 | 6.144
2024-12-09 | 15:38 | Data | 0 | 30.732 | 28.571 | 189.886 | 7.65 | 178.131 | 2119.49 | 26.08 | 45.908 | 6.35 | 1.357 | 4.769 | 8531.18 | 2.093 | 97.8 | 77.9 | 1379 | 22.95 | 5545.3 | 2941.8 | 2953.9 | 4283.9 | 1191.2 | 0.66794 | 6.126
2024-12-09 | 15:38 | Data | 0 | 30.415 | 28.558 | 190.022 | 7.65 | 178.221 | 2116.78 | 26.08 | 45.908 | 6.35 | 1.356 | 4.77 | 8499.53 | 2.133 | 97.8 | 77.9 | 1376 | 22.95 | 5524.7 | 2923 | 2954.6 | 4273.9 | 1191.2 | 0.66546 | 6.126
2024-12-09 | 15:38 | Data | 0 | 30.516 | 28.342 | 189.705 | 7.65 | 178.131 | 2117.68 | 26.08 | 45.818 | 6.35 | 1.364 | 4.79 | 8522.14 | 2.262 | 97.8 | 77.8 | 1377 | 22.95 | 5539.4 | 2958 | 2959.3 | 4300.5 | 1191.2 | 0.66911 | 6.154
2024-12-09 | 15:38 | Data | 0 | 31.022 | 28.7 | 190.022 | 7.65 | 178.221 | 2117.68 | 26.08 | 45.818 | 6.35 | 1.361 | 4.779 | 8485.96 | 2.383 | 97.8 | 77.8 | 1376 | 22.86 | 5515.9 | 2956.6 | 2951.9 | 4293.8 | 1191.2 | 0.67155 | 6.14
2024-12-09 | 15:38 | Data | 0 | 30.469 | 28.342 | 189.886 | 7.65 | 178.176 | 2117.68 | 26.08 | 45.818 | 6.36 | 1.356 | 4.777 | 8481.44 | 2.079 | 97.8 | 77.9 | 1376 | 22.86 | 5512.9 | 2954.3 | 2940 | 4279.6 | 1191.2 | 0.67222 | 6.133
2024-12-09 | 15:38 | Data | 0 | 30.617 | 28.463 | 189.886 | 7.65 | 178.176 | 2114.97 | 26.08 | 45.818 | 6.35 | 1.352 | 4.759 | 8485.96 | 2.275 | 97.8 | 77.9 | 1374 | 22.91 | 5515.9 | 2948.3 | 2922.1 | 4266.9 | 1191.2 | 0.67291 | 6.11
2024-12-09 | 15:38 | Data | 0 | 30.509 | 28.349 | 190.203 | 7.65 | 178.402 | 2111.35 | 26.08 | 45.637 | 6.36 | 1.348 | 4.745 | 8472.39 | 1.985 | 97.8 | 77.9 | 1372 | 22.86 | 5507.1 | 2939.3 | 2941.3 | 4272.7 | 1191.2 | 0.67077 | 6.093
2024-12-09 | 15:38 | Data | 0 | 30.637 | 28.774 | 190.067 | 7.65 | 178.312 | 2112.26 | 26.08 | 45.637 | 6.35 | 1.353 | 4.78 | 8463.35 | 2.079 | 97.8 | 78 | 1372 | 22.91 | 5501.2 | 2951.6 | 2962.8 | 4296.7 | 1191.2 | 0.66886 | 6.132
2024-12-09 | 15:38 | Data | 0 | 30.685 | 28.517 | 190.067 | 7.66 | 178.402 | 2111.35 | 26.08 | 45.727 | 6.35 | 1.352 | 4.749 | 8449.78 | 2.14 | 97.8 | 77.9 | 1372 | 22.91 | 5492.4 | 2943.8 | 2932.3 | 4267.8 | 1191.2 | 0.67268 | 6.104
2024-12-09 | 15:38 | Data | 0 | 30.644 | 28.342 | 189.976 | 7.65 | 178.176 | 2108.64 | 26.08 | 45.818 | 6.35 | 1.362 | 4.757 | 8472.39 | 2.302 | 97.8 | 77.7 | 1371 | 22.86 | 5507.1 | 2943.6 | 2985.9 | 4306.8 | 1191.2 | 0.66471 | 6.119
2024-12-09 | 15:38 | Data | 0 | 30.766 | 28.747 | 190.112 | 7.65 | 178.357 | 2114.06 | 26.08 | 45.637 | 6.35 | 1.372 | 4.764 | 8458.83 | 2.12 | 97.8 | 77.6 | 1374 | 22.82 | 5498.2 | 2936.9 | 2965.1 | 4290.5 | 1191.2 | 0.66693 | 6.135
2024-12-09 | 15:38 | Data | 0 | 30.651 | 28.544 | 190.112 | 7.65 | 178.357 | 2112.26 | 26.08 | 45.727 | 6.35 | 1.357 | 4.748 | 8436.21 | 2.181 | 97.8 | 77.8 | 1375 | 22.86 | 5483.5 | 2951.7 | 2974.6 | 4302.6 | 1191.2 | 0.66857 | 6.104
2024-12-09 | 15:38 | Data | 0 | 30.874 | 28.76 | 190.067 | 7.65 | 178.402 | 2109.54 | 26.08 | 45.727 | 6.36 | 1.348 | 4.769 | 8440.74 | 2.214 | 97.8 | 78 | 1371 | 22.86 | 5486.5 | 2942.7 | 2975.5 | 4296.6 | 1191.2 | 0.66729 | 6.116
2024-12-09 | 15:38 | Data | 0 | 30.651 | 28.673 | 190.157 | 7.65 | 178.312 | 2114.06 | 26.08 | 45.727 | 6.35 | 1.345 | 4.767 | 8422.65 | 2.133 | 97.8 | 78 | 1374 | 22.86 | 5474.7 | 2928.4 | 2956.1 | 4273.4 | 1191.2 | 0.66833 | 6.111
2024-12-09 | 15:38 | Data | 0 | 30.88 | 28.652 | 190.067 | 7.66 | 178.447 | 2112.26 | 26.08 | 45.457 | 6.34 | 1.353 | 4.762 | 8390.99 | 2.039 | 97.8 | 77.9 | 1372 | 22.77 | 5454.1 | 2932.6 | 2944.8 | 4272.4 | 1191.2 | 0.66882 | 6.117
2024-12-09 | 15:38 | Data | 0 | 30.874 | 28.369 | 189.976 | 7.65 | 178.312 | 2114.97 | 26.08 | 45.276 | 6.35 | 1.353 | 4.779 | 8395.51 | 2.275 | 97.9 | 77.9 | 1374 | 22.64 | 5457.1 | 2947.3 | 2936.1 | 4274.7 | 1191.2 | 0.67287 | 6.132
2024-12-09 | 15:38 | Data | 0 | 30.826 | 28.781 | 190.112 | 7.65 | 178.447 | 2112.26 | 26.08 | 45.457 | 6.35 | 1.357 | 4.746 | 8377.43 | 2.167 | 97.8 | 77.8 | 1372 | 22.73 | 5445.3 | 2954.7 | 2923.9 | 4268.1 | 1191.2 | 0.67408 | 6.102
2024-12-09 | 15:38 | Data | 0 | 30.421 | 28.457 | 189.886 | 7.65 | 178.312 | 2109.54 | 26.08 | 45.457 | 6.35 | 1.369 | 4.756 | 8395.51 | 2.079 | 97.8 | 77.6 | 1371 | 22.68 | 5457.1 | 2938.8 | 2933.1 | 4266.6 | 1191.2 | 0.67136 | 6.125
2024-12-09 | 15:38 | Data | 0 | 30.887 | 28.571 | 190.157 | 7.66 | 178.357 | 2107.74 | 26.08 | 45.366 | 6.35 | 1.363 | 4.787 | 8386.47 | 2.14 | 97.8 | 77.8 | 1369 | 22.73 | 5451.2 | 2943.8 | 2930.8 | 4269 | 1191.2 | 0.6717 | 6.15
2024-12-09 | 15:39 | Data | 0 | 30.408 | 28.389 | 189.886 | 7.66 | 178.176 | 2105.03 | 26.08 | 45.457 | 6.35 | 1.358 | 4.773 | 8386.47 | 2.12 | 97.8 | 77.9 | 1368 | 22.73 | 5451.2 | 2941.6 | 2942.7 | 4272.1 | 1191.2 | 0.67127 | 6.13
2024-12-09 | 15:39 | Data | 0 | 30.252 | 28.146 | 189.886 | 7.66 | 178.357 | 2107.74 | 26.08 | 45.457 | 6.35 | 1.361 | 4.773 | 8390.99 | 2.127 | 97.8 | 77.8 | 1369 | 22.73 | 5454.1 | 2938 | 2933.2 | 4266.7 | 1191.2 | 0.67117 | 6.134
2024-12-09 | 15:39 | Data | 0 | 30.192 | 28.092 | 189.796 | 7.65 | 178.131 | 2109.54 | 26.08 | 45.457 | 6.35 | 1.346 | 4.765 | 8363.86 | 2.093 | 97.8 | 78 | 1371 | 22.77 | 5436.5 | 2955.4 | 2958.7 | 4294.9 | 1191.2 | 0.67095 | 6.111
2024-12-09 | 15:39 | Data | 0 | 29.834 | 27.944 | 189.569 | 7.66 | 178.086 | 2109.54 | 26.08 | 45.366 | 6.35 | 1.358 | 4.749 | 8386.47 | 1.877 | 97.8 | 77.8 | 1371 | 22.73 | 5451.2 | 2947.4 | 2943.9 | 4281.5 | 1191.2 | 0.67131 | 6.108
2024-12-09 | 15:39 | Data | 0 | 30.88 | 28.578 | 190.022 | 7.66 | 178.357 | 2111.35 | 26.08 | 45.457 | 6.35 | 1.354 | 4.765 | 8386.47 | 2.187 | 97.8 | 77.9 | 1372 | 22.73 | 5451.2 | 2945.9 | 2936 | 4271.3 | 1191.3 | 0.67213 | 6.119
2024-12-09 | 15:39 | Data | 0 | 30.043 | 27.89 | 189.705 | 7.65 | 177.995 | 2111.35 | 26.08 | 45.457 | 6.35 | 1.358 | 4.757 | 8390.99 | 2.073 | 97.9 | 77.8 | 1372 | 22.73 | 5454.1 | 2940.6 | 2943.5 | 4271.4 | 1191.3 | 0.671 | 6.114
2024-12-09 | 15:39 | Data | 0 | 29.949 | 27.444 | 189.298 | 7.66 | 177.724 | 2114.06 | 26.08 | 45.457 | 6.35 | 1.366 | 4.737 | 8386.47 | 2.289 | 97.9 | 77.6 | 1374 | 22.73 | 5451.2 | 2935 | 2904 | 4241.5 | 1191.3 | 0.67359 | 6.103
2024-12-09 | 15:39 | Data | 0 | 29.085 | 26.762 | 188.665 | 7.66 | 177.182 | 2113.16 | 26.08 | 45.547 | 6.35 | 1.363 | 4.733 | 8400.04 | 2.194 | 97.8 | 77.6 | 1374 | 22.73 | 5460 | 2945.4 | 2909 | 4251.5 | 1191.3 | 0.67588 | 6.095
2024-12-09 | 15:39 | Data | 0 | 29.935 | 27.775 | 189.343 | 7.65 | 177.724 | 2114.06 | 26.08 | 45.637 | 6.35 | 1.351 | 4.74 | 8386.47 | 2.275 | 97.8 | 77.8 | 1374 | 22.82 | 5451.2 | 2950 | 2905.3 | 4253.7 | 1191.3 | 0.67673 | 6.092
2024-12-09 | 15:39 | Data | 0 | 30.192 | 28.2 | 189.75 | 7.65 | 178.04 | 2106.83 | 26.08 | 45.727 | 6.35 | 1.357 | 4.759 | 8395.51 | 2.012 | 97.8 | 77.8 | 1369 | 22.86 | 5457.1 | 2949.6 | 2915.9 | 4261.2 | 1191.3 | 0.67636 | 6.116
2024-12-09 | 15:39 | Data | 0 | 30.185 | 27.971 | 189.479 | 7.65 | 177.905 | 2111.35 | 26.08 | 45.727 | 6.36 | 1.356 | 4.761 | 8400.04 | 2.187 | 97.8 | 77.8 | 1373 | 22.82 | 5460 | 2949.3 | 2906.7 | 4257.8 | 1191.3 | 0.67572 | 6.116
2024-12-09 | 15:39 | Data | 0 | 28.598 | 26.445 | 188.393 | 7.65 | 176.865 | 2114.06 | 26.08 | 45.727 | 6.36 | 1.358 | 4.78 | 8400.04 | 2.295 | 97.8 | 77.9 | 1375 | 22.86 | 5460 | 2946.2 | 2903.9 | 4252.4 | 1191.3 | 0.6746 | 6.139
2024-12-09 | 15:39 | Data | 0 | 29.496 | 27.896 | 189.434 | 7.65 | 177.679 | 2114.06 | 26.08 | 45.457 | 6.36 | 1.352 | 4.755 | 8418.13 | 2.086 | 97.9 | 77.9 | 1374 | 22.68 | 5471.8 | 2943.1 | 2923.9 | 4263.4 | 1191.3 | 0.67305 | 6.105
2024-12-09 | 15:39 | Data | 0 | 30.178 | 27.674 | 189.434 | 7.66 | 177.95 | 2119.49 | 26.08 | 45.637 | 6.36 | 1.353 | 4.74 | 8431.69 | 2.295 | 97.8 | 77.8 | 1378 | 22.82 | 5480.6 | 2958.9 | 2941.3 | 4282.7 | 1191.3 | 0.67088 | 6.092
2024-12-09 | 15:39 | Data | 0 | 30.185 | 27.91 | 189.615 | 7.66 | 177.905 | 2114.06 | 26.08 | 45.727 | 6.35 | 1.367 | 4.749 | 8418.13 | 2.187 | 97.8 | 77.7 | 1373 | 22.86 | 5471.8 | 2953.8 | 2954.2 | 4290.7 | 1191.3 | 0.67094 | 6.117
2024-12-09 | 15:39 | Data | 0 | 30.043 | 27.977 | 189.705 | 7.66 | 177.95 | 2120.39 | 26.08 | 46.089 | 6.37 | 1.367 | 4.763 | 8440.74 | 2.086 | 97.8 | 77.7 | 1378 | 22.91 | 5486.5 | 2955.3 | 2935.7 | 4277 | 1191.3 | 0.67238 | 6.129
2024-12-09 | 15:39 | Data | 0 | 30.144 | 28.072 | 189.66 | 7.66 | 178.04 | 2117.68 | 26.08 | 45.727 | 6.36 | 1.354 | 4.735 | 8454.3 | 2.221 | 97.8 | 77.8 | 1376 | 22.91 | 5495.3 | 2926.8 | 2932.4 | 4260.1 | 1191.3 | 0.66991 | 6.091
2024-12-09 | 15:40 | Data | 0 | 30.185 | 27.89 | 189.615 | 7.66 | 177.995 | 2117.68 | 26.08 | 45.727 | 6.37 | 1.352 | 4.752 | 8454.3 | 2.154 | 97.8 | 77.8 | 1377 | 22.86 | 5495.3 | 2943 | 2944.9 | 4282.1 | 1191.3 | 0.67165 | 6.106
2024-12-09 | 15:40 | Data | 0 | 29.726 | 27.599 | 189.298 | 7.66 | 177.634 | 2124.01 | 26.08 | 45.727 | 6.36 | 1.356 | 4.796 | 8467.87 | 1.985 | 97.9 | 78 | 1380 | 22.82 | 5504.1 | 2946 | 2940.1 | 4273.5 | 1191.3 | 0.67334 | 6.152
2024-12-09 | 15:40 | Data | 0 | 29.044 | 27.329 | 188.936 | 7.65 | 177.317 | 2116.78 | 26.08 | 45.727 | 6.36 | 1.354 | 4.768 | 8458.83 | 1.971 | 97.8 | 77.9 | 1376 | 22.86 | 5498.2 | 2956.7 | 2916.5 | 4268.6 | 1191.3 | 0.67396 | 6.121
2024-12-09 | 15:40 | Data | 0 | 30.07 | 27.896 | 189.705 | 7.66 | 177.905 | 2120.39 | 26.08 | 45.637 | 6.36 | 1.351 | 4.758 | 8472.39 | 2.079 | 97.8 | 77.9 | 1378 | 22.82 | 5507.1 | 2952.2 | 2923.5 | 4268.5 | 1191.3 | 0.67391 | 6.109
2024-12-09 | 15:40 | Data | 0 | 29.557 | 27.619 | 189.434 | 7.66 | 177.769 | 2120.39 | 26.07 | 45.727 | 6.37 | 1.349 | 4.798 | 8485.96 | 1.985 | 97.8 | 78.1 | 1378 | 22.86 | 5515.9 | 2961.5 | 2950.9 | 4294.4 | 1191.3 | 0.67325 | 6.148
2024-12-09 | 15:40 | Data | 0 | 29.739 | 27.647 | 189.162 | 7.66 | 177.679 | 2117.68 | 26.08 | 45.727 | 6.36 | 1.354 | 4.767 | 8485.96 | 2.1 | 97.8 | 77.9 | 1376 | 22.86 | 5515.9 | 2932.4 | 2941.9 | 4270.5 | 1191.3 | 0.66778 | 6.121
2024-12-09 | 15:40 | Data | 0 | 29.051 | 27.322 | 188.891 | 7.66 | 177.363 | 2117.68 | 26.08 | 45.727 | 6.36 | 1.353 | 4.75 | 8458.83 | 1.924 | 97.8 | 77.8 | 1376 | 22.86 | 5498.2 | 2940.7 | 2961 | 4287.6 | 1191.3 | 0.67001 | 6.103
2024-12-09 | 15:40 | Data | 0 | 29.213 | 26.762 | 188.665 | 7.66 | 177.137 | 2114.06 | 26.08 | 45.727 | 6.36 | 1.354 | 4.774 | 8454.3 | 2.295 | 97.8 | 77.9 | 1374 | 22.86 | 5495.3 | 2938.6 | 2982.3 | 4300.1 | 1191.3 | 0.66636 | 6.128
2024-12-09 | 15:40 | Data | 0 | 29.213 | 27.012 | 188.71 | 7.66 | 177.182 | 2113.16 | 26.08 | 45.727 | 6.36 | 1.352 | 4.743 | 8454.3 | 2.133 | 97.8 | 77.8 | 1374 | 22.86 | 5495.3 | 2962.8 | 2993 | 4324.5 | 1191.3 | 0.6687 | 6.095
2024-12-09 | 15:40 | Data | 0 | 29.51 | 27.518 | 189.298 | 7.66 | 177.588 | 2110.45 | 26.08 | 45.637 | 6.36 | 1.352 | 4.735 | 8458.83 | 2.16 | 97.8 | 77.8 | 1372 | 22.86 | 5498.2 | 2955.5 | 2950.1 | 4288.3 | 1191.3 | 0.67261 | 6.087
2024-12-09 | 15:40 | Data | 0 | 29.409 | 27.235 | 188.846 | 7.66 | 177.317 | 2112.26 | 26.08 | 45.637 | 6.36 | 1.359 | 4.748 | 8476.91 | 2.086 | 97.8 | 77.8 | 1372 | 22.82 | 5510 | 2946.7 | 2954.6 | 4289.5 | 1191.3 | 0.66982 | 6.106
2024-12-09 | 15:40 | Data | 0 | 28.808 | 26.512 | 188.439 | 7.66 | 176.911 | 2109.54 | 26.08 | 45.727 | 6.37 | 1.352 | 4.729 | 8467.87 | 2.255 | 97.8 | 77.8 | 1371 | 22.82 | 5504.1 | 2961.6 | 2930.7 | 4278 | 1191.3 | 0.67459 | 6.083
2024-12-09 | 15:40 | Data | 0 | 29.321 | 26.998 | 188.8 | 7.66 | 177.227 | 2116.78 | 26.09 | 45.818 | 6.36 | 1.357 | 4.732 | 8440.74 | 2.194 | 97.8 | 77.7 | 1376 | 22.91 | 5486.5 | 2940.7 | 2912.4 | 4256.6 | 1191.3 | 0.67284 | 6.089
2024-12-09 | 15:40 | Data | 0 | 29.888 | 27.538 | 188.936 | 7.66 | 177.498 | 2117.68 | 26.08 | 45.637 | 6.36 | 1.358 | 4.73 | 8472.39 | 2.194 | 97.8 | 77.7 | 1376 | 22.82 | 5507.1 | 2952 | 2906.5 | 4256.7 | 1191.3 | 0.67659 | 6.089
2024-12-09 | 15:40 | Data | 0 | 28.598 | 26.391 | 188.348 | 7.66 | 176.82 | 2116.78 | 26.08 | 46.089 | 6.36 | 1.359 | 4.759 | 8449.78 | 2.295 | 97.8 | 77.8 | 1375 | 23 | 5492.4 | 2940.9 | 2923.5 | 4261.8 | 1191.3 | 0.67151 | 6.119
2024-12-09 | 15:40 | Data | 0 | 29.037 | 27.133 | 188.665 | 7.66 | 177.046 | 2112.26 | 26.08 | 45.727 | 6.36 | 1.347 | 4.741 | 8445.26 | 2.275 | 97.8 | 77.9 | 1372 | 22.86 | 5489.4 | 2956.3 | 2918.1 | 4268.4 | 1191.3 | 0.67557 | 6.089
2024-12-09 | 15:40 | Data | 0 | 29.321 | 27.397 | 188.981 | 7.66 | 177.498 | 2114.97 | 26.08 | 45.637 | 6.36 | 1.348 | 4.742 | 8449.78 | 2.079 | 97.8 | 77.9 | 1376 | 22.91 | 5492.4 | 2945.7 | 2907.9 | 4260.9 | 1191.3 | 0.67467 | 6.09
2024-12-09 | 15:40 | Data | 0 | 29.726 | 27.64 | 189.208 | 7.66 | 177.588 | 2111.35 | 26.08 | 45.727 | 6.37 | 1.346 | 4.759 | 8431.69 | 2.14 | 97.8 | 77.9 | 1372 | 22.86 | 5480.6 | 2941.1 | 2954.9 | 4286.3 | 1191.3 | 0.66936 | 6.104
2024-12-09 | 15:41 | Data | 0 | 29.962 | 27.89 | 189.388 | 7.66 | 177.814 | 2114.97 | 26.08 | 45.727 | 6.37 | 1.349 | 4.779 | 8418.13 | 2.127 | 97.8 | 78 | 1374 | 22.86 | 5471.8 | 2965.7 | 2948.3 | 4299.5 | 1191.3 | 0.66884 | 6.13
2024-12-09 | 15:41 | Data | 0 | 29.274 | 27.052 | 188.71 | 7.66 | 177.227 | 2112.26 | 26.08 | 45.637 | 6.36 | 1.349 | 4.773 | 8390.99 | 2.127 | 97.8 | 78 | 1372 | 22.86 | 5454.1 | 2929.2 | 2969.4 | 4299.6 | 1191.3 | 0.66863 | 6.123
2024-12-09 | 15:41 | Data | 0 | 28.355 | 26.499 | 188.439 | 7.66 | 176.865 | 2109.54 | 26.08 | 45.727 | 6.38 | 1.344 | 4.729 | 8395.51 | 2.019 | 97.8 | 77.9 | 1371 | 22.82 | 5457.1 | 2957.6 | 2946.1 | 4286.5 | 1191.3 | 0.67255 | 6.074
2024-12-09 | 15:41 | Data | 0 | 28.949 | 27.133 | 188.665 | 7.66 | 177.046 | 2110.45 | 26.08 | 45.727 | 6.37 | 1.351 | 4.738 | 8390.99 | 2.059 | 97.8 | 77.8 | 1370 | 22.86 | 5454.1 | 2954.5 | 2921.5 | 4272 | 1191.3 | 0.67543 | 6.087
2024-12-09 | 15:41 | Data | 0 | 29.037 | 26.742 | 188.484 | 7.66 | 176.956 | 2111.35 | 26.08 | 45.818 | 6.37 | 1.352 | 4.775 | 8449.78 | 2.167 | 97.8 | 77.9 | 1372 | 22.73 | 5492.4 | 2947.4 | 2890.5 | 4241.1 | 1191.3 | 0.67652 | 6.127
2024-12-09 | 15:41 | Data | 0 | 29.037 | 26.938 | 188.71 | 7.66 | 177.182 | 2111.35 | 26.08 | 45.637 | 6.37 | 1.353 | 4.73 | 8445.26 | 2.1 | 97.8 | 77.8 | 1372 | 22.86 | 5489.4 | 2949.6 | 2844.8 | 4212.1 | 1191.4 | 0.68402 | 6.083
2024-12-09 | 15:41 | Data | 0 | 28.862 | 26.796 | 188.529 | 7.66 | 176.956 | 2109.54 | 26.09 | 45.727 | 6.37 | 1.362 | 4.718 | 8440.74 | 2.289 | 97.8 | 77.6 | 1372 | 22.86 | 5486.5 | 2951.2 | 2867.8 | 4236.5 | 1191.4 | 0.68041 | 6.078
2024-12-09 | 15:41 | Data | 0 | 29.294 | 26.971 | 188.8 | 7.66 | 177.317 | 2114.97 | 26.08 | 45.727 | 6.37 | 1.355 | 4.7 | 8445.26 | 2.093 | 97.8 | 77.6 | 1375 | 22.86 | 5489.4 | 2960.9 | 2896.4 | 4257 | 1191.4 | 0.67882 | 6.055
2024-12-09 | 15:41 | Data | 0 | 29.726 | 27.478 | 189.072 | 7.66 | 177.588 | 2110.45 | 26.09 | 45.727 | 6.37 | 1.361 | 4.721 | 8431.69 | 2.248 | 97.8 | 77.6 | 1372 | 22.82 | 5480.6 | 2957.6 | 2924.5 | 4271.1 | 1191.4 | 0.67669 | 6.082
2024-12-09 | 15:41 | Data | 0 | 29.267 | 27.255 | 188.936 | 7.66 | 177.227 | 2111.35 | 26.09 | 45.727 | 6.37 | 1.359 | 4.74 | 8436.21 | 2.295 | 97.8 | 77.7 | 1373 | 22.91 | 5483.5 | 2959.5 | 2961.4 | 4301.5 | 1191.4 | 0.6718 | 6.1
2024-12-09 | 15:41 | Data | 0 | 29.382 | 27.167 | 188.891 | 7.66 | 177.453 | 2114.06 | 26.08 | 45.727 | 6.36 | 1.356 | 4.763 | 8422.65 | 2.174 | 97.8 | 77.8 | 1374 | 22.86 | 5474.7 | 2946.6 | 2948.9 | 4280.2 | 1191.4 | 0.67116 | 6.118
2024-12-09 | 15:41 | Data | 0 | 29.098 | 27.086 | 188.8 | 7.66 | 177.317 | 2114.06 | 26.08 | 45.727 | 6.37 | 1.348 | 4.741 | 8431.69 | 2.073 | 97.8 | 77.8 | 1374 | 22.86 | 5480.6 | 2956.7 | 2984.7 | 4310.6 | 1191.4 | 0.66914 | 6.091
2024-12-09 | 15:41 | Data | 0 | 29.267 | 27.194 | 188.936 | 7.66 | 177.453 | 2119.49 | 26.07 | 45.637 | 6.37 | 1.348 | 4.744 | 8445.26 | 2.066 | 97.9 | 77.9 | 1378 | 22.73 | 5489.4 | 2966.1 | 2966.5 | 4303.2 | 1191.4 | 0.67201 | 6.095
2024-12-09 | 15:41 | Data | 0 | 29.294 | 27.187 | 188.8 | 7.66 | 177.227 | 2114.06 | 26.09 | 45.727 | 6.37 | 1.349 | 4.754 | 8431.69 | 2.086 | 97.8 | 77.9 | 1374 | 22.86 | 5480.6 | 2979.5 | 2979.5 | 4328.1 | 1191.4 | 0.67115 | 6.104
2024-12-09 | 15:41 | Data | 0 | 27.653 | 25.371 | 187.624 | 7.66 | 176.142 | 2109.54 | 26.08 | 45.366 | 6.37 | 1.355 | 4.744 | 8440.74 | 2.059 | 97.8 | 77.8 | 1372 | 22.77 | 5486.5 | 2957.4 | 2936.7 | 4283.1 | 1191.4 | 0.67262 | 6.098
2024-12-09 | 15:41 | Data | 0 | 28.342 | 26.269 | 188.348 | 7.66 | 176.73 | 2116.78 | 26.08 | 45.637 | 6.37 | 1.348 | 4.728 | 8440.74 | 2.1 | 97.8 | 77.8 | 1375 | 22.91 | 5486.5 | 2972.8 | 2887.2 | 4253 | 1191.4 | 0.67988 | 6.074
2024-12-09 | 15:41 | Data | 0 | 29.314 | 26.917 | 188.665 | 7.66 | 177.137 | 2117.68 | 26.08 | 45.727 | 6.37 | 1.348 | 4.749 | 8436.21 | 2.262 | 97.8 | 77.9 | 1376 | 22.82 | 5483.5 | 2961.3 | 2888.7 | 4252.6 | 1191.4 | 0.67879 | 6.099
2024-12-09 | 15:41 | Data | 0 | 28.922 | 26.526 | 188.574 | 7.66 | 177.001 | 2117.68 | 26.08 | 45.727 | 6.37 | 1.369 | 4.762 | 8445.26 | 2.356 | 97.8 | 77.7 | 1376 | 22.82 | 5489.4 | 2949.9 | 2902.3 | 4250.7 | 1191.4 | 0.67685 | 6.13
2024-12-09 | 15:42 | Data | 0 | 28.74 | 26.452 | 188.303 | 7.66 | 176.865 | 2117.68 | 26.08 | 45.637 | 6.37 | 1.364 | 4.759 | 8431.69 | 2.154 | 97.8 | 77.7 | 1376 | 22.82 | 5480.6 | 2951.6 | 2914.1 | 4263.8 | 1191.4 | 0.67502 | 6.121
2024-12-09 | 15:42 | Data | 0 | 28.315 | 26.094 | 188.077 | 7.66 | 176.594 | 2117.68 | 26.08 | 45.727 | 6.37 | 1.359 | 4.748 | 8440.74 | 2.187 | 97.8 | 77.7 | 1376 | 22.86 | 5486.5 | 2942.7 | 2944.1 | 4272 | 1191.4 | 0.67257 | 6.107
2024-12-09 | 15:42 | Data | 0 | 28.686 | 26.283 | 188.348 | 7.66 | 176.82 | 2114.06 | 26.08 | 45.727 | 6.37 | 1.355 | 4.75 | 8445.26 | 2.302 | 97.8 | 77.8 | 1376 | 22.86 | 5489.4 | 2953.6 | 2939.1 | 4278.2 | 1191.4 | 0.67419 | 6.104
2024-12-09 | 15:42 | Data | 0 | 29.213 | 27.025 | 188.891 | 7.66 | 177.227 | 2117.68 | 26.08 | 45.727 | 6.37 | 1.357 | 4.74 | 8445.26 | 2.133 | 97.8 | 77.7 | 1376 | 22.82 | 5489.4 | 2939.4 | 2955.1 | 4284.7 | 1191.4 | 0.66977 | 6.097
2024-12-09 | 15:42 | Data | 0 | 28.625 | 26.445 | 188.122 | 7.66 | 176.865 | 2114.97 | 26.08 | 45.727 | 6.37 | 1.358 | 4.763 | 8454.3 | 2.194 | 97.8 | 77.8 | 1375 | 22.82 | 5495.3 | 2933.5 | 2956.5 | 4277.3 | 1191.4 | 0.66831 | 6.122
2024-12-09 | 15:42 | Data | 0 | 28.092 | 26.141 | 188.077 | 7.66 | 176.639 | 2117.68 | 26.09 | 45.727 | 6.37 | 1.351 | 4.742 | 8458.83 | 2.167 | 97.8 | 77.8 | 1376 | 22.82 | 5498.2 | 2971.3 | 2947.9 | 4301.3 | 1191.4 | 0.67283 | 6.093
2024-12-09 | 15:42 | Data | 0 | 28.571 | 26.181 | 188.303 | 7.65 | 176.911 | 2117.68 | 26.08 | 45.637 | 6.36 | 1.341 | 4.719 | 8427.17 | 2.073 | 97.8 | 77.9 | 1376 | 22.86 | 5477.7 | 2961.2 | 2941.1 | 4286.7 | 1191.4 | 0.67303 | 6.061
2024-12-09 | 15:42 | Data | 0 | 28.565 | 26.181 | 188.439 | 7.66 | 176.956 | 2116.78 | 26.09 | 45.727 | 6.37 | 1.357 | 4.721 | 8445.26 | 2.194 | 97.8 | 77.7 | 1376 | 22.86 | 5489.4 | 2959 | 2928.4 | 4272.5 | 1191.4 | 0.67615 | 6.078
2024-12-09 | 15:42 | Data | 0 | 28.369 | 26.269 | 188.212 | 7.66 | 176.73 | 2114.06 | 26.09 | 45.727 | 6.37 | 1.358 | 4.722 | 8445.26 | 2.079 | 97.8 | 77.6 | 1374 | 22.86 | 5489.4 | 2958.5 | 2903.7 | 4257.1 | 1191.4 | 0.67856 | 6.082
2024-12-09 | 15:42 | Data | 0 | 29.01 | 26.938 | 188.71 | 7.66 | 177.091 | 2114.97 | 26.08 | 45.727 | 6.37 | 1.351 | 4.699 | 8449.78 | 2.174 | 97.8 | 77.7 | 1375 | 22.91 | 5492.4 | 2970.8 | 2920.7 | 4275.8 | 1191.4 | 0.67835 | 6.05
2024-12-09 | 15:42 | Data | 0 | 28.808 | 26.337 | 188.484 | 7.66 | 176.956 | 2114.06 | 26.09 | 45.908 | 6.38 | 1.347 | 4.734 | 8476.91 | 2.262 | 97.8 | 77.9 | 1374 | 22.86 | 5510 | 2950.8 | 2911.7 | 4258.4 | 1191.4 | 0.67651 | 6.08
2024-12-09 | 15:42 | Data | 0 | 28.335 | 26.269 | 188.122 | 7.66 | 176.73 | 2114.06 | 26.08 | 45.818 | 6.37 | 1.341 | 4.714 | 8481.44 | 2.275 | 97.8 | 77.9 | 1374 | 22.86 | 5512.9 | 2951.7 | 2935.2 | 4278.3 | 1191.4 | 0.67328 | 6.056
2024-12-09 | 15:42 | Data | 0 | 28.119 | 26.04 | 187.986 | 7.66 | 176.413 | 2113.16 | 26.09 | 45.727 | 6.37 | 1.357 | 4.725 | 8481.44 | 2.073 | 97.8 | 77.7 | 1374 | 22.86 | 5512.9 | 2975 | 2954.6 | 4304.9 | 1191.4 | 0.67401 | 6.082
2024-12-09 | 15:42 | Data | 0 | 28.808 | 26.728 | 188.62 | 7.66 | 177.001 | 2114.06 | 26.08 | 45.637 | 6.37 | 1.358 | 4.744 | 8472.39 | 2.282 | 97.8 | 77.8 | 1374 | 22.86 | 5507.1 | 2938.6 | 2950.8 | 4281.5 | 1191.4 | 0.66778 | 6.102
2024-12-09 | 15:42 | Data | 0 | 29.503 | 27.451 | 189.072 | 7.66 | 177.588 | 2112.26 | 26.09 | 45.727 | 6.37 | 1.36 | 4.752 | 8883.91 | 2.079 | 97.8 | 77.7 | 1372 | 22.82 | 5774.5 | 2948.5 | 2942.7 | 4281.4 | 1191.4 | 0.67169 | 6.111
2024-12-09 | 15:42 | Data | 0 | 29.51 | 27.316 | 189.253 | 7.65 | 177.543 | 2118.58 | 26.08 | 45.818 | 6.37 | 1.372 | 4.76 | 8431.69 | 2.181 | 97.8 | 77.6 | 1376 | 22.86 | 5480.6 | 2961.2 | 2926.8 | 4277.5 | 1191.4 | 0.67533 | 6.133
2024-12-09 | 15:42 | Data | 0 | 28.571 | 26.114 | 188.348 | 7.66 | 176.82 | 2112.26 | 26.08 | 45.637 | 6.37 | 1.36 | 4.747 | 8440.74 | 2.255 | 97.8 | 77.7 | 1373 | 22.91 | 5486.5 | 2975.3 | 2956 | 4306.1 | 1191.4 | 0.67294 | 6.108
2024-12-09 | 15:42 | Data | 0 | 28.808 | 26.526 | 188.393 | 7.66 | 177.001 | 2113.16 | 26.08 | 45.727 | 6.37 | 1.345 | 4.74 | 8440.74 | 2.282 | 97.8 | 77.9 | 1374 | 22.86 | 5486.5 | 2953.6 | 2938.7 | 4284.9 | 1191.4 | 0.67288 | 6.085
2024-12-09 | 15:43 | Data | 0 | 29.496 | 27.201 | 188.981 | 7.66 | 177.498 | 2108.64 | 26.1 | 45.637 | 6.37 | 1.339 | 4.742 | 8454.3 | 2.248 | 97.8 | 78 | 1371 | 22.82 | 5495.3 | 2973.8 | 2921 | 4278.2 | 1191.4 | 0.67632 | 6.081
2024-12-09 | 15:43 | Data | 0 | 29.834 | 27.43 | 189.162 | 7.66 | 177.634 | 2103.22 | 26.08 | 45.727 | 6.37 | 1.352 | 4.754 | 8458.83 | 2.322 | 97.8 | 77.9 | 1367 | 22.86 | 5498.2 | 2943.7 | 2885.8 | 4233.8 | 1191.4 | 0.67465 | 6.106
2024-12-09 | 15:43 | Data | 0 | 30.09 | 27.89 | 189.66 | 7.66 | 177.95 | 2108.64 | 26.08 | 45.727 | 6.37 | 1.349 | 4.747 | 8454.3 | 2.073 | 97.8 | 77.9 | 1371 | 22.82 | 5495.3 | 2943.4 | 2920.6 | 4261.4 | 1191.4 | 0.67298 | 6.096
2024-12-09 | 15:43 | Data | 0 | 30.307 | 27.903 | 189.841 | 7.66 | 178.131 | 2106.83 | 26.08 | 45.998 | 6.37 | 1.363 | 4.781 | 8458.83 | 2.1 | 97.8 | 77.8 | 1370 | 22.95 | 5498.2 | 2956.3 | 2913.1 | 4267.2 | 1191.4 | 0.67548 | 6.143
2024-12-09 | 15:43 | Data | 0 | 30.556 | 28.416 | 189.75 | 7.65 | 178.176 | 2105.93 | 26.08 | 45.727 | 6.37 | 1.36 | 4.785 | 8495 | 2.133 | 97.8 | 77.9 | 1369 | 22.86 | 5521.8 | 2962.8 | 2902.2 | 4264.4 | 1191.4 | 0.67677 | 6.144
2024-12-09 | 15:43 | Data | 0 | 30.651 | 28.396 | 190.112 | 7.66 | 178.402 | 2106.83 | 26.08 | 45.637 | 6.38 | 1.364 | 4.767 | 8499.53 | 2.093 | 97.8 | 77.8 | 1369 | 22.82 | 5524.7 | 2952.7 | 2900.5 | 4249.1 | 1191.5 | 0.67663 | 6.13
2024-12-09 | 15:43 | Data | 0 | 30.982 | 28.895 | 190.157 | 7.66 | 178.402 | 2105.03 | 26.08 | 45.727 | 6.37 | 1.36 | 4.77 | 8499.53 | 2.154 | 97.8 | 77.8 | 1368 | 22.86 | 5524.7 | 2938.8 | 2906 | 4247.3 | 1191.5 | 0.67369 | 6.13
2024-12-09 | 15:43 | Data | 0 | 30.421 | 28.146 | 189.886 | 7.65 | 178.312 | 2108.64 | 26.08 | 42.838 | 6.37 | 1.356 | 4.764 | 8499.53 | 2.241 | 98 | 77.8 | 1371 | 21.46 | 5524.7 | 2951.5 | 2920.3 | 4267.9 | 1191.5 | 0.67099 | 6.121
2024-12-09 | 15:43 | Data | 0 | 30.961 | 28.592 | 189.886 | 7.66 | 178.357 | 2105.93 | 26.07 | 45.186 | 6.37 | 1.357 | 4.768 | 8458.83 | 2.248 | 97.9 | 77.9 | 1369 | 22.59 | 5498.2 | 2971.6 | 2915.4 | 4274.4 | 1191.5 | 0.67818 | 6.125
2024-12-09 | 15:43 | Data | 0 | 30.698 | 28.247 | 189.976 | 7.66 | 178.357 | 2106.83 | 26.08 | 45.276 | 6.37 | 1.365 | 4.768 | 8467.87 | 2.41 | 97.9 | 77.8 | 1369 | 22.59 | 5504.1 | 2970.6 | 2933.4 | 4289.8 | 1191.5 | 0.67306 | 6.133
2024-12-09 | 15:43 | Data | 0 | 30.624 | 28.463 | 189.796 | 7.66 | 178.086 | 2106.83 | 26.08 | 45.186 | 6.37 | 1.349 | 4.804 | 8458.83 | 2.289 | 97.9 | 78.1 | 1369 | 22.5 | 5498.2 | 2948.1 | 2924.1 | 4268.3 | 1191.5 | 0.67403 | 6.157
2024-12-09 | 15:43 | Data | 0 | 30.651 | 28.74 | 189.343 | 7.66 | 177.724 | 2104.12 | 26.08 | 45.547 | 6.37 | 1.351 | 4.781 | 8467.87 | 1.971 | 97.8 | 78 | 1367 | 22.77 | 5504.1 | 2954.4 | 2944.3 | 4287.7 | 1191.5 | 0.67223 | 6.132
2024-12-09 | 15:43 | Data | 0 | 30.685 | 28.632 | 189.479 | 7.66 | 177.905 | 2104.12 | 26.08 | 45.727 | 6.37 | 1.354 | 4.775 | 8467.87 | 1.965 | 97.8 | 77.9 | 1368 | 22.86 | 5504.1 | 2936.2 | 2960.9 | 4262.1 | 1191.5 | 0.66824 | 6.128
2024-12-09 | 15:43 | Data | 0 | 30.725 | 28.781 | 189.343 | 7.66 | 177.724 | 2103.22 | 26.08 | 45.637 | 6.37 | 1.353 | 4.761 | 8463.35 | 2.025 | 97.8 | 77.9 | 1367 | 22.82 | 5501.2 | 2944.4 | 2931.5 | 4271.8 | 1191.5 | 0.67273 | 6.115
2024-12-09 | 15:43 | Data | 0 | 30.658 | 28.477 | 189.298 | 7.66 | 177.724 | 2100.51 | 26.08 | 45.727 | 6.37 | 1.348 | 4.731 | 8458.83 | 2.241 | 97.8 | 77.8 | 1365 | 22.86 | 5498.2 | 2954.6 | 2979.4 | 4302.5 | 1191.5 | 0.67059 | 6.077
2024-12-09 | 15:43 | Data | 0 | 31.103 | 29.031 | 189.569 | 7.66 | 177.86 | 2100.51 | 26.07 | 45.637 | 6.37 | 1.359 | 4.765 | 8458.83 | 2.079 | 97.8 | 77.8 | 1366 | 22.86 | 5498.2 | 2954 | 2985.9 | 4314 | 1191.5 | 0.66747 | 6.123
2024-12-09 | 15:43 | Data | 0 | 31.265 | 28.841 | 189.479 | 7.66 | 177.905 | 2101.41 | 26.07 | 45.818 | 6.37 | 1.358 | 4.756 | 8467.87 | 2.214 | 97.8 | 77.8 | 1365 | 22.86 | 5504.1 | 2955.2 | 2986.7 | 4310 | 1191.5 | 0.66885 | 6.114
2024-12-09 | 15:44 | Data | 0 | 30.691 | 28.578 | 189.434 | 7.65 | 177.86 | 2099.6 | 26.08 | 45.637 | 6.37 | 1.358 | 4.739 | 8485.96 | 2.073 | 97.8 | 77.7 | 1364 | 22.86 | 5515.9 | 2935.5 | 2958.3 | 4283 | 1191.5 | 0.66987 | 6.095
2024-12-09 | 15:44 | Data | 0 | 31.245 | 28.848 | 189.569 | 7.65 | 178.131 | 2098.7 | 26.08 | 45.727 | 6.37 | 1.357 | 4.754 | 8472.39 | 2.221 | 97.8 | 77.8 | 1363 | 22.86 | 5507.1 | 2933.6 | 2937.3 | 4265.6 | 1191.5 | 0.6694 | 6.11
2024-12-09 | 15:44 | Data | 0 | 31.569 | 29.105 | 190.067 | 7.65 | 178.312 | 2100.51 | 26.06 | 45.727 | 6.37 | 1.351 | 4.757 | 8467.87 | 2.086 | 97.8 | 77.9 | 1365 | 22.82 | 5504.1 | 2937.8 | 2923.2 | 4258.2 | 1191.5 | 0.67243 | 6.107
2024-12-09 | 15:44 | Data | 0 | 31.555 | 29.267 | 189.841 | 7.65 | 178.131 | 2098.7 | 26.07 | 45.727 | 6.37 | 1.355 | 4.756 | 8458.83 | 2.127 | 97.8 | 77.8 | 1363 | 22.86 | 5498.2 | 2933.2 | 2948.9 | 4268 | 1191.5 | 0.66936 | 6.111
2024-12-09 | 15:44 | Data | 0 | 31.555 | 29.496 | 189.841 | 7.65 | 178.221 | 2101.41 | 26.07 | 45.727 | 6.37 | 1.356 | 4.781 | 8445.26 | 2.073 | 97.8 | 77.9 | 1367 | 22.86 | 5489.4 | 2943.6 | 2899.7 | 4244.7 | 1191.5 | 0.67701 | 6.136
2024-12-09 | 15:44 | Data | 0 | 31.569 | 29.328 | 190.067 | 7.65 | 178.357 | 2104.12 | 26.06 | 45.727 | 6.37 | 1.358 | 4.79 | 8431.69 | 2.187 | 97.8 | 77.9 | 1367 | 22.86 | 5480.6 | 2940.7 | 2919.7 | 4259.5 | 1191.5 | 0.67463 | 6.147
2024-12-09 | 15:44 | Data | 0 | 31.799 | 29.766 | 190.248 | 7.65 | 178.583 | 2108.64 | 26.06 | 45.727 | 6.37 | 1.361 | 4.798 | 8445.26 | 1.985 | 97.8 | 77.9 | 1371 | 22.86 | 5489.4 | 2926 | 2911.8 | 4238.4 | 1191.5 | 0.67397 | 6.159
2024-12-09 | 15:44 | Data | 0 | 31.799 | 29.672 | 189.796 | 7.65 | 178.312 | 2111.35 | 26.07 | 45.637 | 6.36 | 1.371 | 4.779 | 8467.87 | 2.295 | 97.8 | 77.7 | 1373 | 22.82 | 5504.1 | 2924.6 | 2926.1 | 4255.3 | 1191.5 | 0.67265 | 6.149
2024-12-09 | 15:44 | Data | 0 | 31.92 | 29.854 | 190.248 | 7.66 | 178.538 | 2111.35 | 26.06 | 45.637 | 6.37 | 1.373 | 4.748 | 8467.87 | 2.073 | 97.8 | 77.6 | 1372 | 22.86 | 5504.1 | 2936.2 | 2921.7 | 4256.9 | 1191.5 | 0.67181 | 6.12
2024-12-09 | 15:44 | Data | 0 | 32.345 | 30.009 | 190.248 | 7.65 | 178.583 | 2112.26 | 26.07 | 45.818 | 6.37 | 1.349 | 4.764 | 8472.39 | 2.032 | 97.8 | 77.9 | 1373 | 22.86 | 5507.1 | 2945.9 | 2928.8 | 4264.5 | 1191.5 | 0.67315 | 6.111
2024-12-09 | 15:44 | Data | 0 | 32.089 | 29.955 | 190.293 | 7.65 | 178.538 | 2108.64 | 26.05 | 45.727 | 6.37 | 1.351 | 4.73 | 8463.35 | 1.911 | 97.8 | 77.8 | 1371 | 22.91 | 5501.2 | 2947.6 | 2939.9 | 4276.8 | 1191.5 | 0.67222 | 6.081
2024-12-09 | 15:44 | Data | 0 | 32.001 | 30.063 | 190.112 | 7.66 | 178.492 | 2108.64 | 26.06 | 45.276 | 6.37 | 1.36 | 4.729 | 8472.39 | 2.12 | 97.9 | 77.7 | 1371 | 22.64 | 5507.1 | 2932.7 | 2910.3 | 4249.2 | 1191.5 | 0.67212 | 6.088
2024-12-09 | 15:44 | Data | 0 | 32.028 | 29.733 | 190.067 | 7.65 | 178.402 | 2109.54 | 26.06 | 45.637 | 6.36 | 1.367 | 4.778 | 8467.87 | 2.282 | 97.8 | 77.7 | 1371 | 22.82 | 5504.1 | 2937.2 | 2950.4 | 4278.3 | 1191.5 | 0.66976 | 6.146
2024-12-09 | 15:44 | Data | 0 | 31.846 | 29.787 | 190.203 | 7.65 | 178.583 | 2107.74 | 26.07 | 45.637 | 6.37 | 1.367 | 4.78 | 8485.96 | 2.019 | 97.8 | 77.8 | 1371 | 22.86 | 5515.9 | 2935.7 | 2981.9 | 4301 | 1191.5 | 0.66471 | 6.147
2024-12-09 | 15:44 | Data | 0 | 32.028 | 29.955 | 190.203 | 7.66 | 178.538 | 2108.64 | 26.07 | 45.727 | 6.37 | 1.36 | 4.767 | 8481.44 | 2.248 | 97.8 | 77.8 | 1371 | 22.86 | 5512.9 | 2925.1 | 2952.8 | 4273.4 | 1191.5 | 0.66643 | 6.124
2024-12-09 | 15:44 | Data | 0 | 32.028 | 29.955 | 190.203 | 7.65 | 178.492 | 2109.54 | 26.06 | 45.637 | 6.37 | 1.354 | 4.774 | 8481.44 | 2.073 | 97.8 | 77.9 | 1371 | 22.86 | 5512.9 | 2924 | 2942.1 | 4265.3 | 1191.5 | 0.66905 | 6.128
2024-12-09 | 15:44 | Data | 0 | 32.028 | 29.962 | 190.203 | 7.65 | 178.492 | 2107.74 | 26.07 | 45.637 | 6.37 | 1.359 | 4.79 | 8476.91 | 2.059 | 97.8 | 77.9 | 1370 | 22.86 | 5510 | 2928.3 | 2921.8 | 4239 | 1191.5 | 0.67006 | 6.15
2024-12-09 | 15:44 | Data | 0 | 32.089 | 29.955 | 190.203 | 7.65 | 178.583 | 2108.64 | 26.06 | 45.727 | 6.37 | 1.358 | 4.759 | 8454.3 | 1.911 | 97.8 | 77.8 | 1371 | 22.86 | 5495.3 | 2937.2 | 2914.2 | 4254.1 | 1191.5 | 0.67368 | 6.119
2024-12-09 | 15:45 | Data | 0 | 32.46 | 30.232 | 190.293 | 7.66 | 178.583 | 2111.35 | 26.06 | 45.727 | 6.37 | 1.353 | 4.787 | 8472.39 | 2.201 | 97.8 | 78 | 1372 | 22.86 | 5507.1 | 2933.7 | 2929.4 | 4261.5 | 1191.5 | 0.67253 | 6.139
2024-12-09 | 15:45 | Data | 0 | 32.291 | 30.131 | 189.615 | 7.65 | 177.95 | 2114.06 | 26.07 | 45.637 | 6.37 | 1.347 | 4.807 | 8481.44 | 2.093 | 97.8 | 78.1 | 1375 | 22.86 | 5512.9 | 2927.8 | 2911.4 | 4247.3 | 1191.5 | 0.67219 | 6.154
2024-12-09 | 15:45 | Data | 0 | 32.352 | 30.077 | 189.343 | 7.65 | 177.769 | 2114.06 | 26.06 | 45.727 | 6.37 | 1.347 | 4.765 | 8458.83 | 2.201 | 97.8 | 78 | 1374 | 22.86 | 5498.2 | 2914.7 | 2882.1 | 4217 | 1191.5 | 0.67235 | 6.111
2024-12-09 | 15:45 | Data | 0 | 32.251 | 30.185 | 189.388 | 7.65 | 177.769 | 2112.26 | 26.06 | 45.637 | 6.37 | 1.355 | 4.754 | 8467.87 | 2.079 | 97.8 | 77.8 | 1374 | 22.86 | 5504.1 | 2925.5 | 2910.3 | 4240.3 | 1191.5 | 0.67409 | 6.111
2024-12-09 | 15:45 | Data | 0 | 32.231 | 30.124 | 189.343 | 7.65 | 177.724 | 2114.97 | 26.03 | 45.818 | 6.37 | 1.353 | 4.74 | 8467.87 | 2.187 | 97.8 | 77.8 | 1375 | 22.82 | 5504.1 | 2935.4 | 2889.4 | 4227.5 | 1191.5 | 0.67502 | 6.093
2024-12-09 | 15:45 | Data | 0 | 32.258 | 30.063 | 189.388 | 7.66 | 177.814 | 2114.06 | 26.07 | 45.818 | 6.37 | 1.36 | 4.745 | 8458.83 | 2.093 | 97.8 | 77.7 | 1374 | 22.86 | 5498.2 | 2921.8 | 2895.8 | 4226.9 | 1191.5 | 0.67296 | 6.104
2024-12-09 | 15:45 | Data | 0 | 32.204 | 30.185 | 189.479 | 7.65 | 177.724 | 2113.16 | 26.07 | 45.637 | 6.37 | 1.345 | 4.773 | 8463.35 | 2.248 | 97.8 | 78 | 1374 | 22.82 | 5501.2 | 2925.9 | 2884.9 | 4225.9 | 1191.6 | 0.67619 | 6.118
2024-12-09 | 15:45 | Data | 0 | 32.359 | 29.969 | 189.434 | 7.65 | 177.769 | 2114.97 | 26.07 | 45.727 | 6.37 | 1.343 | 4.772 | 8458.83 | 2.302 | 97.8 | 78 | 1375 | 22.86 | 5498.2 | 2928.3 | 2885.3 | 4225.7 | 1191.6 | 0.67774 | 6.114
2024-12-09 | 15:45 | Data | 0 | 32.305 | 30.401 | 189.524 | 7.65 | 177.905 | 2109.54 | 26.06 | 45.727 | 6.37 | 1.359 | 4.743 | 8458.83 | 2.079 | 97.8 | 77.7 | 1371 | 22.86 | 5498.2 | 2912.8 | 2875.5 | 4208.3 | 1191.6 | 0.67543 | 6.102
2024-12-09 | 15:45 | Data | 0 | 32.237 | 30.185 | 189.343 | 7.65 | 177.814 | 2107.74 | 26.07 | 45.637 | 6.37 | 1.367 | 4.751 | 8467.87 | 2.073 | 97.8 | 77.7 | 1369 | 22.82 | 5504.1 | 2924.3 | 2862.7 | 4206.7 | 1191.6 | 0.67791 | 6.116
2024-12-09 | 15:45 | Data | 0 | 32.433 | 30.185 | 189.569 | 7.65 | 177.95 | 2101.41 | 26.07 | 45.727 | 6.37 | 1.36 | 4.73 | 8495 | 2.1 | 97.8 | 77.7 | 1366 | 22.86 | 5521.8 | 2944.4 | 2890.1 | 4238.1 | 1191.6 | 0.67787 | 6.089
2024-12-09 | 15:45 | Data | 0 | 32.487 | 30.239 | 189.434 | 7.65 | 177.814 | 2108.64 | 26.07 | 45.637 | 6.36 | 1.353 | 4.755 | 8472.39 | 2.14 | 97.8 | 77.8 | 1371 | 22.82 | 5507.1 | 2931.6 | 2850.2 | 4203.4 | 1191.6 | 0.68045 | 6.108
2024-12-09 | 15:45 | Data | 0 | 31.832 | 29.955 | 189.298 | 7.65 | 177.724 | 2107.74 | 26.06 | 45.727 | 6.37 | 1.353 | 4.718 | 8458.83 | 1.965 | 97.8 | 77.7 | 1369 | 22.86 | 5498.2 | 2933.8 | 2881.7 | 4225.5 | 1191.6 | 0.67788 | 6.071
2024-12-09 | 15:45 | Data | 0 | 32.21 | 30.381 | 189.343 | 7.65 | 177.769 | 2109.54 | 26.07 | 45.637 | 6.37 | 1.357 | 4.733 | 8463.35 | 2.032 | 97.8 | 77.7 | 1372 | 22.91 | 5501.2 | 2927.2 | 2829.2 | 4188.5 | 1191.6 | 0.68073 | 6.089
2024-12-09 | 15:45 | Data | 0 | 32.318 | 30.131 | 189.524 | 7.65 | 177.86 | 2111.35 | 26.06 | 45.818 | 6.37 | 1.355 | 4.78 | 8485.96 | 2.201 | 97.8 | 77.9 | 1372 | 22.86 | 5515.9 | 2926.6 | 2856.2 | 4204.8 | 1191.6 | 0.67924 | 6.136
2024-12-09 | 15:45 | Data | 0 | 32.379 | 30.077 | 189.434 | 7.65 | 177.905 | 2104.12 | 26.07 | 45.727 | 6.38 | 1.348 | 4.762 | 8472.39 | 1.992 | 97.8 | 77.9 | 1367 | 22.86 | 5507.1 | 2920.3 | 2882.1 | 4217.5 | 1191.6 | 0.67547 | 6.111
2024-12-09 | 15:45 | Data | 0 | 32.683 | 30.212 | 189.479 | 7.65 | 177.86 | 2109.54 | 26.06 | 45.637 | 6.37 | 1.369 | 4.745 | 8458.83 | 2.302 | 97.8 | 77.6 | 1371 | 22.86 | 5498.2 | 2944.8 | 2863.1 | 4223.3 | 1191.6 | 0.68007 | 6.112
2024-12-09 | 15:46 | Data | 0 | 32.21 | 30.185 | 189.343 | 7.65 | 177.814 | 2111.35 | 26.08 | 45.727 | 6.37 | 1.354 | 4.787 | 8481.44 | 2.073 | 97.8 | 78 | 1372 | 22.82 | 5512.9 | 2919.5 | 2875.4 | 4213.4 | 1191.6 | 0.67588 | 6.139
2024-12-09 | 15:46 | Data | 0 | 32.312 | 30.009 | 189.524 | 7.65 | 177.814 | 2111.35 | 26.07 | 45.637 | 6.37 | 1.353 | 4.759 | 8472.39 | 1.877 | 97.8 | 77.9 | 1372 | 22.82 | 5507.1 | 2915.6 | 2865.6 | 4206.2 | 1191.6 | 0.67553 | 6.112
2024-12-09 | 15:46 | Data | 0 | 32.264 | 30.225 | 189.434 | 7.65 | 177.769 | 2112.26 | 26.06 | 45.727 | 6.37 | 1.351 | 4.775 | 8458.83 | 1.924 | 97.8 | 77.9 | 1372 | 22.82 | 5498.2 | 2924.9 | 2843.6 | 4196.1 | 1191.6 | 0.68085 | 6.126
2024-12-09 | 15:46 | Data | 0 | 32.028 | 30.07 | 189.208 | 7.65 | 177.588 | 2112.26 | 26.07 | 45.727 | 6.37 | 1.356 | 4.797 | 8481.44 | 2.073 | 97.8 | 78 | 1372 | 22.86 | 5512.9 | 2925.3 | 2876.8 | 4217.7 | 1191.6 | 0.67671 | 6.153
2024-12-09 | 15:46 | Data | 0 | 32.028 | 29.955 | 189.117 | 7.65 | 177.498 | 2114.06 | 26.06 | 45.727 | 6.37 | 1.356 | 4.767 | 8481.44 | 2.073 | 97.8 | 77.9 | 1374 | 22.82 | 5512.9 | 2919.7 | 2833.8 | 4185.3 | 1191.6 | 0.68181 | 6.124
2024-12-09 | 15:46 | Data | 0 | 32.501 | 30.023 | 189.388 | 7.65 | 177.679 | 2113.16 | 26.07 | 45.727 | 6.37 | 1.348 | 4.763 | 8476.91 | 2.14 | 97.8 | 77.9 | 1374 | 22.86 | 5510 | 2927 | 2842.9 | 4196.6 | 1191.6 | 0.6815 | 6.111
2024-12-09 | 15:46 | Data | 0 | 31.846 | 30.171 | 189.162 | 7.65 | 177.588 | 2114.06 | 26.07 | 45.727 | 6.37 | 1.356 | 4.768 | 8485.96 | 1.816 | 97.8 | 77.9 | 1374 | 22.86 | 5515.9 | 2927.9 | 2852.2 | 4203.8 | 1191.6 | 0.67951 | 6.125
2024-12-09 | 15:46 | Data | 0 | 32.028 | 29.739 | 189.117 | 7.65 | 177.543 | 2114.06 | 26.06 | 45.727 | 6.37 | 1.364 | 4.768 | 8490.48 | 2.268 | 97.8 | 77.8 | 1374 | 22.82 | 5518.8 | 2928.4 | 2848.4 | 4202.8 | 1191.6 | 0.68098 | 6.132
2024-12-09 | 15:46 | Data | 0 | 31.913 | 29.955 | 189.117 | 7.65 | 177.588 | 2114.06 | 26.06 | 45.727 | 6.37 | 1.358 | 4.758 | 8467.87 | 2.032 | 97.8 | 77.8 | 1374 | 22.82 | 5504.1 | 2926.3 | 2864.5 | 4214 | 1191.6 | 0.67755 | 6.115
2024-12-09 | 15:46 | Data | 0 | 32.278 | 29.962 | 189.253 | 7.65 | 177.588 | 2114.06 | 26.06 | 45.637 | 6.37 | 1.355 | 4.721 | 8472.39 | 2.12 | 97.8 | 77.7 | 1374 | 22.86 | 5507.1 | 2928.6 | 2852 | 4202 | 1191.6 | 0.68002 | 6.076
2024-12-09 | 15:46 | Data | 0 | 32.379 | 30.016 | 189.298 | 7.65 | 177.588 | 2114.06 | 26.06 | 45.818 | 6.38 | 1.359 | 4.757 | 8467.87 | 2.235 | 97.8 | 77.8 | 1374 | 22.86 | 5504.1 | 2921.4 | 2885.5 | 4222.9 | 1191.6 | 0.6748 | 6.116
2024-12-09 | 15:46 | Data | 0 | 32.035 | 30.131 | 189.388 | 7.65 | 177.679 | 2117.68 | 26.06 | 45.727 | 6.37 | 1.356 | 4.732 | 8467.87 | 1.897 | 97.8 | 77.7 | 1376 | 22.86 | 5504.1 | 2922.7 | 2845.5 | 4191.9 | 1191.6 | 0.68059 | 6.088
2024-12-09 | 15:46 | Data | 0 | 32.264 | 29.962 | 189.208 | 7.65 | 177.588 | 2117.68 | 26.06 | 45.818 | 6.36 | 1.355 | 4.744 | 8467.87 | 2.127 | 97.8 | 77.8 | 1378 | 22.86 | 5504.1 | 2928.4 | 2843.8 | 4197.5 | 1191.6 | 0.68106 | 6.1
2024-12-09 | 15:46 | Data | 0 | 32.318 | 29.976 | 189.253 | 7.65 | 177.634 | 2116.78 | 26.07 | 45.637 | 6.36 | 1.358 | 4.746 | 8472.39 | 2.181 | 97.8 | 77.7 | 1377 | 22.82 | 5507.1 | 2938.6 | 2844.6 | 4203.8 | 1191.6 | 0.6819 | 6.103
2024-12-09 | 15:46 | Data | 0 | 32.177 | 30.171 | 189.208 | 7.65 | 177.588 | 2114.97 | 26.06 | 45.727 | 6.37 | 1.358 | 4.768 | 8467.87 | 2.268 | 97.8 | 77.8 | 1375 | 22.86 | 5504.1 | 2940.1 | 2831.3 | 4194 | 1191.6 | 0.68385 | 6.127
2024-12-09 | 15:46 | Data | 0 | 32.028 | 30.009 | 188.981 | 7.65 | 177.588 | 2114.06 | 26.06 | 45.727 | 6.37 | 1.357 | 4.753 | 8458.83 | 2.066 | 97.8 | 77.8 | 1374 | 22.86 | 5498.2 | 2925.1 | 2836.4 | 4198.4 | 1191.6 | 0.68163 | 6.11
2024-12-09 | 15:46 | Data | 0 | 32.102 | 29.962 | 189.162 | 7.65 | 177.588 | 2114.97 | 26.06 | 45.727 | 6.37 | 1.358 | 4.732 | 8476.91 | 2.093 | 97.8 | 77.7 | 1375 | 22.82 | 5510 | 2915.9 | 2813.3 | 4183.1 | 1191.6 | 0.68207 | 6.09
2024-12-09 | 15:46 | Data | 0 | 32.035 | 29.962 | 189.253 | 7.65 | 177.634 | 2114.06 | 26.06 | 45.727 | 6.37 | 1.358 | 4.759 | 8440.74 | 2.066 | 97.8 | 77.8 | 1374 | 22.86 | 5486.5 | 2919 | 2844.8 | 4192.8 | 1191.6 | 0.68099 | 6.117
2024-12-09 | 15:47 | Data | 0 | 32.042 | 30.131 | 189.343 | 7.65 | 177.543 | 2114.97 | 26.07 | 45.727 | 6.37 | 1.355 | 4.749 | 8436.21 | 2.079 | 97.8 | 77.8 | 1376 | 22.91 | 5483.5 | 2915.4 | 2822.2 | 4172.5 | 1191.6 | 0.68289 | 6.104
2024-12-09 | 15:47 | Data | 0 | 32.264 | 29.962 | 189.208 | 7.65 | 177.634 | 2117.68 | 26.06 | 45.727 | 6.37 | 1.34 | 4.784 | 8436.21 | 2.093 | 97.8 | 78.1 | 1376 | 22.91 | 5483.5 | 2927.6 | 2836.1 | 4191.5 | 1191.6 | 0.68239 | 6.124
2024-12-09 | 15:47 | Data | 0 | 32.089 | 29.982 | 189.162 | 7.65 | 177.588 | 2117.68 | 26.07 | 45.727 | 6.37 | 1.341 | 4.757 | 8422.65 | 2.019 | 97.8 | 78 | 1376 | 22.86 | 5474.7 | 2922.7 | 2807.5 | 4161.6 | 1191.6 | 0.68422 | 6.099
2024-12-09 | 15:47 | Data | 0 | 32.143 | 29.962 | 189.208 | 7.65 | 177.543 | 2118.58 | 26.06 | 45.727 | 6.37 | 1.348 | 4.768 | 8427.17 | 2.093 | 97.8 | 77.9 | 1376 | 22.82 | 5477.7 | 2905.2 | 2828.1 | 4176.1 | 1191.6 | 0.68024 | 6.117
2024-12-09 | 15:47 | Data | 0 | 32.379 | 30.394 | 189.253 | 7.65 | 177.679 | 2118.58 | 26.06 | 45.818 | 6.37 | 1.351 | 4.77 | 8422.65 | 2.086 | 97.8 | 77.9 | 1376 | 22.86 | 5474.7 | 2919.9 | 2817.2 | 4172.6 | 1191.6 | 0.6824 | 6.122
2024-12-09 | 15:47 | Data | 0 | 32.028 | 30.07 | 189.117 | 7.65 | 177.634 | 2113.16 | 26.06 | 45.727 | 6.37 | 1.353 | 4.757 | 8418.13 | 2.194 | 97.8 | 77.8 | 1374 | 22.86 | 5471.8 | 2915.9 | 2828.3 | 4177.4 | 1191.6 | 0.68148 | 6.111
2024-12-09 | 15:47 | Data | 0 | 32.028 | 30.34 | 189.298 | 7.65 | 177.588 | 2114.97 | 26.05 | 45.727 | 6.37 | 1.353 | 4.754 | 8431.69 | 2.025 | 97.8 | 77.9 | 1374 | 22.86 | 5480.6 | 2929.3 | 2802.7 | 4169.5 | 1191.6 | 0.68557 | 6.106
2024-12-09 | 15:47 | Data | 0 | 32.264 | 30.246 | 189.298 | 7.65 | 177.724 | 2114.06 | 26.06 | 45.727 | 6.37 | 1.358 | 4.744 | 8440.74 | 2.039 | 97.8 | 77.7 | 1374 | 22.86 | 5486.5 | 2933.6 | 2799.7 | 4171 | 1191.6 | 0.68651 | 6.102
2024-12-09 | 15:47 | Data | 0 | 31.927 | 29.955 | 189.253 | 7.65 | 177.634 | 2114.06 | 26.07 | 45.818 | 6.37 | 1.361 | 4.748 | 8445.26 | 2.059 | 97.8 | 77.7 | 1374 | 22.86 | 5489.4 | 2927.5 | 2804.2 | 4168.2 | 1191.7 | 0.68589 | 6.109
2024-12-09 | 15:47 | Data | 0 | 31.927 | 29.955 | 189.208 | 7.65 | 177.634 | 2117.68 | 26.07 | 45.727 | 6.37 | 1.366 | 4.726 | 8440.74 | 2.025 | 97.8 | 77.6 | 1376 | 22.86 | 5486.5 | 2927.8 | 2826 | 4182.2 | 1191.7 | 0.68336 | 6.092
2024-12-09 | 15:47 | Data | 0 | 32.258 | 29.969 | 189.208 | 7.65 | 177.543 | 2113.16 | 26.06 | 45.637 | 6.37 | 1.361 | 4.71 | 8445.26 | 2.248 | 97.8 | 77.6 | 1374 | 22.86 | 5489.4 | 2918.9 | 2812.9 | 4170.5 | 1191.7 | 0.68424 | 6.07
2024-12-09 | 15:47 | Data | 0 | 32.028 | 30.394 | 189.298 | 7.65 | 177.634 | 2114.97 | 26.06 | 45.547 | 6.36 | 1.359 | 4.711 | 8427.17 | 2.012 | 97.8 | 77.6 | 1374 | 22.77 | 5477.7 | 2920.4 | 2814 | 4176.2 | 1191.7 | 0.68465 | 6.069
2024-12-09 | 15:47 | Data | 0 | 32.035 | 29.955 | 189.388 | 7.65 | 177.634 | 2117.68 | 26.06 | 45.727 | 6.37 | 1.349 | 4.739 | 8404.56 | 2.073 | 97.8 | 77.8 | 1376 | 22.91 | 5463 | 2914.4 | 2814.2 | 4164.4 | 1191.7 | 0.68275 | 6.087
2024-12-09 | 15:47 | Data | 0 | 32.595 | 30.408 | 189.298 | 7.65 | 177.679 | 2112.26 | 26.06 | 45.727 | 6.37 | 1.357 | 4.729 | 8390.99 | 2.174 | 97.8 | 77.7 | 1372 | 22.86 | 5454.1 | 2926.6 | 2826.9 | 4178.1 | 1191.7 | 0.68358 | 6.086
2024-12-09 | 15:47 | Data | 0 | 32.042 | 30.131 | 189.434 | 7.65 | 177.634 | 2114.97 | 26.06 | 45.727 | 6.37 | 1.359 | 4.738 | 8409.08 | 2.079 | 97.8 | 77.7 | 1375 | 22.86 | 5465.9 | 2926.4 | 2821.4 | 4198 | 1191.7 | 0.68565 | 6.098
2024-12-09 | 15:47 | Data | 0 | 32.096 | 29.982 | 189.388 | 7.65 | 177.724 | 2118.58 | 26.07 | 45.637 | 6.37 | 1.36 | 4.745 | 8431.69 | 2.032 | 97.9 | 77.7 | 1377 | 22.82 | 5480.6 | 2918.3 | 2830.8 | 4181.3 | 1191.7 | 0.68226 | 6.105
2024-12-09 | 15:47 | Data | 0 | 32.372 | 30.07 | 189.208 | 7.65 | 177.588 | 2116.78 | 26.06 | 45.637 | 6.37 | 1.359 | 4.754 | 8436.21 | 2.106 | 97.8 | 77.8 | 1376 | 22.86 | 5483.5 | 2924.6 | 2831.2 | 4187.2 | 1191.7 | 0.68059 | 6.113
2024-12-09 | 15:47 | Data | 0 | 32.237 | 30.408 | 189.343 | 7.65 | 177.724 | 2117.68 | 26.07 | 45.727 | 6.37 | 1.352 | 4.759 | 8436.21 | 2.187 | 97.8 | 77.9 | 1376 | 22.86 | 5483.5 | 2929.5 | 2868.2 | 4197.1 | 1191.7 | 0.68179 | 6.111
2024-12-09 | 15:48 | Data | 0 | 32.433 | 29.969 | 189.343 | 7.65 | 177.634 | 2119.49 | 26.05 | 45.908 | 6.37 | 1.362 | 4.754 | 8440.74 | 2.174 | 97.8 | 77.7 | 1377 | 23 | 5486.5 | 2922.7 | 2853.6 | 4202.6 | 1191.7 | 0.67919 | 6.113
2024-12-09 | 15:48 | Data | 0 | 32.467 | 30.361 | 189.388 | 7.65 | 177.724 | 2116.78 | 26.06 | 46.089 | 6.37 | 1.369 | 4.757 | 8449.78 | 2.187 | 97.8 | 77.7 | 1376 | 23 | 5492.4 | 2914.4 | 2832.8 | 4179.3 | 1191.7 | 0.68048 | 6.124
2024-12-09 | 15:48 | Data | 0 | 32.15 | 30.043 | 189.388 | 7.65 | 177.679 | 2118.58 | 26.06 | 45.998 | 6.37 | 1.358 | 4.753 | 8463.35 | 1.904 | 97.8 | 77.8 | 1376 | 22.95 | 5501.2 | 2943.1 | 2845 | 4206.8 | 1191.7 | 0.68333 | 6.111
2024-12-09 | 15:48 | Data | 0 | 32.035 | 29.962 | 189.208 | 7.65 | 177.588 | 2120.39 | 26.07 | 45.998 | 6.36 | 1.358 | 4.748 | 8467.87 | 2.032 | 97.8 | 77.8 | 1378 | 23 | 5504.1 | 2911.5 | 2840.9 | 4188.6 | 1191.7 | 0.67895 | 6.105
2024-12-09 | 15:48 | Data | 0 | 32.048 | 29.955 | 189.162 | 7.64 | 177.634 | 2120.39 | 26.06 | 45.998 | 6.36 | 1.358 | 4.765 | 8472.39 | 1.965 | 97.8 | 77.8 | 1378 | 22.95 | 5507.1 | 2917.4 | 2833.5 | 4183.1 | 1191.7 | 0.67972 | 6.122
2024-12-09 | 15:48 | Data | 0 | 32.204 | 29.955 | 189.162 | 7.65 | 177.588 | 2120.39 | 26.07 | 45.908 | 6.36 | 1.356 | 4.769 | 8472.39 | 2.282 | 97.8 | 77.9 | 1378 | 23 | 5507.1 | 2918.8 | 2829.3 | 4178.7 | 1191.7 | 0.68143 | 6.124
2024-12-09 | 15:48 | Data | 0 | 32.366 | 30.185 | 189.298 | 7.65 | 177.679 | 2121.29 | 26.06 | 45.998 | 6.37 | 1.348 | 4.738 | 8445.26 | 2.093 | 97.8 | 77.8 | 1378 | 23 | 5489.4 | 2907.8 | 2822.7 | 4166.2 | 1191.7 | 0.68117 | 6.086
2024-12-09 | 15:48 | Data | 0 | 32.271 | 29.962 | 189.253 | 7.65 | 177.679 | 2123.1 | 26.06 | 45.998 | 6.37 | 1.361 | 4.769 | 8449.78 | 2.079 | 97.8 | 77.8 | 1380 | 23 | 5492.4 | 2921.8 | 2817.4 | 4175.8 | 1191.7 | 0.68289 | 6.13
2024-12-09 | 15:48 | Data | 0 | 32.028 | 30.246 | 189.253 | 7.65 | 177.724 | 2123.1 | 26.06 | 45.908 | 6.36 | 1.365 | 4.749 | 8431.69 | 2.194 | 97.8 | 77.7 | 1379 | 22.95 | 5480.6 | 2906 | 2816.2 | 4165.7 | 1191.7 | 0.68019 | 6.113
2024-12-09 | 15:48 | Data | 0 | 32.028 | 29.955 | 189.117 | 7.65 | 177.543 | 2122.2 | 26.07 | 45.998 | 6.37 | 1.351 | 4.747 | 8431.69 | 2.059 | 97.8 | 77.8 | 1380 | 22.91 | 5480.6 | 2935.2 | 2831.3 | 4194.1 | 1191.7 | 0.68419 | 6.1
2024-12-09 | 15:48 | Data | 0 | 32.15 | 30.293 | 189.343 | 7.64 | 177.634 | 2123.1 | 26.07 | 45.908 | 6.37 | 1.343 | 4.745 | 8467.87 | 2.356 | 97.8 | 77.9 | 1380 | 23 | 5504.1 | 2916.2 | 2823.6 | 4176.5 | 1191.7 | 0.6806 | 6.088
2024-12-09 | 15:48 | Data | 0 | 31.947 | 29.746 | 189.162 | 7.65 | 177.679 | 2122.2 | 26.07 | 45.908 | 6.36 | 1.348 | 4.742 | 8467.87 | 2.059 | 97.8 | 77.9 | 1379 | 23.04 | 5504.1 | 2922.5 | 2834.4 | 4183.7 | 1191.7 | 0.68262 | 6.09
2024-12-09 | 15:48 | Data | 0 | 32.406 | 30.293 | 189.388 | 7.65 | 177.724 | 2123.1 | 26.06 | 45.908 | 6.36 | 1.343 | 4.757 | 8897.48 | 2.282 | 97.8 | 78 | 1380 | 23.04 | 5783.4 | 2922.3 | 2836.4 | 4187.7 | 1191.7 | 0.68174 | 6.1
2024-12-09 | 15:48 | Data | 0 | 32.042 | 30.043 | 189.208 | 7.65 | 177.634 | 2124.01 | 26.07 | 45.998 | 6.37 | 1.351 | 4.756 | 8467.87 | 2.127 | 97.8 | 77.9 | 1379 | 23 | 5504.1 | 2922.2 | 2854.8 | 4202.5 | 1191.7 | 0.67842 | 6.108
2024-12-09 | 15:48 | Data | 0 | 32.102 | 29.935 | 189.253 | 7.65 | 177.679 | 2116.78 | 26.06 | 45.998 | 6.37 | 1.348 | 4.768 | 8472.39 | 1.904 | 97.8 | 78 | 1375 | 22.95 | 5507.1 | 2932.2 | 2826.7 | 4188.9 | 1191.7 | 0.68341 | 6.115
2024-12-09 | 15:48 | Data | 0 | 32.494 | 30.239 | 189.434 | 7.65 | 177.814 | 2113.16 | 26.06 | 45.998 | 6.37 | 1.354 | 4.782 | 8476.91 | 2.255 | 97.8 | 77.9 | 1374 | 23 | 5510 | 2927.7 | 2832.8 | 4191.8 | 1191.7 | 0.68149 | 6.136
2024-12-09 | 15:48 | Data | 0 | 32.548 | 30.084 | 189.388 | 7.64 | 177.769 | 2114.06 | 26.07 | 45.908 | 6.37 | 1.355 | 4.77 | 8472.39 | 2.113 | 97.8 | 77.9 | 1374 | 22.95 | 5507.1 | 2908.8 | 2815.4 | 4166.6 | 1191.7 | 0.68102 | 6.126
2024-12-09 | 15:48 | Data | 0 | 32.258 | 30.171 | 189.162 | 7.65 | 177.679 | 2114.97 | 26.06 | 45.998 | 6.37 | 1.358 | 4.768 | 8467.87 | 2.1 | 97.8 | 77.8 | 1374 | 23 | 5504.1 | 2924.7 | 2813.4 | 4174.3 | 1191.7 | 0.68503 | 6.123
2024-12-09 | 15:49 | Data | 0 | 32.177 | 30.016 | 189.388 | 7.65 | 177.769 | 2114.06 | 26.06 | 46.089 | 6.37 | 1.355 | 4.765 | 8458.83 | 1.917 | 97.8 | 77.9 | 1374 | 23.04 | 5498.2 | 2934.1 | 2820.5 | 4184.6 | 1191.7 | 0.68555 | 6.12
2024-12-09 | 15:49 | Data | 0 | 32.48 | 30.3 | 189.434 | 7.65 | 177.724 | 2114.97 | 26.06 | 45.998 | 6.36 | 1.353 | 4.748 | 8472.39 | 2.194 | 97.8 | 77.8 | 1375 | 23 | 5507.1 | 2929.7 | 2825 | 4185.6 | 1191.7 | 0.68369 | 6.102
2024-12-09 | 15:49 | Data | 0 | 32.163 | 30.178 | 189.162 | 7.65 | 177.679 | 2113.16 | 26.07 | 45.908 | 6.36 | 1.362 | 4.744 | 8467.87 | 2.052 | 97.8 | 77.7 | 1374 | 23 | 5504.1 | 2944.8 | 2819.1 | 4190.7 | 1191.7 | 0.68638 | 6.106
2024-12-09 | 15:49 | Data | 0 | 32.494 | 30.03 | 189.479 | 7.65 | 177.769 | 2114.06 | 26.07 | 45.998 | 6.37 | 1.361 | 4.717 | 8454.3 | 2.079 | 97.8 | 77.6 | 1374 | 22.95 | 5495.3 | 2925.2 | 2806.8 | 4171.4 | 1191.7 | 0.68443 | 6.08
2024-12-09 | 15:49 | Data | 0 | 32.055 | 30.138 | 189.253 | 7.64 | 177.724 | 2114.06 | 26.07 | 45.998 | 6.37 | 1.354 | 4.732 | 8472.39 | 2.073 | 97.8 | 77.8 | 1373 | 23 | 5507.1 | 2925.8 | 2802.7 | 4169.3 | 1191.7 | 0.6858 | 6.086
2024-12-09 | 15:49 | Data | 0 | 32.237 | 30.408 | 189.434 | 7.65 | 177.724 | 2114.06 | 26.06 | 45.998 | 6.37 | 1.348 | 4.748 | 8458.83 | 2.167 | 97.8 | 77.9 | 1374 | 22.95 | 5498.2 | 2930.2 | 2799.9 | 4169.5 | 1191.7 | 0.68582 | 6.097
2024-12-09 | 15:49 | Data | 0 | 32.264 | 29.989 | 189.162 | 7.64 | 177.679 | 2114.06 | 26.06 | 45.908 | 6.37 | 1.355 | 4.772 | 8481.44 | 2.241 | 97.8 | 77.9 | 1375 | 23 | 5512.9 | 2929.5 | 2837.3 | 4191.6 | 1191.7 | 0.68326 | 6.127
2024-12-09 | 15:49 | Data | 0 | 32.251 | 29.969 | 189.388 | 7.65 | 177.634 | 2114.06 | 26.06 | 45.637 | 6.36 | 1.363 | 4.762 | 8467.87 | 2.248 | 97.8 | 77.7 | 1374 | 22.82 | 5504.1 | 2929.5 | 2844.9 | 4207 | 1191.7 | 0.68006 | 6.125
2024-12-09 | 15:49 | Data | 0 | 32.575 | 30.286 | 189.208 | 7.65 | 177.634 | 2117.68 | 26.06 | 45.908 | 6.36 | 1.361 | 4.757 | 8467.87 | 2.147 | 97.8 | 77.8 | 1376 | 23 | 5504.1 | 2930.9 | 2854.9 | 4205.8 | 1191.8 | 0.68099 | 6.115
2024-12-09 | 15:49 | Data | 0 | 32.291 | 30.185 | 189.343 | 7.65 | 177.724 | 2112.26 | 26.06 | 45.908 | 6.37 | 1.358 | 4.747 | 8467.87 | 2.079 | 97.8 | 77.8 | 1373 | 23 | 5504.1 | 2919.2 | 2832.3 | 4190.8 | 1191.8 | 0.68256 | 6.104
2024-12-09 | 15:49 | Data | 0 | 32.258 | 30.3 | 189.388 | 7.65 | 177.588 | 2114.97 | 26.06 | 45.998 | 6.37 | 1.348 | 4.754 | 8467.87 | 2.086 | 97.8 | 77.9 | 1374 | 23 | 5504.1 | 2932.1 | 2824.7 | 4186.2 | 1191.8 | 0.68464 | 6.099
2024-12-09 | 15:49 | Data | 0 | 32.042 | 30.388 | 189.388 | 7.64 | 177.769 | 2113.16 | 26.06 | 45.998 | 6.36 | 1.355 | 4.78 | 8463.35 | 2.059 | 97.8 | 77.9 | 1374 | 23 | 5501.2 | 2923.1 | 2855.6 | 4204.2 | 1191.8 | 0.67872 | 6.135
2024-12-09 | 15:49 | Data | 0 | 32.271 | 30.198 | 189.343 | 7.65 | 177.769 | 2114.97 | 26.07 | 45.998 | 6.36 | 1.36 | 4.767 | 8458.83 | 1.938 | 97.8 | 77.8 | 1376 | 23 | 5498.2 | 2927.3 | 2824.4 | 4183.7 | 1191.8 | 0.68335 | 6.129
2024-12-09 | 15:49 | Data | 0 | 31.812 | 29.955 | 189.253 | 7.65 | 177.724 | 2117.68 | 26.07 | 45.998 | 6.37 | 1.358 | 4.74 | 8449.78 | 1.958 | 97.8 | 77.7 | 1376 | 22.95 | 5492.4 | 2918.4 | 2816.7 | 4170.4 | 1191.8 | 0.68313 | 6.098
2024-12-09 | 15:49 | Data | 0 | 32.69 | 30.415 | 189.388 | 7.65 | 177.814 | 2014.64 | 26.07 | 46.089 | 6.37 | 1.344 | 4.765 | 8445.26 | 2.133 | 97.7 | 78 | 1311 | 23.04 | 5489.4 | 2939.5 | 2802.9 | 4178.2 | 1191.8 | 0.68662 | 6.109
2024-12-09 | 15:49 | Data | 0 | 32.163 | 30.55 | 189.434 | 7.65 | 177.724 | 2120.39 | 26.07 | 45.908 | 6.37 | 1.358 | 4.749 | 8458.83 | 1.877 | 97.8 | 77.8 | 1378 | 22.95 | 5498.2 | 2926.3 | 2831.9 | 4194.7 | 1191.8 | 0.68141 | 6.108
2024-12-09 | 15:49 | Data | 0 | 32.433 | 30.239 | 189.298 | 7.64 | 177.769 | 2120.39 | 26.06 | 45.998 | 6.37 | 1.358 | 4.768 | 8445.26 | 2.194 | 97.8 | 77.8 | 1378 | 22.95 | 5489.4 | 2927.9 | 2809.4 | 4172.3 | 1191.8 | 0.68566 | 6.127
2024-12-09 | 15:50 | Data | 0 | 32.042 | 30.016 | 189.298 | 7.65 | 177.588 | 2120.39 | 26.07 | 45.637 | 6.37 | 1.357 | 4.775 | 8445.26 | 2.133 | 97.8 | 77.9 | 1379 | 22.86 | 5489.4 | 2932.9 | 2824.7 | 4189.8 | 1191.8 | 0.6828 | 6.131
2024-12-09 | 15:50 | Data | 0 | 32.453 | 30.523 | 189.388 | 7.65 | 177.769 | 2114.97 | 26.07 | 45.998 | 6.37 | 1.363 | 4.775 | 8458.83 | 2.093 | 97.8 | 77.8 | 1374 | 22.95 | 5498.2 | 2921.4 | 2837.7 | 4190.9 | 1191.8 | 0.67993 | 6.138
2024-12-09 | 15:50 | Data | 0 | 32.035 | 30.3 | 189.388 | 7.65 | 177.679 | 2119.49 | 26.06 | 45.998 | 6.36 | 1.361 | 4.782 | 8458.83 | 1.965 | 97.8 | 77.8 | 1378 | 23 | 5498.2 | 2928.3 | 2828 | 4190.5 | 1191.8 | 0.68249 | 6.146
2024-12-09 | 15:50 | Data | 0 | 32.271 | 30.185 | 189.343 | 7.65 | 177.724 | 2120.39 | 26.06 | 45.547 | 6.36 | 1.358 | 4.769 | 8666.85 | 2.079 | 97.9 | 77.8 | 1378 | 22.73 | 5633.5 | 2934.1 | 2821 | 4184.6 | 1191.8 | 0.68555 | 6.128
2024-12-09 | 15:50 | Data | 0 | 32.19 | 30.077 | 189.298 | 7.65 | 177.769 | 2119.49 | 26.07 | 45.998 | 6.37 | 1.356 | 4.785 | 8657.8 | 1.992 | 97.8 | 77.9 | 1378 | 23 | 5627.6 | 2920.7 | 2822 | 4176.6 | 1191.8 | 0.68298 | 6.14
2024-12-09 | 15:50 | Data | 0 | 32.46 | 29.962 | 189.343 | 7.65 | 177.724 | 2120.39 | 26.07 | 45.818 | 6.37 | 1.355 | 4.774 | 8671.37 | 2.214 | 97.8 | 77.9 | 1378 | 22.86 | 5636.4 | 2917.1 | 2806.3 | 4163.4 | 1191.8 | 0.68435 | 6.13
2024-12-09 | 15:50 | Data | 0 | 32.163 | 30.171 | 189.298 | 7.65 | 177.769 | 2120.39 | 26.05 | 45.727 | 6.36 | 1.348 | 4.742 | 8662.33 | 2.039 | 97.8 | 77.9 | 1378 | 22.86 | 5630.5 | 2931.3 | 2829.3 | 4192.5 | 1191.8 | 0.68241 | 6.09
2024-12-09 | 15:50 | Data | 0 | 32.264 | 30.185 | 189.343 | 7.64 | 177.724 | 2120.39 | 26.07 | 45.818 | 6.37 | 1.352 | 4.747 | 8499.53 | 2.079 | 97.8 | 77.8 | 1378 | 22.86 | 5524.7 | 2932.2 | 2817.2 | 4180 | 1191.8 | 0.68635 | 6.098
2024-12-09 | 15:50 | Data | 0 | 32.028 | 30.07 | 189.298 | 7.64 | 177.679 | 2114.97 | 26.07 | 45.637 | 6.37 | 1.355 | 4.75 | 8481.44 | 2.079 | 97.8 | 77.8 | 1375 | 22.82 | 5512.9 | 2917.2 | 2830.1 | 4184.5 | 1191.8 | 0.68118 | 6.106
2024-12-09 | 15:50 | Data | 0 | 32.089 | 30.077 | 189.253 | 7.65 | 177.679 | 2120.39 | 26.07 | 45.637 | 6.36 | 1.352 | 4.756 | 8467.87 | 2.079 | 97.8 | 77.9 | 1378 | 22.86 | 5504.1 | 2918.2 | 2809 | 4168.4 | 1191.8 | 0.68304 | 6.105
2024-12-09 | 15:50 | Data | 0 | 32.264 | 30.144 | 189.343 | 7.65 | 177.679 | 2119.49 | 26.07 | 45.727 | 6.36 | 1.345 | 4.748 | 8458.83 | 2.167 | 97.8 | 77.9 | 1378 | 22.82 | 5498.2 | 2913.4 | 2816.6 | 4166.7 | 1191.8 | 0.68237 | 6.092
2024-12-09 | 15:50 | Data | 0 | 31.866 | 30.131 | 189.298 | 7.64 | 177.724 | 2119.49 | 26.06 | 45.727 | 6.36 | 1.352 | 4.777 | 8476.91 | 2.046 | 97.8 | 77.9 | 1377 | 22.77 | 5510 | 2925.5 | 2844.2 | 4195 | 1191.8 | 0.68222 | 6.13
2024-12-09 | 15:50 | Data | 0 | 32.264 | 30.354 | 189.253 | 7.64 | 177.724 | 2120.39 | 26.06 | 45.818 | 6.36 | 1.364 | 4.764 | 8476.91 | 2.079 | 97.8 | 77.8 | 1378 | 22.86 | 5510 | 2917.2 | 2827.5 | 4178.2 | 1191.8 | 0.68149 | 6.127
2024-12-09 | 15:50 | Data | 0 | 32.379 | 30.408 | 189.434 | 7.65 | 177.679 | 2120.39 | 26.05 | 45.637 | 6.37 | 1.36 | 4.756 | 8476.91 | 2.208 | 97.8 | 77.8 | 1378 | 22.86 | 5510 | 2914.3 | 2826.8 | 4176.5 | 1191.8 | 0.68156 | 6.115
2024-12-09 | 15:50 | Data | 0 | 32.494 | 29.969 | 189.388 | 7.65 | 177.769 | 2117.68 | 26.06 | 45.637 | 6.37 | 1.362 | 4.746 | 8481.44 | 2.059 | 97.8 | 77.7 | 1376 | 22.86 | 5512.9 | 2917 | 2821.7 | 4176.8 | 1191.8 | 0.68069 | 6.107
2024-12-09 | 15:50 | Data | 0 | 32.251 | 30.185 | 189.298 | 7.65 | 177.634 | 2110.45 | 26.06 | 45.727 | 6.36 | 1.352 | 4.752 | 8481.44 | 2.073 | 97.8 | 77.9 | 1372 | 22.91 | 5512.9 | 2949.6 | 2824.1 | 4195.1 | 1191.8 | 0.68696 | 6.105
2024-12-09 | 15:50 | Data | 0 | 32.15 | 30.273 | 189.298 | 7.65 | 177.769 | 2117.68 | 26.06 | 45.727 | 6.36 | 1.354 | 4.744 | 8472.39 | 2.167 | 97.8 | 77.8 | 1376 | 22.86 | 5507.1 | 2926.2 | 2831.2 | 4187.4 | 1191.8 | 0.68107 | 6.098
2024-12-09 | 15:51 | Data | 0 | 32.204 | 30.131 | 189.343 | 7.65 | 177.724 | 2117.68 | 26.06 | 45.727 | 6.36 | 1.358 | 4.74 | 8481.44 | 2.282 | 97.8 | 77.7 | 1376 | 22.86 | 5512.9 | 2922.9 | 2810.1 | 4170 | 1191.8 | 0.68392 | 6.097
2024-12-09 | 15:51 | Data | 0 | 32.575 | 30.239 | 189.208 | 7.64 | 177.814 | 2117.68 | 26.06 | 45.727 | 6.37 | 1.352 | 4.779 | 8467.87 | 2.147 | 97.8 | 77.9 | 1376 | 22.86 | 5504.1 | 2934.4 | 2817.9 | 4186.4 | 1191.8 | 0.68492 | 6.131
2024-12-09 | 15:51 | Data | 0 | 32.237 | 30.502 | 189.343 | 7.64 | 177.724 | 2120.39 | 26.07 | 45.727 | 6.38 | 1.351 | 4.735 | 8472.39 | 2.221 | 97.8 | 77.8 | 1378 | 22.86 | 5507.1 | 2941 | 2815.7 | 4185.3 | 1191.8 | 0.68384 | 6.087
2024-12-09 | 15:51 | Data | 0 | 32.744 | 30.205 | 189.388 | 7.64 | 177.769 | 2116.78 | 26.07 | 45.818 | 6.36 | 1.349 | 4.729 | 8458.83 | 2.228 | 97.8 | 77.8 | 1376 | 22.86 | 5498.2 | 2932.9 | 2807.3 | 4176.9 | 1191.8 | 0.6867 | 6.079
2024-12-09 | 15:51 | Data | 0 | 32.102 | 29.969 | 189.434 | 7.65 | 177.769 | 2118.58 | 26.06 | 45.818 | 6.37 | 1.354 | 4.767 | 8472.39 | 2.073 | 97.8 | 77.9 | 1376 | 22.86 | 5507.1 | 2919.9 | 2833.2 | 4190.7 | 1191.8 | 0.68463 | 6.119
2024-12-09 | 15:51 | Data | 0 | 32.264 | 30.266 | 189.343 | 7.64 | 177.769 | 2119.49 | 26.06 | 45.637 | 6.37 | 1.358 | 4.751 | 8680.41 | 2.1 | 97.8 | 77.8 | 1378 | 22.86 | 5642.3 | 2923.6 | 2822.4 | 4181.9 | 1191.8 | 0.68147 | 6.109
2024-12-09 | 15:51 | Data | 0 | 32.291 | 30.185 | 189.434 | 7.64 | 177.724 | 2121.29 | 26.07 | 45.637 | 6.36 | 1.357 | 4.744 | 8680.41 | 2.086 | 97.8 | 77.8 | 1378 | 22.91 | 5642.3 | 2923.4 | 2801.1 | 4159.6 | 1191.8 | 0.68413 | 6.102
2024-12-09 | 15:51 | Data | 0 | 32.487 | 30.239 | 189.434 | 7.65 | 177.724 | 2120.39 | 26.06 | 45.818 | 6.37 | 1.345 | 4.746 | 8680.41 | 2.086 | 97.8 | 77.9 | 1378 | 22.86 | 5642.3 | 2930.7 | 2843.9 | 4199.5 | 1191.8 | 0.68185 | 6.09
2024-12-09 | 15:51 | Data | 0 | 32.494 | 30.212 | 189.343 | 7.64 | 177.86 | 2120.39 | 26.06 | 45.908 | 6.37 | 1.354 | 4.742 | 8689.46 | 2.106 | 97.8 | 77.8 | 1379 | 22.91 | 5648.1 | 2917.3 | 2826.2 | 4180.8 | 1191.8 | 0.68164 | 6.097
2024-12-09 | 15:51 | Data | 0 | 32.298 | 30.307 | 189.388 | 7.64 | 177.814 | 2120.39 | 26.07 | 45.818 | 6.37 | 1.356 | 4.744 | 8499.53 | 2.079 | 97.8 | 77.8 | 1378 | 22.95 | 5524.7 | 2941.2 | 2838.7 | 4195.4 | 1191.9 | 0.68363 | 6.098
2024-12-09 | 15:51 | Data | 0 | 32.44 | 30.239 | 189.343 | 7.64 | 177.769 | 2116.78 | 26.07 | 45.908 | 6.36 | 1.356 | 4.731 | 8499.53 | 2.181 | 97.8 | 77.7 | 1376 | 23 | 5524.7 | 2932 | 2835.2 | 4195.7 | 1191.9 | 0.68252 | 6.086
2024-12-09 | 15:51 | Data | 0 | 32.264 | 30.455 | 189.253 | 7.64 | 177.769 | 2119.49 | 26.07 | 45.998 | 6.37 | 1.364 | 4.747 | 8485.96 | 2.012 | 97.8 | 77.7 | 1378 | 23 | 5515.9 | 2933.6 | 2847 | 4205.7 | 1191.9 | 0.68153 | 6.111
2024-12-09 | 15:51 | Data | 0 | 32.494 | 30.415 | 189.434 | 7.64 | 177.814 | 2120.39 | 26.06 | 46.089 | 6.36 | 1.362 | 4.768 | 8495 | 2.079 | 97.8 | 77.8 | 1378 | 23 | 5521.8 | 2933.5 | 2829.9 | 4194.9 | 1191.9 | 0.68143 | 6.13
2024-12-09 | 15:51 | Data | 0 | 32.028 | 30.178 | 189.343 | 7.64 | 177.724 | 2120.39 | 26.06 | 45.998 | 6.37 | 1.361 | 4.773 | 8481.44 | 2.032 | 97.8 | 77.8 | 1378 | 23 | 5512.9 | 2937 | 2846.8 | 4205.1 | 1191.9 | 0.68239 | 6.133
2024-12-09 | 15:51 | Data | 0 | 32.575 | 30.401 | 189.343 | 7.65 | 177.769 | 2120.39 | 26.07 | 45.998 | 6.37 | 1.358 | 4.743 | 8476.91 | 2.147 | 97.8 | 77.7 | 1378 | 23.04 | 5510 | 2932.5 | 2829.4 | 4191.6 | 1191.9 | 0.68323 | 6.101
2024-12-09 | 15:51 | Data | 0 | 32.264 | 30.388 | 189.253 | 7.64 | 177.724 | 2118.58 | 26.07 | 45.998 | 6.37 | 1.346 | 4.752 | 8485.96 | 1.965 | 97.8 | 77.9 | 1377 | 23 | 5515.9 | 2936 | 2841.8 | 4203.5 | 1191.9 | 0.68168 | 6.098
2024-12-09 | 15:51 | Data | 0 | 32.379 | 30.286 | 189.208 | 7.64 | 177.724 | 2120.39 | 26.06 | 45.998 | 6.36 | 1.348 | 4.751 | 8472.39 | 2.079 | 97.8 | 77.9 | 1378 | 23 | 5507.1 | 2925.3 | 2825.9 | 4188.2 | 1191.9 | 0.68235 | 6.1
2024-12-09 | 15:52 | Data | 0 | 32.339 | 30.185 | 189.298 | 7.64 | 177.769 | 2120.39 | 26.07 | 45.998 | 6.37 | 1.355 | 4.746 | 8458.83 | 2.086 | 97.8 | 77.8 | 1378 | 23 | 5498.2 | 2917.9 | 2845.7 | 4194.1 | 1191.9 | 0.67928 | 6.1
2024-12-09 | 15:52 | Data | 0 | 32.487 | 30.408 | 189.343 | 7.64 | 177.814 | 2120.39 | 26.06 | 45.908 | 6.37 | 1.357 | 4.764 | 8440.74 | 2.106 | 97.8 | 77.8 | 1378 | 22.95 | 5486.5 | 2950.6 | 2842.7 | 4207.7 | 1191.9 | 0.68656 | 6.121
2024-12-09 | 15:52 | Data | 0 | 32.588 | 30.192 | 189.524 | 7.64 | 177.814 | 2117.68 | 26.06 | 45.998 | 6.37 | 1.349 | 4.737 | 8440.74 | 2.12 | 97.8 | 77.8 | 1376 | 22.95 | 5486.5 | 2933.7 | 2880.5 | 4226.4 | 1191.9 | 0.67802 | 6.086
2024-12-09 | 15:52 | Data | 0 | 32.372 | 30.124 | 189.388 | 7.64 | 177.724 | 2120.39 | 26.06 | 45.998 | 6.37 | 1.357 | 4.737 | 8445.26 | 2.194 | 97.8 | 77.7 | 1378 | 23 | 5489.4 | 2924.3 | 2893.4 | 4226.8 | 1191.9 | 0.67532 | 6.093
2024-12-09 | 15:52 | Data | 0 | 32.264 | 30.07 | 189.253 | 7.65 | 177.679 | 2120.39 | 26.07 | 45.908 | 6.36 | 1.347 | 4.724 | 8472.39 | 1.904 | 97.8 | 77.8 | 1379 | 23 | 5507.1 | 2961 | 2893.1 | 4255.9 | 1191.9 | 0.67899 | 6.072
2024-12-09 | 15:52 | Data | 0 | 31.974 | 29.955 | 189.298 | 7.64 | 177.679 | 2127.62 | 26.05 | 45.908 | 6.37 | 1.359 | 4.761 | 8449.78 | 2.241 | 97.8 | 77.8 | 1382 | 23 | 5492.4 | 2913.7 | 2814.2 | 4169.1 | 1191.9 | 0.68278 | 6.12
2024-12-09 | 15:52 | Data | 0 | 32.251 | 30.185 | 189.434 | 7.64 | 177.724 | 2120.39 | 26.06 | 45.998 | 6.36 | 1.361 | 4.792 | 8481.44 | 2.079 | 97.8 | 77.9 | 1378 | 22.95 | 5512.9 | 2947.1 | 2850.8 | 4213.9 | 1191.9 | 0.68354 | 6.153
2024-12-09 | 15:52 | Data | 0 | 31.988 | 29.915 | 189.343 | 7.64 | 177.769 | 2121.29 | 26.06 | 45.998 | 6.36 | 1.357 | 4.769 | 8472.39 | 1.971 | 97.8 | 77.9 | 1379 | 23 | 5507.1 | 2928.2 | 2836.7 | 4191.1 | 1191.9 | 0.68178 | 6.126
2024-12-09 | 15:52 | Data | 0 | 32.366 | 30.388 | 189.479 | 7.64 | 177.724 | 2120.39 | 26.06 | 45.998 | 6.37 | 1.352 | 4.76 | 8454.3 | 2.086 | 97.8 | 77.9 | 1378 | 23 | 5495.3 | 2921.9 | 2846.3 | 4194.2 | 1191.9 | 0.68098 | 6.112
2024-12-09 | 15:52 | Data | 0 | 32.264 | 30.016 | 189.298 | 7.65 | 177.769 | 2117.68 | 26.05 | 46.269 | 6.36 | 1.358 | 4.731 | 8454.3 | 2.079 | 97.8 | 77.7 | 1376 | 23.09 | 5495.3 | 2918.3 | 2838.1 | 4188.9 | 1191.9 | 0.68048 | 6.091
2024-12-09 | 15:52 | Data | 0 | 32.487 | 30.239 | 189.388 | 7.65 | 177.769 | 2114.06 | 26.06 | 45.998 | 6.36 | 1.356 | 4.744 | 8458.83 | 2.255 | 97.8 | 77.8 | 1374 | 23 | 5498.2 | 2927.4 | 2857.2 | 4199.7 | 1191.9 | 0.67936 | 6.099
2024-12-09 | 15:52 | Data | 0 | 32.487 | 30.415 | 189.388 | 7.64 | 177.769 | 2114.06 | 26.07 | 45.908 | 6.37 | 1.344 | 4.74 | 8445.26 | 2.079 | 97.8 | 77.9 | 1374 | 23 | 5489.4 | 2918.7 | 2844.6 | 4190 | 1191.9 | 0.68056 | 6.085
2024-12-09 | 15:52 | Data | 0 | 32.521 | 30.415 | 189.524 | 7.64 | 177.814 | 2111.35 | 26.06 | 45.998 | 6.36 | 1.355 | 4.745 | 8427.17 | 1.884 | 97.8 | 77.8 | 1374 | 23 | 5477.7 | 2928 | 2811.8 | 4178.3 | 1191.9 | 0.68437 | 6.101
2024-12-09 | 15:52 | Data | 0 | 32.487 | 30.185 | 189.388 | 7.64 | 177.814 | 2120.39 | 26.06 | 45.908 | 6.37 | 1.357 | 4.74 | 8422.65 | 2.106 | 97.8 | 77.7 | 1378 | 23.04 | 5474.7 | 2922.2 | 2824.9 | 4182.2 | 1191.9 | 0.68334 | 6.098
2024-12-09 | 15:52 | Data | 0 | 32.487 | 30.3 | 189.434 | 7.64 | 177.814 | 2121.29 | 26.05 | 45.998 | 6.37 | 1.357 | 4.758 | 8422.65 | 2.079 | 97.8 | 77.8 | 1378 | 23 | 5474.7 | 2950.5 | 2829.2 | 4178.9 | 1191.9 | 0.68613 | 6.114
2024-12-09 | 15:52 | Data | 0 | 32.379 | 30.354 | 189.388 | 7.64 | 177.814 | 2119.49 | 26.06 | 45.998 | 6.37 | 1.356 | 4.758 | 8427.17 | 2.181 | 97.8 | 77.8 | 1378 | 23.04 | 5477.7 | 2917.8 | 2804.6 | 4165.7 | 1191.9 | 0.68472 | 6.113
2024-12-09 | 15:52 | Data | 0 | 32.649 | 30.192 | 189.569 | 7.64 | 177.86 | 2120.39 | 26.07 | 45.908 | 6.37 | 1.358 | 4.759 | 8445.26 | 2.093 | 97.8 | 77.8 | 1378 | 23 | 5489.4 | 2925.7 | 2806.7 | 4170.6 | 1191.9 | 0.68604 | 6.116
2024-12-09 | 15:52 | Data | 0 | 32.332 | 30.077 | 189.388 | 7.65 | 177.769 | 2119.49 | 26.07 | 45.998 | 6.37 | 1.356 | 4.75 | 8436.21 | 1.796 | 97.8 | 77.8 | 1378 | 22.95 | 5483.5 | 2942.4 | 2807.3 | 4180.9 | 1191.9 | 0.68762 | 6.105
2024-12-09 | 15:53 | Data | 0 | 32.467 | 30.408 | 189.388 | 7.64 | 177.814 | 2121.29 | 26.07 | 45.818 | 6.37 | 1.347 | 4.778 | 8458.83 | 2.086 | 97.8 | 78 | 1378 | 23 | 5498.2 | 2923.5 | 2815.8 | 4176.9 | 1191.9 | 0.68427 | 6.127
2024-12-09 | 15:53 | Data | 0 | 32.48 | 30.361 | 189.434 | 7.64 | 177.724 | 2117.68 | 26.06 | 45.908 | 6.37 | 1.339 | 4.76 | 8445.26 | 1.971 | 97.8 | 78 | 1377 | 23 | 5489.4 | 2928 | 2836.5 | 4193 | 1191.9 | 0.68255 | 6.1
2024-12-09 | 15:53 | Data | 0 | 32.278 | 30.401 | 189.479 | 7.64 | 177.86 | 2116.78 | 26.07 | 45.998 | 6.36 | 1.351 | 4.751 | 8449.78 | 1.904 | 97.8 | 77.9 | 1377 | 23 | 5492.4 | 2931.7 | 2818.8 | 4185.8 | 1191.9 | 0.68395 | 6.102
2024-12-09 | 15:53 | Data | 0 | 32.264 | 30.286 | 189.343 | 7.64 | 177.724 | 2117.68 | 26.06 | 46.089 | 6.36 | 1.353 | 4.756 | 8449.78 | 2.221 | 97.8 | 77.9 | 1376 | 23 | 5492.4 | 2920.9 | 2819.9 | 4174.4 | 1191.9 | 0.68368 | 6.108
2024-12-09 | 15:53 | Data | 0 | 32.264 | 30.185 | 189.253 | 7.64 | 177.724 | 2110.45 | 26.06 | 45.998 | 6.36 | 1.353 | 4.781 | 8454.3 | 2.079 | 97.8 | 77.9 | 1372 | 23 | 5495.3 | 2925.9 | 2828.3 | 4187.3 | 1191.9 | 0.6838 | 6.134
2024-12-09 | 15:53 | Data | 0 | 32.487 | 30.07 | 189.343 | 7.64 | 177.769 | 2111.35 | 26.07 | 45.908 | 6.37 | 1.348 | 4.774 | 8445.26 | 2.005 | 97.8 | 78 | 1372 | 23 | 5489.4 | 2917.2 | 2825.7 | 4177 | 1191.9 | 0.68315 | 6.123
2024-12-09 | 15:53 | Data | 0 | 32.109 | 29.969 | 189.388 | 7.64 | 177.814 | 2111.35 | 26.06 | 45.998 | 6.37 | 1.352 | 4.765 | 8472.39 | 1.965 | 97.8 | 77.9 | 1372 | 23 | 5507.1 | 2926.4 | 2812.9 | 4175.1 | 1191.9 | 0.68481 | 6.12
2024-12-09 | 15:53 | Data | 0 | 32.224 | 30.266 | 189.434 | 7.64 | 177.724 | 2111.35 | 26.07 | 45.908 | 6.37 | 1.355 | 4.723 | 8458.83 | 1.911 | 97.8 | 77.7 | 1372 | 23 | 5498.2 | 2908.2 | 2827.7 | 4173.7 | 1191.9 | 0.68123 | 6.08
2024-12-09 | 15:53 | Data | 0 | 32.298 | 30.361 | 189.479 | 7.64 | 177.814 | 2107.74 | 26.06 | 45.908 | 6.36 | 1.354 | 4.749 | 8481.44 | 2.093 | 97.8 | 77.8 | 1369 | 23 | 5512.9 | 2936.4 | 2826.3 | 4185.5 | 1191.9 | 0.68308 | 6.102
2024-12-09 | 15:53 | Data | 0 | 32.264 | 30.185 | 189.388 | 7.64 | 177.769 | 2108.64 | 26.06 | 45.908 | 6.37 | 1.356 | 4.755 | 8481.44 | 2.079 | 97.8 | 77.8 | 1371 | 23 | 5512.9 | 2927.2 | 2825.5 | 4186.8 | 1191.9 | 0.68236 | 6.111
2024-12-09 | 15:53 | Data | 0 | 32.44 | 30.455 | 189.524 | 7.64 | 177.86 | 2106.83 | 26.07 | 45.908 | 6.36 | 1.348 | 4.759 | 8458.83 | 2.093 | 97.8 | 77.9 | 1370 | 22.95 | 5498.2 | 2940.3 | 2832.9 | 4198.5 | 1192 | 0.68528 | 6.107
2024-12-09 | 15:53 | Data | 0 | 32.264 | 30.347 | 189.388 | 7.64 | 177.769 | 2108.64 | 26.06 | 45.998 | 6.37 | 1.359 | 4.749 | 8449.78 | 1.992 | 97.8 | 77.7 | 1371 | 23 | 5492.4 | 2914.1 | 2815.2 | 4170.5 | 1192 | 0.68277 | 6.106
2024-12-09 | 15:53 | Data | 0 | 32.312 | 30.185 | 189.343 | 7.64 | 177.769 | 2111.35 | 26.07 | 45.998 | 6.37 | 1.36 | 4.75 | 8445.26 | 2.1 | 97.8 | 77.7 | 1372 | 23 | 5489.4 | 2926.9 | 2810.6 | 4169.1 | 1192 | 0.68275 | 6.111
2024-12-09 | 15:53 | Data | 0 | 32.264 | 30.185 | 189.388 | 7.64 | 177.769 | 2108.64 | 26.06 | 45.908 | 6.36 | 1.356 | 4.753 | 8440.74 | 2.086 | 97.8 | 77.8 | 1371 | 23 | 5486.5 | 2924.5 | 2826.2 | 4185.4 | 1192 | 0.68213 | 6.107
2024-12-09 | 15:53 | Data | 0 | 32.278 | 30.732 | 189.388 | 7.64 | 177.86 | 2108.64 | 26.07 | 45.998 | 6.37 | 1.356 | 4.774 | 8449.78 | 1.938 | 97.8 | 77.9 | 1371 | 22.95 | 5492.4 | 2935.8 | 2827.9 | 4193.9 | 1192 | 0.68357 | 6.13
2024-12-09 | 15:53 | Data | 0 | 32.575 | 30.516 | 189.479 | 7.64 | 177.86 | 2109.54 | 26.07 | 45.908 | 6.36 | 1.362 | 4.772 | 8449.78 | 2.187 | 97.8 | 77.8 | 1371 | 23 | 5492.4 | 2926 | 2789.4 | 4161.3 | 1192 | 0.68732 | 6.134
2024-12-09 | 15:53 | Data | 0 | 32.609 | 30.462 | 189.479 | 7.64 | 177.814 | 2104.12 | 26.06 | 45.998 | 6.37 | 1.358 | 4.77 | 8074.44 | 2.073 | 97.8 | 77.8 | 1368 | 23 | 5248.4 | 2915.9 | 2813 | 4183.3 | 1192 | 0.68506 | 6.129
2024-12-09 | 15:53 | Data | 0 | 32.406 | 30.185 | 189.388 | 7.64 | 177.814 | 2109.54 | 26.06 | 45.998 | 6.37 | 1.358 | 4.743 | 8463.35 | 2.1 | 97.8 | 77.7 | 1371 | 23 | 5501.2 | 2929.6 | 2806.3 | 4171.3 | 1192 | 0.68495 | 6.101
2024-12-09 | 15:54 | Data | 0 | 32.102 | 29.969 | 189.388 | 7.64 | 177.724 | 2111.35 | 26.06 | 45.998 | 6.37 | 1.363 | 4.738 | 8454.3 | 1.971 | 97.8 | 77.7 | 1373 | 23 | 5495.3 | 2939.4 | 2820.2 | 4190.5 | 1192 | 0.68405 | 6.102
2024-12-09 | 15:54 | Data | 0 | 32.379 | 30.198 | 189.388 | 7.64 | 177.814 | 2111.35 | 26.06 | 45.998 | 6.36 | 1.358 | 4.762 | 8449.78 | 2.208 | 97.8 | 77.8 | 1373 | 23 | 5492.4 | 2912 | 2823.9 | 4176.2 | 1192 | 0.68083 | 6.12
2024-12-09 | 15:54 | Data | 0 | 32.507 | 30.624 | 189.434 | 7.65 | 177.95 | 2114.06 | 26.06 | 45.998 | 6.38 | 1.346 | 4.762 | 8454.3 | 2.086 | 97.8 | 78 | 1374 | 22.95 | 5495.3 | 2913 | 2836.2 | 4183.1 | 1192 | 0.68061 | 6.105
2024-12-09 | 15:54 | Data | 0 | 32.19 | 30.361 | 189.524 | 7.64 | 177.86 | 2110.45 | 26.06 | 45.998 | 6.36 | 1.351 | 4.762 | 8440.74 | 2.046 | 97.8 | 77.9 | 1372 | 23 | 5486.5 | 2915.3 | 2819.4 | 4174.8 | 1192 | 0.68219 | 6.113
2024-12-09 | 15:54 | Data | 0 | 32.264 | 30.185 | 189.298 | 7.64 | 177.769 | 2112.26 | 26.07 | 45.908 | 6.37 | 1.356 | 4.763 | 8467.87 | 2.079 | 97.8 | 77.8 | 1372 | 22.95 | 5504.1 | 2934.2 | 2834.7 | 4194.4 | 1192 | 0.68404 | 6.119
2024-12-09 | 15:54 | Data | 0 | 32.251 | 30.185 | 189.434 | 7.64 | 177.814 | 2114.06 | 26.06 | 45.998 | 6.37 | 1.351 | 4.776 | 8454.3 | 2.059 | 97.8 | 77.9 | 1374 | 23 | 5495.3 | 2915.6 | 2816 | 4170 | 1192 | 0.68273 | 6.128
2024-12-09 | 15:54 | Data | 0 | 32.271 | 30.347 | 189.388 | 7.64 | 177.86 | 2116.78 | 26.07 | 45.998 | 6.36 | 1.349 | 4.754 | 8454.3 | 1.992 | 97.8 | 77.9 | 1376 | 23 | 5495.3 | 2918.8 | 2819.9 | 4170.3 | 1192 | 0.6818 | 6.103
2024-12-09 | 15:54 | Data | 0 | 32.183 | 30.185 | 189.524 | 7.64 | 177.86 | 2117.68 | 26.05 | 45.998 | 6.36 | 1.356 | 4.768 | 8472.39 | 2.093 | 97.8 | 77.9 | 1376 | 23 | 5507.1 | 2934 | 2839.2 | 4198.3 | 1192 | 0.68279 | 6.124
2024-12-09 | 15:54 | Data | 0 | 32.818 | 30.529 | 189.615 | 7.64 | 177.905 | 2120.39 | 26.07 | 45.908 | 6.37 | 1.361 | 4.765 | 8467.87 | 2.208 | 97.8 | 77.8 | 1378 | 22.95 | 5504.1 | 2916.5 | 2837 | 4188.9 | 1192 | 0.68053 | 6.126
2024-12-09 | 15:54 | Data | 0 | 32.156 | 30.212 | 189.388 | 7.64 | 177.814 | 2120.39 | 26.06 | 45.908 | 6.36 | 1.354 | 4.753 | 8467.87 | 2.052 | 97.8 | 77.8 | 1378 | 22.95 | 5504.1 | 2930.2 | 2824.8 | 4189.5 | 1192 | 0.68327 | 6.106
2024-12-09 | 15:54 | Data | 0 | 32.217 | 30.516 | 189.434 | 7.64 | 177.86 | 2119.49 | 26.06 | 46.089 | 6.37 | 1.353 | 4.745 | 8458.83 | 2.073 | 97.8 | 77.8 | 1378 | 23.04 | 5498.2 | 2929 | 2820.7 | 4181 | 1192 | 0.68532 | 6.1
2024-12-09 | 15:54 | Data | 0 | 32.48 | 30.192 | 189.569 | 7.64 | 177.905 | 2123.1 | 26.06 | 45.998 | 6.37 | 1.355 | 4.742 | 8467.87 | 2.275 | 97.8 | 77.8 | 1380 | 23 | 5504.1 | 2947.7 | 2810.6 | 4186.5 | 1192 | 0.68869 | 6.096
2024-12-09 | 15:54 | Data | 0 | 32.467 | 30.239 | 189.434 | 7.64 | 177.814 | 2123.1 | 26.06 | 45.998 | 6.37 | 1.358 | 4.761 | 8458.83 | 2.248 | 97.8 | 77.8 | 1380 | 23 | 5498.2 | 2945.6 | 2806.6 | 4183.6 | 1192 | 0.68748 | 6.119
2024-12-09 | 15:54 | Data | 0 | 32.413 | 30.185 | 189.569 | 7.64 | 177.905 | 2124.01 | 26.07 | 45.998 | 6.36 | 1.355 | 4.765 | 8431.69 | 1.911 | 97.8 | 77.9 | 1381 | 23 | 5480.6 | 2935 | 2818 | 4186.2 | 1192 | 0.68509 | 6.119
2024-12-09 | 15:54 | Data | 0 | 32.879 | 30.475 | 189.615 | 7.64 | 177.814 | 2125.81 | 26.07 | 45.818 | 6.37 | 1.363 | 4.738 | 8445.26 | 2.289 | 97.8 | 77.7 | 1381 | 23 | 5489.4 | 2933.8 | 2802.8 | 4176.3 | 1192 | 0.68666 | 6.099
2024-12-09 | 15:54 | Data | 0 | 32.264 | 30.3 | 189.343 | 7.64 | 177.769 | 2124.91 | 26.06 | 45.998 | 6.37 | 1.352 | 4.758 | 8422.65 | 2.079 | 97.8 | 77.9 | 1382 | 23 | 5474.7 | 2919.6 | 2806 | 4165.4 | 1192 | 0.68162 | 6.109
2024-12-09 | 15:54 | Data | 0 | 32.278 | 30.361 | 189.434 | 7.64 | 177.86 | 2125.81 | 26.06 | 45.727 | 6.37 | 1.343 | 4.757 | 8431.69 | 2.079 | 97.8 | 78 | 1382 | 22.95 | 5480.6 | 2918.6 | 2814.4 | 4169 | 1192 | 0.68333 | 6.099
2024-12-09 | 15:54 | Data | 0 | 32.656 | 30.631 | 189.434 | 7.65 | 177.86 | 2127.62 | 26.07 | 45.998 | 6.36 | 1.351 | 4.752 | 8440.74 | 2.187 | 97.8 | 77.9 | 1383 | 23 | 5486.5 | 2925.3 | 2822.4 | 4182.1 | 1192 | 0.68338 | 6.103
2024-12-09 | 15:55 | Data | 0 | 32.46 | 30.198 | 189.343 | 7.64 | 177.86 | 2123.1 | 26.06 | 45.998 | 6.37 | 1.356 | 4.762 | 8436.21 | 2.201 | 97.8 | 77.8 | 1379 | 23 | 5483.5 | 2912.7 | 2825.4 | 4179.4 | 1192 | 0.68202 | 6.116
2024-12-09 | 15:55 | Data | 0 | 32.264 | 30.361 | 189.388 | 7.64 | 177.814 | 2123.1 | 26.06 | 45.998 | 6.36 | 1.354 | 4.782 | 8418.13 | 2.14 | 97.8 | 77.9 | 1379 | 22.95 | 5471.8 | 2934.5 | 2814.3 | 4171.4 | 1192 | 0.68345 | 6.138
2024-12-09 | 15:55 | Data | 0 | 32.379 | 30.408 | 189.524 | 7.64 | 177.905 | 2120.39 | 26.06 | 46.54 | 6.37 | 1.362 | 4.764 | 8422.65 | 2.066 | 97.8 | 77.8 | 1378 | 23.27 | 5474.7 | 2925.7 | 2814.7 | 4179.5 | 1192 | 0.68341 | 6.125
2024-12-09 | 15:55 | Data | 0 | 32.703 | 30.624 | 189.524 | 7.64 | 177.905 | 2121.29 | 26.07 | 45.908 | 6.36 | 1.348 | 4.767 | 8418.13 | 2.12 | 97.8 | 77.9 | 1378 | 22.95 | 5471.8 | 2939.3 | 2842.6 | 4194.8 | 1192 | 0.68039 | 6.115
2024-12-09 | 15:55 | Data | 0 | 32.602 | 30.192 | 189.434 | 7.64 | 177.86 | 2120.39 | 26.07 | 45.998 | 6.37 | 1.345 | 4.787 | 8409.08 | 2.113 | 97.8 | 78.1 | 1378 | 23 | 5465.9 | 2914.4 | 2830.5 | 4178.1 | 1192 | 0.68139 | 6.131
2024-12-09 | 15:55 | Data | 0 | 32.345 | 29.982 | 189.388 | 7.64 | 177.814 | 2120.39 | 26.06 | 45.998 | 6.37 | 1.351 | 4.791 | 8431.69 | 2.208 | 97.8 | 78 | 1379 | 23 | 5480.6 | 2922.9 | 2840 | 4183.6 | 1192 | 0.68201 | 6.143
2024-12-09 | 15:55 | Data | 0 | 32.433 | 30.192 | 189.479 | 7.64 | 177.95 | 2123.1 | 26.06 | 45.908 | 6.36 | 1.355 | 4.778 | 8454.3 | 2.093 | 97.8 | 77.9 | 1380 | 22.95 | 5495.3 | 2916.7 | 2836.6 | 4188.5 | 1192 | 0.67896 | 6.132
2024-12-09 | 15:55 | Data | 0 | 32.264 | 30.185 | 189.388 | 7.64 | 177.814 | 2123.1 | 26.06 | 45.998 | 6.36 | 1.359 | 4.745 | 8467.87 | 2.079 | 97.8 | 77.7 | 1381 | 23 | 5504.1 | 2917.8 | 2814.2 | 4171.6 | 1192 | 0.68284 | 6.102
2024-12-09 | 15:55 | Data | 0 | 32.386 | 30.523 | 189.569 | 7.65 | 177.905 | 2123.1 | 26.06 | 45.998 | 6.37 | 1.353 | 4.751 | 8463.35 | 2.032 | 97.8 | 77.8 | 1380 | 23 | 5501.2 | 2931.9 | 2817.8 | 4183.6 | 1192 | 0.68478 | 6.106
2024-12-09 | 15:55 | Data | 0 | 32.291 | 30.307 | 189.479 | 7.64 | 177.769 | 2120.39 | 26.07 | 45.998 | 6.36 | 1.354 | 4.759 | 8458.83 | 2.073 | 97.8 | 77.8 | 1378 | 23 | 5498.2 | 2930.3 | 2836.4 | 4194.2 | 1192 | 0.68278 | 6.114
2024-12-09 | 15:55 | Data | 0 | 32.494 | 30.415 | 189.388 | 7.64 | 177.86 | 2120.39 | 26.07 | 45.998 | 6.36 | 1.349 | 4.763 | 8436.21 | 2.079 | 97.8 | 77.9 | 1378 | 22.95 | 5483.5 | 2921.4 | 2831.9 | 4181.6 | 1192.1 | 0.6821 | 6.112
2024-12-09 | 15:55 | Data | 0 | 32.271 | 30.401 | 189.524 | 7.64 | 177.769 | 2121.29 | 26.07 | 45.998 | 6.36 | 1.36 | 4.769 | 8422.65 | 1.904 | 97.8 | 77.8 | 1378 | 23 | 5474.7 | 2932.7 | 2835.4 | 4197.8 | 1192.1 | 0.68193 | 6.13
2024-12-09 | 15:55 | Data | 0 | 32.771 | 30.327 | 189.524 | 7.64 | 177.995 | 2120.39 | 26.06 | 45.908 | 6.36 | 1.354 | 4.748 | 8431.69 | 2.086 | 97.8 | 77.8 | 1378 | 23 | 5480.6 | 2949.5 | 2833.4 | 4204.3 | 1192.1 | 0.68597 | 6.102
2024-12-09 | 15:55 | Data | 0 | 32.717 | 30.651 | 189.524 | 7.65 | 177.905 | 2121.29 | 26.06 | 45.908 | 6.36 | 1.357 | 4.747 | 8427.17 | 1.904 | 97.8 | 77.8 | 1379 | 23 | 5477.7 | 2929 | 2831.6 | 4190.9 | 1192.1 | 0.68329 | 6.103
2024-12-09 | 15:55 | Data | 0 | 32.264 | 30.138 | 189.479 | 7.64 | 177.86 | 2117.68 | 26.07 | 45.998 | 6.36 | 1.355 | 4.731 | 8463.35 | 2.127 | 97.8 | 77.7 | 1376 | 23.04 | 5501.2 | 2928.3 | 2816.8 | 4181.7 | 1192.1 | 0.68364 | 6.086
2024-12-09 | 15:55 | Data | 0 | 32.379 | 30.185 | 189.434 | 7.64 | 177.86 | 2114.06 | 26.06 | 45.998 | 6.36 | 1.358 | 4.743 | 8490.48 | 1.911 | 97.8 | 77.8 | 1374 | 23 | 5518.8 | 2925.3 | 2836.5 | 4190.6 | 1192.1 | 0.6819 | 6.1
2024-12-09 | 15:55 | Data | 0 | 32.264 | 30.239 | 189.434 | 7.65 | 177.769 | 2112.26 | 26.06 | 45.998 | 6.36 | 1.361 | 4.754 | 8481.44 | 2.052 | 97.8 | 77.7 | 1373 | 22.91 | 5512.9 | 2935.8 | 2826.6 | 4193.9 | 1192.1 | 0.6846 | 6.116
2024-12-09 | 15:56 | Data | 0 | 32.676 | 30.212 | 189.524 | 7.64 | 177.905 | 2113.16 | 26.07 | 45.818 | 6.36 | 1.36 | 4.768 | 8693.98 | 2.289 | 97.8 | 77.8 | 1374 | 22.86 | 5651.1 | 2936.2 | 2837.4 | 4200.6 | 1192.1 | 0.68327 | 6.128
2024-12-09 | 15:56 | Data | 0 | 32.278 | 30.577 | 189.569 | 7.65 | 177.86 | 2114.97 | 26.07 | 45.727 | 6.36 | 1.358 | 4.764 | 8689.46 | 2.086 | 97.8 | 77.8 | 1375 | 22.86 | 5648.1 | 2954 | 2829 | 4209.1 | 1192.1 | 0.68511 | 6.121
2024-12-09 | 15:56 | Data | 0 | 32.521 | 30.388 | 189.479 | 7.64 | 177.905 | 2114.97 | 26.05 | 45.637 | 6.36 | 1.358 | 4.735 | 8684.94 | 2.133 | 97.8 | 77.7 | 1375 | 22.86 | 5645.2 | 2953.6 | 2824.1 | 4203 | 1192.1 | 0.68568 | 6.093
2024-12-09 | 15:56 | Data | 0 | 32.494 | 30.401 | 189.434 | 7.64 | 177.86 | 2117.68 | 26.07 | 45.998 | 6.37 | 1.359 | 4.742 | 8693.98 | 2.1 | 97.8 | 77.7 | 1376 | 23 | 5651.1 | 2953.9 | 2848.8 | 4220.6 | 1192.1 | 0.68306 | 6.102
2024-12-09 | 15:56 | Data | 0 | 32.494 | 30.415 | 189.569 | 7.65 | 177.905 | 2116.78 | 26.07 | 45.908 | 6.37 | 1.359 | 4.751 | 8508.57 | 2.255 | 97.8 | 77.7 | 1376 | 22.95 | 5530.6 | 2954.1 | 2837 | 4215.1 | 1192.1 | 0.68389 | 6.111
2024-12-09 | 15:56 | Data | 0 | 32.494 | 30.408 | 189.434 | 7.64 | 177.86 | 2113.16 | 26.07 | 45.908 | 6.36 | 1.367 | 4.736 | 8495 | 2.106 | 97.8 | 77.6 | 1374 | 23 | 5521.8 | 2935 | 2826 | 4192.8 | 1192.1 | 0.68288 | 6.104
2024-12-09 | 15:56 | Data | 0 | 32.609 | 30.361 | 189.524 | 7.64 | 177.995 | 2117.68 | 26.06 | 45.727 | 6.37 | 1.358 | 4.739 | 8490.48 | 2.187 | 97.8 | 77.7 | 1376 | 22.86 | 5518.8 | 2943.5 | 2825.2 | 4200.3 | 1192.1 | 0.68285 | 6.098
2024-12-09 | 15:56 | Data | 0 | 32.602 | 30.415 | 189.524 | 7.64 | 177.95 | 2117.68 | 26.06 | 45.727 | 6.36 | 1.359 | 4.74 | 8495 | 1.971 | 97.8 | 77.7 | 1376 | 22.86 | 5521.8 | 2942.7 | 2830.9 | 4202.4 | 1192.1 | 0.68433 | 6.1
2024-12-09 | 15:56 | Data | 0 | 32.696 | 30.644 | 189.479 | 7.64 | 177.86 | 2114.06 | 26.06 | 45.998 | 6.37 | 1.36 | 4.749 | 8476.91 | 2.093 | 97.8 | 77.8 | 1374 | 23 | 5510 | 2962.1 | 2841.7 | 4224.7 | 1192.1 | 0.68426 | 6.11
2024-12-09 | 15:56 | Data | 0 | 32.44 | 30.421 | 189.434 | 7.64 | 177.905 | 2114.06 | 26.06 | 45.637 | 6.37 | 1.361 | 4.739 | 8467.87 | 2.262 | 97.8 | 77.7 | 1374 | 22.91 | 5504.1 | 2953.3 | 2824.9 | 4208.4 | 1192.1 | 0.68306 | 6.099
2024-12-09 | 15:56 | Data | 0 | 32.575 | 30.408 | 189.434 | 7.65 | 177.724 | 2113.16 | 26.06 | 45.727 | 6.36 | 1.353 | 4.742 | 8476.91 | 2.275 | 97.8 | 77.8 | 1374 | 22.91 | 5510 | 2954.3 | 2843.5 | 4226.8 | 1192.1 | 0.68288 | 6.095
2024-12-09 | 15:56 | Data | 0 | 32.379 | 30.212 | 189.388 | 7.64 | 177.905 | 2114.06 | 26.07 | 45.547 | 6.37 | 1.328 | 4.785 | 8481.44 | 2.025 | 97.8 | 78.3 | 1374 | 22.86 | 5512.9 | 2958.4 | 2826.3 | 4210.4 | 1192.1 | 0.68642 | 6.112
2024-12-09 | 15:56 | Data | 0 | 32.291 | 30.516 | 189.615 | 7.64 | 177.86 | 2113.16 | 26.06 | 45.637 | 6.36 | 1.347 | 4.768 | 8485.96 | 1.884 | 97.8 | 78 | 1374 | 22.77 | 5515.9 | 2929.9 | 2822.7 | 4193.2 | 1192.1 | 0.68234 | 6.115
2024-12-09 | 15:56 | Data | 0 | 32.264 | 30.185 | 189.524 | 7.64 | 177.86 | 2114.06 | 26.07 | 45.818 | 6.36 | 1.353 | 4.789 | 8481.44 | 2.255 | 97.8 | 78 | 1374 | 22.86 | 5512.9 | 2949.4 | 2817 | 4198.7 | 1192.1 | 0.68582 | 6.143
2024-12-09 | 15:56 | Data | 0 | 32.278 | 30.185 | 189.479 | 7.64 | 177.86 | 2114.06 | 26.06 | 45.727 | 6.36 | 1.341 | 4.777 | 8485.96 | 2.079 | 97.8 | 78.1 | 1374 | 22.91 | 5515.9 | 2947.6 | 2844.8 | 4215.8 | 1192.1 | 0.68223 | 6.118
2024-12-09 | 15:56 | Data | 0 | 32.271 | 30.401 | 189.569 | 7.64 | 177.724 | 2114.97 | 26.05 | 45.998 | 6.37 | 1.351 | 4.73 | 8481.44 | 2.019 | 97.8 | 77.8 | 1374 | 23 | 5512.9 | 2941.9 | 2842.3 | 4210.9 | 1192.1 | 0.68332 | 6.083
2024-12-09 | 15:56 | Data | 0 | 32.568 | 30.192 | 189.569 | 7.64 | 177.86 | 2113.16 | 26.06 | 45.818 | 6.36 | 1.355 | 4.761 | 8467.87 | 2.113 | 97.8 | 77.9 | 1374 | 22.95 | 5504.1 | 2946.5 | 2850.1 | 4219.4 | 1192.1 | 0.68269 | 6.115
2024-12-09 | 15:57 | Data | 0 | 32.663 | 30.442 | 189.569 | 7.64 | 177.95 | 2112.26 | 26.07 | 45.998 | 6.36 | 1.353 | 4.756 | 8481.44 | 2.235 | 97.8 | 77.9 | 1373 | 23 | 5512.9 | 2940.3 | 2823.3 | 4197.9 | 1192.1 | 0.68401 | 6.109
2024-12-09 | 15:57 | Data | 0 | 32.548 | 30.32 | 189.524 | 7.64 | 177.95 | 2117.68 | 26.05 | 45.998 | 6.36 | 1.343 | 4.758 | 8481.44 | 2.113 | 97.8 | 78 | 1376 | 23 | 5512.9 | 2960.3 | 2842.8 | 4229 | 1192.1 | 0.68564 | 6.102
2024-12-09 | 15:57 | Data | 0 | 32.548 | 30.198 | 189.479 | 7.65 | 177.86 | 2114.97 | 26.03 | 45.818 | 6.36 | 1.355 | 4.745 | 8485.96 | 2.106 | 97.8 | 77.8 | 1375 | 22.86 | 5515.9 | 2966 | 2854.2 | 4235.9 | 1192.1 | 0.68387 | 6.101
2024-12-09 | 15:57 | Data | 0 | 32.163 | 30.502 | 189.569 | 7.64 | 177.86 | 2114.06 | 26.06 | 45.727 | 6.36 | 1.354 | 4.74 | 8513.09 | 1.931 | 97.8 | 77.8 | 1374 | 22.86 | 5533.5 | 2951.8 | 2847.4 | 4222.3 | 1192.1 | 0.68164 | 6.093
2024-12-09 | 15:57 | Data | 0 | 32.271 | 30.185 | 189.298 | 7.64 | 177.814 | 2111.35 | 26.06 | 45.908 | 6.37 | 1.364 | 4.773 | 8540.22 | 2.079 | 97.8 | 77.8 | 1372 | 22.95 | 5551.1 | 2939.9 | 2839.8 | 4211 | 1192.1 | 0.68446 | 6.137
2024-12-09 | 15:57 | Data | 0 | 32.48 | 30.388 | 189.434 | 7.64 | 177.86 | 2111.35 | 26.03 | 45.727 | 6.36 | 1.363 | 4.779 | 8517.61 | 2.187 | 97.8 | 77.8 | 1372 | 22.86 | 5536.4 | 2949.8 | 2856.6 | 4225.5 | 1192.1 | 0.68224 | 6.143
2024-12-09 | 15:57 | Data | 0 | 32.278 | 30.415 | 189.479 | 7.64 | 177.86 | 2111.35 | 26.06 | 45.908 | 6.36 | 1.348 | 4.757 | 8513.09 | 1.857 | 97.8 | 77.9 | 1372 | 22.95 | 5533.5 | 2958.9 | 2832.1 | 4215.8 | 1192.1 | 0.68498 | 6.105
2024-12-09 | 15:57 | Data | 0 | 32.69 | 30.192 | 189.569 | 7.64 | 177.95 | 2114.97 | 26.05 | 45.908 | 6.36 | 1.353 | 4.751 | 8485.96 | 1.89 | 97.8 | 77.8 | 1374 | 23 | 5515.9 | 2948.2 | 2839.7 | 4216.9 | 1192.1 | 0.68217 | 6.104
2024-12-09 | 15:57 | Data | 0 | 32.264 | 30.185 | 189.343 | 7.64 | 177.814 | 2114.06 | 26.02 | 45.998 | 6.36 | 1.351 | 4.759 | 8495 | 2.194 | 97.8 | 77.9 | 1374 | 22.95 | 5521.8 | 2960.5 | 2840.9 | 4226.1 | 1192.1 | 0.68358 | 6.11
2024-12-09 | 15:57 | Data | 0 | 32.271 | 30.185 | 189.479 | 7.65 | 177.86 | 2114.06 | 26.03 | 45.998 | 6.36 | 1.355 | 4.724 | 8513.09 | 2.079 | 97.8 | 77.7 | 1374 | 23 | 5533.5 | 2889.3 | 2806.9 | 4142.5 | 1192.1 | 0.6824 | 6.079
2024-12-09 | 15:57 | Data | 0 | 32.494 | 30.313 | 189.479 | 7.64 | 177.905 | 2116.78 | 26.03 | 46.089 | 6.36 | 1.358 | 4.743 | 8495 | 2.181 | 97.8 | 77.7 | 1376 | 23 | 5521.8 | 2898.9 | 2833.2 | 4170 | 1192.1 | 0.67974 | 6.101
2024-12-09 | 15:57 | Data | 0 | 32.298 | 30.3 | 189.524 | 7.64 | 177.905 | 2117.68 | 26.03 | 45.908 | 6.36 | 1.361 | 4.756 | 8513.09 | 2.086 | 97.8 | 77.7 | 1376 | 23.09 | 5533.5 | 2882.5 | 2833.9 | 4155.1 | 1192.2 | 0.67727 | 6.116
2024-12-09 | 15:57 | Data | 0 | 32.163 | 30.185 | 189.569 | 7.64 | 177.95 | 2117.68 | 26.05 | 45.998 | 6.36 | 1.357 | 4.781 | 8508.57 | 2.241 | 97.8 | 77.9 | 1376 | 23 | 5530.6 | 2898.3 | 2830.6 | 4163.2 | 1192.2 | 0.67804 | 6.137
2024-12-09 | 15:57 | Data | 0 | 32.069 | 30.016 | 189.343 | 7.64 | 177.905 | 2111.35 | 26.05 | 45.998 | 6.37 | 1.352 | 4.788 | 8513.09 | 1.971 | 97.8 | 78 | 1372 | 23 | 5533.5 | 2880.9 | 2833.6 | 4155.4 | 1192.2 | 0.67783 | 6.142
2024-12-09 | 15:57 | Data | 0 | 32.163 | 30.07 | 189.298 | 7.64 | 177.814 | 2114.06 | 26.05 | 45.727 | 6.36 | 1.361 | 4.755 | 8495 | 1.877 | 97.8 | 77.7 | 1375 | 22.86 | 5521.8 | 2889.8 | 2820.4 | 4154 | 1192.2 | 0.68053 | 6.116
2024-12-09 | 15:57 | Data | 0 | 32.521 | 30.219 | 189.434 | 7.64 | 177.86 | 2117.68 | 26.03 | 45.908 | 6.37 | 1.354 | 4.746 | 8467.87 | 2.073 | 97.8 | 77.8 | 1377 | 23 | 5504.1 | 2891.1 | 2838.4 | 4161.3 | 1192.2 | 0.678 | 6.1
2024-12-09 | 15:57 | Data | 0 | 32.278 | 30.185 | 189.66 | 7.64 | 177.86 | 2117.68 | 26.05 | 45.998 | 6.37 | 1.356 | 4.765 | 8467.87 | 2.086 | 97.8 | 77.8 | 1376 | 23 | 5504.1 | 2886.4 | 2841.6 | 4163.5 | 1192.2 | 0.6767 | 6.121
2024-12-09 | 15:58 | Data | 0 | 32.494 | 30.415 | 189.479 | 7.64 | 177.86 | 2117.68 | 26.01 | 45.998 | 6.37 | 1.354 | 4.752 | 8472.39 | 2.079 | 97.8 | 77.8 | 1376 | 23 | 5507.1 | 2945.5 | 2856.2 | 4217.4 | 1192.2 | 0.68211 | 6.106
2024-12-09 | 15:58 | Data | 0 | 32.467 | 30.192 | 189.479 | 7.64 | 177.769 | 2120.39 | 26.02 | 45.727 | 6.36 | 1.356 | 4.759 | 8481.44 | 2.154 | 97.8 | 77.8 | 1378 | 22.82 | 5512.9 | 2965.9 | 2852.7 | 4232 | 1192.2 | 0.68445 | 6.116
2024-12-09 | 15:58 | Data | 0 | 32.467 | 30.192 | 189.479 | 7.64 | 177.814 | 2120.39 | 26.02 | 45.908 | 6.36 | 1.359 | 4.746 | 8485.96 | 2.268 | 97.8 | 77.7 | 1378 | 22.95 | 5515.9 | 2939.8 | 2839.8 | 4217 | 1192.2 | 0.68425 | 6.104
2024-12-09 | 15:58 | Data | 0 | 32.264 | 30.138 | 189.388 | 7.64 | 177.814 | 2123.1 | 26.02 | 45.637 | 6.36 | 1.364 | 4.758 | 8485.96 | 2.282 | 97.8 | 77.7 | 1380 | 22.86 | 5515.9 | 2932 | 2815.2 | 4183.3 | 1192.2 | 0.684 | 6.122
2024-12-09 | 15:58 | Data | 0 | 32.494 | 30.185 | 189.569 | 7.64 | 177.905 | 2123.1 | 26.03 | 45.908 | 6.36 | 1.357 | 4.753 | 8454.3 | 2.248 | 97.8 | 77.8 | 1380 | 23.04 | 5495.3 | 2925.6 | 2845.7 | 4203.2 | 1192.2 | 0.67973 | 6.111
2024-12-09 | 15:58 | Data | 0 | 32.561 | 30.307 | 189.524 | 7.65 | 177.905 | 2123.1 | 26.01 | 45.998 | 6.36 | 1.36 | 4.742 | 8476.91 | 2.093 | 97.8 | 77.7 | 1380 | 23.04 | 5510 | 2938.6 | 2851.8 | 4212.3 | 1192.2 | 0.68163 | 6.102
2024-12-09 | 15:58 | Data | 0 | 32.744 | 30.469 | 189.434 | 7.64 | 177.814 | 2123.1 | 26.05 | 46.089 | 6.36 | 1.363 | 4.733 | 8495 | 2.235 | 97.8 | 77.6 | 1380 | 23 | 5521.8 | 2956.2 | 2856.3 | 4224.3 | 1192.2 | 0.68417 | 6.096
2024-12-09 | 15:58 | Data | 0 | 32.298 | 30.502 | 189.479 | 7.64 | 177.86 | 2123.1 | 26.05 | 45.998 | 6.37 | 1.355 | 4.759 | 8495 | 1.971 | 97.8 | 77.8 | 1380 | 23 | 5521.8 | 2941 | 2850.4 | 4210.3 | 1192.2 | 0.6822 | 6.116
2024-12-09 | 15:58 | Data | 0 | 32.21 | 30.3 | 189.343 | 7.64 | 177.814 | 2123.1 | 26.03 | 45.998 | 6.36 | 1.356 | 4.741 | 8485.96 | 2.248 | 97.8 | 77.8 | 1379 | 22.95 | 5515.9 | 2939.5 | 2856.6 | 4220.2 | 1192.2 | 0.68011 | 6.098
2024-12-09 | 15:58 | Data | 0 | 32.231 | 30.185 | 189.253 | 7.64 | 177.814 | 2122.2 | 26.02 | 45.998 | 6.37 | 1.356 | 4.779 | 8499.53 | 2.248 | 97.8 | 77.9 | 1380 | 22.95 | 5524.7 | 2931.6 | 2853.5 | 4210.9 | 1192.2 | 0.68042 | 6.134
2024-12-09 | 15:58 | Data | 0 | 32.264 | 30.347 | 189.343 | 7.64 | 177.724 | 2120.39 | 26.02 | 45.998 | 6.36 | 1.348 | 4.779 | 8472.39 | 2.127 | 97.8 | 78 | 1379 | 23 | 5507.1 | 2935.4 | 2824.9 | 4193.1 | 1192.2 | 0.68387 | 6.128
2024-12-09 | 15:58 | Data | 0 | 32.264 | 30.063 | 189.298 | 7.65 | 177.724 | 2121.29 | 26.01 | 45.908 | 6.37 | 1.355 | 4.743 | 8440.74 | 2.093 | 97.8 | 77.8 | 1378 | 23 | 5486.5 | 2944 | 2829.4 | 4201.3 | 1192.2 | 0.68444 | 6.099
2024-12-09 | 15:58 | Data | 0 | 32.271 | 30.185 | 189.434 | 7.64 | 177.724 | 2123.1 | 26.03 | 45.998 | 6.36 | 1.355 | 4.74 | 8440.74 | 2.079 | 97.8 | 77.8 | 1379 | 23 | 5486.5 | 2942.7 | 2833.1 | 4203.4 | 1192.2 | 0.68472 | 6.095
2024-12-09 | 15:58 | Data | 0 | 32.21 | 30.185 | 189.479 | 7.64 | 177.769 | 2124.91 | 26.02 | 45.908 | 6.36 | 1.349 | 4.747 | 8431.69 | 2.235 | 97.8 | 77.9 | 1381 | 22.95 | 5480.6 | 2940.3 | 2843.3 | 4207.1 | 1192.2 | 0.68226 | 6.096
2024-12-09 | 15:58 | Data | 0 | 32.15 | 30.178 | 189.343 | 7.64 | 177.769 | 2124.91 | 26.02 | 45.818 | 6.36 | 1.36 | 4.759 | 8422.65 | 2.073 | 97.8 | 77.8 | 1381 | 22.91 | 5474.7 | 2939.9 | 2821.8 | 4194 | 1192.2 | 0.68419 | 6.12
2024-12-09 | 15:58 | Data | 0 | 32.264 | 30.408 | 189.298 | 7.64 | 177.769 | 2125.81 | 26.02 | 45.818 | 6.36 | 1.358 | 4.777 | 8431.69 | 2.059 | 97.8 | 77.9 | 1381 | 22.86 | 5480.6 | 2954.1 | 2814.8 | 4200.2 | 1192.2 | 0.68653 | 6.136
2024-12-09 | 15:58 | Data | 0 | 32.318 | 29.989 | 189.479 | 7.64 | 177.86 | 2125.81 | 26.02 | 45.637 | 6.36 | 1.351 | 4.764 | 8454.3 | 2.208 | 97.9 | 77.9 | 1382 | 22.82 | 5495.3 | 2957.5 | 2841.2 | 4213.9 | 1192.2 | 0.68582 | 6.115
2024-12-09 | 15:58 | Data | 0 | 32.379 | 30.435 | 189.434 | 7.65 | 177.905 | 2124.91 | 26.01 | 45.727 | 6.36 | 1.36 | 4.761 | 8449.78 | 2.187 | 97.8 | 77.8 | 1381 | 22.86 | 5492.4 | 2932.3 | 2822.9 | 4191.7 | 1192.2 | 0.68333 | 6.121
2024-12-09 | 15:59 | Data | 0 | 32.204 | 30.171 | 189.253 | 7.64 | 177.634 | 2125.81 | 26.02 | 45.727 | 6.36 | 1.356 | 4.773 | 8454.3 | 2.113 | 97.8 | 77.9 | 1382 | 22.86 | 5495.3 | 2922.5 | 2838.9 | 4191.4 | 1192.2 | 0.6804 | 6.13
2024-12-09 | 15:59 | Data | 0 | 32.001 | 29.854 | 189.208 | 7.64 | 177.634 | 2123.1 | 26.01 | 45.727 | 6.36 | 1.356 | 4.743 | 8458.83 | 2.268 | 97.8 | 77.8 | 1379 | 22.86 | 5498.2 | 2915.7 | 2834.8 | 4186.3 | 1192.2 | 0.68033 | 6.098
2024-12-09 | 15:59 | Data | 0 | 31.913 | 29.928 | 188.936 | 7.64 | 177.498 | 2122.2 | 26.02 | 45.727 | 6.36 | 1.347 | 4.735 | 8445.26 | 2.1 | 97.8 | 77.9 | 1379 | 22.91 | 5489.4 | 2922.4 | 2837.1 | 4187.3 | 1192.2 | 0.6822 | 6.082
2024-12-09 | 15:59 | Data | 0 | 31.88 | 29.787 | 189.208 | 7.64 | 177.679 | 2120.39 | 26.02 | 45.727 | 6.36 | 1.343 | 4.761 | 8463.35 | 1.85 | 97.8 | 78 | 1378 | 22.86 | 5501.2 | 2925.9 | 2842.3 | 4194.1 | 1192.2 | 0.68101 | 6.104
2024-12-09 | 15:59 | Data | 0 | 32.143 | 29.955 | 189.253 | 7.64 | 177.769 | 2123.1 | 26.05 | 45.727 | 6.36 | 1.341 | 4.749 | 8454.3 | 2.079 | 97.8 | 78 | 1380 | 22.86 | 5495.3 | 2929.3 | 2826.6 | 4187.6 | 1192.2 | 0.68258 | 6.092
2024-12-09 | 15:59 | Data | 0 | 32.406 | 30.192 | 189.388 | 7.64 | 177.905 | 2120.39 | 26.05 | 45.727 | 6.36 | 1.351 | 4.741 | 8458.83 | 1.87 | 97.8 | 77.8 | 1378 | 22.86 | 5498.2 | 2935.4 | 2815.5 | 4181.6 | 1192.2 | 0.6868 | 6.091
2024-12-09 | 15:59 | Data | 0 | 32.271 | 30.185 | 189.343 | 7.64 | 177.814 | 2127.62 | 26.06 | 45.637 | 6.37 | 1.356 | 4.735 | 8458.83 | 2.079 | 97.9 | 77.8 | 1383 | 22.86 | 5498.2 | 2942 | 2831 | 4198.7 | 1192.2 | 0.68467 | 6.09
2024-12-09 | 15:59 | Data | 0 | 32.264 | 30.3 | 189.434 | 7.64 | 177.814 | 2123.1 | 26.07 | 45.727 | 6.36 | 1.359 | 4.74 | 8436.21 | 2.079 | 97.8 | 77.7 | 1381 | 22.86 | 5483.5 | 2932.2 | 2858.3 | 4217.2 | 1192.2 | 0.67974 | 6.099
2024-12-09 | 15:59 | Data | 0 | 32.035 | 30.185 | 189.343 | 7.64 | 177.769 | 2120.39 | 26.06 | 45.637 | 6.36 | 1.358 | 4.757 | 8454.3 | 1.965 | 97.8 | 77.8 | 1378 | 22.86 | 5495.3 | 2938 | 2864.4 | 4204.7 | 1192.2 | 0.68127 | 6.113
2024-12-09 | 15:59 | Data | 0 | 32.372 | 30.016 | 189.434 | 7.64 | 177.86 | 2118.58 | 26.06 | 45.727 | 6.37 | 1.365 | 4.738 | 8472.39 | 1.978 | 97.8 | 77.6 | 1378 | 22.86 | 5507.1 | 2933.7 | 2826.7 | 4188.9 | 1192.2 | 0.6834 | 6.102
2024-12-09 | 15:59 | Data | 0 | 32.264 | 30.178 | 189.388 | 7.64 | 177.814 | 2120.39 | 26.07 | 45.727 | 6.36 | 1.367 | 4.729 | 8476.91 | 2.093 | 97.8 | 77.6 | 1378 | 22.82 | 5510 | 2933.6 | 2858.2 | 4215.4 | 1192.2 | 0.67989 | 6.095
2024-12-09 | 15:59 | Data | 0 | 32.48 | 30.185 | 189.615 | 7.64 | 177.814 | 2120.39 | 26.05 | 45.727 | 6.36 | 1.357 | 4.721 | 8476.91 | 1.965 | 97.8 | 77.7 | 1378 | 22.91 | 5510 | 2927.3 | 2851.8 | 4204.6 | 1192.2 | 0.67962 | 6.079
2024-12-09 | 15:59 | Data | 0 | 32.44 | 30.455 | 189.434 | 7.64 | 177.814 | 2114.06 | 26.06 | 45.727 | 6.36 | 1.361 | 4.75 | 8481.44 | 1.897 | 97.8 | 77.7 | 1374 | 22.86 | 5512.9 | 2945.6 | 2870.6 | 4228.7 | 1192.3 | 0.67979 | 6.111
2024-12-09 | 15:59 | Data | 0 | 32.123 | 30.192 | 189.343 | 7.64 | 177.86 | 2114.06 | 26.06 | 45.727 | 6.37 | 1.358 | 4.744 | 8499.53 | 1.85 | 97.8 | 77.8 | 1374 | 22.86 | 5524.7 | 2922.9 | 2856.8 | 4204.5 | 1192.3 | 0.67929 | 6.102
2024-12-09 | 15:59 | Data | 0 | 32.453 | 30.185 | 189.479 | 7.64 | 177.814 | 2111.35 | 26.06 | 45.727 | 6.36 | 1.353 | 4.747 | 8513.09 | 2.214 | 97.8 | 77.8 | 1372 | 22.86 | 5533.5 | 2914.6 | 2822.7 | 4173.5 | 1192.3 | 0.68163 | 6.101
2024-12-09 | 15:59 | Data | 0 | 32.312 | 30.185 | 189.343 | 7.64 | 177.679 | 2106.83 | 26.06 | 45.637 | 6.36 | 1.355 | 4.768 | 8513.09 | 2.228 | 97.8 | 77.9 | 1369 | 22.86 | 5533.5 | 2920.2 | 2847.7 | 4196.1 | 1192.3 | 0.67981 | 6.124
2024-12-09 | 15:59 | Data | 0 | 32.588 | 30.529 | 188.665 | 7.65 | 177.182 | 2106.83 | 26.07 | 45.727 | 6.37 | 1.358 | 8.455 | 8508.57 | 2.275 | 97.8 | 86.1 | 1369 | 22.86 | 5530.6 | 2917.9 | 2817.9 | 4171.6 | 1192.3 | 0.68332 | 9.742
2024-12-09 | 16:00 | Data | 0 | 32.494 | 30.752 | 183.011 | 7.64 | 171.939 | 2101.41 | 26.06 | 45.637 | 6.37 | 1.346 | 4.688 | 8499.53 | 1.944 | 97.8 | 77.7 | 1365 | 22.86 | 5524.7 | 2871.6 | 2778.8 | 4114.9 | 1192.3 | 0.6814 | 6.036
2024-12-09 | 16:00 | Data | 0 | 32.885 | 30.61 | 183.101 | 7.64 | 172.075 | 2109.54 | 26.06 | 45.818 | 6.36 | 1.339 | 4.603 | 8481.44 | 2.025 | 97.8 | 77.5 | 1370 | 22.91 | 5512.9 | 2854.8 | 2772.1 | 4101.2 | 1192.3 | 0.67947 | 5.94
2024-12-09 | 16:00 | Data | 0 | 32.723 | 30.415 | 183.101 | 7.64 | 172.075 | 2112.26 | 26.06 | 45.727 | 6.37 | 1.332 | 4.625 | 8472.39 | 2.106 | 97.8 | 77.6 | 1373 | 22.91 | 5507.1 | 2865.3 | 2777.1 | 4112.7 | 1192.3 | 0.68065 | 5.957
2024-12-09 | 16:00 | Data | 0 | 32.393 | 30.442 | 183.101 | 7.64 | 171.939 | 2109.54 | 26.05 | 46.089 | 6.36 | 1.329 | 4.63 | 8481.44 | 1.911 | 97.8 | 77.7 | 1371 | 23 | 5512.9 | 2830.6 | 2757.4 | 4071.3 | 1192.3 | 0.68021 | 5.959
2024-12-09 | 16:00 | Data | 0 | 32.298 | 30.624 | 182.875 | 7.64 | 171.894 | 2114.06 | 26.06 | 45.998 | 6.37 | 1.332 | 4.64 | 8440.74 | 1.85 | 97.8 | 77.7 | 1374 | 23 | 5486.5 | 2872.7 | 2751.5 | 4096.8 | 1192.3 | 0.68506 | 5.972
2024-12-09 | 16:00 | Data | 0 | 32.636 | 30.536 | 183.056 | 7.64 | 171.984 | 2114.97 | 26.06 | 46.269 | 6.37 | 1.331 | 4.618 | 8445.26 | 1.877 | 97.8 | 77.6 | 1375 | 23.13 | 5489.4 | 2858.9 | 2737 | 4078.7 | 1192.3 | 0.68413 | 5.952
2024-12-09 | 16:00 | Data | 0 | 32.494 | 30.421 | 182.965 | 7.64 | 171.894 | 2117.68 | 26.06 | 46.54 | 6.36 | 1.324 | 4.621 | 8431.69 | 2.059 | 97.8 | 77.7 | 1377 | 23.27 | 5480.6 | 2863.2 | 2775.6 | 4107.6 | 1192.3 | 0.6806 | 5.944
2024-12-09 | 16:00 | Data | 0 | 32.811 | 30.489 | 183.101 | 7.64 | 172.03 | 2111.35 | 26.06 | 46.54 | 6.37 | 1.331 | 4.62 | 8431.69 | 2.1 | 97.8 | 77.6 | 1373 | 23.22 | 5480.6 | 2858.5 | 2769.3 | 4098.6 | 1192.3 | 0.68066 | 5.951
2024-12-09 | 16:00 | Data | 0 | 32.494 | 30.421 | 183.282 | 7.64 | 172.256 | 2120.39 | 26.07 | 46.45 | 6.37 | 1.33 | 4.591 | 8454.3 | 2.073 | 97.8 | 77.5 | 1378 | 23.22 | 5495.3 | 2869.3 | 2777.4 | 4113.3 | 1192.3 | 0.68003 | 5.922
2024-12-09 | 16:00 | Data | 0 | 32.71 | 30.428 | 183.689 | 7.64 | 172.527 | 2120.39 | 26.07 | 46.54 | 6.37 | 1.338 | 4.616 | 8445.26 | 2.093 | 97.8 | 77.5 | 1378 | 23.27 | 5489.4 | 2881.6 | 2787.9 | 4129.4 | 1192.3 | 0.68041 | 5.954
2024-12-09 | 16:00 | Data | 0 | 32.264 | 30.408 | 183.644 | 7.64 | 172.482 | 2119.49 | 26.07 | 46.63 | 6.37 | 1.343 | 4.641 | 8431.69 | 2.032 | 97.8 | 77.6 | 1378 | 23.36 | 5480.6 | 2896.4 | 2775 | 4128.9 | 1192.3 | 0.6856 | 5.984
2024-12-09 | 16:00 | Data | 0 | 32.818 | 30.536 | 183.734 | 7.64 | 172.572 | 2122.2 | 26.06 | 46.721 | 6.37 | 1.345 | 4.656 | 8418.13 | 2.113 | 97.8 | 77.6 | 1379 | 23.36 | 5471.8 | 2877.1 | 2772.5 | 4116.8 | 1192.3 | 0.68277 | 5.999
2024-12-09 | 16:00 | Data | 0 | 32.717 | 30.651 | 183.825 | 7.64 | 172.617 | 2120.39 | 26.07 | 46.54 | 6.37 | 1.338 | 4.625 | 8427.17 | 2.073 | 97.8 | 77.6 | 1378 | 23.22 | 5477.7 | 2863.6 | 2766.4 | 4102.3 | 1192.3 | 0.68246 | 5.962
2024-12-09 | 16:00 | Data | 0 | 32.804 | 30.705 | 183.825 | 7.64 | 172.662 | 2117.68 | 26.07 | 46.54 | 6.37 | 1.335 | 4.601 | 8440.74 | 1.89 | 97.8 | 77.5 | 1376 | 23.27 | 5486.5 | 2855.4 | 2781 | 4104.4 | 1192.3 | 0.67991 | 5.936
2024-12-09 | 16:00 | Data | 0 | 32.933 | 30.455 | 183.87 | 7.64 | 172.753 | 2117.68 | 26.07 | 46.45 | 6.37 | 1.335 | 4.632 | 8436.21 | 2.241 | 97.8 | 77.6 | 1376 | 23.27 | 5483.5 | 2861.6 | 2781.1 | 4113.2 | 1192.3 | 0.67972 | 5.967
2024-12-09 | 16:00 | Data | 0 | 32.568 | 30.637 | 183.915 | 7.64 | 172.753 | 2117.68 | 26.06 | 46.54 | 6.37 | 1.337 | 4.646 | 8427.17 | 1.971 | 97.8 | 77.7 | 1377 | 23.32 | 5477.7 | 2880.3 | 2777.1 | 4119.4 | 1192.3 | 0.68253 | 5.984
2024-12-09 | 16:00 | Data | 0 | 32.501 | 30.428 | 183.825 | 7.64 | 172.798 | 2119.49 | 26.08 | 46.721 | 6.37 | 1.339 | 4.648 | 8449.78 | 2.066 | 97.8 | 77.6 | 1378 | 23.36 | 5492.4 | 2876.1 | 2776.8 | 4118.5 | 1192.3 | 0.6813 | 5.988
2024-12-09 | 16:00 | Data | 0 | 32.514 | 30.59 | 183.825 | 7.64 | 172.662 | 2122.2 | 26.06 | 46.721 | 6.37 | 1.338 | 4.639 | 8440.74 | 1.958 | 97.8 | 77.6 | 1379 | 23.41 | 5486.5 | 2886 | 2769.1 | 4120.8 | 1192.3 | 0.68637 | 5.976
2024-12-09 | 16:01 | Data | 0 | 32.44 | 30.415 | 183.87 | 7.64 | 172.617 | 2114.97 | 26.05 | 46.811 | 6.38 | 1.344 | 4.631 | 8445.26 | 2.16 | 97.8 | 77.5 | 1376 | 23.5 | 5489.4 | 2868.5 | 2767.6 | 4106.5 | 1192.3 | 0.68202 | 5.976
2024-12-09 | 16:01 | Data | 0 | 32.271 | 30.577 | 183.825 | 7.64 | 172.662 | 2123.1 | 26.07 | 46.54 | 6.37 | 1.338 | 4.635 | 8418.13 | 1.931 | 97.8 | 77.6 | 1379 | 23.27 | 5471.8 | 2865.9 | 2769.1 | 4103.6 | 1192.3 | 0.68117 | 5.971
2024-12-09 | 16:01 | Data | 0 | 32.413 | 30.421 | 183.825 | 7.64 | 172.617 | 2125.81 | 26.08 | 46.45 | 6.37 | 1.348 | 4.645 | 8458.83 | 2.039 | 97.8 | 77.5 | 1382 | 23.18 | 5498.2 | 2862.6 | 2762.6 | 4098.6 | 1192.3 | 0.68313 | 5.99
2024-12-09 | 16:01 | Data | 0 | 32.636 | 30.34 | 183.87 | 7.64 | 172.753 | 2119.49 | 26.07 | 46.54 | 6.37 | 1.341 | 4.621 | 8454.3 | 1.971 | 97.8 | 77.5 | 1378 | 23.27 | 5495.3 | 2858.6 | 2765.2 | 4098 | 1192.3 | 0.68186 | 5.962
2024-12-09 | 16:01 | Data | 0 | 32.568 | 30.739 | 183.915 | 7.64 | 172.753 | 2123.1 | 26.07 | 46.54 | 6.37 | 1.344 | 4.637 | 8458.83 | 1.762 | 97.8 | 77.5 | 1379 | 23.22 | 5498.2 | 2862.8 | 2778 | 4105.4 | 1192.3 | 0.68106 | 5.98
2024-12-09 | 16:01 | Data | 0 | 32.494 | 30.624 | 183.734 | 7.64 | 172.708 | 2119.49 | 26.03 | 46.54 | 6.37 | 1.339 | 4.624 | 8463.35 | 1.904 | 97.8 | 77.5 | 1378 | 23.22 | 5501.2 | 2862.9 | 2758.6 | 4095.2 | 1192.3 | 0.68378 | 5.961
2024-12-09 | 16:01 | Data | 0 | 32.717 | 30.766 | 183.734 | 7.64 | 172.708 | 2119.49 | 26.06 | 46.63 | 6.37 | 1.338 | 4.607 | 8418.13 | 2.113 | 97.8 | 77.5 | 1378 | 23.22 | 5471.8 | 2879.5 | 2776.8 | 4117.9 | 1192.3 | 0.68326 | 5.942
2024-12-09 | 16:01 | Data | 0 | 32.609 | 30.678 | 183.961 | 7.64 | 172.798 | 2114.06 | 26.06 | 46.54 | 6.37 | 1.342 | 4.625 | 8418.13 | 2.221 | 97.8 | 77.5 | 1374 | 23.22 | 5471.8 | 2881.6 | 2760.7 | 4108.6 | 1192.3 | 0.68479 | 5.969
2024-12-09 | 16:01 | Data | 0 | 32.494 | 30.637 | 183.825 | 7.64 | 172.662 | 2113.16 | 26.07 | 46.721 | 6.37 | 1.328 | 4.618 | 8427.17 | 1.971 | 97.8 | 77.7 | 1374 | 23.36 | 5477.7 | 2865.1 | 2752.2 | 4095.5 | 1192.3 | 0.68396 | 5.946
2024-12-09 | 16:01 | Data | 0 | 32.919 | 30.786 | 184.051 | 7.64 | 172.753 | 2114.06 | 26.08 | 46.721 | 6.37 | 1.331 | 4.631 | 8422.65 | 1.978 | 97.8 | 77.7 | 1374 | 23.36 | 5474.7 | 2882 | 2765.5 | 4115.2 | 1192.3 | 0.68464 | 5.961
2024-12-09 | 16:01 | Data | 0 | 32.885 | 30.664 | 183.961 | 7.64 | 172.798 | 2111.35 | 26.06 | 46.811 | 6.37 | 1.323 | 4.628 | 8431.69 | 2.113 | 97.8 | 77.8 | 1372 | 23.36 | 5480.6 | 2870.6 | 2772.2 | 4113.5 | 1192.3 | 0.68152 | 5.953
2024-12-09 | 16:01 | Data | 0 | 32.919 | 30.901 | 184.006 | 7.64 | 172.753 | 2111.35 | 26.07 | 46.45 | 6.37 | 1.334 | 4.65 | 8834.17 | 1.931 | 97.8 | 77.7 | 1373 | 23.32 | 5742.2 | 2876.2 | 2772.5 | 4114.4 | 1192.3 | 0.68424 | 5.984
2024-12-09 | 16:01 | Data | 0 | 32.501 | 30.421 | 183.961 | 7.64 | 172.798 | 2112.26 | 26.06 | 46.54 | 6.37 | 1.34 | 4.655 | 8395.51 | 2.052 | 97.8 | 77.6 | 1372 | 23.22 | 5457.1 | 2873.8 | 2757.2 | 4100.9 | 1192.3 | 0.68459 | 5.996
2024-12-09 | 16:01 | Data | 0 | 32.69 | 30.975 | 183.915 | 7.64 | 172.798 | 2112.26 | 26.07 | 46.54 | 6.37 | 1.339 | 4.632 | 8372.9 | 1.87 | 97.8 | 77.6 | 1373 | 23.22 | 5442.4 | 2892.6 | 2773.4 | 4123.8 | 1192.3 | 0.68604 | 5.971
2024-12-09 | 16:01 | Data | 0 | 32.494 | 30.536 | 183.825 | 7.63 | 172.753 | 2003.8 | 26.06 | 46.45 | 6.37 | 1.338 | 4.629 | 8381.95 | 2.079 | 97.7 | 77.6 | 1302 | 23.22 | 5448.3 | 2867.9 | 2771.8 | 4111 | 1192.4 | 0.68115 | 5.967
2024-12-09 | 16:01 | Data | 0 | 32.44 | 30.644 | 183.87 | 7.64 | 172.753 | 2105.03 | 26.07 | 46.45 | 6.37 | 1.347 | 4.648 | 8386.47 | 2.032 | 97.8 | 77.5 | 1369 | 23.22 | 5451.2 | 2862 | 2782.4 | 4111.3 | 1192.4 | 0.67927 | 5.994
2024-12-09 | 16:01 | Data | 0 | 32.75 | 30.651 | 184.006 | 7.64 | 172.753 | 2106.83 | 26.06 | 46.45 | 6.37 | 1.341 | 4.616 | 8381.95 | 2.073 | 97.8 | 77.5 | 1369 | 23.22 | 5448.3 | 2877.6 | 2766.1 | 4109 | 1192.4 | 0.68247 | 5.958
2024-12-09 | 16:01 | Data | 0 | 32.494 | 30.415 | 184.096 | 7.64 | 172.934 | 2106.83 | 26.06 | 46.54 | 6.37 | 1.341 | 4.595 | 8386.47 | 2.079 | 97.8 | 77.4 | 1369 | 23.27 | 5451.2 | 2868.8 | 2765.6 | 4100.8 | 1192.4 | 0.68248 | 5.937
2024-12-09 | 16:02 | Data | 0 | 32.467 | 30.415 | 184.594 | 7.64 | 173.34 | 2106.83 | 26.06 | 46.269 | 6.37 | 1.33 | 4.635 | 8372.9 | 2.127 | 97.8 | 77.7 | 1371 | 23.13 | 5442.4 | 2883.5 | 2778.3 | 4122.2 | 1192.4 | 0.68389 | 5.965
2024-12-09 | 16:02 | Data | 0 | 32.919 | 30.88 | 184.73 | 7.64 | 173.521 | 2120.39 | 26.06 | 46.54 | 6.37 | 1.329 | 4.67 | 8386.47 | 2.066 | 97.8 | 77.8 | 1378 | 23.22 | 5451.2 | 2874.9 | 2755.7 | 4106.7 | 1192.4 | 0.68397 | 5.999
2024-12-09 | 16:02 | Data | 0 | 32.514 | 30.205 | 184.549 | 7.64 | 173.385 | 2122.2 | 26.07 | 46.45 | 6.37 | 1.336 | 4.657 | 8381.95 | 2.073 | 97.8 | 77.7 | 1379 | 23.27 | 5448.3 | 2898.2 | 2776.3 | 4131.8 | 1192.4 | 0.68399 | 5.993
2024-12-09 | 16:02 | Data | 0 | 32.507 | 30.415 | 184.639 | 7.64 | 173.476 | 2122.2 | 26.06 | 46.45 | 6.37 | 1.332 | 4.686 | 8386.47 | 2.079 | 97.8 | 77.9 | 1380 | 23.18 | 5451.2 | 2884.9 | 2769.3 | 4099.6 | 1192.4 | 0.68468 | 6.019
2024-12-09 | 16:02 | Data | 0 | 32.494 | 30.516 | 184.639 | 7.64 | 173.34 | 2123.1 | 26.06 | 46.54 | 6.37 | 1.331 | 4.658 | 8418.13 | 1.904 | 97.8 | 77.8 | 1380 | 23.27 | 5471.8 | 2873.5 | 2775.6 | 4119 | 1192.4 | 0.68032 | 5.989
2024-12-09 | 16:02 | Data | 0 | 32.548 | 30.421 | 184.594 | 7.65 | 173.385 | 2124.01 | 26.07 | 46.54 | 6.36 | 1.34 | 4.626 | 8409.08 | 2.086 | 97.8 | 77.5 | 1381 | 23.27 | 5465.9 | 2903.1 | 2780.4 | 4135.2 | 1192.4 | 0.68467 | 5.968
2024-12-09 | 16:02 | Data | 0 | 32.285 | 30.847 | 184.639 | 7.64 | 173.476 | 2123.1 | 26.05 | 46.45 | 6.37 | 1.342 | 4.616 | 8404.56 | 1.816 | 97.8 | 77.5 | 1381 | 23.27 | 5463 | 2865.4 | 2770.6 | 4107.6 | 1192.4 | 0.67977 | 5.956
2024-12-09 | 16:02 | Data | 0 | 32.926 | 30.455 | 184.73 | 7.64 | 173.521 | 2122.2 | 26.07 | 46.54 | 6.37 | 1.34 | 4.62 | 8409.08 | 2.241 | 97.8 | 77.5 | 1379 | 23.27 | 5465.9 | 2868.5 | 2765.1 | 4110 | 1192.4 | 0.68308 | 5.961
2024-12-09 | 16:02 | Data | 0 | 32.507 | 30.691 | 184.73 | 7.64 | 173.476 | 2128.52 | 26.06 | 46.54 | 6.37 | 1.343 | 4.633 | 8427.17 | 1.857 | 97.8 | 77.5 | 1383 | 23.22 | 5477.7 | 2890.6 | 2768.6 | 4121.3 | 1192.4 | 0.68414 | 5.978
2024-12-09 | 16:02 | Data | 0 | 32.885 | 30.651 | 184.639 | 7.64 | 173.431 | 2122.2 | 26.06 | 46.54 | 6.37 | 1.345 | 4.663 | 8422.65 | 2.086 | 97.8 | 77.6 | 1379 | 23.22 | 5474.7 | 2891.4 | 2767.1 | 4121 | 1192.4 | 0.68298 | 6.007
2024-12-09 | 16:02 | Data | 0 | 32.507 | 30.421 | 184.594 | 7.64 | 173.476 | 2124.91 | 26.07 | 46.45 | 6.37 | 1.34 | 4.654 | 8427.17 | 2.073 | 97.8 | 77.6 | 1382 | 23.22 | 5477.7 | 2870 | 2759.9 | 4103.6 | 1192.4 | 0.68339 | 5.995
2024-12-09 | 16:02 | Data | 0 | 32.906 | 30.664 | 184.594 | 7.64 | 173.476 | 2125.81 | 26.06 | 46.54 | 6.37 | 1.338 | 4.656 | 8431.69 | 2.154 | 97.8 | 77.7 | 1381 | 23.27 | 5480.6 | 2871.6 | 2757.5 | 4100.9 | 1192.4 | 0.68305 | 5.994
2024-12-09 | 16:02 | Data | 0 | 32.366 | 30.415 | 184.594 | 7.64 | 173.521 | 2123.1 | 26.06 | 46.54 | 6.37 | 1.334 | 4.671 | 8440.74 | 1.863 | 97.8 | 77.8 | 1379 | 23.22 | 5486.5 | 2878.6 | 2774.5 | 4119.1 | 1192.4 | 0.68299 | 6.005
2024-12-09 | 16:02 | Data | 0 | 32.426 | 30.415 | 184.549 | 7.64 | 173.476 | 2125.81 | 26.06 | 46.54 | 6.37 | 1.33 | 4.654 | 8445.26 | 1.863 | 97.8 | 77.8 | 1382 | 23.27 | 5489.4 | 2887.8 | 2772.6 | 4120.7 | 1192.4 | 0.68404 | 5.986
2024-12-09 | 16:02 | Data | 0 | 32.494 | 30.415 | 184.594 | 7.64 | 173.431 | 2123.1 | 26.06 | 46.45 | 6.36 | 1.344 | 4.659 | 8440.74 | 2.066 | 97.8 | 77.6 | 1380 | 23.22 | 5486.5 | 2893 | 2770.1 | 4126.1 | 1192.4 | 0.68745 | 6.003
2024-12-09 | 16:02 | Data | 0 | 32.264 | 30.59 | 184.594 | 7.64 | 173.431 | 2123.1 | 26.07 | 46.54 | 6.37 | 1.339 | 4.656 | 8449.78 | 1.85 | 97.8 | 77.7 | 1379 | 23.22 | 5492.4 | 2865.5 | 2764.3 | 4104.2 | 1192.4 | 0.68183 | 5.996
2024-12-09 | 16:02 | Data | 0 | 32.831 | 30.448 | 184.639 | 7.64 | 173.431 | 2124.91 | 26.07 | 46.54 | 6.37 | 1.339 | 4.643 | 8418.13 | 2.093 | 97.8 | 77.6 | 1381 | 23.22 | 5471.8 | 2876.5 | 2776.1 | 4117.2 | 1192.4 | 0.68254 | 5.984
2024-12-09 | 16:02 | Data | 0 | 32.825 | 30.867 | 184.594 | 7.64 | 173.521 | 2102.31 | 26.06 | 46.54 | 6.37 | 1.343 | 4.635 | 8431.69 | 2.073 | 97.8 | 77.5 | 1357 | 23.27 | 5480.6 | 2890.8 | 2747.2 | 4107 | 1192.4 | 0.68801 | 5.979
2024-12-09 | 16:03 | Data | 0 | 32.777 | 30.651 | 184.639 | 7.64 | 173.566 | 2042.66 | 26.06 | 46.54 | 6.37 | 1.341 | 4.638 | 8400.04 | 1.877 | 97.7 | 77.6 | 1335 | 23.22 | 5460 | 2864.5 | 2760.6 | 4097.9 | 1192.4 | 0.68224 | 5.98
2024-12-09 | 16:03 | Data | 0 | 32.48 | 30.415 | 184.73 | 7.64 | 173.431 | 2123.1 | 26.06 | 47.082 | 6.36 | 1.334 | 4.654 | 8404.56 | 2.167 | 97.8 | 77.7 | 1380 | 23.59 | 5463 | 2863.3 | 2770.5 | 4104.9 | 1192.4 | 0.68507 | 5.988
2024-12-09 | 16:03 | Data | 0 | 32.94 | 30.88 | 184.73 | 7.64 | 173.521 | 2123.1 | 26.06 | 46.45 | 6.36 | 1.334 | 4.658 | 8422.65 | 2.073 | 97.8 | 77.8 | 1379 | 23.18 | 5474.7 | 2868 | 2766.4 | 4103.1 | 1192.4 | 0.68291 | 5.99
2024-12-09 | 16:03 | Data | 0 | 32.312 | 30.421 | 184.639 | 7.64 | 173.476 | 2122.2 | 26.07 | 46.45 | 6.37 | 1.345 | 4.652 | 8436.21 | 1.85 | 97.8 | 77.6 | 1379 | 23.27 | 5483.5 | 2888.7 | 2769.6 | 4117.8 | 1192.4 | 0.68709 | 5.998
2024-12-09 | 16:03 | Data | 0 | 32.494 | 30.651 | 184.639 | 7.64 | 173.431 | 2122.2 | 26.06 | 46.45 | 6.37 | 1.347 | 4.649 | 8418.13 | 1.85 | 97.8 | 77.5 | 1380 | 23.22 | 5471.8 | 2882.5 | 2766.9 | 4113.4 | 1192.4 | 0.68414 | 5.996
2024-12-09 | 16:03 | Data | 0 | 32.561 | 30.543 | 184.549 | 7.64 | 173.476 | 2123.1 | 26.06 | 46.54 | 6.37 | 1.337 | 4.651 | 8431.69 | 2.093 | 97.8 | 77.7 | 1380 | 23.27 | 5480.6 | 2889.8 | 2774.7 | 4126.1 | 1192.4 | 0.68278 | 5.988
2024-12-09 | 16:03 | Data | 0 | 32.561 | 30.624 | 184.775 | 7.64 | 173.521 | 2123.1 | 26.07 | 46.45 | 6.37 | 1.329 | 4.647 | 8418.13 | 1.978 | 97.8 | 77.8 | 1380 | 23.22 | 5471.8 | 2883.2 | 2789.5 | 4130.6 | 1192.4 | 0.6818 | 5.975
2024-12-09 | 16:03 | Data | 0 | 32.507 | 30.651 | 184.91 | 7.64 | 173.611 | 2122.2 | 26.06 | 46.54 | 6.37 | 1.337 | 4.65 | 8418.13 | 2.046 | 97.8 | 77.7 | 1379 | 23.27 | 5471.8 | 2882.5 | 2760.9 | 4108.4 | 1192.4 | 0.68427 | 5.987
2024-12-09 | 16:03 | Data | 0 | 32.723 | 30.489 | 184.775 | 7.64 | 173.566 | 2122.2 | 26.07 | 46.269 | 6.37 | 1.332 | 4.656 | 8431.69 | 2.167 | 97.8 | 77.8 | 1379 | 23.13 | 5480.6 | 2885.6 | 2775.6 | 4123 | 1192.4 | 0.68392 | 5.988
2024-12-09 | 16:03 | Data | 0 | 32.575 | 30.509 | 184.639 | 7.64 | 173.385 | 2123.1 | 26.06 | 46.359 | 6.36 | 1.338 | 4.639 | 8431.69 | 2.343 | 97.8 | 77.6 | 1379 | 23.27 | 5480.6 | 2878.2 | 2765.8 | 4111 | 1192.4 | 0.68274 | 5.975
2024-12-09 | 16:03 | Data | 0 | 32.507 | 30.637 | 184.594 | 7.64 | 173.385 | 2123.1 | 26.06 | 46.54 | 6.37 | 1.338 | 4.636 | 8381.95 | 1.897 | 97.8 | 77.6 | 1380 | 23.27 | 5448.3 | 2876.4 | 2775.3 | 4115 | 1192.4 | 0.68384 | 5.973
2024-12-09 | 16:03 | Data | 0 | 32.717 | 30.651 | 184.503 | 7.64 | 173.476 | 2123.1 | 26.06 | 46.45 | 6.37 | 1.343 | 4.618 | 8404.56 | 1.897 | 97.8 | 77.5 | 1379 | 23.22 | 5463 | 2864.9 | 2770.2 | 4102.5 | 1192.4 | 0.68167 | 5.962
2024-12-09 | 16:03 | Data | 0 | 32.723 | 30.874 | 184.82 | 7.64 | 173.476 | 2121.29 | 26.07 | 46.359 | 6.37 | 1.343 | 4.619 | 8409.08 | 2.059 | 97.8 | 77.5 | 1378 | 23.22 | 5465.9 | 2890.1 | 2779.8 | 4119.1 | 1192.4 | 0.68415 | 5.962
2024-12-09 | 16:03 | Data | 0 | 32.825 | 30.448 | 184.639 | 7.64 | 173.611 | 2123.1 | 26.06 | 46.54 | 6.37 | 1.336 | 4.649 | 8390.99 | 2.1 | 97.8 | 77.7 | 1381 | 23.32 | 5454.1 | 2881.5 | 2784.3 | 4125.2 | 1192.4 | 0.68329 | 5.986
2024-12-09 | 16:03 | Data | 0 | 32.723 | 30.853 | 184.865 | 7.64 | 173.431 | 2123.1 | 26.06 | 46.54 | 6.37 | 1.331 | 4.65 | 8400.04 | 2.039 | 97.8 | 77.8 | 1380 | 23.18 | 5460 | 2873.4 | 2779.7 | 4118.3 | 1192.4 | 0.6813 | 5.98
2024-12-09 | 16:03 | Data | 0 | 32.723 | 30.826 | 184.73 | 7.64 | 173.476 | 2123.1 | 26.07 | 46.45 | 6.36 | 1.347 | 4.659 | 8409.08 | 2.073 | 97.8 | 77.6 | 1381 | 23.27 | 5465.9 | 2873.5 | 2771.6 | 4113.1 | 1192.5 | 0.6832 | 6.005
2024-12-09 | 16:03 | Data | 0 | 32.582 | 30.563 | 184.594 | 7.64 | 173.476 | 2122.2 | 26.07 | 46.54 | 6.37 | 1.349 | 4.649 | 8422.65 | 2.235 | 97.8 | 77.5 | 1380 | 23.27 | 5474.7 | 2901.3 | 2787.9 | 4140.2 | 1192.5 | 0.68468 | 5.999
2024-12-09 | 16:04 | Data | 0 | 32.278 | 30.421 | 184.594 | 7.64 | 173.385 | 2123.1 | 26.06 | 46.63 | 6.36 | 1.351 | 4.645 | 8431.69 | 1.843 | 97.8 | 77.5 | 1380 | 23.27 | 5480.6 | 2886.8 | 2763.2 | 4114.2 | 1192.5 | 0.68596 | 5.996
2024-12-09 | 16:04 | Data | 0 | 33.048 | 30.786 | 184.865 | 7.64 | 173.521 | 2123.1 | 26.06 | 46.45 | 6.37 | 1.341 | 4.671 | 8400.04 | 2.052 | 97.8 | 77.7 | 1380 | 23.27 | 5460 | 2891 | 2774.3 | 4125.6 | 1192.5 | 0.68424 | 6.012
2024-12-09 | 16:04 | Data | 0 | 32.595 | 30.651 | 184.594 | 7.64 | 173.476 | 2121.29 | 26.05 | 46.54 | 6.37 | 1.329 | 4.66 | 8404.56 | 2.066 | 97.8 | 77.8 | 1378 | 23.27 | 5463 | 2889 | 2744 | 4105.9 | 1192.5 | 0.68773 | 5.988
2024-12-09 | 16:04 | Data | 0 | 32.325 | 30.415 | 184.639 | 7.64 | 173.431 | 2119.49 | 26.07 | 46.54 | 6.37 | 1.335 | 4.624 | 8400.04 | 2.059 | 97.8 | 77.6 | 1378 | 23.27 | 5460 | 2875.3 | 2758.9 | 4104.7 | 1192.5 | 0.68605 | 5.959
2024-12-09 | 16:04 | Data | 0 | 32.71 | 30.536 | 184.594 | 7.64 | 173.566 | 2120.39 | 26.06 | 46.45 | 6.36 | 1.331 | 4.639 | 8418.13 | 2.086 | 97.8 | 77.7 | 1378 | 23.27 | 5471.8 | 2883 | 2774.5 | 4124 | 1192.5 | 0.68231 | 5.97
2024-12-09 | 16:04 | Data | 0 | 32.75 | 30.61 | 184.775 | 7.64 | 173.476 | 2120.39 | 26.06 | 46.54 | 6.37 | 1.338 | 4.635 | 8395.51 | 2.16 | 97.8 | 77.6 | 1378 | 23.27 | 5457.1 | 2892.5 | 2782.1 | 4130.7 | 1192.5 | 0.68534 | 5.971
2024-12-09 | 16:04 | Data | 0 | 32.507 | 30.327 | 184.594 | 7.64 | 173.476 | 2120.39 | 26.07 | 46.45 | 6.37 | 1.334 | 4.657 | 8418.13 | 1.965 | 97.8 | 77.7 | 1378 | 23.22 | 5471.8 | 2880.4 | 2778.6 | 4122.9 | 1192.5 | 0.68305 | 5.991
2024-12-09 | 16:04 | Data | 0 | 32.494 | 30.759 | 184.775 | 7.64 | 173.476 | 2120.39 | 26.06 | 46.63 | 6.37 | 1.341 | 4.667 | 8427.17 | 1.931 | 97.8 | 77.7 | 1378 | 23.32 | 5477.7 | 2888.3 | 2771.3 | 4127.3 | 1192.5 | 0.68628 | 6.008
2024-12-09 | 16:04 | Data | 0 | 32.825 | 30.448 | 184.82 | 7.64 | 173.566 | 2118.58 | 26.06 | 46.54 | 6.36 | 1.337 | 4.637 | 8422.65 | 2.012 | 97.8 | 77.6 | 1378 | 23.27 | 5474.7 | 2879.8 | 2767.1 | 4110.4 | 1192.5 | 0.68538 | 5.977
2024-12-09 | 16:04 | Data | 0 | 32.649 | 30.421 | 184.73 | 7.64 | 173.521 | 2120.39 | 26.06 | 46.45 | 6.37 | 1.339 | 4.658 | 8395.51 | 1.924 | 97.8 | 77.7 | 1378 | 23.22 | 5457.1 | 2884.8 | 2779.5 | 4125.1 | 1192.5 | 0.68284 | 5.997
2024-12-09 | 16:04 | Data | 0 | 32.831 | 30.982 | 184.82 | 7.64 | 173.566 | 2120.39 | 26.06 | 46.54 | 6.37 | 1.346 | 4.667 | 8400.04 | 1.978 | 97.8 | 77.6 | 1379 | 23.27 | 5460 | 2884.6 | 2784.7 | 4128.6 | 1192.5 | 0.68312 | 6.012
2024-12-09 | 16:04 | Data | 0 | 32.312 | 30.536 | 184.73 | 7.64 | 173.476 | 2119.49 | 26.07 | 46.45 | 6.37 | 1.345 | 4.635 | 8404.56 | 1.87 | 97.8 | 77.5 | 1378 | 23.22 | 5463 | 2878.3 | 2785.7 | 4127.5 | 1192.5 | 0.68057 | 5.979
2024-12-09 | 16:04 | Data | 0 | 32.609 | 31.036 | 184.639 | 7.64 | 173.476 | 2120.39 | 26.06 | 46.54 | 6.37 | 1.346 | 4.647 | 8400.04 | 1.917 | 97.8 | 77.5 | 1378 | 23.27 | 5460 | 2881.1 | 2775.4 | 4118.9 | 1192.5 | 0.68284 | 5.992
2024-12-09 | 16:04 | Data | 0 | 32.339 | 30.725 | 184.82 | 7.64 | 173.476 | 2119.49 | 26.07 | 46.45 | 6.37 | 1.342 | 4.607 | 8418.13 | 1.904 | 97.8 | 77.4 | 1378 | 23.22 | 5471.8 | 2875.2 | 2769.7 | 4114.2 | 1192.5 | 0.68351 | 5.95
2024-12-09 | 16:04 | Data | 0 | 32.305 | 30.59 | 184.594 | 7.64 | 173.521 | 2119.49 | 26.06 | 46.54 | 6.37 | 1.338 | 4.647 | 8418.13 | 1.965 | 97.8 | 77.6 | 1377 | 23.18 | 5471.8 | 2902.4 | 2770.1 | 4126.6 | 1192.5 | 0.68712 | 5.986
2024-12-09 | 16:04 | Data | 0 | 32.94 | 30.88 | 184.865 | 7.64 | 173.566 | 2114.97 | 26.07 | 46.45 | 6.37 | 1.338 | 4.651 | 8427.17 | 2.073 | 97.8 | 77.7 | 1376 | 23.22 | 5477.7 | 2891.3 | 2770.9 | 4124.9 | 1192.5 | 0.68396 | 5.989
2024-12-09 | 16:04 | Data | 0 | 32.615 | 30.475 | 184.865 | 7.64 | 173.611 | 2117.68 | 26.06 | 46.45 | 6.37 | 1.347 | 4.67 | 8418.13 | 1.971 | 97.8 | 77.6 | 1377 | 23.22 | 5471.8 | 2879.7 | 2766.6 | 4112.6 | 1192.5 | 0.68422 | 6.016
2024-12-09 | 16:04 | Data | 0 | 32.528 | 30.536 | 184.594 | 7.64 | 173.521 | 2123.1 | 26.06 | 46.54 | 6.37 | 1.342 | 4.638 | 8386.47 | 2.079 | 97.8 | 77.6 | 1379 | 23.27 | 5451.2 | 2892.3 | 2789.2 | 4133.6 | 1192.5 | 0.68244 | 5.98
2024-12-09 | 16:05 | Data | 0 | 32.865 | 30.874 | 184.865 | 7.64 | 173.611 | 2117.68 | 26.06 | 46.63 | 6.37 | 1.341 | 4.642 | 8395.51 | 2.1 | 97.8 | 77.6 | 1376 | 23.27 | 5457.1 | 2895.7 | 2783.4 | 4130.1 | 1192.5 | 0.68383 | 5.981
2024-12-09 | 16:05 | Data | 0 | 32.811 | 30.961 | 184.82 | 7.64 | 173.521 | 2123.1 | 26.07 | 46.45 | 6.37 | 1.337 | 4.638 | 8377.43 | 2.066 | 97.8 | 77.6 | 1380 | 23.27 | 5445.3 | 2896.5 | 2793.2 | 4148.3 | 1192.5 | 0.68281 | 5.974
2024-12-09 | 16:05 | Data | 0 | 32.48 | 30.59 | 184.594 | 7.64 | 173.431 | 2122.2 | 26.06 | 46.54 | 6.37 | 1.335 | 4.65 | 8377.43 | 2.248 | 97.8 | 77.7 | 1379 | 23.27 | 5445.3 | 2889.2 | 2770.8 | 4121 | 1192.5 | 0.68474 | 5.984
2024-12-09 | 16:05 | Data | 0 | 32.44 | 30.644 | 184.73 | 7.64 | 173.476 | 2123.1 | 26.06 | 46.54 | 6.37 | 1.34 | 4.645 | 8381.95 | 2.133 | 97.8 | 77.6 | 1380 | 23.22 | 5448.3 | 2882.1 | 2784.2 | 4124.8 | 1192.5 | 0.68316 | 5.987
2024-12-09 | 16:05 | Data | 0 | 32.764 | 30.651 | 184.82 | 7.64 | 173.521 | 2122.2 | 26.07 | 46.45 | 6.36 | 1.343 | 4.641 | 8386.47 | 2.066 | 97.8 | 77.6 | 1379 | 23.22 | 5451.2 | 2885.4 | 2788.4 | 4131.4 | 1192.5 | 0.68239 | 5.985
2024-12-09 | 16:05 | Data | 0 | 32.494 | 30.421 | 184.639 | 7.64 | 173.431 | 2125.81 | 26.06 | 46.721 | 6.37 | 1.336 | 4.666 | 8400.04 | 2.066 | 97.8 | 77.7 | 1382 | 23.41 | 5460 | 2882.6 | 2784.3 | 4127.5 | 1192.5 | 0.68238 | 6.002
2024-12-09 | 16:05 | Data | 0 | 32.838 | 30.435 | 184.775 | 7.64 | 173.566 | 2124.91 | 26.06 | 46.721 | 6.36 | 1.33 | 4.645 | 8386.47 | 2.1 | 97.8 | 77.7 | 1382 | 23.36 | 5451.2 | 2875.1 | 2775.5 | 4114.5 | 1192.5 | 0.68184 | 5.975
2024-12-09 | 16:05 | Data | 0 | 32.723 | 30.678 | 184.865 | 7.64 | 173.521 | 2124.91 | 26.06 | 46.811 | 6.37 | 1.337 | 4.635 | 8395.51 | 2.059 | 97.8 | 77.6 | 1382 | 23.41 | 5457.1 | 2881.8 | 2787.8 | 4129.3 | 1192.5 | 0.68095 | 5.969
2024-12-09 | 16:05 | Data | 0 | 32.521 | 30.739 | 184.82 | 7.64 | 173.476 | 2116.78 | 26.07 | 46.721 | 6.37 | 1.337 | 4.648 | 8395.51 | 1.904 | 97.8 | 77.7 | 1376 | 23.36 | 5457.1 | 2892.5 | 2780.4 | 4130 | 1192.5 | 0.68439 | 5.986
2024-12-09 | 16:05 | Data | 0 | 32.379 | 30.806 | 184.639 | 7.64 | 173.431 | 2121.29 | 26.05 | 46.811 | 6.36 | 1.338 | 4.641 | 8381.95 | 1.965 | 97.8 | 77.6 | 1378 | 23.36 | 5448.3 | 2882.3 | 2787.6 | 4126.9 | 1192.5 | 0.67981 | 5.978
2024-12-09 | 16:05 | Data | 0 | 32.521 | 30.428 | 184.549 | 7.64 | 173.431 | 2125.81 | 26.06 | 46.721 | 6.37 | 1.329 | 4.645 | 8386.47 | 1.89 | 97.8 | 77.7 | 1381 | 23.41 | 5451.2 | 2876.4 | 2793.6 | 4127.4 | 1192.5 | 0.68068 | 5.974
2024-12-09 | 16:05 | Data | 0 | 32.609 | 30.442 | 184.594 | 7.64 | 173.385 | 2125.81 | 26.07 | 46.721 | 6.37 | 1.33 | 4.654 | 8390.99 | 2.019 | 97.8 | 77.8 | 1382 | 23.36 | 5454.1 | 2885.9 | 2778.6 | 4123.4 | 1192.5 | 0.68259 | 5.984
2024-12-09 | 16:05 | Data | 0 | 32.717 | 30.651 | 184.639 | 7.64 | 173.476 | 2125.81 | 26.06 | 46.811 | 6.37 | 1.335 | 4.654 | 8386.47 | 2.073 | 97.8 | 77.7 | 1381 | 23.41 | 5451.2 | 2873.7 | 2775.8 | 4125.5 | 1192.5 | 0.68184 | 5.988
2024-12-09 | 16:05 | Data | 0 | 32.919 | 30.448 | 184.639 | 7.64 | 173.476 | 2125.81 | 26.06 | 46.721 | 6.36 | 1.337 | 4.651 | 8372.9 | 2.079 | 97.8 | 77.7 | 1382 | 23.5 | 5442.4 | 2903.8 | 2766.7 | 4129.1 | 1192.5 | 0.68704 | 5.988
2024-12-09 | 16:05 | Data | 0 | 32.447 | 30.644 | 184.775 | 7.64 | 173.476 | 2123.1 | 26.06 | 46.721 | 6.37 | 1.328 | 4.654 | 8386.47 | 1.998 | 97.8 | 77.8 | 1379 | 23.41 | 5451.2 | 2883.4 | 2798.7 | 4138.3 | 1192.5 | 0.6811 | 5.982
2024-12-09 | 16:05 | Data | 0 | 32.602 | 30.847 | 184.775 | 7.64 | 173.476 | 2123.1 | 26.07 | 46.811 | 6.37 | 1.339 | 4.659 | 8390.99 | 2.025 | 97.8 | 77.7 | 1381 | 23.41 | 5454.1 | 2880.4 | 2782.5 | 4128.5 | 1192.5 | 0.67995 | 5.997
2024-12-09 | 16:05 | Data | 0 | 32.73 | 30.658 | 184.73 | 7.64 | 173.566 | 2123.1 | 26.05 | 46.811 | 6.37 | 1.341 | 4.666 | 8381.95 | 2.059 | 97.8 | 77.7 | 1380 | 23.41 | 5448.3 | 2876.9 | 2780.6 | 4123 | 1192.5 | 0.68115 | 6.007
2024-12-09 | 16:05 | Data | 0 | 32.271 | 30.637 | 184.73 | 7.64 | 173.476 | 2120.39 | 26.06 | 46.721 | 6.37 | 1.345 | 4.665 | 8400.04 | 2.012 | 97.8 | 77.6 | 1378 | 23.36 | 5460 | 2875.8 | 2798 | 4131.5 | 1192.6 | 0.68049 | 6.01
2024-12-09 | 16:06 | Data | 0 | 32.494 | 30.82 | 184.775 | 7.64 | 173.476 | 2114.06 | 26.07 | 46.721 | 6.37 | 1.343 | 4.659 | 8418.13 | 1.938 | 97.8 | 77.6 | 1375 | 23.36 | 5471.8 | 2867.6 | 2786.9 | 4114.7 | 1192.6 | 0.68108 | 6.003
2024-12-09 | 16:06 | Data | 0 | 32.723 | 30.536 | 184.639 | 7.64 | 173.521 | 2119.49 | 26.06 | 46.721 | 6.36 | 1.343 | 4.673 | 8395.51 | 1.985 | 97.8 | 77.7 | 1378 | 23.41 | 5457.1 | 2877.7 | 2782.1 | 4121.2 | 1192.6 | 0.68097 | 6.017
2024-12-09 | 16:06 | Data | 0 | 32.494 | 30.651 | 184.639 | 7.64 | 173.476 | 2117.68 | 26.07 | 46.63 | 6.36 | 1.342 | 4.641 | 8390.99 | 1.965 | 97.8 | 77.6 | 1376 | 23.41 | 5454.1 | 2879.8 | 2790.7 | 4128.8 | 1192.6 | 0.68089 | 5.985
2024-12-09 | 16:06 | Data | 0 | 32.501 | 30.631 | 184.73 | 7.64 | 173.431 | 2117.68 | 26.05 | 46.811 | 6.36 | 1.345 | 4.634 | 8395.51 | 1.931 | 97.8 | 77.5 | 1377 | 23.41 | 5457.1 | 2870.9 | 2774.6 | 4113.4 | 1192.6 | 0.68097 | 5.979
2024-12-09 | 16:06 | Data | 0 | 32.723 | 30.651 | 184.594 | 7.64 | 173.476 | 2116.78 | 26.06 | 46.721 | 6.37 | 1.337 | 4.658 | 8400.04 | 2.073 | 97.8 | 77.7 | 1376 | 23.41 | 5460 | 2882.7 | 2777.6 | 4124.5 | 1192.6 | 0.68202 | 5.995
2024-12-09 | 16:06 | Data | 0 | 32.669 | 30.435 | 184.775 | 7.64 | 173.566 | 2118.58 | 26.07 | 46.811 | 6.37 | 1.347 | 4.655 | 8404.56 | 2.086 | 97.8 | 77.6 | 1376 | 23.32 | 5463 | 2884.4 | 2770.4 | 4112.3 | 1192.6 | 0.68442 | 6.001
2024-12-09 | 16:06 | Data | 0 | 32.507 | 30.475 | 184.639 | 7.64 | 173.476 | 2119.49 | 26.07 | 46.811 | 6.37 | 1.338 | 4.657 | 8390.99 | 1.85 | 97.8 | 77.7 | 1377 | 23.36 | 5454.1 | 2852.6 | 2765.4 | 4094.7 | 1192.6 | 0.68213 | 5.995
2024-12-09 | 16:06 | Data | 0 | 32.636 | 30.82 | 184.82 | 7.64 | 173.521 | 2121.29 | 26.06 | 46.721 | 6.36 | 1.336 | 4.655 | 8386.47 | 1.89 | 97.8 | 77.7 | 1378 | 23.36 | 5451.2 | 2879.9 | 2799 | 4134.9 | 1192.6 | 0.68067 | 5.991
2024-12-09 | 16:06 | Data | 0 | 32.777 | 30.435 | 184.73 | 7.64 | 173.566 | 2122.2 | 26.05 | 46.54 | 6.37 | 1.339 | 4.654 | 8381.95 | 2.079 | 97.8 | 77.7 | 1379 | 23.27 | 5448.3 | 2880.1 | 2786.7 | 4126.7 | 1192.6 | 0.68192 | 5.994
2024-12-09 | 16:06 | Data | 0 | 32.94 | 30.658 | 184.82 | 7.64 | 173.566 | 2117.68 | 26.07 | 46.45 | 6.36 | 1.342 | 4.664 | 8377.43 | 2.167 | 97.8 | 77.7 | 1376 | 23.27 | 5445.3 | 2885.2 | 2787.2 | 4131.3 | 1192.6 | 0.68258 | 6.005
2024-12-09 | 16:06 | Data | 0 | 32.386 | 30.421 | 184.73 | 7.64 | 173.521 | 2117.68 | 26.08 | 46.45 | 6.37 | 1.353 | 4.632 | 8395.51 | 1.87 | 97.8 | 77.4 | 1376 | 23.18 | 5457.1 | 2878.8 | 2781.2 | 4117.4 | 1192.6 | 0.68202 | 5.984
2024-12-09 | 16:06 | Data | 0 | 32.723 | 30.658 | 184.865 | 7.64 | 173.521 | 2114.06 | 26.06 | 46.45 | 6.37 | 1.342 | 4.607 | 8386.47 | 2.059 | 97.8 | 77.4 | 1374 | 23.22 | 5451.2 | 2876.2 | 2787.1 | 4129.4 | 1192.6 | 0.67988 | 5.949
2024-12-09 | 16:06 | Data | 0 | 32.649 | 30.651 | 185.091 | 7.64 | 173.747 | 2117.68 | 26.07 | 46.179 | 6.37 | 1.343 | 4.614 | 8386.47 | 2.066 | 97.8 | 77.4 | 1376 | 23.04 | 5451.2 | 2887.7 | 2759.3 | 4114.1 | 1192.6 | 0.68327 | 5.958
2024-12-09 | 16:06 | Data | 0 | 32.879 | 30.597 | 185.091 | 7.64 | 173.928 | 2119.49 | 26.05 | 46.54 | 6.36 | 1.342 | 4.629 | 8418.13 | 2.073 | 97.8 | 77.5 | 1378 | 23.27 | 5471.8 | 2866.4 | 2764 | 4102.3 | 1192.6 | 0.68305 | 5.972
2024-12-09 | 16:06 | Data | 0 | 32.811 | 30.705 | 185.182 | 7.64 | 173.792 | 2121.29 | 26.07 | 46.54 | 6.37 | 1.344 | 4.616 | 8427.17 | 2.019 | 97.8 | 77.4 | 1378 | 23.32 | 5477.7 | 2886.4 | 2766.6 | 4115.3 | 1192.6 | 0.68503 | 5.96
2024-12-09 | 16:06 | Data | 0 | 32.946 | 30.766 | 185.182 | 7.64 | 173.928 | 2121.29 | 26.06 | 46.45 | 6.37 | 1.34 | 4.676 | 8431.69 | 1.897 | 97.8 | 77.7 | 1379 | 23.22 | 5480.6 | 2888.7 | 2788.3 | 4133.3 | 1192.6 | 0.68246 | 6.017
2024-12-09 | 16:06 | Data | 0 | 32.71 | 30.84 | 185.182 | 7.64 | 173.792 | 2120.39 | 26.06 | 46.54 | 6.36 | 1.337 | 4.654 | 8431.69 | 1.924 | 97.8 | 77.7 | 1378 | 23.27 | 5480.6 | 2886 | 2767 | 4118.8 | 1192.6 | 0.68265 | 5.991
2024-12-09 | 16:06 | Data | 0 | 32.609 | 30.651 | 185.091 | 7.64 | 173.837 | 2123.1 | 26.07 | 46.179 | 6.36 | 1.343 | 4.674 | 8427.17 | 2.046 | 97.8 | 77.7 | 1380 | 23.13 | 5477.7 | 2866.6 | 2774.9 | 4105.9 | 1192.6 | 0.68115 | 6.017
2024-12-09 | 16:07 | Data | 0 | 32.521 | 30.644 | 185.001 | 7.64 | 173.747 | 2117.68 | 26.06 | 46.45 | 6.37 | 1.345 | 4.662 | 8400.04 | 1.897 | 97.8 | 77.6 | 1376 | 23.22 | 5460 | 2868.6 | 2779.1 | 4116.2 | 1192.6 | 0.68047 | 6.007
2024-12-09 | 16:07 | Data | 0 | 32.777 | 30.658 | 185.182 | 7.64 | 173.792 | 2123.1 | 26.07 | 46.359 | 6.36 | 1.334 | 4.649 | 8409.08 | 2.073 | 97.8 | 77.7 | 1380 | 23.22 | 5465.9 | 2878.6 | 2786 | 4125.9 | 1192.6 | 0.68146 | 5.982
2024-12-09 | 16:07 | Data | 0 | 32.602 | 30.685 | 185.046 | 7.64 | 173.837 | 2122.2 | 26.05 | 46.63 | 6.37 | 1.338 | 4.663 | 8395.51 | 2.073 | 97.8 | 77.7 | 1380 | 23.27 | 5457.1 | 2884.2 | 2763 | 4113.8 | 1192.6 | 0.68326 | 6
2024-12-09 | 16:07 | Data | 0 | 32.521 | 30.644 | 185.091 | 7.64 | 173.837 | 2122.2 | 26.05 | 46.54 | 6.37 | 1.339 | 4.654 | 8404.56 | 1.863 | 97.8 | 77.6 | 1379 | 23.32 | 5463 | 2882.1 | 2774 | 4123.2 | 1192.6 | 0.68235 | 5.997
2024-12-09 | 16:07 | Data | 0 | 32.636 | 30.651 | 185.091 | 7.64 | 173.928 | 2118.58 | 26.05 | 46.45 | 6.36 | 1.341 | 4.667 | 8404.56 | 1.87 | 97.8 | 77.7 | 1377 | 23.22 | 5463 | 2863.9 | 2756.8 | 4093.9 | 1192.6 | 0.68381 | 6.007
2024-12-09 | 16:07 | Data | 0 | 32.953 | 30.705 | 185.046 | 7.63 | 173.837 | 2122.2 | 26.07 | 46.54 | 6.37 | 1.349 | 4.654 | 8418.13 | 2.012 | 97.8 | 77.5 | 1379 | 23.27 | 5471.8 | 2876.7 | 2779.4 | 4117.9 | 1192.6 | 0.68458 | 6.004
2024-12-09 | 16:07 | Data | 0 | 32.946 | 30.658 | 185.182 | 7.64 | 173.973 | 2123.1 | 26.05 | 46.359 | 6.37 | 1.349 | 4.653 | 8418.13 | 2.174 | 97.8 | 77.5 | 1380 | 23.22 | 5471.8 | 2879.4 | 2773.6 | 4121.8 | 1192.6 | 0.68383 | 6.002
2024-12-09 | 16:07 | Data | 0 | 32.946 | 30.489 | 185.137 | 7.64 | 173.928 | 2122.2 | 26.05 | 46.54 | 6.36 | 1.343 | 4.649 | 8409.08 | 2.093 | 97.8 | 77.6 | 1379 | 23.27 | 5465.9 | 2882.9 | 2780.9 | 4121.3 | 1192.6 | 0.68429 | 5.992
2024-12-09 | 16:07 | Data | 0 | 32.71 | 30.766 | 185.091 | 7.64 | 173.928 | 2123.1 | 26.06 | 46.45 | 6.36 | 1.329 | 4.656 | 8445.26 | 2.073 | 97.8 | 77.8 | 1381 | 23.27 | 5489.4 | 2886.1 | 2764.8 | 4114.1 | 1192.6 | 0.68489 | 5.988
2024-12-09 | 16:07 | Data | 0 | 32.534 | 30.415 | 185.001 | 7.64 | 173.837 | 2123.1 | 26.07 | 46.63 | 6.36 | 1.329 | 4.684 | 8440.74 | 1.877 | 97.8 | 77.9 | 1381 | 23.22 | 5486.5 | 2880.1 | 2788.3 | 4123.9 | 1192.6 | 0.68347 | 6.012
2024-12-09 | 16:07 | Data | 0 | 32.636 | 30.651 | 185.046 | 7.64 | 173.837 | 2121.29 | 26.05 | 46.54 | 6.36 | 1.346 | 4.681 | 8454.3 | 1.911 | 97.8 | 77.7 | 1379 | 23.22 | 5495.3 | 2872.3 | 2757.4 | 4098.9 | 1192.6 | 0.68452 | 6.027
2024-12-09 | 16:07 | Data | 0 | 32.946 | 30.772 | 185.137 | 7.64 | 173.973 | 2125.81 | 26.05 | 46.45 | 6.37 | 1.339 | 4.675 | 8445.26 | 1.884 | 97.8 | 77.7 | 1382 | 23.22 | 5489.4 | 2874.5 | 2740.4 | 4094.1 | 1192.6 | 0.68569 | 6.014
2024-12-09 | 16:07 | Data | 0 | 32.582 | 30.651 | 185.137 | 7.64 | 173.837 | 2123.1 | 26.06 | 46.45 | 6.35 | 1.342 | 4.67 | 8463.35 | 2.052 | 97.8 | 77.7 | 1380 | 23.22 | 5501.2 | 2877.8 | 2744.5 | 4094 | 1192.6 | 0.6875 | 6.012
2024-12-09 | 16:07 | Data | 0 | 32.609 | 30.637 | 185.091 | 7.64 | 173.837 | 2124.01 | 26.05 | 46.54 | 6.37 | 1.34 | 4.659 | 8454.3 | 2.073 | 97.8 | 77.6 | 1379 | 23.27 | 5495.3 | 2878.7 | 2754 | 4100.2 | 1192.6 | 0.68617 | 6
2024-12-09 | 16:07 | Data | 0 | 32.264 | 30.415 | 184.956 | 7.64 | 173.747 | 2123.1 | 26.05 | 46.45 | 6.37 | 1.342 | 4.664 | 8481.44 | 2.106 | 97.8 | 77.7 | 1380 | 23.22 | 5512.9 | 2844.3 | 2743.7 | 4077.2 | 1192.6 | 0.68213 | 6.006
2024-12-09 | 16:07 | Data | 0 | 32.94 | 30.766 | 185.318 | 7.64 | 174.018 | 2122.2 | 26.06 | 46.54 | 6.36 | 1.336 | 4.665 | 8458.83 | 2.073 | 97.8 | 77.7 | 1379 | 23.27 | 5498.2 | 2880.2 | 2742.1 | 4094.4 | 1192.6 | 0.68807 | 6.002
2024-12-09 | 16:07 | Data | 0 | 32.507 | 30.637 | 185.091 | 7.64 | 173.792 | 2120.39 | 26.05 | 46.45 | 6.36 | 1.34 | 4.658 | 8883.91 | 1.863 | 97.8 | 77.7 | 1378 | 23.22 | 5774.5 | 2875.7 | 2765.4 | 4106.9 | 1192.6 | 0.68515 | 5.998
2024-12-09 | 16:08 | Data | 0 | 32.345 | 30.597 | 185.091 | 7.64 | 173.928 | 2118.58 | 26.07 | 46.45 | 6.37 | 1.342 | 4.653 | 8431.69 | 1.884 | 97.8 | 77.6 | 1377 | 23.27 | 5480.6 | 2871.7 | 2765.5 | 4106.2 | 1192.6 | 0.68366 | 5.995
2024-12-09 | 16:08 | Data | 0 | 32.838 | 30.907 | 185.182 | 7.64 | 173.973 | 2127.62 | 26.05 | 46.54 | 6.37 | 1.344 | 4.67 | 8445.26 | 1.911 | 97.8 | 77.7 | 1383 | 23.27 | 5489.4 | 2894 | 2751.6 | 4114.5 | 1192.7 | 0.68733 | 6.014
2024-12-09 | 16:08 | Data | 0 | 32.514 | 30.597 | 185.091 | 7.64 | 173.837 | 2123.1 | 26.03 | 46.54 | 6.37 | 1.353 | 4.646 | 8431.69 | 2.079 | 97.8 | 77.5 | 1379 | 23.22 | 5480.6 | 2881.9 | 2761 | 4108.6 | 1192.7 | 0.68497 | 5.999
2024-12-09 | 16:08 | Data | 0 | 32.528 | 30.536 | 185.091 | 7.64 | 173.837 | 2124.01 | 26.06 | 46.54 | 6.36 | 1.352 | 4.642 | 8418.13 | 1.836 | 97.8 | 77.4 | 1381 | 23.22 | 5471.8 | 2875.3 | 2774.6 | 4116.1 | 1192.7 | 0.6836 | 5.994
2024-12-09 | 16:08 | Data | 0 | 32.737 | 30.651 | 185.227 | 7.64 | 173.973 | 2119.49 | 26.05 | 46.54 | 6.36 | 1.351 | 4.625 | 8431.69 | 1.897 | 97.8 | 77.4 | 1378 | 23.27 | 5480.6 | 2878 | 2759.8 | 4101.9 | 1192.7 | 0.68623 | 5.977
2024-12-09 | 16:08 | Data | 0 | 32.723 | 30.678 | 185.091 | 7.64 | 173.973 | 2120.39 | 26.03 | 46.45 | 6.36 | 1.33 | 4.656 | 8418.13 | 2.046 | 97.8 | 77.8 | 1378 | 23.27 | 5471.8 | 2872.4 | 2765.4 | 4105.7 | 1192.7 | 0.68312 | 5.986
2024-12-09 | 16:08 | Data | 0 | 32.696 | 30.637 | 185.091 | 7.64 | 173.837 | 2120.39 | 26.03 | 46.54 | 6.36 | 1.342 | 4.665 | 8409.08 | 2.106 | 97.8 | 77.6 | 1378 | 23.22 | 5465.9 | 2891.4 | 2764.6 | 4118.9 | 1192.7 | 0.68423 | 6.008
2024-12-09 | 16:08 | Data | 0 | 32.494 | 30.536 | 184.956 | 7.64 | 173.747 | 2118.58 | 26.03 | 46.45 | 6.36 | 1.348 | 4.673 | 8445.26 | 2.079 | 97.8 | 77.6 | 1378 | 23.22 | 5489.4 | 2881.1 | 2729.8 | 4082.2 | 1192.7 | 0.69027 | 6.022
2024-12-09 | 16:08 | Data | 0 | 32.609 | 30.442 | 185.182 | 7.64 | 173.928 | 2124.01 | 26.05 | 46.45 | 6.37 | 1.34 | 4.662 | 8445.26 | 2.032 | 97.8 | 77.7 | 1381 | 23.22 | 5489.4 | 2892.4 | 2766.1 | 4121 | 1192.7 | 0.68666 | 6.003
2024-12-09 | 16:08 | Data | 0 | 32.42 | 30.421 | 185.001 | 7.64 | 173.792 | 2119.49 | 26.05 | 46.45 | 6.36 | 1.339 | 4.679 | 8445.26 | 2.059 | 97.8 | 77.7 | 1378 | 23.22 | 5489.4 | 2861.7 | 2757.5 | 4093.6 | 1192.7 | 0.68231 | 6.018
2024-12-09 | 16:08 | Data | 0 | 32.717 | 30.428 | 184.956 | 7.64 | 173.837 | 2114.06 | 26.02 | 46.54 | 6.36 | 1.347 | 4.641 | 8454.3 | 2.073 | 97.8 | 77.5 | 1374 | 23.27 | 5495.3 | 2877.3 | 2748.6 | 4102.7 | 1192.7 | 0.68481 | 5.988
2024-12-09 | 16:08 | Data | 0 | 32.501 | 30.651 | 185.091 | 7.64 | 173.792 | 2117.68 | 26.05 | 46.45 | 6.36 | 1.353 | 4.655 | 8458.83 | 2.046 | 97.8 | 77.5 | 1377 | 23.27 | 5498.2 | 2865.2 | 2752.7 | 4093.1 | 1192.7 | 0.68463 | 6.007
2024-12-09 | 16:08 | Data | 0 | 32.717 | 30.475 | 185.046 | 7.64 | 173.837 | 2118.58 | 26.02 | 46.54 | 6.36 | 1.341 | 4.667 | 8458.83 | 2.046 | 97.8 | 77.7 | 1376 | 23.22 | 5498.2 | 2887.7 | 2759.2 | 4108.1 | 1192.7 | 0.68697 | 6.008
2024-12-09 | 16:08 | Data | 0 | 32.946 | 30.664 | 185.001 | 7.64 | 173.928 | 2116.78 | 26.06 | 46.45 | 6.36 | 1.329 | 4.65 | 8440.74 | 2.086 | 97.8 | 77.8 | 1376 | 23.22 | 5486.5 | 2885.2 | 2745 | 4102.1 | 1192.7 | 0.68777 | 5.979
2024-12-09 | 16:08 | Data | 0 | 32.926 | 30.705 | 185.091 | 7.64 | 173.928 | 2120.39 | 26.05 | 46.54 | 6.36 | 1.341 | 4.659 | 8440.74 | 2.127 | 97.8 | 77.6 | 1378 | 23.27 | 5486.5 | 2880.7 | 2746.9 | 4087.9 | 1192.7 | 0.68709 | 6.001
2024-12-09 | 16:08 | Data | 0 | 32.723 | 30.651 | 185.046 | 7.64 | 173.747 | 2122.2 | 26.03 | 46.54 | 6.37 | 1.341 | 4.651 | 8431.69 | 1.958 | 97.8 | 77.6 | 1380 | 23.22 | 5480.6 | 2878.2 | 2735.2 | 4087.9 | 1192.7 | 0.68661 | 5.992
2024-12-09 | 16:08 | Data | 0 | 32.501 | 30.907 | 185.091 | 7.64 | 173.973 | 2120.39 | 26.02 | 46.089 | 6.37 | 1.341 | 4.651 | 8436.21 | 1.965 | 97.8 | 77.6 | 1379 | 23 | 5483.5 | 2891.2 | 2757.1 | 4103.9 | 1192.7 | 0.68716 | 5.992
2024-12-09 | 16:08 | Data | 0 | 32.946 | 30.651 | 185.091 | 7.64 | 173.928 | 2120.39 | 26.05 | 46.54 | 6.36 | 1.346 | 4.657 | 8445.26 | 2.12 | 97.8 | 77.6 | 1378 | 23.27 | 5489.4 | 2884.3 | 2777.2 | 4122.5 | 1192.7 | 0.68268 | 6.003
2024-12-09 | 16:08 | Data | 0 | 32.723 | 30.826 | 185.227 | 7.64 | 173.973 | 2120.39 | 26.03 | 46.269 | 6.36 | 1.346 | 4.653 | 8445.26 | 1.958 | 97.8 | 77.6 | 1379 | 23.13 | 5489.4 | 2905.6 | 2777.1 | 4137.4 | 1192.7 | 0.68616 | 5.998
2024-12-09 | 16:09 | Data | 0 | 32.913 | 30.651 | 185.182 | 7.64 | 173.928 | 2119.49 | 26.07 | 46.359 | 6.37 | 1.342 | 4.664 | 8427.17 | 2.127 | 97.8 | 77.6 | 1379 | 23.04 | 5477.7 | 2874.7 | 2767 | 4108.6 | 1192.7 | 0.68442 | 6.007
2024-12-09 | 16:09 | Data | 0 | 32.777 | 30.55 | 185.227 | 7.64 | 173.928 | 2117.68 | 26.03 | 46.269 | 6.36 | 1.342 | 4.663 | 8431.69 | 1.944 | 97.8 | 77.6 | 1376 | 23.13 | 5480.6 | 2878.8 | 2729 | 4081.7 | 1192.7 | 0.68855 | 6.005
2024-12-09 | 16:09 | Data | 0 | 32.71 | 30.658 | 185.046 | 7.64 | 173.973 | 2117.68 | 26.03 | 46.179 | 6.36 | 1.339 | 4.638 | 8449.78 | 2.059 | 97.8 | 77.6 | 1376 | 23.09 | 5492.4 | 2875.6 | 2737.4 | 4090.3 | 1192.7 | 0.68824 | 5.977
2024-12-09 | 16:09 | Data | 0 | 32.933 | 30.651 | 185.091 | 7.64 | 173.973 | 2117.68 | 26.02 | 46.54 | 6.37 | 1.347 | 4.679 | 8427.17 | 1.904 | 97.8 | 77.7 | 1376 | 23.27 | 5477.7 | 2888.5 | 2748.8 | 4103.7 | 1192.7 | 0.68981 | 6.026
2024-12-09 | 16:09 | Data | 0 | 32.339 | 30.475 | 185.091 | 7.64 | 173.928 | 2117.68 | 26.05 | 46.179 | 6.36 | 1.348 | 4.673 | 8431.69 | 1.762 | 97.8 | 77.6 | 1376 | 23.04 | 5480.6 | 2892 | 2729.6 | 4093.5 | 1192.7 | 0.69036 | 6.024
2024-12-09 | 16:09 | Data | 0 | 32.865 | 30.651 | 185.182 | 7.64 | 174.109 | 2116.78 | 26.01 | 46.54 | 6.37 | 1.353 | 4.667 | 8445.26 | 1.971 | 97.8 | 77.5 | 1376 | 23.32 | 5489.4 | 2870.7 | 2730.4 | 4082.5 | 1192.7 | 0.68886 | 6.019
2024-12-09 | 16:09 | Data | 0 | 32.946 | 30.678 | 185.046 | 7.64 | 173.837 | 2114.06 | 26.03 | 46.54 | 6.36 | 1.342 | 4.656 | 8436.21 | 1.958 | 97.8 | 77.6 | 1374 | 23.22 | 5483.5 | 2872.2 | 2722.8 | 4077.1 | 1192.7 | 0.68936 | 5.998
2024-12-09 | 16:09 | Data | 0 | 32.669 | 30.442 | 185.046 | 7.64 | 173.928 | 2114.06 | 26.03 | 46.179 | 6.36 | 1.34 | 4.674 | 8440.74 | 2.275 | 97.8 | 77.7 | 1374 | 23.04 | 5486.5 | 2895.6 | 2745.1 | 4106 | 1192.7 | 0.69056 | 6.014
2024-12-09 | 16:09 | Data | 0 | 32.723 | 30.651 | 185.001 | 7.64 | 173.837 | 2113.16 | 26.05 | 46.269 | 6.37 | 1.338 | 4.656 | 8454.3 | 2.059 | 97.8 | 77.7 | 1374 | 23.09 | 5495.3 | 2888.8 | 2756.7 | 4111.7 | 1192.7 | 0.68668 | 5.994
2024-12-09 | 16:09 | Data | 0 | 32.892 | 30.59 | 185.137 | 7.64 | 173.973 | 2114.06 | 26.02 | 46.179 | 6.36 | 1.343 | 4.662 | 8454.3 | 2.073 | 97.8 | 77.7 | 1374 | 23.09 | 5495.3 | 2889.9 | 2758 | 4114.1 | 1192.7 | 0.6863 | 6.003
2024-12-09 | 16:09 | Data | 0 | 32.696 | 30.651 | 185.091 | 7.64 | 173.792 | 2114.97 | 26.02 | 46.269 | 6.36 | 1.336 | 4.641 | 8467.87 | 2.066 | 97.8 | 77.6 | 1374 | 23.13 | 5504.1 | 2892.4 | 2740 | 4102.7 | 1192.7 | 0.68591 | 5.977
2024-12-09 | 16:09 | Data | 0 | 32.723 | 30.752 | 185.182 | 7.64 | 173.973 | 2114.06 | 26.02 | 46.45 | 6.36 | 1.338 | 4.666 | 8101.57 | 1.971 | 97.8 | 77.7 | 1375 | 23.22 | 5266 | 2899.8 | 2780.1 | 4135.9 | 1192.7 | 0.68511 | 6.003
2024-12-09 | 16:09 | Data | 0 | 32.528 | 30.651 | 185.227 | 7.64 | 173.973 | 2117.68 | 26.03 | 46.45 | 6.36 | 1.341 | 4.656 | 8083.48 | 2.019 | 97.8 | 77.7 | 1376 | 23.27 | 5254.3 | 2864 | 2760.8 | 4093.6 | 1192.7 | 0.68511 | 5.998
2024-12-09 | 16:09 | Data | 0 | 32.501 | 30.421 | 185.182 | 7.64 | 173.973 | 2118.58 | 26.06 | 46.54 | 6.37 | 1.343 | 4.654 | 8359.34 | 2.181 | 97.8 | 77.6 | 1375 | 23.27 | 5433.6 | 2875 | 2730.6 | 4087 | 1192.7 | 0.68667 | 5.998
2024-12-09 | 16:09 | Data | 0 | 32.447 | 30.442 | 185.182 | 7.64 | 173.837 | 2116.78 | 26.02 | 46.54 | 6.36 | 1.353 | 4.645 | 8409.08 | 2.154 | 97.8 | 77.4 | 1376 | 23.32 | 5465.9 | 2895.3 | 2749.7 | 4110.2 | 1192.7 | 0.68875 | 5.998
2024-12-09 | 16:09 | Data | 0 | 32.507 | 30.421 | 185.227 | 7.64 | 174.063 | 2117.68 | 26.03 | 46.45 | 6.37 | 1.354 | 4.638 | 8418.13 | 2.059 | 97.8 | 77.4 | 1376 | 23.27 | 5471.8 | 2882.4 | 2733.6 | 4091 | 1192.7 | 0.68764 | 5.991
2024-12-09 | 16:09 | Data | 0 | 32.669 | 30.772 | 185.318 | 7.64 | 173.928 | 2111.35 | 26.02 | 46.63 | 6.37 | 1.337 | 4.663 | 8404.56 | 2.187 | 97.8 | 77.7 | 1372 | 23.41 | 5463 | 2870.6 | 2740.7 | 4090.6 | 1192.7 | 0.68707 | 5.998
2024-12-09 | 16:10 | Data | 0 | 32.636 | 30.536 | 185.227 | 7.64 | 173.973 | 2121.29 | 26.05 | 46.45 | 6.37 | 1.339 | 4.673 | 8422.65 | 1.904 | 97.8 | 77.7 | 1378 | 23.27 | 5474.7 | 2889.9 | 2750.8 | 4111.7 | 1192.7 | 0.68754 | 6.011
2024-12-09 | 16:10 | Data | 0 | 33.054 | 30.685 | 185.227 | 7.64 | 174.018 | 2120.39 | 26.03 | 46.54 | 6.35 | 1.341 | 4.649 | 8440.74 | 2.194 | 97.8 | 77.6 | 1378 | 23.27 | 5486.5 | 2871.6 | 2732.5 | 4083.6 | 1192.7 | 0.68769 | 5.991
2024-12-09 | 16:10 | Data | 0 | 32.71 | 30.651 | 185.046 | 7.64 | 173.928 | 2120.39 | 26.01 | 46.54 | 6.36 | 1.339 | 4.626 | 8449.78 | 1.965 | 97.8 | 77.5 | 1379 | 23.27 | 5492.4 | 2871 | 2717.3 | 4071.3 | 1192.8 | 0.68867 | 5.966
2024-12-09 | 16:10 | Data | 0 | 33.108 | 30.685 | 185.182 | 7.64 | 174.018 | 2121.29 | 26.05 | 46.721 | 6.37 | 1.34 | 4.656 | 8445.26 | 2.052 | 97.8 | 77.6 | 1379 | 23.27 | 5489.4 | 2874.2 | 2736.8 | 4091.5 | 1192.8 | 0.68657 | 5.998
2024-12-09 | 16:10 | Data | 0 | 32.811 | 30.874 | 185.227 | 7.64 | 173.928 | 2125.81 | 26.03 | 46.54 | 6.36 | 1.346 | 4.655 | 8436.21 | 2.241 | 97.8 | 77.6 | 1381 | 23.27 | 5483.5 | 2881.6 | 2740.4 | 4091.4 | 1192.8 | 0.68897 | 6.001
2024-12-09 | 16:10 | Data | 0 | 32.94 | 30.651 | 185.182 | 7.64 | 173.928 | 2124.01 | 26.02 | 46.45 | 6.37 | 1.343 | 4.643 | 8458.83 | 1.978 | 97.8 | 77.6 | 1382 | 23.27 | 5498.2 | 2882.3 | 2743.4 | 4096.7 | 1192.8 | 0.68732 | 5.985
2024-12-09 | 16:10 | Data | 0 | 32.48 | 30.624 | 185.137 | 7.64 | 173.747 | 2125.81 | 26.03 | 46.45 | 6.36 | 1.338 | 4.665 | 8454.3 | 2.012 | 97.8 | 77.7 | 1382 | 23.32 | 5495.3 | 2876.7 | 2755.8 | 4100.4 | 1192.8 | 0.68653 | 6.002
2024-12-09 | 16:10 | Data | 0 | 33.007 | 30.786 | 185.318 | 7.64 | 174.018 | 2128.52 | 26.02 | 46.54 | 6.37 | 1.336 | 4.672 | 8449.78 | 2.255 | 97.8 | 77.8 | 1384 | 23.32 | 5492.4 | 2886.3 | 2719.6 | 4083 | 1192.8 | 0.69193 | 6.007
2024-12-09 | 16:10 | Data | 0 | 32.777 | 30.658 | 185.182 | 7.64 | 173.837 | 2128.52 | 26.05 | 46.54 | 6.37 | 1.34 | 4.664 | 8472.39 | 2.073 | 97.8 | 77.7 | 1383 | 23.27 | 5507.1 | 2861.3 | 2735.9 | 4075.9 | 1192.8 | 0.68705 | 6.005
2024-12-09 | 16:10 | Data | 0 | 32.568 | 30.759 | 185.182 | 7.64 | 173.928 | 2127.62 | 26.02 | 46.45 | 6.36 | 1.342 | 4.652 | 8463.35 | 1.742 | 97.8 | 77.6 | 1383 | 23.22 | 5501.2 | 2865.4 | 2748.5 | 4095.2 | 1192.8 | 0.68651 | 5.995
2024-12-09 | 16:10 | Data | 0 | 32.696 | 30.651 | 185.091 | 7.64 | 173.928 | 2124.91 | 26.03 | 46.45 | 6.37 | 1.346 | 4.665 | 8454.3 | 2.066 | 97.8 | 77.6 | 1381 | 23.22 | 5495.3 | 2878.1 | 2726.2 | 4082.5 | 1192.8 | 0.68924 | 6.01
2024-12-09 | 16:10 | Data | 0 | 32.609 | 30.637 | 185.091 | 7.64 | 173.928 | 2124.91 | 26.03 | 46.54 | 6.37 | 1.341 | 4.673 | 8440.74 | 2.073 | 97.8 | 77.7 | 1382 | 23.22 | 5486.5 | 2872.8 | 2724.6 | 4078.7 | 1192.8 | 0.6879 | 6.014
2024-12-09 | 16:10 | Data | 0 | 32.622 | 30.651 | 185.227 | 7.64 | 173.928 | 2124.91 | 26.06 | 46.359 | 6.37 | 1.351 | 4.682 | 8467.87 | 1.965 | 97.8 | 77.6 | 1381 | 23.27 | 5504.1 | 2876.3 | 2726.8 | 4078.9 | 1192.8 | 0.6884 | 6.034
2024-12-09 | 16:10 | Data | 0 | 32.494 | 30.651 | 185.046 | 7.64 | 173.928 | 2122.2 | 26.03 | 46.54 | 6.36 | 1.347 | 4.654 | 8472.39 | 1.843 | 97.8 | 77.6 | 1379 | 23.27 | 5507.1 | 2886.8 | 2735.4 | 4083.9 | 1192.8 | 0.68841 | 6
2024-12-09 | 16:10 | Data | 0 | 32.514 | 30.563 | 185.091 | 7.64 | 173.973 | 2123.1 | 26.03 | 46.54 | 6.36 | 1.339 | 4.643 | 8481.44 | 1.965 | 97.8 | 77.6 | 1380 | 23.27 | 5512.9 | 2879.8 | 2742.3 | 4090.4 | 1192.8 | 0.68668 | 5.983
2024-12-09 | 16:10 | Data | 0 | 32.615 | 30.536 | 185.182 | 7.64 | 173.928 | 2124.01 | 26.02 | 46.54 | 6.36 | 1.336 | 4.673 | 8481.44 | 2.012 | 97.8 | 77.8 | 1379 | 23.22 | 5512.9 | 2881.7 | 2727 | 4087.8 | 1192.8 | 0.6884 | 6.01
2024-12-09 | 16:10 | Data | 0 | 32.528 | 30.766 | 185.227 | 7.64 | 174.018 | 2120.39 | 26.03 | 46.54 | 6.36 | 1.329 | 4.654 | 8499.53 | 1.958 | 97.8 | 77.8 | 1379 | 23.27 | 5524.7 | 2857.7 | 2755.8 | 4093.9 | 1192.8 | 0.68178 | 5.984
2024-12-09 | 16:10 | Data | 0 | 32.555 | 30.975 | 185.227 | 7.64 | 173.837 | 2116.78 | 26.02 | 46.54 | 6.36 | 1.344 | 4.651 | 8481.44 | 2.005 | 97.8 | 77.6 | 1376 | 23.27 | 5512.9 | 2881.9 | 2722.1 | 4081.5 | 1192.8 | 0.68743 | 5.995
2024-12-09 | 16:11 | Data | 0 | 32.717 | 30.651 | 185.091 | 7.64 | 173.928 | 2116.78 | 26.03 | 46.54 | 6.36 | 1.342 | 4.664 | 8513.09 | 2.066 | 97.8 | 77.7 | 1376 | 23.32 | 5533.5 | 2877.5 | 2750.6 | 4103.4 | 1192.8 | 0.6849 | 6.005
2024-12-09 | 16:11 | Data | 0 | 32.777 | 30.664 | 185.137 | 7.64 | 173.928 | 2117.68 | 26.02 | 46.54 | 6.37 | 1.327 | 4.662 | 8513.09 | 2.025 | 97.8 | 77.9 | 1376 | 23.22 | 5533.5 | 2856.3 | 2729 | 4071 | 1192.8 | 0.68389 | 5.988
2024-12-09 | 16:11 | Data | 0 | 32.696 | 30.604 | 185.182 | 7.64 | 173.928 | 2117.68 | 26.05 | 46.54 | 6.36 | 1.325 | 4.637 | 8476.91 | 2.241 | 97.8 | 77.8 | 1375 | 23.27 | 5510 | 2874.2 | 2747.4 | 4094.5 | 1192.8 | 0.68715 | 5.962
2024-12-09 | 16:11 | Data | 0 | 32.629 | 30.651 | 185.182 | 7.64 | 173.837 | 2118.58 | 26.02 | 46.54 | 6.37 | 1.334 | 4.647 | 8481.44 | 1.904 | 97.8 | 77.7 | 1376 | 23.22 | 5512.9 | 2882.7 | 2748.6 | 4102.1 | 1192.8 | 0.68742 | 5.983
2024-12-09 | 16:11 | Data | 0 | 32.723 | 30.691 | 185.137 | 7.64 | 173.973 | 2117.68 | 26.02 | 46.63 | 6.36 | 1.336 | 4.638 | 8476.91 | 2.032 | 97.8 | 77.6 | 1377 | 23.27 | 5510 | 2872.6 | 2740.1 | 4089.1 | 1192.8 | 0.68497 | 5.975
2024-12-09 | 16:11 | Data | 0 | 32.386 | 30.59 | 185.091 | 7.64 | 173.837 | 2121.29 | 26.02 | 46.45 | 6.37 | 1.34 | 4.651 | 8467.87 | 2.059 | 97.8 | 77.6 | 1380 | 23.27 | 5504.1 | 2886.2 | 2733.2 | 4091 | 1192.8 | 0.69019 | 5.992
2024-12-09 | 16:11 | Data | 0 | 32.865 | 30.84 | 185.363 | 7.64 | 174.018 | 2120.39 | 26.02 | 46.45 | 6.36 | 1.334 | 4.639 | 8458.83 | 2.046 | 97.8 | 77.7 | 1378 | 23.18 | 5498.2 | 2873.6 | 2748.7 | 4095 | 1192.8 | 0.6852 | 5.971
2024-12-09 | 16:11 | Data | 0 | 32.723 | 30.651 | 185.046 | 7.64 | 173.973 | 2114.97 | 26.02 | 46.45 | 6.37 | 1.339 | 4.631 | 8458.83 | 2.025 | 97.8 | 77.6 | 1375 | 23.27 | 5498.2 | 2865.9 | 2730.1 | 4080.8 | 1192.8 | 0.68488 | 5.971
2024-12-09 | 16:11 | Data | 0 | 32.71 | 30.651 | 185.182 | 7.64 | 174.018 | 2117.68 | 26.03 | 46.54 | 6.36 | 1.342 | 4.646 | 8458.83 | 2.066 | 97.8 | 77.6 | 1376 | 23.27 | 5498.2 | 2892.4 | 2767 | 4120.2 | 1192.8 | 0.68633 | 5.987
2024-12-09 | 16:11 | Data | 0 | 32.669 | 30.847 | 185.137 | 7.64 | 173.837 | 2114.06 | 26.01 | 46.54 | 6.36 | 1.341 | 4.679 | 8454.3 | 1.985 | 97.8 | 77.7 | 1374 | 23.27 | 5495.3 | 2879.4 | 2774.5 | 4117.2 | 1192.8 | 0.68248 | 6.019
2024-12-09 | 16:11 | Data | 0 | 32.609 | 31.036 | 185.227 | 7.64 | 173.973 | 2113.16 | 26.03 | 46.54 | 6.37 | 1.344 | 4.68 | 8422.65 | 1.863 | 97.8 | 77.7 | 1374 | 23.32 | 5474.7 | 2881 | 2736.1 | 4092.7 | 1192.8 | 0.68612 | 6.025
2024-12-09 | 16:11 | Data | 0 | 32.777 | 30.658 | 185.137 | 7.64 | 174.063 | 2114.06 | 26.02 | 46.54 | 6.37 | 1.344 | 4.648 | 8409.08 | 1.944 | 97.8 | 77.6 | 1374 | 23.22 | 5465.9 | 2877.9 | 2748 | 4102.6 | 1192.8 | 0.68526 | 5.992
2024-12-09 | 16:11 | Data | 0 | 32.555 | 30.536 | 185.137 | 7.64 | 173.928 | 2117.68 | 26.02 | 46.269 | 6.36 | 1.345 | 4.65 | 8431.69 | 1.965 | 97.8 | 77.6 | 1376 | 23.13 | 5480.6 | 2877.6 | 2741.6 | 4089.2 | 1192.8 | 0.68688 | 5.995
2024-12-09 | 16:11 | Data | 0 | 32.514 | 30.597 | 185.408 | 7.64 | 174.018 | 2120.39 | 26.02 | 46.45 | 6.37 | 1.341 | 4.637 | 8431.69 | 1.965 | 97.8 | 77.6 | 1378 | 23.22 | 5480.6 | 2882.6 | 2739.3 | 4091.6 | 1192.8 | 0.68855 | 5.979
2024-12-09 | 16:11 | Data | 0 | 32.501 | 30.651 | 185.137 | 7.64 | 173.928 | 2121.29 | 26.03 | 46.54 | 6.37 | 1.332 | 4.675 | 8472.39 | 1.958 | 97.8 | 77.8 | 1379 | 23.27 | 5507.1 | 2891.2 | 2733.9 | 4096.2 | 1192.8 | 0.68968 | 6.009
2024-12-09 | 16:11 | Data | 0 | 32.703 | 30.759 | 185.227 | 7.64 | 173.837 | 2128.52 | 26.02 | 46.54 | 6.37 | 1.332 | 4.673 | 8467.87 | 1.904 | 97.8 | 77.8 | 1383 | 23.36 | 5504.1 | 2882.2 | 2752.4 | 4100.9 | 1192.8 | 0.68777 | 6.005
2024-12-09 | 16:11 | Data | 0 | 32.723 | 30.651 | 185.182 | 7.64 | 174.018 | 2130.33 | 26.02 | 46.63 | 6.36 | 1.335 | 4.666 | 8454.3 | 2.073 | 97.8 | 77.8 | 1384 | 23.22 | 5495.3 | 2892.5 | 2748.9 | 4107.5 | 1192.8 | 0.68762 | 6.001
2024-12-09 | 16:12 | Data | 0 | 33.054 | 30.793 | 185.227 | 7.64 | 174.018 | 2128.52 | 26.02 | 46.45 | 6.36 | 1.339 | 4.66 | 8440.74 | 2.181 | 97.8 | 77.7 | 1383 | 23.27 | 5486.5 | 2874.8 | 2751.6 | 4094.1 | 1192.8 | 0.68638 | 6.002
2024-12-09 | 16:12 | Data | 0 | 32.71 | 31.103 | 185.227 | 7.64 | 173.973 | 2128.52 | 26.02 | 46.54 | 6.36 | 1.336 | 4.65 | 8440.74 | 2.019 | 97.8 | 77.7 | 1384 | 23.27 | 5486.5 | 2901.6 | 2768.1 | 4126.1 | 1192.8 | 0.68747 | 5.986
2024-12-09 | 16:12 | Data | 0 | 32.71 | 30.55 | 185.091 | 7.64 | 173.928 | 2130.33 | 26.03 | 46.45 | 6.36 | 1.337 | 4.671 | 8458.83 | 1.998 | 97.8 | 77.7 | 1384 | 23.22 | 5498.2 | 2871.4 | 2765.7 | 4105.9 | 1192.8 | 0.6828 | 6.007
2024-12-09 | 16:12 | Data | 0 | 32.892 | 30.664 | 185.227 | 7.64 | 174.018 | 2131.24 | 26.02 | 46.45 | 6.36 | 1.338 | 4.645 | 8467.87 | 2.282 | 97.8 | 77.7 | 1385 | 23.22 | 5504.1 | 2885.2 | 2745.6 | 4099 | 1192.8 | 0.68613 | 5.981
2024-12-09 | 16:12 | Data | 0 | 32.73 | 30.88 | 185.272 | 7.64 | 174.018 | 2131.24 | 26.02 | 46.359 | 6.36 | 1.334 | 4.641 | 8458.83 | 2.019 | 97.8 | 77.7 | 1385 | 23.13 | 5498.2 | 2889.8 | 2752.8 | 4109.3 | 1192.9 | 0.68653 | 5.975
2024-12-09 | 16:12 | Data | 0 | 32.723 | 30.658 | 185.137 | 7.64 | 173.928 | 2131.24 | 26.02 | 46.45 | 6.36 | 1.34 | 4.675 | 8449.78 | 2.066 | 97.8 | 77.7 | 1385 | 23.27 | 5492.4 | 2884.9 | 2759.2 | 4108.4 | 1192.9 | 0.68622 | 6.016
2024-12-09 | 16:12 | Data | 0 | 32.723 | 30.57 | 185.182 | 7.64 | 174.063 | 2133.95 | 26.01 | 46.45 | 6.36 | 1.352 | 4.686 | 8445.26 | 2.241 | 97.8 | 77.6 | 1387 | 23.32 | 5489.4 | 2884.4 | 2771 | 4120.9 | 1192.9 | 0.68386 | 6.036
2024-12-09 | 16:12 | Data | 0 | 32.609 | 30.651 | 185.182 | 7.64 | 174.018 | 2134.85 | 26.02 | 46.45 | 6.36 | 1.344 | 4.639 | 8458.83 | 1.87 | 97.8 | 77.5 | 1388 | 23.27 | 5498.2 | 2897.1 | 2756.4 | 4111.5 | 1192.9 | 0.68701 | 5.985
2024-12-09 | 16:12 | Data | 0 | 32.723 | 30.853 | 185.272 | 7.64 | 174.063 | 2137.56 | 26.03 | 46.359 | 6.36 | 1.343 | 4.646 | 8454.3 | 2.073 | 97.8 | 77.6 | 1389 | 23.18 | 5495.3 | 2879.6 | 2750.7 | 4096.1 | 1192.9 | 0.68732 | 5.988
2024-12-09 | 16:12 | Data | 0 | 32.744 | 30.853 | 185.227 | 7.64 | 174.018 | 2135.76 | 26.02 | 46.45 | 6.36 | 1.336 | 4.68 | 8445.26 | 1.958 | 97.8 | 77.8 | 1388 | 23.22 | 5489.4 | 2869.8 | 2751.5 | 4097.5 | 1192.9 | 0.68439 | 6.015
2024-12-09 | 16:12 | Data | 0 | 32.764 | 30.766 | 185.227 | 7.64 | 174.063 | 2134.85 | 26.02 | 46.54 | 6.37 | 1.337 | 4.669 | 8431.69 | 2.079 | 97.8 | 77.7 | 1388 | 23.18 | 5480.6 | 2882 | 2758.1 | 4106.6 | 1192.9 | 0.68635 | 6.007
2024-12-09 | 16:12 | Data | 0 | 33.378 | 31.015 | 185.318 | 7.64 | 174.063 | 2137.56 | 26.01 | 46.54 | 6.37 | 1.347 | 4.664 | 8431.69 | 2.133 | 97.8 | 77.6 | 1390 | 23.27 | 5480.6 | 2886.2 | 2746.1 | 4099.6 | 1192.9 | 0.68744 | 6.01
2024-12-09 | 16:12 | Data | 0 | 32.501 | 30.82 | 185.182 | 7.64 | 173.973 | 2137.56 | 26.02 | 46.54 | 6.36 | 1.343 | 4.657 | 8440.74 | 1.917 | 97.8 | 77.6 | 1389 | 23.27 | 5486.5 | 2892.5 | 2753.4 | 4114.5 | 1192.9 | 0.68807 | 5.999
2024-12-09 | 16:12 | Data | 0 | 33.115 | 30.988 | 185.408 | 7.64 | 174.109 | 2140.27 | 26.02 | 46.269 | 6.36 | 1.339 | 4.656 | 8463.35 | 1.951 | 97.8 | 77.7 | 1391 | 23.04 | 5501.2 | 2835.7 | 2735.8 | 4062.5 | 1192.9 | 0.683 | 5.997
2024-12-09 | 16:12 | Data | 0 | 32.831 | 30.664 | 185.091 | 7.64 | 173.973 | 2138.47 | 26.02 | 46.269 | 6.37 | 1.348 | 4.639 | 8472.39 | 2.066 | 97.8 | 77.5 | 1391 | 23.13 | 5507.1 | 1785.3 | 2216.5 | 2858.8 | 1192.9 | 0.6218 | 5.988
2024-12-09 | 16:12 | Data | 0 | 32.723 | 30.968 | 185.137 | 7.64 | 173.973 | 2140.27 | 26.02 | 46.179 | 6.36 | 1.346 | 4.646 | 8485.96 | 2.073 | 97.8 | 77.6 | 1391 | 23.04 | 5515.9 | 1810.2 | 2208.1 | 2867.7 | 1192.9 | 0.62913 | 5.992
2024-12-09 | 16:12 | Data | 0 | 32.946 | 30.894 | 185.182 | 7.64 | 174.063 | 2139.37 | 26.01 | 46.179 | 6.36 | 1.343 | 4.656 | 8476.91 | 2.046 | 97.8 | 77.6 | 1391 | 23.13 | 5510 | 1809.1 | 2199.8 | 2859.9 | 1192.9 | 0.62774 | 6.001
2024-12-09 | 16:12 | Data | 0 | 32.723 | 30.664 | 185.182 | 7.64 | 173.928 | 2137.56 | 26.01 | 46.269 | 6.36 | 1.339 | 4.641 | 8440.74 | 2.059 | 97.8 | 77.6 | 1389 | 23.18 | 5486.5 | 1802.8 | 2188.8 | 2847 | 1192.9 | 0.6309 | 5.98
2024-12-09 | 16:13 | Data | 0 | 33.162 | 30.739 | 185.182 | 7.64 | 174.063 | 2136.66 | 26.02 | 46.45 | 6.36 | 1.348 | 4.636 | 8440.74 | 2.187 | 97.8 | 77.5 | 1389 | 23.27 | 5486.5 | 1811.4 | 2202.6 | 2868.2 | 1192.9 | 0.63199 | 5.984
2024-12-09 | 16:13 | Data | 0 | 32.953 | 30.766 | 185.318 | 7.64 | 174.063 | 2133.95 | 26.02 | 46.359 | 6.36 | 1.347 | 4.658 | 8440.74 | 1.958 | 97.8 | 77.6 | 1387 | 23.13 | 5486.5 | 1807.8 | 2199.8 | 2856.7 | 1192.9 | 0.62895 | 6.004
2024-12-09 | 16:13 | Data | 0 | 32.926 | 30.88 | 185.091 | 7.64 | 173.973 | 2131.24 | 26.03 | 46.359 | 6.37 | 1.346 | 4.653 | 8458.83 | 2.181 | 97.8 | 77.6 | 1385 | 23.27 | 5498.2 | 1809.4 | 2189.9 | 2851.9 | 1192.9 | 0.63207 | 5.998
2024-12-09 | 16:13 | Data | 0 | 32.568 | 30.766 | 185.318 | 7.64 | 174.063 | 2133.95 | 26.02 | 46.089 | 6.36 | 1.345 | 4.666 | 8458.83 | 1.857 | 97.8 | 77.6 | 1387 | 23.04 | 5498.2 | 1807.6 | 2191.7 | 2851.4 | 1192.9 | 0.63108 | 6.011
2024-12-09 | 16:13 | Data | 0 | 32.609 | 30.678 | 185.137 | 7.64 | 174.018 | 2134.85 | 26.02 | 46.45 | 6.36 | 1.332 | 4.665 | 8445.26 | 1.911 | 97.8 | 77.8 | 1387 | 23.27 | 5489.4 | 1808.6 | 2205.1 | 2863.8 | 1192.9 | 0.62884 | 5.998
2024-12-09 | 16:13 | Data | 0 | 33.034 | 30.712 | 185.318 | 7.64 | 174.018 | 2134.85 | 26.01 | 46.63 | 6.36 | 1.349 | 4.637 | 8445.26 | 2.073 | 97.8 | 77.5 | 1388 | 23.27 | 5489.4 | 1801.9 | 2205.4 | 2873.9 | 1192.9 | 0.62735 | 5.985
2024-12-09 | 16:13 | Data | 0 | 32.615 | 30.698 | 185.227 | 7.64 | 174.018 | 2133.95 | 26.02 | 46.54 | 6.36 | 1.358 | 4.643 | 8445.26 | 1.843 | 97.8 | 77.4 | 1388 | 23.27 | 5489.4 | 1807.8 | 2218.2 | 2873.6 | 1192.9 | 0.62676 | 6
2024-12-09 | 16:13 | Data | 0 | 32.953 | 30.678 | 185.318 | 7.64 | 173.928 | 2133.95 | 26.02 | 46.45 | 6.37 | 1.337 | 4.682 | 8038.26 | 2.073 | 97.8 | 77.8 | 1388 | 23.22 | 5224.9 | 1791.9 | 2204.5 | 2852.9 | 1192.9 | 0.6251 | 6.018
2024-12-09 | 16:13 | Data | 0 | 32.717 | 30.651 | 185.046 | 7.64 | 173.928 | 2133.95 | 26.03 | 46.54 | 6.36 | 1.338 | 4.686 | 8395.51 | 2.066 | 97.8 | 77.8 | 1386 | 23.27 | 5457.1 | 1814.5 | 2198 | 2862.2 | 1192.9 | 0.63107 | 6.023
2024-12-09 | 16:13 | Data | 0 | 32.555 | 30.651 | 185.182 | 7.64 | 174.018 | 2131.24 | 26.02 | 46.54 | 6.36 | 1.336 | 4.662 | 8395.51 | 1.857 | 97.8 | 77.7 | 1385 | 23.22 | 5457.1 | 1789.7 | 2194.2 | 2849.7 | 1192.9 | 0.62806 | 5.997
2024-12-09 | 16:13 | Data | 0 | 32.717 | 30.651 | 185.227 | 7.64 | 173.928 | 2128.52 | 26.01 | 46.54 | 6.36 | 1.342 | 4.645 | 8377.43 | 2.066 | 97.8 | 77.6 | 1384 | 23.27 | 5445.3 | 1804.4 | 2190.4 | 2852.4 | 1192.9 | 0.62926 | 5.988
2024-12-09 | 16:13 | Data | 0 | 32.669 | 30.766 | 185.272 | 7.64 | 174.063 | 2128.52 | 26.03 | 46.45 | 6.36 | 1.346 | 4.654 | 8418.13 | 2.147 | 97.8 | 77.6 | 1383 | 23.27 | 5471.8 | 1811.4 | 2183.8 | 2848.3 | 1192.9 | 0.6332 | 5.999
2024-12-09 | 16:13 | Data | 0 | 32.696 | 30.82 | 185.227 | 7.64 | 173.928 | 2128.52 | 26.02 | 46.45 | 6.36 | 1.347 | 4.649 | 8445.26 | 1.965 | 97.8 | 77.5 | 1383 | 23.27 | 5489.4 | 1799.6 | 2176.9 | 2836.3 | 1192.9 | 0.63159 | 5.997
2024-12-09 | 16:13 | Data | 0 | 32.865 | 30.671 | 185.182 | 7.64 | 173.973 | 2126.72 | 26.02 | 46.54 | 6.36 | 1.352 | 4.65 | 8436.21 | 2.073 | 97.8 | 77.5 | 1383 | 23.27 | 5483.5 | 1819.4 | 2180.1 | 2851.7 | 1192.9 | 0.63609 | 6.003
2024-12-09 | 16:13 | Data | 0 | 32.501 | 30.678 | 185.137 | 7.64 | 173.928 | 2128.52 | 26.02 | 46.54 | 6.36 | 1.353 | 4.658 | 8440.74 | 2.019 | 97.8 | 77.5 | 1384 | 23.22 | 5486.5 | 1814.7 | 2180.1 | 2849.2 | 1192.9 | 0.63442 | 6.011
2024-12-09 | 16:13 | Data | 0 | 32.501 | 30.766 | 185.137 | 7.64 | 173.973 | 2175.52 | 26.02 | 46.45 | 6.36 | 1.346 | 4.655 | 8440.74 | 2.019 | 97.9 | 77.6 | 1414 | 23.22 | 5486.5 | 1806.5 | 2179.5 | 2836.7 | 1192.9 | 0.63302 | 6.002
2024-12-09 | 16:13 | Data | 0 | 32.933 | 30.664 | 185.137 | 7.64 | 174.018 | 2172.81 | 26.03 | 46.45 | 6.36 | 1.341 | 4.629 | 8454.3 | 2.154 | 97.9 | 77.5 | 1412 | 23.27 | 5495.3 | 1790.7 | 2179.1 | 2832 | 1192.9 | 0.6299 | 5.971
2024-12-09 | 16:13 | Data | 0 | 32.696 | 30.88 | 185.182 | 7.64 | 173.973 | 2178.24 | 26.01 | 46.54 | 6.37 | 1.342 | 4.635 | 8458.83 | 2.154 | 97.9 | 77.5 | 1416 | 23.27 | 5498.2 | 1788.3 | 2184.8 | 2844.2 | 1192.9 | 0.62744 | 5.977
2024-12-09 | 16:14 | Data | 0 | 32.723 | 30.563 | 185.046 | 7.64 | 173.928 | 2177.33 | 26.02 | 46.45 | 6.36 | 1.342 | 4.641 | 8472.39 | 2.248 | 97.9 | 77.6 | 1415 | 23.27 | 5507.1 | 1790.3 | 2180.6 | 2834.8 | 1192.9 | 0.62923 | 5.982
2024-12-09 | 16:14 | Data | 0 | 32.723 | 30.448 | 185.137 | 7.64 | 173.837 | 2131.24 | 26.02 | 46.359 | 6.36 | 1.346 | 4.636 | 8458.83 | 2.167 | 97.8 | 77.5 | 1385 | 23.22 | 5498.2 | 1819.7 | 2186.3 | 2857.8 | 1192.9 | 0.63175 | 5.983
2024-12-09 | 16:14 | Data | 0 | 32.69 | 30.988 | 185.182 | 7.64 | 174.018 | 2127.62 | 26.03 | 46.54 | 6.36 | 1.34 | 4.638 | 8467.87 | 2.012 | 97.8 | 77.6 | 1383 | 23.27 | 5504.1 | 1805.8 | 2198.2 | 2857.2 | 1192.9 | 0.62968 | 5.979
2024-12-09 | 16:14 | Data | 0 | 32.696 | 31.009 | 185.272 | 7.64 | 173.928 | 2127.62 | 26.03 | 46.269 | 6.36 | 1.332 | 4.654 | 8472.39 | 1.978 | 97.8 | 77.8 | 1383 | 23.13 | 5507.1 | 1812.7 | 2179.8 | 2847 | 1192.9 | 0.63466 | 5.988
2024-12-09 | 16:14 | Data | 0 | 32.602 | 30.651 | 185.182 | 7.64 | 173.837 | 2126.72 | 26.01 | 46.54 | 6.36 | 1.334 | 4.654 | 8463.35 | 2.066 | 97.8 | 77.7 | 1382 | 23.27 | 5501.2 | 1802.5 | 2179 | 2840.9 | 1192.9 | 0.63176 | 5.988
2024-12-09 | 16:14 | Data | 0 | 32.609 | 30.59 | 185.091 | 7.64 | 173.928 | 2126.72 | 26.02 | 46.45 | 6.36 | 1.348 | 4.665 | 8472.39 | 2.079 | 97.8 | 77.6 | 1382 | 23.22 | 5507.1 | 1799.9 | 2186.1 | 2843 | 1192.9 | 0.63062 | 6.01
2024-12-09 | 16:14 | Data | 0 | 32.494 | 30.536 | 185.091 | 7.64 | 173.792 | 2125.81 | 26.02 | 46.45 | 6.36 | 1.345 | 4.658 | 8472.39 | 2.16 | 97.8 | 77.6 | 1382 | 23.27 | 5507.1 | 1784.7 | 2166.7 | 2820.1 | 1192.9 | 0.63076 | 6.003
2024-12-09 | 16:14 | Data | 0 | 32.622 | 30.597 | 185.182 | 7.64 | 173.928 | 2123.1 | 26.01 | 46.54 | 6.36 | 1.343 | 4.635 | 8467.87 | 2.235 | 97.8 | 77.5 | 1379 | 23.27 | 5504.1 | 1814.1 | 2185.3 | 2853.3 | 1192.9 | 0.63297 | 5.978
2024-12-09 | 16:14 | Data | 0 | 32.494 | 30.415 | 185.001 | 7.64 | 173.792 | 2119.49 | 26.02 | 46.54 | 6.36 | 1.339 | 4.656 | 8454.3 | 2.079 | 97.8 | 77.7 | 1378 | 23.27 | 5495.3 | 1813 | 2186 | 2848 | 1192.9 | 0.63137 | 5.995
2024-12-09 | 16:14 | Data | 0 | 32.771 | 30.82 | 185.272 | 7.64 | 173.973 | 2122.2 | 26.01 | 46.45 | 6.36 | 1.335 | 4.635 | 8481.44 | 2.1 | 97.8 | 77.6 | 1379 | 23.22 | 5512.9 | 1800.1 | 2176.3 | 2835.7 | 1192.9 | 0.63214 | 5.969
2024-12-09 | 16:14 | Data | 0 | 32.575 | 30.475 | 185.227 | 7.64 | 174.018 | 2121.29 | 26.03 | 46.54 | 6.36 | 1.339 | 4.659 | 8458.83 | 1.857 | 97.8 | 77.7 | 1378 | 23.27 | 5498.2 | 1799.9 | 2204 | 2858 | 1192.9 | 0.6272 | 5.999
2024-12-09 | 16:14 | Data | 0 | 32.953 | 30.435 | 185.227 | 7.64 | 174.063 | 2120.39 | 26.02 | 46.54 | 6.37 | 1.349 | 4.64 | 8449.78 | 2.073 | 97.8 | 77.4 | 1378 | 23.22 | 5492.4 | 1804.7 | 2204.5 | 2860.9 | 1192.9 | 0.62843 | 5.993
2024-12-09 | 16:14 | Data | 0 | 32.494 | 30.955 | 185.182 | 7.64 | 173.973 | 2120.39 | 26.02 | 46.45 | 6.36 | 1.342 | 4.643 | 8485.96 | 2.106 | 97.8 | 77.6 | 1379 | 23.27 | 5515.9 | 1797.3 | 2201.4 | 2853 | 1192.9 | 0.62807 | 5.987
2024-12-09 | 16:14 | Data | 0 | 32.507 | 30.536 | 185.137 | 7.64 | 173.928 | 2117.68 | 26.02 | 46.45 | 6.36 | 1.338 | 4.653 | 8499.53 | 2.086 | 97.8 | 77.7 | 1376 | 23.27 | 5524.7 | 1795.9 | 2192.8 | 2846.4 | 1192.9 | 0.62615 | 5.992
2024-12-09 | 16:14 | Data | 0 | 32.413 | 30.415 | 185.182 | 7.64 | 173.973 | 2117.68 | 26.01 | 46.45 | 6.37 | 1.334 | 4.66 | 8481.44 | 2.066 | 97.8 | 77.7 | 1376 | 23.27 | 5512.9 | 1797.8 | 2217.8 | 2868.9 | 1192.9 | 0.62416 | 5.994
2024-12-09 | 16:14 | Data | 0 | 33.108 | 30.766 | 185.227 | 7.64 | 173.973 | 2117.68 | 26.02 | 45.998 | 6.36 | 1.332 | 4.66 | 8513.09 | 2.093 | 97.8 | 77.7 | 1376 | 23 | 5533.5 | 1816.2 | 2221.3 | 2880.1 | 1192.9 | 0.6281 | 5.995
2024-12-09 | 16:14 | Data | 0 | 32.507 | 30.475 | 185.182 | 7.64 | 173.837 | 2118.58 | 26 | 46.45 | 6.36 | 1.338 | 4.645 | 8499.53 | 1.85 | 97.8 | 77.7 | 1376 | 23.27 | 5524.7 | 1818.6 | 2210.1 | 2869.1 | 1192.9 | 0.62957 | 5.981
2024-12-09 | 16:14 | Data | 0 | 33.054 | 30.88 | 185.227 | 7.64 | 173.973 | 2114.97 | 26.02 | 46.269 | 6.37 | 1.341 | 4.653 | 8481.44 | 2.1 | 97.8 | 77.6 | 1375 | 23.13 | 5512.9 | 1800.6 | 2197.3 | 2848 | 1192.9 | 0.62642 | 5.993
2024-12-09 | 16:15 | Data | 0 | 32.723 | 30.853 | 185.137 | 7.64 | 173.973 | 2111.35 | 26.02 | 46.179 | 6.36 | 1.339 | 4.635 | 8476.91 | 1.958 | 97.8 | 77.6 | 1372 | 23.09 | 5510 | 1791.3 | 2201.3 | 2851.3 | 1192.9 | 0.62974 | 5.975
2024-12-09 | 16:15 | Data | 0 | 32.494 | 30.82 | 185.137 | 7.64 | 173.973 | 2111.35 | 26.02 | 46.269 | 6.36 | 1.348 | 4.648 | 8458.83 | 2.052 | 97.8 | 77.5 | 1372 | 23.09 | 5498.2 | 1801.7 | 2187.1 | 2842.7 | 1192.9 | 0.62988 | 5.999
2024-12-09 | 16:15 | Data | 0 | 32.494 | 30.698 | 185.137 | 7.64 | 173.973 | 2109.54 | 26.02 | 46.269 | 6.36 | 1.345 | 4.645 | 8458.83 | 1.83 | 97.8 | 77.5 | 1371 | 23.09 | 5498.2 | 1806.3 | 2186.6 | 2843.1 | 1192.9 | 0.62941 | 5.99
2024-12-09 | 16:15 | Data | 0 | 32.494 | 30.644 | 185.182 | 7.64 | 173.837 | 2108.64 | 26.02 | 46.269 | 6.36 | 1.339 | 4.651 | 8467.87 | 2.025 | 97.8 | 77.6 | 1371 | 23.13 | 5504.1 | 1812.9 | 2188.2 | 2853.4 | 1193 | 0.63312 | 5.99
2024-12-09 | 16:15 | Data | 0 | 32.669 | 30.637 | 185.137 | 7.64 | 173.973 | 2109.54 | 26.02 | 46.179 | 6.36 | 1.339 | 4.675 | 8431.69 | 2.079 | 97.8 | 77.7 | 1371 | 23.09 | 5480.6 | 1785.4 | 2182.3 | 2831.8 | 1193 | 0.62856 | 6.015
2024-12-09 | 16:15 | Data | 0 | 32.345 | 30.205 | 185.137 | 7.64 | 173.973 | 2108.64 | 26.02 | 46.269 | 6.37 | 1.347 | 4.662 | 8445.26 | 2.046 | 97.8 | 77.6 | 1371 | 23.04 | 5489.4 | 1811.2 | 2192.8 | 2857.2 | 1193 | 0.63155 | 6.008
2024-12-09 | 16:15 | Data | 0 | 32.271 | 30.523 | 185.091 | 7.64 | 173.837 | 2110.45 | 26.02 | 46.269 | 6.36 | 1.347 | 4.666 | 8431.69 | 1.884 | 97.8 | 77.6 | 1371 | 23.13 | 5480.6 | 1805 | 2203.8 | 2861 | 1193 | 0.62697 | 6.014
2024-12-09 | 16:15 | Data | 0 | 32.696 | 30.651 | 185.182 | 7.64 | 173.837 | 2105.93 | 26.02 | 46.269 | 6.35 | 1.342 | 4.638 | 8427.17 | 2.073 | 97.8 | 77.5 | 1369 | 23.09 | 5477.7 | 1800.6 | 2201.7 | 2856.7 | 1193 | 0.63172 | 5.981
2024-12-09 | 16:15 | Data | 0 | 32.507 | 30.421 | 185.227 | 7.64 | 173.837 | 2103.22 | 26.02 | 46.269 | 6.36 | 1.344 | 4.628 | 8422.65 | 2.052 | 97.8 | 77.5 | 1367 | 23.13 | 5474.7 | 1797.7 | 2185.5 | 2842.9 | 1193 | 0.6299 | 5.971
2024-12-09 | 16:15 | Data | 0 | 32.393 | 30.502 | 185.046 | 7.64 | 173.837 | 2103.22 | 26.02 | 46.179 | 6.36 | 1.341 | 4.638 | 8418.13 | 1.688 | 97.8 | 77.6 | 1367 | 23.13 | 5471.8 | 1806.9 | 2195.2 | 2856.1 | 1193 | 0.63029 | 5.979
2024-12-09 | 16:15 | Data | 0 | 32.609 | 30.968 | 185.137 | 7.64 | 173.837 | 2106.83 | 26.02 | 46.269 | 6.36 | 1.346 | 4.683 | 8427.17 | 1.985 | 97.8 | 77.7 | 1369 | 23.09 | 5477.7 | 1802.1 | 2195.6 | 2852.2 | 1193 | 0.62935 | 6.029
2024-12-09 | 16:15 | Data | 0 | 32.771 | 30.435 | 185.182 | 7.64 | 174.018 | 2105.03 | 26.02 | 46.269 | 6.36 | 1.341 | 4.646 | 8445.26 | 2.093 | 97.8 | 77.6 | 1369 | 23.09 | 5489.4 | 1801.3 | 2190 | 2852 | 1193 | 0.63082 | 5.987
2024-12-09 | 16:15 | Data | 0 | 32.514 | 30.59 | 185.137 | 7.64 | 173.747 | 2105.93 | 26.02 | 46.179 | 6.36 | 1.344 | 4.615 | 8454.3 | 2.086 | 97.8 | 77.5 | 1369 | 23.09 | 5495.3 | 2878 | 3211 | 4596.1 | 1193 | 0.67326 | 5.958
2024-12-09 | 16:15 | Data | 0 | 32.345 | 30.421 | 185.091 | 7.64 | 173.837 | 2108.64 | 26.01 | 46.269 | 6.36 | 1.344 | 4.635 | 8445.26 | 1.85 | 97.8 | 77.5 | 1370 | 23.09 | 5489.4 | 2875.1 | 2765.4 | 4105.3 | 1193 | 0.68511 | 5.979
2024-12-09 | 16:15 | Data | 0 | 32.636 | 30.428 | 185.137 | 7.64 | 173.973 | 2111.35 | 26.02 | 46.179 | 6.35 | 1.344 | 4.645 | 8427.17 | 1.884 | 97.8 | 77.6 | 1372 | 23.09 | 5477.7 | 2880.8 | 2776 | 4121.7 | 1193 | 0.6837 | 5.988
2024-12-09 | 16:15 | Data | 0 | 32.825 | 30.752 | 185.137 | 7.64 | 174.018 | 2111.35 | 26.01 | 46.269 | 6.36 | 1.344 | 4.648 | 8431.69 | 2.059 | 97.8 | 77.5 | 1372 | 23.18 | 5480.6 | 2877.7 | 2757.6 | 4101 | 1193 | 0.68632 | 5.99
2024-12-09 | 16:15 | Data | 0 | 32.352 | 30.421 | 185.091 | 7.64 | 173.928 | 2114.97 | 26.01 | 46.269 | 6.36 | 1.334 | 4.651 | 8436.21 | 1.857 | 97.8 | 77.7 | 1374 | 23.13 | 5483.5 | 2884.9 | 2751.1 | 4106.4 | 1193 | 0.68599 | 5.985
2024-12-09 | 16:16 | Data | 0 | 32.494 | 30.502 | 185.137 | 7.64 | 173.837 | 2109.54 | 26.02 | 46.179 | 6.36 | 1.336 | 4.634 | 8422.65 | 1.992 | 97.8 | 77.6 | 1371 | 23.09 | 5474.7 | 2860.5 | 2754.8 | 4093.1 | 1193 | 0.68323 | 5.969
2024-12-09 | 16:16 | Data | 0 | 32.582 | 30.867 | 185.182 | 7.64 | 173.837 | 2113.16 | 26.02 | 46.179 | 6.36 | 1.344 | 4.652 | 8431.69 | 2.16 | 97.8 | 77.6 | 1374 | 23.13 | 5480.6 | 2866.4 | 2753.4 | 4097.6 | 1193 | 0.68375 | 5.994
2024-12-09 | 16:16 | Data | 0 | 32.285 | 30.874 | 185.182 | 7.64 | 173.928 | 2117.68 | 26.03 | 46.269 | 6.37 | 1.357 | 4.64 | 8440.74 | 1.924 | 97.8 | 77.4 | 1377 | 23.13 | 5486.5 | 2894.5 | 2764 | 4123 | 1193 | 0.68544 | 5.998
2024-12-09 | 16:16 | Data | 0 | 32.69 | 30.529 | 185.137 | 7.64 | 173.928 | 2120.39 | 26.01 | 46.269 | 6.36 | 1.341 | 4.631 | 8467.87 | 1.951 | 97.8 | 77.5 | 1378 | 23.13 | 5504.1 | 2888.6 | 2765.3 | 4117.5 | 1193 | 0.68595 | 5.971
2024-12-09 | 16:16 | Data | 0 | 32.744 | 30.651 | 185.227 | 7.64 | 173.973 | 2117.68 | 26.02 | 46.45 | 6.36 | 1.34 | 4.673 | 8458.83 | 2.066 | 97.8 | 77.7 | 1376 | 23.22 | 5498.2 | 2866.4 | 2760.3 | 4102.1 | 1193 | 0.68351 | 6.013
2024-12-09 | 16:16 | Data | 0 | 32.723 | 30.529 | 185.091 | 7.64 | 173.837 | 2116.78 | 26.02 | 46.54 | 6.36 | 1.345 | 4.655 | 8458.83 | 1.958 | 97.8 | 77.6 | 1375 | 23.22 | 5498.2 | 2890.3 | 2754.7 | 4113.1 | 1193 | 0.68663 | 6.001
2024-12-09 | 16:16 | Data | 0 | 32.494 | 30.415 | 185.046 | 7.64 | 173.747 | 2122.2 | 26.02 | 46.54 | 6.36 | 1.348 | 4.673 | 8436.21 | 2.194 | 97.8 | 77.6 | 1380 | 23.27 | 5483.5 | 2890 | 2765.5 | 4116.2 | 1193 | 0.68594 | 6.021
2024-12-09 | 16:16 | Data | 0 | 32.946 | 30.489 | 185.227 | 7.64 | 173.928 | 2121.29 | 26.01 | 46.45 | 6.36 | 1.344 | 4.645 | 8436.21 | 2.16 | 97.8 | 77.6 | 1379 | 23.27 | 5483.5 | 2874.2 | 2764.8 | 4105.4 | 1193 | 0.68399 | 5.989
2024-12-09 | 16:16 | Data | 0 | 32.44 | 30.59 | 185.182 | 7.64 | 173.792 | 2122.2 | 25.99 | 46.54 | 6.36 | 1.341 | 4.636 | 8440.74 | 2.073 | 97.8 | 77.6 | 1381 | 23.27 | 5486.5 | 2881.1 | 2762.6 | 4111.7 | 1193 | 0.68486 | 5.977
2024-12-09 | 16:16 | Data | 0 | 32.507 | 30.637 | 185.046 | 7.64 | 173.792 | 2123.1 | 26.02 | 46.45 | 6.36 | 1.329 | 4.627 | 8440.74 | 1.857 | 97.8 | 77.7 | 1379 | 23.27 | 5486.5 | 2867.9 | 2770.8 | 4109.6 | 1193 | 0.68114 | 5.957
2024-12-09 | 16:16 | Data | 0 | 32.285 | 30.415 | 185.182 | 7.64 | 173.747 | 2122.2 | 26 | 46.45 | 6.35 | 1.343 | 4.638 | 8431.69 | 1.971 | 97.8 | 77.5 | 1380 | 23.22 | 5480.6 | 2876.3 | 2763.6 | 4106.3 | 1193 | 0.68474 | 5.981
2024-12-09 | 16:16 | Data | 0 | 32.379 | 30.415 | 185.001 | 7.64 | 173.792 | 2124.91 | 26 | 46.45 | 6.36 | 1.346 | 4.664 | 8458.83 | 2.241 | 97.8 | 77.6 | 1381 | 23.27 | 5498.2 | 2878.1 | 2757.8 | 4102.9 | 1193 | 0.68609 | 6.011
2024-12-09 | 16:16 | Data | 0 | 32.332 | 30.631 | 185.137 | 7.64 | 173.973 | 2123.1 | 26 | 46.45 | 6.36 | 1.348 | 4.668 | 8467.87 | 1.87 | 97.8 | 77.6 | 1380 | 23.27 | 5504.1 | 2882.5 | 2757.6 | 4104.1 | 1193 | 0.68537 | 6.015
2024-12-09 | 16:16 | Data | 0 | 32.696 | 30.718 | 185.227 | 7.64 | 174.018 | 2120.39 | 25.99 | 46.54 | 6.36 | 1.349 | 4.627 | 8454.3 | 1.951 | 97.8 | 77.4 | 1378 | 23.22 | 5495.3 | 2879.6 | 2752.3 | 4105 | 1193 | 0.68665 | 5.977
2024-12-09 | 16:16 | Data | 0 | 32.521 | 30.415 | 185.046 | 7.64 | 173.837 | 2121.29 | 26.01 | 46.54 | 6.36 | 1.345 | 4.652 | 8476.91 | 1.911 | 97.8 | 77.6 | 1378 | 23.22 | 5510 | 2877.3 | 2765.3 | 4110.2 | 1193 | 0.6851 | 5.998
2024-12-09 | 16:16 | Data | 0 | 32.811 | 30.867 | 185.046 | 7.64 | 173.837 | 2120.39 | 26.02 | 46.45 | 6.36 | 1.357 | 4.671 | 8463.35 | 2.066 | 97.8 | 77.5 | 1378 | 23.27 | 5501.2 | 2872.3 | 2751 | 4102.2 | 1193 | 0.68413 | 6.026
2024-12-09 | 16:16 | Data | 0 | 32.494 | 30.536 | 185.046 | 7.64 | 173.747 | 2120.39 | 26.03 | 46.45 | 6.37 | 1.346 | 4.654 | 8472.39 | 2.079 | 97.8 | 77.6 | 1378 | 23.27 | 5507.1 | 2886.3 | 2749.5 | 4107.3 | 1193 | 0.68631 | 5.999
2024-12-09 | 16:16 | Data | 0 | 32.507 | 30.637 | 185.137 | 7.64 | 173.792 | 2120.39 | 26.02 | 46.45 | 6.36 | 1.343 | 4.645 | 8467.87 | 1.87 | 97.8 | 77.6 | 1378 | 23.22 | 5504.1 | 2880.1 | 2754 | 4102.6 | 1193 | 0.6866 | 5.987
2024-12-09 | 16:17 | Data | 0 | 32.649 | 30.651 | 185.227 | 7.64 | 173.973 | 2116.78 | 26.02 | 46.54 | 6.36 | 1.343 | 4.642 | 8463.35 | 2.262 | 97.8 | 77.6 | 1378 | 23.27 | 5501.2 | 2877 | 2753.5 | 4102.4 | 1193 | 0.68329 | 5.985
2024-12-09 | 16:17 | Data | 0 | 32.494 | 30.739 | 185.137 | 7.64 | 173.928 | 2117.68 | 26.02 | 46.45 | 6.37 | 1.348 | 4.647 | 8445.26 | 1.958 | 97.8 | 77.5 | 1376 | 23.22 | 5489.4 | 2862.5 | 2751.9 | 4086.6 | 1193 | 0.68531 | 5.994
2024-12-09 | 16:17 | Data | 0 | 32.501 | 30.644 | 185.046 | 7.64 | 173.928 | 2117.68 | 26.02 | 46.54 | 6.36 | 1.341 | 4.653 | 8427.17 | 1.87 | 97.8 | 77.6 | 1376 | 23.22 | 5477.7 | 2879.6 | 2726.1 | 4081.8 | 1193 | 0.68652 | 5.995
2024-12-09 | 16:17 | Data | 0 | 32.946 | 30.685 | 185.363 | 7.64 | 174.018 | 2120.39 | 26.02 | 46.54 | 6.36 | 1.336 | 4.667 | 8440.74 | 2.12 | 97.8 | 77.8 | 1378 | 23.22 | 5486.5 | 2880.2 | 2750.8 | 4104.4 | 1193 | 0.68518 | 6.003
2024-12-09 | 16:17 | Data | 0 | 32.561 | 30.448 | 185.137 | 7.64 | 173.973 | 2120.39 | 26.02 | 46.359 | 6.36 | 1.34 | 4.651 | 8517.61 | 1.985 | 97.8 | 77.6 | 1378 | 23.22 | 5536.4 | 2867.3 | 2747.8 | 4093.6 | 1193 | 0.68461 | 5.991
2024-12-09 | 16:17 | Data | 0 | 32.663 | 30.644 | 185.091 | 7.64 | 173.928 | 2119.49 | 26.01 | 46.54 | 6.35 | 1.348 | 4.63 | 8671.37 | 2.073 | 97.8 | 77.5 | 1378 | 23.22 | 5636.4 | 2887 | 2746.4 | 4103.2 | 1193 | 0.68631 | 5.978
2024-12-09 | 16:17 | Data | 0 | 32.305 | 30.637 | 185.137 | 7.64 | 173.837 | 2121.29 | 26.02 | 46.54 | 6.35 | 1.355 | 4.647 | 8666.85 | 1.911 | 97.8 | 77.4 | 1378 | 23.22 | 5633.5 | 2890.5 | 2770.4 | 4119.4 | 1193 | 0.68453 | 6.003
2024-12-09 | 16:17 | Data | 0 | 32.568 | 30.428 | 185.137 | 7.64 | 173.928 | 2116.78 | 26.01 | 46.54 | 6.36 | 1.349 | 4.655 | 8666.85 | 2.079 | 97.8 | 77.5 | 1376 | 23.32 | 5633.5 | 2884.3 | 2751.9 | 4106 | 1193 | 0.68648 | 6.004
2024-12-09 | 16:17 | Data | 0 | 32.494 | 30.651 | 185.091 | 7.64 | 173.837 | 2114.06 | 26.02 | 46.45 | 6.36 | 1.331 | 4.649 | 8617.1 | 2.046 | 97.8 | 77.8 | 1375 | 23.27 | 5601.1 | 2865.6 | 2739.7 | 4085.7 | 1193.1 | 0.68474 | 5.979
2024-12-09 | 16:17 | Data | 0 | 32.696 | 30.651 | 185.091 | 7.64 | 173.837 | 2112.26 | 26.01 | 46.45 | 6.36 | 1.343 | 4.654 | 8458.83 | 2.066 | 97.8 | 77.6 | 1373 | 23.22 | 5498.2 | 2889.8 | 2745.1 | 4112.1 | 1193.1 | 0.68848 | 5.998
2024-12-09 | 16:17 | Data | 0 | 32.75 | 30.55 | 185.182 | 7.64 | 173.928 | 2112.26 | 26.03 | 46.45 | 6.36 | 1.344 | 4.645 | 8454.3 | 1.938 | 97.8 | 77.6 | 1373 | 23.22 | 5495.3 | 2877.4 | 2759.6 | 4104.3 | 1193.1 | 0.68518 | 5.99
2024-12-09 | 16:17 | Data | 0 | 32.723 | 30.475 | 185.046 | 7.64 | 173.973 | 2107.74 | 26.02 | 46.45 | 6.36 | 1.344 | 4.673 | 8454.3 | 2.079 | 97.8 | 77.7 | 1370 | 23.22 | 5495.3 | 2896.6 | 2741.8 | 4107.1 | 1193.1 | 0.687 | 6.018
2024-12-09 | 16:17 | Data | 0 | 32.717 | 30.651 | 185.091 | 7.64 | 173.837 | 2108.64 | 26.02 | 46.54 | 6.37 | 1.347 | 4.658 | 8458.83 | 2.073 | 97.8 | 77.6 | 1371 | 23.27 | 5498.2 | 2859.9 | 2779 | 4108.8 | 1193.1 | 0.68014 | 6.005
2024-12-09 | 16:17 | Data | 0 | 32.278 | 30.57 | 185.227 | 7.64 | 173.973 | 2111.35 | 26.02 | 46.45 | 6.36 | 1.338 | 4.652 | 8485.96 | 1.789 | 97.8 | 77.7 | 1372 | 23.27 | 5515.9 | 2880.8 | 2769.5 | 4112.3 | 1193.1 | 0.68324 | 5.989
2024-12-09 | 16:17 | Data | 0 | 32.595 | 30.732 | 185.137 | 7.64 | 173.928 | 2114.97 | 26.01 | 46.63 | 6.36 | 1.339 | 4.646 | 8467.87 | 2.039 | 97.8 | 77.6 | 1375 | 23.22 | 5504.1 | 2874.9 | 2743.1 | 4093.2 | 1193.1 | 0.68666 | 5.986
2024-12-09 | 16:17 | Data | 0 | 32.669 | 30.82 | 185.091 | 7.64 | 173.837 | 2117.68 | 26.02 | 46.54 | 6.36 | 1.337 | 4.643 | 8445.26 | 2.079 | 97.8 | 77.6 | 1376 | 23.27 | 5489.4 | 2887.4 | 2742.6 | 4099.9 | 1193.1 | 0.68883 | 5.982
2024-12-09 | 16:17 | Data | 0 | 32.501 | 30.651 | 185.091 | 7.64 | 173.837 | 2117.68 | 26.01 | 46.721 | 6.36 | 1.343 | 4.663 | 8445.26 | 1.85 | 97.8 | 77.6 | 1377 | 23.18 | 5489.4 | 2858.5 | 2740.4 | 4077.2 | 1193.1 | 0.68232 | 6.006
2024-12-09 | 16:17 | Data | 0 | 32.831 | 30.435 | 185.137 | 7.64 | 173.928 | 2117.68 | 26.03 | 46.45 | 6.36 | 1.34 | 4.638 | 8445.26 | 2.127 | 97.8 | 77.6 | 1376 | 23.22 | 5489.4 | 2865.5 | 2764.6 | 4098.8 | 1193.1 | 0.68366 | 5.978
2024-12-09 | 16:18 | Data | 0 | 32.582 | 30.651 | 185.227 | 7.64 | 174.063 | 2117.68 | 26.02 | 46.45 | 6.35 | 1.347 | 4.652 | 8427.17 | 2.167 | 97.8 | 77.5 | 1376 | 23.27 | 5477.7 | 2869.9 | 2744.8 | 4090.2 | 1193.1 | 0.68445 | 5.998
2024-12-09 | 16:18 | Data | 0 | 32.831 | 30.489 | 185.227 | 7.64 | 173.973 | 2116.78 | 26.02 | 46.54 | 6.36 | 1.338 | 4.651 | 8445.26 | 2.073 | 97.8 | 77.7 | 1376 | 23.27 | 5489.4 | 2874.6 | 2731.3 | 4085.2 | 1193.1 | 0.6855 | 5.99
2024-12-09 | 16:18 | Data | 0 | 32.413 | 30.415 | 185.001 | 7.64 | 173.928 | 2117.68 | 26.01 | 46.54 | 6.36 | 1.34 | 4.646 | 8431.69 | 1.85 | 97.8 | 77.6 | 1376 | 23.22 | 5480.6 | 2857.8 | 2741.4 | 4080.6 | 1193.1 | 0.68437 | 5.986
2024-12-09 | 16:18 | Data | 0 | 32.494 | 30.475 | 185.272 | 7.64 | 174.018 | 2120.39 | 26.01 | 46.45 | 6.36 | 1.345 | 4.655 | 8445.26 | 2.052 | 97.8 | 77.6 | 1378 | 23.27 | 5489.4 | 2876.6 | 2741.5 | 4091.7 | 1193.1 | 0.68576 | 6.001
2024-12-09 | 16:18 | Data | 0 | 32.494 | 30.644 | 185.227 | 7.64 | 173.928 | 2119.49 | 26.02 | 46.54 | 6.36 | 1.347 | 4.654 | 8458.83 | 1.971 | 97.8 | 77.6 | 1378 | 23.27 | 5498.2 | 2870.2 | 2749.1 | 4092.5 | 1193.1 | 0.68616 | 6.001
2024-12-09 | 16:18 | Data | 0 | 32.406 | 30.415 | 185.137 | 7.64 | 173.973 | 2122.2 | 26.02 | 46.45 | 6.36 | 1.347 | 4.666 | 8440.74 | 1.863 | 97.8 | 77.6 | 1379 | 23.22 | 5486.5 | 2862.2 | 2770.9 | 4105.4 | 1193.1 | 0.68093 | 6.015
2024-12-09 | 16:18 | Data | 0 | 32.507 | 30.624 | 185.001 | 7.64 | 173.928 | 2123.1 | 26.02 | 46.54 | 6.36 | 1.348 | 4.675 | 8445.26 | 1.965 | 97.8 | 77.6 | 1380 | 23.27 | 5489.4 | 2880.5 | 2761 | 4107.3 | 1193.1 | 0.68419 | 6.023
2024-12-09 | 16:18 | Data | 0 | 32.838 | 30.55 | 185.182 | 7.64 | 174.063 | 2123.1 | 26.02 | 46.54 | 6.36 | 1.342 | 4.666 | 8395.51 | 2.073 | 97.8 | 77.7 | 1380 | 23.22 | 5457.1 | 2885.4 | 2752.8 | 4106.6 | 1193.1 | 0.68652 | 6.008
2024-12-09 | 16:18 | Data | 0 | 32.723 | 30.482 | 185.091 | 7.64 | 174.018 | 2121.29 | 26.02 | 46.45 | 6.36 | 1.347 | 4.652 | 8400.04 | 2.181 | 97.8 | 77.5 | 1378 | 23.27 | 5460 | 2885.9 | 2731.7 | 4092.6 | 1193.1 | 0.68866 | 5.998
2024-12-09 | 16:18 | Data | 0 | 32.582 | 30.799 | 185.272 | 7.64 | 173.973 | 2122.2 | 26.03 | 46.54 | 6.36 | 1.339 | 4.642 | 8404.56 | 2.187 | 97.8 | 77.6 | 1379 | 23.27 | 5463 | 2878.4 | 2727.9 | 4082.4 | 1193.1 | 0.68878 | 5.981
2024-12-09 | 16:18 | Data | 0 | 32.811 | 30.955 | 185.227 | 7.64 | 173.973 | 2124.91 | 26.02 | 46.54 | 6.36 | 1.338 | 4.654 | 8418.13 | 1.924 | 97.8 | 77.7 | 1381 | 23.22 | 5471.8 | 2871.2 | 2750.6 | 4094.3 | 1193.1 | 0.68541 | 5.991
2024-12-09 | 16:18 | Data | 0 | 32.534 | 30.415 | 185.091 | 7.64 | 173.928 | 2124.91 | 26.02 | 46.54 | 6.36 | 1.344 | 4.658 | 8449.78 | 1.965 | 97.8 | 77.6 | 1381 | 23.27 | 5492.4 | 2878.5 | 2751.5 | 4098.6 | 1193.1 | 0.68604 | 6
2024-12-09 | 16:18 | Data | 0 | 32.447 | 30.651 | 185.137 | 7.64 | 174.018 | 2125.81 | 26.02 | 46.45 | 6.36 | 1.337 | 4.658 | 8440.74 | 1.951 | 97.8 | 77.7 | 1382 | 23.22 | 5486.5 | 2886.4 | 2750.9 | 4106.3 | 1193.1 | 0.68632 | 5.995
2024-12-09 | 16:18 | Data | 0 | 32.494 | 30.644 | 185.001 | 7.64 | 173.928 | 2125.81 | 26.01 | 46.54 | 6.36 | 1.349 | 4.65 | 8445.26 | 1.87 | 97.8 | 77.5 | 1383 | 23.22 | 5489.4 | 2882.9 | 2748.8 | 4101.2 | 1193.1 | 0.68602 | 5.999
2024-12-09 | 16:18 | Data | 0 | 32.818 | 30.529 | 185.318 | 7.64 | 174.018 | 2128.52 | 26.03 | 46.54 | 6.37 | 1.349 | 4.645 | 8431.69 | 1.911 | 97.8 | 77.5 | 1383 | 23.27 | 5480.6 | 2884 | 2756.4 | 4106.2 | 1193.1 | 0.68636 | 5.995
2024-12-09 | 16:18 | Data | 0 | 32.494 | 30.536 | 185.182 | 7.64 | 173.928 | 2128.52 | 26.01 | 46.45 | 6.36 | 1.339 | 4.628 | 8431.69 | 1.958 | 97.8 | 77.6 | 1384 | 23.27 | 5480.6 | 2859.8 | 2758.3 | 4090.7 | 1193.1 | 0.68236 | 5.968
2024-12-09 | 16:18 | Data | 0 | 32.359 | 30.415 | 185.046 | 7.64 | 173.973 | 2128.52 | 26.02 | 46.45 | 6.36 | 1.348 | 4.649 | 8431.69 | 1.857 | 97.8 | 77.5 | 1384 | 23.22 | 5480.6 | 2875.6 | 2744.4 | 4094.3 | 1193.1 | 0.68915 | 5.997
2024-12-09 | 16:18 | Data | 0 | 32.494 | 30.421 | 185.137 | 7.64 | 173.928 | 2128.52 | 26.02 | 46.54 | 6.36 | 1.349 | 4.641 | 8431.69 | 2.073 | 97.8 | 77.5 | 1384 | 23.22 | 5480.6 | 2864.1 | 2737.9 | 4098 | 1193.1 | 0.68445 | 5.992
2024-12-09 | 16:19 | Data | 0 | 32.501 | 30.469 | 185.091 | 7.64 | 173.837 | 2127.62 | 26.02 | 46.54 | 6.36 | 1.345 | 4.634 | 8445.26 | 1.87 | 97.8 | 77.5 | 1384 | 23.22 | 5489.4 | 2882.4 | 2749.8 | 4100.4 | 1193.1 | 0.68338 | 5.979
2024-12-09 | 16:19 | Data | 0 | 32.723 | 30.853 | 185.182 | 7.64 | 174.018 | 2127.62 | 26.02 | 46.54 | 6.35 | 1.345 | 4.631 | 8454.3 | 2.059 | 97.8 | 77.5 | 1384 | 23.22 | 5495.3 | 2878.2 | 2743.1 | 4097.3 | 1193.1 | 0.68625 | 5.977
2024-12-09 | 16:19 | Data | 0 | 32.393 | 30.415 | 185.182 | 7.64 | 173.928 | 2127.62 | 26.01 | 46.54 | 6.36 | 1.339 | 4.64 | 8454.3 | 2.039 | 97.8 | 77.6 | 1383 | 23.27 | 5495.3 | 2909.5 | 2750.1 | 4123.9 | 1193.1 | 0.69039 | 5.979
2024-12-09 | 16:19 | Data | 0 | 32.649 | 30.563 | 185.182 | 7.64 | 174.018 | 2125.81 | 26.02 | 46.54 | 6.36 | 1.338 | 4.637 | 8467.87 | 1.863 | 97.8 | 77.6 | 1382 | 23.27 | 5504.1 | 2900.1 | 2776 | 4125.1 | 1193.1 | 0.68503 | 5.974
2024-12-09 | 16:19 | Data | 0 | 32.474 | 30.651 | 185.091 | 7.64 | 173.928 | 2125.81 | 26.02 | 46.45 | 6.36 | 1.343 | 4.641 | 8485.96 | 1.958 | 97.8 | 77.6 | 1382 | 23.18 | 5515.9 | 2895.1 | 2736.7 | 4106.6 | 1193.1 | 0.68734 | 5.984
2024-12-09 | 16:19 | Data | 0 | 32.609 | 30.651 | 185.091 | 7.64 | 174.063 | 2127.62 | 26.02 | 46.54 | 6.36 | 1.347 | 4.656 | 8476.91 | 2.059 | 97.8 | 77.6 | 1383 | 23.27 | 5510 | 2889.9 | 2742.4 | 4105.8 | 1193.1 | 0.68824 | 6.004
2024-12-09 | 16:19 | Data | 0 | 32.44 | 30.88 | 185.272 | 7.64 | 173.973 | 2125.81 | 26.02 | 46.63 | 6.36 | 1.34 | 4.679 | 8458.83 | 2.019 | 97.8 | 77.7 | 1381 | 23.27 | 5498.2 | 2907 | 2722.5 | 4103.4 | 1193.1 | 0.69001 | 6.019
2024-12-09 | 16:19 | Data | 0 | 32.602 | 30.644 | 185.137 | 7.64 | 173.837 | 2126.72 | 26.02 | 46.54 | 6.37 | 1.343 | 4.658 | 8449.78 | 2.039 | 97.8 | 77.6 | 1382 | 23.18 | 5492.4 | 2894.4 | 2766.2 | 4122.9 | 1193.1 | 0.68467 | 6.001
2024-12-09 | 16:19 | Data | 0 | 32.831 | 30.435 | 185.227 | 7.64 | 174.109 | 2125.81 | 26.02 | 46.45 | 6.36 | 1.349 | 4.64 | 8458.83 | 2.12 | 97.8 | 77.5 | 1382 | 23.18 | 5498.2 | 2921.3 | 2767.9 | 4136.1 | 1193.1 | 0.68534 | 5.989
2024-12-09 | 16:19 | Data | 0 | 32.501 | 30.442 | 185.137 | 7.64 | 173.792 | 2125.81 | 26.02 | 46.269 | 6.36 | 1.338 | 4.655 | 8458.83 | 1.85 | 97.8 | 77.7 | 1382 | 23.27 | 5498.2 | 2891.8 | 2770.7 | 4125.8 | 1193.2 | 0.68571 | 5.992
2024-12-09 | 16:19 | Data | 0 | 32.386 | 30.644 | 185.046 | 7.64 | 173.837 | 2124.91 | 26.02 | 46.54 | 6.36 | 1.335 | 4.674 | 8454.3 | 1.816 | 97.8 | 77.8 | 1381 | 23.27 | 5495.3 | 2886.7 | 2777.9 | 4127 | 1193.2 | 0.68203 | 6.009
2024-12-09 | 16:19 | Data | 0 | 32.669 | 30.759 | 185.272 | 7.64 | 174.018 | 2128.52 | 26.02 | 46.45 | 6.35 | 1.334 | 4.654 | 8454.3 | 1.958 | 97.8 | 77.7 | 1383 | 23.22 | 5495.3 | 2900.4 | 2773.9 | 4134.7 | 1193.2 | 0.68424 | 5.988
2024-12-09 | 16:19 | Data | 0 | 32.669 | 30.658 | 185.318 | 7.64 | 174.063 | 2022.78 | 26.02 | 46.45 | 6.36 | 1.344 | 4.637 | 8431.69 | 2.052 | 97.7 | 77.5 | 1315 | 23.22 | 5480.6 | 2915.7 | 2769.9 | 4141.8 | 1193.2 | 0.68791 | 5.98
2024-12-09 | 16:19 | Data | 0 | 32.723 | 30.766 | 185.137 | 7.63 | 173.928 | 2125.81 | 26.03 | 46.45 | 6.36 | 1.347 | 4.652 | 8449.78 | 2.073 | 97.8 | 77.6 | 1381 | 23.27 | 5492.4 | 2912.7 | 2768.6 | 4138.3 | 1193.2 | 0.68674 | 5.999
2024-12-09 | 16:19 | Data | 0 | 32.723 | 30.455 | 185.227 | 7.64 | 174.018 | 2120.39 | 26 | 45.998 | 6.36 | 1.342 | 4.656 | 8436.21 | 2.133 | 97.8 | 77.6 | 1378 | 23 | 5483.5 | 2894.9 | 2759.4 | 4121.5 | 1193.2 | 0.685 | 5.998
2024-12-09 | 16:19 | Data | 0 | 32.717 | 30.651 | 185.182 | 7.64 | 173.973 | 2120.39 | 26.02 | 46.54 | 6.36 | 1.342 | 4.652 | 8436.21 | 2.073 | 97.8 | 77.6 | 1378 | 23.27 | 5483.5 | 2911.2 | 2766.9 | 4141.2 | 1193.2 | 0.68587 | 5.993
2024-12-09 | 16:19 | Data | 0 | 32.663 | 30.651 | 185.227 | 7.64 | 173.973 | 2125.81 | 26.02 | 46.179 | 6.36 | 1.339 | 4.642 | 8445.26 | 2.268 | 97.8 | 77.6 | 1382 | 23.09 | 5489.4 | 2908.3 | 2753.9 | 4122.2 | 1193.2 | 0.69159 | 5.98
2024-12-09 | 16:20 | Data | 0 | 32.494 | 30.563 | 185.137 | 7.64 | 173.973 | 2124.01 | 26.02 | 46.269 | 6.36 | 1.34 | 4.632 | 8449.78 | 2.073 | 97.8 | 77.6 | 1381 | 23.13 | 5492.4 | 2907.5 | 2776 | 4141.8 | 1193.2 | 0.68492 | 5.971
2024-12-09 | 16:20 | Data | 0 | 32.892 | 30.88 | 185.227 | 7.64 | 174.063 | 2122.2 | 26.01 | 46.54 | 6.36 | 1.328 | 4.637 | 8440.74 | 2.066 | 97.8 | 77.7 | 1380 | 23.27 | 5486.5 | 2915.9 | 2750.6 | 4129.6 | 1193.2 | 0.68906 | 5.964
2024-12-09 | 16:20 | Data | 0 | 32.548 | 30.428 | 185.137 | 7.64 | 173.928 | 2122.2 | 26.02 | 46.54 | 6.36 | 1.341 | 4.626 | 8440.74 | 2.052 | 97.8 | 77.5 | 1380 | 23.27 | 5486.5 | 2911.5 | 2763.8 | 4133.5 | 1193.2 | 0.68829 | 5.968
2024-12-09 | 16:20 | Data | 0 | 32.609 | 30.671 | 185.137 | 7.64 | 174.063 | 2122.2 | 26.02 | 46.45 | 6.36 | 1.349 | 4.637 | 8431.69 | 1.823 | 97.8 | 77.5 | 1379 | 23.22 | 5480.6 | 2906.2 | 2799.2 | 4151.4 | 1193.2 | 0.68349 | 5.987
2024-12-09 | 16:20 | Data | 0 | 32.723 | 30.529 | 185.091 | 7.64 | 173.928 | 2123.1 | 26.02 | 46.54 | 6.36 | 1.339 | 4.647 | 8422.65 | 2.073 | 97.8 | 77.6 | 1380 | 23.18 | 5474.7 | 2912.7 | 2771.2 | 4138 | 1193.2 | 0.68701 | 5.986
2024-12-09 | 16:20 | Data | 0 | 32.555 | 30.475 | 185.182 | 7.64 | 174.018 | 2121.29 | 26.02 | 46.45 | 6.36 | 1.34 | 4.675 | 8422.65 | 2.019 | 97.8 | 77.7 | 1379 | 23.27 | 5474.7 | 2894.9 | 2766.2 | 4125.1 | 1193.2 | 0.68521 | 6.017
2024-12-09 | 16:20 | Data | 0 | 32.636 | 30.529 | 185.182 | 7.64 | 173.928 | 2123.1 | 26.02 | 46.54 | 6.36 | 1.353 | 4.633 | 8400.04 | 2.268 | 97.8 | 77.4 | 1380 | 23.27 | 5460 | 2909.7 | 2792 | 4154.7 | 1193.2 | 0.68767 | 5.987
2024-12-09 | 16:20 | Data | 0 | 32.723 | 30.793 | 185.091 | 7.64 | 173.973 | 2123.1 | 26.01 | 46.269 | 6.36 | 1.353 | 4.662 | 8400.04 | 1.931 | 97.8 | 77.5 | 1379 | 23.09 | 5460 | 2894.8 | 2773 | 4130.3 | 1193.2 | 0.68496 | 6.015
2024-12-09 | 16:20 | Data | 0 | 32.615 | 30.442 | 185.137 | 7.64 | 173.928 | 2122.2 | 26.02 | 46.54 | 6.36 | 1.348 | 4.654 | 8390.99 | 2.079 | 97.8 | 77.6 | 1380 | 23.22 | 5454.1 | 2909.5 | 2775.8 | 4140.8 | 1193.2 | 0.68639 | 5.999
2024-12-09 | 16:20 | Data | 0 | 32.44 | 30.624 | 185.091 | 7.64 | 173.928 | 2124.01 | 26.03 | 46.359 | 6.36 | 1.351 | 4.649 | 8418.13 | 1.951 | 97.8 | 77.5 | 1380 | 23.13 | 5471.8 | 2854.5 | 2751.7 | 4082.7 | 1193.2 | 0.6822 | 5.998
2024-12-09 | 16:20 | Data | 0 | 32.811 | 30.901 | 185.453 | 7.64 | 173.973 | 2122.2 | 26.02 | 46.54 | 6.36 | 1.348 | 4.651 | 8418.13 | 2.174 | 97.8 | 77.5 | 1379 | 23.27 | 5471.8 | 2840.2 | 2769.2 | 4084.1 | 1193.2 | 0.68021 | 5.998
2024-12-09 | 16:20 | Data | 0 | 32.501 | 30.475 | 185.091 | 7.64 | 173.928 | 2120.39 | 26.02 | 46.359 | 6.35 | 1.343 | 4.664 | 8418.13 | 1.965 | 97.8 | 77.6 | 1378 | 23.22 | 5471.8 | 2822 | 2738.8 | 4044.2 | 1193.2 | 0.67835 | 6.008
2024-12-09 | 16:20 | Data | 0 | 32.649 | 30.867 | 185.182 | 7.64 | 173.973 | 2120.39 | 26.02 | 46.45 | 6.36 | 1.342 | 4.673 | 8458.83 | 2.039 | 97.8 | 77.7 | 1378 | 23.27 | 5498.2 | 2824.4 | 2754.1 | 4060.2 | 1193.2 | 0.67958 | 6.015
2024-12-09 | 16:20 | Data | 0 | 32.609 | 30.448 | 185.137 | 7.64 | 173.837 | 2118.58 | 26.02 | 46.54 | 6.36 | 1.34 | 4.664 | 8467.87 | 2.005 | 97.8 | 77.7 | 1377 | 23.27 | 5504.1 | 2835.9 | 2761.9 | 4073.5 | 1193.2 | 0.67911 | 6.005
2024-12-09 | 16:20 | Data | 0 | 32.926 | 30.772 | 185.227 | 7.64 | 173.928 | 2117.68 | 26.01 | 46.63 | 6.36 | 1.348 | 4.648 | 8454.3 | 2.194 | 97.8 | 77.5 | 1377 | 23.27 | 5495.3 | 2841.5 | 2761.2 | 4073.4 | 1193.2 | 0.68186 | 5.997
2024-12-09 | 16:20 | Data | 0 | 32.453 | 30.806 | 185.182 | 7.64 | 173.928 | 2117.68 | 26.02 | 46.54 | 6.36 | 1.331 | 4.634 | 8458.83 | 2.005 | 97.8 | 77.7 | 1376 | 23.27 | 5498.2 | 2835.7 | 2747.3 | 4063 | 1193.2 | 0.68256 | 5.966
2024-12-09 | 16:20 | Data | 0 | 32.919 | 30.678 | 185.182 | 7.64 | 174.018 | 2117.68 | 26.02 | 46.45 | 6.36 | 1.33 | 4.641 | 8418.13 | 1.985 | 97.8 | 77.7 | 1376 | 23.22 | 5471.8 | 2809.2 | 2753.4 | 4050.6 | 1193.2 | 0.67781 | 5.971
2024-12-09 | 16:20 | Data | 0 | 32.717 | 30.651 | 185.182 | 7.64 | 174.018 | 2117.68 | 26.01 | 46.45 | 6.36 | 1.347 | 4.655 | 8422.65 | 2.073 | 97.8 | 77.6 | 1376 | 23.27 | 5474.7 | 2843.2 | 2741.5 | 4069.5 | 1193.2 | 0.68248 | 6.002
2024-12-09 | 16:21 | Data | 0 | 32.298 | 30.59 | 185.137 | 7.64 | 173.973 | 2117.68 | 26.02 | 46.269 | 6.35 | 1.345 | 4.654 | 8427.17 | 1.884 | 97.8 | 77.6 | 1376 | 23.13 | 5477.7 | 2901.4 | 2762 | 4122.8 | 1193.2 | 0.68755 | 5.999
2024-12-09 | 16:21 | Data | 0 | 32.494 | 30.428 | 185.182 | 7.64 | 173.837 | 2120.39 | 26.01 | 46.359 | 6.36 | 1.353 | 4.646 | 8418.13 | 2.059 | 97.8 | 77.4 | 1378 | 23.13 | 5471.8 | 2883.4 | 2742.4 | 4103.3 | 1193.2 | 0.68592 | 6.001
2024-12-09 | 16:21 | Data | 0 | 32.494 | 30.59 | 185.182 | 7.64 | 173.928 | 2114.06 | 26.02 | 46.45 | 6.36 | 1.34 | 4.654 | 8458.83 | 2.019 | 97.8 | 77.6 | 1374 | 23.27 | 5498.2 | 2906.2 | 2744.6 | 4117.3 | 1193.2 | 0.6901 | 5.994
2024-12-09 | 16:21 | Data | 0 | 32.514 | 30.415 | 185.137 | 7.64 | 173.973 | 2117.68 | 26.05 | 46.45 | 6.36 | 1.339 | 4.631 | 8463.35 | 2.073 | 97.8 | 77.6 | 1376 | 23.27 | 5501.2 | 2889.2 | 2747 | 4110.2 | 1193.2 | 0.68561 | 5.97
2024-12-09 | 16:21 | Data | 0 | 32.555 | 30.415 | 185.182 | 7.64 | 173.792 | 2116.78 | 26.03 | 46.54 | 6.36 | 1.348 | 4.64 | 8458.83 | 1.85 | 97.8 | 77.5 | 1376 | 23.27 | 5498.2 | 2899.9 | 2773.5 | 4133.5 | 1193.2 | 0.68524 | 5.988
2024-12-09 | 16:21 | Data | 0 | 32.636 | 30.428 | 185.091 | 7.64 | 173.973 | 2116.78 | 26.03 | 46.359 | 6.35 | 1.342 | 4.685 | 8454.3 | 1.978 | 97.8 | 77.7 | 1376 | 23.22 | 5495.3 | 2898.2 | 2760.6 | 4121.2 | 1193.2 | 0.6865 | 6.027
2024-12-09 | 16:21 | Data | 0 | 32.494 | 30.59 | 185.137 | 7.64 | 173.837 | 2116.78 | 26.01 | 46.54 | 6.35 | 1.339 | 4.673 | 8436.21 | 1.958 | 97.8 | 77.8 | 1376 | 23.22 | 5483.5 | 2910.4 | 2769.1 | 4137.2 | 1193.2 | 0.6868 | 6.012
2024-12-09 | 16:21 | Data | 0 | 32.406 | 30.502 | 185.182 | 7.64 | 174.063 | 2122.2 | 26.02 | 46.45 | 6.37 | 1.341 | 4.648 | 8427.17 | 1.89 | 97.8 | 77.6 | 1379 | 23.27 | 5477.7 | 2886.8 | 2764.1 | 4112.9 | 1193.2 | 0.68542 | 5.99
2024-12-09 | 16:21 | Data | 0 | 32.501 | 30.847 | 185.091 | 7.64 | 173.837 | 2117.68 | 26.02 | 46.089 | 6.36 | 1.342 | 4.639 | 8427.17 | 1.87 | 97.8 | 77.6 | 1376 | 23.04 | 5477.7 | 2886.9 | 2769.2 | 4117.5 | 1193.2 | 0.68514 | 5.981
2024-12-09 | 16:21 | Data | 0 | 32.71 | 30.428 | 185.091 | 7.64 | 173.928 | 2122.2 | 26.01 | 46.54 | 6.36 | 1.337 | 4.65 | 8454.3 | 2.133 | 97.8 | 77.7 | 1379 | 23.22 | 5495.3 | 2905 | 2779.4 | 4120.1 | 1193.2 | 0.68903 | 5.985
2024-12-09 | 16:21 | Data | 0 | 32.285 | 30.469 | 185.046 | 7.64 | 173.837 | 2123.1 | 26.01 | 46.359 | 6.36 | 1.334 | 4.641 | 8445.26 | 1.877 | 97.8 | 77.7 | 1380 | 23.27 | 5489.4 | 2880.7 | 2772.3 | 4119.2 | 1193.2 | 0.68225 | 5.976
2024-12-09 | 16:21 | Data | 0 | 32.487 | 30.415 | 185.137 | 7.64 | 173.928 | 2123.1 | 26.01 | 46.721 | 6.36 | 1.343 | 4.624 | 8445.26 | 2.079 | 97.8 | 77.5 | 1379 | 23.41 | 5489.4 | 2874.3 | 2770.4 | 4118.1 | 1193.3 | 0.68388 | 5.966
2024-12-09 | 16:21 | Data | 0 | 32.494 | 30.415 | 185.046 | 7.64 | 173.837 | 2122.2 | 26.01 | 46.45 | 6.36 | 1.337 | 4.628 | 8440.74 | 2.079 | 97.8 | 77.6 | 1380 | 23.22 | 5486.5 | 2904.8 | 2775.6 | 4136.8 | 1193.3 | 0.68664 | 5.966
2024-12-09 | 16:21 | Data | 0 | 32.602 | 30.428 | 185.001 | 7.64 | 173.973 | 2125.81 | 26 | 46.54 | 6.36 | 1.341 | 4.642 | 8445.26 | 2.073 | 97.8 | 77.6 | 1382 | 23.32 | 5489.4 | 2898 | 2813.5 | 4160.4 | 1193.3 | 0.67998 | 5.983
2024-12-09 | 16:21 | Data | 0 | 32.494 | 30.415 | 185.137 | 7.64 | 173.837 | 2124.91 | 26.02 | 46.54 | 6.36 | 1.351 | 4.651 | 8427.17 | 2.079 | 97.8 | 77.5 | 1382 | 23.27 | 5477.7 | 2911.2 | 2805.1 | 4161.3 | 1193.3 | 0.68361 | 6
2024-12-09 | 16:21 | Data | 0 | 32.271 | 30.428 | 184.956 | 7.64 | 173.837 | 2128.52 | 26.02 | 46.54 | 6.36 | 1.339 | 4.654 | 8431.69 | 1.911 | 97.8 | 77.7 | 1383 | 23.27 | 5480.6 | 2898.6 | 2807.4 | 4153.4 | 1193.3 | 0.68088 | 5.991
2024-12-09 | 16:21 | Data | 0 | 32.487 | 30.415 | 184.956 | 7.64 | 173.792 | 2126.72 | 26.02 | 46.45 | 6.35 | 1.342 | 4.671 | 8427.17 | 2.079 | 97.8 | 77.7 | 1382 | 23.27 | 5477.7 | 2878.3 | 2801.8 | 4137.2 | 1193.3 | 0.67954 | 6.014
2024-12-09 | 16:22 | Data | 0 | 32.379 | 30.252 | 185.001 | 7.64 | 173.837 | 2127.62 | 26.02 | 46.45 | 6.36 | 1.342 | 4.641 | 8427.17 | 1.877 | 97.8 | 77.6 | 1384 | 23.22 | 5477.7 | 2887.4 | 2804.7 | 4141.4 | 1193.3 | 0.67938 | 5.984
2024-12-09 | 16:22 | Data | 0 | 32.501 | 30.59 | 185.001 | 7.64 | 173.747 | 2131.24 | 26.01 | 46.45 | 6.36 | 1.346 | 4.646 | 8440.74 | 2.079 | 97.8 | 77.5 | 1385 | 23.22 | 5486.5 | 2883.9 | 2813.6 | 4151.6 | 1193.3 | 0.67752 | 5.993
2024-12-09 | 16:22 | Data | 0 | 32.028 | 29.955 | 184.73 | 7.64 | 173.611 | 2131.24 | 26 | 46.54 | 6.36 | 1.341 | 4.641 | 8445.26 | 2.073 | 97.8 | 77.6 | 1385 | 23.27 | 5489.4 | 2882.9 | 2803.1 | 4140 | 1193.3 | 0.68029 | 5.982
2024-12-09 | 16:22 | Data | 0 | 32.035 | 30.016 | 184.956 | 7.64 | 173.702 | 2125.81 | 26 | 46.54 | 6.35 | 1.344 | 4.621 | 8431.69 | 1.83 | 97.8 | 77.5 | 1382 | 23.27 | 5480.6 | 2881.7 | 2788.4 | 4128.3 | 1193.3 | 0.68097 | 5.966
2024-12-09 | 16:22 | Data | 0 | 32.46 | 30.529 | 184.956 | 7.64 | 173.702 | 2130.33 | 26.01 | 46.54 | 6.36 | 1.339 | 4.637 | 8427.17 | 2.073 | 97.8 | 77.6 | 1385 | 23.22 | 5477.7 | 2894.9 | 2800.5 | 4146.4 | 1193.3 | 0.68095 | 5.975
2024-12-09 | 16:22 | Data | 0 | 32.771 | 30.529 | 184.956 | 7.64 | 173.837 | 2133.95 | 26.02 | 46.45 | 6.35 | 1.338 | 4.659 | 8440.74 | 1.985 | 97.8 | 77.7 | 1387 | 23.22 | 5486.5 | 2867.4 | 2790.7 | 4120.3 | 1193.3 | 0.68077 | 5.997
2024-12-09 | 16:22 | Data | 0 | 32.703 | 30.624 | 185.046 | 7.64 | 173.837 | 2133.95 | 26.03 | 46.54 | 6.36 | 1.337 | 4.664 | 8463.35 | 1.978 | 97.8 | 77.7 | 1386 | 23.27 | 5501.2 | 2879.3 | 2791.3 | 4128.3 | 1193.3 | 0.68119 | 5.999
2024-12-09 | 16:22 | Data | 0 | 32.197 | 30.361 | 185.091 | 7.64 | 174.018 | 2133.95 | 26.02 | 46.45 | 6.35 | 1.337 | 4.656 | 8449.78 | 1.688 | 97.8 | 77.7 | 1388 | 23.22 | 5492.4 | 2899.7 | 2780.7 | 4119.2 | 1193.3 | 0.68122 | 5.993
2024-12-09 | 16:22 | Data | 0 | 32.717 | 30.671 | 185.137 | 7.64 | 173.837 | 2131.24 | 26.02 | 46.45 | 6.36 | 1.343 | 4.664 | 8454.3 | 2.052 | 97.8 | 77.6 | 1385 | 23.22 | 5495.3 | 2887.8 | 2798.6 | 4140.8 | 1193.3 | 0.68159 | 6.007
2024-12-09 | 16:22 | Data | 0 | 32.264 | 30.529 | 185.001 | 7.64 | 173.792 | 2128.52 | 26.02 | 46.45 | 6.35 | 1.337 | 4.631 | 8458.83 | 2.025 | 97.8 | 77.6 | 1384 | 23.27 | 5498.2 | 2883.2 | 2796.3 | 4136.7 | 1193.3 | 0.6799 | 5.969
2024-12-09 | 16:22 | Data | 0 | 32.264 | 30.617 | 185.091 | 7.64 | 173.747 | 2139.37 | 26.02 | 46.54 | 6.36 | 1.339 | 4.641 | 8458.83 | 1.884 | 97.8 | 77.6 | 1390 | 23.27 | 5498.2 | 2868.9 | 2786.1 | 4121.6 | 1193.3 | 0.68054 | 5.98
2024-12-09 | 16:22 | Data | 0 | 32.271 | 30.415 | 185.137 | 7.64 | 173.792 | 2132.14 | 26.01 | 46.991 | 6.36 | 1.341 | 4.658 | 8458.83 | 1.965 | 97.8 | 77.7 | 1386 | 23.41 | 5498.2 | 2879.4 | 2796.4 | 4132.4 | 1193.3 | 0.68023 | 5.998
2024-12-09 | 16:22 | Data | 0 | 32.521 | 30.415 | 185.091 | 7.64 | 173.837 | 2132.14 | 26.02 | 46.54 | 6.35 | 1.341 | 4.64 | 8458.83 | 2.073 | 97.8 | 77.6 | 1385 | 23.22 | 5498.2 | 2894.1 | 2806.6 | 4141.7 | 1193.3 | 0.679 | 5.981
2024-12-09 | 16:22 | Data | 0 | 32.656 | 30.806 | 185.091 | 7.64 | 173.928 | 2131.24 | 26.02 | 46.54 | 6.36 | 1.341 | 4.616 | 8458.83 | 1.978 | 97.8 | 77.5 | 1385 | 23.22 | 5498.2 | 2872.1 | 2802.3 | 4132.3 | 1193.3 | 0.67829 | 5.958
2024-12-09 | 16:22 | Data | 0 | 32.494 | 30.469 | 185.182 | 7.64 | 173.928 | 2129.43 | 26.02 | 46.54 | 6.36 | 1.339 | 4.66 | 8458.83 | 1.971 | 97.8 | 77.7 | 1384 | 23.27 | 5498.2 | 2870.6 | 2791.3 | 4123.8 | 1193.3 | 0.67944 | 5.998
2024-12-09 | 16:22 | Data | 0 | 32.494 | 30.556 | 185.137 | 7.64 | 173.928 | 2123.1 | 26.02 | 46.45 | 6.36 | 1.334 | 4.653 | 8454.3 | 1.985 | 97.8 | 77.7 | 1381 | 23.22 | 5495.3 | 2879.3 | 2783.6 | 4121.8 | 1193.3 | 0.68335 | 5.989
2024-12-09 | 16:22 | Data | 0 | 32.885 | 30.874 | 185.137 | 7.64 | 173.928 | 2128.52 | 26.02 | 46.45 | 6.36 | 1.347 | 4.627 | 8472.39 | 2.066 | 97.8 | 77.5 | 1384 | 23.27 | 5507.1 | 2882.6 | 2789.1 | 4130.4 | 1193.3 | 0.68119 | 5.974
2024-12-09 | 16:22 | Data | 0 | 32.548 | 30.624 | 185.137 | 7.64 | 173.928 | 2128.52 | 26.02 | 46.45 | 6.36 | 1.342 | 4.63 | 8445.26 | 2.093 | 97.8 | 77.5 | 1384 | 23.22 | 5489.4 | 2892.2 | 2804.3 | 4148.6 | 1193.3 | 0.68161 | 5.972
2024-12-09 | 16:23 | Data | 0 | 32.298 | 30.469 | 185.137 | 7.64 | 173.973 | 2127.62 | 26.01 | 46.45 | 6.35 | 1.339 | 4.668 | 8431.69 | 1.755 | 97.8 | 77.7 | 1384 | 23.27 | 5480.6 | 2888.2 | 2806.2 | 4147.4 | 1193.3 | 0.6804 | 6.007
2024-12-09 | 16:23 | Data | 0 | 32.811 | 30.759 | 185.227 | 7.64 | 173.928 | 2128.52 | 26.02 | 46.45 | 6.35 | 1.334 | 4.666 | 8431.69 | 2.032 | 97.8 | 77.8 | 1383 | 23.27 | 5480.6 | 2881.9 | 2785.3 | 4127.1 | 1193.3 | 0.68103 | 5.999
2024-12-09 | 16:23 | Data | 0 | 32.494 | 30.415 | 185.046 | 7.64 | 173.928 | 2123.1 | 26.02 | 46.45 | 6.36 | 1.343 | 4.641 | 8427.17 | 2.079 | 97.8 | 77.6 | 1380 | 23.22 | 5477.7 | 2888.7 | 2769 | 4118.1 | 1193.3 | 0.68498 | 5.983
2024-12-09 | 16:23 | Data | 0 | 32.48 | 30.415 | 185.091 | 7.64 | 173.928 | 2117.68 | 26.02 | 46.54 | 6.36 | 1.346 | 4.643 | 8454.3 | 2.079 | 97.8 | 77.5 | 1376 | 23.27 | 5495.3 | 2873 | 2781 | 4114.4 | 1193.3 | 0.68027 | 5.988
2024-12-09 | 16:23 | Data | 0 | 32.723 | 30.651 | 185.091 | 7.64 | 173.837 | 2117.68 | 26.02 | 46.54 | 6.36 | 1.348 | 4.667 | 8463.35 | 2.073 | 97.8 | 77.6 | 1376 | 23.27 | 5501.2 | 2880.9 | 2798.1 | 4134.9 | 1193.3 | 0.6807 | 6.015
2024-12-09 | 16:23 | Data | 0 | 32.507 | 30.428 | 185.272 | 7.64 | 174.063 | 2114.06 | 26.01 | 46.63 | 6.36 | 1.337 | 4.635 | 8458.83 | 2.066 | 97.8 | 77.6 | 1374 | 23.27 | 5498.2 | 2894.4 | 2771.3 | 4121.5 | 1193.3 | 0.6862 | 5.972
2024-12-09 | 16:23 | Data | 0 | 32.892 | 30.874 | 185.137 | 7.64 | 173.928 | 2114.06 | 26.02 | 46.45 | 6.36 | 1.339 | 4.65 | 8449.78 | 2.073 | 97.8 | 77.6 | 1374 | 23.27 | 5492.4 | 2891.1 | 2788.9 | 4135.6 | 1193.3 | 0.68162 | 5.988
2024-12-09 | 16:23 | Data | 0 | 32.75 | 30.658 | 185.227 | 7.64 | 174.018 | 2114.06 | 26.03 | 46.45 | 6.35 | 1.343 | 4.653 | 8458.83 | 1.897 | 97.8 | 77.6 | 1374 | 23.22 | 5498.2 | 2880.8 | 2812.6 | 4147.9 | 1193.3 | 0.67646 | 5.997
2024-12-09 | 16:23 | Data | 0 | 32.717 | 30.415 | 185.091 | 7.64 | 173.928 | 2113.16 | 26.02 | 46.54 | 6.36 | 1.345 | 4.664 | 8458.83 | 2.079 | 97.8 | 77.6 | 1374 | 23.27 | 5498.2 | 2890.1 | 2801.1 | 4139.7 | 1193.3 | 0.68113 | 6.01
2024-12-09 | 16:23 | Data | 0 | 32.494 | 30.415 | 185.091 | 7.64 | 173.973 | 2111.35 | 26.03 | 46.45 | 6.36 | 1.338 | 4.663 | 8463.35 | 2.079 | 97.8 | 77.7 | 1372 | 23.22 | 5501.2 | 2881.8 | 2808.2 | 4139.8 | 1193.3 | 0.67862 | 6
2024-12-09 | 16:23 | Data | 0 | 32.609 | 30.739 | 185.137 | 7.64 | 173.973 | 2111.35 | 26.01 | 46.54 | 6.36 | 1.339 | 4.636 | 8467.87 | 2.133 | 97.8 | 77.6 | 1372 | 23.27 | 5504.1 | 2879.1 | 2813 | 4142.7 | 1193.3 | 0.67704 | 5.976
2024-12-09 | 16:23 | Data | 0 | 32.494 | 30.759 | 185.137 | 7.64 | 174.109 | 2111.35 | 26.01 | 46.45 | 6.36 | 1.339 | 4.651 | 8449.78 | 2.059 | 97.8 | 77.7 | 1373 | 23.22 | 5492.4 | 2892.4 | 2808.9 | 4146.9 | 1193.3 | 0.68129 | 5.989
2024-12-09 | 16:23 | Data | 0 | 32.602 | 30.448 | 185.182 | 7.64 | 173.973 | 2109.54 | 26.02 | 46.54 | 6.36 | 1.331 | 4.654 | 8440.74 | 2.005 | 97.8 | 77.8 | 1371 | 23.27 | 5486.5 | 2898 | 2799.4 | 4146.3 | 1193.3 | 0.68299 | 5.986
2024-12-09 | 16:23 | Data | 0 | 32.494 | 30.415 | 185.001 | 7.64 | 173.837 | 2108.64 | 26.02 | 46.54 | 6.37 | 1.339 | 4.675 | 8449.78 | 2.079 | 97.8 | 77.7 | 1371 | 23.22 | 5492.4 | 2867.8 | 2797.5 | 4125.8 | 1193.4 | 0.67814 | 6.014
2024-12-09 | 16:23 | Data | 0 | 32.494 | 30.624 | 185.091 | 7.64 | 173.837 | 2106.83 | 26.02 | 46.54 | 6.36 | 1.336 | 4.641 | 8436.21 | 2.073 | 97.8 | 77.6 | 1369 | 23.27 | 5483.5 | 2879.3 | 2792.5 | 4127.9 | 1193.4 | 0.68154 | 5.977
2024-12-09 | 16:23 | Data | 0 | 32.602 | 30.415 | 185.046 | 7.64 | 173.837 | 2110.45 | 26.03 | 46.54 | 6.36 | 1.327 | 4.651 | 8454.3 | 2.093 | 97.8 | 77.8 | 1370 | 23.27 | 5495.3 | 2879.2 | 2798.5 | 4132.1 | 1193.4 | 0.68166 | 5.979
2024-12-09 | 16:23 | Data | 0 | 32.298 | 30.59 | 185.137 | 7.64 | 174.018 | 2109.54 | 26.01 | 46.45 | 6.36 | 1.332 | 4.66 | 8409.08 | 1.735 | 97.8 | 77.8 | 1371 | 23.27 | 5465.9 | 2883.9 | 2807.1 | 4145.2 | 1193.4 | 0.68006 | 5.992
2024-12-09 | 16:23 | Data | 0 | 32.494 | 30.644 | 185.001 | 7.64 | 173.837 | 2105.93 | 26.01 | 46.54 | 6.35 | 1.349 | 4.664 | 8445.26 | 1.857 | 97.8 | 77.6 | 1369 | 23.27 | 5489.4 | 2881.9 | 2778 | 4124.7 | 1193.4 | 0.6825 | 6.011
2024-12-09 | 16:24 | Data | 0 | 32.831 | 30.664 | 185.091 | 7.64 | 173.973 | 2108.64 | 26.02 | 46.54 | 6.36 | 1.348 | 4.673 | 8427.17 | 2.073 | 97.8 | 77.6 | 1371 | 23.27 | 5477.7 | 2885 | 2793.3 | 4133.6 | 1193.4 | 0.68244 | 6.019
2024-12-09 | 16:24 | Data | 0 | 32.487 | 30.415 | 185.046 | 7.64 | 173.928 | 2109.54 | 26.02 | 46.269 | 6.36 | 1.343 | 4.654 | 8436.21 | 2.079 | 97.8 | 77.6 | 1371 | 23.13 | 5483.5 | 2896.4 | 2792.5 | 4141.5 | 1193.4 | 0.68388 | 5.998
2024-12-09 | 16:24 | Data | 0 | 32.494 | 30.705 | 185.182 | 7.64 | 173.928 | 2106.83 | 26.02 | 46.54 | 6.36 | 1.347 | 4.645 | 8458.83 | 1.931 | 97.8 | 77.5 | 1371 | 23.22 | 5498.2 | 2884.7 | 2795.7 | 4136.1 | 1193.4 | 0.67953 | 5.992
2024-12-09 | 16:24 | Data | 0 | 32.298 | 30.847 | 185.272 | 7.64 | 173.973 | 2105.93 | 26.03 | 46.45 | 6.36 | 1.347 | 4.65 | 8472.39 | 1.776 | 97.8 | 77.5 | 1369 | 23.22 | 5507.1 | 2890.8 | 2802.7 | 4145.4 | 1193.4 | 0.68177 | 5.997
2024-12-09 | 16:24 | Data | 0 | 32.501 | 30.637 | 185.001 | 7.64 | 173.837 | 2107.74 | 26.02 | 46.63 | 6.36 | 1.332 | 4.636 | 8467.87 | 1.87 | 97.8 | 77.7 | 1369 | 23.27 | 5504.1 | 2890 | 2797.5 | 4135.1 | 1193.4 | 0.68286 | 5.969
2024-12-09 | 16:24 | Data | 0 | 32.696 | 30.766 | 185.272 | 7.64 | 174.063 | 2105.93 | 26.02 | 46.45 | 6.36 | 1.331 | 4.654 | 8458.83 | 2.066 | 97.8 | 77.7 | 1369 | 23.27 | 5498.2 | 2883.3 | 2792.3 | 4132.7 | 1193.4 | 0.68112 | 5.986
2024-12-09 | 16:24 | Data | 0 | 32.325 | 30.415 | 185.182 | 7.64 | 173.928 | 2106.83 | 26.02 | 46.45 | 6.35 | 1.34 | 4.645 | 8458.83 | 2.174 | 97.8 | 77.6 | 1370 | 23.22 | 5498.2 | 2897.4 | 2790.6 | 4143.5 | 1193.4 | 0.68294 | 5.986
2024-12-09 | 16:24 | Data | 0 | 32.609 | 30.644 | 185.046 | 7.64 | 173.928 | 2109.54 | 26.02 | 45.998 | 6.36 | 1.34 | 4.654 | 8454.3 | 2.066 | 97.8 | 77.6 | 1370 | 23 | 5495.3 | 2878.4 | 2797.4 | 4135.1 | 1193.4 | 0.68009 | 5.996
2024-12-09 | 16:24 | Data | 0 | 32.723 | 30.475 | 185.091 | 7.64 | 173.928 | 2111.35 | 26.02 | 46.269 | 6.36 | 1.342 | 4.639 | 8458.83 | 1.958 | 97.8 | 77.6 | 1372 | 23.13 | 5498.2 | 2883.9 | 2797.8 | 4138.5 | 1193.4 | 0.6801 | 5.98
2024-12-09 | 16:24 | Data | 0 | 33.088 | 30.516 | 185.272 | 7.64 | 173.973 | 2111.35 | 26.02 | 46.179 | 6.36 | 1.33 | 4.617 | 8436.21 | 2.39 | 97.8 | 77.6 | 1372 | 23.13 | 5483.5 | 2881.3 | 2786 | 4130.4 | 1193.4 | 0.68158 | 5.949
2024-12-09 | 16:24 | Data | 0 | 32.494 | 30.415 | 185.091 | 7.64 | 174.018 | 2112.26 | 26.02 | 46.089 | 6.36 | 1.345 | 4.655 | 8427.17 | 2.079 | 97.8 | 77.6 | 1373 | 23.04 | 5477.7 | 2889.6 | 2785.9 | 4133 | 1193.4 | 0.68309 | 6
2024-12-09 | 16:24 | Data | 0 | 32.669 | 30.813 | 185.137 | 7.64 | 173.928 | 2112.26 | 26.02 | 46.179 | 6.36 | 1.346 | 4.654 | 8422.65 | 2.019 | 97.8 | 77.6 | 1372 | 23.13 | 5474.7 | 2873.2 | 2793.5 | 4126.8 | 1193.4 | 0.67915 | 6.001
2024-12-09 | 16:24 | Data | 0 | 32.42 | 30.415 | 185.001 | 7.64 | 173.928 | 2111.35 | 26.02 | 46.269 | 6.35 | 1.352 | 4.668 | 8431.69 | 1.877 | 97.8 | 77.5 | 1372 | 23.13 | 5480.6 | 2883.7 | 2805.9 | 4142.2 | 1193.4 | 0.67921 | 6.02
2024-12-09 | 16:24 | Data | 0 | 32.271 | 30.394 | 185.046 | 7.64 | 173.928 | 2114.97 | 26.01 | 46.269 | 6.36 | 1.347 | 4.669 | 8431.69 | 2.066 | 97.8 | 77.6 | 1376 | 23.09 | 5480.6 | 2884.6 | 2803.1 | 4142.8 | 1193.4 | 0.6786 | 6.016
2024-12-09 | 16:24 | Data | 0 | 32.528 | 30.421 | 185.182 | 7.64 | 173.973 | 2116.78 | 26.02 | 46.269 | 6.36 | 1.34 | 4.623 | 8449.78 | 1.897 | 97.8 | 77.5 | 1376 | 23.09 | 5492.4 | 2897.1 | 2819.5 | 4157.7 | 1193.4 | 0.68124 | 5.962
2024-12-09 | 16:24 | Data | 0 | 32.602 | 30.428 | 185.001 | 7.64 | 173.837 | 2117.68 | 26.03 | 46.179 | 6.36 | 1.337 | 4.639 | 8440.74 | 1.904 | 97.8 | 77.6 | 1376 | 23.09 | 5486.5 | 2889.5 | 2804.6 | 4141.4 | 1193.4 | 0.67922 | 5.974
2024-12-09 | 16:24 | Data | 0 | 32.264 | 30.509 | 185.046 | 7.64 | 173.837 | 2112.26 | 26.02 | 46.269 | 6.36 | 1.341 | 4.64 | 8458.83 | 2.052 | 97.8 | 77.6 | 1373 | 23.09 | 5498.2 | 2862.9 | 2787 | 4117.2 | 1193.4 | 0.67847 | 5.98
2024-12-09 | 16:24 | Data | 0 | 32.831 | 30.428 | 185.182 | 7.64 | 174.063 | 2117.68 | 26.02 | 46.179 | 6.36 | 1.343 | 4.628 | 8445.26 | 2.032 | 97.8 | 77.5 | 1376 | 23.13 | 5489.4 | 2864.2 | 2818.8 | 4140.8 | 1193.4 | 0.67465 | 5.97
2024-12-09 | 16:25 | Data | 0 | 32.494 | 30.739 | 185.091 | 7.64 | 173.973 | 2117.68 | 26.02 | 46.179 | 6.36 | 1.345 | 4.652 | 8445.26 | 2.073 | 97.8 | 77.6 | 1377 | 23.09 | 5489.4 | 2887.5 | 2791.7 | 4135.3 | 1193.4 | 0.68113 | 5.998
2024-12-09 | 16:25 | Data | 0 | 32.865 | 30.88 | 185.272 | 7.64 | 174.063 | 2117.68 | 26.02 | 46.179 | 6.36 | 1.342 | 4.657 | 8427.17 | 2.046 | 97.8 | 77.6 | 1376 | 23.13 | 5477.7 | 2875.8 | 2800.1 | 4129.2 | 1193.4 | 0.68118 | 5.998
2024-12-09 | 16:25 | Data | 0 | 32.723 | 30.637 | 185.137 | 7.64 | 173.928 | 2120.39 | 26.02 | 46.179 | 6.36 | 1.342 | 4.664 | 8883.91 | 2.012 | 97.8 | 77.7 | 1378 | 23.09 | 5774.5 | 2891.5 | 2806.1 | 4151.9 | 1193.4 | 0.68061 | 6.005
2024-12-09 | 16:25 | Data | 0 | 32.609 | 30.421 | 185.137 | 7.64 | 173.973 | 2116.78 | 26.02 | 46.54 | 6.36 | 1.339 | 4.653 | 8427.17 | 2.086 | 97.8 | 77.6 | 1376 | 23.22 | 5477.7 | 2894.5 | 2802.6 | 4148.5 | 1193.4 | 0.6816 | 5.992
2024-12-09 | 16:25 | Data | 0 | 32.825 | 30.766 | 185.227 | 7.64 | 174.063 | 2117.68 | 26.02 | 46.54 | 6.36 | 1.338 | 4.633 | 8418.13 | 2.046 | 97.8 | 77.6 | 1376 | 23.22 | 5471.8 | 2888 | 2818.3 | 4153.7 | 1193.4 | 0.67915 | 5.97
2024-12-09 | 16:25 | Data | 0 | 32.305 | 30.469 | 185.091 | 7.64 | 173.973 | 2117.68 | 26.02 | 46.54 | 6.35 | 1.348 | 4.638 | 8404.56 | 1.742 | 97.8 | 77.5 | 1376 | 23.27 | 5463 | 2888 | 2779.4 | 4126.5 | 1193.4 | 0.68316 | 5.987
2024-12-09 | 16:25 | Data | 0 | 32.494 | 30.617 | 185.363 | 7.64 | 174.018 | 2122.2 | 26.02 | 46.269 | 6.35 | 1.351 | 4.624 | 8431.69 | 1.877 | 97.8 | 77.4 | 1379 | 23.18 | 5480.6 | 2874.5 | 2791.3 | 4126.5 | 1193.4 | 0.68022 | 5.975
2024-12-09 | 16:25 | Data | 0 | 32.494 | 30.469 | 185.137 | 7.64 | 173.928 | 2125.81 | 26.02 | 46.54 | 6.36 | 1.34 | 4.628 | 8422.65 | 1.857 | 97.8 | 77.5 | 1382 | 23.27 | 5474.7 | 2899.5 | 2801.3 | 4149.2 | 1193.4 | 0.68277 | 5.969
2024-12-09 | 16:25 | Data | 0 | 32.501 | 30.59 | 185.137 | 7.64 | 173.928 | 2127.62 | 26.02 | 46.269 | 6.36 | 1.348 | 4.662 | 8404.56 | 1.958 | 97.8 | 77.6 | 1382 | 23.09 | 5463 | 2884.9 | 2779.7 | 4127 | 1193.4 | 0.68038 | 6.009
2024-12-09 | 16:25 | Data | 0 | 32.899 | 30.766 | 185.272 | 7.64 | 174.109 | 2125.81 | 26.02 | 46.269 | 6.36 | 1.342 | 4.656 | 8418.13 | 2.066 | 97.8 | 77.6 | 1382 | 23.18 | 5471.8 | 2872.9 | 2792.6 | 4126.5 | 1193.4 | 0.67994 | 6
2024-12-09 | 16:25 | Data | 0 | 32.339 | 30.624 | 185.137 | 7.64 | 174.018 | 2125.81 | 26.01 | 46.45 | 6.36 | 1.34 | 4.638 | 8409.08 | 1.803 | 97.8 | 77.6 | 1382 | 23.22 | 5465.9 | 2892.6 | 2821.3 | 4156.3 | 1193.4 | 0.67931 | 5.979
2024-12-09 | 16:25 | Data | 0 | 32.501 | 30.644 | 185.091 | 7.64 | 173.837 | 2123.1 | 26.03 | 46.45 | 6.35 | 1.352 | 4.654 | 8422.65 | 1.965 | 97.8 | 77.5 | 1380 | 23.22 | 5474.7 | 2881.9 | 2795.7 | 4141.7 | 1193.4 | 0.6783 | 6.006
2024-12-09 | 16:25 | Data | 0 | 32.487 | 30.644 | 185.137 | 7.64 | 173.928 | 2124.91 | 26.02 | 46.179 | 6.36 | 1.339 | 4.628 | 8458.83 | 2.059 | 97.8 | 77.5 | 1381 | 23.09 | 5498.2 | 2860.6 | 2774 | 4104.6 | 1193.4 | 0.68081 | 5.969
2024-12-09 | 16:25 | Data | 0 | 32.615 | 30.921 | 185.318 | 7.64 | 173.973 | 2126.72 | 26.02 | 46.54 | 6.36 | 1.339 | 4.638 | 8445.26 | 1.958 | 97.8 | 77.6 | 1381 | 23.27 | 5489.4 | 2885.7 | 2800.7 | 4141.9 | 1193.4 | 0.67942 | 5.977
2024-12-09 | 16:25 | Data | 0 | 32.946 | 30.658 | 185.318 | 7.64 | 174.063 | 2129.43 | 26.02 | 46.269 | 6.36 | 1.343 | 4.642 | 8458.83 | 1.998 | 97.8 | 77.6 | 1384 | 23.13 | 5498.2 | 2902.7 | 2817 | 4159.9 | 1193.5 | 0.67922 | 5.985
2024-12-09 | 16:25 | Data | 0 | 32.42 | 30.421 | 185.272 | 7.64 | 174.018 | 2129.43 | 26.02 | 46.269 | 6.36 | 1.34 | 4.675 | 8454.3 | 1.863 | 97.8 | 77.7 | 1384 | 23.09 | 5495.3 | 2874.9 | 2788.7 | 4128.1 | 1193.5 | 0.68011 | 6.016
2024-12-09 | 16:25 | Data | 0 | 32.521 | 30.536 | 185.137 | 7.64 | 173.837 | 2125.81 | 26.02 | 46.45 | 6.36 | 1.338 | 4.653 | 8418.13 | 2.079 | 97.8 | 77.7 | 1382 | 23.27 | 5471.8 | 2881 | 2810.6 | 4145 | 1193.5 | 0.67789 | 5.991
2024-12-09 | 16:25 | Data | 0 | 32.723 | 30.543 | 185.227 | 7.64 | 174.018 | 2125.81 | 26.02 | 46.45 | 6.36 | 1.34 | 4.662 | 8418.13 | 1.971 | 97.8 | 77.7 | 1382 | 23.22 | 5471.8 | 2897.4 | 2807.7 | 4148.7 | 1193.5 | 0.6809 | 5.999
2024-12-09 | 16:26 | Data | 0 | 32.609 | 30.651 | 185.182 | 7.64 | 173.973 | 2124.01 | 26.02 | 46.179 | 6.36 | 1.353 | 4.643 | 8445.26 | 1.904 | 97.8 | 77.4 | 1381 | 23.09 | 5489.4 | 2885.7 | 2803.4 | 4144.3 | 1193.5 | 0.68194 | 5.995
2024-12-09 | 16:26 | Data | 0 | 32.278 | 30.415 | 185.046 | 7.64 | 173.928 | 2123.1 | 26.02 | 46.269 | 6.35 | 1.344 | 4.654 | 8427.17 | 1.971 | 97.8 | 77.6 | 1380 | 23.04 | 5477.7 | 2907.5 | 2812.6 | 4159.6 | 1193.5 | 0.68281 | 5.997
2024-12-09 | 16:26 | Data | 0 | 32.723 | 30.664 | 185.227 | 7.64 | 174.063 | 2124.91 | 26.02 | 46.269 | 6.35 | 1.342 | 4.653 | 8431.69 | 2.046 | 97.8 | 77.6 | 1382 | 23.13 | 5480.6 | 2892.3 | 2793 | 4143.1 | 1193.5 | 0.68091 | 5.994
2024-12-09 | 16:26 | Data | 0 | 32.494 | 30.84 | 185.318 | 7.64 | 173.973 | 2129.43 | 26.02 | 46.269 | 6.36 | 1.336 | 4.638 | 8427.17 | 1.816 | 97.8 | 77.6 | 1385 | 23.13 | 5477.7 | 2882.8 | 2796.5 | 4132.2 | 1193.5 | 0.68098 | 5.974
2024-12-09 | 16:26 | Data | 0 | 32.717 | 30.766 | 185.091 | 7.64 | 173.837 | 2125.81 | 25.99 | 46.179 | 6.36 | 1.344 | 4.629 | 8445.26 | 2.073 | 97.8 | 77.5 | 1382 | 23.13 | 5489.4 | 2882.8 | 2796.4 | 4135.5 | 1193.5 | 0.68102 | 5.973
2024-12-09 | 16:26 | Data | 0 | 32.271 | 30.752 | 185.137 | 7.64 | 173.928 | 2124.91 | 26.02 | 46.179 | 6.35 | 1.346 | 4.635 | 8440.74 | 2.066 | 97.8 | 77.5 | 1381 | 23.13 | 5486.5 | 2893.1 | 2796.4 | 4140.4 | 1193.5 | 0.68195 | 5.98
2024-12-09 | 16:26 | Data | 0 | 32.865 | 30.475 | 185.318 | 7.64 | 174.109 | 2123.1 | 26.02 | 46.089 | 6.35 | 1.339 | 4.636 | 8490.48 | 1.708 | 97.8 | 77.6 | 1380 | 23.09 | 5518.8 | 2870.6 | 2804.9 | 4133.1 | 1193.5 | 0.67807 | 5.975
2024-12-09 | 16:26 | Data | 0 | 32.494 | 30.759 | 185.182 | 7.64 | 174.018 | 2122.2 | 26.02 | 46.359 | 6.35 | 1.336 | 4.634 | 8481.44 | 2.032 | 97.8 | 77.6 | 1380 | 23.18 | 5512.9 | 2865.6 | 2781.6 | 4112 | 1193.5 | 0.68013 | 5.969
2024-12-09 | 16:26 | Data | 0 | 32.494 | 30.421 | 185.091 | 7.64 | 173.837 | 2119.49 | 26.02 | 46.269 | 6.36 | 1.34 | 4.637 | 8481.44 | 2.052 | 97.8 | 77.6 | 1379 | 23.13 | 5512.9 | 2874.5 | 2816.8 | 4144.9 | 1193.5 | 0.67824 | 5.978
2024-12-09 | 16:26 | Data | 0 | 32.615 | 30.901 | 185.227 | 7.64 | 173.973 | 2122.2 | 26.02 | 46.359 | 6.36 | 1.343 | 4.622 | 8481.44 | 1.924 | 97.8 | 77.5 | 1378 | 23.13 | 5512.9 | 2888.9 | 2794 | 4138.9 | 1193.5 | 0.68097 | 5.964
2024-12-09 | 16:26 | Data | 0 | 32.723 | 30.529 | 185.137 | 7.64 | 174.018 | 2122.2 | 26.02 | 46.359 | 6.35 | 1.344 | 4.654 | 8485.96 | 1.958 | 97.8 | 77.6 | 1379 | 23.09 | 5515.9 | 2874.3 | 2809.2 | 4139.9 | 1193.5 | 0.67747 | 5.997
2024-12-09 | 16:26 | Data | 0 | 32.285 | 30.415 | 185.182 | 7.64 | 174.018 | 2124.01 | 26.02 | 46.45 | 6.35 | 1.344 | 4.659 | 8481.44 | 1.971 | 97.8 | 77.6 | 1380 | 23.27 | 5512.9 | 2904.5 | 2811.8 | 4157.2 | 1193.5 | 0.68276 | 6.003
2024-12-09 | 16:26 | Data | 0 | 32.771 | 30.651 | 185.182 | 7.64 | 173.973 | 2122.2 | 26.02 | 46.269 | 6.36 | 1.34 | 4.643 | 8476.91 | 1.904 | 97.8 | 77.6 | 1379 | 23.13 | 5510 | 2907.4 | 2827.1 | 4172 | 1193.5 | 0.68232 | 5.984
2024-12-09 | 16:26 | Data | 0 | 32.494 | 30.59 | 185.046 | 7.64 | 173.928 | 2117.68 | 26.03 | 46.179 | 6.36 | 1.348 | 4.641 | 8458.83 | 2.079 | 97.8 | 77.5 | 1376 | 23.04 | 5498.2 | 2889.9 | 2796.6 | 4139.4 | 1193.5 | 0.68084 | 5.988
2024-12-09 | 16:26 | Data | 0 | 32.818 | 30.604 | 185.272 | 7.64 | 174.018 | 2123.1 | 26.02 | 46.179 | 6.35 | 1.348 | 4.643 | 8472.39 | 2.167 | 97.8 | 77.5 | 1379 | 23.09 | 5507.1 | 2877.1 | 2801.7 | 4138.4 | 1193.5 | 0.67956 | 5.988
2024-12-09 | 16:26 | Data | 0 | 32.723 | 30.651 | 185.182 | 7.64 | 174.018 | 2125.81 | 26.02 | 46.54 | 6.36 | 1.339 | 4.669 | 8440.74 | 1.958 | 97.8 | 77.7 | 1382 | 23.22 | 5486.5 | 2888.4 | 2819.5 | 4157.4 | 1193.5 | 0.67791 | 6.008
2024-12-09 | 16:26 | Data | 0 | 32.487 | 30.523 | 185.182 | 7.64 | 173.928 | 2125.81 | 26.02 | 46.54 | 6.36 | 1.34 | 4.656 | 8445.26 | 1.877 | 97.8 | 77.6 | 1382 | 23.27 | 5489.4 | 2876.7 | 2810.4 | 4142.3 | 1193.5 | 0.67787 | 5.996
2024-12-09 | 16:27 | Data | 0 | 32.831 | 30.482 | 185.091 | 7.64 | 174.018 | 2123.1 | 26.03 | 46.54 | 6.36 | 1.348 | 4.665 | 8454.3 | 2.073 | 97.8 | 77.6 | 1380 | 23.27 | 5495.3 | 2894.9 | 2810.4 | 4153 | 1193.5 | 0.68125 | 6.011
2024-12-09 | 16:27 | Data | 0 | 32.426 | 30.752 | 185.272 | 7.64 | 174.063 | 2123.1 | 26.02 | 46.45 | 6.35 | 1.345 | 4.665 | 8472.39 | 1.776 | 97.8 | 77.6 | 1380 | 23.22 | 5507.1 | 2890.3 | 2800.1 | 4139.7 | 1193.5 | 0.68178 | 6.01
2024-12-09 | 16:27 | Data | 0 | 32.636 | 30.428 | 185.137 | 7.64 | 174.063 | 2123.1 | 26.02 | 46.54 | 6.36 | 1.335 | 4.67 | 8445.26 | 1.924 | 97.8 | 77.8 | 1380 | 23.27 | 5489.4 | 2886.2 | 2814.3 | 4149.4 | 1193.5 | 0.67907 | 6.006
2024-12-09 | 16:27 | Data | 0 | 32.494 | 30.59 | 185.046 | 7.64 | 173.837 | 2124.91 | 26.02 | 46.54 | 6.36 | 1.338 | 4.636 | 8445.26 | 1.958 | 97.8 | 77.6 | 1381 | 23.22 | 5489.4 | 2869.2 | 2815.4 | 4139.9 | 1193.5 | 0.67585 | 5.973
2024-12-09 | 16:27 | Data | 0 | 32.44 | 30.847 | 185.137 | 7.64 | 173.973 | 2124.91 | 26.02 | 46.269 | 6.35 | 1.345 | 4.63 | 8458.83 | 2.025 | 97.8 | 77.5 | 1382 | 23.18 | 5498.2 | 2882.3 | 2811 | 4144.2 | 1193.5 | 0.68012 | 5.974
2024-12-09 | 16:27 | Data | 0 | 32.636 | 30.428 | 185.091 | 7.64 | 173.973 | 2124.01 | 26.02 | 46.45 | 6.36 | 1.349 | 4.628 | 8449.78 | 1.904 | 97.8 | 77.4 | 1379 | 23.27 | 5492.4 | 2891.8 | 2837 | 4169.3 | 1193.5 | 0.67784 | 5.977
2024-12-09 | 16:27 | Data | 0 | 32.946 | 30.968 | 185.091 | 7.64 | 174.018 | 2123.1 | 26.02 | 46.45 | 6.35 | 1.341 | 4.618 | 8440.74 | 2.181 | 97.8 | 77.5 | 1381 | 23.18 | 5486.5 | 2882.9 | 2810.5 | 4147.3 | 1193.5 | 0.67784 | 5.959
2024-12-09 | 16:27 | Data | 0 | 32.345 | 30.415 | 185.137 | 7.64 | 173.973 | 2123.1 | 26.02 | 46.45 | 6.35 | 1.332 | 4.659 | 8445.26 | 1.857 | 97.8 | 77.8 | 1380 | 23.22 | 5489.4 | 2891.9 | 2825.8 | 4161.6 | 1193.5 | 0.67767 | 5.991
2024-12-09 | 16:27 | Data | 0 | 32.305 | 30.617 | 185.137 | 7.64 | 174.018 | 2122.2 | 26.02 | 46.45 | 6.36 | 1.342 | 4.685 | 8436.21 | 2.16 | 97.8 | 77.7 | 1379 | 23.22 | 5483.5 | 2874.6 | 2807.9 | 4138.5 | 1193.5 | 0.67714 | 6.028
2024-12-09 | 16:27 | Data | 0 | 32.946 | 30.55 | 185.227 | 7.64 | 174.109 | 2112.26 | 26.01 | 46.45 | 6.36 | 1.348 | 4.65 | 8440.74 | 2.228 | 97.8 | 77.5 | 1374 | 23.22 | 5486.5 | 2899.1 | 2805.6 | 4148 | 1193.5 | 0.68225 | 5.998
2024-12-09 | 16:27 | Data | 0 | 32.831 | 30.509 | 185.272 | 7.64 | 174.063 | 2119.49 | 26.02 | 46.45 | 6.35 | 1.348 | 4.657 | 8454.3 | 2.154 | 97.8 | 77.6 | 1378 | 23.22 | 5495.3 | 2902.9 | 2816.1 | 4163.1 | 1193.5 | 0.67893 | 6.007
2024-12-09 | 16:27 | Data | 0 | 32.609 | 30.421 | 185.272 | 7.64 | 174.063 | 2120.39 | 26.01 | 46.54 | 6.35 | 1.342 | 4.635 | 8454.3 | 2.079 | 97.8 | 77.6 | 1378 | 23.22 | 5495.3 | 2882.8 | 2842.1 | 4174.2 | 1193.5 | 0.67547 | 5.979
2024-12-09 | 16:27 | Data | 0 | 32.399 | 30.955 | 185.272 | 7.64 | 174.109 | 2119.49 | 26.02 | 46.54 | 6.36 | 1.346 | 4.626 | 8454.3 | 1.742 | 97.8 | 77.5 | 1378 | 23.27 | 5495.3 | 2885.6 | 2837.1 | 4164.5 | 1193.5 | 0.67477 | 5.973
2024-12-09 | 16:27 | Data | 0 | 32.696 | 30.435 | 185.227 | 7.64 | 173.973 | 2120.39 | 26.02 | 46.54 | 6.36 | 1.344 | 4.628 | 8431.69 | 2.221 | 97.8 | 77.5 | 1378 | 23.27 | 5480.6 | 2888.9 | 2850.4 | 4174.8 | 1193.5 | 0.67588 | 5.972
2024-12-09 | 16:27 | Data | 0 | 33.108 | 30.887 | 185.272 | 7.64 | 173.928 | 2117.68 | 26.02 | 46.45 | 6.36 | 1.342 | 4.642 | 8427.17 | 2.093 | 97.8 | 77.6 | 1377 | 23.22 | 5477.7 | 2887.7 | 2820.8 | 4157.2 | 1193.5 | 0.67776 | 5.983
2024-12-09 | 16:27 | Data | 0 | 32.946 | 30.705 | 185.318 | 7.64 | 174.063 | 2117.68 | 26.03 | 46.45 | 6.35 | 1.336 | 4.652 | 8440.74 | 2.073 | 97.8 | 77.7 | 1376 | 23.22 | 5486.5 | 2898.6 | 2816.2 | 4160.2 | 1193.5 | 0.67974 | 5.988
2024-12-09 | 16:27 | Data | 0 | 32.494 | 30.624 | 185.182 | 7.64 | 173.928 | 2117.68 | 26.03 | 46.45 | 6.35 | 1.342 | 4.637 | 8427.17 | 2.154 | 97.8 | 77.6 | 1376 | 23.22 | 5477.7 | 2883.4 | 2817.5 | 4151.2 | 1193.6 | 0.67669 | 5.979
2024-12-09 | 16:27 | Data | 0 | 32.494 | 30.442 | 185.227 | 7.64 | 173.973 | 2117.68 | 26.01 | 46.45 | 6.36 | 1.345 | 4.654 | 8440.74 | 2.093 | 97.8 | 77.6 | 1376 | 23.27 | 5486.5 | 2884.3 | 2835.2 | 4164.5 | 1193.6 | 0.67447 | 5.999
2024-12-09 | 16:28 | Data | 0 | 32.953 | 30.712 | 185.363 | 7.64 | 174.063 | 2114.06 | 26.01 | 46.54 | 6.35 | 1.336 | 4.646 | 8454.3 | 2.046 | 97.8 | 77.7 | 1374 | 23.27 | 5495.3 | 2881.7 | 2821.1 | 4158.4 | 1193.6 | 0.67518 | 5.981
2024-12-09 | 16:28 | Data | 0 | 32.528 | 30.421 | 185.182 | 7.64 | 174.063 | 2108.64 | 26.02 | 46.54 | 6.36 | 1.343 | 4.645 | 8467.87 | 2.073 | 97.8 | 77.6 | 1371 | 23.22 | 5504.1 | 2884.5 | 2840.6 | 4168 | 1193.6 | 0.67586 | 5.988
2024-12-09 | 16:28 | Data | 0 | 32.501 | 30.644 | 185.182 | 7.64 | 173.973 | 2105.93 | 26.02 | 46.54 | 6.37 | 1.351 | 4.633 | 8458.83 | 2.025 | 97.8 | 77.4 | 1369 | 23.27 | 5498.2 | 2883.3 | 2829.1 | 4156.9 | 1193.6 | 0.67884 | 5.984
2024-12-09 | 16:28 | Data | 0 | 32.858 | 30.658 | 185.318 | 7.64 | 174.063 | 2112.26 | 26.02 | 46.45 | 6.36 | 1.345 | 4.624 | 8458.83 | 1.884 | 97.8 | 77.5 | 1372 | 23.22 | 5498.2 | 2890.3 | 2824.4 | 4158.3 | 1193.6 | 0.67908 | 5.968
2024-12-09 | 16:28 | Data | 0 | 32.669 | 30.664 | 185.137 | 7.64 | 173.973 | 2111.35 | 26.02 | 46.54 | 6.35 | 1.337 | 4.672 | 8467.87 | 1.992 | 97.8 | 77.8 | 1372 | 23.22 | 5504.1 | 2889.4 | 2803.1 | 4144.4 | 1193.6 | 0.68094 | 6.01
2024-12-09 | 16:28 | Data | 0 | 32.609 | 30.651 | 185.227 | 7.64 | 173.973 | 2109.54 | 26.01 | 46.359 | 6.35 | 1.342 | 4.655 | 8467.87 | 2.059 | 97.8 | 77.6 | 1371 | 23.18 | 5504.1 | 2884.7 | 2808.4 | 4145 | 1193.6 | 0.67934 | 5.997
2024-12-09 | 16:28 | Data | 0 | 32.98 | 30.664 | 185.363 | 7.64 | 174.063 | 2111.35 | 26.02 | 46.45 | 6.36 | 1.345 | 4.648 | 8458.83 | 1.978 | 97.8 | 77.6 | 1372 | 23.27 | 5498.2 | 2893.5 | 2819.8 | 4155.3 | 1193.6 | 0.68092 | 5.993
2024-12-09 | 16:28 | Data | 0 | 32.426 | 30.469 | 185.408 | 7.64 | 173.973 | 2112.26 | 26.02 | 46.54 | 6.35 | 1.339 | 4.657 | 8472.39 | 1.688 | 97.8 | 77.7 | 1374 | 23.27 | 5507.1 | 2870.4 | 2791.7 | 4126.4 | 1193.6 | 0.67817 | 5.995
2024-12-09 | 16:28 | Data | 0 | 32.994 | 30.448 | 185.182 | 7.64 | 174.109 | 2111.35 | 26.02 | 46.54 | 6.36 | 1.346 | 4.641 | 8445.26 | 2.1 | 97.8 | 77.5 | 1373 | 23.27 | 5489.4 | 2876.8 | 2793.8 | 4130 | 1193.6 | 0.68007 | 5.987
2024-12-09 | 16:28 | Data | 0 | 32.447 | 30.536 | 185.091 | 7.64 | 173.973 | 2111.35 | 26.02 | 46.45 | 6.36 | 1.334 | 4.653 | 8458.83 | 2.181 | 97.8 | 77.7 | 1372 | 23.27 | 5498.2 | 2879.8 | 2810.7 | 4141.9 | 1193.6 | 0.67825 | 5.984
2024-12-09 | 16:28 | Data | 0 | 32.609 | 30.84 | 185.227 | 7.64 | 174.018 | 2112.26 | 26.02 | 46.54 | 6.36 | 1.331 | 4.664 | 8458.83 | 1.87 | 97.8 | 77.8 | 1372 | 23.22 | 5498.2 | 2882.7 | 2797.8 | 4137.5 | 1193.6 | 0.68093 | 5.995
2024-12-09 | 16:28 | Data | 0 | 32.94 | 30.543 | 185.272 | 7.64 | 174.199 | 2113.16 | 26.02 | 46.54 | 6.36 | 1.331 | 4.656 | 8422.65 | 1.998 | 97.8 | 77.8 | 1373 | 23.22 | 5474.7 | 2891.7 | 2827.5 | 4162.1 | 1193.6 | 0.6758 | 5.988
2024-12-09 | 16:28 | Data | 0 | 32.811 | 30.658 | 185.227 | 7.64 | 174.018 | 2114.06 | 26.01 | 46.54 | 6.36 | 1.336 | 4.631 | 8418.13 | 2.12 | 97.8 | 77.6 | 1374 | 23.27 | 5471.8 | 2897.1 | 2803.7 | 4149.4 | 1193.6 | 0.68128 | 5.965
2024-12-09 | 16:28 | Data | 0 | 32.602 | 30.975 | 185.182 | 7.64 | 173.928 | 2114.97 | 26.02 | 46.45 | 6.36 | 1.342 | 4.635 | 8418.13 | 1.904 | 97.8 | 77.5 | 1374 | 23.27 | 5471.8 | 2893.9 | 2812.4 | 4156 | 1193.6 | 0.67911 | 5.977
2024-12-09 | 16:28 | Data | 0 | 32.507 | 30.415 | 185.091 | 7.64 | 173.973 | 2114.97 | 26.01 | 46.54 | 6.35 | 1.334 | 4.635 | 8418.13 | 2.079 | 97.8 | 77.7 | 1375 | 23.27 | 5471.8 | 2870.7 | 2823.7 | 4148.7 | 1193.6 | 0.67548 | 5.969
2024-12-09 | 16:28 | Data | 0 | 32.771 | 30.968 | 185.227 | 7.64 | 174.018 | 2236.08 | 26.02 | 46.45 | 6.36 | 1.337 | 4.64 | 8449.78 | 1.958 | 97.9 | 77.6 | 1453 | 23.22 | 5492.4 | 2885.5 | 2842.4 | 4170.9 | 1193.6 | 0.67342 | 5.976
2024-12-09 | 16:28 | Data | 0 | 32.528 | 30.442 | 185.137 | 7.64 | 174.063 | 2067.97 | 26.02 | 46.54 | 6.36 | 1.338 | 4.672 | 8467.87 | 2.025 | 97.8 | 77.7 | 1344 | 23.27 | 5504.1 | 2892.1 | 2823.4 | 4161.6 | 1193.6 | 0.67875 | 6.01
2024-12-09 | 16:28 | Data | 0 | 32.717 | 30.543 | 185.272 | 7.64 | 174.018 | 2065.26 | 26.03 | 46.45 | 6.35 | 1.341 | 4.668 | 8467.87 | 2.052 | 97.7 | 77.7 | 1342 | 23.27 | 5504.1 | 2884.6 | 2831.1 | 4159.2 | 1193.6 | 0.67828 | 6.009
2024-12-09 | 16:29 | Data | 0 | 32.318 | 30.651 | 185.272 | 7.64 | 174.063 | 2067.97 | 26.01 | 46.54 | 6.35 | 1.344 | 4.659 | 8467.87 | 2.005 | 97.8 | 77.6 | 1345 | 23.22 | 5504.1 | 2894.9 | 2843.5 | 4175.7 | 1193.6 | 0.67758 | 6.002
2024-12-09 | 16:29 | Data | 0 | 32.703 | 30.745 | 185.182 | 7.64 | 174.018 | 2070.68 | 26.02 | 46.359 | 6.35 | 1.343 | 4.647 | 8449.78 | 1.917 | 97.8 | 77.6 | 1346 | 23.27 | 5492.4 | 2879.8 | 2850.3 | 4170.3 | 1193.6 | 0.6729 | 5.989
2024-12-09 | 16:29 | Data | 0 | 32.528 | 30.597 | 185.001 | 7.64 | 173.973 | 2073.39 | 25.99 | 46.54 | 6.35 | 1.344 | 4.65 | 8440.74 | 1.816 | 97.8 | 77.6 | 1348 | 23.22 | 5486.5 | 2874.8 | 2817.4 | 4144.7 | 1193.6 | 0.67716 | 5.993
2024-12-09 | 16:29 | Data | 0 | 32.946 | 30.88 | 185.408 | 7.64 | 174.109 | 2075.2 | 26.02 | 46.54 | 6.36 | 1.345 | 4.643 | 8440.74 | 1.958 | 97.8 | 77.5 | 1349 | 23.27 | 5486.5 | 2882 | 2835.9 | 4160.2 | 1193.6 | 0.67456 | 5.988
2024-12-09 | 16:29 | Data | 0 | 32.514 | 30.968 | 185.227 | 7.64 | 174.109 | 2078.81 | 26.01 | 46.45 | 6.36 | 1.342 | 4.662 | 8440.74 | 1.843 | 97.8 | 77.6 | 1351 | 23.22 | 5486.5 | 2889.1 | 2820.3 | 4156.7 | 1193.6 | 0.6773 | 6.004
2024-12-09 | 16:29 | Data | 0 | 32.514 | 30.475 | 185.318 | 7.64 | 174.109 | 2082.43 | 26.03 | 46.54 | 6.36 | 1.342 | 4.664 | 8440.74 | 1.836 | 97.8 | 77.6 | 1353 | 23.27 | 5486.5 | 2877.2 | 2827.1 | 4154.2 | 1193.6 | 0.67614 | 6.007
2024-12-09 | 16:29 | Data | 0 | 32.494 | 30.421 | 185.182 | 7.64 | 173.973 | 2084.24 | 26.02 | 46.45 | 6.36 | 1.338 | 4.666 | 8422.65 | 2.066 | 97.8 | 77.7 | 1355 | 23.27 | 5474.7 | 2877.5 | 2839.8 | 4163 | 1193.6 | 0.67504 | 6.004
2024-12-09 | 16:29 | Data | 0 | 32.514 | 30.442 | 185.272 | 7.64 | 174.063 | 2085.14 | 26.02 | 46.45 | 6.35 | 1.34 | 4.66 | 8409.08 | 2.025 | 97.8 | 77.7 | 1356 | 23.22 | 5465.9 | 2894.9 | 2849.2 | 4180.1 | 1193.6 | 0.67671 | 5.999
2024-12-09 | 16:29 | Data | 0 | 32.737 | 30.826 | 185.227 | 7.64 | 174.018 | 2089.66 | 26.02 | 46.54 | 6.35 | 1.334 | 4.673 | 8418.13 | 2.073 | 97.8 | 77.8 | 1358 | 23.22 | 5471.8 | 2898.3 | 2827 | 4170.1 | 1193.6 | 0.67711 | 6.008
2024-12-09 | 16:29 | Data | 0 | 32.717 | 30.563 | 185.182 | 7.64 | 174.018 | 2092.37 | 26.02 | 46.54 | 6.35 | 1.339 | 4.642 | 8549.27 | 2.073 | 97.8 | 77.6 | 1360 | 23.22 | 5557 | 2882.6 | 2808.6 | 4140.5 | 1193.6 | 0.67897 | 5.984
2024-12-09 | 16:29 | Data | 0 | 32.737 | 30.766 | 185.318 | 7.64 | 174.154 | 2094.18 | 26.01 | 46.45 | 6.36 | 1.348 | 4.622 | 8644.24 | 1.85 | 97.8 | 77.4 | 1362 | 23.27 | 5618.8 | 2883.3 | 2815.2 | 4152 | 1193.6 | 0.67823 | 5.968
2024-12-09 | 16:29 | Data | 0 | 32.723 | 30.651 | 185.318 | 7.64 | 174.063 | 2098.7 | 26.02 | 46.54 | 6.35 | 1.343 | 4.657 | 8630.67 | 1.87 | 97.8 | 77.6 | 1365 | 23.27 | 5609.9 | 2882.2 | 2809.4 | 4143.1 | 1193.6 | 0.67834 | 5.999
2024-12-09 | 16:29 | Data | 0 | 32.609 | 30.658 | 185.272 | 7.64 | 174.063 | 2104.12 | 26.01 | 46.179 | 6.35 | 1.346 | 4.673 | 8635.19 | 2.046 | 97.8 | 77.7 | 1367 | 23.13 | 5612.9 | 2868 | 2814.5 | 4139 | 1193.6 | 0.67609 | 6.017
2024-12-09 | 16:29 | Data | 0 | 32.44 | 30.624 | 185.227 | 7.64 | 174.063 | 2105.93 | 26.02 | 46.269 | 6.36 | 1.34 | 4.662 | 8535.7 | 1.89 | 97.8 | 77.7 | 1369 | 23.09 | 5548.2 | 2880.4 | 2804.7 | 4138.6 | 1193.6 | 0.68072 | 6.002
2024-12-09 | 16:29 | Data | 0 | 32.804 | 30.658 | 185.408 | 7.64 | 174.109 | 2109.54 | 26.02 | 46.269 | 6.35 | 1.342 | 4.639 | 8454.3 | 1.762 | 97.8 | 77.6 | 1371 | 23.09 | 5495.3 | 2869.2 | 2823.6 | 4143.6 | 1193.6 | 0.67606 | 5.981
2024-12-09 | 16:29 | Data | 0 | 32.723 | 31.069 | 185.363 | 7.64 | 174.109 | 2108.64 | 26.05 | 46.269 | 6.36 | 1.351 | 4.676 | 8445.26 | 1.877 | 97.8 | 77.6 | 1371 | 23.18 | 5489.4 | 2883 | 2828.5 | 4158.8 | 1193.6 | 0.67757 | 6.028
2024-12-09 | 16:29 | Data | 0 | 32.777 | 30.428 | 185.318 | 7.64 | 174.063 | 2109.54 | 26.02 | 46.179 | 6.35 | 1.343 | 4.642 | 8445.26 | 2.079 | 97.8 | 77.6 | 1371 | 23.13 | 5489.4 | 2883.9 | 2791.5 | 4135.7 | 1193.7 | 0.68088 | 5.985
2024-12-09 | 16:29 | Data | 0 | 32.696 | 30.651 | 185.182 | 7.64 | 173.973 | 2117.68 | 26.02 | 46.269 | 6.35 | 1.335 | 4.648 | 8458.83 | 2.066 | 97.8 | 77.7 | 1376 | 23.09 | 5498.2 | 2900 | 2786.8 | 4139.1 | 1193.7 | 0.68458 | 5.983
2024-12-09 | 16:30 | Data | 0 | 32.723 | 30.752 | 185.318 | 7.64 | 174.109 | 2120.39 | 26.03 | 46.269 | 6.36 | 1.326 | 4.638 | 8454.3 | 1.87 | 97.8 | 77.8 | 1378 | 23.13 | 5495.3 | 2904 | 2820.5 | 4165.8 | 1193.7 | 0.6809 | 5.965
2024-12-09 | 16:30 | Data | 0 | 32.501 | 30.651 | 185.272 | 7.64 | 174.063 | 2121.29 | 26.03 | 46.269 | 6.36 | 1.329 | 4.658 | 8440.74 | 1.958 | 97.8 | 77.8 | 1378 | 23.09 | 5486.5 | 2885.7 | 2786.9 | 4130.6 | 1193.7 | 0.68266 | 5.989
2024-12-09 | 16:30 | Data | 0 | 32.919 | 30.853 | 185.318 | 7.64 | 174.109 | 2120.39 | 26.02 | 46.269 | 6.36 | 1.339 | 4.67 | 8454.3 | 2.12 | 97.8 | 77.7 | 1377 | 23.09 | 5495.3 | 2871.4 | 2791.5 | 4121.9 | 1193.7 | 0.68013 | 6.008
2024-12-09 | 16:30 | Data | 0 | 32.899 | 30.678 | 185.318 | 7.64 | 174.063 | 2121.29 | 26.01 | 46.179 | 6.36 | 1.346 | 4.632 | 8472.39 | 2.241 | 97.8 | 77.5 | 1378 | 23.09 | 5507.1 | 2890.7 | 2777.5 | 4130.4 | 1193.7 | 0.68211 | 5.977
2024-12-09 | 16:30 | Data | 0 | 32.609 | 30.415 | 185.227 | 7.64 | 174.109 | 2123.1 | 26.02 | 46.089 | 6.36 | 1.343 | 4.654 | 8481.44 | 2.275 | 97.8 | 77.6 | 1379 | 23.13 | 5512.9 | 2899 | 2787.7 | 4137.7 | 1193.7 | 0.68461 | 5.998
2024-12-09 | 16:30 | Data | 0 | 32.791 | 30.658 | 185.182 | 7.64 | 174.063 | 2123.1 | 26.02 | 46.359 | 6.36 | 1.332 | 4.601 | 8467.87 | 1.87 | 97.8 | 77.5 | 1380 | 23.13 | 5504.1 | 2884.6 | 2808.4 | 4148.4 | 1193.7 | 0.67848 | 5.933
2024-12-09 | 16:30 | Data | 0 | 32.494 | 30.644 | 185.589 | 7.64 | 174.335 | 2122.2 | 26.01 | 46.269 | 6.35 | 1.343 | 4.654 | 8481.44 | 1.85 | 97.8 | 77.6 | 1380 | 23.13 | 5512.9 | 2885.4 | 2807.8 | 4143.3 | 1193.7 | 0.68162 | 5.997
2024-12-09 | 16:30 | Data | 0 | 32.94 | 30.448 | 185.589 | 7.64 | 174.289 | 2120.39 | 26.02 | 46.269 | 6.35 | 1.348 | 4.67 | 8481.44 | 2.113 | 97.8 | 77.6 | 1378 | 23.09 | 5512.9 | 2893.5 | 2812.1 | 4153.6 | 1193.7 | 0.67933 | 6.017
2024-12-09 | 16:30 | Data | 0 | 32.663 | 30.428 | 185.498 | 7.64 | 174.289 | 2118.58 | 26.02 | 46.179 | 6.35 | 1.352 | 4.677 | 8440.74 | 2.16 | 97.8 | 77.6 | 1377 | 23.04 | 5486.5 | 2878.3 | 2818.1 | 4149.9 | 1193.7 | 0.67559 | 6.029
2024-12-09 | 16:30 | Data | 0 | 32.71 | 30.475 | 185.498 | 7.64 | 174.38 | 2117.68 | 26.02 | 46.179 | 6.35 | 1.33 | 4.693 | 8838.69 | 2.187 | 97.8 | 77.9 | 1376 | 23.09 | 5745.1 | 2881.2 | 2821.1 | 4151.6 | 1193.7 | 0.67686 | 6.024
2024-12-09 | 16:30 | Data | 0 | 32.723 | 30.651 | 185.589 | 7.64 | 174.335 | 2114.06 | 26.02 | 46.269 | 6.35 | 1.337 | 4.669 | 8400.04 | 2.073 | 97.8 | 77.7 | 1374 | 23.13 | 5460 | 2877.8 | 2821.5 | 4149.9 | 1193.7 | 0.67667 | 6.006
2024-12-09 | 16:30 | Data | 0 | 32.494 | 30.536 | 185.634 | 7.64 | 174.38 | 2114.97 | 26 | 46.089 | 6.35 | 1.347 | 4.654 | 8418.13 | 2.073 | 97.8 | 77.6 | 1374 | 23.04 | 5471.8 | 2890 | 2816.5 | 4151.9 | 1193.7 | 0.67869 | 5.999
2024-12-09 | 16:30 | Data | 0 | 32.494 | 30.415 | 185.589 | 7.64 | 174.38 | 2114.06 | 26.01 | 46.269 | 6.36 | 1.342 | 4.671 | 8400.04 | 2.079 | 97.8 | 77.7 | 1374 | 23.09 | 5460 | 2897.5 | 2794.6 | 4136.4 | 1193.7 | 0.68174 | 6.012
2024-12-09 | 16:30 | Data | 0 | 32.514 | 30.421 | 185.634 | 7.64 | 174.47 | 2114.97 | 26 | 46.179 | 6.35 | 1.337 | 4.639 | 8395.51 | 2.073 | 97.8 | 77.6 | 1375 | 23.13 | 5457.1 | 2880.4 | 2821.6 | 4149.3 | 1193.7 | 0.6787 | 5.976
2024-12-09 | 16:30 | Data | 0 | 32.507 | 30.644 | 185.589 | 7.64 | 174.244 | 2117.68 | 26.02 | 46.179 | 6.36 | 1.34 | 4.673 | 8395.51 | 1.985 | 97.8 | 77.7 | 1376 | 23.13 | 5457.1 | 2886.5 | 2790.5 | 4136.2 | 1193.7 | 0.68308 | 6.013
2024-12-09 | 16:30 | Data | 0 | 32.933 | 30.907 | 185.679 | 7.64 | 174.38 | 2117.68 | 26.02 | 46.45 | 6.35 | 1.342 | 4.663 | 8404.56 | 2.046 | 97.8 | 77.6 | 1376 | 23.22 | 5463 | 2880.4 | 2790.1 | 4130.6 | 1193.7 | 0.67988 | 6.005
2024-12-09 | 16:30 | Data | 0 | 32.568 | 30.651 | 185.589 | 7.64 | 174.38 | 2117.68 | 26.02 | 46.45 | 6.36 | 1.346 | 4.637 | 8422.65 | 1.85 | 97.8 | 77.5 | 1376 | 23.27 | 5474.7 | 2915.3 | 2810.3 | 4163.7 | 1193.7 | 0.68286 | 5.981
2024-12-09 | 16:31 | Data | 0 | 32.561 | 30.597 | 185.498 | 7.64 | 174.289 | 2118.58 | 26.02 | 46.63 | 6.35 | 1.348 | 4.624 | 8400.04 | 1.971 | 97.8 | 77.4 | 1376 | 23.22 | 5460 | 2882.9 | 2813.6 | 4146 | 1193.7 | 0.67882 | 5.975
2024-12-09 | 16:31 | Data | 0 | 32.98 | 30.496 | 185.679 | 7.64 | 174.425 | 2117.68 | 26.02 | 46.54 | 6.36 | 1.343 | 4.645 | 8400.04 | 2.147 | 97.8 | 77.6 | 1376 | 23.27 | 5460 | 2879.7 | 2813.3 | 4144.5 | 1193.7 | 0.67745 | 5.988
2024-12-09 | 16:31 | Data | 0 | 32.825 | 30.968 | 185.77 | 7.64 | 174.425 | 2119.49 | 26.02 | 46.54 | 6.35 | 1.331 | 4.647 | 8422.65 | 2.12 | 97.8 | 77.7 | 1378 | 23.22 | 5474.7 | 2883.6 | 2808.7 | 4140.7 | 1193.7 | 0.67641 | 5.979
2024-12-09 | 16:31 | Data | 0 | 32.723 | 30.82 | 185.453 | 7.64 | 174.289 | 2120.39 | 26.02 | 46.359 | 6.35 | 1.34 | 4.662 | 8386.47 | 1.904 | 97.8 | 77.7 | 1378 | 23.27 | 5451.2 | 2886 | 2820.4 | 4152.5 | 1193.7 | 0.67857 | 6.002
2024-12-09 | 16:31 | Data | 0 | 32.953 | 30.766 | 185.679 | 7.64 | 174.335 | 2118.58 | 26.02 | 46.45 | 6.36 | 1.345 | 4.663 | 8395.51 | 1.965 | 97.8 | 77.6 | 1378 | 23.27 | 5457.1 | 2874.5 | 2817.4 | 4144.8 | 1193.7 | 0.67744 | 6.007
2024-12-09 | 16:31 | Data | 0 | 32.723 | 30.475 | 185.498 | 7.64 | 174.335 | 2117.68 | 26.02 | 46.359 | 6.35 | 1.356 | 4.65 | 8395.51 | 2.073 | 97.8 | 77.4 | 1376 | 23.22 | 5457.1 | 2880.7 | 2812.5 | 4145.3 | 1193.7 | 0.67886 | 6.005
2024-12-09 | 16:31 | Data | 0 | 33.149 | 30.779 | 185.589 | 7.64 | 174.38 | 2123.1 | 26.01 | 46.54 | 6.35 | 1.354 | 4.68 | 8386.47 | 2.073 | 97.8 | 77.6 | 1380 | 23.22 | 5451.2 | 2879.7 | 2803.7 | 4137.3 | 1193.7 | 0.67899 | 6.034
2024-12-09 | 16:31 | Data | 0 | 32.521 | 30.428 | 185.498 | 7.64 | 174.289 | 2125.81 | 26.02 | 46.54 | 6.35 | 1.339 | 4.658 | 8422.65 | 2.167 | 97.8 | 77.7 | 1382 | 23.27 | 5474.7 | 2887.4 | 2798.1 | 4141.4 | 1193.7 | 0.68059 | 5.998
2024-12-09 | 16:31 | Data | 0 | 32.501 | 30.597 | 185.453 | 7.64 | 174.289 | 2125.81 | 26.03 | 46.45 | 6.36 | 1.351 | 4.646 | 8440.74 | 2.052 | 97.8 | 77.5 | 1382 | 23.13 | 5486.5 | 2888.6 | 2823.1 | 4158.5 | 1193.7 | 0.67905 | 5.998
2024-12-09 | 16:31 | Data | 0 | 32.804 | 30.644 | 185.589 | 7.64 | 174.335 | 2124.01 | 26.03 | 46.54 | 6.35 | 1.362 | 4.665 | 8431.69 | 2.086 | 97.8 | 77.4 | 1381 | 23.27 | 5480.6 | 2881.6 | 2844.6 | 4156.5 | 1193.7 | 0.67668 | 6.026
2024-12-09 | 16:31 | Data | 0 | 32.717 | 30.874 | 185.589 | 7.64 | 174.335 | 2124.01 | 26.02 | 46.179 | 6.36 | 1.354 | 4.641 | 8431.69 | 1.863 | 97.8 | 77.4 | 1381 | 23.04 | 5480.6 | 2886.4 | 2823.2 | 4156.8 | 1193.7 | 0.67837 | 5.994
2024-12-09 | 16:31 | Data | 0 | 32.717 | 30.644 | 185.634 | 7.64 | 174.335 | 2127.62 | 26.02 | 46.45 | 6.35 | 1.344 | 4.647 | 8422.65 | 1.904 | 97.8 | 77.6 | 1383 | 23.27 | 5474.7 | 2880.3 | 2809 | 4141.7 | 1193.7 | 0.67826 | 5.991
2024-12-09 | 16:31 | Data | 0 | 32.609 | 30.651 | 185.589 | 7.64 | 174.38 | 2129.43 | 26.02 | 46.63 | 6.35 | 1.341 | 4.656 | 8404.56 | 2.046 | 97.8 | 77.6 | 1384 | 23.27 | 5463 | 2894 | 2808.8 | 4151.7 | 1193.7 | 0.68235 | 5.998
2024-12-09 | 16:31 | Data | 0 | 32.609 | 30.651 | 185.498 | 7.64 | 174.335 | 2128.52 | 26.01 | 46.54 | 6.35 | 1.345 | 4.66 | 8422.65 | 2.025 | 97.8 | 77.6 | 1383 | 23.27 | 5474.7 | 2884.1 | 2796.2 | 4137.9 | 1193.7 | 0.68008 | 6.005
2024-12-09 | 16:31 | Data | 0 | 32.494 | 30.651 | 185.589 | 7.64 | 174.335 | 2127.62 | 26.02 | 46.269 | 6.35 | 1.346 | 4.654 | 8436.21 | 2.046 | 97.8 | 77.6 | 1384 | 23.13 | 5483.5 | 2882.3 | 2803.6 | 4141.4 | 1193.7 | 0.67935 | 6.001
2024-12-09 | 16:31 | Data | 0 | 33.034 | 30.664 | 185.679 | 7.64 | 174.38 | 2134.85 | 26.02 | 46.179 | 6.35 | 1.347 | 4.664 | 8440.74 | 1.965 | 97.8 | 77.6 | 1387 | 23.09 | 5486.5 | 2891.4 | 2803.5 | 4145.5 | 1193.7 | 0.68034 | 6.01
2024-12-09 | 16:31 | Data | 0 | 32.723 | 30.651 | 185.679 | 7.64 | 174.38 | 2133.95 | 26.03 | 46.269 | 6.35 | 1.342 | 4.655 | 8467.87 | 2.066 | 97.8 | 77.6 | 1388 | 23.09 | 5504.1 | 2880.1 | 2812.7 | 4144.9 | 1193.7 | 0.67922 | 5.996
2024-12-09 | 16:31 | Data | 0 | 32.723 | 30.651 | 185.453 | 7.64 | 174.335 | 2127.62 | 26.02 | 46.269 | 6.35 | 1.342 | 4.652 | 8463.35 | 2.073 | 97.8 | 77.6 | 1383 | 23.09 | 5501.2 | 2861.9 | 2835.4 | 4151.1 | 1193.7 | 0.67246 | 5.994
2024-12-09 | 16:32 | Data | 0 | 32.615 | 30.624 | 185.589 | 7.64 | 174.335 | 2128.52 | 26.02 | 46.54 | 6.35 | 1.342 | 4.665 | 8445.26 | 2.012 | 97.8 | 77.7 | 1384 | 23.27 | 5489.4 | 2874.7 | 2838.7 | 4156.9 | 1193.8 | 0.67523 | 6.007
2024-12-09 | 16:32 | Data | 0 | 32.501 | 30.651 | 185.589 | 7.64 | 174.38 | 2127.62 | 26.02 | 46.54 | 6.35 | 1.348 | 4.654 | 8427.17 | 2.046 | 97.8 | 77.5 | 1383 | 23.27 | 5477.7 | 2894.5 | 2850.8 | 4186.9 | 1193.8 | 0.67453 | 6.002
2024-12-09 | 16:32 | Data | 0 | 32.723 | 30.867 | 185.634 | 7.64 | 174.38 | 2128.52 | 26.02 | 46.45 | 6.35 | 1.352 | 4.643 | 8418.13 | 2.012 | 97.8 | 77.5 | 1384 | 23.27 | 5471.8 | 2892.9 | 2825.5 | 4161.8 | 1193.8 | 0.67722 | 5.997
2024-12-09 | 16:32 | Data | 0 | 32.723 | 30.705 | 185.589 | 7.64 | 174.38 | 2127.62 | 26.02 | 46.54 | 6.35 | 1.337 | 4.636 | 8427.17 | 1.958 | 97.8 | 77.6 | 1382 | 23.27 | 5477.7 | 2880.3 | 2827.2 | 4154.4 | 1193.8 | 0.67647 | 5.971
2024-12-09 | 16:32 | Data | 0 | 32.892 | 30.988 | 185.725 | 7.64 | 174.47 | 2125.81 | 26.02 | 46.359 | 6.35 | 1.344 | 4.632 | 8431.69 | 2.073 | 97.8 | 77.5 | 1382 | 23.22 | 5480.6 | 2887.7 | 2825.7 | 4160.8 | 1193.8 | 0.67644 | 5.976
2024-12-09 | 16:32 | Data | 0 | 32.723 | 30.651 | 185.498 | 7.64 | 174.38 | 2125.81 | 26.01 | 46.45 | 6.35 | 1.349 | 4.653 | 8463.35 | 2.073 | 97.8 | 77.5 | 1381 | 23.22 | 5501.2 | 2882.3 | 2815.2 | 4150.4 | 1193.8 | 0.67799 | 6.001
2024-12-09 | 16:32 | Data | 0 | 32.717 | 30.658 | 185.77 | 7.64 | 174.38 | 2124.91 | 26.02 | 46.54 | 6.35 | 1.349 | 4.653 | 8445.26 | 2.039 | 97.8 | 77.5 | 1381 | 23.22 | 5489.4 | 2899.5 | 2828.8 | 4170.1 | 1193.8 | 0.67888 | 6.001
2024-12-09 | 16:32 | Data | 0 | 32.723 | 30.793 | 185.679 | 7.64 | 174.425 | 2126.72 | 26.02 | 46.54 | 6.36 | 1.345 | 4.673 | 8445.26 | 2.221 | 97.8 | 77.6 | 1382 | 23.22 | 5489.4 | 2880.5 | 2804.6 | 4140.2 | 1193.8 | 0.67808 | 6.018
2024-12-09 | 16:32 | Data | 0 | 32.521 | 30.671 | 185.589 | 7.64 | 174.335 | 2124.91 | 26.03 | 46.54 | 6.36 | 1.348 | 4.667 | 8440.74 | 1.857 | 97.8 | 77.6 | 1381 | 23.27 | 5486.5 | 2865.1 | 2817 | 4138.5 | 1193.8 | 0.67528 | 6.015
2024-12-09 | 16:32 | Data | 0 | 32.831 | 30.658 | 185.634 | 7.64 | 174.38 | 2124.01 | 26.02 | 46.54 | 6.36 | 1.346 | 4.701 | 8445.26 | 2.147 | 97.8 | 77.7 | 1381 | 23.22 | 5489.4 | 2898.3 | 2813.5 | 4158.6 | 1193.8 | 0.68096 | 6.045
2024-12-09 | 16:32 | Data | 0 | 32.946 | 30.995 | 185.86 | 7.64 | 174.38 | 2122.2 | 26.02 | 46.54 | 6.36 | 1.343 | 4.677 | 8015.65 | 2.073 | 97.8 | 77.7 | 1379 | 23.22 | 5210.2 | 2883.3 | 2816.6 | 4149.6 | 1193.8 | 0.67837 | 6.02
2024-12-09 | 16:32 | Data | 0 | 32.636 | 30.543 | 185.498 | 7.64 | 174.38 | 2123.1 | 26.02 | 46.54 | 6.35 | 1.349 | 4.645 | 8445.26 | 2.086 | 97.8 | 77.5 | 1379 | 23.27 | 5489.4 | 2890.1 | 2823.6 | 4161 | 1193.8 | 0.6773 | 5.996
2024-12-09 | 16:32 | Data | 0 | 32.615 | 30.658 | 185.498 | 7.64 | 174.425 | 2122.2 | 26.03 | 46.359 | 6.36 | 1.342 | 4.689 | 8445.26 | 2.16 | 97.8 | 77.7 | 1379 | 23.22 | 5489.4 | 2891.9 | 2809.4 | 4151.1 | 1193.8 | 0.68049 | 6.031
2024-12-09 | 16:32 | Data | 0 | 32.953 | 30.651 | 185.815 | 7.64 | 174.47 | 2123.1 | 26.02 | 46.54 | 6.35 | 1.351 | 4.663 | 8431.69 | 2.093 | 97.8 | 77.5 | 1380 | 23.22 | 5480.6 | 2895.9 | 2797.2 | 4143.7 | 1193.8 | 0.68191 | 6.014
2024-12-09 | 16:32 | Data | 0 | 32.555 | 30.651 | 185.634 | 7.64 | 174.38 | 2123.1 | 26.02 | 46.54 | 6.36 | 1.348 | 4.654 | 8431.69 | 1.85 | 97.8 | 77.5 | 1380 | 23.22 | 5480.6 | 2894 | 2794.6 | 4140.9 | 1193.8 | 0.68083 | 6.002
2024-12-09 | 16:32 | Data | 0 | 32.717 | 30.536 | 185.453 | 7.64 | 174.244 | 2123.1 | 26.02 | 46.269 | 6.35 | 1.341 | 4.651 | 8440.74 | 2.066 | 97.8 | 77.6 | 1379 | 23.18 | 5486.5 | 2895.4 | 2821.7 | 4157.4 | 1193.8 | 0.67906 | 5.992
2024-12-09 | 16:32 | Data | 0 | 32.723 | 30.482 | 185.589 | 7.64 | 174.335 | 2125.81 | 26.02 | 46.179 | 6.36 | 1.342 | 4.67 | 8436.21 | 2.046 | 97.8 | 77.7 | 1382 | 23.04 | 5483.5 | 2878.5 | 2829.3 | 4155.8 | 1193.8 | 0.67605 | 6.011
2024-12-09 | 16:33 | Data | 0 | 32.669 | 30.874 | 185.634 | 7.64 | 174.38 | 2123.1 | 26.02 | 46.269 | 6.35 | 1.339 | 4.671 | 8431.69 | 2.073 | 97.8 | 77.7 | 1380 | 23.09 | 5480.6 | 2895.7 | 2829.2 | 4167.5 | 1193.8 | 0.67791 | 6.008
2024-12-09 | 16:33 | Data | 0 | 32.507 | 30.604 | 185.498 | 7.64 | 174.335 | 2123.1 | 26.02 | 46.269 | 6.36 | 1.345 | 4.679 | 8440.74 | 2.066 | 97.8 | 77.7 | 1379 | 23.13 | 5486.5 | 2889 | 2828.7 | 4161 | 1193.8 | 0.67732 | 6.025
2024-12-09 | 16:33 | Data | 0 | 32.73 | 30.651 | 185.725 | 7.64 | 174.38 | 2122.2 | 26.01 | 46.179 | 6.36 | 1.347 | 4.663 | 8431.69 | 2.066 | 97.8 | 77.6 | 1380 | 23.13 | 5480.6 | 2865.9 | 2836.6 | 4153.1 | 1193.8 | 0.67246 | 6.01
2024-12-09 | 16:33 | Data | 0 | 33.149 | 30.779 | 185.77 | 7.64 | 174.515 | 2120.39 | 26.01 | 46.269 | 6.36 | 1.343 | 4.646 | 8427.17 | 2.093 | 97.8 | 77.6 | 1378 | 23.13 | 5477.7 | 2866 | 2820.2 | 4143.3 | 1193.8 | 0.67484 | 5.989
2024-12-09 | 16:33 | Data | 0 | 32.609 | 30.563 | 185.498 | 7.64 | 174.335 | 2121.29 | 26.02 | 46.179 | 6.35 | 1.341 | 4.641 | 8445.26 | 2.046 | 97.8 | 77.6 | 1379 | 23.13 | 5489.4 | 2894.6 | 2824.7 | 4159.9 | 1193.8 | 0.67958 | 5.981
2024-12-09 | 16:33 | Data | 0 | 32.609 | 30.55 | 185.589 | 7.64 | 174.335 | 2119.49 | 26.02 | 46.269 | 6.35 | 1.349 | 4.662 | 8427.17 | 2.268 | 97.8 | 77.6 | 1378 | 23.09 | 5477.7 | 2871.3 | 2815.2 | 4143.6 | 1193.8 | 0.67674 | 6.011
2024-12-09 | 16:33 | Data | 0 | 32.94 | 30.982 | 185.589 | 7.64 | 174.38 | 2120.39 | 26.02 | 46.179 | 6.36 | 1.338 | 4.652 | 8431.69 | 2.012 | 97.8 | 77.7 | 1378 | 23.13 | 5480.6 | 2865.9 | 2810.8 | 4144.6 | 1193.8 | 0.67564 | 5.988
2024-12-09 | 16:33 | Data | 0 | 33.034 | 31.096 | 185.77 | 7.64 | 174.335 | 2120.39 | 26.01 | 46.179 | 6.35 | 1.337 | 4.65 | 8427.17 | 2.066 | 97.8 | 77.7 | 1378 | 23.13 | 5477.7 | 2875.4 | 2835.7 | 4157.7 | 1193.8 | 0.67508 | 5.988
2024-12-09 | 16:33 | Data | 0 | 32.723 | 30.867 | 185.815 | 7.64 | 174.425 | 2120.39 | 26.02 | 46.179 | 6.35 | 1.341 | 4.662 | 8400.04 | 2.019 | 97.8 | 77.7 | 1378 | 23.09 | 5460 | 2887.8 | 2814.2 | 4153.1 | 1193.8 | 0.67834 | 6.004
2024-12-09 | 16:33 | Data | 0 | 32.892 | 30.88 | 185.634 | 7.64 | 174.47 | 2120.39 | 26.02 | 46.179 | 6.35 | 1.343 | 4.647 | 8377.43 | 2.039 | 97.8 | 77.6 | 1378 | 23.09 | 5445.3 | 2887.3 | 2845.4 | 4172.6 | 1193.8 | 0.67529 | 5.99
2024-12-09 | 16:33 | Data | 0 | 32.892 | 30.968 | 185.634 | 7.64 | 174.425 | 2119.49 | 26.02 | 46.269 | 6.35 | 1.347 | 4.66 | 8390.99 | 2.16 | 97.8 | 77.6 | 1378 | 23.13 | 5454.1 | 2903.1 | 2855.4 | 4189.3 | 1193.8 | 0.67669 | 6.007
2024-12-09 | 16:33 | Data | 0 | 32.953 | 30.678 | 185.679 | 7.64 | 174.425 | 2120.39 | 26.01 | 45.727 | 6.35 | 1.348 | 4.652 | 8395.51 | 2.181 | 97.8 | 77.5 | 1378 | 22.86 | 5457.1 | 2899.3 | 2829 | 4172.6 | 1193.8 | 0.67805 | 6
2024-12-09 | 16:33 | Data | 0 | 32.946 | 30.678 | 185.679 | 7.64 | 174.47 | 2120.39 | 26.03 | 46.179 | 6.35 | 1.345 | 4.655 | 8418.13 | 2.073 | 97.8 | 77.6 | 1378 | 23.13 | 5471.8 | 2894.3 | 2810.3 | 4149.9 | 1193.8 | 0.67984 | 6
2024-12-09 | 16:33 | Data | 0 | 32.717 | 30.698 | 185.634 | 7.64 | 174.38 | 2114.06 | 26.02 | 46.179 | 6.35 | 1.34 | 4.676 | 8418.13 | 1.971 | 97.8 | 77.7 | 1374 | 23.13 | 5471.8 | 2888.5 | 2813.8 | 4151.1 | 1193.8 | 0.67828 | 6.017
2024-12-09 | 16:33 | Data | 0 | 32.669 | 30.874 | 185.77 | 7.64 | 174.515 | 2120.39 | 26.02 | 46.179 | 6.35 | 1.343 | 4.675 | 8409.08 | 2.046 | 97.8 | 77.7 | 1378 | 23.09 | 5465.9 | 2889.6 | 2809.1 | 4147.7 | 1193.8 | 0.68021 | 6.018
2024-12-09 | 16:33 | Data | 0 | 33.196 | 31.11 | 185.77 | 7.64 | 174.56 | 2116.78 | 26.01 | 46.269 | 6.36 | 1.346 | 4.652 | 8418.13 | 2.275 | 97.8 | 77.6 | 1376 | 23.13 | 5471.8 | 2894.9 | 2796.1 | 4142.9 | 1193.8 | 0.68238 | 5.998
2024-12-09 | 16:33 | Data | 0 | 32.75 | 30.853 | 185.589 | 7.64 | 174.38 | 2117.68 | 26.02 | 46.269 | 6.35 | 1.339 | 4.654 | 8431.69 | 1.965 | 97.8 | 77.7 | 1376 | 23.09 | 5480.6 | 2898.1 | 2797.6 | 4146.8 | 1193.8 | 0.68218 | 5.991
2024-12-09 | 16:33 | Data | 0 | 32.575 | 30.651 | 185.634 | 7.64 | 174.425 | 2118.58 | 26.02 | 46.269 | 6.35 | 1.348 | 4.652 | 8445.26 | 1.857 | 97.8 | 77.5 | 1376 | 23.09 | 5489.4 | 2897.8 | 2793.1 | 4142.4 | 1193.8 | 0.68438 | 5.999
2024-12-09 | 16:34 | Data | 0 | 32.514 | 30.651 | 185.679 | 7.64 | 174.47 | 2117.68 | 26.02 | 46.269 | 6.35 | 1.341 | 4.641 | 8422.65 | 1.857 | 97.8 | 77.6 | 1378 | 23.13 | 5474.7 | 2885.1 | 2802.3 | 4142.5 | 1193.8 | 0.68105 | 5.983
2024-12-09 | 16:34 | Data | 0 | 32.892 | 30.88 | 185.679 | 7.64 | 174.425 | 2114.06 | 26.01 | 46.179 | 6.35 | 1.344 | 4.669 | 8427.17 | 2.154 | 97.8 | 77.6 | 1374 | 23.13 | 5477.7 | 2888.9 | 2823.6 | 4158.3 | 1193.8 | 0.67934 | 6.013
2024-12-09 | 16:34 | Data | 0 | 32.75 | 30.543 | 185.589 | 7.64 | 174.38 | 2114.06 | 26.02 | 46.179 | 6.35 | 1.347 | 4.645 | 8418.13 | 1.965 | 97.8 | 77.5 | 1374 | 23.13 | 5471.8 | 2900.8 | 2797.4 | 4149.9 | 1193.9 | 0.68256 | 5.992
2024-12-09 | 16:34 | Data | 0 | 32.622 | 30.853 | 185.77 | 7.64 | 174.335 | 2114.06 | 26.02 | 46.179 | 6.35 | 1.348 | 4.633 | 8404.56 | 1.911 | 97.8 | 77.5 | 1374 | 23.13 | 5463 | 2895.8 | 2799.1 | 4150.8 | 1193.9 | 0.68021 | 5.982
2024-12-09 | 16:34 | Data | 0 | 33.054 | 30.793 | 185.77 | 7.64 | 174.425 | 2114.06 | 26.01 | 46.269 | 6.35 | 1.356 | 4.645 | 8400.04 | 2.181 | 97.8 | 77.4 | 1374 | 23.09 | 5460 | 2891.2 | 2810.9 | 4149.5 | 1193.9 | 0.68036 | 6.001
2024-12-09 | 16:34 | Data | 0 | 32.514 | 30.651 | 185.634 | 7.64 | 174.425 | 2114.97 | 26.02 | 46.269 | 6.35 | 1.353 | 4.645 | 8381.95 | 2.019 | 97.8 | 77.4 | 1374 | 23.13 | 5448.3 | 2509.9 | 2595.5 | 3688.2 | 1193.9 | 0.65916 | 5.998
2024-12-09 | 16:34 | Data | 0 | 32.913 | 30.874 | 185.634 | 7.64 | 174.425 | 2114.06 | 26.02 | 46.359 | 6.36 | 1.347 | 4.641 | 8372.9 | 1.863 | 97.8 | 77.5 | 1374 | 23.18 | 5442.4 | 1813.7 | 2245.6 | 2898.5 | 1193.9 | 0.62304 | 5.988
2024-12-09 | 16:34 | Data | 0 | 32.73 | 30.624 | 185.679 | 7.64 | 174.38 | 2114.06 | 26.02 | 46.269 | 6.35 | 1.352 | 4.683 | 8377.43 | 1.978 | 97.8 | 77.6 | 1374 | 23.13 | 5445.3 | 1819.8 | 2234.7 | 2894.2 | 1193.9 | 0.62621 | 6.036
2024-12-09 | 16:34 | Data | 0 | 32.94 | 30.88 | 185.725 | 7.64 | 174.425 | 2114.06 | 26.02 | 46.269 | 6.35 | 1.354 | 4.671 | 8381.95 | 2.073 | 97.8 | 77.5 | 1375 | 23.13 | 5448.3 | 1808.3 | 2259.1 | 2905.7 | 1193.9 | 0.6197 | 6.024
2024-12-09 | 16:34 | Data | 0 | 32.852 | 30.685 | 185.815 | 7.64 | 174.56 | 2113.16 | 26.02 | 46.269 | 6.35 | 1.344 | 4.646 | 8372.9 | 2.052 | 97.8 | 77.6 | 1374 | 23.13 | 5442.4 | 1820 | 2247.7 | 2902.9 | 1193.9 | 0.62473 | 5.991
2024-12-09 | 16:34 | Data | 0 | 32.723 | 30.766 | 185.725 | 7.64 | 174.335 | 2114.06 | 26.02 | 46.269 | 6.35 | 1.351 | 4.651 | 8400.04 | 2.073 | 97.8 | 77.5 | 1375 | 23.13 | 5460 | 1817 | 2234.2 | 2893.9 | 1193.9 | 0.62482 | 6
2024-12-09 | 16:34 | Data | 0 | 33.095 | 31.103 | 185.77 | 7.64 | 174.425 | 2114.06 | 26.03 | 46.179 | 6.35 | 1.346 | 4.671 | 8418.13 | 2.059 | 97.8 | 77.6 | 1375 | 23.09 | 5471.8 | 1815.9 | 2228.3 | 2888.3 | 1193.9 | 0.62603 | 6.017
2024-12-09 | 16:34 | Data | 0 | 33 | 30.448 | 185.589 | 7.64 | 174.425 | 2113.16 | 26.02 | 46.269 | 6.36 | 1.339 | 4.646 | 8418.13 | 2.039 | 97.8 | 77.6 | 1374 | 23.13 | 5471.8 | 1821.7 | 2235.8 | 2895 | 1193.9 | 0.62674 | 5.986
2024-12-09 | 16:34 | Data | 0 | 32.561 | 30.448 | 185.634 | 7.64 | 174.425 | 2114.06 | 26.01 | 46.179 | 6.35 | 1.337 | 4.66 | 8400.04 | 2.052 | 97.8 | 77.7 | 1375 | 23.13 | 5460 | 1806.7 | 2228.4 | 2881.9 | 1193.9 | 0.62423 | 5.997
2024-12-09 | 16:34 | Data | 0 | 32.723 | 30.651 | 185.815 | 7.64 | 174.425 | 2118.58 | 26.02 | 46.269 | 6.35 | 1.329 | 4.683 | 8386.47 | 2.073 | 97.8 | 77.9 | 1376 | 23.13 | 5451.2 | 1811 | 2221.4 | 2879.3 | 1193.9 | 0.62642 | 6.012
2024-12-09 | 16:34 | Data | 0 | 33.034 | 30.934 | 185.77 | 7.64 | 174.47 | 2118.58 | 26.02 | 45.998 | 6.36 | 1.338 | 4.692 | 8400.04 | 1.978 | 97.8 | 77.8 | 1377 | 23.04 | 5460 | 1817.8 | 2237.1 | 2895.4 | 1193.9 | 0.62489 | 6.029
2024-12-09 | 16:34 | Data | 0 | 33.135 | 30.732 | 185.815 | 7.64 | 174.425 | 2117.68 | 26.03 | 46.179 | 6.35 | 1.339 | 4.637 | 8386.47 | 2.275 | 97.8 | 77.6 | 1376 | 23.13 | 5451.2 | 1819.3 | 2228.5 | 2888.2 | 1193.9 | 0.6266 | 5.978
2024-12-09 | 16:34 | Data | 0 | 32.642 | 30.88 | 185.725 | 7.64 | 174.335 | 2117.68 | 26.02 | 46.179 | 6.35 | 1.341 | 4.639 | 8386.47 | 1.83 | 97.8 | 77.6 | 1377 | 23.13 | 5451.2 | 1796.5 | 2246.2 | 2889.2 | 1193.9 | 0.61928 | 5.979
2024-12-09 | 16:35 | Data | 0 | 32.541 | 30.651 | 185.815 | 7.64 | 174.38 | 2114.97 | 26.01 | 46.269 | 6.36 | 1.345 | 4.658 | 8372.9 | 1.978 | 97.8 | 77.6 | 1375 | 23.13 | 5442.4 | 1809.4 | 2242.5 | 2900.4 | 1193.9 | 0.62108 | 6.004
2024-12-09 | 16:35 | Data | 0 | 32.636 | 30.874 | 185.679 | 7.64 | 174.335 | 2117.68 | 26.02 | 46.179 | 6.36 | 1.353 | 4.684 | 8372.9 | 1.83 | 97.8 | 77.6 | 1376 | 23.13 | 5442.4 | 1813.4 | 2224.1 | 2881.5 | 1193.9 | 0.62685 | 6.036
2024-12-09 | 16:35 | Data | 0 | 32.771 | 30.651 | 185.77 | 7.64 | 174.425 | 2114.06 | 26.02 | 46.179 | 6.35 | 1.342 | 4.66 | 8386.47 | 1.904 | 97.8 | 77.6 | 1374 | 23.04 | 5451.2 | 1802.4 | 2241.7 | 2888.5 | 1193.9 | 0.62162 | 6.002
2024-12-09 | 16:35 | Data | 0 | 32.561 | 30.739 | 185.679 | 7.64 | 174.425 | 2114.06 | 26.02 | 46.179 | 6.36 | 1.337 | 4.638 | 8377.43 | 1.971 | 97.8 | 77.6 | 1374 | 23.09 | 5445.3 | 1816.7 | 2250.2 | 2904.4 | 1193.9 | 0.62277 | 5.975
2024-12-09 | 16:35 | Data | 0 | 32.71 | 30.867 | 185.634 | 7.64 | 174.38 | 2116.78 | 26.03 | 46.269 | 6.36 | 1.342 | 4.648 | 8372.9 | 2.025 | 97.8 | 77.6 | 1376 | 23.13 | 5442.4 | 1802 | 2244.3 | 2891.1 | 1193.9 | 0.62058 | 5.99
2024-12-09 | 16:35 | Data | 0 | 32.467 | 30.651 | 185.634 | 7.64 | 174.38 | 2117.68 | 26.01 | 46.179 | 6.35 | 1.344 | 4.67 | 8386.47 | 1.944 | 97.8 | 77.7 | 1376 | 23.13 | 5451.2 | 1819.8 | 2244.6 | 2901.1 | 1193.9 | 0.62452 | 6.012
2024-12-09 | 16:35 | Data | 0 | 32.494 | 30.637 | 185.498 | 7.64 | 174.289 | 2118.58 | 26.02 | 46.359 | 6.35 | 1.345 | 4.647 | 8372.9 | 2.059 | 97.8 | 77.6 | 1376 | 23.13 | 5442.4 | 1793.5 | 2238.2 | 2881.4 | 1193.9 | 0.61915 | 5.992
2024-12-09 | 16:35 | Data | 0 | 32.723 | 30.874 | 185.498 | 7.64 | 174.425 | 2118.58 | 26.02 | 46.179 | 6.36 | 1.348 | 4.655 | 8400.04 | 1.965 | 97.8 | 77.6 | 1377 | 23.09 | 5460 | 1793.6 | 2245.8 | 2895.6 | 1193.9 | 0.62248 | 6.003
2024-12-09 | 16:35 | Data | 0 | 32.528 | 30.475 | 185.679 | 7.64 | 174.47 | 2116.78 | 26.02 | 46.179 | 6.35 | 1.347 | 4.672 | 8409.08 | 2.019 | 97.8 | 77.6 | 1376 | 23.09 | 5465.9 | 1821.7 | 2239.6 | 2897.7 | 1193.9 | 0.62603 | 6.018
2024-12-09 | 16:35 | Data | 0 | 32.501 | 30.847 | 185.815 | 7.64 | 174.47 | 2117.68 | 26.02 | 46.269 | 6.35 | 1.34 | 4.664 | 8422.65 | 1.965 | 97.8 | 77.7 | 1376 | 23.13 | 5474.7 | 1800.8 | 2234.7 | 2884.4 | 1193.9 | 0.62132 | 6.005
2024-12-09 | 16:35 | Data | 0 | 32.94 | 30.651 | 185.679 | 7.64 | 174.425 | 2114.06 | 26.02 | 46.269 | 6.36 | 1.344 | 4.635 | 8422.65 | 1.958 | 97.8 | 77.5 | 1374 | 23.13 | 5474.7 | 1805.5 | 2230.6 | 2881.2 | 1193.9 | 0.62415 | 5.979
2024-12-09 | 16:35 | Data | 0 | 32.757 | 30.435 | 185.679 | 7.63 | 174.47 | 2117.68 | 26.02 | 46.179 | 6.35 | 1.341 | 4.635 | 8431.69 | 2.066 | 97.8 | 77.6 | 1377 | 23.09 | 5480.6 | 1829.8 | 2244.8 | 2907.5 | 1193.9 | 0.62724 | 5.977
2024-12-09 | 16:35 | Data | 0 | 32.669 | 30.88 | 185.77 | 7.64 | 174.47 | 2117.68 | 26.02 | 46.269 | 6.35 | 1.342 | 4.656 | 8440.74 | 2.019 | 97.8 | 77.6 | 1376 | 23.09 | 5486.5 | 1804.2 | 2250.4 | 2898.4 | 1193.9 | 0.62489 | 6
2024-12-09 | 16:35 | Data | 0 | 32.501 | 30.604 | 185.679 | 7.64 | 174.289 | 2117.68 | 26.03 | 46.269 | 6.35 | 1.345 | 4.662 | 8449.78 | 1.938 | 97.8 | 77.6 | 1376 | 23.18 | 5492.4 | 1812.9 | 2240.3 | 2894.3 | 1193.9 | 0.62429 | 6.007
2024-12-09 | 16:35 | Data | 0 | 32.494 | 30.624 | 185.725 | 7.64 | 174.335 | 2117.68 | 26.01 | 46.269 | 6.35 | 1.339 | 4.626 | 8445.26 | 1.87 | 97.8 | 77.6 | 1376 | 23.18 | 5489.4 | 1806.8 | 2255.1 | 2902.3 | 1193.9 | 0.61956 | 5.965
2024-12-09 | 16:35 | Data | 0 | 32.858 | 30.482 | 185.679 | 7.64 | 174.47 | 2118.58 | 26.02 | 46.269 | 6.35 | 1.346 | 4.624 | 8454.3 | 2.086 | 97.8 | 77.5 | 1377 | 23.13 | 5495.3 | 1814.3 | 2256.3 | 2907.2 | 1193.9 | 0.62111 | 5.969
2024-12-09 | 16:35 | Data | 0 | 32.501 | 30.597 | 185.634 | 7.64 | 174.38 | 2117.68 | 26.02 | 46.179 | 6.35 | 1.344 | 4.632 | 8445.26 | 2.073 | 97.8 | 77.5 | 1377 | 23.09 | 5489.4 | 1803 | 2248.3 | 2893.6 | 1193.9 | 0.62107 | 5.976
2024-12-09 | 16:35 | Data | 0 | 33.034 | 30.988 | 185.77 | 7.64 | 174.425 | 2117.68 | 26.02 | 46.269 | 6.35 | 1.339 | 4.65 | 8440.74 | 2.059 | 97.8 | 77.7 | 1376 | 23.13 | 5486.5 | 1819.9 | 2243.5 | 2901.1 | 1193.9 | 0.62518 | 5.987
2024-12-09 | 16:36 | Data | 0 | 32.717 | 30.428 | 185.498 | 7.64 | 174.335 | 2116.78 | 26.02 | 46.269 | 6.35 | 1.339 | 4.671 | 8463.35 | 2.073 | 97.8 | 77.7 | 1375 | 23.09 | 5501.2 | 1815.5 | 2243.9 | 2898.3 | 1193.9 | 0.62395 | 6.01
2024-12-09 | 16:36 | Data | 0 | 32.663 | 30.421 | 185.589 | 7.64 | 174.38 | 2118.58 | 26.03 | 46.269 | 6.35 | 1.345 | 4.648 | 8458.83 | 1.911 | 97.8 | 77.5 | 1377 | 23.13 | 5498.2 | 1821 | 2254.6 | 2909 | 1193.9 | 0.62369 | 5.994
2024-12-09 | 16:36 | Data | 0 | 33.021 | 30.732 | 185.679 | 7.64 | 174.425 | 2112.26 | 26.02 | 45.818 | 6.35 | 1.339 | 4.657 | 8458.83 | 2.235 | 97.8 | 77.7 | 1374 | 22.86 | 5498.2 | 1820.6 | 2251.5 | 2905.7 | 1193.9 | 0.62415 | 5.997
2024-12-09 | 16:36 | Data | 0 | 32.494 | 30.415 | 185.589 | 7.64 | 174.335 | 2112.26 | 26.02 | 46.179 | 6.35 | 1.34 | 4.654 | 8472.39 | 2.079 | 97.8 | 77.6 | 1372 | 23.13 | 5507.1 | 1800.6 | 2231 | 2880.2 | 1193.9 | 0.62225 | 5.995
2024-12-09 | 16:36 | Data | 0 | 32.507 | 30.597 | 185.679 | 7.64 | 174.38 | 2112.26 | 26.02 | 46.179 | 6.35 | 1.339 | 4.682 | 8458.83 | 1.897 | 97.8 | 77.8 | 1372 | 23.13 | 5498.2 | 1793.8 | 2246.3 | 2888 | 1193.9 | 0.61855 | 6.021
2024-12-09 | 16:36 | Data | 0 | 32.71 | 30.921 | 185.498 | 7.64 | 174.38 | 2110.45 | 26.02 | 46.269 | 6.36 | 1.346 | 4.676 | 8449.78 | 1.992 | 97.8 | 77.7 | 1372 | 23.13 | 5492.4 | 1816.3 | 2220.5 | 2879.9 | 1193.9 | 0.62342 | 6.021
2024-12-09 | 16:36 | Data | 0 | 32.73 | 30.874 | 185.725 | 7.64 | 174.38 | 2111.35 | 26.02 | 46.179 | 6.35 | 1.339 | 4.682 | 8454.3 | 1.87 | 97.8 | 77.8 | 1372 | 23.04 | 5495.3 | 1801.3 | 2222.3 | 2872.8 | 1193.9 | 0.62496 | 6.02
2024-12-09 | 16:36 | Data | 0 | 32.636 | 30.475 | 185.453 | 7.64 | 174.38 | 2110.45 | 26.02 | 46.179 | 6.35 | 1.341 | 4.67 | 8445.26 | 1.924 | 97.8 | 77.7 | 1372 | 23.13 | 5489.4 | 1814.8 | 2246.3 | 2899.5 | 1193.9 | 0.62313 | 6.011
2024-12-09 | 16:36 | Data | 0 | 32.879 | 30.772 | 185.86 | 7.64 | 174.425 | 2111.35 | 26.02 | 46.269 | 6.36 | 1.339 | 4.673 | 8449.78 | 1.978 | 97.8 | 77.7 | 1373 | 23.13 | 5492.4 | 1819.6 | 2232.8 | 2891.2 | 1193.9 | 0.62642 | 6.012
2024-12-09 | 16:36 | Data | 0 | 32.521 | 30.752 | 185.679 | 7.64 | 174.38 | 2114.06 | 26 | 46.269 | 6.35 | 1.338 | 4.667 | 8463.35 | 1.877 | 97.8 | 77.7 | 1374 | 23.13 | 5501.2 | 1826.2 | 2243.6 | 2904.9 | 1193.9 | 0.62637 | 6.005
2024-12-09 | 16:36 | Data | 0 | 32.534 | 30.536 | 185.498 | 7.64 | 174.38 | 2117.68 | 26.02 | 46.179 | 6.36 | 1.34 | 4.652 | 8458.83 | 1.884 | 97.8 | 77.6 | 1376 | 23.09 | 5498.2 | 1813.1 | 2237.1 | 2891.5 | 1193.9 | 0.62319 | 5.991
2024-12-09 | 16:36 | Data | 0 | 32.501 | 30.644 | 185.634 | 7.64 | 174.244 | 2117.68 | 26.03 | 46.179 | 6.35 | 1.34 | 4.664 | 8440.74 | 1.985 | 97.8 | 77.7 | 1377 | 23.04 | 5486.5 | 1816.7 | 2242.6 | 2898.1 | 1193.9 | 0.62434 | 6.003
2024-12-09 | 16:36 | Data | 0 | 32.609 | 30.651 | 185.408 | 7.64 | 174.289 | 2114.97 | 26.02 | 46.179 | 6.35 | 1.341 | 4.657 | 8440.74 | 1.951 | 97.8 | 77.6 | 1376 | 23.13 | 5486.5 | 1811.8 | 2272 | 2918.7 | 1193.9 | 0.61819 | 5.998
2024-12-09 | 16:36 | Data | 0 | 32.75 | 30.651 | 185.589 | 7.64 | 174.289 | 2109.54 | 26.02 | 46.269 | 6.35 | 1.347 | 4.656 | 8445.26 | 2.079 | 97.8 | 77.6 | 1371 | 23.13 | 5489.4 | 1817.5 | 2269.4 | 2919.7 | 1193.9 | 0.62055 | 6.002
2024-12-09 | 16:36 | Data | 0 | 32.926 | 30.874 | 185.679 | 7.64 | 174.335 | 2118.58 | 26.02 | 46.269 | 6.35 | 1.339 | 4.676 | 8431.69 | 1.958 | 97.8 | 77.7 | 1376 | 23.09 | 5480.6 | 1810.6 | 2275 | 2921 | 1193.9 | 0.61681 | 6.015
2024-12-09 | 16:36 | Data | 0 | 32.622 | 30.428 | 185.679 | 7.64 | 174.38 | 2114.06 | 26.02 | 46.269 | 6.36 | 1.339 | 4.668 | 8445.26 | 2.1 | 97.8 | 77.7 | 1375 | 23.13 | 5489.4 | 1820.7 | 2262.7 | 2917.7 | 1193.9 | 0.6219 | 6.008
2024-12-09 | 16:36 | Data | 0 | 32.44 | 30.59 | 185.363 | 7.64 | 174.244 | 2114.97 | 26.01 | 46.269 | 6.35 | 1.346 | 4.667 | 8458.83 | 2.052 | 97.8 | 77.6 | 1374 | 23.13 | 5498.2 | 1811.6 | 2255.8 | 2904.6 | 1193.9 | 0.62144 | 6.013
2024-12-09 | 16:36 | Data | 0 | 32.379 | 30.415 | 185.453 | 7.64 | 174.244 | 2113.16 | 26.02 | 46.269 | 6.35 | 1.342 | 4.664 | 8418.13 | 1.978 | 97.8 | 77.7 | 1374 | 23.13 | 5471.8 | 1798.9 | 2250.9 | 2893.7 | 1193.9 | 0.61915 | 6.005
2024-12-09 | 16:37 | Data | 0 | 32.494 | 30.219 | 185.453 | 7.64 | 174.289 | 2112.26 | 26.02 | 46.179 | 6.35 | 1.34 | 4.679 | 8427.17 | 2.241 | 97.8 | 77.7 | 1372 | 23.09 | 5477.7 | 1803.4 | 2253.7 | 2898.2 | 1193.9 | 0.61985 | 6.018
2024-12-09 | 16:37 | Data | 0 | 32.501 | 30.597 | 185.589 | 7.64 | 174.244 | 2111.35 | 26.02 | 46.179 | 6.35 | 1.345 | 4.66 | 8427.17 | 1.897 | 97.8 | 77.6 | 1372 | 23.13 | 5477.7 | 1814.8 | 2259.5 | 2911.5 | 1193.9 | 0.62059 | 6.004
2024-12-09 | 16:37 | Data | 0 | 32.717 | 30.651 | 185.498 | 7.64 | 174.335 | 2112.26 | 26.02 | 46.269 | 6.35 | 1.339 | 4.652 | 8431.69 | 2.073 | 97.8 | 77.6 | 1372 | 23.09 | 5480.6 | 1805 | 2251.6 | 2898.6 | 1193.9 | 0.61911 | 5.992
2024-12-09 | 16:37 | Data | 0 | 32.818 | 30.82 | 185.498 | 7.64 | 174.289 | 2111.35 | 26.02 | 46.269 | 6.35 | 1.338 | 4.642 | 8422.65 | 2.289 | 97.8 | 77.6 | 1372 | 23.22 | 5474.7 | 1799.1 | 2231.5 | 2879.6 | 1193.9 | 0.62198 | 5.978
2024-12-09 | 16:37 | Data | 0 | 32.831 | 30.334 | 185.408 | 7.64 | 174.335 | 2111.35 | 26.02 | 46.269 | 6.35 | 1.342 | 4.669 | 8400.04 | 2.12 | 97.8 | 77.7 | 1372 | 23.18 | 5460 | 2878 | 2835.4 | 4164.9 | 1193.9 | 0.67386 | 6.011
2024-12-09 | 16:37 | Data | 0 | 32.831 | 30.651 | 185.679 | 7.64 | 174.38 | 2114.06 | 26.02 | 46.179 | 6.35 | 1.339 | 4.669 | 8395.51 | 1.877 | 97.8 | 77.7 | 1374 | 23.13 | 5457.1 | 2898.9 | 2848.4 | 4184.9 | 1194 | 0.67609 | 6.007
2024-12-09 | 16:37 | Data | 0 | 32.501 | 30.624 | 185.453 | 7.64 | 174.244 | 2117.68 | 26.02 | 46.179 | 6.35 | 1.336 | 4.668 | 8409.08 | 1.958 | 97.8 | 77.7 | 1376 | 23.13 | 5465.9 | 2898.8 | 2834.2 | 4174.7 | 1194 | 0.68047 | 6.004
2024-12-09 | 16:37 | Data | 0 | 32.521 | 30.651 | 185.498 | 7.64 | 174.335 | 2117.68 | 26.03 | 46.269 | 6.35 | 1.347 | 4.642 | 8418.13 | 1.857 | 97.8 | 77.5 | 1376 | 23.13 | 5471.8 | 2890.8 | 2854.6 | 4182.7 | 1194 | 0.67386 | 5.988
2024-12-09 | 16:37 | Data | 0 | 32.723 | 30.536 | 185.589 | 7.64 | 174.335 | 2117.68 | 26.02 | 46.359 | 6.36 | 1.345 | 4.666 | 8418.13 | 1.87 | 97.8 | 77.6 | 1375 | 23.13 | 5471.8 | 2888.6 | 2820.3 | 4159.5 | 1194 | 0.67703 | 6.014
2024-12-09 | 16:37 | Data | 0 | 32.717 | 30.442 | 185.408 | 7.64 | 174.154 | 2121.29 | 26.01 | 46.269 | 6.35 | 1.339 | 4.646 | 8440.74 | 2.14 | 97.8 | 77.6 | 1379 | 23.13 | 5486.5 | 2869.1 | 2854.5 | 4151.8 | 1194 | 0.67165 | 5.988
2024-12-09 | 16:37 | Data | 0 | 32.339 | 30.415 | 185.363 | 7.64 | 174.38 | 2120.39 | 26.02 | 46.179 | 6.36 | 1.336 | 4.647 | 8431.69 | 1.863 | 97.8 | 77.7 | 1379 | 23.09 | 5480.6 | 2897.6 | 2769.7 | 4128.8 | 1194 | 0.68753 | 5.982
2024-12-09 | 16:37 | Data | 0 | 32.379 | 30.644 | 185.453 | 7.64 | 174.335 | 2120.39 | 26.01 | 46.269 | 6.35 | 1.342 | 4.643 | 8431.69 | 1.85 | 97.8 | 77.6 | 1378 | 23.13 | 5480.6 | 2891.6 | 2808.6 | 4151.9 | 1194 | 0.6799 | 5.985
2024-12-09 | 16:37 | Data | 0 | 32.339 | 30.442 | 185.589 | 7.64 | 174.38 | 2113.16 | 26 | 46.089 | 6.36 | 1.345 | 4.641 | 8427.17 | 1.85 | 97.8 | 77.5 | 1374 | 23.04 | 5477.7 | 2895.5 | 2832.8 | 4173.1 | 1194 | 0.67472 | 5.985
2024-12-09 | 16:37 | Data | 0 | 32.318 | 30.415 | 185.498 | 7.64 | 174.244 | 2114.97 | 25.99 | 46.179 | 6.36 | 1.339 | 4.632 | 8445.26 | 1.992 | 97.8 | 77.6 | 1374 | 23.09 | 5489.4 | 2889.7 | 2825.2 | 4164.2 | 1194 | 0.67717 | 5.97
2024-12-09 | 16:37 | Data | 0 | 32.352 | 30.442 | 185.725 | 7.64 | 174.425 | 2111.35 | 26.01 | 46.269 | 6.35 | 1.339 | 4.635 | 8427.17 | 1.89 | 97.8 | 77.6 | 1372 | 23.09 | 5477.7 | 2882.5 | 2810.2 | 4151.3 | 1194 | 0.68086 | 5.973
2024-12-09 | 16:37 | Data | 0 | 32.494 | 30.624 | 185.77 | 7.64 | 174.425 | 2112.26 | 25.99 | 46.269 | 6.35 | 1.348 | 4.664 | 8422.65 | 2.133 | 97.8 | 77.6 | 1372 | 23.18 | 5474.7 | 2917.2 | 2829.1 | 4183.9 | 1194 | 0.68107 | 6.013
2024-12-09 | 16:37 | Data | 0 | 32.494 | 30.624 | 185.725 | 7.64 | 174.38 | 2114.97 | 26 | 46.269 | 6.35 | 1.343 | 4.683 | 8436.21 | 1.897 | 97.8 | 77.7 | 1377 | 23.13 | 5483.5 | 2905.5 | 2821.6 | 4168.8 | 1194 | 0.67889 | 6.026
2024-12-09 | 16:38 | Data | 0 | 32.561 | 30.442 | 185.77 | 7.64 | 174.47 | 2111.35 | 26 | 46.179 | 6.35 | 1.347 | 4.639 | 8418.13 | 1.965 | 97.8 | 77.5 | 1373 | 23.13 | 5471.8 | 2884.2 | 2819.9 | 4157.2 | 1194 | 0.67737 | 5.986
2024-12-09 | 16:38 | Data | 0 | 32.426 | 30.421 | 186.132 | 7.64 | 174.877 | 2110.45 | 25.99 | 46.269 | 6.35 | 1.347 | 4.624 | 8418.13 | 1.87 | 97.8 | 77.5 | 1373 | 23.13 | 5471.8 | 2890.8 | 2828.7 | 4167.3 | 1194 | 0.6775 | 5.969
2024-12-09 | 16:38 | Data | 0 | 32.406 | 30.415 | 186.222 | 7.64 | 175.012 | 2111.35 | 26 | 46.269 | 6.35 | 1.348 | 4.671 | 8418.13 | 2.059 | 97.8 | 77.6 | 1372 | 23.09 | 5471.8 | 2908.8 | 2843.4 | 4190.1 | 1194 | 0.67617 | 6.018
2024-12-09 | 16:38 | Data | 0 | 32.521 | 30.421 | 186.313 | 7.64 | 174.967 | 2114.06 | 26 | 46.269 | 6.35 | 1.354 | 4.664 | 8404.56 | 2.073 | 97.8 | 77.5 | 1374 | 23.13 | 5463 | 2864.5 | 2858.5 | 4166.9 | 1194 | 0.67164 | 6.017
2024-12-09 | 16:38 | Data | 0 | 32.521 | 30.415 | 186.177 | 7.64 | 174.967 | 2114.06 | 26 | 46.359 | 6.35 | 1.345 | 4.641 | 8449.78 | 2.079 | 97.8 | 77.5 | 1374 | 23.13 | 5492.4 | 2905.3 | 2851.6 | 4192.7 | 1194 | 0.67523 | 5.986
2024-12-09 | 16:38 | Data | 0 | 32.622 | 30.415 | 186.358 | 7.64 | 175.193 | 2117.68 | 25.99 | 46.179 | 6.35 | 1.342 | 4.666 | 8431.69 | 1.877 | 97.8 | 77.7 | 1376 | 23.09 | 5480.6 | 2882.7 | 2844.9 | 4170.4 | 1194 | 0.67542 | 6.007
2024-12-09 | 16:38 | Data | 0 | 32.71 | 30.651 | 186.448 | 7.64 | 175.058 | 2114.97 | 26 | 46.269 | 6.35 | 1.334 | 4.698 | 8427.17 | 2.073 | 97.8 | 77.9 | 1374 | 23.09 | 5477.7 | 2898.3 | 2829 | 4172.9 | 1194 | 0.678 | 6.032
2024-12-09 | 16:38 | Data | 0 | 32.494 | 30.252 | 186.448 | 7.64 | 175.103 | 2116.78 | 26 | 46.269 | 6.35 | 1.349 | 4.688 | 8440.74 | 2.167 | 97.8 | 77.6 | 1376 | 23.09 | 5486.5 | 2900.9 | 2833 | 4175.5 | 1194 | 0.67896 | 6.037
2024-12-09 | 16:38 | Data | 0 | 32.44 | 30.529 | 186.267 | 7.64 | 175.058 | 2116.78 | 26 | 45.908 | 6.35 | 1.354 | 4.658 | 8458.83 | 2.241 | 97.8 | 77.5 | 1376 | 22.95 | 5498.2 | 2901.1 | 2823.6 | 4168.9 | 1194 | 0.67873 | 6.012
2024-12-09 | 16:38 | Data | 0 | 32.467 | 30.219 | 186.448 | 7.64 | 175.148 | 2114.06 | 26 | 45.998 | 6.35 | 1.347 | 4.676 | 8454.3 | 2.16 | 97.8 | 77.6 | 1375 | 23 | 5495.3 | 2895.7 | 2840 | 4176.8 | 1194 | 0.67737 | 6.021
2024-12-09 | 16:38 | Data | 0 | 32.379 | 30.536 | 186.358 | 7.64 | 175.103 | 2114.97 | 26 | 45.908 | 6.35 | 1.355 | 4.692 | 8458.83 | 2.052 | 97.8 | 77.6 | 1375 | 23.04 | 5498.2 | 2914.5 | 2817 | 4177.5 | 1194 | 0.67875 | 6.046
2024-12-09 | 16:38 | Data | 0 | 32.831 | 30.448 | 186.494 | 7.64 | 175.193 | 2114.06 | 26 | 45.998 | 6.35 | 1.348 | 4.645 | 8467.87 | 2.086 | 97.8 | 77.5 | 1375 | 23 | 5504.1 | 2894.7 | 2849.7 | 4180.7 | 1194 | 0.67416 | 5.994
2024-12-09 | 16:38 | Data | 0 | 32.298 | 30.307 | 186.313 | 7.64 | 175.103 | 2114.06 | 26 | 45.908 | 6.35 | 1.351 | 4.648 | 8431.69 | 1.965 | 97.8 | 77.5 | 1374 | 22.95 | 5480.6 | 2878.2 | 2844.4 | 4169.3 | 1194 | 0.67614 | 5.999
2024-12-09 | 16:38 | Data | 0 | 32.69 | 30.516 | 186.494 | 7.64 | 175.193 | 2113.16 | 26 | 45.998 | 6.35 | 1.347 | 4.654 | 8458.83 | 2.005 | 97.8 | 77.6 | 1374 | 23 | 5498.2 | 2912.5 | 2854.8 | 4201.7 | 1194 | 0.67674 | 6
2024-12-09 | 16:38 | Data | 0 | 32.332 | 30.388 | 186.448 | 7.64 | 175.148 | 2114.06 | 26 | 45.998 | 6.35 | 1.354 | 4.667 | 8449.78 | 1.978 | 97.8 | 77.5 | 1374 | 22.95 | 5492.4 | 2895 | 2851.6 | 4182.8 | 1194 | 0.67563 | 6.021
2024-12-09 | 16:38 | Data | 0 | 32.669 | 30.516 | 186.358 | 7.64 | 175.148 | 2114.06 | 26 | 46.269 | 6.35 | 1.352 | 4.694 | 8440.74 | 1.978 | 97.8 | 77.6 | 1375 | 23.09 | 5486.5 | 2897.4 | 2837.4 | 4175.6 | 1194 | 0.67674 | 6.046
2024-12-09 | 16:38 | Data | 0 | 32.717 | 30.752 | 186.448 | 7.64 | 175.103 | 2117.68 | 26 | 45.998 | 6.35 | 1.357 | 4.674 | 8454.3 | 1.87 | 97.8 | 77.5 | 1376 | 22.95 | 5495.3 | 2898.8 | 2846.6 | 4182.8 | 1194 | 0.67632 | 6.031
2024-12-09 | 16:38 | Data | 0 | 32.71 | 30.644 | 186.358 | 7.64 | 175.148 | 2117.68 | 26 | 45.998 | 6.35 | 1.345 | 4.677 | 8458.83 | 2.093 | 97.8 | 77.7 | 1376 | 23 | 5498.2 | 2871 | 2847.7 | 4163.1 | 1194 | 0.67346 | 6.022
2024-12-09 | 16:39 | Data | 0 | 32.609 | 30.86 | 186.448 | 7.64 | 175.148 | 2116.78 | 26.01 | 45.908 | 6.35 | 1.348 | 4.685 | 8458.83 | 1.978 | 97.8 | 77.7 | 1376 | 23 | 5498.2 | 2910.3 | 2846.6 | 4193.4 | 1194 | 0.67807 | 6.034
2024-12-09 | 16:39 | Data | 0 | 32.831 | 30.543 | 186.539 | 7.64 | 175.193 | 2112.26 | 26 | 45.908 | 6.35 | 1.339 | 4.679 | 8463.35 | 2.019 | 97.8 | 77.7 | 1373 | 23 | 5501.2 | 2912.5 | 2814.4 | 4166.4 | 1194 | 0.683 | 6.018
2024-12-09 | 16:39 | Data | 0 | 32.602 | 30.415 | 186.494 | 7.64 | 175.193 | 2112.26 | 26 | 45.998 | 6.34 | 1.331 | 4.691 | 8476.91 | 2.127 | 97.8 | 77.9 | 1372 | 23 | 5510 | 2885.8 | 2843.8 | 4170.9 | 1194 | 0.67592 | 6.022
2024-12-09 | 16:39 | Data | 0 | 32.879 | 30.671 | 186.494 | 7.64 | 175.148 | 2110.45 | 26.01 | 45.998 | 6.34 | 1.34 | 4.66 | 8481.44 | 2.187 | 97.8 | 77.7 | 1372 | 23 | 5512.9 | 2881.8 | 2824.3 | 4155.6 | 1194 | 0.67796 | 6
2024-12-09 | 16:39 | Data | 0 | 32.494 | 30.415 | 186.448 | 7.64 | 175.103 | 2111.35 | 26 | 45.998 | 6.35 | 1.346 | 4.681 | 8481.44 | 2.079 | 97.8 | 77.7 | 1372 | 23 | 5512.9 | 2879.7 | 2833.5 | 4162.3 | 1194 | 0.67507 | 6.026
2024-12-09 | 16:39 | Data | 0 | 32.467 | 30.415 | 186.448 | 7.64 | 175.103 | 2116.78 | 26 | 45.908 | 6.35 | 1.353 | 4.693 | 8485.96 | 2.066 | 97.8 | 77.6 | 1376 | 23 | 5515.9 | 2899.8 | 2827.7 | 4166.2 | 1194 | 0.67982 | 6.045
2024-12-09 | 16:39 | Data | 0 | 32.723 | 30.428 | 186.358 | 7.64 | 175.193 | 2111.35 | 26.01 | 46.269 | 6.35 | 1.346 | 4.669 | 8449.78 | 2.079 | 97.8 | 77.6 | 1372 | 23.13 | 5492.4 | 2898.4 | 2848.9 | 4180.5 | 1194.1 | 0.67631 | 6.015
2024-12-09 | 16:39 | Data | 0 | 32.561 | 30.415 | 186.448 | 7.64 | 175.193 | 2108.64 | 26.01 | 45.908 | 6.35 | 1.339 | 4.649 | 8454.3 | 1.884 | 97.8 | 77.6 | 1371 | 22.95 | 5495.3 | 2898.8 | 2811.1 | 4157.9 | 1194.1 | 0.67892 | 5.987
2024-12-09 | 16:39 | Data | 0 | 32.285 | 30.3 | 186.448 | 7.64 | 175.103 | 2106.83 | 25.99 | 46.089 | 6.35 | 1.345 | 4.667 | 8458.83 | 1.857 | 97.8 | 77.6 | 1369 | 23 | 5498.2 | 2891.2 | 2851.5 | 4180.3 | 1194.1 | 0.67492 | 6.012
2024-12-09 | 16:39 | Data | 0 | 32.494 | 30.3 | 186.313 | 7.64 | 175.058 | 2106.83 | 26 | 45.908 | 6.35 | 1.347 | 4.663 | 8454.3 | 2.079 | 97.8 | 77.6 | 1369 | 23 | 5495.3 | 2896.9 | 2833 | 4167.4 | 1194.1 | 0.67724 | 6.009
2024-12-09 | 16:39 | Data | 0 | 32.555 | 30.415 | 186.584 | 7.64 | 175.148 | 2106.83 | 26 | 45.908 | 6.35 | 1.348 | 4.657 | 8485.96 | 1.911 | 97.8 | 77.6 | 1369 | 23 | 5515.9 | 2894.1 | 2850 | 4179.6 | 1194.1 | 0.67493 | 6.005
2024-12-09 | 16:39 | Data | 0 | 32.467 | 30.421 | 186.358 | 7.65 | 175.103 | 2108.64 | 26 | 45.998 | 6.35 | 1.338 | 4.67 | 8467.87 | 2.059 | 97.8 | 77.7 | 1371 | 23.09 | 5504.1 | 2887.4 | 2870.4 | 4187.9 | 1194.1 | 0.6721 | 6.008
2024-12-09 | 16:39 | Data | 0 | 32.777 | 30.651 | 186.674 | 7.64 | 175.284 | 2109.54 | 26 | 45.998 | 6.35 | 1.341 | 4.672 | 8476.91 | 1.911 | 97.8 | 77.7 | 1371 | 22.95 | 5510 | 2893.1 | 2857 | 4180.5 | 1194.1 | 0.67486 | 6.011
2024-12-09 | 16:39 | Data | 0 | 32.494 | 30.536 | 186.539 | 7.64 | 175.148 | 2111.35 | 26 | 45.998 | 6.35 | 1.344 | 4.686 | 8467.87 | 2.079 | 97.8 | 77.7 | 1373 | 22.95 | 5504.1 | 2894.1 | 2878 | 4198.6 | 1194.1 | 0.67152 | 6.03
2024-12-09 | 16:39 | Data | 0 | 32.94 | 30.563 | 186.629 | 7.64 | 175.238 | 2112.26 | 26 | 45.908 | 6.35 | 1.348 | 4.702 | 8454.3 | 2.1 | 97.8 | 77.7 | 1373 | 22.95 | 5495.3 | 2890.8 | 2864.8 | 4187.1 | 1194.1 | 0.67412 | 6.05
2024-12-09 | 16:39 | Data | 0 | 32.946 | 30.651 | 186.448 | 7.64 | 175.148 | 2112.26 | 26 | 45.998 | 6.35 | 1.362 | 4.684 | 8431.69 | 1.917 | 97.8 | 77.5 | 1372 | 23 | 5480.6 | 2910.5 | 2810.6 | 4166.1 | 1194.1 | 0.68009 | 6.045
2024-12-09 | 16:39 | Data | 0 | 32.494 | 30.604 | 186.539 | 7.64 | 175.103 | 2108.64 | 26 | 45.908 | 6.35 | 1.357 | 4.673 | 8422.65 | 1.992 | 97.8 | 77.5 | 1371 | 22.95 | 5474.7 | 2900 | 2808.9 | 4174.5 | 1194.1 | 0.67961 | 6.03
2024-12-09 | 16:39 | Data | 0 | 32.669 | 30.901 | 186.539 | 7.64 | 175.193 | 2108.64 | 26.01 | 46.089 | 6.35 | 1.359 | 4.687 | 8445.26 | 1.998 | 97.8 | 77.5 | 1371 | 23 | 5489.4 | 2894.4 | 2821.4 | 4160.1 | 1194.1 | 0.67342 | 6.045
2024-12-09 | 16:40 | Data | 0 | 33.034 | 30.901 | 186.674 | 7.65 | 175.238 | 2105.93 | 26.01 | 45.908 | 6.35 | 1.357 | 4.7 | 8440.74 | 2.052 | 97.8 | 77.6 | 1369 | 23 | 5486.5 | 2901.5 | 2821.9 | 4166 | 1194.1 | 0.67777 | 6.055
2024-12-09 | 16:40 | Data | 0 | 32.71 | 30.752 | 186.448 | 7.64 | 175.238 | 2108.64 | 26 | 45.908 | 6.35 | 1.348 | 4.66 | 8440.74 | 2.073 | 97.8 | 77.5 | 1371 | 23 | 5486.5 | 2894.6 | 2853.8 | 4180.8 | 1194.1 | 0.67593 | 6.008
2024-12-09 | 16:40 | Data | 0 | 32.561 | 30.421 | 186.448 | 7.64 | 175.238 | 2108.64 | 26.01 | 46.089 | 6.35 | 1.351 | 4.635 | 8440.74 | 2.079 | 97.8 | 77.4 | 1371 | 23 | 5486.5 | 2896.2 | 2850.8 | 4181.4 | 1194.1 | 0.67532 | 5.986
2024-12-09 | 16:40 | Data | 0 | 32.278 | 30.246 | 186.448 | 7.64 | 175.238 | 2108.64 | 25.99 | 45.908 | 6.35 | 1.354 | 4.683 | 8051.82 | 1.971 | 97.8 | 77.6 | 1371 | 22.95 | 5233.7 | 2886 | 2826 | 4156.3 | 1194.1 | 0.67675 | 6.037
2024-12-09 | 16:40 | Data | 0 | 32.622 | 30.766 | 186.674 | 7.64 | 175.238 | 2106.83 | 26 | 45.998 | 6.34 | 1.343 | 4.672 | 8612.58 | 1.904 | 97.8 | 77.7 | 1369 | 23 | 5598.2 | 2908.7 | 2820.8 | 4172 | 1194.1 | 0.67951 | 6.014
2024-12-09 | 16:40 | Data | 0 | 32.163 | 30.401 | 186.448 | 7.64 | 175.148 | 2107.74 | 26.01 | 45.998 | 6.35 | 1.348 | 4.676 | 8608.06 | 1.857 | 97.8 | 77.6 | 1371 | 23 | 5595.2 | 2902.3 | 2816.9 | 4168.1 | 1194.1 | 0.68028 | 6.025
2024-12-09 | 16:40 | Data | 0 | 32.831 | 30.421 | 186.539 | 7.64 | 175.238 | 2108.64 | 26.01 | 45.998 | 6.35 | 1.347 | 4.686 | 8612.58 | 2.012 | 97.8 | 77.7 | 1371 | 23 | 5598.2 | 2893.3 | 2804.1 | 4154.4 | 1194.1 | 0.68009 | 6.033
2024-12-09 | 16:40 | Data | 0 | 32.717 | 30.536 | 186.448 | 7.64 | 175.284 | 2108.64 | 26.01 | 45.366 | 6.35 | 1.356 | 4.667 | 8599.01 | 2.133 | 97.8 | 77.5 | 1371 | 22.73 | 5589.4 | 2923.8 | 2825.4 | 4180.1 | 1194.1 | 0.68456 | 6.023
2024-12-09 | 16:40 | Data | 0 | 32.467 | 30.82 | 186.539 | 7.64 | 175.238 | 2104.12 | 26 | 45.908 | 6.35 | 1.345 | 4.683 | 8594.49 | 2.046 | 97.8 | 77.7 | 1368 | 23 | 5586.4 | 2911 | 2814.9 | 4167.1 | 1194.1 | 0.68232 | 6.026
2024-12-09 | 16:40 | Data | 0 | 32.825 | 30.664 | 186.72 | 7.64 | 175.238 | 2108.64 | 26.01 | 45.908 | 6.35 | 1.341 | 4.683 | 8594.49 | 2.262 | 97.8 | 77.7 | 1371 | 22.95 | 5586.4 | 2902.6 | 2846.2 | 4176.4 | 1194.1 | 0.67819 | 6.024
2024-12-09 | 16:40 | Data | 0 | 32.696 | 30.651 | 186.494 | 7.64 | 175.193 | 2111.35 | 26.01 | 45.998 | 6.35 | 1.347 | 4.657 | 8567.36 | 2.066 | 97.8 | 77.6 | 1372 | 22.95 | 5568.8 | 2893.6 | 2826.5 | 4167 | 1194.1 | 0.67541 | 6.004
2024-12-09 | 16:40 | Data | 0 | 32.649 | 30.718 | 186.629 | 7.64 | 175.329 | 2117.68 | 26 | 45.998 | 6.35 | 1.339 | 4.674 | 8567.36 | 1.796 | 97.8 | 77.7 | 1376 | 23 | 5568.8 | 2905 | 2833.8 | 4177 | 1194.1 | 0.67857 | 6.014
2024-12-09 | 16:40 | Data | 0 | 32.494 | 30.415 | 186.313 | 7.64 | 175.058 | 2096.89 | 26 | 45.998 | 6.35 | 1.346 | 4.692 | 8531.18 | 2.079 | 97.8 | 77.7 | 1364 | 22.95 | 5545.3 | 2879 | 2835.4 | 4161.2 | 1194.1 | 0.67569 | 6.038
2024-12-09 | 16:40 | Data | 0 | 32.548 | 30.421 | 186.539 | 7.64 | 175.193 | 2117.68 | 26 | 45.998 | 6.34 | 1.348 | 4.677 | 8513.09 | 2.079 | 97.8 | 77.6 | 1376 | 22.95 | 5533.5 | 2886.8 | 2824.3 | 4157.5 | 1194.1 | 0.67588 | 6.026
2024-12-09 | 16:40 | Data | 0 | 32.528 | 30.624 | 186.358 | 7.64 | 175.238 | 2114.06 | 26.02 | 45.998 | 6.35 | 1.347 | 4.663 | 8495 | 1.863 | 97.8 | 77.6 | 1374 | 22.95 | 5521.8 | 2898.1 | 2845.2 | 4179.6 | 1194.1 | 0.67721 | 6.008
2024-12-09 | 16:40 | Data | 0 | 32.777 | 30.428 | 186.539 | 7.64 | 175.193 | 2114.06 | 26.01 | 45.908 | 6.35 | 1.348 | 4.672 | 8508.57 | 1.971 | 97.8 | 77.6 | 1374 | 23 | 5530.6 | 2906.2 | 2826.1 | 4171.9 | 1194.1 | 0.67983 | 6.018
2024-12-09 | 16:40 | Data | 0 | 32.501 | 30.637 | 186.629 | 7.64 | 175.284 | 2117.68 | 26.01 | 46.089 | 6.35 | 1.347 | 4.673 | 8513.09 | 2.046 | 97.8 | 77.6 | 1376 | 23 | 5533.5 | 2906.9 | 2837.3 | 4176.6 | 1194.1 | 0.67817 | 6.017
2024-12-09 | 16:40 | Data | 0 | 32.494 | 30.59 | 186.539 | 7.64 | 175.193 | 2117.68 | 26 | 45.998 | 6.35 | 1.347 | 4.68 | 8526.66 | 2.079 | 97.8 | 77.6 | 1376 | 23 | 5542.3 | 2904 | 2850.4 | 4188.6 | 1194.1 | 0.67693 | 6.027
2024-12-09 | 16:41 | Data | 0 | 32.879 | 30.651 | 186.584 | 7.64 | 175.238 | 2117.68 | 26 | 45.998 | 6.34 | 1.347 | 4.681 | 8485.96 | 2.12 | 97.8 | 77.7 | 1376 | 23 | 5515.9 | 2900 | 2853 | 4179.9 | 1194.1 | 0.67428 | 6.027
2024-12-09 | 16:41 | Data | 0 | 32.717 | 30.421 | 186.539 | 7.64 | 175.193 | 2120.39 | 26.01 | 45.998 | 6.35 | 1.348 | 4.666 | 8467.87 | 2.1 | 97.8 | 77.6 | 1378 | 23 | 5504.1 | 2891.1 | 2825.1 | 4165 | 1194.1 | 0.67761 | 6.015
2024-12-09 | 16:41 | Data | 0 | 32.973 | 30.448 | 186.539 | 7.64 | 175.284 | 2120.39 | 26 | 45.908 | 6.34 | 1.348 | 4.663 | 8472.39 | 2.133 | 97.8 | 77.6 | 1378 | 22.95 | 5507.1 | 2912.7 | 2814.6 | 4166.5 | 1194.1 | 0.68089 | 6.011
2024-12-09 | 16:41 | Data | 0 | 32.94 | 30.347 | 186.539 | 7.64 | 175.284 | 2123.1 | 26 | 45.998 | 6.35 | 1.339 | 4.675 | 8467.87 | 2.235 | 97.8 | 77.7 | 1380 | 22.95 | 5504.1 | 2871.3 | 2822.1 | 4148.2 | 1194.1 | 0.67312 | 6.015
2024-12-09 | 16:41 | Data | 0 | 32.555 | 30.59 | 186.448 | 7.63 | 175.193 | 2123.1 | 26 | 45.998 | 6.35 | 1.339 | 4.673 | 8458.83 | 2.113 | 97.8 | 77.7 | 1380 | 23 | 5498.2 | 2899.3 | 2821.8 | 4167 | 1194.1 | 0.67942 | 6.012
2024-12-09 | 16:41 | Data | 0 | 32.723 | 30.448 | 186.539 | 7.64 | 175.148 | 2122.2 | 26 | 45.908 | 6.35 | 1.347 | 4.635 | 8454.3 | 2.1 | 97.8 | 77.5 | 1380 | 23 | 5495.3 | 2907.6 | 2845.4 | 4188.7 | 1194.1 | 0.67851 | 5.981
2024-12-09 | 16:41 | Data | 0 | 32.609 | 30.847 | 186.494 | 7.64 | 175.238 | 2120.39 | 26.01 | 45.998 | 6.35 | 1.34 | 4.641 | 8431.69 | 2.046 | 97.8 | 77.6 | 1378 | 23 | 5480.6 | 2911.9 | 2863.5 | 4199.3 | 1194.1 | 0.67674 | 5.981
2024-12-09 | 16:41 | Data | 0 | 33.142 | 30.489 | 186.674 | 7.64 | 175.284 | 2124.91 | 26 | 45.998 | 6.35 | 1.348 | 4.673 | 8422.65 | 2.275 | 97.8 | 77.6 | 1381 | 23 | 5474.7 | 2904.1 | 2884.1 | 4209.3 | 1194.2 | 0.67568 | 6.022
2024-12-09 | 16:41 | Data | 0 | 32.541 | 30.415 | 186.584 | 7.64 | 175.284 | 2125.81 | 26 | 45.998 | 6.35 | 1.352 | 4.692 | 8431.69 | 1.971 | 97.8 | 77.6 | 1382 | 23 | 5480.6 | 2891.7 | 2853.2 | 4180.4 | 1194.2 | 0.67425 | 6.045
2024-12-09 | 16:41 | Data | 0 | 32.892 | 30.678 | 186.72 | 7.64 | 175.193 | 2122.2 | 26 | 45.908 | 6.34 | 1.341 | 4.665 | 8431.69 | 2.127 | 97.8 | 77.7 | 1380 | 23 | 5480.6 | 2900 | 2875.5 | 4199.2 | 1194.2 | 0.67442 | 6.007
2024-12-09 | 16:41 | Data | 0 | 32.494 | 30.59 | 186.494 | 7.64 | 175.103 | 2123.1 | 26 | 45.998 | 6.34 | 1.351 | 4.675 | 8458.83 | 1.904 | 97.8 | 77.6 | 1380 | 23 | 5498.2 | 2899.6 | 2860.4 | 4190.3 | 1194.2 | 0.67389 | 6.026
2024-12-09 | 16:41 | Data | 0 | 32.548 | 30.421 | 186.494 | 7.64 | 175.148 | 2118.58 | 26 | 45.998 | 6.34 | 1.345 | 4.677 | 8481.44 | 2.079 | 97.8 | 77.7 | 1376 | 23 | 5512.9 | 2897.6 | 2870 | 4192.6 | 1194.2 | 0.6754 | 6.024
2024-12-09 | 16:41 | Data | 0 | 32.582 | 30.475 | 186.448 | 7.64 | 175.103 | 2124.01 | 26 | 45.998 | 6.35 | 1.338 | 4.698 | 8467.87 | 1.89 | 97.8 | 77.8 | 1380 | 23 | 5504.1 | 2893.3 | 2845.6 | 4177.4 | 1194.2 | 0.67582 | 6.035
2024-12-09 | 16:41 | Data | 0 | 32.723 | 30.651 | 186.584 | 7.64 | 175.284 | 2120.39 | 26 | 45.998 | 6.35 | 1.343 | 4.691 | 8485.96 | 1.89 | 97.8 | 77.7 | 1378 | 23 | 5515.9 | 2876.2 | 2850.7 | 4177.5 | 1194.2 | 0.67068 | 6.034
2024-12-09 | 16:41 | Data | 0 | 32.339 | 30.624 | 186.448 | 7.64 | 175.148 | 2119.49 | 26.01 | 45.998 | 6.35 | 1.345 | 4.655 | 8454.3 | 1.85 | 97.8 | 77.6 | 1378 | 22.95 | 5495.3 | 2879.3 | 2811.4 | 4142.2 | 1194.2 | 0.6764 | 6.001
2024-12-09 | 16:41 | Data | 0 | 32.676 | 30.847 | 186.584 | 7.64 | 175.284 | 2119.49 | 26.01 | 45.998 | 6.34 | 1.341 | 4.664 | 8436.21 | 1.978 | 97.8 | 77.7 | 1378 | 23 | 5483.5 | 2902.9 | 2806.7 | 4157.4 | 1194.2 | 0.68027 | 6.004
2024-12-09 | 16:41 | Data | 0 | 32.494 | 30.536 | 186.539 | 7.64 | 175.148 | 2122.2 | 26 | 45.998 | 6.35 | 1.342 | 4.695 | 8436.21 | 2.059 | 97.8 | 77.8 | 1379 | 23 | 5483.5 | 2897 | 2838.3 | 4173.3 | 1194.2 | 0.67619 | 6.037
2024-12-09 | 16:42 | Data | 0 | 32.723 | 30.874 | 186.674 | 7.64 | 175.238 | 2120.39 | 26 | 46.089 | 6.35 | 1.345 | 4.681 | 8440.74 | 2.052 | 97.8 | 77.7 | 1378 | 23 | 5486.5 | 2867.8 | 2855.6 | 4166.1 | 1194.2 | 0.66824 | 6.026
2024-12-09 | 16:42 | Data | 0 | 32.71 | 30.55 | 186.494 | 7.64 | 175.148 | 2121.29 | 26 | 45.998 | 6.35 | 1.349 | 4.672 | 8445.26 | 2.241 | 97.8 | 77.6 | 1379 | 23 | 5489.4 | 2918.4 | 2909.8 | 4239.6 | 1194.2 | 0.67283 | 6.021
2024-12-09 | 16:42 | Data | 0 | 32.994 | 30.705 | 186.674 | 7.65 | 175.329 | 2120.39 | 26 | 45.998 | 6.35 | 1.34 | 4.692 | 8445.26 | 2.113 | 97.8 | 77.8 | 1378 | 22.95 | 5489.4 | 2919.7 | 2922.5 | 4228.2 | 1194.2 | 0.66873 | 6.031
2024-12-09 | 16:42 | Data | 0 | 32.339 | 30.644 | 186.494 | 7.64 | 175.193 | 2117.68 | 26 | 45.998 | 6.35 | 1.347 | 4.694 | 8440.74 | 1.843 | 97.8 | 77.7 | 1376 | 23 | 5486.5 | 2956.1 | 2906.9 | 4249.9 | 1194.2 | 0.67134 | 6.041
2024-12-09 | 16:42 | Data | 0 | 32.339 | 30.394 | 186.539 | 7.64 | 175.148 | 2117.68 | 26 | 45.908 | 6.35 | 1.348 | 4.683 | 8467.87 | 1.897 | 97.8 | 77.6 | 1376 | 22.95 | 5504.1 | 2907.5 | 2896.9 | 4227.8 | 1194.2 | 0.66748 | 6.032
2024-12-09 | 16:42 | Data | 0 | 32.494 | 30.637 | 186.539 | 7.64 | 175.238 | 2117.68 | 26 | 45.998 | 6.34 | 1.343 | 4.679 | 8472.39 | 2.046 | 97.8 | 77.7 | 1376 | 22.95 | 5507.1 | 2917.3 | 2870.2 | 4215.7 | 1194.2 | 0.67449 | 6.022
2024-12-09 | 16:42 | Data | 0 | 32.501 | 30.651 | 186.629 | 7.64 | 175.238 | 2117.68 | 26 | 45.998 | 6.35 | 1.349 | 4.674 | 8472.39 | 1.85 | 97.8 | 77.6 | 1376 | 23 | 5507.1 | 2924.8 | 2850.7 | 4203.8 | 1194.2 | 0.67826 | 6.026
2024-12-09 | 16:42 | Data | 0 | 32.494 | 30.631 | 186.358 | 7.64 | 175.193 | 2117.68 | 26 | 45.998 | 6.35 | 1.348 | 4.664 | 8454.3 | 1.877 | 97.8 | 77.6 | 1376 | 23.04 | 5495.3 | 2910 | 2854.2 | 4194.4 | 1194.2 | 0.67904 | 6.013
2024-12-09 | 16:42 | Data | 0 | 32.413 | 30.415 | 186.81 | 7.64 | 175.51 | 2116.78 | 26 | 45.818 | 6.35 | 1.345 | 4.64 | 8458.83 | 2.059 | 97.8 | 77.5 | 1376 | 22.86 | 5498.2 | 2916.1 | 2824.8 | 4181 | 1194.2 | 0.67914 | 5.985
2024-12-09 | 16:42 | Data | 0 | 32.494 | 30.415 | 186.81 | 7.64 | 175.464 | 2118.58 | 26.01 | 45.818 | 6.35 | 1.346 | 4.675 | 8445.26 | 2.079 | 97.8 | 77.6 | 1377 | 22.95 | 5489.4 | 2953 | 2835.6 | 4224.2 | 1194.2 | 0.68007 | 6.02
2024-12-09 | 16:42 | Data | 0 | 32.521 | 30.415 | 186.765 | 7.64 | 175.419 | 2119.49 | 26 | 45.998 | 6.35 | 1.345 | 4.647 | 8418.13 | 2.093 | 97.8 | 77.6 | 1378 | 23 | 5471.8 | 2924.2 | 2857.4 | 4209.6 | 1194.2 | 0.6788 | 5.992
2024-12-09 | 16:42 | Data | 0 | 32.663 | 30.921 | 186.946 | 7.64 | 175.555 | 2111.35 | 26 | 45.727 | 6.35 | 1.353 | 4.69 | 8431.69 | 1.992 | 97.8 | 77.6 | 1372 | 22.86 | 5480.6 | 2927.6 | 2885.1 | 4237.3 | 1194.2 | 0.67014 | 6.043
2024-12-09 | 16:42 | Data | 0 | 32.892 | 30.651 | 186.946 | 7.64 | 175.555 | 2111.35 | 26 | 45.998 | 6.35 | 1.349 | 4.683 | 8431.69 | 2.12 | 97.8 | 77.6 | 1373 | 23 | 5480.6 | 2927.5 | 2841.9 | 4203.5 | 1194.2 | 0.67744 | 6.032
2024-12-09 | 16:42 | Data | 0 | 32.723 | 30.766 | 186.855 | 7.64 | 175.51 | 2114.97 | 26 | 45.998 | 6.35 | 1.352 | 4.669 | 8418.13 | 2.073 | 97.8 | 77.5 | 1374 | 23 | 5471.8 | 2915.3 | 2869.1 | 4212.4 | 1194.2 | 0.67433 | 6.021
2024-12-09 | 16:42 | Data | 0 | 32.609 | 30.59 | 186.81 | 7.64 | 175.555 | 2114.06 | 26 | 45.998 | 6.34 | 1.355 | 4.675 | 8418.13 | 2.106 | 97.8 | 77.5 | 1374 | 22.95 | 5471.8 | 2931.2 | 2844.7 | 4209.1 | 1194.2 | 0.67986 | 6.03
2024-12-09 | 16:42 | Data | 0 | 32.494 | 30.442 | 186.901 | 7.64 | 175.464 | 2113.16 | 26 | 45.998 | 6.35 | 1.345 | 4.724 | 8404.56 | 1.978 | 97.8 | 77.8 | 1374 | 22.95 | 5463 | 2927.4 | 2843.6 | 4201.1 | 1194.2 | 0.68106 | 6.069
2024-12-09 | 16:42 | Data | 0 | 32.507 | 30.421 | 186.946 | 7.64 | 175.51 | 2114.06 | 26 | 45.998 | 6.35 | 1.339 | 4.702 | 8409.08 | 2.073 | 97.8 | 77.8 | 1374 | 23 | 5465.9 | 2922.7 | 2843.6 | 4195.1 | 1194.2 | 0.67811 | 6.042
2024-12-09 | 16:42 | Data | 0 | 32.69 | 30.637 | 186.901 | 7.64 | 175.555 | 2114.06 | 26 | 45.908 | 6.35 | 1.345 | 4.709 | 8418.13 | 2.167 | 97.8 | 77.8 | 1374 | 22.95 | 5471.8 | 2948.9 | 2837.6 | 4210 | 1194.2 | 0.6831 | 6.054
2024-12-09 | 16:43 | Data | 0 | 32.494 | 30.536 | 186.765 | 7.64 | 175.555 | 2114.06 | 26 | 45.998 | 6.34 | 1.354 | 4.692 | 8422.65 | 2.079 | 97.8 | 77.6 | 1375 | 23 | 5474.7 | 2924.9 | 2853.2 | 4205.2 | 1194.2 | 0.67995 | 6.045
2024-12-09 | 16:43 | Data | 0 | 32.399 | 30.415 | 186.855 | 7.64 | 175.51 | 2114.06 | 26 | 45.998 | 6.35 | 1.343 | 4.69 | 8418.13 | 1.863 | 97.8 | 77.7 | 1375 | 23 | 5471.8 | 2950.6 | 2821.2 | 4200.6 | 1194.2 | 0.68442 | 6.033
2024-12-09 | 16:43 | Data | 0 | 32.737 | 30.651 | 187.036 | 7.64 | 175.555 | 2114.06 | 26 | 45.998 | 6.35 | 1.351 | 4.669 | 8431.69 | 1.87 | 97.8 | 77.6 | 1374 | 23 | 5480.6 | 2945.2 | 2837.1 | 4211.1 | 1194.2 | 0.6826 | 6.018
2024-12-09 | 16:43 | Data | 0 | 32.541 | 30.415 | 186.855 | 7.64 | 175.464 | 2113.16 | 26 | 45.998 | 6.35 | 1.357 | 4.671 | 8409.08 | 2.093 | 97.8 | 77.5 | 1374 | 23 | 5465.9 | 2927.9 | 2831.5 | 4193.6 | 1194.2 | 0.68194 | 6.028
2024-12-09 | 16:43 | Data | 0 | 32.548 | 30.577 | 186.901 | 7.64 | 175.6 | 2114.06 | 26 | 45.998 | 6.34 | 1.361 | 4.674 | 8445.26 | 1.965 | 97.8 | 77.4 | 1374 | 22.95 | 5489.4 | 2928.6 | 2842.3 | 4202.6 | 1194.2 | 0.67955 | 6.036
2024-12-09 | 16:43 | Data | 0 | 32.501 | 30.59 | 186.765 | 7.64 | 175.555 | 2113.16 | 26 | 45.908 | 6.35 | 1.361 | 4.642 | 8458.83 | 1.904 | 97.8 | 77.3 | 1374 | 23 | 5498.2 | 2933.1 | 2857.6 | 4217.1 | 1194.2 | 0.67834 | 6.003
2024-12-09 | 16:43 | Data | 0 | 32.609 | 31.015 | 186.991 | 7.64 | 175.555 | 2114.06 | 26 | 45.998 | 6.35 | 1.357 | 4.648 | 8427.17 | 2.1 | 97.8 | 77.4 | 1374 | 23 | 5477.7 | 2924.5 | 2871.1 | 4217.2 | 1194.2 | 0.68012 | 6.005
2024-12-09 | 16:43 | Data | 0 | 32.723 | 30.543 | 186.991 | 7.64 | 175.555 | 2114.06 | 26 | 45.998 | 6.34 | 1.347 | 4.688 | 8431.69 | 2.241 | 97.8 | 77.7 | 1374 | 23 | 5480.6 | 2915.5 | 2846.7 | 4198.2 | 1194.2 | 0.6778 | 6.035
2024-12-09 | 16:43 | Data | 0 | 32.717 | 30.543 | 186.855 | 7.64 | 175.464 | 2114.97 | 26.01 | 45.908 | 6.35 | 1.339 | 4.676 | 8431.69 | 2.012 | 97.8 | 77.7 | 1374 | 22.95 | 5480.6 | 2921.3 | 2834.7 | 4184.4 | 1194.3 | 0.68128 | 6.017
2024-12-09 | 16:43 | Data | 0 | 32.501 | 30.428 | 186.81 | 7.64 | 175.555 | 2116.78 | 26.01 | 46.089 | 6.35 | 1.343 | 4.673 | 8427.17 | 2.019 | 97.8 | 77.7 | 1376 | 23 | 5477.7 | 2851.4 | 2841.5 | 4142 | 1194.3 | 0.67235 | 6.016
2024-12-09 | 16:43 | Data | 0 | 32.723 | 30.651 | 186.901 | 7.64 | 175.51 | 2117.68 | 26.01 | 45.998 | 6.35 | 1.341 | 4.67 | 8422.65 | 2.073 | 97.8 | 77.7 | 1377 | 22.95 | 5474.7 | 2861.9 | 2805.1 | 4124.2 | 1194.3 | 0.67842 | 6.011
2024-12-09 | 16:43 | Data | 0 | 32.332 | 30.415 | 186.765 | 7.64 | 175.464 | 2111.35 | 26 | 45.998 | 6.35 | 1.346 | 4.681 | 8418.13 | 1.877 | 97.8 | 77.7 | 1373 | 23 | 5471.8 | 2848.7 | 2819.4 | 4123.8 | 1194.3 | 0.67377 | 6.027
2024-12-09 | 16:43 | Data | 0 | 32.494 | 30.651 | 186.72 | 7.64 | 175.464 | 2117.68 | 26 | 45.908 | 6.35 | 1.348 | 4.682 | 8431.69 | 1.958 | 97.8 | 77.6 | 1376 | 22.95 | 5480.6 | 2864.3 | 2813.8 | 4131.5 | 1194.3 | 0.67605 | 6.029
2024-12-09 | 16:43 | Data | 0 | 32.582 | 30.624 | 186.765 | 7.64 | 175.419 | 2120.39 | 26 | 45.908 | 6.35 | 1.342 | 4.656 | 8431.69 | 2.1 | 97.8 | 77.6 | 1378 | 22.91 | 5480.6 | 2858.9 | 2821.7 | 4130.3 | 1194.3 | 0.67612 | 5.998
2024-12-09 | 16:43 | Data | 0 | 32.892 | 30.651 | 186.991 | 7.64 | 175.555 | 2119.49 | 26.01 | 45.998 | 6.35 | 1.341 | 4.657 | 8431.69 | 2.079 | 97.8 | 77.6 | 1378 | 23 | 5480.6 | 2874.3 | 2845.2 | 4156.1 | 1194.3 | 0.67534 | 5.998
2024-12-09 | 16:43 | Data | 0 | 33.048 | 30.563 | 186.855 | 7.64 | 175.6 | 2114.06 | 26 | 45.727 | 6.35 | 1.342 | 4.664 | 8409.08 | 2.1 | 97.8 | 77.7 | 1374 | 22.86 | 5465.9 | 2860 | 2884.4 | 4172.4 | 1194.3 | 0.66846 | 6.006
2024-12-09 | 16:43 | Data | 0 | 32.521 | 30.475 | 186.901 | 7.64 | 175.51 | 2120.39 | 26 | 45.998 | 6.35 | 1.339 | 4.693 | 8418.13 | 1.857 | 97.8 | 77.8 | 1378 | 23 | 5471.8 | 2854.3 | 2864 | 4157.7 | 1194.3 | 0.67032 | 6.033
2024-12-09 | 16:44 | Data | 0 | 32.305 | 30.361 | 186.72 | 7.64 | 175.464 | 2117.68 | 26 | 46.089 | 6.34 | 1.356 | 4.673 | 8418.13 | 2.066 | 97.8 | 77.5 | 1376 | 23 | 5471.8 | 2839.4 | 2880.7 | 4166.8 | 1194.3 | 0.66724 | 6.029
2024-12-09 | 16:44 | Data | 0 | 32.663 | 30.847 | 186.855 | 7.64 | 175.51 | 2117.68 | 26.01 | 45.908 | 6.35 | 1.347 | 4.662 | 8409.08 | 1.904 | 97.8 | 77.6 | 1376 | 23 | 5465.9 | 2907.3 | 2891.2 | 4217.5 | 1194.3 | 0.67199 | 6.007
2024-12-09 | 16:44 | Data | 0 | 32.622 | 30.428 | 186.674 | 7.64 | 175.51 | 2114.06 | 26 | 45.998 | 6.34 | 1.344 | 4.648 | 8427.17 | 2.079 | 97.8 | 77.6 | 1374 | 23 | 5477.7 | 2913.1 | 2876.3 | 4211.3 | 1194.3 | 0.67403 | 5.992
2024-12-09 | 16:44 | Data | 0 | 32.528 | 30.597 | 186.81 | 7.64 | 175.555 | 2113.16 | 26.01 | 45.908 | 6.35 | 1.345 | 4.68 | 8454.3 | 1.904 | 97.8 | 77.7 | 1374 | 22.95 | 5495.3 | 2903.4 | 2849 | 4191 | 1194.3 | 0.6745 | 6.025
2024-12-09 | 16:44 | Data | 0 | 32.264 | 30.327 | 186.674 | 7.65 | 175.374 | 2119.49 | 25.99 | 45.998 | 6.34 | 1.356 | 4.692 | 8431.69 | 2.14 | 97.8 | 77.6 | 1377 | 23 | 5480.6 | 2897.3 | 2831.3 | 4168.3 | 1194.3 | 0.67847 | 6.046
2024-12-09 | 16:44 | Data | 0 | 32.501 | 30.637 | 186.901 | 7.64 | 175.464 | 2116.78 | 26.01 | 45.998 | 6.35 | 1.359 | 4.685 | 8445.26 | 1.897 | 97.8 | 77.5 | 1376 | 23 | 5489.4 | 2925.2 | 2830.1 | 4189.1 | 1194.3 | 0.68028 | 6.045
2024-12-09 | 16:44 | Data | 0 | 32.359 | 30.408 | 186.901 | 7.64 | 175.51 | 2117.68 | 26 | 45.998 | 6.35 | 1.348 | 4.707 | 8440.74 | 1.904 | 97.8 | 77.7 | 1376 | 22.95 | 5486.5 | 2909 | 2834.9 | 4183.1 | 1194.3 | 0.67839 | 6.055
2024-12-09 | 16:44 | Data | 0 | 32.582 | 30.469 | 186.81 | 7.64 | 175.419 | 2116.78 | 26.01 | 45.908 | 6.35 | 1.352 | 4.695 | 8856.78 | 2.235 | 97.8 | 77.6 | 1376 | 23 | 5756.9 | 2902.4 | 2841.1 | 4176.9 | 1194.3 | 0.67894 | 6.047
2024-12-09 | 16:44 | Data | 0 | 32.474 | 30.415 | 186.72 | 7.64 | 175.464 | 2117.68 | 26 | 45.998 | 6.35 | 1.348 | 4.675 | 8445.26 | 2.079 | 97.8 | 77.6 | 1376 | 22.95 | 5489.4 | 2913.5 | 2839.9 | 4187.7 | 1194.3 | 0.67792 | 6.024
2024-12-09 | 16:44 | Data | 0 | 32.44 | 30.374 | 186.765 | 7.64 | 175.464 | 2117.68 | 26.01 | 45.998 | 6.35 | 1.348 | 4.697 | 8431.69 | 2.16 | 97.8 | 77.7 | 1376 | 23 | 5480.6 | 2924.3 | 2863.6 | 4210.4 | 1194.3 | 0.67852 | 6.046
2024-12-09 | 16:44 | Data | 0 | 32.501 | 30.536 | 186.991 | 7.64 | 175.555 | 2116.78 | 26 | 45.998 | 6.35 | 1.347 | 4.682 | 8445.26 | 2.079 | 97.8 | 77.7 | 1376 | 22.95 | 5489.4 | 2899.1 | 2886.6 | 4210.7 | 1194.3 | 0.67136 | 6.027
2024-12-09 | 16:44 | Data | 0 | 32.44 | 30.442 | 186.765 | 7.64 | 175.329 | 2116.78 | 25.99 | 46.089 | 6.35 | 1.341 | 4.682 | 8409.08 | 1.85 | 97.8 | 77.7 | 1376 | 23.04 | 5465.9 | 2895.8 | 2859.9 | 4189.6 | 1194.3 | 0.67352 | 6.023
2024-12-09 | 16:44 | Data | 0 | 32.858 | 30.556 | 186.81 | 7.64 | 175.555 | 2118.58 | 26.01 | 45.998 | 6.35 | 1.351 | 4.683 | 8381.95 | 2.181 | 97.8 | 77.6 | 1376 | 22.95 | 5448.3 | 2923 | 2859.1 | 4208.6 | 1194.3 | 0.67352 | 6.033
2024-12-09 | 16:44 | Data | 0 | 32.291 | 30.361 | 186.72 | 7.64 | 175.329 | 2114.97 | 26 | 45.908 | 6.35 | 1.346 | 4.703 | 8386.47 | 2.073 | 97.8 | 77.7 | 1374 | 23 | 5451.2 | 2910.8 | 2854.9 | 4200.7 | 1194.3 | 0.67651 | 6.048
2024-12-09 | 16:44 | Data | 0 | 32.494 | 30.415 | 186.72 | 7.64 | 175.419 | 2118.58 | 26.01 | 45.998 | 6.35 | 1.339 | 4.692 | 8381.95 | 2.079 | 97.8 | 77.8 | 1376 | 23 | 5448.3 | 2928 | 2819.2 | 4182.1 | 1194.3 | 0.68348 | 6.031
2024-12-09 | 16:44 | Data | 0 | 32.663 | 30.523 | 186.765 | 7.64 | 175.464 | 2114.97 | 26 | 45.908 | 6.35 | 1.34 | 4.686 | 8418.13 | 2.073 | 97.8 | 77.8 | 1374 | 22.95 | 5471.8 | 2883.2 | 2837.1 | 4173.6 | 1194.3 | 0.67333 | 6.026
2024-12-09 | 16:44 | Data | 0 | 32.325 | 30.415 | 186.629 | 7.64 | 175.419 | 2114.06 | 26 | 45.908 | 6.35 | 1.339 | 4.671 | 8400.04 | 1.884 | 97.8 | 77.7 | 1374 | 23 | 5460 | 2934.9 | 2827 | 4192.2 | 1194.3 | 0.68332 | 6.01
2024-12-09 | 16:44 | Data | 0 | 32.379 | 30.806 | 186.72 | 7.64 | 175.419 | 2114.97 | 26.01 | 45.998 | 6.35 | 1.339 | 4.685 | 8418.13 | 2.046 | 97.8 | 77.8 | 1374 | 23 | 5471.8 | 2904.8 | 2832.3 | 4175.3 | 1194.3 | 0.67903 | 6.025
2024-12-09 | 16:45 | Data | 0 | 32.609 | 30.428 | 186.72 | 7.64 | 175.329 | 2117.68 | 26 | 45.908 | 6.35 | 1.338 | 4.683 | 8409.08 | 1.965 | 97.8 | 77.8 | 1376 | 23 | 5465.9 | 2901.5 | 2834.6 | 4173.9 | 1194.3 | 0.6814 | 6.02
2024-12-09 | 16:45 | Data | 0 | 32.494 | 30.415 | 186.72 | 7.64 | 175.419 | 2111.35 | 26.01 | 45.998 | 6.34 | 1.345 | 4.681 | 8400.04 | 2.079 | 97.8 | 77.7 | 1372 | 23 | 5460 | 2875.9 | 2824.7 | 4152.1 | 1194.3 | 0.67564 | 6.026
2024-12-09 | 16:45 | Data | 0 | 32.649 | 30.313 | 186.539 | 7.64 | 175.193 | 2104.12 | 26.01 | 45.908 | 6.35 | 1.343 | 4.695 | 8395.51 | 2.1 | 97.8 | 77.8 | 1368 | 22.95 | 5457.1 | 2908.4 | 2866.2 | 4193.8 | 1194.3 | 0.674 | 6.038
2024-12-09 | 16:45 | Data | 0 | 32.487 | 30.415 | 186.674 | 7.64 | 175.374 | 2111.35 | 26 | 45.908 | 6.35 | 1.351 | 4.674 | 8400.04 | 2.079 | 97.8 | 77.6 | 1372 | 23 | 5460 | 2884.1 | 2865.2 | 4184.6 | 1194.3 | 0.67162 | 6.026
2024-12-09 | 16:45 | Data | 0 | 32.609 | 30.475 | 186.855 | 7.64 | 175.464 | 2111.35 | 26 | 45.908 | 6.35 | 1.347 | 4.684 | 8400.04 | 2.167 | 97.8 | 77.7 | 1373 | 23 | 5460 | 2892.6 | 2869.8 | 4192.4 | 1194.3 | 0.67209 | 6.031
2024-12-09 | 16:45 | Data | 0 | 32.777 | 30.428 | 186.946 | 7.64 | 175.51 | 2114.06 | 25.99 | 45.998 | 6.35 | 1.34 | 4.69 | 8418.13 | 1.998 | 97.8 | 77.8 | 1374 | 23 | 5471.8 | 2897.6 | 2860.4 | 4191.6 | 1194.3 | 0.67294 | 6.03
2024-12-09 | 16:45 | Data | 0 | 32.703 | 30.374 | 186.72 | 7.64 | 175.51 | 2114.06 | 26 | 46.089 | 6.34 | 1.339 | 4.686 | 8431.69 | 2.289 | 97.8 | 77.8 | 1374 | 23 | 5480.6 | 2888.5 | 2829.3 | 4157.1 | 1194.3 | 0.67753 | 6.026
2024-12-09 | 16:45 | Data | 0 | 32.42 | 30.307 | 186.81 | 7.64 | 175.419 | 2117.68 | 26.02 | 45.908 | 6.35 | 1.345 | 4.7 | 8418.13 | 1.863 | 97.8 | 77.8 | 1376 | 23 | 5471.8 | 2892.5 | 2793.1 | 4141 | 1194.3 | 0.68204 | 6.045
2024-12-09 | 16:45 | Data | 0 | 32.487 | 30.307 | 186.629 | 7.64 | 175.374 | 2114.97 | 26.02 | 45.998 | 6.35 | 1.332 | 4.685 | 8418.13 | 2.167 | 97.8 | 77.8 | 1375 | 23 | 5471.8 | 2905.6 | 2783 | 4140.5 | 1194.4 | 0.68559 | 6.019
2024-12-09 | 16:45 | Data | 0 | 32.467 | 30.246 | 186.765 | 7.64 | 175.419 | 2114.06 | 26.02 | 45.998 | 6.35 | 1.344 | 4.665 | 8422.65 | 2.174 | 97.8 | 77.6 | 1374 | 22.95 | 5474.7 | 2909.9 | 2799.9 | 4153.4 | 1194.4 | 0.68354 | 6.01
2024-12-09 | 16:45 | Data | 0 | 32.609 | 30.205 | 186.765 | 7.65 | 175.419 | 2114.06 | 26.02 | 45.998 | 6.34 | 1.34 | 4.677 | 8418.13 | 2.073 | 97.8 | 77.7 | 1374 | 23 | 5471.8 | 2898.8 | 2803.3 | 4158.6 | 1194.4 | 0.67868 | 6.018
2024-12-09 | 16:45 | Data | 0 | 32.521 | 30.415 | 186.81 | 7.64 | 175.374 | 2114.97 | 26.02 | 45.998 | 6.35 | 1.346 | 4.681 | 8431.69 | 2.079 | 97.8 | 77.7 | 1375 | 23 | 5480.6 | 2902.1 | 2864.1 | 4193.8 | 1194.4 | 0.6745 | 6.026
2024-12-09 | 16:45 | Data | 0 | 32.278 | 30.401 | 186.72 | 7.64 | 175.419 | 2111.35 | 26.02 | 45.998 | 6.35 | 1.348 | 4.638 | 8359.34 | 1.911 | 97.8 | 77.5 | 1372 | 23 | 5433.6 | 2899.6 | 2879.5 | 4200 | 1194.4 | 0.67306 | 5.986
2024-12-09 | 16:45 | Data | 0 | 32.548 | 30.374 | 186.81 | 7.64 | 175.51 | 2111.35 | 26.02 | 45.998 | 6.35 | 1.344 | 4.679 | 8377.43 | 1.911 | 97.8 | 77.7 | 1372 | 22.95 | 5445.3 | 2889.6 | 2858 | 4181.9 | 1194.4 | 0.67413 | 6.023
2024-12-09 | 16:45 | Data | 0 | 32.379 | 30.475 | 186.72 | 7.64 | 175.419 | 2111.35 | 26.02 | 45.998 | 6.34 | 1.339 | 4.662 | 8377.43 | 2.14 | 97.8 | 77.7 | 1372 | 23 | 5445.3 | 2891.9 | 2876.3 | 4195.2 | 1194.4 | 0.67335 | 6.001
2024-12-09 | 16:45 | Data | 0 | 32.413 | 30.219 | 186.855 | 7.64 | 175.51 | 2109.54 | 26.02 | 45.908 | 6.35 | 1.345 | 4.668 | 8363.86 | 2.025 | 97.8 | 77.6 | 1371 | 22.95 | 5436.5 | 2894.4 | 2858.5 | 4183.5 | 1194.4 | 0.67499 | 6.013
2024-12-09 | 16:46 | Data | 0 | 32.71 | 30.793 | 186.855 | 7.64 | 175.374 | 2111.35 | 26.02 | 45.998 | 6.35 | 1.353 | 4.669 | 8454.3 | 1.931 | 97.8 | 77.5 | 1372 | 23 | 5495.3 | 2904.4 | 2818.5 | 4160.1 | 1194.4 | 0.68099 | 6.022
2024-12-09 | 16:46 | Data | 0 | 32.494 | 30.415 | 186.72 | 7.64 | 175.51 | 2111.35 | 26.02 | 46.089 | 6.35 | 1.352 | 4.67 | 8445.26 | 2.079 | 97.8 | 77.5 | 1372 | 23.04 | 5489.4 | 2893 | 2814 | 4152.8 | 1194.4 | 0.6814 | 6.023
2024-12-09 | 16:46 | Data | 0 | 32.669 | 30.752 | 186.901 | 7.64 | 175.464 | 2111.35 | 26.01 | 45.998 | 6.34 | 1.356 | 4.66 | 8445.26 | 1.958 | 97.8 | 77.5 | 1373 | 23 | 5489.4 | 2890.9 | 2815.1 | 4153.3 | 1194.4 | 0.68005 | 6.016
2024-12-09 | 16:46 | Data | 0 | 32.271 | 30.212 | 186.855 | 7.64 | 175.464 | 2111.35 | 26.01 | 45.908 | 6.35 | 1.344 | 4.681 | 8454.3 | 1.971 | 97.8 | 77.7 | 1372 | 23 | 5495.3 | 2898.1 | 2800.3 | 4143.9 | 1194.4 | 0.68232 | 6.025
2024-12-09 | 16:46 | Data | 0 | 32.575 | 30.415 | 186.855 | 7.64 | 175.419 | 2109.54 | 26.03 | 45.998 | 6.34 | 1.347 | 4.68 | 8454.3 | 2.1 | 97.8 | 77.7 | 1371 | 22.95 | 5495.3 | 2909.6 | 2825.9 | 4172.5 | 1194.4 | 0.68018 | 6.026
2024-12-09 | 16:46 | Data | 0 | 32.325 | 30.3 | 186.72 | 7.64 | 175.419 | 2110.45 | 26.03 | 45.908 | 6.34 | 1.352 | 4.686 | 8454.3 | 2.079 | 97.8 | 77.6 | 1372 | 23 | 5495.3 | 2904.2 | 2834.3 | 4171.3 | 1194.4 | 0.68076 | 6.039
2024-12-09 | 16:46 | Data | 0 | 32.48 | 30.415 | 186.674 | 7.64 | 175.419 | 2106.83 | 26.02 | 45.998 | 6.35 | 1.339 | 4.689 | 8454.3 | 2.167 | 97.8 | 77.8 | 1369 | 23 | 5495.3 | 2907.7 | 2835.1 | 4178.4 | 1194.4 | 0.67866 | 6.027
2024-12-09 | 16:46 | Data | 0 | 32.501 | 30.415 | 186.765 | 7.64 | 175.464 | 2118.58 | 26.01 | 45.998 | 6.35 | 1.332 | 4.645 | 8454.3 | 1.911 | 97.8 | 77.7 | 1377 | 23 | 5495.3 | 2883.8 | 2820 | 4153.6 | 1194.4 | 0.67796 | 5.978
2024-12-09 | 16:46 | Data | 0 | 32.271 | 30.536 | 186.72 | 7.64 | 175.419 | 2114.97 | 26.02 | 45.998 | 6.35 | 1.345 | 4.665 | 8427.17 | 1.857 | 97.8 | 77.6 | 1375 | 23 | 5477.7 | 2892.9 | 2821.1 | 4156.5 | 1194.4 | 0.6788 | 6.009
2024-12-09 | 16:46 | Data | 0 | 32.156 | 30.212 | 186.81 | 7.65 | 175.464 | 2118.58 | 26.02 | 45.908 | 6.35 | 1.356 | 4.67 | 8431.69 | 2.127 | 97.8 | 77.5 | 1376 | 22.95 | 5480.6 | 2888.4 | 2826.5 | 4159.6 | 1194.4 | 0.67772 | 6.026
2024-12-09 | 16:46 | Data | 0 | 32.548 | 30.624 | 186.72 | 7.64 | 175.419 | 2116.78 | 26.02 | 45.998 | 6.35 | 1.345 | 4.675 | 8431.69 | 1.877 | 97.8 | 77.7 | 1375 | 23 | 5480.6 | 2884 | 2819.6 | 4152.6 | 1194.4 | 0.67933 | 6.02
2024-12-09 | 16:46 | Data | 0 | 32.879 | 30.475 | 186.81 | 7.64 | 175.555 | 2117.68 | 26.03 | 45.998 | 6.35 | 1.346 | 4.704 | 8431.69 | 2.221 | 97.8 | 77.8 | 1376 | 22.95 | 5480.6 | 2896.4 | 2818.9 | 4165.2 | 1194.4 | 0.68091 | 6.05
2024-12-09 | 16:46 | Data | 0 | 32.777 | 30.334 | 186.765 | 7.64 | 175.464 | 2116.78 | 26.02 | 45.998 | 6.35 | 1.352 | 4.672 | 8481.44 | 2.275 | 97.8 | 77.6 | 1376 | 23 | 5512.9 | 2897.2 | 2825.1 | 4159.9 | 1194.4 | 0.67845 | 6.024
2024-12-09 | 16:46 | Data | 0 | 32.669 | 30.752 | 186.81 | 7.65 | 175.6 | 2118.58 | 26.02 | 45.998 | 6.34 | 1.361 | 4.657 | 8485.96 | 2.046 | 97.8 | 77.4 | 1376 | 22.95 | 5515.9 | 2888.9 | 2811.2 | 4153.1 | 1194.4 | 0.67789 | 6.019
2024-12-09 | 16:46 | Data | 0 | 32.595 | 30.84 | 186.855 | 7.64 | 175.374 | 2117.68 | 26.02 | 45.998 | 6.35 | 1.357 | 4.641 | 8476.91 | 2.1 | 97.8 | 77.4 | 1376 | 23 | 5510 | 2877.8 | 2822.1 | 4151 | 1194.4 | 0.67623 | 5.997
2024-12-09 | 16:46 | Data | 0 | 32.44 | 30.482 | 186.81 | 7.64 | 175.419 | 2120.39 | 26.01 | 45.998 | 6.35 | 1.338 | 4.689 | 8467.87 | 2.309 | 97.8 | 77.8 | 1378 | 23 | 5504.1 | 2887.2 | 2844.3 | 4171.4 | 1194.4 | 0.67555 | 6.027
2024-12-09 | 16:46 | Data | 0 | 32.831 | 30.34 | 186.855 | 7.64 | 175.51 | 2123.1 | 26.03 | 45.908 | 6.35 | 1.339 | 4.674 | 8445.26 | 2.106 | 97.8 | 77.7 | 1380 | 22.95 | 5489.4 | 2887.2 | 2865.2 | 4186.2 | 1194.4 | 0.6729 | 6.013
2024-12-09 | 16:46 | Data | 0 | 32.339 | 30.192 | 186.81 | 7.64 | 175.51 | 2125.81 | 26.03 | 45.998 | 6.35 | 1.348 | 4.676 | 8431.69 | 2.079 | 97.8 | 77.6 | 1381 | 23 | 5480.6 | 2904.8 | 2844.1 | 4182.1 | 1194.4 | 0.67768 | 6.024
2024-12-09 | 16:47 | Data | 0 | 32.494 | 30.415 | 186.72 | 7.64 | 175.419 | 2124.91 | 26.02 | 45.998 | 6.35 | 1.347 | 4.651 | 8449.78 | 2.079 | 97.8 | 77.5 | 1381 | 23 | 5492.4 | 2906.8 | 2851.6 | 4184.5 | 1194.4 | 0.67778 | 5.998
2024-12-09 | 16:47 | Data | 0 | 32.278 | 30.415 | 186.674 | 7.64 | 175.419 | 2123.1 | 26.01 | 45.998 | 6.34 | 1.341 | 4.649 | 8427.17 | 1.971 | 97.8 | 77.6 | 1379 | 23 | 5477.7 | 2901.8 | 2870.5 | 4200.7 | 1194.4 | 0.6748 | 5.99
2024-12-09 | 16:47 | Data | 0 | 32.494 | 30.536 | 186.72 | 7.64 | 175.419 | 2123.1 | 26.02 | 45.998 | 6.35 | 1.348 | 4.656 | 8440.74 | 2.073 | 97.8 | 77.6 | 1380 | 23.04 | 5486.5 | 2891.6 | 2825.5 | 4162.8 | 1194.4 | 0.67978 | 6.003
2024-12-09 | 16:47 | Data | 0 | 32.609 | 30.678 | 186.901 | 7.64 | 175.6 | 2118.58 | 26.02 | 45.908 | 6.34 | 1.352 | 4.688 | 8440.74 | 2.012 | 97.8 | 77.6 | 1377 | 23 | 5486.5 | 2885.8 | 2849.5 | 4173.8 | 1194.4 | 0.67527 | 6.04
2024-12-09 | 16:47 | Data | 0 | 32.386 | 30.3 | 186.81 | 7.64 | 175.464 | 2120.39 | 26.02 | 45.998 | 6.35 | 1.339 | 4.69 | 8445.26 | 2.066 | 97.8 | 77.8 | 1378 | 23 | 5489.4 | 2901.3 | 2845.5 | 4178 | 1194.4 | 0.67616 | 6.028
2024-12-09 | 16:47 | Data | 0 | 32.325 | 30.415 | 186.81 | 7.64 | 175.419 | 2122.2 | 26.02 | 45.998 | 6.35 | 1.357 | 4.676 | 8445.26 | 1.863 | 97.8 | 77.5 | 1380 | 23 | 5489.4 | 2900.3 | 2854.2 | 4182.5 | 1194.4 | 0.67807 | 6.034
2024-12-09 | 16:47 | Data | 0 | 32.636 | 30.361 | 186.81 | 7.64 | 175.555 | 2122.2 | 26.01 | 45.998 | 6.35 | 1.352 | 4.672 | 8395.51 | 1.971 | 97.8 | 77.6 | 1379 | 23 | 5457.1 | 2898.7 | 2850.6 | 4182.6 | 1194.4 | 0.67518 | 6.023
2024-12-09 | 16:47 | Data | 0 | 32.487 | 30.529 | 186.72 | 7.64 | 175.419 | 2124.91 | 26.02 | 45.998 | 6.35 | 1.349 | 4.668 | 8418.13 | 1.965 | 97.8 | 77.6 | 1382 | 23 | 5471.8 | 2872.9 | 2856.6 | 4170.1 | 1194.4 | 0.67246 | 6.017
2024-12-09 | 16:47 | Data | 0 | 32.453 | 30.415 | 186.765 | 7.65 | 175.51 | 2124.01 | 26.01 | 45.998 | 6.35 | 1.351 | 4.672 | 8390.99 | 2.073 | 97.8 | 77.6 | 1381 | 22.95 | 5454.1 | 2896.7 | 2848.8 | 4178.7 | 1194.4 | 0.67676 | 6.022
2024-12-09 | 16:47 | Data | 0 | 32.507 | 30.651 | 186.991 | 7.64 | 175.464 | 2121.29 | 26.02 | 45.998 | 6.35 | 1.345 | 4.706 | 8400.04 | 2.052 | 97.8 | 77.8 | 1379 | 23 | 5460 | 2898.9 | 2857 | 4179.7 | 1194.4 | 0.67533 | 6.052
2024-12-09 | 16:47 | Data | 0 | 32.507 | 30.448 | 186.81 | 7.64 | 175.555 | 2120.39 | 26.02 | 45.908 | 6.35 | 1.349 | 4.652 | 8409.08 | 2.019 | 97.8 | 77.5 | 1378 | 22.95 | 5465.9 | 2907.4 | 2847.6 | 4185.5 | 1194.4 | 0.677 | 6.003
2024-12-09 | 16:47 | Data | 0 | 32.467 | 30.516 | 186.81 | 7.64 | 175.419 | 2119.49 | 26.02 | 45.998 | 6.35 | 1.34 | 4.689 | 8422.65 | 2.1 | 97.8 | 77.8 | 1378 | 23 | 5474.7 | 2897.7 | 2848.5 | 4177.8 | 1194.5 | 0.67579 | 6.029
2024-12-09 | 16:47 | Data | 0 | 32.494 | 30.219 | 186.81 | 7.64 | 175.374 | 2121.29 | 26.03 | 45.998 | 6.35 | 1.344 | 4.691 | 8422.65 | 2.066 | 97.8 | 77.7 | 1378 | 23 | 5474.7 | 2885.9 | 2858 | 4179.9 | 1194.5 | 0.67437 | 6.035
2024-12-09 | 16:47 | Data | 0 | 32.649 | 30.644 | 186.81 | 7.65 | 175.374 | 2120.39 | 26.02 | 45.998 | 6.35 | 1.347 | 4.687 | 8418.13 | 2.066 | 97.8 | 77.7 | 1378 | 23 | 5471.8 | 2894.5 | 2879.4 | 4200.8 | 1194.5 | 0.67143 | 6.034
2024-12-09 | 16:47 | Data | 0 | 32.609 | 30.252 | 186.81 | 7.65 | 175.419 | 2119.49 | 26.02 | 45.998 | 6.35 | 1.346 | 4.686 | 8400.04 | 2.154 | 97.8 | 77.7 | 1378 | 22.95 | 5460 | 2881.8 | 2873.6 | 4190.4 | 1194.5 | 0.66987 | 6.031
2024-12-09 | 16:47 | Data | 0 | 32.838 | 30.442 | 186.901 | 7.64 | 175.419 | 2120.39 | 26.02 | 45.908 | 6.35 | 1.352 | 4.665 | 8395.51 | 2.228 | 97.8 | 77.5 | 1378 | 22.95 | 5457.1 | 2884.8 | 2879 | 4189.4 | 1194.5 | 0.67113 | 6.018
2024-12-09 | 16:47 | Data | 0 | 32.426 | 30.415 | 186.946 | 7.65 | 175.51 | 2120.39 | 26.02 | 45.998 | 6.35 | 1.345 | 4.656 | 8409.08 | 2.046 | 97.8 | 77.6 | 1378 | 22.95 | 5465.9 | 2890.2 | 2876.4 | 4192.6 | 1194.5 | 0.67246 | 6.001
2024-12-09 | 16:47 | Data | 0 | 32.291 | 30.415 | 186.72 | 7.64 | 175.419 | 2120.39 | 26.02 | 45.998 | 6.34 | 1.345 | 4.653 | 8400.04 | 2.073 | 97.8 | 77.6 | 1378 | 23 | 5460 | 2894.2 | 2856.7 | 4184.6 | 1194.5 | 0.67564 | 5.997
2024-12-09 | 16:48 | Data | 0 | 32.305 | 30.428 | 186.855 | 7.64 | 175.464 | 2117.68 | 26.01 | 45.998 | 6.34 | 1.348 | 4.692 | 8418.13 | 1.83 | 97.8 | 77.7 | 1376 | 22.95 | 5471.8 | 2893.3 | 2819.3 | 4159.1 | 1194.5 | 0.67856 | 6.04
2024-12-09 | 16:48 | Data | 0 | 32.663 | 30.421 | 186.901 | 7.64 | 175.464 | 2117.68 | 26.02 | 45.998 | 6.35 | 1.348 | 4.664 | 8431.69 | 2.1 | 97.8 | 77.6 | 1376 | 23 | 5480.6 | 2886.7 | 2829 | 4163.1 | 1194.5 | 0.67644 | 6.013
2024-12-09 | 16:48 | Data | 0 | 32.467 | 30.408 | 186.81 | 7.65 | 175.419 | 2117.68 | 26.02 | 45.998 | 6.35 | 1.349 | 4.677 | 8418.13 | 2.1 | 97.8 | 77.6 | 1376 | 22.95 | 5471.8 | 2888.7 | 2827 | 4157.9 | 1194.5 | 0.67797 | 6.026
2024-12-09 | 16:48 | Data | 0 | 32.723 | 30.475 | 186.81 | 7.64 | 175.51 | 2116.78 | 26.01 | 45.998 | 6.35 | 1.351 | 4.674 | 8427.17 | 2.046 | 97.8 | 77.6 | 1376 | 23 | 5477.7 | 2911.3 | 2843.7 | 4184.3 | 1194.5 | 0.67928 | 6.026
2024-12-09 | 16:48 | Data | 0 | 32.386 | 30.421 | 186.81 | 7.64 | 175.464 | 2117.68 | 26.02 | 45.998 | 6.35 | 1.351 | 4.648 | 8440.74 | 1.998 | 97.8 | 77.5 | 1377 | 23 | 5486.5 | 2896.9 | 2822.1 | 4159.5 | 1194.5 | 0.67739 | 5.998
2024-12-09 | 16:48 | Data | 0 | 32.494 | 30.415 | 186.765 | 7.64 | 175.419 | 2120.39 | 26 | 45.998 | 6.35 | 1.344 | 4.67 | 8440.74 | 2.079 | 97.8 | 77.6 | 1378 | 23 | 5486.5 | 2896.3 | 2851.5 | 4179.9 | 1194.5 | 0.67693 | 6.013
2024-12-09 | 16:48 | Data | 0 | 32.595 | 30.644 | 186.901 | 7.64 | 175.6 | 2120.39 | 26.02 | 45.908 | 6.35 | 1.346 | 4.679 | 8440.74 | 2.046 | 97.8 | 77.7 | 1378 | 23 | 5486.5 | 2904.2 | 2840.6 | 4176.6 | 1194.5 | 0.67855 | 6.026
2024-12-09 | 16:48 | Data | 0 | 32.663 | 30.658 | 186.81 | 7.64 | 175.419 | 2125.81 | 26.02 | 45.998 | 6.35 | 1.34 | 4.703 | 8431.69 | 2.046 | 97.8 | 77.8 | 1382 | 23 | 5480.6 | 2908.5 | 2841 | 4177.6 | 1194.5 | 0.67975 | 6.044
2024-12-09 | 16:48 | Data | 0 | 32.494 | 30.415 | 186.765 | 7.64 | 175.464 | 2121.29 | 26.02 | 45.998 | 6.35 | 1.343 | 4.703 | 8445.26 | 2.079 | 97.8 | 77.8 | 1379 | 23 | 5489.4 | 2901.1 | 2855.4 | 4184.3 | 1194.5 | 0.67405 | 6.046
2024-12-09 | 16:48 | Data | 0 | 32.609 | 30.651 | 186.901 | 7.64 | 175.51 | 2124.91 | 26.02 | 45.998 | 6.34 | 1.349 | 4.697 | 8445.26 | 2.059 | 97.8 | 77.7 | 1382 | 22.95 | 5489.4 | 2900.3 | 2859.5 | 4186 | 1194.5 | 0.67627 | 6.046
2024-12-09 | 16:48 | Data | 0 | 32.48 | 30.415 | 186.72 | 7.64 | 175.419 | 2123.1 | 26.02 | 45.998 | 6.35 | 1.344 | 4.705 | 8445.26 | 2.079 | 97.8 | 77.8 | 1380 | 23 | 5489.4 | 2891.4 | 2851.5 | 4175.1 | 1194.5 | 0.67515 | 6.047
2024-12-09 | 16:48 | Data | 0 | 32.453 | 30.732 | 186.901 | 7.64 | 175.51 | 2124.91 | 26.02 | 45.998 | 6.35 | 1.34 | 4.69 | 8454.3 | 1.884 | 97.8 | 77.8 | 1382 | 22.95 | 5495.3 | 2900.8 | 2841.9 | 4177.4 | 1194.5 | 0.67655 | 6.03
2024-12-09 | 16:48 | Data | 0 | 32.528 | 30.415 | 186.901 | 7.64 | 175.51 | 2125.81 | 26.02 | 45.998 | 6.35 | 1.346 | 4.681 | 8431.69 | 1.911 | 97.8 | 77.7 | 1382 | 22.95 | 5480.6 | 2886.3 | 2794.6 | 4131.9 | 1194.5 | 0.68064 | 6.026
2024-12-09 | 16:48 | Data | 0 | 32.325 | 30.415 | 186.72 | 7.64 | 175.464 | 2124.91 | 26.02 | 45.998 | 6.35 | 1.342 | 4.685 | 8427.17 | 1.87 | 97.8 | 77.7 | 1382 | 23 | 5477.7 | 2902.6 | 2805.2 | 4151.5 | 1194.5 | 0.68237 | 6.027
2024-12-09 | 16:48 | Data | 0 | 32.494 | 30.3 | 186.72 | 7.64 | 175.374 | 2123.1 | 26.02 | 45.998 | 6.34 | 1.353 | 4.697 | 8422.65 | 2.079 | 97.8 | 77.6 | 1380 | 23 | 5474.7 | 2891.5 | 2820.8 | 4159.1 | 1194.5 | 0.68116 | 6.05
2024-12-09 | 16:48 | Data | 0 | 32.494 | 30.408 | 186.81 | 7.64 | 175.374 | 2122.2 | 26.02 | 45.998 | 6.35 | 1.357 | 4.673 | 8418.13 | 2.086 | 97.8 | 77.5 | 1379 | 22.95 | 5471.8 | 2889 | 2831.2 | 4160 | 1194.5 | 0.67778 | 6.029
2024-12-09 | 16:48 | Data | 0 | 32.379 | 30.212 | 186.72 | 7.65 | 175.419 | 2123.1 | 26.02 | 45.908 | 6.35 | 1.348 | 4.664 | 8445.26 | 1.904 | 97.8 | 77.6 | 1380 | 22.95 | 5489.4 | 2881.9 | 2826.6 | 4159 | 1194.5 | 0.67643 | 6.011
2024-12-09 | 16:48 | Data | 0 | 32.885 | 30.55 | 186.991 | 7.64 | 175.6 | 2123.1 | 26.02 | 45.998 | 6.34 | 1.345 | 4.681 | 8440.74 | 2.187 | 97.8 | 77.7 | 1379 | 23 | 5486.5 | 2902.7 | 2849.3 | 4178.4 | 1194.5 | 0.6765 | 6.025
2024-12-09 | 16:49 | Data | 0 | 32.777 | 30.651 | 186.901 | 7.65 | 175.51 | 2123.1 | 26.02 | 45.998 | 6.35 | 1.348 | 4.687 | 8431.69 | 1.911 | 97.8 | 77.7 | 1379 | 23 | 5480.6 | 2888 | 2810.3 | 4182.5 | 1194.5 | 0.67728 | 6.035
2024-12-09 | 16:49 | Data | 0 | 32.386 | 30.415 | 186.855 | 7.64 | 175.555 | 2120.39 | 26.01 | 45.908 | 6.35 | 1.344 | 4.649 | 8436.21 | 2.073 | 97.8 | 77.6 | 1379 | 23 | 5483.5 | 2915.4 | 2803.5 | 4161.1 | 1194.5 | 0.68301 | 5.991
2024-12-09 | 16:49 | Data | 0 | 32.663 | 30.948 | 186.946 | 7.65 | 175.51 | 2123.1 | 26.02 | 45.998 | 6.35 | 1.344 | 4.67 | 8440.74 | 1.87 | 97.8 | 77.7 | 1380 | 23 | 5486.5 | 2871 | 2852.6 | 4165.9 | 1194.5 | 0.67259 | 6.014
2024-12-09 | 16:49 | Data | 0 | 32.501 | 30.556 | 186.81 | 7.64 | 175.555 | 2123.1 | 26.01 | 45.908 | 6.35 | 1.339 | 4.666 | 8445.26 | 2.025 | 97.8 | 77.7 | 1379 | 23 | 5489.4 | 2894.6 | 2849.5 | 4181.4 | 1194.5 | 0.67367 | 6.005
2024-12-09 | 16:49 | Data | 0 | 32.94 | 30.678 | 186.991 | 7.64 | 175.69 | 2120.39 | 26.01 | 45.998 | 6.35 | 1.341 | 4.656 | 8445.26 | 2.235 | 97.8 | 77.6 | 1378 | 23 | 5489.4 | 2896.6 | 2825 | 4158 | 1194.5 | 0.67574 | 5.998
2024-12-09 | 16:49 | Data | 0 | 32.568 | 30.543 | 186.991 | 7.64 | 175.6 | 2120.39 | 26.02 | 45.998 | 6.35 | 1.34 | 4.668 | 8454.3 | 1.958 | 97.8 | 77.7 | 1378 | 23 | 5495.3 | 2896 | 2854.7 | 4183.3 | 1194.5 | 0.67607 | 6.007
2024-12-09 | 16:49 | Data | 0 | 32.879 | 30.489 | 186.946 | 7.64 | 175.51 | 2120.39 | 26.01 | 45.998 | 6.35 | 1.343 | 4.683 | 8427.17 | 2.147 | 97.8 | 77.7 | 1378 | 23 | 5477.7 | 2898.4 | 2872.2 | 4196 | 1194.5 | 0.67541 | 6.025
2024-12-09 | 16:49 | Data | 0 | 32.602 | 30.415 | 186.901 | 7.64 | 175.51 | 2119.49 | 26.01 | 45.998 | 6.35 | 1.347 | 4.68 | 8422.65 | 2.167 | 97.8 | 77.7 | 1378 | 23 | 5474.7 | 2914.3 | 2840.2 | 4189.2 | 1194.5 | 0.67643 | 6.026
2024-12-09 | 16:49 | Data | 0 | 33.021 | 30.739 | 186.946 | 7.64 | 175.69 | 2120.39 | 26.02 | 46.089 | 6.35 | 1.339 | 4.714 | 8418.13 | 2.14 | 97.8 | 77.9 | 1378 | 23 | 5471.8 | 2904.7 | 2868.9 | 4199.9 | 1194.5 | 0.67628 | 6.054
2024-12-09 | 16:49 | Data | 0 | 32.494 | 30.421 | 186.81 | 7.64 | 175.464 | 2118.58 | 26.02 | 45.908 | 6.35 | 1.34 | 4.683 | 8418.13 | 2.073 | 97.8 | 77.7 | 1377 | 23 | 5471.8 | 2898.5 | 2869.5 | 4197.1 | 1194.5 | 0.6753 | 6.024
2024-12-09 | 16:49 | Data | 0 | 32.582 | 30.475 | 186.81 | 7.65 | 175.51 | 2119.49 | 26.02 | 45.908 | 6.35 | 1.352 | 4.683 | 8454.3 | 2.039 | 97.8 | 77.6 | 1377 | 22.95 | 5495.3 | 2898.9 | 2854.8 | 4189.9 | 1194.5 | 0.6729 | 6.036
2024-12-09 | 16:49 | Data | 0 | 32.933 | 30.664 | 186.901 | 7.65 | 175.6 | 2114.97 | 26.03 | 45.818 | 6.35 | 1.362 | 4.674 | 8454.3 | 2.086 | 97.8 | 77.4 | 1374 | 23 | 5495.3 | 2889.1 | 2830 | 4162.2 | 1194.5 | 0.67901 | 6.037
2024-12-09 | 16:49 | Data | 0 | 32.501 | 30.597 | 186.81 | 7.64 | 175.51 | 2113.16 | 26.02 | 46.089 | 6.34 | 1.356 | 4.673 | 8445.26 | 1.965 | 97.8 | 77.5 | 1374 | 23 | 5489.4 | 2910 | 2844.9 | 4189.6 | 1194.6 | 0.67655 | 6.028
2024-12-09 | 16:49 | Data | 0 | 32.656 | 30.664 | 186.72 | 7.64 | 175.464 | 2114.06 | 26.01 | 45.908 | 6.34 | 1.348 | 4.672 | 8463.35 | 2.214 | 97.8 | 77.6 | 1374 | 23 | 5501.2 | 2913.3 | 2847.9 | 4192 | 1194.6 | 0.67954 | 6.02
2024-12-09 | 16:49 | Data | 0 | 32.298 | 30.415 | 186.765 | 7.64 | 175.51 | 2114.06 | 26.02 | 46.089 | 6.35 | 1.341 | 4.704 | 8467.87 | 1.85 | 97.8 | 77.8 | 1374 | 23 | 5504.1 | 2900.4 | 2877.3 | 4202.9 | 1194.6 | 0.67486 | 6.045
2024-12-09 | 16:49 | Data | 0 | 32.507 | 30.415 | 186.81 | 7.64 | 175.51 | 2114.06 | 26.01 | 46.089 | 6.35 | 1.336 | 4.688 | 8467.87 | 2.079 | 97.8 | 77.8 | 1375 | 22.95 | 5504.1 | 2893.7 | 2864.2 | 4186.5 | 1194.6 | 0.67559 | 6.024
2024-12-09 | 16:49 | Data | 0 | 32.291 | 30.482 | 186.765 | 7.64 | 175.464 | 2113.16 | 26.02 | 45.998 | 6.35 | 1.339 | 4.675 | 8485.96 | 2.079 | 97.8 | 77.7 | 1374 | 23 | 5515.9 | 2905.7 | 2852.5 | 4192.4 | 1194.6 | 0.67796 | 6.015
2024-12-09 | 16:50 | Data | 0 | 32.494 | 30.415 | 186.72 | 7.64 | 175.419 | 2114.06 | 26.02 | 45.998 | 6.35 | 1.341 | 4.65 | 8481.44 | 2.079 | 97.8 | 77.6 | 1374 | 23 | 5512.9 | 2910.4 | 2876.4 | 4208.2 | 1194.6 | 0.67326 | 5.991
2024-12-09 | 16:50 | Data | 0 | 32.933 | 30.421 | 186.901 | 7.64 | 175.6 | 2114.97 | 26.02 | 45.998 | 6.35 | 1.352 | 4.656 | 8463.35 | 2.073 | 97.8 | 77.5 | 1375 | 23 | 5501.2 | 2901.7 | 2868.1 | 4195.1 | 1194.6 | 0.67423 | 6.008
2024-12-09 | 16:50 | Data | 0 | 32.946 | 30.658 | 186.991 | 7.64 | 175.555 | 2114.97 | 26.02 | 45.998 | 6.35 | 1.351 | 4.666 | 8454.3 | 2.241 | 97.8 | 77.5 | 1374 | 23 | 5495.3 | 2888.2 | 2862.5 | 4178.5 | 1194.6 | 0.67237 | 6.018
2024-12-09 | 16:50 | Data | 0 | 32.723 | 30.482 | 187.082 | 7.64 | 175.6 | 2114.06 | 26.01 | 45.998 | 6.34 | 1.355 | 4.698 | 8458.83 | 2.046 | 97.8 | 77.6 | 1374 | 23 | 5498.2 | 2882.4 | 2878.9 | 4193.7 | 1194.6 | 0.67015 | 6.052
2024-12-09 | 16:50 | Data | 0 | 32.696 | 30.651 | 186.855 | 7.64 | 175.555 | 2114.06 | 26.02 | 45.998 | 6.34 | 1.341 | 4.705 | 8472.39 | 2.052 | 97.8 | 77.8 | 1374 | 22.95 | 5507.1 | 2902.2 | 2868 | 4199.5 | 1194.6 | 0.67333 | 6.046
2024-12-09 | 16:50 | Data | 0 | 32.501 | 30.59 | 186.901 | 7.64 | 175.464 | 2116.78 | 26.02 | 45.998 | 6.35 | 1.347 | 4.699 | 8467.87 | 1.958 | 97.8 | 77.7 | 1376 | 23 | 5504.1 | 2883.1 | 2816.3 | 4150.1 | 1194.6 | 0.67766 | 6.045
2024-12-09 | 16:50 | Data | 0 | 32.453 | 30.637 | 186.946 | 7.64 | 175.6 | 2117.68 | 26.02 | 45.998 | 6.35 | 1.341 | 4.669 | 8445.26 | 1.863 | 97.8 | 77.7 | 1376 | 23 | 5489.4 | 2893 | 2820.8 | 4157.8 | 1194.6 | 0.67954 | 6.01
2024-12-09 | 16:50 | Data | 0 | 32.521 | 30.536 | 186.901 | 7.64 | 175.555 | 2117.68 | 26.02 | 46.089 | 6.34 | 1.348 | 4.697 | 8458.83 | 1.965 | 97.8 | 77.7 | 1376 | 23 | 5498.2 | 2888 | 2854 | 4180.1 | 1194.6 | 0.67347 | 6.046
2024-12-09 | 16:50 | Data | 0 | 32.696 | 30.691 | 186.855 | 7.64 | 175.555 | 2118.58 | 26.02 | 46.089 | 6.35 | 1.358 | 4.707 | 8454.3 | 1.985 | 97.8 | 77.6 | 1377 | 23 | 5495.3 | 2915.8 | 2815.4 | 4164.6 | 1194.6 | 0.68279 | 6.065
2024-12-09 | 16:50 | Data | 0 | 32.339 | 30.388 | 186.991 | 7.64 | 175.555 | 2119.49 | 26.01 | 46.089 | 6.35 | 1.356 | 4.704 | 8445.26 | 1.938 | 97.8 | 77.6 | 1378 | 23 | 5489.4 | 2894.2 | 2809.3 | 4146.8 | 1194.6 | 0.68403 | 6.06
2024-12-09 | 16:50 | Data | 0 | 32.507 | 30.59 | 186.81 | 7.64 | 175.51 | 2120.39 | 26.02 | 45.908 | 6.35 | 1.353 | 4.726 | 8445.26 | 1.877 | 97.8 | 77.7 | 1378 | 22.95 | 5489.4 | 2914.2 | 2840.9 | 4185.5 | 1194.6 | 0.6773 | 6.079
2024-12-09 | 16:50 | Data | 0 | 32.919 | 30.658 | 186.901 | 7.64 | 175.6 | 2119.49 | 26.02 | 45.908 | 6.35 | 1.356 | 4.711 | 8440.74 | 2.12 | 97.8 | 77.7 | 1378 | 22.95 | 5486.5 | 2889.8 | 2852.1 | 4178.3 | 1194.6 | 0.67468 | 6.067
2024-12-09 | 16:50 | Data | 0 | 32.622 | 30.313 | 186.855 | 7.64 | 175.555 | 2120.39 | 26.03 | 45.998 | 6.34 | 1.342 | 4.702 | 8431.69 | 2.073 | 97.8 | 77.8 | 1378 | 23 | 5480.6 | 2894.9 | 2848.4 | 4177.6 | 1194.6 | 0.67456 | 6.044
2024-12-09 | 16:50 | Data | 0 | 32.622 | 30.259 | 186.946 | 7.64 | 175.69 | 2119.49 | 26.03 | 45.998 | 6.35 | 1.334 | 4.703 | 8440.74 | 2.059 | 97.8 | 77.9 | 1378 | 22.95 | 5486.5 | 2897.8 | 2858.7 | 4188.4 | 1194.6 | 0.67356 | 6.039
2024-12-09 | 16:50 | Data | 0 | 32.393 | 30.475 | 186.901 | 7.64 | 175.51 | 2124.01 | 26.02 | 45.908 | 6.35 | 1.351 | 4.673 | 8440.74 | 2.032 | 97.8 | 77.6 | 1381 | 22.95 | 5486.5 | 2904.4 | 2868.6 | 4197.7 | 1194.6 | 0.67675 | 6.026
2024-12-09 | 16:50 | Data | 0 | 32.487 | 30.415 | 186.855 | 7.64 | 175.464 | 2121.29 | 26.02 | 45.998 | 6.35 | 1.36 | 4.701 | 8445.26 | 2.079 | 97.8 | 77.6 | 1379 | 22.95 | 5489.4 | 2892.5 | 2816.9 | 4150.2 | 1194.6 | 0.67973 | 6.061
2024-12-09 | 16:50 | Data | 0 | 32.264 | 30.415 | 186.81 | 7.64 | 175.51 | 2120.39 | 26.02 | 45.998 | 6.35 | 1.367 | 4.679 | 8454.3 | 2.167 | 97.8 | 77.4 | 1378 | 23 | 5495.3 | 2891.1 | 2807.8 | 4144.5 | 1194.6 | 0.68161 | 6.047
2024-12-09 | 16:50 | Data | 0 | 32.723 | 30.475 | 186.855 | 7.64 | 175.51 | 2120.39 | 26.02 | 45.998 | 6.35 | 1.358 | 4.673 | 8454.3 | 2.005 | 97.8 | 77.5 | 1378 | 23 | 5495.3 | 2903.5 | 2815.4 | 4160.1 | 1194.6 | 0.68042 | 6.03
2024-12-09 | 16:51 | Data | 0 | 32.271 | 30.482 | 186.991 | 7.64 | 175.6 | 2120.39 | 26.02 | 45.908 | 6.35 | 1.348 | 4.665 | 8481.44 | 2.052 | 97.8 | 77.6 | 1379 | 23 | 5512.9 | 2910.3 | 2850.1 | 4187 | 1194.6 | 0.67837 | 6.014
2024-12-09 | 16:51 | Data | 0 | 32.615 | 30.421 | 186.946 | 7.64 | 175.6 | 2120.39 | 26.02 | 45.908 | 6.35 | 1.353 | 4.673 | 8458.83 | 2.086 | 97.8 | 77.5 | 1378 | 22.95 | 5498.2 | 2903.2 | 2832.2 | 4173.7 | 1194.6 | 0.6793 | 6.026
2024-12-09 | 16:51 | Data | 0 | 32.777 | 30.536 | 187.036 | 7.64 | 175.6 | 2120.39 | 26.02 | 45.998 | 6.35 | 1.351 | 4.701 | 8458.83 | 1.877 | 97.8 | 77.7 | 1378 | 23 | 5498.2 | 2930.5 | 2860.8 | 4210.9 | 1194.6 | 0.68061 | 6.052
2024-12-09 | 16:51 | Data | 0 | 32.507 | 30.678 | 186.901 | 7.64 | 175.6 | 2120.39 | 26.02 | 45.998 | 6.35 | 1.339 | 4.711 | 8445.26 | 2.032 | 97.8 | 77.9 | 1378 | 23.04 | 5489.4 | 2907.9 | 2860.4 | 4194.7 | 1194.6 | 0.67589 | 6.051
2024-12-09 | 16:51 | Data | 0 | 32.609 | 30.637 | 186.855 | 7.64 | 175.51 | 2122.2 | 26.02 | 45.998 | 6.34 | 1.346 | 4.699 | 8454.3 | 2.079 | 97.8 | 77.7 | 1379 | 22.95 | 5495.3 | 2909 | 2875.7 | 4207.3 | 1194.6 | 0.67336 | 6.045
2024-12-09 | 16:51 | Data | 0 | 32.474 | 30.813 | 186.901 | 7.64 | 175.51 | 2123.1 | 26.02 | 45.998 | 6.35 | 1.352 | 4.705 | 8454.3 | 1.971 | 97.8 | 77.7 | 1381 | 22.95 | 5495.3 | 2889.2 | 2853.8 | 4176.7 | 1194.6 | 0.6741 | 6.057
2024-12-09 | 16:51 | Data | 0 | 32.501 | 30.421 | 186.855 | 7.64 | 175.555 | 2123.1 | 26.02 | 45.998 | 6.34 | 1.349 | 4.687 | 8467.87 | 2.025 | 97.8 | 77.6 | 1379 | 23 | 5504.1 | 2910.5 | 2871.4 | 4203.3 | 1194.6 | 0.67488 | 6.036
2024-12-09 | 16:51 | Data | 0 | 32.798 | 30.705 | 186.901 | 7.64 | 175.69 | 2122.2 | 26.02 | 45.998 | 6.35 | 1.352 | 4.664 | 8458.83 | 2.329 | 97.8 | 77.5 | 1379 | 22.95 | 5498.2 | 2905 | 2868.1 | 4192.5 | 1194.6 | 0.67602 | 6.017
2024-12-09 | 16:51 | Data | 0 | 32.94 | 30.705 | 187.036 | 7.64 | 175.6 | 2122.2 | 26.03 | 45.998 | 6.34 | 1.345 | 4.663 | 8458.83 | 2.187 | 97.8 | 77.6 | 1379 | 23 | 5498.2 | 2894.4 | 2849.7 | 4173.9 | 1194.6 | 0.67699 | 6.008
2024-12-09 | 16:51 | Data | 0 | 32.568 | 30.536 | 186.901 | 7.64 | 175.69 | 2123.1 | 26.02 | 45.908 | 6.35 | 1.347 | 4.673 | 8458.83 | 1.965 | 97.8 | 77.6 | 1380 | 22.95 | 5498.2 | 2895 | 2807.9 | 4151 | 1194.6 | 0.67978 | 6.019
2024-12-09 | 16:51 | Data | 0 | 32.838 | 30.55 | 186.946 | 7.64 | 175.69 | 2123.1 | 26.01 | 45.908 | 6.35 | 1.348 | 4.664 | 8458.83 | 2.241 | 97.8 | 77.6 | 1380 | 22.95 | 5498.2 | 2884.1 | 2821.2 | 4154.1 | 1194.6 | 0.67682 | 6.012
2024-12-09 | 16:51 | Data | 0 | 32.669 | 30.86 | 187.127 | 7.65 | 175.69 | 2123.1 | 26.02 | 45.998 | 6.35 | 1.349 | 4.668 | 8458.83 | 2.059 | 97.8 | 77.6 | 1380 | 23 | 5498.2 | 2895.1 | 2808.3 | 4145.2 | 1194.6 | 0.6801 | 6.017
2024-12-09 | 16:51 | Data | 0 | 32.831 | 30.82 | 187.036 | 7.65 | 175.69 | 2122.2 | 26.02 | 45.908 | 6.35 | 1.347 | 4.684 | 8445.26 | 1.998 | 97.8 | 77.7 | 1380 | 23 | 5489.4 | 2889.8 | 2784.7 | 4129.5 | 1194.6 | 0.68232 | 6.031
2024-12-09 | 16:51 | Data | 0 | 32.717 | 30.475 | 186.901 | 7.65 | 175.555 | 2123.1 | 26.02 | 45.998 | 6.35 | 1.339 | 4.672 | 8454.3 | 2.079 | 97.8 | 77.7 | 1379 | 23 | 5495.3 | 2877.7 | 2797 | 4134.9 | 1194.7 | 0.67824 | 6.011
2024-12-09 | 16:51 | Data | 0 | 32.494 | 30.59 | 186.855 | 7.64 | 175.51 | 2122.2 | 26.02 | 45.998 | 6.35 | 1.347 | 4.664 | 8445.26 | 2.079 | 97.8 | 77.6 | 1380 | 22.95 | 5489.4 | 2886.2 | 2824.2 | 4160.3 | 1194.7 | 0.67647 | 6.01
2024-12-09 | 16:51 | Data | 0 | 32.298 | 30.556 | 186.901 | 7.64 | 175.51 | 2120.39 | 26.01 | 45.998 | 6.35 | 1.348 | 4.675 | 8431.69 | 1.965 | 97.8 | 77.6 | 1378 | 23 | 5480.6 | 2910.4 | 2805 | 4156.7 | 1194.7 | 0.684 | 6.023
2024-12-09 | 16:51 | Data | 0 | 32.946 | 30.455 | 186.946 | 7.64 | 175.69 | 2120.39 | 26.02 | 46.089 | 6.35 | 1.346 | 4.682 | 8454.3 | 2.133 | 97.8 | 77.7 | 1378 | 23 | 5495.3 | 2907.9 | 2833.3 | 4173.3 | 1194.7 | 0.68107 | 6.027
2024-12-09 | 16:52 | Data | 0 | 32.838 | 30.664 | 186.991 | 7.64 | 175.69 | 2121.29 | 26.01 | 45.998 | 6.35 | 1.345 | 4.701 | 8458.83 | 2.262 | 97.8 | 77.8 | 1379 | 23.04 | 5498.2 | 2891.2 | 2832.9 | 4169.4 | 1194.7 | 0.67599 | 6.045
2024-12-09 | 16:52 | Data | 0 | 33.034 | 30.421 | 186.946 | 7.64 | 175.736 | 2122.2 | 26.02 | 45.998 | 6.35 | 1.338 | 4.667 | 8440.74 | 2.133 | 97.8 | 77.7 | 1380 | 23 | 5486.5 | 2895.1 | 2848.4 | 4179.8 | 1194.7 | 0.67604 | 6.005
2024-12-09 | 16:52 | Data | 0 | 32.933 | 30.556 | 186.855 | 7.64 | 175.6 | 2123.1 | 26.02 | 45.908 | 6.34 | 1.358 | 4.67 | 8445.26 | 2.073 | 97.8 | 77.5 | 1380 | 23 | 5489.4 | 2892.7 | 2849.3 | 4177.9 | 1194.7 | 0.67612 | 6.027
2024-12-09 | 16:52 | Data | 0 | 32.494 | 30.415 | 186.991 | 7.64 | 175.51 | 2122.2 | 26.03 | 45.908 | 6.34 | 1.352 | 4.675 | 8458.83 | 2.073 | 97.8 | 77.6 | 1379 | 23 | 5498.2 | 2887.7 | 2822.3 | 4155.7 | 1194.7 | 0.67737 | 6.027
2024-12-09 | 16:52 | Data | 0 | 32.507 | 30.523 | 186.855 | 7.65 | 175.51 | 2125.81 | 26.02 | 45.998 | 6.35 | 1.343 | 4.672 | 8458.83 | 2.16 | 97.8 | 77.7 | 1381 | 23 | 5498.2 | 2877.4 | 2789.1 | 4129.6 | 1194.7 | 0.67947 | 6.015
2024-12-09 | 16:52 | Data | 0 | 32.494 | 30.421 | 186.81 | 7.64 | 175.6 | 2125.81 | 26.01 | 45.998 | 6.35 | 1.347 | 4.683 | 8440.74 | 2.167 | 97.8 | 77.7 | 1382 | 22.95 | 5486.5 | 2901.5 | 2791.1 | 4144.4 | 1194.7 | 0.67914 | 6.029
2024-12-09 | 16:52 | Data | 0 | 32.561 | 30.435 | 186.81 | 7.64 | 175.51 | 2123.1 | 26.02 | 45.998 | 6.35 | 1.349 | 4.682 | 8445.26 | 1.83 | 97.8 | 77.6 | 1380 | 23 | 5489.4 | 2884.6 | 2778.1 | 4124.8 | 1194.7 | 0.68236 | 6.03
2024-12-09 | 16:52 | Data | 0 | 32.501 | 30.529 | 186.991 | 7.65 | 175.555 | 2123.1 | 26.01 | 45.998 | 6.35 | 1.337 | 4.691 | 8418.13 | 1.857 | 97.8 | 77.8 | 1380 | 22.95 | 5471.8 | 2914.2 | 2789.5 | 4146.6 | 1194.7 | 0.68672 | 6.027
2024-12-09 | 16:52 | Data | 0 | 32.723 | 30.664 | 186.991 | 7.64 | 175.6 | 2125.81 | 26.02 | 45.998 | 6.35 | 1.339 | 4.652 | 8431.69 | 2.133 | 97.8 | 77.7 | 1381 | 22.95 | 5480.6 | 2892.1 | 2779.4 | 4129.1 | 1194.7 | 0.68237 | 5.99
2024-12-09 | 16:52 | Data | 0 | 32.609 | 30.597 | 186.81 | 7.64 | 175.51 | 2125.81 | 26.02 | 45.998 | 6.35 | 1.339 | 4.662 | 8431.69 | 1.965 | 97.8 | 77.7 | 1381 | 23 | 5480.6 | 2890.3 | 2795.2 | 4140.3 | 1194.7 | 0.68173 | 6
2024-12-09 | 16:52 | Data | 0 | 32.494 | 30.421 | 186.855 | 7.64 | 175.51 | 2125.81 | 26.02 | 45.998 | 6.35 | 1.348 | 4.687 | 8427.17 | 2.268 | 97.8 | 77.7 | 1382 | 23 | 5477.7 | 2901.7 | 2822.5 | 4165.6 | 1194.7 | 0.6803 | 6.035
2024-12-09 | 16:52 | Data | 0 | 32.494 | 30.394 | 186.72 | 7.64 | 175.464 | 2125.81 | 26.01 | 45.998 | 6.35 | 1.347 | 4.692 | 8436.21 | 2.127 | 97.8 | 77.7 | 1382 | 22.95 | 5483.5 | 2910.5 | 2837.2 | 4181.9 | 1194.7 | 0.67969 | 6.04
2024-12-09 | 16:52 | Data | 0 | 32.892 | 30.678 | 187.127 | 7.64 | 175.69 | 2123.1 | 26 | 45.998 | 6.35 | 1.348 | 4.669 | 8431.69 | 2.268 | 97.8 | 77.6 | 1379 | 23 | 5480.6 | 2904.6 | 2810.5 | 4153.7 | 1194.7 | 0.68309 | 6.017
2024-12-09 | 16:52 | Data | 0 | 32.534 | 30.415 | 186.901 | 7.64 | 175.51 | 2122.2 | 26 | 46.089 | 6.35 | 1.348 | 4.667 | 8418.13 | 2.086 | 97.8 | 77.6 | 1380 | 23 | 5471.8 | 2912.8 | 2837.7 | 4183.9 | 1194.7 | 0.67299 | 6.016
2024-12-09 | 16:52 | Data | 0 | 32.548 | 30.651 | 186.946 | 7.64 | 175.51 | 2120.39 | 26.02 | 45.908 | 6.35 | 1.34 | 4.67 | 8431.69 | 1.85 | 97.8 | 77.7 | 1378 | 22.95 | 5480.6 | 2897.6 | 2807.1 | 4151.5 | 1194.7 | 0.68251 | 6.009
2024-12-09 | 16:52 | Data | 0 | 32.609 | 30.536 | 186.855 | 7.64 | 175.51 | 2120.39 | 26.02 | 46.089 | 6.35 | 1.34 | 4.673 | 8431.69 | 2.019 | 97.8 | 77.7 | 1378 | 23 | 5480.6 | 2904.3 | 2852.3 | 4184.1 | 1194.7 | 0.67557 | 6.013
2024-12-09 | 16:52 | Data | 0 | 32.494 | 30.536 | 186.901 | 7.64 | 175.555 | 2123.1 | 26.01 | 45.998 | 6.35 | 1.339 | 4.687 | 8418.13 | 1.958 | 97.8 | 77.8 | 1379 | 22.95 | 5471.8 | 2900.7 | 2813.7 | 4155.1 | 1194.7 | 0.681 | 6.026
2024-12-09 | 16:52 | Data | 0 | 32.521 | 30.651 | 186.901 | 7.64 | 175.6 | 2122.2 | 26.01 | 45.998 | 6.35 | 1.342 | 4.701 | 8427.17 | 1.85 | 97.8 | 77.8 | 1380 | 23 | 5477.7 | 2893.8 | 2796 | 4147.8 | 1194.7 | 0.68069 | 6.042
2024-12-09 | 16:52 | Data | 0 | 32.71 | 30.921 | 186.991 | 7.64 | 175.69 | 2123.1 | 26.02 | 45.998 | 6.35 | 1.354 | 4.672 | 8436.21 | 1.87 | 97.8 | 77.5 | 1380 | 23 | 5483.5 | 2895.4 | 2804.1 | 4151.9 | 1194.7 | 0.68188 | 6.026
2024-12-09 | 16:53 | Data | 0 | 32.825 | 30.651 | 186.991 | 7.64 | 175.69 | 2123.1 | 26.03 | 46.179 | 6.35 | 1.338 | 4.669 | 8427.17 | 2.086 | 97.8 | 77.7 | 1381 | 23.13 | 5477.7 | 2883.6 | 2777.3 | 4131.7 | 1194.7 | 0.68236 | 6.007
2024-12-09 | 16:53 | Data | 0 | 32.507 | 30.421 | 186.855 | 7.64 | 175.555 | 2125.81 | 26.02 | 46.269 | 6.35 | 1.347 | 4.692 | 8431.69 | 2.032 | 97.8 | 77.7 | 1382 | 23.13 | 5480.6 | 2878.5 | 2796.5 | 4131.8 | 1194.7 | 0.6807 | 6.037
2024-12-09 | 16:53 | Data | 0 | 32.71 | 30.867 | 186.991 | 7.64 | 175.69 | 2125.81 | 26.02 | 46.179 | 6.35 | 1.341 | 4.692 | 8427.17 | 1.857 | 97.8 | 77.8 | 1382 | 23.13 | 5477.7 | 2889 | 2814 | 4150.5 | 1194.7 | 0.68031 | 6.034
2024-12-09 | 16:53 | Data | 0 | 32.494 | 30.847 | 186.901 | 7.64 | 175.464 | 2125.81 | 26.02 | 46.269 | 6.35 | 1.347 | 4.687 | 8440.74 | 1.904 | 97.8 | 77.7 | 1382 | 23.13 | 5486.5 | 2913.9 | 2821.5 | 4152.9 | 1194.7 | 0.6834 | 6.034
2024-12-09 | 16:53 | Data | 0 | 32.723 | 30.435 | 186.991 | 7.64 | 175.6 | 2126.72 | 26.01 | 46.269 | 6.35 | 1.348 | 4.714 | 8476.91 | 2.073 | 97.8 | 77.8 | 1382 | 23.09 | 5510 | 2885.1 | 2845.9 | 4170.4 | 1194.7 | 0.6745 | 6.062
2024-12-09 | 16:53 | Data | 0 | 32.285 | 30.415 | 186.901 | 7.64 | 175.6 | 2123.1 | 26.01 | 46.179 | 6.35 | 1.354 | 4.665 | 8458.83 | 2.025 | 97.8 | 77.5 | 1379 | 23.09 | 5498.2 | 2889.6 | 2847.8 | 4174.5 | 1194.7 | 0.6748 | 6.019
2024-12-09 | 16:53 | Data | 0 | 32.548 | 30.651 | 187.127 | 7.64 | 175.6 | 2122.2 | 26.01 | 46.269 | 6.35 | 1.352 | 4.658 | 8463.35 | 2.019 | 97.8 | 77.5 | 1380 | 23.13 | 5501.2 | 2900.7 | 2844.5 | 4174.7 | 1194.7 | 0.6777 | 6.009
2024-12-09 | 16:53 | Data | 0 | 32.676 | 30.651 | 186.855 | 7.64 | 175.464 | 2123.1 | 26.02 | 46.179 | 6.34 | 1.345 | 4.68 | 8454.3 | 2.066 | 97.8 | 77.7 | 1380 | 23.09 | 5495.3 | 2892.4 | 2833 | 4164.2 | 1194.7 | 0.67645 | 6.025
2024-12-09 | 16:53 | Data | 0 | 32.717 | 30.442 | 186.901 | 7.64 | 175.555 | 2123.1 | 26.02 | 46.179 | 6.35 | 1.348 | 4.676 | 8445.26 | 2.066 | 97.8 | 77.6 | 1380 | 23.09 | 5489.4 | 2900.5 | 2811 | 4156.8 | 1194.7 | 0.68077 | 6.025
2024-12-09 | 16:53 | Data | 0 | 32.946 | 30.658 | 187.082 | 7.64 | 175.69 | 2124.91 | 26.02 | 46.359 | 6.35 | 1.348 | 4.703 | 8449.78 | 2.12 | 97.8 | 77.7 | 1381 | 23.13 | 5492.4 | 2907.7 | 2792.7 | 4147.9 | 1194.7 | 0.68228 | 6.051
2024-12-09 | 16:53 | Data | 0 | 32.609 | 30.82 | 186.946 | 7.64 | 175.6 | 2125.81 | 26 | 46.179 | 6.34 | 1.358 | 4.691 | 8440.74 | 1.931 | 97.8 | 77.6 | 1381 | 23.09 | 5486.5 | 2902.3 | 2791.2 | 4142.4 | 1194.7 | 0.6858 | 6.047
2024-12-09 | 16:53 | Data | 0 | 32.723 | 30.442 | 186.946 | 7.64 | 175.69 | 2124.91 | 26.02 | 46.269 | 6.35 | 1.356 | 4.7 | 8431.69 | 2.187 | 97.8 | 77.6 | 1381 | 23.09 | 5480.6 | 2895.1 | 2805.1 | 4148.5 | 1194.7 | 0.68243 | 6.055
2024-12-09 | 16:53 | Data | 0 | 32.507 | 30.475 | 186.991 | 7.65 | 175.555 | 2073.39 | 26.02 | 46.179 | 6.34 | 1.347 | 4.683 | 8431.69 | 1.971 | 97.8 | 77.7 | 1342 | 23.09 | 5480.6 | 2906.1 | 2791.1 | 4144.5 | 1194.7 | 0.68504 | 6.03
2024-12-09 | 16:53 | Data | 0 | 32.696 | 30.651 | 186.901 | 7.64 | 175.464 | 2056.22 | 26.02 | 46.269 | 6.35 | 1.345 | 4.664 | 8431.69 | 2.066 | 97.8 | 77.6 | 1342 | 23.13 | 5480.6 | 2884.2 | 2802.7 | 4149.3 | 1194.7 | 0.68123 | 6.008
2024-12-09 | 16:53 | Data | 0 | 32.717 | 30.421 | 186.991 | 7.65 | 175.51 | 2120.39 | 26.01 | 46.269 | 6.35 | 1.335 | 4.668 | 8449.78 | 1.931 | 97.8 | 77.8 | 1378 | 23.09 | 5492.4 | 2875.8 | 2794.2 | 4131 | 1194.8 | 0.67938 | 6.003
2024-12-09 | 16:53 | Data | 0 | 32.723 | 30.489 | 186.946 | 7.64 | 175.6 | 2118.58 | 26.01 | 46.269 | 6.35 | 1.334 | 4.674 | 8440.74 | 1.971 | 97.8 | 77.8 | 1377 | 23.13 | 5486.5 | 2912.4 | 2829.3 | 4179.3 | 1194.8 | 0.67843 | 6.008
2024-12-09 | 16:53 | Data | 0 | 32.534 | 30.536 | 186.991 | 7.64 | 175.6 | 2116.78 | 26.02 | 46.269 | 6.35 | 1.346 | 4.694 | 8440.74 | 1.884 | 97.8 | 77.7 | 1376 | 23.13 | 5486.5 | 2885.2 | 2858.5 | 4182.8 | 1194.8 | 0.67131 | 6.041
2024-12-09 | 16:54 | Data | 0 | 32.568 | 30.651 | 187.127 | 7.65 | 175.736 | 2120.39 | 26.02 | 46.179 | 6.35 | 1.351 | 4.669 | 8431.69 | 1.85 | 97.8 | 77.6 | 1378 | 23.09 | 5480.6 | 2889.2 | 2841.6 | 4171.8 | 1194.8 | 0.67701 | 6.02
2024-12-09 | 16:54 | Data | 0 | 32.703 | 30.604 | 186.946 | 7.64 | 175.464 | 2117.68 | 26.02 | 46.269 | 6.34 | 1.351 | 4.677 | 8431.69 | 1.958 | 97.8 | 77.6 | 1376 | 23.09 | 5480.6 | 2890.1 | 2841.8 | 4166.1 | 1194.8 | 0.67649 | 6.028
2024-12-09 | 16:54 | Data | 0 | 32.399 | 30.421 | 186.946 | 7.64 | 175.555 | 2111.35 | 26.02 | 46.179 | 6.35 | 1.342 | 4.685 | 8431.69 | 2.032 | 97.8 | 77.7 | 1372 | 23.13 | 5480.6 | 2900.2 | 2802 | 4150.5 | 1194.8 | 0.68251 | 6.027
2024-12-09 | 16:54 | Data | 0 | 32.683 | 30.651 | 186.901 | 7.64 | 175.6 | 2117.68 | 26.02 | 46.269 | 6.35 | 1.345 | 4.697 | 8264.37 | 2.073 | 97.8 | 77.8 | 1376 | 23.13 | 5371.8 | 2905.4 | 2802.8 | 4149.6 | 1194.8 | 0.68323 | 6.042
2024-12-09 | 16:54 | Data | 0 | 32.973 | 30.55 | 187.036 | 7.64 | 175.736 | 2117.68 | 26.02 | 46.269 | 6.35 | 1.352 | 4.699 | 8250.8 | 2.12 | 97.8 | 77.7 | 1376 | 23.09 | 5363 | 2909 | 2787.1 | 4146.3 | 1194.8 | 0.68534 | 6.051
2024-12-09 | 16:54 | Data | 0 | 32.73 | 30.705 | 186.946 | 7.64 | 175.736 | 2120.39 | 26.02 | 45.998 | 6.35 | 1.352 | 4.692 | 8255.33 | 1.857 | 97.8 | 77.6 | 1378 | 23 | 5366 | 2887 | 2770.2 | 4126.4 | 1194.8 | 0.68841 | 6.045
2024-12-09 | 16:54 | Data | 0 | 32.777 | 30.705 | 186.946 | 7.64 | 175.6 | 2116.78 | 26.03 | 45.998 | 6.35 | 1.349 | 4.656 | 8219.15 | 1.965 | 97.8 | 77.5 | 1376 | 23 | 5342.4 | 2884.2 | 2802.6 | 4140 | 1194.8 | 0.68004 | 6.006
2024-12-09 | 16:54 | Data | 0 | 32.831 | 30.664 | 186.901 | 7.64 | 175.69 | 2120.39 | 26.02 | 45.998 | 6.35 | 1.342 | 4.653 | 8386.47 | 2.073 | 97.8 | 77.6 | 1378 | 22.95 | 5451.2 | 2901.6 | 2790.6 | 4143.5 | 1194.8 | 0.68323 | 5.995
2024-12-09 | 16:54 | Data | 0 | 32.582 | 30.59 | 186.901 | 7.65 | 175.69 | 2114.06 | 26.01 | 45.998 | 6.35 | 1.349 | 4.681 | 8404.56 | 2.316 | 97.8 | 77.6 | 1375 | 23 | 5463 | 2876.6 | 2809.9 | 4139.4 | 1194.8 | 0.6783 | 6.03
2024-12-09 | 16:54 | Data | 0 | 32.271 | 30.793 | 187.036 | 7.64 | 175.555 | 2114.97 | 26.02 | 45.908 | 6.34 | 1.355 | 4.679 | 8400.04 | 1.931 | 97.8 | 77.5 | 1375 | 22.95 | 5460 | 2892.8 | 2804.7 | 4149.9 | 1194.8 | 0.68038 | 6.034
2024-12-09 | 16:54 | Data | 0 | 32.777 | 30.448 | 186.946 | 7.65 | 175.6 | 2109.54 | 26.01 | 45.998 | 6.35 | 1.347 | 4.679 | 8404.56 | 1.978 | 97.8 | 77.7 | 1371 | 23 | 5463 | 2881.7 | 2778.6 | 4121.8 | 1194.8 | 0.68303 | 6.025
2024-12-09 | 16:54 | Data | 0 | 32.892 | 30.867 | 187.036 | 7.64 | 175.69 | 2114.06 | 26.01 | 46.089 | 6.34 | 1.338 | 4.686 | 8431.69 | 1.863 | 97.8 | 77.8 | 1374 | 23 | 5480.6 | 2890.1 | 2797 | 4140.5 | 1194.8 | 0.68197 | 6.024
2024-12-09 | 16:54 | Data | 0 | 33.027 | 30.901 | 187.036 | 7.64 | 175.69 | 2114.06 | 26 | 45.908 | 6.35 | 1.339 | 4.675 | 8431.69 | 2.14 | 97.8 | 77.7 | 1374 | 22.95 | 5480.6 | 2911.4 | 2792.6 | 4152.7 | 1194.8 | 0.68395 | 6.015
2024-12-09 | 16:54 | Data | 0 | 32.696 | 30.475 | 186.946 | 7.65 | 175.6 | 2114.06 | 26.01 | 45.908 | 6.34 | 1.34 | 4.675 | 8431.69 | 2.187 | 97.8 | 77.7 | 1374 | 22.95 | 5480.6 | 2893.3 | 2791 | 4137.5 | 1194.8 | 0.68235 | 6.016
2024-12-09 | 16:54 | Data | 0 | 32.467 | 30.759 | 187.082 | 7.65 | 175.6 | 2116.78 | 26.02 | 45.998 | 6.35 | 1.349 | 4.672 | 8445.26 | 1.951 | 97.8 | 77.6 | 1376 | 22.95 | 5489.4 | 2890.1 | 2787.2 | 4134.3 | 1194.8 | 0.68261 | 6.021
2024-12-09 | 16:54 | Data | 0 | 32.723 | 30.826 | 187.036 | 7.65 | 175.736 | 2114.06 | 26.01 | 45.998 | 6.35 | 1.337 | 4.687 | 8445.26 | 1.958 | 97.8 | 77.8 | 1374 | 23 | 5489.4 | 2890.8 | 2787.1 | 4131.9 | 1194.8 | 0.68275 | 6.024
2024-12-09 | 16:54 | Data | 0 | 32.669 | 30.759 | 186.901 | 7.65 | 175.69 | 2114.97 | 26.01 | 46.089 | 6.35 | 1.349 | 4.686 | 8454.3 | 2.059 | 97.8 | 77.6 | 1374 | 23.04 | 5495.3 | 2880.3 | 2786.3 | 4129 | 1194.8 | 0.6837 | 6.036
2024-12-09 | 16:54 | Data | 0 | 32.892 | 30.536 | 186.946 | 7.64 | 175.736 | 2117.68 | 26 | 45.998 | 6.35 | 1.348 | 4.684 | 8440.74 | 1.992 | 97.8 | 77.7 | 1376 | 23 | 5486.5 | 2892.2 | 2769 | 4123.8 | 1194.8 | 0.6841 | 6.035
2024-12-09 | 16:55 | Data | 0 | 32.609 | 30.624 | 186.901 | 7.64 | 175.51 | 2117.68 | 26.01 | 45.908 | 6.35 | 1.344 | 4.658 | 8445.26 | 2.106 | 97.8 | 77.6 | 1376 | 23 | 5489.4 | 2898.2 | 2772 | 4120.4 | 1194.8 | 0.68383 | 6.002
2024-12-09 | 16:55 | Data | 0 | 32.98 | 30.658 | 187.036 | 7.64 | 175.736 | 2120.39 | 26.01 | 45.998 | 6.35 | 1.338 | 4.687 | 8445.26 | 2.093 | 97.8 | 77.8 | 1378 | 22.95 | 5489.4 | 2897.6 | 2758.2 | 4116.6 | 1194.8 | 0.68636 | 6.025
2024-12-09 | 16:55 | Data | 0 | 32.528 | 30.651 | 186.991 | 7.64 | 175.6 | 2120.39 | 26 | 45.908 | 6.35 | 1.345 | 4.691 | 8481.44 | 1.857 | 97.8 | 77.7 | 1378 | 23 | 5512.9 | 2883.1 | 2777.3 | 4123.5 | 1194.8 | 0.68502 | 6.036
2024-12-09 | 16:55 | Data | 0 | 32.501 | 30.442 | 186.991 | 7.65 | 175.6 | 2117.68 | 26.01 | 45.998 | 6.35 | 1.346 | 4.674 | 8440.74 | 2.052 | 97.8 | 77.6 | 1377 | 23 | 5486.5 | 2904.9 | 2803.6 | 4157.5 | 1194.8 | 0.68288 | 6.021
2024-12-09 | 16:55 | Data | 0 | 32.723 | 30.732 | 187.082 | 7.64 | 175.69 | 2118.58 | 25.99 | 45.998 | 6.34 | 1.34 | 4.67 | 8440.74 | 1.992 | 97.8 | 77.7 | 1377 | 23 | 5486.5 | 2898.1 | 2764.4 | 4117.6 | 1194.8 | 0.68878 | 6.01
2024-12-09 | 16:55 | Data | 0 | 32.501 | 30.59 | 186.991 | 7.64 | 175.6 | 2116.78 | 26.02 | 45.998 | 6.35 | 1.346 | 4.671 | 8400.04 | 2.019 | 97.8 | 77.6 | 1376 | 23 | 5460 | 2882.9 | 2788.3 | 4131 | 1194.8 | 0.6821 | 6.017
2024-12-09 | 16:55 | Data | 0 | 32.737 | 30.664 | 187.172 | 7.65 | 175.736 | 2120.39 | 26 | 45.908 | 6.34 | 1.353 | 4.692 | 8422.65 | 2.059 | 97.8 | 77.6 | 1378 | 22.95 | 5474.7 | 2915.5 | 2798.9 | 4155.5 | 1194.8 | 0.6851 | 6.045
2024-12-09 | 16:55 | Data | 0 | 32.723 | 30.658 | 186.991 | 7.64 | 175.69 | 2117.68 | 26.01 | 45.998 | 6.35 | 1.348 | 4.7 | 8386.47 | 2.1 | 97.8 | 77.7 | 1376 | 23 | 5451.2 | 2890.9 | 2817.2 | 4152.1 | 1194.8 | 0.6801 | 6.045
2024-12-09 | 16:55 | Data | 0 | 32.588 | 30.421 | 186.991 | 7.64 | 175.69 | 2117.68 | 26.02 | 45.908 | 6.34 | 1.341 | 4.692 | 8395.51 | 2.086 | 97.8 | 77.8 | 1376 | 22.95 | 5457.1 | 2887 | 2809.3 | 4142.2 | 1194.8 | 0.68076 | 6.035
2024-12-09 | 16:55 | Data | 0 | 32.723 | 30.543 | 186.946 | 7.64 | 175.6 | 2117.68 | 26 | 45.908 | 6.35 | 1.342 | 4.669 | 8427.17 | 2.086 | 97.8 | 77.7 | 1377 | 23 | 5477.7 | 2907 | 2794.4 | 4145.1 | 1194.8 | 0.68438 | 6.012
2024-12-09 | 16:55 | Data | 0 | 32.75 | 30.475 | 187.036 | 7.64 | 175.781 | 2120.39 | 26.02 | 45.998 | 6.34 | 1.352 | 4.673 | 8418.13 | 1.904 | 97.8 | 77.6 | 1378 | 23 | 5471.8 | 2909 | 2796.8 | 4148.4 | 1194.8 | 0.68362 | 6.025
2024-12-09 | 16:55 | Data | 0 | 32.528 | 30.637 | 186.946 | 7.64 | 175.736 | 2122.2 | 26.02 | 45.908 | 6.34 | 1.346 | 4.684 | 8422.65 | 1.904 | 97.8 | 77.7 | 1379 | 22.95 | 5474.7 | 2905 | 2819 | 4165.4 | 1194.8 | 0.6807 | 6.031
2024-12-09 | 16:55 | Data | 0 | 32.838 | 30.543 | 187.082 | 7.64 | 175.826 | 2123.1 | 26.01 | 45.998 | 6.35 | 1.352 | 4.689 | 8400.04 | 2.073 | 97.8 | 77.6 | 1380 | 23 | 5460 | 2891.3 | 2812.8 | 4152.9 | 1194.8 | 0.67996 | 6.041
2024-12-09 | 16:55 | Data | 0 | 32.676 | 30.448 | 186.901 | 7.64 | 175.6 | 2122.2 | 26.01 | 45.908 | 6.35 | 1.341 | 4.692 | 8400.04 | 2.019 | 97.8 | 77.8 | 1379 | 22.95 | 5460 | 2898.6 | 2801.1 | 4148.2 | 1194.8 | 0.6828 | 6.034
2024-12-09 | 16:55 | Data | 0 | 32.879 | 30.968 | 187.036 | 7.64 | 175.736 | 2122.2 | 26 | 45.998 | 6.35 | 1.341 | 4.702 | 8404.56 | 2.268 | 97.8 | 77.8 | 1379 | 22.95 | 5463 | 2915.3 | 2818.3 | 4174.7 | 1194.8 | 0.68098 | 6.044
2024-12-09 | 16:55 | Data | 0 | 32.507 | 30.766 | 186.901 | 7.64 | 175.6 | 2122.2 | 26 | 45.998 | 6.35 | 1.335 | 4.697 | 8404.56 | 1.958 | 97.8 | 77.9 | 1379 | 23 | 5463 | 2887.7 | 2811 | 4149.3 | 1194.8 | 0.68036 | 6.032
2024-12-09 | 16:55 | Data | 0 | 32.926 | 30.894 | 187.127 | 7.64 | 175.69 | 2124.01 | 26 | 45.998 | 6.34 | 1.347 | 4.697 | 8395.51 | 2.012 | 97.8 | 77.7 | 1381 | 22.95 | 5457.1 | 2180.9 | 2411.5 | 3292.3 | 1194.9 | 0.64982 | 6.044
2024-12-09 | 16:56 | Data | 0 | 32.723 | 30.658 | 187.082 | 7.64 | 175.69 | 2068.87 | 26.01 | 45.998 | 6.34 | 1.348 | 4.702 | 8418.13 | 2.066 | 97.8 | 77.7 | 1339 | 23 | 5471.8 | 1831.3 | 2243.9 | 2907.9 | 1194.9 | 0.62735 | 6.05
2024-12-09 | 16:56 | Data | 0 | 32.723 | 30.489 | 186.946 | 7.64 | 175.736 | 2020.97 | 26 | 45.998 | 6.35 | 1.353 | 4.693 | 8400.04 | 2.019 | 97.7 | 77.6 | 1314 | 23 | 5460 | 1806.5 | 2235.3 | 2886.4 | 1194.9 | 0.62263 | 6.047
2024-12-09 | 16:56 | Data | 0 | 32.501 | 30.442 | 186.901 | 7.64 | 175.555 | 2122.2 | 26.01 | 45.998 | 6.35 | 1.341 | 4.701 | 8418.13 | 1.965 | 97.8 | 77.8 | 1380 | 23 | 5471.8 | 1789.8 | 2249 | 2886.8 | 1194.9 | 0.61793 | 6.041
2024-12-09 | 16:56 | Data | 0 | 32.609 | 30.644 | 186.946 | 7.64 | 175.6 | 2123.1 | 26 | 45.998 | 6.35 | 1.345 | 4.683 | 8400.04 | 2.106 | 97.8 | 77.7 | 1379 | 22.95 | 5460 | 1822.6 | 2230.6 | 2893.1 | 1194.9 | 0.6272 | 6.027
2024-12-09 | 16:56 | Data | 0 | 32.507 | 30.421 | 187.036 | 7.64 | 175.736 | 2123.1 | 26.01 | 45.908 | 6.35 | 1.357 | 4.695 | 8404.56 | 2.073 | 97.8 | 77.6 | 1380 | 23 | 5463 | 1817.5 | 2230 | 2884 | 1194.9 | 0.62269 | 6.052
2024-12-09 | 16:56 | Data | 0 | 32.71 | 30.759 | 187.036 | 7.65 | 175.69 | 2123.1 | 26.01 | 45.998 | 6.35 | 1.348 | 4.684 | 8409.08 | 2.086 | 97.8 | 77.6 | 1380 | 23 | 5465.9 | 1836.2 | 2226.2 | 2873.3 | 1194.9 | 0.62779 | 6.033
2024-12-09 | 16:56 | Data | 0 | 32.723 | 30.651 | 187.082 | 7.64 | 175.69 | 2123.1 | 26 | 45.998 | 6.35 | 1.341 | 4.675 | 8418.13 | 2.073 | 97.8 | 77.7 | 1380 | 23 | 5471.8 | 1816 | 2218.6 | 2878.9 | 1194.9 | 0.62873 | 6.017
2024-12-09 | 16:56 | Data | 0 | 33.108 | 30.705 | 187.082 | 7.64 | 175.781 | 2123.1 | 26 | 45.998 | 6.34 | 1.348 | 4.701 | 8418.13 | 2.12 | 97.8 | 77.7 | 1380 | 23 | 5471.8 | 1814.8 | 2196.5 | 2858.5 | 1194.9 | 0.63073 | 6.049
2024-12-09 | 16:56 | Data | 0 | 32.892 | 30.874 | 187.127 | 7.65 | 175.6 | 2123.1 | 26.01 | 45.998 | 6.35 | 1.345 | 4.689 | 8400.04 | 1.877 | 97.8 | 77.7 | 1380 | 23 | 5460 | 1821.8 | 2226.6 | 2888.9 | 1194.9 | 0.6283 | 6.035
2024-12-09 | 16:56 | Data | 0 | 32.501 | 30.651 | 186.991 | 7.64 | 175.6 | 2123.1 | 26.01 | 45.908 | 6.34 | 1.347 | 4.663 | 8400.04 | 1.971 | 97.8 | 77.6 | 1380 | 22.95 | 5460 | 1823.8 | 2236.6 | 2898.8 | 1194.9 | 0.62685 | 6.009
2024-12-09 | 16:56 | Data | 0 | 32.521 | 30.428 | 186.901 | 7.65 | 175.555 | 2123.1 | 26 | 45.908 | 6.35 | 1.348 | 4.677 | 8400.04 | 2.073 | 97.8 | 77.6 | 1380 | 23 | 5460 | 1824.5 | 2235.6 | 2898.4 | 1194.9 | 0.62748 | 6.026
2024-12-09 | 16:56 | Data | 0 | 32.953 | 30.739 | 187.036 | 7.64 | 175.736 | 2117.68 | 26 | 45.908 | 6.35 | 1.356 | 4.692 | 8400.04 | 2.012 | 97.8 | 77.6 | 1376 | 22.95 | 5460 | 1802.6 | 2215.1 | 2868.2 | 1194.9 | 0.62641 | 6.046
2024-12-09 | 16:56 | Data | 0 | 32.696 | 30.705 | 186.946 | 7.64 | 175.69 | 2121.29 | 26 | 45.998 | 6.35 | 1.349 | 4.685 | 8400.04 | 2.025 | 97.8 | 77.6 | 1379 | 23 | 5460 | 1799.1 | 2222.9 | 2874.1 | 1194.9 | 0.62298 | 6.035
2024-12-09 | 16:56 | Data | 0 | 32.609 | 30.624 | 186.855 | 7.64 | 175.464 | 2118.58 | 26.01 | 45.998 | 6.35 | 1.352 | 4.682 | 8418.13 | 2.086 | 97.8 | 77.6 | 1376 | 23 | 5471.8 | 1836 | 2225.9 | 2887 | 1194.9 | 0.62895 | 6.034
2024-12-09 | 16:56 | Data | 0 | 32.858 | 30.55 | 187.036 | 7.64 | 175.781 | 2117.68 | 26 | 45.998 | 6.35 | 1.349 | 4.675 | 8422.65 | 1.911 | 97.8 | 77.6 | 1376 | 23 | 5474.7 | 1822.1 | 2212.3 | 2878.5 | 1194.9 | 0.63128 | 6.025
2024-12-09 | 16:56 | Data | 0 | 32.696 | 30.759 | 186.991 | 7.64 | 175.6 | 2117.68 | 26.01 | 45.998 | 6.34 | 1.345 | 4.658 | 8440.74 | 1.857 | 97.8 | 77.6 | 1376 | 23 | 5486.5 | 1801.1 | 2203.6 | 2860.8 | 1194.9 | 0.62584 | 6.003
2024-12-09 | 16:56 | Data | 0 | 32.73 | 30.489 | 186.901 | 7.64 | 175.69 | 2117.68 | 26 | 45.998 | 6.35 | 1.352 | 4.67 | 8431.69 | 1.965 | 97.8 | 77.5 | 1376 | 22.95 | 5480.6 | 1813.7 | 2210.6 | 2875.1 | 1194.9 | 0.63196 | 6.022
2024-12-09 | 16:56 | Data | 0 | 32.501 | 30.597 | 186.855 | 7.64 | 175.6 | 2116.78 | 26 | 45.908 | 6.35 | 1.351 | 4.658 | 8418.13 | 2.025 | 97.8 | 77.5 | 1376 | 22.95 | 5471.8 | 1806.5 | 2188.7 | 2850.8 | 1194.9 | 0.63057 | 6.009
2024-12-09 | 16:57 | Data | 0 | 32.568 | 30.198 | 186.855 | 7.64 | 175.555 | 2118.58 | 26 | 46.45 | 6.35 | 1.354 | 4.666 | 8431.69 | 2.052 | 97.8 | 77.5 | 1376 | 23.22 | 5480.6 | 1820.2 | 2206.7 | 2874 | 1194.9 | 0.63002 | 6.019
2024-12-09 | 16:57 | Data | 0 | 32.494 | 30.651 | 187.082 | 7.64 | 175.69 | 2117.68 | 26 | 45.998 | 6.35 | 1.354 | 4.682 | 8431.69 | 1.958 | 97.8 | 77.6 | 1376 | 23 | 5480.6 | 1805.5 | 2205.9 | 2863.1 | 1194.9 | 0.63415 | 6.035
2024-12-09 | 16:57 | Data | 0 | 32.271 | 30.415 | 186.901 | 7.65 | 175.555 | 2117.68 | 26 | 45.998 | 6.35 | 1.347 | 4.665 | 8400.04 | 1.857 | 97.8 | 77.6 | 1376 | 23 | 5460 | 1818.7 | 2244.8 | 2901.1 | 1194.9 | 0.62421 | 6.012
2024-12-09 | 16:57 | Data | 0 | 32.777 | 30.448 | 186.901 | 7.64 | 175.69 | 2117.68 | 26 | 45.998 | 6.35 | 1.349 | 4.686 | 8440.74 | 2.1 | 97.8 | 77.6 | 1376 | 23 | 5486.5 | 1822.4 | 2236.6 | 2898.7 | 1194.9 | 0.62654 | 6.036
2024-12-09 | 16:57 | Data | 0 | 32.609 | 30.59 | 186.901 | 7.64 | 175.6 | 2022.78 | 26.01 | 45.998 | 6.35 | 1.361 | 4.654 | 8454.3 | 2.16 | 97.7 | 77.4 | 1314 | 22.95 | 5495.3 | 1807.6 | 2246.6 | 2896.1 | 1194.9 | 0.62111 | 6.016
2024-12-09 | 16:57 | Data | 0 | 32.69 | 30.651 | 186.991 | 7.65 | 175.6 | 2120.39 | 26.01 | 45.908 | 6.34 | 1.348 | 4.669 | 8431.69 | 2.154 | 97.8 | 77.6 | 1378 | 22.95 | 5480.6 | 1830.2 | 2233.7 | 2898 | 1194.9 | 0.63 | 6.017
2024-12-09 | 16:57 | Data | 0 | 32.892 | 30.496 | 186.946 | 7.64 | 175.69 | 2127.62 | 26 | 45.998 | 6.35 | 1.349 | 4.673 | 8440.74 | 2.187 | 97.8 | 77.6 | 1384 | 23 | 5486.5 | 1826.3 | 2209.8 | 2897.1 | 1194.9 | 0.62991 | 6.022
2024-12-09 | 16:57 | Data | 0 | 32.879 | 30.901 | 186.991 | 7.64 | 175.6 | 2122.2 | 26 | 45.998 | 6.34 | 1.356 | 4.676 | 8639.71 | 2.079 | 97.8 | 77.5 | 1380 | 23 | 5615.8 | 1812.8 | 2200.3 | 2864.3 | 1194.9 | 0.63059 | 6.032
2024-12-09 | 16:57 | Data | 0 | 32.71 | 30.543 | 186.991 | 7.64 | 175.69 | 2123.1 | 26 | 45.818 | 6.35 | 1.345 | 4.666 | 8639.71 | 2.248 | 97.8 | 77.6 | 1380 | 22.86 | 5615.8 | 1810.7 | 2211.5 | 2870.4 | 1194.9 | 0.6296 | 6.011
2024-12-09 | 16:57 | Data | 0 | 32.514 | 30.806 | 186.901 | 7.64 | 175.6 | 2123.1 | 26 | 45.998 | 6.35 | 1.341 | 4.675 | 8639.71 | 1.877 | 97.8 | 77.7 | 1379 | 23 | 5615.8 | 1814.9 | 2227.3 | 2880.5 | 1194.9 | 0.63039 | 6.016
2024-12-09 | 16:57 | Data | 0 | 32.609 | 30.428 | 186.855 | 7.64 | 175.736 | 2123.1 | 26 | 45.998 | 6.35 | 1.343 | 4.69 | 8635.19 | 2.268 | 97.8 | 77.7 | 1379 | 22.95 | 5612.9 | 1821.3 | 2180.2 | 2851.8 | 1194.9 | 0.63743 | 6.034
2024-12-09 | 16:57 | Data | 0 | 32.669 | 30.482 | 187.036 | 7.64 | 175.555 | 2122.2 | 26 | 45.998 | 6.35 | 1.339 | 4.705 | 8409.08 | 2.093 | 97.8 | 77.8 | 1379 | 23 | 5465.9 | 1808.9 | 2197.6 | 2859.3 | 1194.9 | 0.62926 | 6.045
2024-12-09 | 16:57 | Data | 0 | 32.663 | 30.84 | 186.946 | 7.64 | 175.69 | 2122.2 | 26 | 45.908 | 6.34 | 1.342 | 4.707 | 8418.13 | 1.985 | 97.8 | 77.8 | 1379 | 23 | 5471.8 | 1826.3 | 2206.9 | 2873.8 | 1194.9 | 0.63335 | 6.049
2024-12-09 | 16:57 | Data | 0 | 32.771 | 30.678 | 187.082 | 7.64 | 175.736 | 2118.58 | 25.99 | 45.998 | 6.34 | 1.348 | 4.68 | 8409.08 | 2.052 | 97.8 | 77.7 | 1378 | 22.95 | 5465.9 | 1815.7 | 2234.1 | 2892.1 | 1194.9 | 0.62639 | 6.026
2024-12-09 | 16:57 | Data | 0 | 32.595 | 30.766 | 186.946 | 7.64 | 175.51 | 2119.49 | 26 | 45.998 | 6.35 | 1.352 | 4.685 | 8400.04 | 2.059 | 97.8 | 77.6 | 1378 | 23.04 | 5460 | 1806.9 | 2206.7 | 2864.6 | 1194.9 | 0.62207 | 6.037
2024-12-09 | 16:57 | Data | 0 | 32.71 | 30.421 | 186.991 | 7.64 | 175.6 | 2123.1 | 25.99 | 45.908 | 6.35 | 1.348 | 4.683 | 8418.13 | 2.295 | 97.8 | 77.6 | 1380 | 23 | 5471.8 | 1805.7 | 2249 | 2895.3 | 1194.9 | 0.62092 | 6.032
2024-12-09 | 16:57 | Data | 0 | 32.494 | 30.415 | 186.855 | 7.64 | 175.555 | 2122.2 | 26.01 | 45.908 | 6.35 | 1.349 | 4.683 | 8400.04 | 2.079 | 97.8 | 77.6 | 1380 | 22.95 | 5460 | 1816.9 | 2234.1 | 2881.5 | 1194.9 | 0.62369 | 6.033
2024-12-09 | 16:57 | Data | 0 | 32.494 | 30.624 | 186.901 | 7.64 | 175.6 | 2123.1 | 26 | 45.908 | 6.35 | 1.343 | 4.672 | 8418.13 | 1.897 | 97.8 | 77.7 | 1380 | 23 | 5471.8 | 1827.8 | 2237.2 | 2901.5 | 1194.9 | 0.62593 | 6.017
2024-12-09 | 16:58 | Data | 0 | 32.467 | 30.745 | 186.855 | 7.64 | 175.555 | 2123.1 | 26.01 | 45.908 | 6.35 | 1.352 | 4.686 | 8395.51 | 2.032 | 97.8 | 77.6 | 1380 | 22.95 | 5457.1 | 1813.8 | 2243.6 | 2894.3 | 1194.9 | 0.62528 | 6.039
2024-12-09 | 16:58 | Data | 0 | 32.636 | 30.536 | 187.036 | 7.65 | 175.69 | 2123.1 | 26 | 45.908 | 6.35 | 1.347 | 4.692 | 8409.08 | 1.992 | 97.8 | 77.7 | 1380 | 23 | 5465.9 | 1825.8 | 2242.1 | 2902.3 | 1194.9 | 0.62668 | 6.039
2024-12-09 | 16:58 | Data | 0 | 32.919 | 30.556 | 187.036 | 7.64 | 175.69 | 2120.39 | 26 | 45.908 | 6.35 | 1.348 | 4.682 | 8409.08 | 2.127 | 97.8 | 77.7 | 1378 | 23 | 5465.9 | 1819.1 | 2229.9 | 2890.4 | 1194.9 | 0.62647 | 6.03
2024-12-09 | 16:58 | Data | 0 | 32.555 | 30.84 | 186.991 | 7.64 | 175.6 | 2119.49 | 26.01 | 45.998 | 6.35 | 1.344 | 4.69 | 8427.17 | 2.032 | 97.8 | 77.7 | 1378 | 23 | 5477.7 | 1808.5 | 2207.9 | 2866.1 | 1194.9 | 0.62915 | 6.034
2024-12-09 | 16:58 | Data | 0 | 32.494 | 30.394 | 186.855 | 7.64 | 175.464 | 2120.39 | 26 | 45.908 | 6.35 | 1.344 | 4.695 | 8431.69 | 2.1 | 97.8 | 77.8 | 1378 | 22.95 | 5480.6 | 1834 | 2214.2 | 2884.9 | 1194.9 | 0.63409 | 6.038
2024-12-09 | 16:58 | Data | 0 | 32.494 | 30.428 | 186.765 | 7.64 | 175.555 | 2114.06 | 26.01 | 45.998 | 6.35 | 1.339 | 4.687 | 8427.17 | 2.019 | 97.8 | 77.8 | 1374 | 23 | 5477.7 | 1811.2 | 2218.7 | 2875.9 | 1194.9 | 0.62778 | 6.026
2024-12-09 | 16:58 | Data | 0 | 32.494 | 30.442 | 186.946 | 7.64 | 175.51 | 2121.29 | 26 | 45.998 | 6.35 | 1.351 | 4.686 | 8400.04 | 1.978 | 97.8 | 77.6 | 1379 | 23 | 5460 | 1808.4 | 2223.4 | 2880.7 | 1194.9 | 0.62472 | 6.037
2024-12-09 | 16:58 | Data | 0 | 32.487 | 30.637 | 187.082 | 7.64 | 175.555 | 2120.39 | 26 | 45.908 | 6.35 | 1.353 | 4.705 | 8400.04 | 1.951 | 97.8 | 77.7 | 1378 | 23 | 5460 | 1827.5 | 2233.2 | 2895.8 | 1194.9 | 0.62932 | 6.059
2024-12-09 | 16:58 | Data | 0 | 32.413 | 30.415 | 186.901 | 7.64 | 175.555 | 2117.68 | 26.01 | 45.998 | 6.34 | 1.355 | 4.683 | 8400.04 | 2.059 | 97.8 | 77.6 | 1376 | 23 | 5460 | 1812.4 | 2237.4 | 2891.4 | 1194.9 | 0.62303 | 6.039
2024-12-09 | 16:58 | Data | 0 | 32.494 | 30.529 | 186.901 | 7.65 | 175.6 | 2117.68 | 26.01 | 45.998 | 6.35 | 1.349 | 4.671 | 8449.78 | 2.046 | 97.8 | 77.6 | 1376 | 23 | 5492.4 | 1814.7 | 2255.7 | 2906.3 | 1194.9 | 0.62417 | 6.021
2024-12-09 | 16:58 | Data | 0 | 32.717 | 30.428 | 186.946 | 7.64 | 175.6 | 2110.45 | 26 | 45.998 | 6.35 | 1.346 | 4.679 | 8458.83 | 2.079 | 97.8 | 77.7 | 1372 | 23.04 | 5498.2 | 1798.2 | 2243.6 | 2888.2 | 1194.9 | 0.62164 | 6.025
2024-12-09 | 16:58 | Data | 0 | 32.264 | 30.361 | 186.81 | 7.64 | 175.555 | 2114.06 | 26 | 45.998 | 6.35 | 1.339 | 4.7 | 8458.83 | 2.194 | 97.8 | 77.8 | 1374 | 22.95 | 5498.2 | 1823.3 | 2232.2 | 2894.1 | 1194.9 | 0.62802 | 6.037
2024-12-09 | 16:58 | Data | 0 | 32.561 | 30.212 | 186.991 | 7.64 | 175.6 | 2117.68 | 26.01 | 45.908 | 6.35 | 1.339 | 4.687 | 8454.3 | 2.106 | 97.8 | 77.8 | 1376 | 23 | 5495.3 | 1810.3 | 2215.7 | 2872.9 | 1194.9 | 0.62767 | 6.026
2024-12-09 | 16:58 | Data | 0 | 32.487 | 30.394 | 186.765 | 7.64 | 175.51 | 2117.68 | 26 | 45.998 | 6.34 | 1.34 | 4.688 | 8445.26 | 2.12 | 97.8 | 77.8 | 1376 | 23 | 5489.4 | 1824.9 | 2194.1 | 2865.2 | 1194.9 | 0.63451 | 6.028
2024-12-09 | 16:58 | Data | 0 | 32.305 | 30.415 | 186.901 | 7.65 | 175.555 | 2123.1 | 26 | 45.908 | 6.35 | 1.348 | 4.703 | 8472.39 | 1.863 | 97.8 | 77.7 | 1379 | 22.95 | 5507.1 | 3148.3 | 3446.5 | 4739.3 | 1194.9 | 0.63324 | 6.051
2024-12-09 | 16:58 | Data | 0 | 32.663 | 30.428 | 186.765 | 7.64 | 175.51 | 2120.39 | 26 | 45.998 | 6.35 | 1.34 | 4.674 | 8481.44 | 2.228 | 97.8 | 77.7 | 1378 | 23 | 5512.9 | 2899.6 | 2811 | 4158.9 | 1194.9 | 0.68087 | 6.015
2024-12-09 | 16:58 | Data | 0 | 32.885 | 30.678 | 187.036 | 7.64 | 175.6 | 2120.39 | 26 | 45.998 | 6.35 | 1.336 | 4.673 | 8481.44 | 2.066 | 97.8 | 77.8 | 1378 | 22.91 | 5512.9 | 2882.7 | 2794.9 | 4132.7 | 1194.9 | 0.68233 | 6.007
2024-12-09 | 16:58 | Data | 0 | 32.879 | 30.759 | 187.036 | 7.65 | 175.69 | 2120.39 | 26 | 45.998 | 6.35 | 1.353 | 4.702 | 8481.44 | 2.059 | 97.8 | 77.6 | 1378 | 22.95 | 5512.9 | 2894.8 | 2798.8 | 4147.2 | 1194.9 | 0.68115 | 6.054
2024-12-09 | 16:59 | Data | 0 | 32.548 | 30.442 | 187.036 | 7.64 | 175.69 | 2120.39 | 26.01 | 45.998 | 6.35 | 1.348 | 4.677 | 8472.39 | 2.032 | 97.8 | 77.6 | 1378 | 23 | 5507.1 | 2900.4 | 2800.6 | 4150.4 | 1194.9 | 0.68337 | 6.026
2024-12-09 | 16:59 | Data | 0 | 32.467 | 30.651 | 186.901 | 7.64 | 175.51 | 2120.39 | 26 | 45.998 | 6.35 | 1.351 | 4.679 | 8472.39 | 2.066 | 97.8 | 77.6 | 1378 | 22.95 | 5507.1 | 2909.7 | 2786.6 | 4152.1 | 1195 | 0.68408 | 6.03
2024-12-09 | 16:59 | Data | 0 | 32.494 | 30.637 | 186.901 | 7.64 | 175.69 | 2117.68 | 26 | 45.998 | 6.35 | 1.348 | 4.664 | 8481.44 | 1.904 | 97.8 | 77.6 | 1376 | 22.95 | 5512.9 | 2890.6 | 2799.6 | 4150.2 | 1195 | 0.68074 | 6.01
2024-12-09 | 16:59 | Data | 0 | 32.717 | 30.442 | 187.082 | 7.64 | 175.555 | 2117.68 | 26 | 45.908 | 6.35 | 1.348 | 4.684 | 8445.26 | 2.187 | 97.8 | 77.7 | 1377 | 22.95 | 5489.4 | 2879.5 | 2802.9 | 4141.2 | 1195 | 0.68104 | 6.033
2024-12-09 | 16:59 | Data | 0 | 32.447 | 30.394 | 186.901 | 7.64 | 175.555 | 2119.49 | 26 | 45.998 | 6.35 | 1.349 | 4.662 | 8431.69 | 2.019 | 97.8 | 77.6 | 1378 | 23 | 5480.6 | 2882.6 | 2802.5 | 4141 | 1195 | 0.6809 | 6.012
2024-12-09 | 16:59 | Data | 0 | 32.804 | 30.84 | 186.855 | 7.64 | 175.6 | 2120.39 | 26 | 45.998 | 6.35 | 1.356 | 4.683 | 8418.13 | 1.897 | 97.8 | 77.6 | 1378 | 23 | 5471.8 | 2898.7 | 2797.4 | 4146.7 | 1195 | 0.68392 | 6.039
2024-12-09 | 16:59 | Data | 0 | 32.622 | 30.86 | 186.901 | 7.64 | 175.555 | 2120.39 | 25.99 | 46.179 | 6.35 | 1.346 | 4.7 | 8418.13 | 2.066 | 97.8 | 77.7 | 1378 | 23.09 | 5471.8 | 2890.6 | 2810.1 | 4149.3 | 1195 | 0.68035 | 6.046
2024-12-09 | 16:59 | Data | 0 | 32.885 | 30.34 | 186.991 | 7.64 | 175.6 | 2123.1 | 25.99 | 45.908 | 6.35 | 1.345 | 4.695 | 8467.87 | 2.16 | 97.8 | 77.7 | 1380 | 22.95 | 5504.1 | 2869.2 | 2813.1 | 4139.6 | 1195 | 0.67873 | 6.042
2024-12-09 | 16:59 | Data | 0 | 32.271 | 30.415 | 186.946 | 7.64 | 175.51 | 2122.2 | 25.99 | 45.998 | 6.35 | 1.341 | 4.684 | 8476.91 | 2.025 | 97.8 | 77.7 | 1380 | 22.95 | 5510 | 2897.2 | 2804.5 | 4147.5 | 1195 | 0.68243 | 6.026
2024-12-09 | 16:59 | Data | 0 | 32.663 | 30.624 | 186.946 | 7.64 | 175.464 | 2122.2 | 25.98 | 45.908 | 6.35 | 1.339 | 4.672 | 8481.44 | 2.093 | 97.8 | 77.7 | 1379 | 23 | 5512.9 | 2885.7 | 2792.9 | 4133.7 | 1195 | 0.6818 | 6.01
2024-12-09 | 16:59 | Data | 0 | 32.264 | 30.84 | 186.81 | 7.64 | 175.51 | 2120.39 | 25.99 | 45.998 | 6.35 | 1.344 | 4.666 | 8481.44 | 2.12 | 97.8 | 77.7 | 1378 | 22.95 | 5512.9 | 2898.9 | 2766.2 | 4123.9 | 1195 | 0.6869 | 6.009
2024-12-09 | 16:59 | Data | 0 | 32.494 | 30.415 | 186.855 | 7.64 | 175.464 | 2121.29 | 25.97 | 45.998 | 6.34 | 1.356 | 4.664 | 8458.83 | 2.079 | 97.8 | 77.5 | 1379 | 22.95 | 5498.2 | 2898 | 2782.2 | 4137.6 | 1195 | 0.68461 | 6.019
2024-12-09 | 16:59 | Data | 0 | 32.663 | 30.448 | 187.036 | 7.64 | 175.69 | 2121.29 | 25.97 | 46.089 | 6.35 | 1.351 | 4.681 | 8467.87 | 2.032 | 97.8 | 77.6 | 1378 | 23.09 | 5504.1 | 2903.2 | 2787.4 | 4141.4 | 1195 | 0.68503 | 6.032
2024-12-09 | 16:59 | Data | 0 | 32.494 | 30.246 | 186.81 | 7.64 | 175.419 | 2117.68 | 25.97 | 46.269 | 6.35 | 1.345 | 4.671 | 8467.87 | 2.079 | 97.8 | 77.6 | 1376 | 23.09 | 5504.1 | 2897.7 | 2788.3 | 4145.9 | 1195 | 0.68331 | 6.015
2024-12-09 | 16:59 | Data | 0 | 32.379 | 30.644 | 186.991 | 7.64 | 175.6 | 2124.01 | 25.99 | 46.269 | 6.35 | 1.352 | 4.695 | 8467.87 | 2.005 | 97.8 | 77.6 | 1381 | 23.09 | 5504.1 | 2901.5 | 2776.8 | 4130 | 1195 | 0.68657 | 6.047
2024-12-09 | 16:59 | Data | 0 | 32.501 | 30.624 | 186.855 | 7.64 | 175.555 | 2123.1 | 25.99 | 46.089 | 6.35 | 1.351 | 4.668 | 8445.26 | 1.944 | 97.8 | 77.6 | 1379 | 23.09 | 5489.4 | 2881.9 | 2802.7 | 4141.8 | 1195 | 0.68002 | 6.017
2024-12-09 | 16:59 | Data | 0 | 32.636 | 30.651 | 186.991 | 7.64 | 175.736 | 2121.29 | 25.99 | 46.179 | 6.35 | 1.339 | 4.641 | 8436.21 | 1.863 | 97.8 | 77.6 | 1379 | 23.09 | 5483.5 | 2900.9 | 2804 | 4154.9 | 1195 | 0.68121 | 5.979
2024-12-09 | 17:00 | Data | 0 | 32.919 | 30.705 | 186.991 | 7.64 | 175.555 | 2119.49 | 25.99 | 46.179 | 6.35 | 1.342 | 4.659 | 8431.69 | 2.073 | 97.8 | 77.6 | 1378 | 23.18 | 5480.6 | 2895.4 | 2818.2 | 4155.4 | 1195 | 0.6808 | 6.002
2024-12-09 | 17:00 | Data | 0 | 32.332 | 30.59 | 186.901 | 7.64 | 175.69 | 2120.39 | 25.98 | 46.269 | 6.35 | 1.344 | 4.655 | 8445.26 | 1.688 | 97.8 | 77.6 | 1378 | 23.13 | 5489.4 | 2886.9 | 2804.4 | 4140.4 | 1195 | 0.68082 | 5.999
2024-12-09 | 17:00 | Data | 0 | 32.548 | 30.624 | 186.901 | 7.64 | 175.6 | 2122.2 | 25.99 | 46.269 | 6.35 | 1.355 | 4.697 | 8436.21 | 1.911 | 97.8 | 77.6 | 1379 | 23.13 | 5483.5 | 2904.4 | 2797.8 | 4148.9 | 1195 | 0.68439 | 6.05
2024-12-09 | 17:00 | Data | 0 | 32.359 | 30.536 | 186.946 | 7.64 | 175.6 | 2125.81 | 25.99 | 46.179 | 6.35 | 1.347 | 4.68 | 8445.26 | 1.863 | 97.8 | 77.7 | 1382 | 23.13 | 5489.4 | 2904.7 | 2789.1 | 4145.8 | 1195 | 0.68488 | 6.027
2024-12-09 | 17:00 | Data | 0 | 32.717 | 30.415 | 186.81 | 7.64 | 175.51 | 2124.91 | 25.99 | 46.269 | 6.34 | 1.348 | 4.654 | 8445.26 | 2.093 | 97.8 | 77.5 | 1381 | 23.13 | 5489.4 | 2885.9 | 2775.5 | 4124.3 | 1195 | 0.68453 | 6.002
2024-12-09 | 17:00 | Data | 0 | 32.602 | 30.502 | 186.946 | 7.64 | 175.6 | 2125.81 | 25.99 | 46.179 | 6.35 | 1.353 | 4.648 | 8445.26 | 2.248 | 97.8 | 77.5 | 1381 | 23.09 | 5489.4 | 2895.7 | 2783.6 | 4137.9 | 1195 | 0.68561 | 6
2024-12-09 | 17:00 | Data | 0 | 32.467 | 30.644 | 186.901 | 7.64 | 175.51 | 2125.81 | 25.99 | 46.179 | 6.35 | 1.354 | 4.667 | 8440.74 | 2.16 | 97.8 | 77.5 | 1382 | 23.09 | 5486.5 | 2875.3 | 2787.4 | 4130.6 | 1195 | 0.67965 | 6.021
2024-12-09 | 17:00 | Data | 0 | 32.332 | 30.421 | 186.855 | 7.64 | 175.555 | 2125.81 | 26 | 46.269 | 6.35 | 1.346 | 4.686 | 8440.74 | 1.857 | 97.8 | 77.7 | 1382 | 23.09 | 5486.5 | 2894.7 | 2794.8 | 4145 | 1195 | 0.68227 | 6.032
2024-12-09 | 17:00 | Data | 0 | 32.494 | 30.536 | 187.036 | 7.64 | 175.555 | 2125.81 | 25.99 | 45.998 | 6.35 | 1.345 | 4.653 | 8445.26 | 2.194 | 97.8 | 77.6 | 1381 | 23 | 5489.4 | 2891.7 | 2783.1 | 4132.3 | 1195 | 0.68328 | 5.998
2024-12-09 | 17:00 | Data | 0 | 32.501 | 30.624 | 186.855 | 7.64 | 175.555 | 2123.1 | 26 | 46.179 | 6.35 | 1.347 | 4.653 | 8431.69 | 1.958 | 97.8 | 77.6 | 1380 | 23.13 | 5480.6 | 2898.7 | 2790.6 | 4140.8 | 1195 | 0.68386 | 5.999
2024-12-09 | 17:00 | Data | 0 | 32.609 | 30.644 | 186.946 | 7.64 | 175.6 | 2125.81 | 25.99 | 45.908 | 6.35 | 1.348 | 4.667 | 8427.17 | 2.046 | 97.8 | 77.6 | 1382 | 22.95 | 5477.7 | 2895.2 | 2803.9 | 4146.2 | 1195 | 0.68156 | 6.015
2024-12-09 | 17:00 | Data | 0 | 32.609 | 30.698 | 186.946 | 7.64 | 175.69 | 2125.81 | 26 | 45.998 | 6.35 | 1.354 | 4.699 | 8427.17 | 2.113 | 97.8 | 77.6 | 1382 | 22.95 | 5477.7 | 2883 | 2814.5 | 4145.2 | 1195 | 0.67895 | 6.053
2024-12-09 | 17:00 | Data | 0 | 32.271 | 30.59 | 186.946 | 7.64 | 175.464 | 2125.81 | 26 | 45.998 | 6.34 | 1.355 | 4.682 | 8431.69 | 2.046 | 97.8 | 77.6 | 1381 | 22.95 | 5480.6 | 2903.3 | 2821.8 | 4167.6 | 1195 | 0.68009 | 6.036
2024-12-09 | 17:00 | Data | 0 | 32.723 | 30.482 | 186.946 | 7.65 | 175.51 | 2125.81 | 26 | 46.089 | 6.35 | 1.351 | 4.701 | 8427.17 | 2.167 | 97.8 | 77.7 | 1382 | 23.04 | 5477.7 | 2916.1 | 2797.7 | 4157.6 | 1195 | 0.68375 | 6.052
2024-12-09 | 17:00 | Data | 0 | 32.818 | 30.759 | 186.946 | 7.64 | 175.69 | 2124.91 | 26 | 46.089 | 6.35 | 1.34 | 4.69 | 8445.26 | 2.052 | 97.8 | 77.8 | 1382 | 23 | 5489.4 | 2900.9 | 2791.3 | 4144.2 | 1195 | 0.68369 | 6.031
2024-12-09 | 17:00 | Data | 0 | 32.69 | 30.651 | 186.991 | 7.65 | 175.555 | 2125.81 | 26 | 45.998 | 6.35 | 1.347 | 4.664 | 8440.74 | 2.268 | 97.8 | 77.6 | 1382 | 23 | 5486.5 | 2907.4 | 2794.4 | 4147.3 | 1195 | 0.68515 | 6.01
2024-12-09 | 17:00 | Data | 0 | 33.048 | 30.55 | 187.082 | 7.64 | 175.781 | 2126.72 | 26.01 | 45.998 | 6.35 | 1.351 | 4.684 | 8454.3 | 2.039 | 97.8 | 77.6 | 1382 | 22.95 | 5495.3 | 2904.7 | 2793.9 | 4148.2 | 1195 | 0.68391 | 6.036
2024-12-09 | 17:00 | Data | 0 | 33.061 | 30.455 | 186.946 | 7.64 | 175.736 | 2124.91 | 26 | 45.998 | 6.35 | 1.359 | 4.673 | 8458.83 | 2.154 | 97.8 | 77.5 | 1382 | 22.95 | 5498.2 | 2877.6 | 2803.1 | 4141.3 | 1195 | 0.67914 | 6.032
2024-12-09 | 17:01 | Data | 0 | 32.494 | 30.421 | 186.855 | 7.64 | 175.6 | 2124.91 | 26 | 45.998 | 6.35 | 1.344 | 4.665 | 8467.87 | 2.167 | 97.8 | 77.6 | 1382 | 23 | 5504.1 | 2905.2 | 2784.9 | 4129.5 | 1195 | 0.68706 | 6.009
2024-12-09 | 17:01 | Data | 0 | 32.561 | 30.428 | 186.946 | 7.64 | 175.781 | 2124.91 | 26 | 45.998 | 6.35 | 1.355 | 4.683 | 8467.87 | 2.073 | 97.8 | 77.6 | 1381 | 23 | 5504.1 | 2894.3 | 2798.8 | 4145.5 | 1195 | 0.68303 | 6.036
2024-12-09 | 17:01 | Data | 0 | 33.102 | 30.678 | 186.991 | 7.64 | 175.736 | 2126.72 | 26 | 45.908 | 6.35 | 1.348 | 4.695 | 8467.87 | 2.343 | 97.8 | 77.7 | 1382 | 22.95 | 5504.1 | 2913 | 2776.1 | 4142 | 1195.1 | 0.68415 | 6.044
2024-12-09 | 17:01 | Data | 0 | 32.534 | 30.624 | 186.855 | 7.64 | 175.69 | 2125.81 | 25.99 | 45.908 | 6.34 | 1.341 | 4.654 | 8481.44 | 1.978 | 97.8 | 77.6 | 1381 | 23 | 5512.9 | 2887.4 | 2791.4 | 4134 | 1195.1 | 0.68558 | 5.996
2024-12-09 | 17:01 | Data | 0 | 32.885 | 30.482 | 187.082 | 7.64 | 175.736 | 2125.81 | 26 | 45.908 | 6.35 | 1.356 | 4.693 | 8454.3 | 2.093 | 97.8 | 77.6 | 1382 | 23 | 5495.3 | 2886.1 | 2762.6 | 4112 | 1195.1 | 0.68485 | 6.048
2024-12-09 | 17:01 | Data | 0 | 32.723 | 30.887 | 186.991 | 7.65 | 175.781 | 2123.1 | 26 | 45.998 | 6.35 | 1.345 | 4.66 | 8454.3 | 2.032 | 97.8 | 77.6 | 1380 | 22.95 | 5495.3 | 2885.2 | 2809.8 | 4150.5 | 1195.1 | 0.67832 | 6.005
2024-12-09 | 17:01 | Data | 0 | 32.71 | 30.874 | 186.991 | 7.64 | 175.69 | 2122.2 | 26 | 45.998 | 6.35 | 1.352 | 4.664 | 8472.39 | 2.052 | 97.8 | 77.5 | 1380 | 22.95 | 5507.1 | 2896.6 | 2800.4 | 4149.8 | 1195.1 | 0.68248 | 6.017
2024-12-09 | 17:01 | Data | 0 | 32.717 | 30.644 | 186.946 | 7.64 | 175.6 | 2120.39 | 26 | 45.908 | 6.35 | 1.355 | 4.692 | 8454.3 | 1.978 | 97.8 | 77.6 | 1378 | 22.95 | 5495.3 | 2897.8 | 2775 | 4127.8 | 1195.1 | 0.68631 | 6.047
2024-12-09 | 17:01 | Data | 0 | 32.494 | 30.415 | 186.855 | 7.64 | 175.555 | 2120.39 | 26 | 46.089 | 6.34 | 1.347 | 4.705 | 8458.83 | 2.073 | 97.8 | 77.7 | 1378 | 23 | 5498.2 | 2893.5 | 2802.1 | 4148.8 | 1195.1 | 0.68157 | 6.052
2024-12-09 | 17:01 | Data | 0 | 32.501 | 30.523 | 186.901 | 7.64 | 175.6 | 2120.39 | 26 | 45.998 | 6.35 | 1.338 | 4.703 | 8440.74 | 1.87 | 97.8 | 77.9 | 1378 | 22.95 | 5486.5 | 2891.2 | 2793.7 | 4139.3 | 1195.1 | 0.68178 | 6.041
2024-12-09 | 17:01 | Data | 0 | 32.453 | 30.759 | 186.946 | 7.64 | 175.736 | 2120.39 | 26 | 45.998 | 6.35 | 1.345 | 4.677 | 8445.26 | 2.019 | 97.8 | 77.7 | 1378 | 23 | 5489.4 | 2895.3 | 2793 | 4145.9 | 1195.1 | 0.68141 | 6.022
2024-12-09 | 17:01 | Data | 0 | 32.555 | 30.421 | 186.991 | 7.64 | 175.736 | 2120.39 | 26.01 | 45.998 | 6.35 | 1.348 | 4.641 | 8445.26 | 2.079 | 97.8 | 77.5 | 1378 | 22.95 | 5489.4 | 2902.7 | 2797.5 | 4152.4 | 1195.1 | 0.68307 | 5.989
2024-12-09 | 17:01 | Data | 0 | 32.548 | 30.415 | 186.991 | 7.64 | 175.736 | 2123.1 | 26.01 | 45.998 | 6.35 | 1.356 | 4.687 | 8431.69 | 2.086 | 97.8 | 77.6 | 1380 | 23 | 5480.6 | 2890.1 | 2809.8 | 4149.9 | 1195.1 | 0.68287 | 6.042
2024-12-09 | 17:01 | Data | 0 | 32.494 | 30.644 | 186.946 | 7.64 | 175.555 | 2119.49 | 26 | 45.998 | 6.35 | 1.355 | 4.649 | 8440.74 | 1.904 | 97.8 | 77.4 | 1378 | 22.95 | 5486.5 | 2902.8 | 2808.2 | 4156.9 | 1195.1 | 0.68237 | 6.005
2024-12-09 | 17:01 | Data | 0 | 32.494 | 30.469 | 186.855 | 7.65 | 175.6 | 2112.26 | 26 | 45.998 | 6.35 | 1.356 | 4.635 | 8445.26 | 2.025 | 97.8 | 77.4 | 1373 | 22.95 | 5489.4 | 2883.6 | 2785.9 | 4134 | 1195.1 | 0.68182 | 5.991
2024-12-09 | 17:01 | Data | 0 | 32.723 | 30.651 | 186.901 | 7.65 | 175.555 | 2119.49 | 26 | 45.998 | 6.35 | 1.342 | 4.648 | 8445.26 | 1.958 | 97.8 | 77.6 | 1378 | 23 | 5489.4 | 2886.9 | 2806.2 | 4147.5 | 1195.1 | 0.68071 | 5.99
2024-12-09 | 17:01 | Data | 0 | 32.494 | 30.415 | 186.946 | 7.64 | 175.69 | 2122.2 | 26 | 45.998 | 6.35 | 1.345 | 4.672 | 8458.83 | 2.079 | 97.8 | 77.6 | 1379 | 22.95 | 5498.2 | 2902.6 | 2782.3 | 4124.7 | 1195.1 | 0.68618 | 6.017
2024-12-09 | 17:01 | Data | 0 | 32.926 | 30.712 | 186.946 | 7.64 | 175.69 | 2124.91 | 25.99 | 45.998 | 6.34 | 1.343 | 4.673 | 8458.83 | 2.066 | 97.8 | 77.7 | 1381 | 23 | 5498.2 | 2891.4 | 2777.1 | 4132.1 | 1195.1 | 0.68486 | 6.016
2024-12-09 | 17:02 | Data | 0 | 32.413 | 30.516 | 186.901 | 7.64 | 175.6 | 2122.2 | 26 | 45.998 | 6.35 | 1.348 | 4.689 | 8445.26 | 1.863 | 97.8 | 77.7 | 1380 | 23 | 5489.4 | 2890.4 | 2764.5 | 4121.7 | 1195.1 | 0.68398 | 6.037
2024-12-09 | 17:02 | Data | 0 | 32.582 | 30.421 | 187.036 | 7.64 | 175.69 | 2122.2 | 26 | 45.908 | 6.35 | 1.348 | 4.7 | 8458.83 | 1.911 | 97.8 | 77.7 | 1380 | 22.95 | 5498.2 | 2904.6 | 2776.5 | 4132.5 | 1195.1 | 0.6875 | 6.048
2024-12-09 | 17:02 | Data | 0 | 32.494 | 30.415 | 186.901 | 7.64 | 175.69 | 2123.1 | 26 | 45.908 | 6.35 | 1.348 | 4.694 | 8418.13 | 2.079 | 97.8 | 77.7 | 1379 | 22.95 | 5471.8 | 2907.7 | 2794.6 | 4149.8 | 1195.1 | 0.68274 | 6.043
2024-12-09 | 17:02 | Data | 0 | 32.494 | 30.651 | 186.765 | 7.64 | 175.6 | 2123.1 | 26.01 | 45.908 | 6.35 | 1.339 | 4.682 | 8418.13 | 2.066 | 97.8 | 77.8 | 1380 | 22.95 | 5471.8 | 2901.8 | 2819.8 | 4163.8 | 1195.1 | 0.68068 | 6.021
2024-12-09 | 17:02 | Data | 0 | 32.994 | 31.036 | 187.082 | 7.64 | 175.6 | 2122.2 | 26 | 45.998 | 6.35 | 1.344 | 4.641 | 8427.17 | 2.167 | 97.8 | 77.6 | 1380 | 23 | 5477.7 | 2897.6 | 2815.3 | 4154.6 | 1195.1 | 0.68135 | 5.984
2024-12-09 | 17:02 | Data | 0 | 32.501 | 30.523 | 186.901 | 7.64 | 175.6 | 2119.49 | 26 | 45.998 | 6.35 | 1.346 | 4.663 | 8431.69 | 2.147 | 97.8 | 77.6 | 1378 | 22.95 | 5480.6 | 2900.2 | 2828 | 4169 | 1195.1 | 0.67878 | 6.008
2024-12-09 | 17:02 | Data | 0 | 32.494 | 30.644 | 186.991 | 7.64 | 175.69 | 2117.68 | 26 | 45.998 | 6.35 | 1.348 | 4.679 | 8440.74 | 1.87 | 97.8 | 77.6 | 1377 | 22.95 | 5486.5 | 2892.8 | 2779.7 | 4128.5 | 1195.1 | 0.6842 | 6.027
2024-12-09 | 17:02 | Data | 0 | 32.501 | 30.536 | 187.036 | 7.64 | 175.69 | 2116.78 | 26.01 | 45.998 | 6.35 | 1.349 | 4.67 | 8440.74 | 2.073 | 97.8 | 77.6 | 1376 | 23 | 5486.5 | 2894.2 | 2790.3 | 4139.1 | 1195.1 | 0.68267 | 6.019
2024-12-09 | 17:02 | Data | 0 | 32.534 | 30.644 | 186.946 | 7.64 | 175.555 | 2117.68 | 26.01 | 45.908 | 6.35 | 1.346 | 4.669 | 8440.74 | 1.904 | 97.8 | 77.6 | 1376 | 22.95 | 5486.5 | 2916.4 | 2783.4 | 4145.8 | 1195.1 | 0.6844 | 6.015
2024-12-09 | 17:02 | Data | 0 | 32.737 | 30.651 | 187.036 | 7.65 | 175.781 | 2119.49 | 26 | 45.998 | 6.35 | 1.338 | 4.682 | 8440.74 | 1.904 | 97.8 | 77.8 | 1378 | 23 | 5486.5 | 2896.8 | 2797.8 | 4149.5 | 1195.1 | 0.6813 | 6.019
2024-12-09 | 17:02 | Data | 0 | 32.811 | 30.975 | 187.082 | 7.65 | 175.736 | 2118.58 | 26 | 45.998 | 6.35 | 1.344 | 4.705 | 8427.17 | 2.133 | 97.8 | 77.8 | 1377 | 22.95 | 5477.7 | 2893.3 | 2805.9 | 4147.7 | 1195.1 | 0.68268 | 6.049
2024-12-09 | 17:02 | Data | 0 | 32.642 | 30.651 | 186.901 | 7.64 | 175.69 | 2114.06 | 26 | 45.998 | 6.35 | 1.349 | 4.699 | 8454.3 | 1.877 | 97.8 | 77.7 | 1374 | 23 | 5495.3 | 2898.3 | 2806.9 | 4149.4 | 1195.1 | 0.68293 | 6.048
2024-12-09 | 17:02 | Data | 0 | 32.784 | 30.475 | 187.082 | 7.64 | 175.781 | 2114.06 | 26.01 | 45.998 | 6.35 | 1.355 | 4.647 | 8445.26 | 1.897 | 97.8 | 77.4 | 1374 | 23 | 5489.4 | 2900.7 | 2812.1 | 4152.1 | 1195.1 | 0.67905 | 6.001
2024-12-09 | 17:02 | Data | 0 | 32.501 | 30.752 | 187.036 | 7.64 | 175.6 | 2114.06 | 26 | 45.998 | 6.35 | 1.355 | 4.659 | 8467.87 | 2.019 | 97.8 | 77.5 | 1375 | 22.95 | 5504.1 | 2930.2 | 2813.5 | 4174.7 | 1195.1 | 0.68416 | 6.013
2024-12-09 | 17:02 | Data | 0 | 32.609 | 30.651 | 186.901 | 7.65 | 175.781 | 2113.16 | 26 | 45.998 | 6.35 | 1.348 | 4.676 | 8431.69 | 2.059 | 97.8 | 77.6 | 1375 | 22.95 | 5480.6 | 2879.3 | 2780.6 | 4123.6 | 1195.1 | 0.68155 | 6.024
2024-12-09 | 17:02 | Data | 0 | 32.696 | 30.442 | 186.81 | 7.64 | 175.6 | 2117.68 | 26 | 45.908 | 6.35 | 1.339 | 4.692 | 8409.08 | 1.992 | 97.8 | 77.8 | 1376 | 23 | 5465.9 | 2894 | 2792.5 | 4140.6 | 1195.1 | 0.68244 | 6.031
2024-12-09 | 17:02 | Data | 0 | 32.723 | 30.442 | 186.946 | 7.64 | 175.69 | 2114.97 | 26 | 45.998 | 6.35 | 1.351 | 4.674 | 8418.13 | 2.133 | 97.8 | 77.6 | 1375 | 23 | 5471.8 | 2891.1 | 2811.9 | 4153.2 | 1195.1 | 0.67979 | 6.026
2024-12-09 | 17:02 | Data | 0 | 32.521 | 30.712 | 186.855 | 7.65 | 175.555 | 2117.68 | 26 | 46.089 | 6.35 | 1.352 | 4.664 | 8418.13 | 2.079 | 97.8 | 77.5 | 1376 | 23 | 5471.8 | 2893.2 | 2793.4 | 4141.4 | 1195.1 | 0.68117 | 6.017
2024-12-09 | 17:03 | Data | 0 | 32.494 | 30.388 | 186.946 | 7.64 | 175.69 | 2114.97 | 26 | 45.908 | 6.35 | 1.348 | 4.673 | 8431.69 | 2.181 | 97.8 | 77.6 | 1375 | 23 | 5480.6 | 2901.2 | 2793.3 | 4143.5 | 1195.1 | 0.68472 | 6.019
2024-12-09 | 17:03 | Data | 0 | 32.811 | 30.867 | 186.991 | 7.64 | 175.6 | 2111.35 | 26 | 45.998 | 6.34 | 1.347 | 4.684 | 8418.13 | 2.059 | 97.8 | 77.7 | 1372 | 22.95 | 5471.8 | 2903.1 | 2785.4 | 4137.8 | 1195.1 | 0.68575 | 6.031
2024-12-09 | 17:03 | Data | 0 | 32.946 | 30.489 | 187.172 | 7.65 | 175.736 | 2111.35 | 26.01 | 45.998 | 6.35 | 1.341 | 4.677 | 8440.74 | 2.214 | 97.8 | 77.7 | 1372 | 22.95 | 5486.5 | 2907.2 | 2808.2 | 4161.1 | 1195.1 | 0.6823 | 6.017
2024-12-09 | 17:03 | Data | 0 | 32.548 | 30.766 | 186.901 | 7.64 | 175.6 | 2111.35 | 25.99 | 45.998 | 6.35 | 1.348 | 4.672 | 8431.69 | 1.985 | 97.8 | 77.6 | 1372 | 23 | 5480.6 | 2904 | 2800.9 | 4151.4 | 1195.2 | 0.68156 | 6.017
2024-12-09 | 17:03 | Data | 0 | 32.467 | 30.415 | 186.991 | 7.65 | 175.555 | 2108.64 | 26 | 45.998 | 6.35 | 1.353 | 4.658 | 8603.54 | 2.073 | 97.8 | 77.5 | 1371 | 23 | 5592.3 | 2898.6 | 2801.1 | 4151.4 | 1195.2 | 0.68119 | 6.012
2024-12-09 | 17:03 | Data | 0 | 32.609 | 30.644 | 186.946 | 7.64 | 175.6 | 2109.54 | 26 | 45.998 | 6.35 | 1.346 | 4.673 | 8626.15 | 2.086 | 97.8 | 77.6 | 1371 | 22.95 | 5607 | 2895.3 | 2840.8 | 4173 | 1195.2 | 0.67621 | 6.019
2024-12-09 | 17:03 | Data | 0 | 32.811 | 30.705 | 186.991 | 7.64 | 175.69 | 2108.64 | 26 | 45.998 | 6.35 | 1.342 | 4.683 | 8612.58 | 2.228 | 97.8 | 77.7 | 1371 | 23 | 5598.2 | 2885.6 | 2839.3 | 4167.4 | 1195.2 | 0.67552 | 6.026
2024-12-09 | 17:03 | Data | 0 | 32.494 | 30.415 | 186.991 | 7.64 | 175.6 | 2111.35 | 26 | 45.908 | 6.35 | 1.355 | 4.692 | 8608.06 | 2.079 | 97.8 | 77.6 | 1372 | 22.95 | 5595.2 | 2907.9 | 2844.9 | 4187.3 | 1195.2 | 0.6777 | 6.048
2024-12-09 | 17:03 | Data | 0 | 32.399 | 30.415 | 186.991 | 7.65 | 175.555 | 2110.45 | 26.01 | 45.998 | 6.35 | 1.346 | 4.674 | 8458.83 | 1.911 | 97.8 | 77.6 | 1373 | 23 | 5498.2 | 2890.7 | 2835.3 | 4161.6 | 1195.2 | 0.6784 | 6.02
2024-12-09 | 17:03 | Data | 0 | 32.737 | 30.766 | 187.036 | 7.65 | 175.781 | 2111.35 | 26 | 45.998 | 6.35 | 1.345 | 4.673 | 8431.69 | 1.904 | 97.8 | 77.7 | 1372 | 22.95 | 5480.6 | 2883.1 | 2825.3 | 4152.2 | 1195.2 | 0.67773 | 6.019
2024-12-09 | 17:03 | Data | 0 | 32.467 | 30.428 | 186.991 | 7.64 | 175.736 | 2111.35 | 25.99 | 45.998 | 6.35 | 1.348 | 4.673 | 8427.17 | 2.268 | 97.8 | 77.6 | 1372 | 23 | 5477.7 | 2863.8 | 2798.5 | 4122.2 | 1195.2 | 0.67716 | 6.02
2024-12-09 | 17:03 | Data | 0 | 32.507 | 30.421 | 187.082 | 7.65 | 175.69 | 2110.45 | 26 | 45.998 | 6.34 | 1.354 | 4.683 | 8440.74 | 2.052 | 97.8 | 77.6 | 1372 | 23 | 5486.5 | 2880.6 | 2798.6 | 4151 | 1195.2 | 0.67966 | 6.036
2024-12-09 | 17:03 | Data | 0 | 32.885 | 30.928 | 187.127 | 7.64 | 175.736 | 2116.78 | 26 | 45.908 | 6.35 | 1.348 | 4.683 | 8440.74 | 2.14 | 97.8 | 77.6 | 1376 | 23 | 5486.5 | 2916.2 | 2795.6 | 4158.3 | 1195.2 | 0.68398 | 6.03
2024-12-09 | 17:03 | Data | 0 | 32.494 | 30.651 | 187.036 | 7.64 | 175.69 | 2119.49 | 26.01 | 45.998 | 6.35 | 1.342 | 4.689 | 8436.21 | 2.025 | 97.8 | 77.7 | 1378 | 23 | 5483.5 | 2890 | 2816.8 | 4152.1 | 1195.2 | 0.68088 | 6.031
2024-12-09 | 17:03 | Data | 0 | 32.669 | 30.705 | 187.082 | 7.64 | 175.736 | 2123.1 | 26 | 45.998 | 6.34 | 1.349 | 4.689 | 8422.65 | 2.133 | 97.8 | 77.7 | 1380 | 22.95 | 5474.7 | 2894.2 | 2783.4 | 4131 | 1195.2 | 0.68415 | 6.038
2024-12-09 | 17:03 | Data | 0 | 32.548 | 30.658 | 187.127 | 7.64 | 175.781 | 2119.49 | 26.01 | 45.908 | 6.34 | 1.358 | 4.69 | 8422.65 | 2.032 | 97.8 | 77.6 | 1378 | 23 | 5474.7 | 2906.1 | 2827 | 4173 | 1195.2 | 0.67897 | 6.046
2024-12-09 | 17:03 | Data | 0 | 32.609 | 30.651 | 186.946 | 7.64 | 175.736 | 2123.1 | 26 | 45.998 | 6.34 | 1.346 | 4.67 | 8427.17 | 1.897 | 97.8 | 77.6 | 1380 | 23 | 5477.7 | 2900.6 | 2802.2 | 4149.3 | 1195.2 | 0.68145 | 6.017
2024-12-09 | 17:04 | Data | 0 | 32.967 | 30.536 | 186.991 | 7.64 | 175.781 | 2123.1 | 26 | 45.998 | 6.35 | 1.351 | 4.664 | 8449.78 | 1.965 | 97.8 | 77.5 | 1380 | 23 | 5492.4 | 2904.4 | 2838.8 | 4175.2 | 1195.2 | 0.67921 | 6.016
2024-12-09 | 17:04 | Data | 0 | 32.94 | 30.658 | 187.172 | 7.64 | 175.736 | 2122.2 | 26.01 | 45.998 | 6.35 | 1.355 | 4.666 | 8454.3 | 1.971 | 97.8 | 77.5 | 1380 | 23.04 | 5495.3 | 2903.5 | 2825.6 | 4173.8 | 1195.2 | 0.67785 | 6.021
2024-12-09 | 17:04 | Data | 0 | 32.723 | 30.597 | 186.991 | 7.64 | 175.6 | 2123.1 | 26 | 45.998 | 6.35 | 1.349 | 4.673 | 8449.78 | 2.181 | 97.8 | 77.6 | 1380 | 22.95 | 5492.4 | 2907 | 2842.6 | 4180.9 | 1195.2 | 0.68092 | 6.023
2024-12-09 | 17:04 | Data | 0 | 32.669 | 30.874 | 187.217 | 7.65 | 175.736 | 2122.2 | 26 | 45.998 | 6.34 | 1.348 | 4.665 | 8427.17 | 2.167 | 97.8 | 77.6 | 1380 | 23 | 5477.7 | 2907 | 2797.2 | 4151.5 | 1195.2 | 0.68201 | 6.013
2024-12-09 | 17:04 | Data | 0 | 32.669 | 30.543 | 186.991 | 7.64 | 175.69 | 2117.68 | 26 | 45.998 | 6.35 | 1.346 | 4.694 | 8210.1 | 2.208 | 97.8 | 77.7 | 1376 | 22.95 | 5336.6 | 2911.4 | 2815.2 | 4170.9 | 1195.2 | 0.68057 | 6.039
2024-12-09 | 17:04 | Data | 0 | 33.061 | 30.813 | 187.172 | 7.64 | 175.781 | 2123.1 | 26.01 | 45.908 | 6.35 | 1.343 | 4.664 | 8142.27 | 2.052 | 97.8 | 77.6 | 1380 | 23 | 5292.5 | 2890.2 | 2814.1 | 4156.3 | 1195.2 | 0.67957 | 6.007
2024-12-09 | 17:04 | Data | 0 | 32.717 | 30.442 | 186.901 | 7.65 | 175.736 | 2123.1 | 26 | 45.908 | 6.34 | 1.348 | 4.659 | 8381.95 | 2.073 | 97.8 | 77.6 | 1380 | 22.95 | 5448.3 | 2902.3 | 2835.3 | 4171 | 1195.2 | 0.68238 | 6.007
2024-12-09 | 17:04 | Data | 0 | 32.494 | 30.59 | 186.991 | 7.64 | 175.69 | 2123.1 | 26 | 45.998 | 6.35 | 1.345 | 4.676 | 8395.51 | 2.255 | 97.8 | 77.7 | 1380 | 23 | 5457.1 | 2914.5 | 2806.7 | 4162.2 | 1195.2 | 0.68452 | 6.021
2024-12-09 | 17:04 | Data | 0 | 32.946 | 30.988 | 187.036 | 7.64 | 175.781 | 2124.91 | 26 | 46.089 | 6.34 | 1.343 | 4.671 | 8440.74 | 1.863 | 97.8 | 77.7 | 1381 | 22.95 | 5486.5 | 2899.5 | 2812 | 4157 | 1195.2 | 0.68298 | 6.016
2024-12-09 | 17:04 | Data | 0 | 32.622 | 30.428 | 186.946 | 7.64 | 175.736 | 2125.81 | 26 | 46.089 | 6.35 | 1.347 | 4.681 | 8436.21 | 2.066 | 97.8 | 77.7 | 1382 | 23 | 5483.5 | 2885.3 | 2821.7 | 4154.3 | 1195.2 | 0.6801 | 6.027
2024-12-09 | 17:04 | Data | 0 | 32.723 | 30.543 | 186.991 | 7.64 | 175.69 | 2125.81 | 26 | 45.998 | 6.34 | 1.359 | 4.686 | 8431.69 | 2.167 | 97.8 | 77.5 | 1382 | 23 | 5480.6 | 2883.3 | 2823 | 4157.3 | 1195.2 | 0.679 | 6.045
2024-12-09 | 17:04 | Data | 0 | 32.69 | 30.651 | 186.991 | 7.64 | 175.736 | 2120.39 | 26.01 | 45.998 | 6.35 | 1.351 | 4.684 | 8427.17 | 2.059 | 97.8 | 77.6 | 1378 | 23 | 5477.7 | 2871.4 | 2802.5 | 4135.5 | 1195.2 | 0.678 | 6.036
2024-12-09 | 17:04 | Data | 0 | 32.858 | 30.435 | 186.991 | 7.64 | 175.736 | 2125.81 | 26 | 45.908 | 6.35 | 1.357 | 4.674 | 8418.13 | 2.066 | 97.8 | 77.5 | 1382 | 22.95 | 5471.8 | 2903.3 | 2806.2 | 4159.3 | 1195.2 | 0.68068 | 6.031
2024-12-09 | 17:04 | Data | 0 | 33.048 | 30.691 | 187.127 | 7.64 | 175.826 | 2124.91 | 26 | 45.998 | 6.35 | 1.354 | 4.677 | 8418.13 | 1.985 | 97.8 | 77.6 | 1381 | 23 | 5471.8 | 2916.5 | 2807.2 | 4166.1 | 1195.2 | 0.68293 | 6.031
2024-12-09 | 17:04 | Data | 0 | 32.946 | 30.604 | 187.036 | 7.64 | 175.736 | 2125.81 | 26 | 45.908 | 6.35 | 1.342 | 4.702 | 8404.56 | 2.032 | 97.8 | 77.8 | 1382 | 22.95 | 5463 | 2891.5 | 2795.6 | 4143.4 | 1195.2 | 0.67891 | 6.045
2024-12-09 | 17:04 | Data | 0 | 32.636 | 30.786 | 187.036 | 7.64 | 175.826 | 2125.81 | 25.99 | 45.998 | 6.35 | 1.342 | 4.669 | 8436.21 | 2.073 | 97.8 | 77.7 | 1382 | 23 | 5483.5 | 2903.6 | 2804.2 | 4156.5 | 1195.2 | 0.67784 | 6.012
2024-12-09 | 17:04 | Data | 0 | 32.494 | 30.671 | 186.946 | 7.64 | 175.69 | 2123.1 | 26 | 45.998 | 6.35 | 1.344 | 4.659 | 8440.74 | 1.917 | 97.8 | 77.6 | 1380 | 23 | 5486.5 | 2894.9 | 2787.7 | 4138.9 | 1195.2 | 0.67988 | 6.003
2024-12-09 | 17:04 | Data | 0 | 32.494 | 30.529 | 187.082 | 7.64 | 175.736 | 2123.1 | 25.98 | 45.998 | 6.35 | 1.348 | 4.679 | 8436.21 | 2.019 | 97.8 | 77.6 | 1380 | 22.95 | 5483.5 | 2921.1 | 2815.8 | 4171.9 | 1195.2 | 0.684 | 6.026
2024-12-09 | 17:05 | Data | 0 | 32.528 | 30.651 | 187.036 | 7.64 | 175.736 | 2123.1 | 26.01 | 45.908 | 6.35 | 1.342 | 4.686 | 8427.17 | 2.046 | 97.8 | 77.7 | 1379 | 23 | 5477.7 | 2922.7 | 2820.3 | 4176.4 | 1195.2 | 0.68301 | 6.027
2024-12-09 | 17:05 | Data | 0 | 32.723 | 30.543 | 187.036 | 7.64 | 175.69 | 2123.1 | 26 | 45.998 | 6.35 | 1.343 | 4.695 | 8427.17 | 2.181 | 97.8 | 77.7 | 1380 | 22.95 | 5477.7 | 2938.6 | 2822.4 | 4189.1 | 1195.2 | 0.68392 | 6.039
2024-12-09 | 17:05 | Data | 0 | 32.636 | 30.651 | 186.991 | 7.64 | 175.736 | 2123.1 | 26 | 45.908 | 6.35 | 1.353 | 4.732 | 8404.56 | 1.863 | 97.8 | 77.8 | 1380 | 23 | 5463 | 2931.2 | 2812.1 | 4174.5 | 1195.2 | 0.68479 | 6.085
2024-12-09 | 17:05 | Data | 0 | 32.501 | 30.651 | 186.991 | 7.65 | 175.781 | 2124.01 | 26 | 45.998 | 6.35 | 1.347 | 4.685 | 8422.65 | 2.046 | 97.8 | 77.7 | 1380 | 22.95 | 5474.7 | 2901.5 | 2794.9 | 4150.9 | 1195.2 | 0.68071 | 6.032
2024-12-09 | 17:05 | Data | 0 | 32.825 | 30.88 | 187.082 | 7.64 | 175.781 | 2123.1 | 25.99 | 45.998 | 6.35 | 1.347 | 4.69 | 8431.69 | 2.039 | 97.8 | 77.7 | 1380 | 23 | 5480.6 | 2921.2 | 2781.8 | 4154.9 | 1195.2 | 0.68362 | 6.036
2024-12-09 | 17:05 | Data | 0 | 32.501 | 30.536 | 187.036 | 7.65 | 175.69 | 2123.1 | 25.99 | 45.998 | 6.35 | 1.342 | 4.677 | 8427.17 | 2.16 | 97.8 | 77.7 | 1380 | 23 | 5477.7 | 2934.7 | 2791.3 | 4172.4 | 1195.3 | 0.6853 | 6.018
2024-12-09 | 17:05 | Data | 0 | 32.696 | 30.732 | 186.991 | 7.64 | 175.6 | 2123.1 | 26.01 | 45.998 | 6.35 | 1.339 | 4.667 | 8445.26 | 1.985 | 97.8 | 77.7 | 1379 | 22.95 | 5489.4 | 2898.5 | 2805.4 | 4160.4 | 1195.3 | 0.68016 | 6.007
2024-12-09 | 17:05 | Data | 0 | 32.669 | 30.853 | 187.036 | 7.64 | 175.69 | 2122.2 | 26 | 46.45 | 6.35 | 1.342 | 4.668 | 8445.26 | 2.066 | 97.8 | 77.7 | 1379 | 23.22 | 5489.4 | 2934.4 | 2819 | 4187.2 | 1195.3 | 0.68648 | 6.01
2024-12-09 | 17:05 | Data | 0 | 32.514 | 30.651 | 186.991 | 7.64 | 175.736 | 2123.1 | 26.01 | 45.998 | 6.35 | 1.337 | 4.667 | 8431.69 | 1.958 | 97.8 | 77.7 | 1379 | 23.04 | 5480.6 | 2925.8 | 2815.8 | 4174.8 | 1195.3 | 0.68331 | 6.004
2024-12-09 | 17:05 | Data | 0 | 32.825 | 30.428 | 186.991 | 7.64 | 175.826 | 2125.81 | 25.99 | 45.908 | 6.35 | 1.338 | 4.691 | 8431.69 | 2.174 | 97.8 | 77.8 | 1382 | 23 | 5480.6 | 2930.8 | 2790.3 | 4172.2 | 1195.3 | 0.6862 | 6.028
2024-12-09 | 17:05 | Data | 0 | 32.717 | 30.928 | 187.127 | 7.64 | 175.736 | 2123.1 | 26 | 45.908 | 6.35 | 1.339 | 4.682 | 8431.69 | 2.12 | 97.8 | 77.8 | 1379 | 23 | 5480.6 | 2920.4 | 2787.2 | 4153.6 | 1195.3 | 0.68623 | 6.02
2024-12-09 | 17:05 | Data | 0 | 33.142 | 30.509 | 187.082 | 7.64 | 175.736 | 2118.58 | 26 | 45.908 | 6.35 | 1.338 | 4.676 | 8440.74 | 2.262 | 97.8 | 77.8 | 1377 | 23 | 5486.5 | 2905.1 | 2811 | 4165.1 | 1195.3 | 0.68194 | 6.013
2024-12-09 | 17:05 | Data | 0 | 32.926 | 30.563 | 187.172 | 7.64 | 175.736 | 2121.29 | 26 | 45.908 | 6.35 | 1.352 | 4.7 | 8431.69 | 2.066 | 97.8 | 77.7 | 1379 | 22.95 | 5480.6 | 2944.4 | 2784.5 | 4175.3 | 1195.3 | 0.68881 | 6.05
2024-12-09 | 17:05 | Data | 0 | 32.312 | 30.421 | 186.946 | 7.64 | 175.736 | 2123.1 | 25.99 | 45.998 | 6.35 | 1.344 | 4.69 | 8418.13 | 1.87 | 97.8 | 77.7 | 1379 | 22.95 | 5471.8 | 2923.1 | 2779 | 4155.5 | 1195.3 | 0.68578 | 6.034
2024-12-09 | 17:05 | Data | 0 | 32.723 | 30.651 | 186.991 | 7.64 | 175.736 | 2123.1 | 26 | 45.908 | 6.35 | 1.34 | 4.683 | 8445.26 | 1.87 | 97.8 | 77.7 | 1379 | 23 | 5489.4 | 2933 | 2792.8 | 4168.1 | 1195.3 | 0.6853 | 6.024
2024-12-09 | 17:05 | Data | 0 | 32.811 | 30.644 | 186.991 | 7.64 | 175.69 | 2123.1 | 25.99 | 45.998 | 6.35 | 1.342 | 4.669 | 8427.17 | 2.275 | 97.8 | 77.7 | 1380 | 23 | 5477.7 | 2940 | 2784.5 | 4170.1 | 1195.3 | 0.68711 | 6.011
2024-12-09 | 17:06 | Data | 0 | 32.98 | 30.975 | 187.036 | 7.64 | 175.781 | 2123.1 | 26 | 46.089 | 6.35 | 1.343 | 4.663 | 8418.13 | 2.181 | 97.8 | 77.6 | 1380 | 23 | 5471.8 | 2923.8 | 2785.8 | 4160.8 | 1195.3 | 0.68557 | 6.007
2024-12-09 | 17:06 | Data | 0 | 32.386 | 30.624 | 186.991 | 7.64 | 175.69 | 2124.01 | 26 | 45.908 | 6.35 | 1.348 | 4.669 | 8418.13 | 1.877 | 97.8 | 77.6 | 1380 | 23 | 5471.8 | 2924.9 | 2793.8 | 4166 | 1195.3 | 0.68504 | 6.017
2024-12-09 | 17:06 | Data | 0 | 32.73 | 30.853 | 187.172 | 7.64 | 175.781 | 2124.91 | 26.01 | 45.998 | 6.35 | 1.339 | 4.671 | 8400.04 | 1.958 | 97.8 | 77.7 | 1381 | 23 | 5460 | 2934.2 | 2785.6 | 4165.5 | 1195.3 | 0.68851 | 6.01
2024-12-09 | 17:06 | Data | 0 | 32.723 | 30.651 | 187.036 | 7.64 | 175.826 | 2125.81 | 25.99 | 45.998 | 6.35 | 1.347 | 4.668 | 8427.17 | 1.87 | 97.8 | 77.6 | 1382 | 22.95 | 5477.7 | 2933.6 | 2805.6 | 4178.5 | 1195.3 | 0.68537 | 6.016
2024-12-09 | 17:06 | Data | 0 | 32.494 | 30.739 | 186.901 | 7.64 | 175.69 | 2126.72 | 26 | 45.998 | 6.35 | 1.352 | 4.65 | 8409.08 | 1.958 | 97.8 | 77.5 | 1382 | 23 | 5465.9 | 2952.2 | 2853.9 | 4224.5 | 1195.3 | 0.68335 | 6.001
2024-12-09 | 17:06 | Data | 0 | 32.994 | 30.894 | 187.082 | 7.65 | 175.736 | 2126.72 | 26 | 45.998 | 6.35 | 1.352 | 4.673 | 8418.13 | 2.248 | 97.8 | 77.6 | 1382 | 23 | 5471.8 | 2920.5 | 2822.3 | 4181.4 | 1195.3 | 0.68141 | 6.026
2024-12-09 | 17:06 | Data | 0 | 32.494 | 30.475 | 186.901 | 7.64 | 175.555 | 2125.81 | 26 | 45.998 | 6.35 | 1.348 | 4.685 | 8390.99 | 2.066 | 97.8 | 77.6 | 1382 | 23 | 5454.1 | 2913.5 | 2814.1 | 4173 | 1195.3 | 0.67916 | 6.036
2024-12-09 | 17:06 | Data | 0 | 32.541 | 30.55 | 187.036 | 7.65 | 175.69 | 2124.91 | 26.01 | 45.998 | 6.35 | 1.349 | 4.71 | 8372.9 | 2.039 | 97.8 | 77.7 | 1381 | 23 | 5442.4 | 2931.4 | 2837 | 4200.7 | 1195.3 | 0.68045 | 6.058
2024-12-09 | 17:06 | Data | 0 | 32.723 | 30.766 | 186.901 | 7.64 | 175.69 | 2125.81 | 25.99 | 45.998 | 6.35 | 1.356 | 4.684 | 8395.51 | 2.073 | 97.8 | 77.6 | 1382 | 22.95 | 5457.1 | 2936.1 | 2810.5 | 4183.3 | 1195.3 | 0.68382 | 6.04
2024-12-09 | 17:06 | Data | 0 | 32.723 | 30.847 | 187.172 | 7.64 | 175.6 | 2124.91 | 26.01 | 45.998 | 6.35 | 1.351 | 4.7 | 8400.04 | 1.904 | 97.8 | 77.7 | 1381 | 23 | 5460 | 2941.3 | 2813.9 | 4190.5 | 1195.3 | 0.68567 | 6.051
2024-12-09 | 17:06 | Data | 0 | 32.777 | 30.637 | 187.082 | 7.64 | 175.781 | 2124.91 | 26 | 46.089 | 6.35 | 1.345 | 4.705 | 8404.56 | 1.917 | 97.8 | 77.8 | 1382 | 23 | 5463 | 2859.8 | 2780.7 | 4107.2 | 1195.3 | 0.68129 | 6.047
2024-12-09 | 17:06 | Data | 0 | 32.622 | 30.597 | 187.036 | 7.64 | 175.736 | 2125.81 | 26 | 46.089 | 6.35 | 1.348 | 4.702 | 8400.04 | 2.086 | 97.8 | 77.7 | 1382 | 23.04 | 5460 | 2856.3 | 2723.7 | 4063.3 | 1195.3 | 0.69014 | 6.05
2024-12-09 | 17:06 | Data | 0 | 32.885 | 30.718 | 186.946 | 7.64 | 175.736 | 2128.52 | 26 | 45.998 | 6.35 | 1.346 | 4.679 | 8427.17 | 2.073 | 97.8 | 77.7 | 1382 | 23 | 5477.7 | 2870.8 | 2826.7 | 4143.1 | 1195.3 | 0.67551 | 6.023
2024-12-09 | 17:06 | Data | 0 | 32.609 | 30.428 | 186.901 | 7.65 | 175.555 | 2125.81 | 26 | 45.998 | 6.35 | 1.349 | 4.692 | 8427.17 | 2.235 | 97.8 | 77.7 | 1382 | 23 | 5477.7 | 2852 | 2803.4 | 4113 | 1195.3 | 0.67872 | 6.041
2024-12-09 | 17:06 | Data | 0 | 32.69 | 30.651 | 186.946 | 7.64 | 175.736 | 2124.91 | 26.01 | 45.998 | 6.34 | 1.349 | 4.637 | 8422.65 | 1.958 | 97.8 | 77.5 | 1381 | 23 | 5474.7 | 2865.9 | 2810.6 | 4122.8 | 1195.3 | 0.67993 | 5.987
2024-12-09 | 17:06 | Data | 0 | 32.669 | 30.82 | 187.082 | 7.64 | 175.6 | 2124.91 | 26 | 45.998 | 6.34 | 1.353 | 4.645 | 8431.69 | 2.046 | 97.8 | 77.4 | 1381 | 23 | 5480.6 | 2848.3 | 2801.3 | 4111 | 1195.3 | 0.67615 | 5.998
2024-12-09 | 17:06 | Data | 0 | 32.879 | 30.651 | 186.946 | 7.64 | 175.781 | 2125.81 | 25.99 | 45.908 | 6.35 | 1.341 | 4.664 | 8422.65 | 2.167 | 97.8 | 77.7 | 1382 | 22.95 | 5474.7 | 2873.7 | 2799.6 | 4125 | 1195.3 | 0.6803 | 6.005
2024-12-09 | 17:06 | Data | 0 | 32.494 | 30.691 | 186.946 | 7.64 | 175.6 | 2124.91 | 25.99 | 45.998 | 6.35 | 1.353 | 4.662 | 8418.13 | 1.904 | 97.8 | 77.5 | 1382 | 23 | 5471.8 | 2838.9 | 2798.9 | 4107 | 1195.3 | 0.67581 | 6.017
2024-12-09 | 17:07 | Data | 0 | 32.548 | 30.651 | 186.946 | 7.64 | 175.69 | 2130.33 | 26 | 45.998 | 6.35 | 1.356 | 4.666 | 8418.13 | 1.85 | 97.8 | 77.5 | 1385 | 22.95 | 5471.8 | 2924.6 | 2824.2 | 4186.4 | 1195.3 | 0.68266 | 6.022
2024-12-09 | 17:07 | Data | 0 | 32.494 | 30.442 | 186.901 | 7.64 | 175.6 | 2127.62 | 26.01 | 45.908 | 6.35 | 1.341 | 4.657 | 8409.08 | 2.093 | 97.8 | 77.6 | 1383 | 23 | 5465.9 | 2922.6 | 2807 | 4168.5 | 1195.3 | 0.68337 | 5.998
2024-12-09 | 17:07 | Data | 0 | 32.636 | 30.651 | 187.036 | 7.64 | 175.781 | 2134.85 | 26 | 45.908 | 6.34 | 1.337 | 4.672 | 8418.13 | 1.863 | 97.9 | 77.8 | 1387 | 22.95 | 5471.8 | 2913.4 | 2794.7 | 4158.8 | 1195.3 | 0.68297 | 6.007
2024-12-09 | 17:07 | Data | 0 | 32.609 | 30.583 | 186.991 | 7.64 | 175.736 | 2128.52 | 25.99 | 45.998 | 6.35 | 1.342 | 4.672 | 8418.13 | 1.836 | 97.8 | 77.7 | 1382 | 23 | 5471.8 | 2919.8 | 2822.3 | 4181 | 1195.3 | 0.68271 | 6.011
2024-12-09 | 17:07 | Data | 0 | 32.501 | 30.421 | 186.901 | 7.65 | 175.736 | 2127.62 | 25.99 | 45.908 | 6.35 | 1.337 | 4.671 | 8404.56 | 2.073 | 97.8 | 77.7 | 1384 | 22.95 | 5463 | 2898.9 | 2816.1 | 4157.6 | 1195.3 | 0.68294 | 6.007
2024-12-09 | 17:07 | Data | 0 | 32.683 | 30.867 | 187.082 | 7.64 | 175.6 | 2127.62 | 25.98 | 46.089 | 6.35 | 1.336 | 4.679 | 8418.13 | 2.1 | 97.8 | 77.8 | 1383 | 23.04 | 5471.8 | 2906 | 2800.9 | 4156.3 | 1195.3 | 0.68317 | 6.013
2024-12-09 | 17:07 | Data | 0 | 32.379 | 30.739 | 186.901 | 7.64 | 175.69 | 2125.81 | 25.99 | 45.998 | 6.35 | 1.339 | 4.655 | 8418.13 | 2.174 | 97.8 | 77.7 | 1382 | 23 | 5471.8 | 2910.6 | 2806 | 4164.5 | 1195.4 | 0.68242 | 5.995
2024-12-09 | 17:07 | Data | 0 | 32.609 | 30.415 | 186.72 | 7.64 | 175.51 | 2127.62 | 25.99 | 45.998 | 6.35 | 1.347 | 4.649 | 8400.04 | 2.167 | 97.8 | 77.5 | 1383 | 23 | 5460 | 2929.9 | 2817 | 4182 | 1195.4 | 0.68386 | 5.996
2024-12-09 | 17:07 | Data | 0 | 32.669 | 30.428 | 186.946 | 7.64 | 175.69 | 2121.29 | 25.99 | 45.998 | 6.35 | 1.34 | 4.658 | 8400.04 | 1.978 | 97.8 | 77.7 | 1378 | 23 | 5460 | 2918.9 | 2838.9 | 4192 | 1195.4 | 0.67798 | 5.998
2024-12-09 | 17:07 | Data | 0 | 32.528 | 30.421 | 186.901 | 7.64 | 175.6 | 2127.62 | 25.99 | 45.908 | 6.35 | 1.337 | 4.669 | 8400.04 | 2.073 | 97.8 | 77.7 | 1384 | 22.95 | 5460 | 2906.7 | 2814.7 | 4166.4 | 1195.4 | 0.67964 | 6.007
2024-12-09 | 17:07 | Data | 0 | 32.609 | 30.651 | 186.991 | 7.64 | 175.69 | 2128.52 | 25.99 | 45.998 | 6.35 | 1.344 | 4.665 | 8400.04 | 2.059 | 97.8 | 77.6 | 1384 | 22.95 | 5460 | 2901.6 | 2813.8 | 4165.2 | 1195.4 | 0.68229 | 6.009
2024-12-09 | 17:07 | Data | 0 | 32.325 | 30.415 | 186.855 | 7.64 | 175.51 | 2128.52 | 25.99 | 45.998 | 6.35 | 1.346 | 4.664 | 8454.3 | 2.032 | 97.8 | 77.6 | 1384 | 22.95 | 5495.3 | 2899.5 | 2826.1 | 4171.1 | 1195.4 | 0.67813 | 6.008
2024-12-09 | 17:07 | Data | 0 | 32.73 | 30.712 | 186.991 | 7.64 | 175.69 | 2129.43 | 25.99 | 45.998 | 6.35 | 1.343 | 4.664 | 8454.3 | 1.958 | 97.8 | 77.6 | 1384 | 23 | 5495.3 | 2935.9 | 2809.1 | 4178.7 | 1195.4 | 0.68559 | 6.007
2024-12-09 | 17:07 | Data | 0 | 32.669 | 30.489 | 186.991 | 7.64 | 175.736 | 2127.62 | 25.99 | 45.998 | 6.34 | 1.354 | 4.641 | 8440.74 | 2.221 | 97.8 | 77.4 | 1384 | 23 | 5486.5 | 2890.9 | 2827 | 4166.8 | 1195.4 | 0.67633 | 5.995
2024-12-09 | 17:07 | Data | 0 | 32.494 | 30.415 | 186.901 | 7.64 | 175.555 | 2128.52 | 25.99 | 46.54 | 6.35 | 1.348 | 4.67 | 8440.74 | 2.066 | 97.8 | 77.6 | 1384 | 23.22 | 5486.5 | 2903.9 | 2836.9 | 4180.2 | 1195.4 | 0.67863 | 6.018
2024-12-09 | 17:08 | Data | 0 | 32.663 | 30.529 | 186.901 | 7.64 | 175.555 | 2130.33 | 25.98 | 45.908 | 6.35 | 1.348 | 4.676 | 8472.39 | 2.059 | 97.8 | 77.6 | 1385 | 23 | 5507.1 | 2909.6 | 2863.3 | 4199 | 1195.4 | 0.67502 | 6.024
2024-12-09 | 17:08 | Data | 0 | 32.325 | 30.408 | 186.855 | 7.64 | 175.51 | 2130.33 | 25.98 | 45.998 | 6.35 | 1.348 | 4.672 | 8427.17 | 1.87 | 97.8 | 77.6 | 1385 | 23.04 | 5477.7 | 2896.8 | 2854.2 | 4184.3 | 1195.4 | 0.67493 | 6.019
2024-12-09 | 17:08 | Data | 0 | 32.487 | 30.428 | 186.81 | 7.64 | 175.555 | 2130.33 | 25.98 | 45.998 | 6.35 | 1.348 | 4.66 | 8445.26 | 2.025 | 97.8 | 77.6 | 1385 | 23 | 5489.4 | 2896.5 | 2850.9 | 4181.1 | 1195.4 | 0.67545 | 6.007
2024-12-09 | 17:08 | Data | 0 | 32.548 | 30.847 | 186.991 | 7.64 | 175.6 | 2120.39 | 25.99 | 45.998 | 6.35 | 1.349 | 4.667 | 8458.83 | 1.911 | 97.8 | 77.6 | 1379 | 22.95 | 5498.2 | 2888.9 | 2868.8 | 4186.6 | 1195.4 | 0.6734 | 6.017
2024-12-09 | 17:08 | Data | 0 | 32.312 | 30.394 | 187.036 | 7.64 | 175.555 | 2120.39 | 25.99 | 45.818 | 6.35 | 1.348 | 4.665 | 8440.74 | 1.897 | 97.8 | 77.6 | 1378 | 22.91 | 5486.5 | 2891 | 2823.3 | 4156.8 | 1195.4 | 0.67748 | 6.014
2024-12-09 | 17:08 | Data | 0 | 32.71 | 30.415 | 186.946 | 7.64 | 175.69 | 2120.39 | 26 | 45.998 | 6.35 | 1.347 | 4.677 | 8427.17 | 2.127 | 97.8 | 77.6 | 1378 | 23 | 5477.7 | 2880.5 | 2827.7 | 4159.9 | 1195.4 | 0.6762 | 6.024
2024-12-09 | 17:08 | Data | 0 | 32.339 | 30.246 | 186.901 | 7.64 | 175.6 | 2120.39 | 26 | 46.089 | 6.35 | 1.339 | 4.647 | 8400.04 | 1.971 | 97.8 | 77.6 | 1378 | 23 | 5460 | 2908.4 | 2822.3 | 4164.6 | 1195.4 | 0.68181 | 5.988
2024-12-09 | 17:08 | Data | 0 | 32.669 | 30.442 | 186.946 | 7.64 | 175.6 | 2123.1 | 26 | 45.998 | 6.34 | 1.346 | 4.689 | 8440.74 | 2.019 | 97.8 | 77.7 | 1380 | 23 | 5486.5 | 2900.7 | 2818.1 | 4159.2 | 1195.4 | 0.68105 | 6.036
2024-12-09 | 17:08 | Data | 0 | 32.717 | 30.651 | 187.036 | 7.64 | 175.6 | 2122.2 | 26 | 45.998 | 6.35 | 1.33 | 4.7 | 8440.74 | 2.073 | 97.8 | 77.9 | 1379 | 23 | 5486.5 | 2893.4 | 2835.5 | 4172.8 | 1195.4 | 0.676 | 6.03
2024-12-09 | 17:08 | Data | 0 | 32.717 | 30.421 | 186.901 | 7.64 | 175.6 | 2123.1 | 26 | 45.998 | 6.35 | 1.344 | 4.664 | 8463.35 | 2.127 | 97.8 | 77.6 | 1380 | 22.95 | 5501.2 | 2913.1 | 2822.4 | 4171.6 | 1195.4 | 0.68163 | 6.007
2024-12-09 | 17:08 | Data | 0 | 32.318 | 30.415 | 186.855 | 7.64 | 175.464 | 2123.1 | 26 | 45.908 | 6.35 | 1.351 | 4.673 | 8463.35 | 2.059 | 97.8 | 77.6 | 1380 | 22.95 | 5501.2 | 2897.6 | 2834.6 | 4178.5 | 1195.4 | 0.67773 | 6.025
2024-12-09 | 17:08 | Data | 0 | 32.21 | 30.408 | 186.855 | 7.64 | 175.555 | 2123.1 | 26.01 | 45.998 | 6.35 | 1.34 | 4.675 | 8472.39 | 2.025 | 97.8 | 77.7 | 1380 | 23 | 5507.1 | 2908.3 | 2836.6 | 4177.7 | 1195.4 | 0.67859 | 6.016
2024-12-09 | 17:08 | Data | 0 | 32.717 | 30.442 | 186.855 | 7.64 | 175.69 | 2123.1 | 26 | 45.998 | 6.35 | 1.34 | 4.665 | 8467.87 | 2.106 | 97.8 | 77.7 | 1380 | 23 | 5504.1 | 2896 | 2835.9 | 4175.2 | 1195.4 | 0.67677 | 6.007
2024-12-09 | 17:08 | Data | 0 | 32.494 | 30.523 | 186.855 | 7.64 | 175.555 | 2122.2 | 26 | 45.908 | 6.35 | 1.346 | 4.677 | 8436.21 | 1.971 | 97.8 | 77.7 | 1380 | 23 | 5483.5 | 2892.8 | 2851.7 | 4181.1 | 1195.4 | 0.67404 | 6.023
2024-12-09 | 17:08 | Data | 0 | 32.723 | 30.475 | 186.946 | 7.64 | 175.826 | 2123.1 | 26.01 | 45.908 | 6.35 | 1.352 | 4.691 | 8436.21 | 2.073 | 97.8 | 77.6 | 1380 | 22.95 | 5483.5 | 2903.6 | 2842 | 4183.2 | 1195.4 | 0.67802 | 6.043
2024-12-09 | 17:08 | Data | 0 | 32.717 | 30.421 | 186.901 | 7.64 | 175.6 | 2122.2 | 26 | 45.998 | 6.35 | 1.351 | 4.689 | 8427.17 | 2.174 | 97.8 | 77.7 | 1379 | 23.04 | 5477.7 | 2911.5 | 2819.2 | 4166.6 | 1195.4 | 0.68208 | 6.038
2024-12-09 | 17:08 | Data | 0 | 32.453 | 30.86 | 186.901 | 7.64 | 175.69 | 2124.91 | 26 | 45.908 | 6.35 | 1.354 | 4.663 | 8440.74 | 2.019 | 97.8 | 77.5 | 1382 | 23 | 5486.5 | 2906.7 | 2791.8 | 4146.2 | 1195.4 | 0.68469 | 6.016
2024-12-09 | 17:08 | Data | 0 | 32.494 | 30.644 | 186.946 | 7.65 | 175.736 | 2126.72 | 26 | 45.998 | 6.35 | 1.345 | 4.672 | 8458.83 | 1.85 | 97.8 | 77.7 | 1381 | 23 | 5498.2 | 2880.9 | 2816.1 | 4149.6 | 1195.4 | 0.67963 | 6.016
2024-12-09 | 17:09 | Data | 0 | 32.771 | 30.421 | 187.036 | 7.64 | 175.555 | 2125.81 | 26.01 | 45.998 | 6.35 | 1.351 | 4.651 | 8481.44 | 1.985 | 97.8 | 77.5 | 1382 | 23 | 5512.9 | 2882.2 | 2825.4 | 4157.5 | 1195.4 | 0.68177 | 6.003
2024-12-09 | 17:09 | Data | 0 | 32.298 | 30.84 | 186.855 | 7.64 | 175.6 | 2125.81 | 26 | 45.908 | 6.35 | 1.353 | 4.646 | 8481.44 | 1.965 | 97.8 | 77.4 | 1382 | 23 | 5512.9 | 2933.8 | 2795.3 | 4167.7 | 1195.4 | 0.68732 | 5.999
2024-12-09 | 17:09 | Data | 0 | 32.494 | 30.536 | 186.901 | 7.64 | 175.6 | 2125.81 | 26.01 | 45.998 | 6.35 | 1.347 | 4.649 | 8463.35 | 2.079 | 97.8 | 77.5 | 1381 | 23 | 5501.2 | 2906 | 2806.3 | 4152 | 1195.4 | 0.68053 | 5.996
2024-12-09 | 17:09 | Data | 0 | 32.831 | 30.475 | 187.036 | 7.65 | 175.69 | 2120.39 | 26.01 | 45.908 | 6.36 | 1.344 | 4.674 | 8458.83 | 1.958 | 97.8 | 77.7 | 1379 | 23 | 5498.2 | 2909 | 2793.2 | 4150.4 | 1195.4 | 0.68314 | 6.017
2024-12-09 | 17:09 | Data | 0 | 32.521 | 30.252 | 186.901 | 7.64 | 175.6 | 2121.29 | 25.99 | 45.908 | 6.35 | 1.344 | 4.699 | 8436.21 | 2.039 | 97.8 | 77.8 | 1379 | 23 | 5483.5 | 2891 | 2841.1 | 4171.8 | 1195.4 | 0.67685 | 6.043
2024-12-09 | 17:09 | Data | 0 | 32.494 | 30.523 | 186.946 | 7.64 | 175.6 | 2122.2 | 26.01 | 45.818 | 6.35 | 1.339 | 4.671 | 8431.69 | 1.857 | 97.8 | 77.7 | 1380 | 22.95 | 5480.6 | 2911 | 2824 | 4171.5 | 1195.4 | 0.6812 | 6.01
2024-12-09 | 17:09 | Data | 0 | 32.609 | 30.847 | 186.81 | 7.64 | 175.555 | 2125.81 | 25.99 | 46.089 | 6.35 | 1.334 | 4.667 | 8436.21 | 1.951 | 97.8 | 77.8 | 1382 | 23 | 5483.5 | 2909.2 | 2818.3 | 4168 | 1195.4 | 0.67992 | 6.001
2024-12-09 | 17:09 | Data | 0 | 32.777 | 30.448 | 186.855 | 7.64 | 175.6 | 2127.62 | 26 | 45.998 | 6.35 | 1.349 | 4.647 | 8431.69 | 2.079 | 97.8 | 77.5 | 1382 | 23 | 5480.6 | 2911.1 | 2827.1 | 4176.7 | 1195.5 | 0.67969 | 5.997
2024-12-09 | 17:09 | Data | 0 | 32.555 | 30.759 | 186.946 | 7.64 | 175.736 | 2125.81 | 26.01 | 45.818 | 6.35 | 1.338 | 4.657 | 8409.08 | 2.167 | 97.8 | 77.7 | 1382 | 22.91 | 5465.9 | 2901 | 2810.2 | 4153.9 | 1195.5 | 0.68137 | 5.994
2024-12-09 | 17:09 | Data | 0 | 32.494 | 30.752 | 186.855 | 7.64 | 175.555 | 2124.91 | 26.01 | 45.998 | 6.35 | 1.338 | 4.693 | 8422.65 | 2.079 | 97.8 | 77.8 | 1381 | 23 | 5474.7 | 2918 | 2806.8 | 4166.8 | 1195.5 | 0.68337 | 6.032
2024-12-09 | 17:09 | Data | 0 | 32.386 | 30.415 | 186.901 | 7.64 | 175.736 | 2124.91 | 26 | 45.998 | 6.35 | 1.345 | 4.687 | 8409.08 | 1.863 | 97.8 | 77.7 | 1381 | 23.04 | 5465.9 | 2890.4 | 2806.2 | 4149.3 | 1195.5 | 0.67968 | 6.032
2024-12-09 | 17:09 | Data | 0 | 32.663 | 30.334 | 186.946 | 7.64 | 175.69 | 2123.1 | 25.99 | 45.998 | 6.35 | 1.341 | 4.671 | 8395.51 | 2.012 | 97.8 | 77.7 | 1380 | 22.95 | 5457.1 | 2906.5 | 2805.6 | 4157.5 | 1195.5 | 0.68319 | 6.011
2024-12-09 | 17:09 | Data | 0 | 32.609 | 30.691 | 186.946 | 7.64 | 175.69 | 2123.1 | 26 | 45.998 | 6.35 | 1.346 | 4.68 | 8404.56 | 2.066 | 97.8 | 77.7 | 1380 | 23 | 5463 | 2889.2 | 2800.8 | 4146.7 | 1195.5 | 0.67986 | 6.026
2024-12-09 | 17:09 | Data | 0 | 32.325 | 30.246 | 187.036 | 7.65 | 175.69 | 2123.1 | 26 | 45.908 | 6.35 | 1.344 | 4.666 | 8418.13 | 1.992 | 97.8 | 77.6 | 1380 | 22.95 | 5471.8 | 2914.7 | 2785.9 | 4139.4 | 1195.5 | 0.68362 | 6.01
2024-12-09 | 17:09 | Data | 0 | 32.494 | 30.415 | 186.946 | 7.65 | 175.6 | 2120.39 | 26.01 | 45.908 | 6.35 | 1.349 | 4.683 | 8418.13 | 2.275 | 97.8 | 77.6 | 1379 | 23 | 5471.8 | 2898.8 | 2809.3 | 4159.6 | 1195.5 | 0.67945 | 6.032
2024-12-09 | 17:09 | Data | 0 | 32.663 | 30.847 | 187.082 | 7.64 | 175.69 | 2122.2 | 26 | 45.908 | 6.36 | 1.351 | 4.677 | 8418.13 | 2.073 | 97.8 | 77.6 | 1380 | 22.91 | 5471.8 | 2902.1 | 2807.6 | 4160.6 | 1195.5 | 0.68085 | 6.028
2024-12-09 | 17:09 | Data | 0 | 32.494 | 30.415 | 186.901 | 7.64 | 175.555 | 2123.1 | 26 | 45.998 | 6.35 | 1.34 | 4.663 | 8445.26 | 2.079 | 97.8 | 77.7 | 1380 | 23 | 5489.4 | 2896.3 | 2826 | 4160.6 | 1195.5 | 0.67938 | 6.003
2024-12-09 | 17:09 | Data | 0 | 32.723 | 30.712 | 186.946 | 7.64 | 175.736 | 2123.1 | 26 | 45.998 | 6.35 | 1.344 | 4.68 | 8458.83 | 2.073 | 97.8 | 77.7 | 1380 | 22.95 | 5498.2 | 2893.3 | 2842.7 | 4181 | 1195.5 | 0.67738 | 6.023
2024-12-09 | 17:10 | Data | 0 | 32.798 | 30.759 | 186.991 | 7.65 | 175.736 | 2120.39 | 26.01 | 45.998 | 6.35 | 1.348 | 4.682 | 8445.26 | 2.228 | 97.8 | 77.6 | 1378 | 23 | 5489.4 | 2894.3 | 2835.8 | 4169.6 | 1195.5 | 0.67599 | 6.029
2024-12-09 | 17:10 | Data | 0 | 33.034 | 30.496 | 186.991 | 7.65 | 175.69 | 2116.78 | 26 | 45.908 | 6.35 | 1.358 | 4.686 | 8445.26 | 2.228 | 97.8 | 77.5 | 1376 | 23 | 5489.4 | 2908.3 | 2817.4 | 4161.3 | 1195.5 | 0.68205 | 6.043
2024-12-09 | 17:10 | Data | 0 | 32.278 | 30.307 | 186.855 | 7.64 | 175.51 | 2118.58 | 26 | 45.998 | 6.35 | 1.354 | 4.683 | 8445.26 | 2.133 | 97.8 | 77.6 | 1376 | 23 | 5489.4 | 2889.8 | 2847.3 | 4176.9 | 1195.5 | 0.67473 | 6.037
2024-12-09 | 17:10 | Data | 0 | 32.548 | 30.415 | 186.855 | 7.64 | 175.6 | 2111.35 | 26 | 45.908 | 6.35 | 1.358 | 4.676 | 8445.26 | 2.1 | 97.8 | 77.5 | 1374 | 22.95 | 5489.4 | 2911.1 | 2802 | 4158.6 | 1195.5 | 0.68333 | 6.034
2024-12-09 | 17:10 | Data | 0 | 32.669 | 30.651 | 187.127 | 7.65 | 175.6 | 2122.2 | 26 | 45.998 | 6.35 | 1.357 | 4.657 | 8440.74 | 2.066 | 97.8 | 77.4 | 1379 | 23 | 5486.5 | 2868.2 | 2819.6 | 4141.8 | 1195.5 | 0.67577 | 6.014
2024-12-09 | 17:10 | Data | 0 | 32.494 | 30.415 | 186.991 | 7.64 | 175.555 | 2124.01 | 26 | 45.998 | 6.35 | 1.359 | 4.662 | 8445.26 | 2.079 | 97.8 | 77.4 | 1380 | 23 | 5489.4 | 2897.8 | 2800.8 | 4144.7 | 1195.5 | 0.68281 | 6.022
2024-12-09 | 17:10 | Data | 0 | 32.264 | 30.415 | 186.855 | 7.64 | 175.555 | 2123.1 | 26 | 45.998 | 6.35 | 1.348 | 4.658 | 8445.26 | 2.052 | 97.8 | 77.6 | 1379 | 23 | 5489.4 | 2899.1 | 2823.9 | 4168.3 | 1195.5 | 0.67909 | 6.007
2024-12-09 | 17:10 | Data | 0 | 32.804 | 30.759 | 187.082 | 7.65 | 175.736 | 2121.29 | 26 | 46.089 | 6.35 | 1.347 | 4.681 | 8449.78 | 2.066 | 97.8 | 77.6 | 1378 | 22.95 | 5492.4 | 2889.3 | 2798.7 | 4144.6 | 1195.5 | 0.68145 | 6.028
2024-12-09 | 17:10 | Data | 0 | 32.649 | 30.637 | 187.082 | 7.64 | 175.6 | 2123.1 | 26.01 | 45.998 | 6.35 | 1.345 | 4.646 | 8445.26 | 2.113 | 97.8 | 77.6 | 1379 | 23 | 5489.4 | 2904.6 | 2781.2 | 4141 | 1195.5 | 0.68426 | 5.992
2024-12-09 | 17:10 | Data | 0 | 32.494 | 30.739 | 186.901 | 7.64 | 175.6 | 2122.2 | 26.01 | 45.908 | 6.35 | 1.342 | 4.667 | 8454.3 | 2.079 | 97.8 | 77.7 | 1379 | 22.95 | 5495.3 | 2911.9 | 2824.2 | 4172.3 | 1195.5 | 0.68034 | 6.007
2024-12-09 | 17:10 | Data | 0 | 32.649 | 30.529 | 186.901 | 7.64 | 175.69 | 2120.39 | 25.99 | 45.998 | 6.35 | 1.357 | 4.691 | 8445.26 | 2.275 | 97.8 | 77.6 | 1378 | 22.95 | 5489.4 | 2898.9 | 2833.9 | 4172.5 | 1195.5 | 0.67918 | 6.047
2024-12-09 | 17:10 | Data | 0 | 32.521 | 30.644 | 186.901 | 7.64 | 175.69 | 2120.39 | 26 | 45.908 | 6.35 | 1.352 | 4.68 | 8449.78 | 1.965 | 97.8 | 77.6 | 1378 | 23 | 5492.4 | 2901.7 | 2826.5 | 4172.1 | 1195.5 | 0.67697 | 6.031
2024-12-09 | 17:10 | Data | 0 | 32.723 | 30.651 | 186.946 | 7.64 | 175.6 | 2120.39 | 25.99 | 45.998 | 6.35 | 1.345 | 4.68 | 8458.83 | 2.073 | 97.8 | 77.7 | 1378 | 23 | 5498.2 | 2889.6 | 2850.8 | 4176.6 | 1195.5 | 0.67254 | 6.024
2024-12-09 | 17:10 | Data | 0 | 32.717 | 30.745 | 186.946 | 7.64 | 175.6 | 2120.39 | 26.01 | 45.908 | 6.35 | 1.351 | 4.669 | 8449.78 | 2.019 | 97.8 | 77.6 | 1379 | 23 | 5492.4 | 2910.8 | 2875.1 | 4202.8 | 1195.5 | 0.67752 | 6.02
2024-12-09 | 17:10 | Data | 0 | 32.615 | 30.739 | 187.127 | 7.64 | 175.781 | 2119.49 | 26 | 45.908 | 6.35 | 1.339 | 4.68 | 8467.87 | 2.12 | 97.8 | 77.8 | 1378 | 22.95 | 5504.1 | 2869.3 | 2837.2 | 4188.2 | 1195.5 | 0.67376 | 6.018
2024-12-09 | 17:10 | Data | 0 | 32.453 | 30.435 | 186.855 | 7.64 | 175.555 | 2119.49 | 26 | 45.998 | 6.35 | 1.347 | 4.673 | 8467.87 | 1.978 | 97.8 | 77.6 | 1378 | 23 | 5504.1 | 2904.5 | 2833.2 | 4167.3 | 1195.5 | 0.67954 | 6.02
2024-12-09 | 17:10 | Data | 0 | 32.555 | 30.766 | 187.036 | 7.64 | 175.736 | 2120.39 | 26 | 45.998 | 6.35 | 1.346 | 4.673 | 8467.87 | 2.066 | 97.8 | 77.6 | 1378 | 23 | 5504.1 | 2885.4 | 2831.4 | 4160 | 1195.5 | 0.67743 | 6.018
2024-12-09 | 17:10 | Data | 0 | 32.494 | 30.705 | 186.991 | 7.64 | 175.69 | 2120.39 | 26 | 45.998 | 6.35 | 1.348 | 4.676 | 8472.39 | 2.255 | 97.8 | 77.6 | 1378 | 23 | 5507.1 | 2882.4 | 2817.5 | 4152 | 1195.5 | 0.67707 | 6.023
2024-12-09 | 17:11 | Data | 0 | 32.676 | 30.597 | 186.946 | 7.64 | 175.69 | 2119.49 | 26.01 | 45.998 | 6.35 | 1.349 | 4.702 | 8463.35 | 2.255 | 97.8 | 77.7 | 1378 | 23.04 | 5501.2 | 2885.4 | 2801 | 4139.8 | 1195.5 | 0.67997 | 6.05
2024-12-09 | 17:11 | Data | 0 | 32.946 | 30.482 | 186.946 | 7.65 | 175.736 | 2114.06 | 26 | 45.908 | 6.35 | 1.336 | 4.698 | 8467.87 | 2.086 | 97.8 | 77.9 | 1374 | 23 | 5504.1 | 2886 | 2802.9 | 4138.5 | 1195.5 | 0.68014 | 6.034
2024-12-09 | 17:11 | Data | 0 | 32.305 | 30.961 | 186.901 | 7.64 | 175.6 | 2118.58 | 26 | 45.998 | 6.35 | 1.344 | 4.667 | 8467.87 | 1.843 | 97.8 | 77.7 | 1378 | 23 | 5504.1 | 2910.4 | 2839.2 | 4173.5 | 1195.5 | 0.68018 | 6.01
2024-12-09 | 17:11 | Data | 0 | 32.582 | 30.651 | 186.991 | 7.64 | 175.736 | 2119.49 | 26.01 | 45.908 | 6.35 | 1.358 | 4.701 | 8476.91 | 2.052 | 97.8 | 77.6 | 1378 | 23 | 5510 | 2912.3 | 2806.7 | 4151 | 1195.5 | 0.68381 | 6.057
2024-12-09 | 17:11 | Data | 0 | 32.386 | 30.421 | 187.036 | 7.64 | 175.555 | 2119.49 | 26.01 | 45.998 | 6.35 | 1.346 | 4.694 | 8476.91 | 2.046 | 97.8 | 77.7 | 1378 | 23 | 5510 | 2887.6 | 2812.7 | 4150 | 1195.5 | 0.67925 | 6.04
2024-12-09 | 17:11 | Data | 0 | 32.737 | 30.536 | 187.036 | 7.64 | 175.826 | 2120.39 | 26 | 45.998 | 6.35 | 1.336 | 4.656 | 8485.96 | 2.133 | 97.8 | 77.7 | 1378 | 23 | 5515.9 | 2890 | 2799.3 | 4136.8 | 1195.5 | 0.67963 | 5.992
2024-12-09 | 17:11 | Data | 0 | 32.744 | 30.428 | 186.855 | 7.64 | 175.826 | 2120.39 | 25.99 | 45.998 | 6.35 | 1.346 | 4.66 | 8499.53 | 2.093 | 97.8 | 77.6 | 1378 | 22.91 | 5524.7 | 2903.5 | 2859 | 4193.6 | 1195.5 | 0.67746 | 6.005
2024-12-09 | 17:11 | Data | 0 | 32.919 | 30.88 | 186.991 | 7.64 | 175.736 | 2117.68 | 26.01 | 45.998 | 6.35 | 1.348 | 4.673 | 8490.48 | 2.073 | 97.8 | 77.6 | 1371 | 23 | 5518.8 | 2913.6 | 2843.7 | 4188.9 | 1195.5 | 0.67878 | 6.021
2024-12-09 | 17:11 | Data | 0 | 32.494 | 30.475 | 186.946 | 7.64 | 175.736 | 2065.26 | 26 | 45.998 | 6.35 | 1.345 | 4.657 | 8499.53 | 2.019 | 97.8 | 77.6 | 1342 | 23 | 5524.7 | 2898.9 | 2832.2 | 4168.5 | 1195.6 | 0.68235 | 6.001
2024-12-09 | 17:11 | Data | 0 | 32.717 | 30.543 | 186.991 | 7.65 | 175.69 | 2066.16 | 25.99 | 45.818 | 6.35 | 1.335 | 4.673 | 8495 | 2.12 | 97.8 | 77.8 | 1342 | 22.86 | 5521.8 | 2901.7 | 2829.8 | 4166.8 | 1195.6 | 0.67893 | 6.007
2024-12-09 | 17:11 | Data | 0 | 33.021 | 31.063 | 187.036 | 7.65 | 175.781 | 2067.97 | 26 | 45.998 | 6.35 | 1.344 | 4.672 | 8495 | 2.127 | 97.8 | 77.7 | 1344 | 23 | 5521.8 | 2900.4 | 2832 | 4173.7 | 1195.6 | 0.67684 | 6.016
2024-12-09 | 17:11 | Data | 0 | 32.75 | 30.651 | 186.991 | 7.65 | 175.6 | 2065.26 | 26 | 45.908 | 6.35 | 1.344 | 4.675 | 8481.44 | 1.877 | 97.8 | 77.7 | 1342 | 22.95 | 5512.9 | 2907 | 2840.5 | 4179 | 1195.6 | 0.67838 | 6.017
2024-12-09 | 17:11 | Data | 0 | 32.534 | 30.806 | 187.036 | 7.64 | 175.69 | 2119.49 | 26 | 45.998 | 6.34 | 1.339 | 4.679 | 8472.39 | 2.032 | 97.8 | 77.8 | 1378 | 22.95 | 5507.1 | 2898.3 | 2832.6 | 4169.3 | 1195.6 | 0.67898 | 6.018
2024-12-09 | 17:11 | Data | 0 | 32.71 | 30.421 | 186.901 | 7.64 | 175.6 | 2123.1 | 26.01 | 45.998 | 6.35 | 1.343 | 4.64 | 8458.83 | 2.093 | 97.8 | 77.6 | 1381 | 22.95 | 5498.2 | 2911.2 | 2872.2 | 4209.1 | 1195.6 | 0.6769 | 5.983
2024-12-09 | 17:11 | Data | 0 | 32.339 | 30.415 | 186.946 | 7.64 | 175.6 | 2122.2 | 26 | 45.998 | 6.35 | 1.337 | 4.646 | 8458.83 | 1.87 | 97.8 | 77.6 | 1379 | 22.95 | 5498.2 | 2890 | 2845 | 4178.9 | 1195.6 | 0.67274 | 5.984
2024-12-09 | 17:11 | Data | 0 | 32.71 | 30.55 | 186.855 | 7.64 | 175.69 | 2123.1 | 26.01 | 45.908 | 6.35 | 1.34 | 4.662 | 8463.35 | 2.282 | 97.8 | 77.7 | 1380 | 23 | 5501.2 | 2888.5 | 2853.6 | 4175.7 | 1195.6 | 0.67457 | 6.002
2024-12-09 | 17:11 | Data | 0 | 32.413 | 30.644 | 186.946 | 7.64 | 175.69 | 2125.81 | 26 | 45.998 | 6.35 | 1.347 | 4.672 | 8458.83 | 2.012 | 97.8 | 77.6 | 1381 | 23 | 5498.2 | 2882.5 | 2850.2 | 4172.8 | 1195.6 | 0.67535 | 6.018
2024-12-09 | 17:12 | Data | 0 | 32.494 | 30.637 | 186.946 | 7.64 | 175.736 | 2122.2 | 26 | 45.998 | 6.35 | 1.335 | 4.662 | 8467.87 | 1.904 | 97.8 | 77.7 | 1379 | 23 | 5504.1 | 2918.7 | 2826.9 | 4180.1 | 1195.6 | 0.67997 | 5.997
2024-12-09 | 17:12 | Data | 0 | 32.494 | 30.428 | 186.901 | 7.64 | 175.6 | 2125.81 | 26.01 | 45.908 | 6.35 | 1.34 | 4.662 | 8485.96 | 2.059 | 97.8 | 77.7 | 1382 | 22.95 | 5515.9 | 2902.6 | 2834.8 | 4170.5 | 1195.6 | 0.67791 | 6.003
2024-12-09 | 17:12 | Data | 0 | 32.717 | 30.84 | 186.901 | 7.64 | 175.736 | 2126.72 | 26 | 45.998 | 6.35 | 1.349 | 4.664 | 8472.39 | 2.086 | 97.8 | 77.6 | 1381 | 23 | 5507.1 | 2905.1 | 2809.7 | 4157.9 | 1195.6 | 0.68297 | 6.013
2024-12-09 | 17:12 | Data | 0 | 32.723 | 30.745 | 186.991 | 7.64 | 175.781 | 2125.81 | 26 | 45.998 | 6.35 | 1.351 | 4.638 | 8472.39 | 2.12 | 97.8 | 77.4 | 1382 | 22.95 | 5507.1 | 2895.7 | 2802.2 | 4150.4 | 1195.6 | 0.68036 | 5.989
2024-12-09 | 17:12 | Data | 0 | 32.548 | 30.421 | 186.991 | 7.65 | 175.6 | 2122.2 | 26.01 | 45.908 | 6.35 | 1.344 | 4.666 | 8454.3 | 2.046 | 97.8 | 77.6 | 1380 | 22.95 | 5495.3 | 2910.1 | 2825.4 | 4164.7 | 1195.6 | 0.68081 | 6.008
2024-12-09 | 17:12 | Data | 0 | 32.723 | 30.867 | 187.036 | 7.64 | 175.69 | 2122.2 | 26 | 45.998 | 6.35 | 1.348 | 4.664 | 8467.87 | 2.059 | 97.8 | 77.6 | 1379 | 23 | 5504.1 | 2893.7 | 2836.9 | 4171.6 | 1195.6 | 0.67766 | 6.012
2024-12-09 | 17:12 | Data | 0 | 32.926 | 30.509 | 187.217 | 7.65 | 175.826 | 2124.91 | 26 | 45.998 | 6.34 | 1.351 | 4.658 | 8485.96 | 2.16 | 97.8 | 77.5 | 1382 | 23 | 5515.9 | 2873.5 | 2810 | 4151.4 | 1195.6 | 0.67913 | 6.007
2024-12-09 | 17:12 | Data | 0 | 32.494 | 30.428 | 186.946 | 7.64 | 175.69 | 2125.81 | 26 | 45.998 | 6.35 | 1.348 | 4.664 | 8481.44 | 2.052 | 97.8 | 77.6 | 1382 | 23 | 5512.9 | 2917.6 | 2838.4 | 4182.7 | 1195.6 | 0.68016 | 6.011
2024-12-09 | 17:12 | Data | 0 | 32.723 | 30.448 | 186.991 | 7.65 | 175.555 | 2124.91 | 26.01 | 45.908 | 6.36 | 1.343 | 4.677 | 8481.44 | 2.073 | 97.8 | 77.7 | 1382 | 22.95 | 5512.9 | 2900.1 | 2816 | 4153 | 1195.6 | 0.68249 | 6.02
2024-12-09 | 17:12 | Data | 0 | 32.946 | 30.563 | 187.127 | 7.65 | 175.781 | 2125.81 | 26 | 45.998 | 6.35 | 1.348 | 4.689 | 8481.44 | 2.073 | 97.8 | 77.7 | 1381 | 23.04 | 5512.9 | 2899 | 2833.8 | 4169 | 1195.6 | 0.68024 | 6.037
2024-12-09 | 17:12 | Data | 0 | 32.777 | 30.651 | 187.082 | 7.64 | 175.781 | 2124.91 | 26 | 45.998 | 6.35 | 1.347 | 4.677 | 8467.87 | 1.755 | 97.8 | 77.7 | 1381 | 23 | 5504.1 | 2883.5 | 2812.8 | 4153.8 | 1195.6 | 0.67718 | 6.022
2024-12-09 | 17:12 | Data | 0 | 32.919 | 30.678 | 186.991 | 7.64 | 175.781 | 2123.1 | 26.02 | 45.908 | 6.34 | 1.352 | 4.664 | 8481.44 | 2.073 | 97.8 | 77.5 | 1381 | 23 | 5512.9 | 2901.1 | 2826.1 | 4174.3 | 1195.6 | 0.67717 | 6.017
2024-12-09 | 17:12 | Data | 0 | 32.582 | 30.651 | 186.991 | 7.64 | 175.69 | 2123.1 | 26 | 45.908 | 6.35 | 1.34 | 4.686 | 8485.96 | 2.073 | 97.8 | 77.8 | 1379 | 22.95 | 5515.9 | 2897 | 2804.3 | 4150.3 | 1195.6 | 0.6822 | 6.025
2024-12-09 | 17:12 | Data | 0 | 32.723 | 31.069 | 187.082 | 7.64 | 175.69 | 2123.1 | 26.01 | 45.908 | 6.34 | 1.347 | 4.702 | 8490.48 | 1.857 | 97.8 | 77.7 | 1380 | 22.95 | 5518.8 | 2888.2 | 2850.5 | 4173.3 | 1195.6 | 0.67586 | 6.048
2024-12-09 | 17:12 | Data | 0 | 32.636 | 30.34 | 186.901 | 7.64 | 175.781 | 2122.2 | 26 | 45.998 | 6.35 | 1.34 | 4.681 | 8485.96 | 2.059 | 97.8 | 77.7 | 1378 | 22.95 | 5515.9 | 2897.3 | 2842.6 | 4177.2 | 1195.6 | 0.67416 | 6.02
2024-12-09 | 17:12 | Data | 0 | 32.413 | 30.637 | 187.036 | 7.64 | 175.736 | 2114.97 | 26 | 45.908 | 6.35 | 1.336 | 4.654 | 8472.39 | 1.85 | 97.8 | 77.7 | 1374 | 23 | 5507.1 | 2897.6 | 2818.4 | 4161.4 | 1195.6 | 0.67907 | 5.991
2024-12-09 | 17:12 | Data | 0 | 32.298 | 30.59 | 186.946 | 7.64 | 175.781 | 2120.39 | 25.99 | 45.998 | 6.35 | 1.347 | 4.672 | 8467.87 | 1.978 | 97.8 | 77.6 | 1378 | 23 | 5504.1 | 2888.3 | 2838.7 | 4164.9 | 1195.6 | 0.67811 | 6.02
2024-12-09 | 17:12 | Data | 0 | 32.494 | 30.442 | 186.901 | 7.64 | 175.6 | 2119.49 | 26 | 45.998 | 6.35 | 1.355 | 4.682 | 8472.39 | 1.978 | 97.8 | 77.6 | 1378 | 23.04 | 5507.1 | 2894.1 | 2868.8 | 4190.4 | 1195.6 | 0.67262 | 6.036
2024-12-09 | 17:13 | Data | 0 | 32.723 | 30.651 | 187.082 | 7.64 | 175.781 | 2120.39 | 26 | 45.998 | 6.35 | 1.347 | 4.691 | 8476.91 | 2.073 | 97.8 | 77.7 | 1378 | 23 | 5510 | 2893.6 | 2858 | 4190.4 | 1195.6 | 0.67379 | 6.038
2024-12-09 | 17:13 | Data | 0 | 32.865 | 30.759 | 186.901 | 7.65 | 175.736 | 2119.49 | 26 | 45.998 | 6.35 | 1.344 | 4.664 | 8445.26 | 2.066 | 97.8 | 77.6 | 1378 | 23 | 5489.4 | 2916.7 | 2834 | 4179.4 | 1195.6 | 0.68213 | 6.01
2024-12-09 | 17:13 | Data | 0 | 32.622 | 30.651 | 187.036 | 7.64 | 175.736 | 2123.1 | 26 | 45.908 | 6.36 | 1.347 | 4.651 | 8445.26 | 1.904 | 97.8 | 77.5 | 1379 | 23 | 5489.4 | 2894.4 | 2827.7 | 4167.2 | 1195.6 | 0.67692 | 5.998
2024-12-09 | 17:13 | Data | 0 | 32.501 | 30.651 | 186.946 | 7.65 | 175.6 | 2120.39 | 26.01 | 45.998 | 6.35 | 1.351 | 4.673 | 8431.69 | 1.843 | 97.8 | 77.6 | 1378 | 22.95 | 5480.6 | 2921 | 2819.9 | 4175.2 | 1195.6 | 0.68406 | 6.024
2024-12-09 | 17:13 | Data | 0 | 32.717 | 30.651 | 187.082 | 7.64 | 175.781 | 2123.1 | 26 | 46.089 | 6.36 | 1.348 | 4.685 | 8427.17 | 2.073 | 97.8 | 77.6 | 1380 | 23 | 5477.7 | 2903.1 | 2830.1 | 4178.6 | 1195.6 | 0.6789 | 6.034
2024-12-09 | 17:13 | Data | 0 | 32.494 | 30.59 | 186.855 | 7.64 | 175.555 | 2124.01 | 26 | 45.998 | 6.35 | 1.339 | 4.683 | 8445.26 | 2.079 | 97.8 | 77.7 | 1380 | 23 | 5489.4 | 2899.2 | 2823.2 | 4166.8 | 1195.6 | 0.67746 | 6.023
2024-12-09 | 17:13 | Data | 0 | 32.609 | 30.745 | 187.127 | 7.64 | 175.736 | 2124.91 | 25.99 | 45.998 | 6.35 | 1.354 | 4.694 | 8454.3 | 1.971 | 97.8 | 77.6 | 1381 | 23 | 5495.3 | 2908.7 | 2840.3 | 4175.7 | 1195.6 | 0.67653 | 6.047
2024-12-09 | 17:13 | Data | 0 | 32.386 | 30.421 | 186.901 | 7.64 | 175.736 | 2124.01 | 26.01 | 45.908 | 6.35 | 1.357 | 4.699 | 8431.69 | 2.025 | 97.8 | 77.6 | 1381 | 22.95 | 5480.6 | 2905.7 | 2817.9 | 4149.3 | 1195.6 | 0.67845 | 6.056
2024-12-09 | 17:13 | Data | 0 | 32.717 | 30.853 | 187.082 | 7.64 | 175.781 | 2124.91 | 26 | 45.998 | 6.35 | 1.352 | 4.706 | 8422.65 | 1.87 | 97.8 | 77.7 | 1381 | 22.95 | 5474.7 | 2900.4 | 2849.2 | 4182.2 | 1195.6 | 0.67571 | 6.058
2024-12-09 | 17:13 | Data | 0 | 32.494 | 30.617 | 186.991 | 7.64 | 175.555 | 2119.49 | 26 | 45.998 | 6.35 | 1.339 | 4.683 | 8440.74 | 2.086 | 97.8 | 77.8 | 1378 | 23.04 | 5486.5 | 2901.6 | 2810.8 | 4159.4 | 1195.7 | 0.67947 | 6.023
2024-12-09 | 17:13 | Data | 0 | 32.94 | 30.658 | 187.036 | 7.64 | 175.781 | 2124.01 | 26 | 45.998 | 6.35 | 1.335 | 4.648 | 8440.74 | 2.241 | 97.8 | 77.7 | 1380 | 23 | 5486.5 | 2913.5 | 2846.3 | 4193.2 | 1195.7 | 0.67811 | 5.985
2024-12-09 | 17:13 | Data | 0 | 32.379 | 30.637 | 187.036 | 7.64 | 175.6 | 2122.2 | 26 | 45.998 | 6.36 | 1.339 | 4.654 | 8454.3 | 1.958 | 97.8 | 77.6 | 1379 | 23.04 | 5495.3 | 2909.8 | 2842 | 4185.5 | 1195.7 | 0.67822 | 5.992
2024-12-09 | 17:13 | Data | 0 | 32.548 | 30.415 | 186.946 | 7.65 | 175.69 | 2123.1 | 26 | 45.908 | 6.35 | 1.345 | 4.669 | 8472.39 | 2.086 | 97.8 | 77.6 | 1380 | 22.95 | 5507.1 | 2908.6 | 2844.1 | 4185 | 1195.7 | 0.67854 | 6.013
2024-12-09 | 17:13 | Data | 0 | 32.501 | 30.651 | 187.036 | 7.64 | 175.736 | 2121.29 | 26 | 45.998 | 6.35 | 1.356 | 4.692 | 8445.26 | 2.019 | 97.8 | 77.6 | 1380 | 23 | 5489.4 | 2921.6 | 2809.9 | 4170.2 | 1195.7 | 0.68313 | 6.047
2024-12-09 | 17:13 | Data | 0 | 32.595 | 30.644 | 186.991 | 7.64 | 175.6 | 2123.1 | 26 | 45.998 | 6.35 | 1.353 | 4.663 | 8445.26 | 2.052 | 97.8 | 77.5 | 1380 | 23.04 | 5489.4 | 2900.8 | 2791.3 | 4141.1 | 1195.7 | 0.68377 | 6.016
2024-12-09 | 17:13 | Data | 0 | 32.669 | 30.651 | 186.991 | 7.64 | 175.736 | 2117.68 | 25.99 | 45.998 | 6.35 | 1.34 | 4.656 | 8445.26 | 2.066 | 97.8 | 77.7 | 1376 | 23 | 5489.4 | 2892.7 | 2815.9 | 4153.4 | 1195.7 | 0.67985 | 5.998
2024-12-09 | 17:13 | Data | 0 | 32.501 | 30.469 | 186.991 | 7.64 | 175.736 | 2125.81 | 26 | 45.998 | 6.35 | 1.347 | 4.664 | 8418.13 | 1.978 | 97.8 | 77.6 | 1382 | 23 | 5471.8 | 2901.8 | 2835.6 | 4173.2 | 1195.7 | 0.67794 | 6.01
2024-12-09 | 17:13 | Data | 0 | 32.75 | 30.475 | 186.946 | 7.64 | 175.781 | 2125.81 | 25.99 | 45.998 | 6.35 | 1.354 | 4.642 | 8467.87 | 1.965 | 97.8 | 77.4 | 1381 | 23 | 5504.1 | 2898.9 | 2814 | 4159 | 1195.7 | 0.68018 | 5.996
2024-12-09 | 17:14 | Data | 0 | 32.838 | 30.448 | 187.082 | 7.64 | 175.826 | 2128.52 | 25.99 | 45.998 | 6.35 | 1.347 | 4.658 | 8490.48 | 2.12 | 97.8 | 77.6 | 1384 | 23 | 5518.8 | 2908.1 | 2829.6 | 4170.4 | 1195.7 | 0.67976 | 6.004
2024-12-09 | 17:14 | Data | 0 | 32.548 | 30.536 | 186.946 | 7.64 | 175.6 | 2128.52 | 26 | 45.998 | 6.35 | 1.348 | 4.659 | 8481.44 | 2.14 | 97.8 | 77.6 | 1384 | 23 | 5512.9 | 2895 | 2833.4 | 4165.5 | 1195.7 | 0.67718 | 6.007
2024-12-09 | 17:14 | Data | 0 | 32.71 | 30.597 | 186.946 | 7.64 | 175.736 | 2125.81 | 26 | 45.908 | 6.35 | 1.347 | 4.658 | 8485.96 | 2.012 | 97.8 | 77.6 | 1382 | 22.95 | 5515.9 | 2901.6 | 2819.1 | 4159.6 | 1195.7 | 0.6805 | 6.004
2024-12-09 | 17:14 | Data | 0 | 32.669 | 30.577 | 187.127 | 7.64 | 175.826 | 2125.81 | 26.01 | 45.998 | 6.35 | 1.342 | 4.656 | 8472.39 | 2.187 | 97.8 | 77.6 | 1382 | 23 | 5507.1 | 2904.2 | 2837.9 | 4176.3 | 1195.7 | 0.67726 | 5.997
2024-12-09 | 17:14 | Data | 0 | 32.703 | 30.651 | 186.991 | 7.64 | 175.736 | 2124.91 | 26.01 | 45.908 | 6.35 | 1.348 | 4.656 | 8481.44 | 1.958 | 97.8 | 77.6 | 1381 | 23 | 5512.9 | 2879.7 | 2822.1 | 4150.2 | 1195.7 | 0.67528 | 6.004
2024-12-09 | 17:14 | Data | 0 | 32.494 | 30.624 | 186.991 | 7.65 | 175.6 | 2124.01 | 26.01 | 45.908 | 6.35 | 1.348 | 4.664 | 8445.26 | 2.046 | 97.8 | 77.6 | 1381 | 23 | 5489.4 | 2891.9 | 2818.9 | 4159.5 | 1195.7 | 0.67978 | 6.011
2024-12-09 | 17:14 | Data | 0 | 32.521 | 30.644 | 187.082 | 7.64 | 175.69 | 2123.1 | 26 | 45.818 | 6.35 | 1.342 | 4.674 | 8467.87 | 1.877 | 97.8 | 77.7 | 1381 | 22.95 | 5504.1 | 2878.8 | 2812.1 | 4145.5 | 1195.7 | 0.68005 | 6.018
2024-12-09 | 17:14 | Data | 0 | 32.717 | 30.475 | 186.991 | 7.64 | 175.69 | 2125.81 | 26 | 45.998 | 6.35 | 1.352 | 4.657 | 8467.87 | 2.248 | 97.8 | 77.5 | 1382 | 23 | 5504.1 | 2891.2 | 2816.6 | 4152.5 | 1195.7 | 0.68061 | 6.008
2024-12-09 | 17:14 | Data | 0 | 32.831 | 30.664 | 187.127 | 7.64 | 175.916 | 2125.81 | 26 | 45.998 | 6.35 | 1.359 | 4.648 | 8467.87 | 2.073 | 97.8 | 77.4 | 1381 | 23 | 5504.1 | 2890.3 | 2828.9 | 4164.5 | 1195.7 | 0.67728 | 6.007
2024-12-09 | 17:14 | Data | 0 | 32.723 | 30.853 | 186.991 | 7.65 | 175.736 | 2122.2 | 26 | 45.908 | 6.35 | 1.353 | 4.647 | 8476.91 | 2.086 | 97.8 | 77.4 | 1379 | 23 | 5510 | 2893.6 | 2825.4 | 4166.7 | 1195.7 | 0.67772 | 6.002
2024-12-09 | 17:14 | Data | 0 | 32.494 | 30.415 | 186.991 | 7.64 | 175.736 | 2126.72 | 26 | 45.998 | 6.35 | 1.342 | 4.666 | 8481.44 | 2.066 | 97.8 | 77.7 | 1383 | 23 | 5512.9 | 2908 | 2832.3 | 4173.8 | 1195.7 | 0.68087 | 6.008
2024-12-09 | 17:14 | Data | 0 | 32.946 | 30.705 | 187.127 | 7.64 | 175.781 | 2125.81 | 26.01 | 45.908 | 6.35 | 1.344 | 4.663 | 8472.39 | 1.965 | 97.8 | 77.6 | 1382 | 22.95 | 5507.1 | 2890.4 | 2859.4 | 4183.1 | 1195.7 | 0.67371 | 6.007
2024-12-09 | 17:14 | Data | 0 | 32.494 | 30.739 | 186.991 | 7.64 | 175.69 | 2124.91 | 26 | 45.998 | 6.35 | 1.351 | 4.692 | 8454.3 | 1.958 | 97.8 | 77.6 | 1382 | 23 | 5495.3 | 2885.7 | 2832.6 | 4162 | 1195.7 | 0.67649 | 6.044
2024-12-09 | 17:14 | Data | 0 | 32.514 | 30.637 | 186.946 | 7.64 | 175.736 | 2124.91 | 26 | 46.269 | 6.35 | 1.353 | 4.663 | 8445.26 | 1.877 | 97.8 | 77.5 | 1381 | 23.18 | 5489.4 | 2886.6 | 2809 | 4148.2 | 1195.7 | 0.67954 | 6.016
2024-12-09 | 17:14 | Data | 0 | 32.892 | 30.482 | 187.217 | 7.64 | 175.781 | 2125.81 | 26 | 45.908 | 6.35 | 1.354 | 4.643 | 8445.26 | 2.127 | 97.8 | 77.4 | 1382 | 23 | 5489.4 | 2902.8 | 2813 | 4156.5 | 1195.7 | 0.68258 | 5.997
2024-12-09 | 17:14 | Data | 0 | 32.609 | 30.597 | 186.991 | 7.64 | 175.69 | 2127.62 | 26 | 46.269 | 6.35 | 1.341 | 4.681 | 8445.26 | 2.093 | 97.8 | 77.7 | 1383 | 23.09 | 5489.4 | 2904 | 2811.9 | 4160.4 | 1195.7 | 0.68162 | 6.02
2024-12-09 | 17:14 | Data | 0 | 32.717 | 30.961 | 187.036 | 7.64 | 175.826 | 2127.62 | 26.01 | 45.998 | 6.35 | 1.347 | 4.706 | 8454.3 | 1.965 | 97.8 | 77.8 | 1383 | 22.95 | 5495.3 | 2884.7 | 2827.2 | 4154.4 | 1195.7 | 0.67747 | 6.053
2024-12-09 | 17:15 | Data | 0 | 32.582 | 30.637 | 187.082 | 7.64 | 175.826 | 2127.62 | 26.01 | 45.998 | 6.35 | 1.343 | 4.676 | 8440.74 | 1.911 | 97.8 | 77.7 | 1383 | 23 | 5486.5 | 2889 | 2821 | 4156 | 1195.7 | 0.67874 | 6.019
2024-12-09 | 17:15 | Data | 0 | 32.669 | 31.144 | 187.217 | 7.64 | 175.871 | 2123.1 | 26.01 | 46.179 | 6.35 | 1.341 | 4.675 | 8427.17 | 1.985 | 97.8 | 77.7 | 1380 | 23.13 | 5477.7 | 2894 | 2805.5 | 4146.2 | 1195.7 | 0.68034 | 6.017
2024-12-09 | 17:15 | Data | 0 | 32.474 | 30.644 | 187.082 | 7.64 | 175.736 | 2126.72 | 26 | 46.269 | 6.35 | 1.352 | 4.642 | 8440.74 | 1.965 | 97.8 | 77.4 | 1382 | 23.13 | 5486.5 | 2910.9 | 2809.5 | 4161.9 | 1195.7 | 0.68321 | 5.994
2024-12-09 | 17:15 | Data | 0 | 32.71 | 30.421 | 187.036 | 7.64 | 175.736 | 2125.81 | 26 | 46.359 | 6.35 | 1.353 | 4.645 | 8422.65 | 2.302 | 97.8 | 77.4 | 1382 | 23.18 | 5474.7 | 2914.6 | 2813.8 | 4169.1 | 1195.7 | 0.6816 | 5.998
2024-12-09 | 17:15 | Data | 0 | 32.494 | 30.59 | 186.991 | 7.64 | 175.69 | 2124.91 | 25.99 | 46.179 | 6.35 | 1.343 | 4.653 | 8427.17 | 2.073 | 97.8 | 77.6 | 1381 | 23.09 | 5477.7 | 2885.6 | 2829.2 | 4158.5 | 1195.7 | 0.6778 | 5.996
2024-12-09 | 17:15 | Data | 0 | 32.696 | 30.428 | 187.036 | 7.64 | 175.736 | 2127.62 | 25.99 | 46.269 | 6.35 | 1.342 | 4.667 | 8418.13 | 2.282 | 97.8 | 77.7 | 1383 | 23.13 | 5471.8 | 2915.1 | 2811 | 4165.3 | 1195.7 | 0.68305 | 6.01
2024-12-09 | 17:15 | Data | 0 | 32.865 | 30.462 | 187.082 | 7.64 | 175.871 | 2127.62 | 26 | 46.089 | 6.35 | 1.339 | 4.658 | 8409.08 | 2.059 | 97.8 | 77.7 | 1384 | 23.04 | 5465.9 | 2905.2 | 2817.9 | 4159.5 | 1195.7 | 0.68304 | 5.997
2024-12-09 | 17:15 | Data | 0 | 32.94 | 30.556 | 187.036 | 7.64 | 175.736 | 2128.52 | 26 | 46.179 | 6.35 | 1.34 | 4.664 | 8418.13 | 2.073 | 97.8 | 77.7 | 1382 | 23.09 | 5471.8 | 2888.7 | 2809.7 | 4143.2 | 1195.7 | 0.67977 | 6.004
2024-12-09 | 17:15 | Data | 0 | 32.568 | 30.631 | 187.172 | 7.64 | 175.826 | 2130.33 | 26 | 46.089 | 6.35 | 1.342 | 4.657 | 8431.69 | 1.89 | 97.8 | 77.6 | 1385 | 23.09 | 5480.6 | 2881.6 | 2800 | 4146.7 | 1195.7 | 0.6807 | 6
2024-12-09 | 17:15 | Data | 0 | 32.386 | 30.59 | 186.946 | 7.64 | 175.736 | 2128.52 | 25.99 | 46.269 | 6.34 | 1.348 | 4.676 | 8427.17 | 2.025 | 97.8 | 77.6 | 1384 | 23.04 | 5477.7 | 2908.6 | 2805.1 | 4153.5 | 1195.7 | 0.68303 | 6.025
2024-12-09 | 17:15 | Data | 0 | 32.764 | 30.448 | 186.991 | 7.64 | 175.781 | 2127.62 | 26 | 46.089 | 6.35 | 1.344 | 4.66 | 8422.65 | 2.14 | 97.8 | 77.6 | 1384 | 23 | 5474.7 | 2877 | 2830.7 | 4157.3 | 1195.7 | 0.67617 | 6.004
2024-12-09 | 17:15 | Data | 0 | 32.946 | 30.475 | 187.036 | 7.64 | 175.736 | 2128.52 | 26 | 45.998 | 6.35 | 1.335 | 4.664 | 8422.65 | 1.809 | 97.8 | 77.7 | 1383 | 23 | 5474.7 | 2892.8 | 2820.4 | 4159.4 | 1195.8 | 0.6791 | 5.998
2024-12-09 | 17:15 | Data | 0 | 32.676 | 30.86 | 187.082 | 7.64 | 175.871 | 2124.91 | 26.01 | 46.089 | 6.35 | 1.353 | 4.682 | 8409.08 | 1.884 | 97.8 | 77.6 | 1381 | 23.04 | 5465.9 | 2899.4 | 2832.2 | 4167.7 | 1195.8 | 0.67931 | 6.034
2024-12-09 | 17:15 | Data | 0 | 32.723 | 30.867 | 187.036 | 7.64 | 175.736 | 2125.81 | 26 | 45.908 | 6.35 | 1.343 | 4.692 | 8409.08 | 1.911 | 97.8 | 77.8 | 1382 | 23 | 5465.9 | 2902.5 | 2841 | 4178.9 | 1195.8 | 0.67591 | 6.036
2024-12-09 | 17:15 | Data | 0 | 33.149 | 30.739 | 186.991 | 7.64 | 175.826 | 2126.72 | 26 | 45.998 | 6.35 | 1.339 | 4.691 | 8404.56 | 2.127 | 97.8 | 77.8 | 1382 | 23 | 5463 | 2897.8 | 2874.1 | 4196.1 | 1195.8 | 0.67286 | 6.029
2024-12-09 | 17:15 | Data | 0 | 32.723 | 30.435 | 187.036 | 7.64 | 175.69 | 2125.81 | 26.01 | 45.998 | 6.36 | 1.339 | 4.664 | 8395.51 | 2.167 | 97.8 | 77.7 | 1382 | 23 | 5457.1 | 2912.4 | 2863.9 | 4196.3 | 1195.8 | 0.67636 | 6.003
2024-12-09 | 17:15 | Data | 0 | 32.609 | 30.651 | 187.127 | 7.64 | 175.736 | 2125.81 | 26 | 45.818 | 6.34 | 1.353 | 4.672 | 8314.11 | 2.059 | 97.8 | 77.5 | 1382 | 23 | 5404.2 | 2908.3 | 2851 | 4188.2 | 1195.8 | 0.676 | 6.025
2024-12-09 | 17:15 | Data | 0 | 32.879 | 30.705 | 187.036 | 7.64 | 175.826 | 2124.91 | 26.01 | 45.998 | 6.35 | 1.348 | 4.683 | 8128.7 | 2.187 | 97.8 | 77.7 | 1381 | 23 | 5283.7 | 2893.8 | 2797 | 4140.3 | 1195.8 | 0.68157 | 6.032
2024-12-09 | 17:16 | Data | 0 | 32.494 | 30.415 | 186.946 | 7.64 | 175.6 | 2124.91 | 26 | 45.908 | 6.35 | 1.355 | 4.657 | 8422.65 | 2.079 | 97.8 | 77.5 | 1382 | 22.95 | 5474.7 | 2890.2 | 2797.9 | 4144.6 | 1195.8 | 0.68114 | 6.011
2024-12-09 | 17:16 | Data | 0 | 32.946 | 30.766 | 187.127 | 7.64 | 175.871 | 2123.1 | 26 | 45.998 | 6.35 | 1.357 | 4.673 | 8400.04 | 2.066 | 97.8 | 77.5 | 1380 | 23 | 5460 | 2908.8 | 2794.9 | 4150 | 1195.8 | 0.68373 | 6.029
2024-12-09 | 17:16 | Data | 0 | 32.818 | 30.813 | 187.127 | 7.65 | 175.736 | 2122.2 | 26.01 | 45.818 | 6.35 | 1.354 | 4.689 | 8404.56 | 2.262 | 97.8 | 77.6 | 1379 | 22.95 | 5463 | 2897 | 2799.2 | 4149.3 | 1195.8 | 0.68095 | 6.042
2024-12-09 | 17:16 | Data | 0 | 32.757 | 30.651 | 187.082 | 7.64 | 175.871 | 2123.1 | 25.99 | 46.179 | 6.34 | 1.351 | 4.687 | 8400.04 | 1.958 | 97.8 | 77.6 | 1379 | 23.04 | 5460 | 2909.6 | 2824.7 | 4174 | 1195.8 | 0.68123 | 6.038
2024-12-09 | 17:16 | Data | 0 | 32.777 | 30.658 | 187.217 | 7.64 | 175.871 | 2122.2 | 25.99 | 45.908 | 6.35 | 1.352 | 4.674 | 8400.04 | 1.904 | 97.8 | 77.6 | 1380 | 22.91 | 5460 | 2889.2 | 2835.6 | 4162.9 | 1195.8 | 0.67732 | 6.027
2024-12-09 | 17:16 | Data | 0 | 32.723 | 30.705 | 187.127 | 7.64 | 175.826 | 2123.1 | 26.01 | 45.998 | 6.35 | 1.34 | 4.668 | 8431.69 | 2.194 | 97.8 | 77.7 | 1379 | 22.95 | 5480.6 | 2893 | 2835.5 | 4171.1 | 1195.8 | 0.67538 | 6.009
2024-12-09 | 17:16 | Data | 0 | 32.717 | 30.651 | 186.855 | 7.65 | 175.781 | 2122.2 | 26.01 | 45.998 | 6.35 | 1.339 | 4.684 | 8445.26 | 2.073 | 97.8 | 77.8 | 1380 | 23 | 5489.4 | 2888.6 | 2843.8 | 4167.9 | 1195.8 | 0.6753 | 6.024
2024-12-09 | 17:16 | Data | 0 | 32.609 | 30.752 | 187.036 | 7.64 | 175.736 | 2122.2 | 26 | 45.998 | 6.35 | 1.347 | 4.687 | 8440.74 | 1.951 | 97.8 | 77.7 | 1379 | 23 | 5486.5 | 2919.4 | 2867.2 | 4193.6 | 1195.8 | 0.67495 | 6.034
2024-12-09 | 17:16 | Data | 0 | 32.548 | 30.637 | 187.127 | 7.64 | 175.781 | 2123.1 | 26 | 45.998 | 6.35 | 1.342 | 4.671 | 8445.26 | 2.025 | 97.8 | 77.7 | 1380 | 22.95 | 5489.4 | 2900.7 | 2832.6 | 4170.2 | 1195.8 | 0.67827 | 6.013
2024-12-09 | 17:16 | Data | 0 | 32.953 | 30.705 | 187.127 | 7.64 | 175.826 | 2125.81 | 26.01 | 45.998 | 6.35 | 1.339 | 4.664 | 8395.51 | 2.248 | 97.8 | 77.7 | 1381 | 23 | 5457.1 | 2905.6 | 2834.7 | 4174.7 | 1195.8 | 0.67905 | 6.003
2024-12-09 | 17:16 | Data | 0 | 32.744 | 30.435 | 187.036 | 7.64 | 175.781 | 2125.81 | 26 | 45.998 | 6.35 | 1.348 | 4.659 | 8418.13 | 2.052 | 97.8 | 77.5 | 1382 | 22.95 | 5471.8 | 2899.7 | 2815.9 | 4157.2 | 1195.8 | 0.68175 | 6.005
2024-12-09 | 17:16 | Data | 0 | 32.919 | 30.475 | 187.082 | 7.64 | 175.781 | 2124.91 | 26 | 46.089 | 6.35 | 1.345 | 4.666 | 8418.13 | 2.1 | 97.8 | 77.6 | 1381 | 23 | 5471.8 | 2904.3 | 2806.3 | 4153.9 | 1195.8 | 0.68169 | 6.011
2024-12-09 | 17:16 | Data | 0 | 32.838 | 30.435 | 187.127 | 7.64 | 175.826 | 2125.81 | 26 | 45.908 | 6.35 | 1.345 | 4.646 | 8422.65 | 2.073 | 97.8 | 77.6 | 1382 | 22.95 | 5474.7 | 2909.6 | 2813.5 | 4161.6 | 1195.8 | 0.68314 | 5.991
2024-12-09 | 17:16 | Data | 0 | 32.892 | 30.651 | 186.946 | 7.64 | 175.781 | 2124.91 | 26 | 45.727 | 6.35 | 1.339 | 4.655 | 8418.13 | 2.093 | 97.8 | 77.6 | 1381 | 22.91 | 5471.8 | 2906 | 2829.6 | 4174.5 | 1195.8 | 0.67896 | 5.995
2024-12-09 | 17:16 | Data | 0 | 32.723 | 30.982 | 187.217 | 7.64 | 175.871 | 2124.01 | 26 | 45.908 | 6.35 | 1.351 | 4.675 | 8431.69 | 2.073 | 97.8 | 77.6 | 1380 | 23 | 5480.6 | 2886.1 | 2837.9 | 4165 | 1195.8 | 0.67632 | 6.026
2024-12-09 | 17:16 | Data | 0 | 32.723 | 30.874 | 187.172 | 7.64 | 175.781 | 2127.62 | 25.99 | 45.908 | 6.35 | 1.353 | 4.674 | 8418.13 | 2.052 | 97.8 | 77.6 | 1384 | 22.95 | 5471.8 | 2891.6 | 2840.8 | 4172.1 | 1195.8 | 0.67797 | 6.027
2024-12-09 | 17:16 | Data | 0 | 32.723 | 30.968 | 187.172 | 7.64 | 175.826 | 2128.52 | 26 | 46.269 | 6.36 | 1.343 | 4.65 | 8431.69 | 2.073 | 97.8 | 77.6 | 1384 | 23.13 | 5480.6 | 2904.6 | 2860.2 | 4193.6 | 1195.8 | 0.67466 | 5.993
2024-12-09 | 17:16 | Data | 0 | 32.568 | 30.597 | 187.082 | 7.64 | 175.781 | 2127.62 | 26 | 46.269 | 6.35 | 1.343 | 4.654 | 8454.3 | 1.958 | 97.8 | 77.6 | 1384 | 23.13 | 5495.3 | 2884.2 | 2877.7 | 4194.1 | 1195.8 | 0.67059 | 5.997
2024-12-09 | 17:17 | Data | 0 | 33 | 30.678 | 187.036 | 7.64 | 175.871 | 2127.62 | 26 | 45.998 | 6.35 | 1.354 | 4.702 | 8440.74 | 2.079 | 97.8 | 77.6 | 1382 | 23 | 5486.5 | 2908.6 | 2873.8 | 4203 | 1195.8 | 0.67423 | 6.056
2024-12-09 | 17:17 | Data | 0 | 32.73 | 30.678 | 187.082 | 7.65 | 175.736 | 2125.81 | 26 | 46.269 | 6.35 | 1.341 | 4.711 | 8458.83 | 2.221 | 97.8 | 77.8 | 1382 | 23.09 | 5498.2 | 2894.8 | 2877.4 | 4202.1 | 1195.8 | 0.67101 | 6.053
2024-12-09 | 17:17 | Data | 0 | 32.757 | 30.826 | 187.082 | 7.64 | 175.871 | 2124.91 | 26 | 46.179 | 6.35 | 1.347 | 4.673 | 8445.26 | 1.971 | 97.8 | 77.6 | 1382 | 23.13 | 5489.4 | 2902.3 | 2881.5 | 4205.5 | 1195.8 | 0.67265 | 6.019
2024-12-09 | 17:17 | Data | 0 | 32.723 | 30.543 | 186.946 | 7.64 | 175.736 | 2124.91 | 26 | 46.269 | 6.34 | 1.351 | 4.71 | 8431.69 | 2.106 | 97.8 | 77.7 | 1381 | 23.13 | 5480.6 | 2888.1 | 2856.8 | 4180.1 | 1195.8 | 0.67327 | 6.062
2024-12-09 | 17:17 | Data | 0 | 32.609 | 30.651 | 186.991 | 7.64 | 175.69 | 2127.62 | 26 | 46.089 | 6.35 | 1.344 | 4.693 | 8431.69 | 2.025 | 97.8 | 77.7 | 1384 | 23 | 5480.6 | 2906.4 | 2814.7 | 4159 | 1195.8 | 0.68124 | 6.036
2024-12-09 | 17:17 | Data | 0 | 32.777 | 30.435 | 187.127 | 7.64 | 175.871 | 2127.62 | 26 | 46.269 | 6.35 | 1.345 | 4.654 | 8427.17 | 2.127 | 97.8 | 77.6 | 1384 | 23.13 | 5477.7 | 2903.7 | 2823.3 | 4164.1 | 1195.8 | 0.67982 | 5.998
2024-12-09 | 17:17 | Data | 0 | 33 | 30.462 | 187.082 | 7.64 | 175.781 | 2128.52 | 26.01 | 46.179 | 6.35 | 1.352 | 4.669 | 8431.69 | 1.992 | 97.8 | 77.5 | 1383 | 23.09 | 5480.6 | 2890.2 | 2837.7 | 4165.1 | 1195.8 | 0.67812 | 6.021
2024-12-09 | 17:17 | Data | 0 | 32.656 | 30.82 | 187.082 | 7.64 | 175.826 | 2124.01 | 26 | 46.269 | 6.35 | 1.347 | 4.677 | 8467.87 | 2.12 | 97.8 | 77.7 | 1381 | 23.13 | 5504.1 | 2913.4 | 2814.5 | 4168.2 | 1195.8 | 0.68164 | 6.026
2024-12-09 | 17:17 | Data | 0 | 32.723 | 30.853 | 187.263 | 7.64 | 175.781 | 2125.81 | 26 | 46.179 | 6.35 | 1.349 | 4.671 | 8485.96 | 1.958 | 97.8 | 77.6 | 1381 | 23.04 | 5515.9 | 2886.8 | 2871.3 | 4200.3 | 1195.8 | 0.67382 | 6.018
2024-12-09 | 17:17 | Data | 0 | 32.838 | 30.712 | 187.217 | 7.64 | 175.871 | 2125.81 | 26 | 46.089 | 6.34 | 1.344 | 4.673 | 8467.87 | 1.985 | 97.8 | 77.7 | 1382 | 23.09 | 5504.1 | 2436.7 | 2911.1 | 3828.7 | 1195.8 | 0.63821 | 6.017
2024-12-09 | 17:17 | Data | 0 | 32.663 | 30.597 | 187.172 | 7.64 | 175.781 | 2126.72 | 26 | 46.179 | 6.35 | 1.342 | 4.673 | 8481.44 | 1.924 | 97.8 | 77.7 | 1381 | 23.13 | 5512.9 | 1811 | 2342.5 | 2973.5 | 1195.8 | 0.6098 | 6.015
2024-12-09 | 17:17 | Data | 0 | 33.048 | 30.489 | 187.127 | 7.64 | 175.871 | 2124.91 | 26.01 | 46.269 | 6.35 | 1.34 | 4.706 | 8445.26 | 2.106 | 97.8 | 77.8 | 1381 | 23.13 | 5489.4 | 1815.6 | 2341.7 | 2973.2 | 1195.8 | 0.60754 | 6.045
2024-12-09 | 17:17 | Data | 0 | 32.723 | 30.766 | 187.082 | 7.65 | 175.69 | 2122.2 | 25.99 | 46.359 | 6.35 | 1.347 | 4.683 | 8458.83 | 2.073 | 97.8 | 77.7 | 1380 | 23.13 | 5498.2 | 1826.4 | 2331 | 2964.6 | 1195.8 | 0.60897 | 6.029
2024-12-09 | 17:17 | Data | 0 | 32.615 | 30.536 | 187.127 | 7.65 | 175.826 | 2125.81 | 26 | 46.179 | 6.34 | 1.337 | 4.667 | 8458.83 | 2.032 | 97.8 | 77.7 | 1381 | 23.09 | 5498.2 | 1830.2 | 2300.7 | 2950.7 | 1195.9 | 0.61335 | 6.004
2024-12-09 | 17:17 | Data | 0 | 32.548 | 30.651 | 187.172 | 7.65 | 175.826 | 2124.91 | 26.01 | 46.179 | 6.35 | 1.339 | 4.667 | 8436.21 | 1.965 | 97.8 | 77.7 | 1381 | 23.09 | 5483.5 | 1820.2 | 2292.5 | 2923.9 | 1195.9 | 0.61151 | 6.007
2024-12-09 | 17:17 | Data | 0 | 32.669 | 30.691 | 187.127 | 7.64 | 175.781 | 2124.91 | 26.01 | 46.269 | 6.35 | 1.345 | 4.65 | 8440.74 | 2.019 | 97.8 | 77.6 | 1382 | 23.13 | 5486.5 | 1822.2 | 2244.4 | 2901.4 | 1195.9 | 0.62555 | 5.994
2024-12-09 | 17:17 | Data | 0 | 32.838 | 30.651 | 186.991 | 7.64 | 175.826 | 2125.81 | 26 | 46.269 | 6.35 | 1.343 | 4.655 | 8440.74 | 1.911 | 97.8 | 77.6 | 1382 | 23.13 | 5486.5 | 1833.6 | 2264.2 | 2923.2 | 1195.9 | 0.62528 | 5.998
2024-12-09 | 17:18 | Data | 0 | 32.507 | 30.428 | 187.082 | 7.64 | 175.781 | 2122.2 | 25.99 | 46.269 | 6.35 | 1.348 | 4.667 | 8445.26 | 2.025 | 97.8 | 77.6 | 1379 | 23.09 | 5489.4 | 1809.9 | 2264.7 | 2911.5 | 1195.9 | 0.62493 | 6.016
2024-12-09 | 17:18 | Data | 0 | 32.669 | 30.651 | 186.991 | 7.64 | 175.826 | 2123.1 | 25.99 | 46.359 | 6.34 | 1.346 | 4.667 | 8440.74 | 1.863 | 97.8 | 77.6 | 1380 | 23.13 | 5486.5 | 1827.6 | 2310.6 | 2958.2 | 1195.9 | 0.61447 | 6.016
2024-12-09 | 17:18 | Data | 0 | 32.723 | 30.651 | 187.127 | 7.64 | 175.871 | 2123.1 | 26 | 46.179 | 6.35 | 1.357 | 4.683 | 8440.74 | 2.073 | 97.8 | 77.5 | 1380 | 23.13 | 5486.5 | 1824.5 | 2311.2 | 2956.3 | 1195.9 | 0.61434 | 6.04
2024-12-09 | 17:18 | Data | 0 | 32.696 | 30.759 | 187.082 | 7.64 | 175.781 | 2122.2 | 26 | 46.269 | 6.35 | 1.351 | 4.662 | 8436.21 | 2.079 | 97.8 | 77.5 | 1380 | 23.13 | 5483.5 | 1822.8 | 2332.6 | 2971.6 | 1195.9 | 0.61105 | 6.013
2024-12-09 | 17:18 | Data | 0 | 32.838 | 30.489 | 187.082 | 7.64 | 175.961 | 2123.1 | 26 | 46.179 | 6.35 | 1.355 | 4.638 | 8440.74 | 2.187 | 97.8 | 77.4 | 1380 | 23.09 | 5486.5 | 1807.1 | 2340.4 | 2970 | 1195.9 | 0.60624 | 5.993
2024-12-09 | 17:18 | Data | 0 | 32.413 | 30.421 | 187.127 | 7.64 | 175.826 | 2125.81 | 25.99 | 46.179 | 6.35 | 1.357 | 4.69 | 8431.69 | 1.971 | 97.8 | 77.6 | 1382 | 23.13 | 5480.6 | 1817.4 | 2327.5 | 2963 | 1195.9 | 0.60791 | 6.046
2024-12-09 | 17:18 | Data | 0 | 32.501 | 30.644 | 187.263 | 7.64 | 175.781 | 2125.81 | 26.01 | 46.179 | 6.35 | 1.357 | 4.711 | 8395.51 | 1.85 | 97.8 | 77.6 | 1382 | 23.04 | 5457.1 | 1813.8 | 2306.9 | 2945 | 1195.9 | 0.61171 | 6.068
2024-12-09 | 17:18 | Data | 0 | 32.892 | 30.928 | 187.263 | 7.64 | 175.961 | 2125.81 | 25.99 | 46.269 | 6.35 | 1.34 | 4.68 | 8400.04 | 2.059 | 97.8 | 77.8 | 1381 | 23.13 | 5460 | 1817.2 | 2267.1 | 2917 | 1195.9 | 0.62042 | 6.02
2024-12-09 | 17:18 | Data | 0 | 32.723 | 30.698 | 187.127 | 7.64 | 175.826 | 2125.81 | 25.99 | 46.359 | 6.35 | 1.338 | 4.666 | 8400.04 | 2.025 | 97.8 | 77.7 | 1382 | 23.09 | 5460 | 1817.1 | 2266.9 | 2909 | 1195.9 | 0.62067 | 6.003
2024-12-09 | 17:18 | Data | 0 | 32.804 | 30.975 | 187.172 | 7.65 | 175.826 | 2123.1 | 25.99 | 46.089 | 6.35 | 1.344 | 4.662 | 8395.51 | 1.958 | 97.8 | 77.6 | 1380 | 23.09 | 5457.1 | 1822.8 | 2257.1 | 2912.8 | 1195.9 | 0.62314 | 6.006
2024-12-09 | 17:18 | Data | 0 | 32.723 | 30.658 | 187.127 | 7.64 | 175.871 | 2123.1 | 25.99 | 46.269 | 6.35 | 1.344 | 4.654 | 8400.04 | 2.262 | 97.8 | 77.6 | 1379 | 23.13 | 5460 | 1817.3 | 2274.4 | 2921.5 | 1195.9 | 0.61884 | 5.998
2024-12-09 | 17:18 | Data | 0 | 32.892 | 30.766 | 187.127 | 7.64 | 175.916 | 2122.2 | 26 | 46.269 | 6.34 | 1.339 | 4.691 | 8404.56 | 2.005 | 97.8 | 77.8 | 1380 | 23.09 | 5463 | 1829.2 | 2309.1 | 2956.6 | 1195.9 | 0.61639 | 6.029
2024-12-09 | 17:18 | Data | 0 | 32.953 | 30.678 | 187.489 | 7.64 | 176.007 | 2121.29 | 25.99 | 46.269 | 6.35 | 1.348 | 4.666 | 8386.47 | 2.133 | 97.8 | 77.6 | 1379 | 23.13 | 5451.2 | 1824.5 | 2286.9 | 2918.7 | 1195.9 | 0.61736 | 6.015
2024-12-09 | 17:18 | Data | 0 | 32.514 | 30.415 | 187.082 | 7.64 | 175.871 | 2120.39 | 25.99 | 46.179 | 6.35 | 1.348 | 4.674 | 8395.51 | 2.073 | 97.8 | 77.6 | 1378 | 23.13 | 5457.1 | 1819.9 | 2291.6 | 2938.9 | 1195.9 | 0.61672 | 6.021
2024-12-09 | 17:18 | Data | 0 | 32.696 | 30.874 | 187.127 | 7.64 | 175.826 | 2120.39 | 25.99 | 46.179 | 6.35 | 1.346 | 4.665 | 8400.04 | 1.978 | 97.8 | 77.6 | 1379 | 23.09 | 5460 | 1827.6 | 2302.4 | 2952.1 | 1195.9 | 0.61587 | 6.012
2024-12-09 | 17:18 | Data | 0 | 32.521 | 30.651 | 187.353 | 7.64 | 175.961 | 2117.68 | 25.99 | 46.269 | 6.35 | 1.353 | 4.635 | 8400.04 | 1.857 | 97.8 | 77.4 | 1376 | 23.13 | 5460 | 1822.2 | 2328.5 | 2967.2 | 1195.9 | 0.6119 | 5.988
2024-12-09 | 17:18 | Data | 0 | 32.521 | 30.651 | 187.172 | 7.65 | 175.961 | 2121.29 | 25.99 | 46.179 | 6.35 | 1.342 | 4.671 | 8400.04 | 1.85 | 97.8 | 77.7 | 1378 | 23.09 | 5460 | 1802.9 | 2283.9 | 2920.3 | 1195.9 | 0.61521 | 6.014
2024-12-09 | 17:18 | Data | 0 | 32.602 | 30.529 | 187.443 | 7.64 | 175.871 | 2119.49 | 26 | 46.179 | 6.35 | 1.347 | 4.655 | 8386.47 | 2.032 | 97.8 | 77.6 | 1377 | 23.13 | 5451.2 | 1837 | 2258.6 | 2921.4 | 1195.9 | 0.62657 | 6.003
2024-12-09 | 17:19 | Data | 0 | 32.555 | 30.428 | 187.443 | 7.64 | 176.007 | 2120.39 | 25.99 | 46.179 | 6.35 | 1.344 | 4.676 | 8431.69 | 1.911 | 97.8 | 77.7 | 1378 | 23.09 | 5480.6 | 1820.2 | 2263.9 | 2919.2 | 1195.9 | 0.62355 | 6.02
2024-12-09 | 17:19 | Data | 0 | 32.528 | 30.536 | 187.263 | 7.64 | 176.007 | 2119.49 | 25.99 | 46.179 | 6.35 | 1.346 | 4.689 | 8436.21 | 2.079 | 97.8 | 77.7 | 1378 | 23.09 | 5483.5 | 1811.4 | 2266.6 | 2913 | 1195.9 | 0.61973 | 6.034
2024-12-09 | 17:19 | Data | 0 | 32.386 | 30.482 | 187.263 | 7.64 | 175.916 | 2119.49 | 25.99 | 46.269 | 6.35 | 1.349 | 4.686 | 8418.13 | 2.079 | 97.8 | 77.7 | 1379 | 23.18 | 5471.8 | 1806.7 | 2258.8 | 2905.1 | 1195.9 | 0.6196 | 6.035
2024-12-09 | 17:19 | Data | 0 | 32.723 | 30.455 | 187.353 | 7.64 | 176.052 | 2120.39 | 25.99 | 45.727 | 6.35 | 1.348 | 4.688 | 8431.69 | 2.066 | 97.8 | 77.7 | 1378 | 22.91 | 5480.6 | 1836.4 | 2261.5 | 2924.2 | 1195.9 | 0.62521 | 6.037
2024-12-09 | 17:19 | Data | 0 | 32.649 | 30.536 | 187.579 | 7.64 | 176.052 | 2121.29 | 25.99 | 46.269 | 6.35 | 1.352 | 4.668 | 8440.74 | 1.992 | 97.8 | 77.5 | 1378 | 23.13 | 5486.5 | 1830.5 | 2231.3 | 2898.5 | 1195.9 | 0.62865 | 6.02
2024-12-09 | 17:19 | Data | 0 | 32.696 | 30.651 | 187.172 | 7.64 | 175.916 | 2122.2 | 25.99 | 46.179 | 6.35 | 1.347 | 4.66 | 8467.87 | 2.066 | 97.8 | 77.6 | 1380 | 23.13 | 5504.1 | 1820.6 | 2284.3 | 2935.3 | 1195.9 | 0.61738 | 6.007
2024-12-09 | 17:19 | Data | 0 | 32.636 | 30.597 | 187.353 | 7.64 | 176.007 | 2117.68 | 25.99 | 46.269 | 6.35 | 1.348 | 4.657 | 8454.3 | 1.965 | 97.8 | 77.6 | 1376 | 23.13 | 5495.3 | 1799.2 | 2291.6 | 2925.8 | 1195.9 | 0.61243 | 6.007
2024-12-09 | 17:19 | Data | 0 | 32.48 | 30.529 | 187.263 | 7.64 | 176.007 | 2113.16 | 26 | 46.269 | 6.35 | 1.348 | 4.664 | 8454.3 | 2.019 | 97.8 | 77.6 | 1375 | 23.13 | 5495.3 | 1825.9 | 2328.2 | 2971.2 | 1195.9 | 0.61171 | 6.012
2024-12-09 | 17:19 | Data | 0 | 32.494 | 30.637 | 187.172 | 7.64 | 176.007 | 2117.68 | 25.99 | 46.269 | 6.35 | 1.342 | 4.689 | 8445.26 | 1.877 | 97.8 | 77.7 | 1376 | 23.09 | 5489.4 | 1822 | 2319.7 | 2960.9 | 1195.9 | 0.61249 | 6.032
2024-12-09 | 17:19 | Data | 0 | 32.717 | 30.442 | 187.353 | 7.64 | 176.052 | 2117.68 | 25.99 | 46.269 | 6.35 | 1.337 | 4.66 | 8458.83 | 2.073 | 97.8 | 77.7 | 1377 | 23.13 | 5498.2 | 1826.7 | 2296.5 | 2945.9 | 1195.9 | 0.61415 | 5.997
2024-12-09 | 17:19 | Data | 0 | 32.507 | 30.637 | 187.443 | 7.64 | 176.007 | 2119.49 | 25.99 | 46.179 | 6.35 | 1.343 | 4.664 | 8440.74 | 1.904 | 97.8 | 77.6 | 1378 | 23.18 | 5486.5 | 1820.6 | 2306.8 | 2956.2 | 1195.9 | 0.61448 | 6.007
2024-12-09 | 17:19 | Data | 0 | 32.717 | 30.82 | 187.217 | 7.64 | 175.916 | 2121.29 | 25.99 | 46.179 | 6.35 | 1.356 | 4.66 | 8436.21 | 1.958 | 97.8 | 77.5 | 1381 | 23.13 | 5483.5 | 1825.8 | 2248 | 2908.3 | 1195.9 | 0.62449 | 6.016
2024-12-09 | 17:19 | Data | 0 | 32.494 | 30.415 | 187.263 | 7.64 | 175.916 | 2122.2 | 25.99 | 46.269 | 6.35 | 1.356 | 4.698 | 8440.74 | 2.079 | 97.8 | 77.6 | 1380 | 23.09 | 5486.5 | 1841.3 | 2279.2 | 2940.5 | 1195.9 | 0.62341 | 6.054
2024-12-09 | 17:19 | Data | 0 | 32.764 | 30.563 | 187.217 | 7.64 | 176.052 | 2123.1 | 25.99 | 46.269 | 6.35 | 1.359 | 4.727 | 8445.26 | 2.208 | 97.8 | 77.7 | 1380 | 23.13 | 5489.4 | 1818.5 | 2276.8 | 2925.7 | 1195.9 | 0.61924 | 6.085
2024-12-09 | 17:19 | Data | 0 | 32.379 | 30.644 | 187.443 | 7.64 | 176.007 | 2122.2 | 25.99 | 46.269 | 6.35 | 1.348 | 4.692 | 8445.26 | 1.924 | 97.8 | 77.7 | 1380 | 23.13 | 5489.4 | 1809.1 | 2259 | 2904.9 | 1195.9 | 0.62079 | 6.041
2024-12-09 | 17:19 | Data | 0 | 32.71 | 30.651 | 187.353 | 7.64 | 175.916 | 2123.1 | 25.98 | 45.998 | 6.35 | 1.334 | 4.671 | 8445.26 | 2.073 | 97.8 | 77.8 | 1380 | 23 | 5489.4 | 1834.2 | 2276.4 | 2935.4 | 1195.9 | 0.6227 | 6.003
2024-12-09 | 17:19 | Data | 0 | 32.44 | 30.847 | 187.353 | 7.64 | 176.052 | 2122.2 | 25.99 | 45.998 | 6.35 | 1.349 | 4.673 | 8445.26 | 2.046 | 97.8 | 77.6 | 1380 | 23.04 | 5489.4 | 1801.3 | 2279.3 | 2917.9 | 1195.9 | 0.61765 | 6.023
2024-12-09 | 17:19 | Data | 0 | 32.649 | 30.752 | 187.398 | 7.64 | 175.961 | 2123.1 | 25.99 | 45.998 | 6.34 | 1.349 | 4.681 | 8445.26 | 2.046 | 97.8 | 77.6 | 1380 | 23 | 5489.4 | 1821.3 | 2303.1 | 2946.1 | 1195.9 | 0.61603 | 6.03
2024-12-09 | 17:20 | Data | 0 | 32.548 | 30.421 | 187.398 | 7.64 | 176.052 | 2125.81 | 25.99 | 45.998 | 6.35 | 1.341 | 4.665 | 8445.26 | 2.073 | 97.8 | 77.7 | 1382 | 23.04 | 5489.4 | 1817.1 | 2306.8 | 2947 | 1195.9 | 0.61467 | 6.005
2024-12-09 | 17:20 | Data | 0 | 32.507 | 30.428 | 187.263 | 7.64 | 175.916 | 2126.72 | 25.99 | 46.179 | 6.34 | 1.348 | 4.687 | 8458.83 | 2.059 | 97.8 | 77.7 | 1383 | 23.09 | 5498.2 | 1834.1 | 2320.1 | 2967.9 | 1195.9 | 0.61564 | 6.035
2024-12-09 | 17:20 | Data | 0 | 32.71 | 30.644 | 187.217 | 7.65 | 175.916 | 2123.1 | 25.98 | 45.998 | 6.35 | 1.342 | 4.694 | 8404.56 | 2.133 | 97.8 | 77.8 | 1380 | 22.95 | 5463 | 1817.1 | 2308.5 | 2948.6 | 1195.9 | 0.61369 | 6.037
2024-12-09 | 17:20 | Data | 0 | 32.723 | 30.651 | 187.353 | 7.64 | 176.007 | 2126.72 | 25.98 | 45.998 | 6.35 | 1.344 | 4.665 | 8409.08 | 2.066 | 97.8 | 77.6 | 1384 | 22.95 | 5465.9 | 1814.2 | 2291.5 | 2933.7 | 1195.9 | 0.61619 | 6.01
2024-12-09 | 17:20 | Data | 0 | 32.494 | 30.3 | 187.082 | 7.64 | 175.871 | 2128.52 | 25.99 | 45.908 | 6.35 | 1.344 | 4.66 | 8400.04 | 2.019 | 97.8 | 77.6 | 1384 | 23 | 5460 | 1848.4 | 2321.5 | 2958.3 | 1195.9 | 0.62029 | 6.004
2024-12-09 | 17:20 | Data | 0 | 32.987 | 30.462 | 187.263 | 7.64 | 175.916 | 2125.81 | 25.99 | 45.998 | 6.34 | 1.342 | 4.674 | 8409.08 | 2.154 | 97.8 | 77.7 | 1382 | 23 | 5465.9 | 1819.9 | 2270.5 | 2921.8 | 1195.9 | 0.61775 | 6.017
2024-12-09 | 17:20 | Data | 0 | 32.467 | 30.442 | 187.263 | 7.64 | 175.916 | 2126.72 | 25.99 | 45.998 | 6.35 | 1.349 | 4.683 | 8427.17 | 2.194 | 97.8 | 77.6 | 1382 | 23 | 5477.7 | 1810.9 | 2265.4 | 2913.1 | 1195.9 | 0.61971 | 6.031
2024-12-09 | 17:20 | Data | 0 | 32.615 | 30.421 | 187.263 | 7.64 | 176.007 | 2125.81 | 25.99 | 46.179 | 6.34 | 1.351 | 4.699 | 8422.65 | 2.1 | 97.8 | 77.7 | 1382 | 23.04 | 5474.7 | 2917.6 | 2831.4 | 4184.4 | 1195.9 | 0.68089 | 6.051
2024-12-09 | 17:20 | Data | 0 | 32.494 | 30.732 | 187.353 | 7.64 | 176.007 | 2127.62 | 25.99 | 45.908 | 6.35 | 1.349 | 4.672 | 8431.69 | 1.931 | 97.8 | 77.6 | 1383 | 22.95 | 5480.6 | 2917.8 | 2802.4 | 4161.5 | 1195.9 | 0.6845 | 6.021
2024-12-09 | 17:20 | Data | 0 | 32.561 | 30.334 | 187.263 | 7.64 | 175.916 | 2127.62 | 25.99 | 45.908 | 6.35 | 1.347 | 4.64 | 8436.21 | 2.255 | 97.8 | 77.5 | 1384 | 22.95 | 5483.5 | 2902.4 | 2830.6 | 4171.8 | 1195.9 | 0.67994 | 5.987
2024-12-09 | 17:20 | Data | 0 | 32.494 | 30.59 | 187.353 | 7.64 | 175.916 | 2126.72 | 25.99 | 45.998 | 6.35 | 1.347 | 4.689 | 8431.69 | 1.944 | 97.8 | 77.7 | 1384 | 23 | 5480.6 | 2909.5 | 2818.6 | 4163.1 | 1195.9 | 0.68205 | 6.036
2024-12-09 | 17:20 | Data | 0 | 32.494 | 30.644 | 187.353 | 7.64 | 175.961 | 2126.72 | 25.99 | 45.998 | 6.35 | 1.343 | 4.669 | 8458.83 | 2.052 | 97.8 | 77.6 | 1383 | 23.04 | 5498.2 | 2900.7 | 2818.8 | 4165.2 | 1195.9 | 0.67596 | 6.013
2024-12-09 | 17:20 | Data | 0 | 32.183 | 30.475 | 187.263 | 7.64 | 176.007 | 2125.81 | 25.98 | 45.998 | 6.34 | 1.345 | 4.648 | 8427.17 | 1.971 | 97.8 | 77.6 | 1382 | 23.04 | 5477.7 | 2901.8 | 2857.7 | 4190.3 | 1195.9 | 0.67547 | 5.993
2024-12-09 | 17:20 | Data | 0 | 32.595 | 30.415 | 187.263 | 7.64 | 175.961 | 2125.81 | 25.99 | 45.998 | 6.35 | 1.349 | 4.676 | 8427.17 | 2.106 | 97.8 | 77.6 | 1382 | 23.04 | 5477.7 | 2889.8 | 2868.5 | 4190.8 | 1195.9 | 0.67207 | 6.025
2024-12-09 | 17:20 | Data | 0 | 32.838 | 30.556 | 187.443 | 7.64 | 176.097 | 2121.29 | 25.98 | 46.089 | 6.35 | 1.349 | 4.691 | 8440.74 | 2.235 | 97.8 | 77.7 | 1379 | 22.95 | 5486.5 | 2900.9 | 2828.7 | 4166.8 | 1196 | 0.68076 | 6.04
2024-12-09 | 17:20 | Data | 0 | 32.399 | 30.415 | 187.353 | 7.64 | 176.007 | 2124.91 | 25.98 | 45.998 | 6.35 | 1.346 | 4.684 | 8427.17 | 1.911 | 97.8 | 77.7 | 1381 | 22.95 | 5477.7 | 2915.2 | 2847.8 | 4192.2 | 1196 | 0.67768 | 6.03
2024-12-09 | 17:20 | Data | 0 | 32.494 | 30.415 | 187.036 | 7.65 | 175.871 | 2128.52 | 25.97 | 45.998 | 6.35 | 1.352 | 4.674 | 8431.69 | 2.079 | 97.8 | 77.6 | 1384 | 23 | 5480.6 | 2907.4 | 2846.4 | 4186.1 | 1196 | 0.67824 | 6.026
2024-12-09 | 17:20 | Data | 0 | 32.271 | 30.502 | 187.217 | 7.64 | 175.826 | 2129.43 | 25.96 | 45.998 | 6.34 | 1.351 | 4.67 | 8458.83 | 1.796 | 97.8 | 77.6 | 1384 | 22.95 | 5498.2 | 2904 | 2811.6 | 4160.6 | 1196 | 0.68109 | 6.021
2024-12-09 | 17:21 | Data | 0 | 32.561 | 30.624 | 187.217 | 7.64 | 176.007 | 2131.24 | 25.97 | 45.998 | 6.35 | 1.352 | 4.672 | 8454.3 | 1.904 | 97.8 | 77.6 | 1385 | 23 | 5495.3 | 2901 | 2817.6 | 4163.8 | 1196 | 0.67912 | 6.024
2024-12-09 | 17:21 | Data | 0 | 32.723 | 30.543 | 187.217 | 7.64 | 175.871 | 2130.33 | 25.99 | 45.998 | 6.35 | 1.346 | 4.67 | 8454.3 | 2.282 | 97.8 | 77.6 | 1385 | 23 | 5495.3 | 2901.7 | 2823.3 | 4166.3 | 1196 | 0.67849 | 6.015
2024-12-09 | 17:21 | Data | 0 | 32.723 | 30.651 | 187.398 | 7.64 | 176.097 | 2133.95 | 25.98 | 45.998 | 6.35 | 1.344 | 4.679 | 8449.78 | 2.073 | 97.8 | 77.7 | 1386 | 23 | 5492.4 | 2897.6 | 2825.4 | 4164 | 1196 | 0.67884 | 6.023
2024-12-09 | 17:21 | Data | 0 | 32.501 | 30.529 | 187.353 | 7.64 | 175.916 | 2133.95 | 25.98 | 45.818 | 6.35 | 1.351 | 4.65 | 8440.74 | 1.965 | 97.8 | 77.5 | 1387 | 22.95 | 5486.5 | 2897.9 | 2856.3 | 4184.7 | 1196 | 0.6756 | 6.001
2024-12-09 | 17:21 | Data | 0 | 32.494 | 30.536 | 187.172 | 7.64 | 175.961 | 2136.66 | 25.97 | 45.998 | 6.35 | 1.348 | 4.675 | 8445.26 | 2.079 | 97.9 | 77.6 | 1389 | 22.95 | 5489.4 | 2902.4 | 2867.1 | 4201.4 | 1196 | 0.67387 | 6.024
2024-12-09 | 17:21 | Data | 0 | 32.487 | 30.415 | 187.172 | 7.64 | 175.916 | 2136.66 | 25.98 | 46.089 | 6.35 | 1.341 | 4.672 | 8436.21 | 2.079 | 97.8 | 77.7 | 1389 | 23.09 | 5483.5 | 2908.4 | 2873 | 4205 | 1196 | 0.67407 | 6.013
2024-12-09 | 17:21 | Data | 0 | 32.723 | 30.489 | 187.489 | 7.64 | 176.097 | 2140.27 | 25.96 | 45.998 | 6.34 | 1.345 | 4.694 | 8440.74 | 2.167 | 97.8 | 77.7 | 1391 | 22.95 | 5486.5 | 2927.3 | 2844.7 | 4192.7 | 1196 | 0.68146 | 6.037
2024-12-09 | 17:21 | Data | 0 | 32.494 | 30.597 | 187.217 | 7.64 | 175.916 | 2138.47 | 25.97 | 45.998 | 6.35 | 1.344 | 4.679 | 8454.3 | 1.944 | 97.8 | 77.7 | 1390 | 23 | 5495.3 | 2905.7 | 2814 | 4161.7 | 1196 | 0.68076 | 6.024
2024-12-09 | 17:21 | Data | 0 | 32.73 | 30.556 | 187.353 | 7.64 | 176.052 | 2139.37 | 25.98 | 45.818 | 6.35 | 1.341 | 4.693 | 8472.39 | 1.755 | 97.9 | 77.8 | 1391 | 22.95 | 5507.1 | 2893.1 | 2807.9 | 4152.2 | 1196 | 0.68201 | 6.034
2024-12-09 | 17:21 | Data | 0 | 32.413 | 30.536 | 187.398 | 7.64 | 175.961 | 2139.37 | 25.98 | 45.908 | 6.35 | 1.336 | 4.683 | 8472.39 | 1.749 | 97.9 | 77.8 | 1390 | 23 | 5507.1 | 2905.6 | 2788 | 4153 | 1196 | 0.68429 | 6.02
2024-12-09 | 17:21 | Data | 0 | 32.447 | 30.759 | 187.353 | 7.64 | 176.052 | 2139.37 | 25.98 | 45.998 | 6.35 | 1.332 | 4.637 | 8467.87 | 1.958 | 97.9 | 77.7 | 1391 | 22.95 | 5504.1 | 2894.5 | 2800.2 | 4158.6 | 1196 | 0.68061 | 5.97
2024-12-09 | 17:21 | Data | 0 | 32.501 | 30.442 | 187.263 | 7.64 | 175.871 | 2142.08 | 25.97 | 45.998 | 6.35 | 1.341 | 4.662 | 8454.3 | 2.025 | 97.9 | 77.7 | 1392 | 23 | 5495.3 | 2910 | 2804.2 | 4160.8 | 1196 | 0.68394 | 6.003
2024-12-09 | 17:21 | Data | 0 | 32.723 | 30.489 | 187.489 | 7.64 | 176.007 | 2142.08 | 25.97 | 45.908 | 6.35 | 1.342 | 4.665 | 8436.21 | 2.052 | 97.9 | 77.7 | 1392 | 23 | 5483.5 | 2897.3 | 2809.4 | 4153.8 | 1196 | 0.68119 | 6.008
2024-12-09 | 17:21 | Data | 0 | 32.764 | 30.252 | 187.172 | 7.64 | 175.916 | 2142.99 | 25.98 | 45.998 | 6.35 | 1.349 | 4.684 | 8427.17 | 2.106 | 97.9 | 77.6 | 1392 | 22.95 | 5477.7 | 2899.7 | 2810.8 | 4157.2 | 1196 | 0.68249 | 6.033
2024-12-09 | 17:21 | Data | 0 | 32.555 | 30.421 | 187.263 | 7.64 | 176.052 | 2142.99 | 25.98 | 45.998 | 6.35 | 1.346 | 4.679 | 8431.69 | 1.917 | 97.9 | 77.7 | 1392 | 22.95 | 5480.6 | 2915.3 | 2821.5 | 4173.6 | 1196 | 0.68132 | 6.024
2024-12-09 | 17:21 | Data | 0 | 32.649 | 30.637 | 187.353 | 7.64 | 176.007 | 2142.08 | 25.98 | 45.998 | 6.35 | 1.347 | 4.681 | 8449.78 | 2.093 | 97.9 | 77.6 | 1392 | 22.95 | 5492.4 | 2889.9 | 2828.8 | 4163.1 | 1196 | 0.67678 | 6.027
2024-12-09 | 17:21 | Data | 0 | 32.75 | 30.482 | 187.398 | 7.64 | 176.097 | 2142.99 | 25.97 | 45.998 | 6.35 | 1.352 | 4.665 | 8467.87 | 1.931 | 97.9 | 77.5 | 1393 | 23 | 5504.1 | 2902.5 | 2832.9 | 4174.1 | 1196 | 0.67684 | 6.017
2024-12-09 | 17:22 | Data | 0 | 32.663 | 30.914 | 187.534 | 7.64 | 176.052 | 2142.99 | 25.98 | 46.089 | 6.35 | 1.346 | 4.694 | 8454.3 | 1.87 | 97.9 | 77.7 | 1392 | 23 | 5495.3 | 2912.5 | 2825.2 | 4172.6 | 1196 | 0.68041 | 6.039
2024-12-09 | 17:22 | Data | 0 | 32.777 | 30.651 | 187.217 | 7.64 | 175.916 | 2142.08 | 25.97 | 45.908 | 6.35 | 1.352 | 4.691 | 8458.83 | 1.965 | 97.9 | 77.6 | 1392 | 23 | 5498.2 | 2895.3 | 2827.6 | 4166.1 | 1196 | 0.67841 | 6.043
2024-12-09 | 17:22 | Data | 0 | 32.494 | 30.442 | 187.217 | 7.64 | 175.916 | 2135.76 | 25.97 | 45.998 | 6.35 | 1.349 | 4.67 | 8843.21 | 2.174 | 97.8 | 77.6 | 1389 | 23 | 5748.1 | 2896.7 | 2835 | 4175.5 | 1196 | 0.67662 | 6.021
2024-12-09 | 17:22 | Data | 0 | 32.521 | 30.428 | 187.353 | 7.64 | 175.961 | 2136.66 | 25.97 | 46.089 | 6.35 | 1.353 | 4.642 | 8870.35 | 2.039 | 97.9 | 77.4 | 1389 | 22.95 | 5765.7 | 2890.7 | 2838.3 | 4167.4 | 1196 | 0.67804 | 5.996
2024-12-09 | 17:22 | Data | 0 | 32.723 | 30.536 | 187.263 | 7.64 | 176.052 | 2133.95 | 25.97 | 45.998 | 6.35 | 1.349 | 4.707 | 8879.39 | 1.897 | 97.8 | 77.7 | 1388 | 22.95 | 5771.6 | 2906.7 | 2827.3 | 4170.6 | 1196 | 0.68024 | 6.058
2024-12-09 | 17:22 | Data | 0 | 32.561 | 30.536 | 187.353 | 7.64 | 176.007 | 2133.95 | 25.98 | 45.998 | 6.35 | 1.348 | 4.685 | 8476.91 | 1.884 | 97.8 | 77.7 | 1387 | 23 | 5510 | 2909.3 | 2824.7 | 4169.8 | 1196 | 0.68289 | 6.033
2024-12-09 | 17:22 | Data | 0 | 32.467 | 30.624 | 187.443 | 7.64 | 176.052 | 2022.78 | 25.97 | 45.998 | 6.35 | 1.342 | 4.67 | 8431.69 | 2.059 | 97.7 | 77.7 | 1315 | 23 | 5480.6 | 2922.3 | 2824.6 | 4178.5 | 1196 | 0.6836 | 6.013
2024-12-09 | 17:22 | Data | 0 | 32.669 | 30.421 | 187.263 | 7.64 | 175.961 | 2127.62 | 25.97 | 45.998 | 6.34 | 1.353 | 4.703 | 8440.74 | 2.181 | 97.8 | 77.7 | 1383 | 23 | 5486.5 | 2908.2 | 2802.5 | 4156.1 | 1196 | 0.6829 | 6.056
2024-12-09 | 17:22 | Data | 0 | 32.271 | 30.205 | 187.263 | 7.64 | 175.961 | 2129.43 | 25.98 | 45.998 | 6.34 | 1.343 | 4.679 | 8445.26 | 2.248 | 97.8 | 77.7 | 1384 | 23 | 5489.4 | 2895.3 | 2810.6 | 4157.8 | 1196 | 0.68017 | 6.019
2024-12-09 | 17:22 | Data | 0 | 32.555 | 30.543 | 187.443 | 7.64 | 176.007 | 2123.1 | 25.99 | 45.998 | 6.35 | 1.347 | 4.671 | 8440.74 | 1.958 | 97.8 | 77.6 | 1380 | 23 | 5486.5 | 2893.1 | 2789.2 | 4138.9 | 1196 | 0.68145 | 6.017
2024-12-09 | 17:22 | Data | 0 | 32.696 | 30.469 | 187.263 | 7.64 | 175.961 | 2125.81 | 25.98 | 46.179 | 6.35 | 1.358 | 4.68 | 8436.21 | 2.066 | 97.8 | 77.5 | 1381 | 23.09 | 5483.5 | 2904.6 | 2782.7 | 4143.1 | 1196 | 0.68479 | 6.037
2024-12-09 | 17:22 | Data | 0 | 32.494 | 30.502 | 187.172 | 7.64 | 176.007 | 2125.81 | 25.97 | 45.998 | 6.35 | 1.339 | 4.664 | 8440.74 | 2.187 | 97.8 | 77.7 | 1381 | 23 | 5486.5 | 2907 | 2814.4 | 4161.7 | 1196 | 0.68174 | 6.002
2024-12-09 | 17:22 | Data | 0 | 32.669 | 30.469 | 187.172 | 7.64 | 176.052 | 2125.81 | 25.98 | 45.908 | 6.34 | 1.352 | 4.66 | 8436.21 | 2.066 | 97.8 | 77.5 | 1382 | 23 | 5483.5 | 2886.8 | 2807.4 | 4143 | 1196 | 0.67959 | 6.014
2024-12-09 | 17:22 | Data | 0 | 32.494 | 30.415 | 187.217 | 7.64 | 175.961 | 2125.81 | 25.98 | 45.908 | 6.35 | 1.345 | 4.692 | 8436.21 | 2.079 | 97.8 | 77.7 | 1382 | 22.95 | 5483.5 | 2886 | 2840.2 | 4165.1 | 1196 | 0.67683 | 6.036
2024-12-09 | 17:22 | Data | 0 | 32.723 | 30.529 | 187.217 | 7.64 | 176.007 | 2124.91 | 25.98 | 45.998 | 6.35 | 1.343 | 4.688 | 8436.21 | 2.019 | 97.8 | 77.7 | 1381 | 23 | 5483.5 | 2925.1 | 2807.7 | 4166.7 | 1196 | 0.68548 | 6.031
2024-12-09 | 17:22 | Data | 0 | 32.487 | 30.415 | 187.353 | 7.64 | 176.052 | 2122.2 | 25.98 | 45.908 | 6.34 | 1.353 | 4.683 | 8454.3 | 2.282 | 97.8 | 77.6 | 1379 | 23 | 5495.3 | 2893.7 | 2804 | 4153.9 | 1196.1 | 0.68004 | 6.035
2024-12-09 | 17:22 | Data | 0 | 32.933 | 30.651 | 187.443 | 7.64 | 176.097 | 2124.01 | 25.97 | 45.998 | 6.35 | 1.354 | 4.66 | 8458.83 | 1.985 | 97.8 | 77.5 | 1381 | 23 | 5498.2 | 2894.3 | 2795.1 | 4143.9 | 1196.1 | 0.68146 | 6.014
2024-12-09 | 17:22 | Data | 0 | 32.48 | 30.637 | 187.398 | 7.64 | 176.052 | 2123.1 | 25.99 | 45.908 | 6.35 | 1.359 | 4.671 | 8463.35 | 2.012 | 97.8 | 77.5 | 1380 | 22.95 | 5501.2 | 2892.6 | 2823.9 | 4158.6 | 1196.1 | 0.67789 | 6.031
2024-12-09 | 17:23 | Data | 0 | 32.777 | 30.421 | 187.489 | 7.64 | 176.187 | 2123.1 | 25.97 | 45.998 | 6.35 | 1.355 | 4.635 | 8458.83 | 2.079 | 97.8 | 77.4 | 1380 | 23.04 | 5498.2 | 2892.1 | 2800.8 | 4151.8 | 1196.1 | 0.68083 | 5.99
2024-12-09 | 17:23 | Data | 0 | 32.696 | 30.705 | 187.489 | 7.64 | 176.097 | 2124.91 | 25.98 | 45.998 | 6.35 | 1.351 | 4.664 | 8454.3 | 2.187 | 97.8 | 77.5 | 1381 | 23 | 5495.3 | 2893.5 | 2816.1 | 4158.5 | 1196.1 | 0.68088 | 6.017
2024-12-09 | 17:23 | Data | 0 | 32.717 | 30.651 | 187.398 | 7.64 | 176.097 | 2125.81 | 25.97 | 45.908 | 6.35 | 1.339 | 4.692 | 8440.74 | 2.073 | 97.8 | 77.8 | 1382 | 22.95 | 5486.5 | 2878.9 | 2807.2 | 4137.9 | 1196.1 | 0.68044 | 6.031
2024-12-09 | 17:23 | Data | 0 | 32.609 | 30.874 | 187.67 | 7.64 | 176.187 | 2124.91 | 25.98 | 45.998 | 6.35 | 1.349 | 4.685 | 8440.74 | 1.978 | 97.8 | 77.6 | 1382 | 22.95 | 5486.5 | 2896.1 | 2813.5 | 4154.5 | 1196.1 | 0.68391 | 6.036
2024-12-09 | 17:23 | Data | 0 | 32.622 | 30.59 | 187.398 | 7.64 | 176.142 | 2125.81 | 25.97 | 45.818 | 6.34 | 1.359 | 4.687 | 8454.3 | 2.133 | 97.8 | 77.5 | 1382 | 23.04 | 5495.3 | 2893.4 | 2802.1 | 4144 | 1196.1 | 0.68237 | 6.047
2024-12-09 | 17:23 | Data | 0 | 32.494 | 30.415 | 187.353 | 7.64 | 176.097 | 2124.91 | 25.98 | 45.998 | 6.35 | 1.346 | 4.707 | 8445.26 | 2.079 | 97.8 | 77.8 | 1381 | 22.95 | 5489.4 | 2918.5 | 2823.2 | 4175.2 | 1196.1 | 0.68202 | 6.054
2024-12-09 | 17:23 | Data | 0 | 32.494 | 30.806 | 187.398 | 7.64 | 176.142 | 2125.81 | 25.98 | 45.908 | 6.34 | 1.34 | 4.706 | 8454.3 | 1.877 | 97.8 | 77.8 | 1382 | 23 | 5495.3 | 2896.7 | 2813.9 | 4154.6 | 1196.1 | 0.68023 | 6.046
2024-12-09 | 17:23 | Data | 0 | 32.609 | 30.678 | 187.443 | 7.64 | 176.097 | 2125.81 | 25.97 | 45.998 | 6.35 | 1.346 | 4.694 | 8458.83 | 2.113 | 97.8 | 77.7 | 1382 | 23 | 5498.2 | 2895.2 | 2810 | 4157.2 | 1196.1 | 0.67941 | 6.04
2024-12-09 | 17:23 | Data | 0 | 32.494 | 30.637 | 187.353 | 7.64 | 176.052 | 2124.01 | 25.98 | 45.998 | 6.35 | 1.342 | 4.698 | 8445.26 | 1.904 | 97.8 | 77.8 | 1381 | 23 | 5489.4 | 2900.2 | 2806.6 | 4155.1 | 1196.1 | 0.68096 | 6.041
2024-12-09 | 17:23 | Data | 0 | 32.723 | 30.482 | 187.489 | 7.64 | 176.233 | 2124.91 | 25.98 | 45.908 | 6.35 | 1.345 | 4.702 | 8454.3 | 2.046 | 97.8 | 77.8 | 1381 | 23 | 5495.3 | 2908.2 | 2801.2 | 4150.6 | 1196.1 | 0.68152 | 6.045
2024-12-09 | 17:23 | Data | 0 | 32.507 | 30.651 | 187.443 | 7.64 | 176.097 | 2121.29 | 25.98 | 45.998 | 6.35 | 1.347 | 4.697 | 8454.3 | 1.85 | 97.8 | 77.7 | 1378 | 23 | 5495.3 | 2892.4 | 2823.5 | 4159.9 | 1196.1 | 0.6781 | 6.042
2024-12-09 | 17:23 | Data | 0 | 32.183 | 30.637 | 187.217 | 7.64 | 176.142 | 2121.29 | 25.98 | 45.998 | 6.35 | 1.361 | 4.687 | 8440.74 | 2.073 | 97.8 | 77.5 | 1379 | 23 | 5486.5 | 2900.5 | 2810.4 | 4161.3 | 1196.1 | 0.682 | 6.046
2024-12-09 | 17:23 | Data | 0 | 32.44 | 30.59 | 187.489 | 7.64 | 176.097 | 2127.62 | 25.98 | 45.998 | 6.35 | 1.341 | 4.692 | 8445.26 | 2.113 | 97.8 | 77.8 | 1382 | 23 | 5489.4 | 2899.1 | 2826 | 4166.1 | 1196.1 | 0.67818 | 6.033
2024-12-09 | 17:23 | Data | 0 | 32.291 | 30.502 | 187.353 | 7.64 | 176.142 | 2127.62 | 25.97 | 45.998 | 6.35 | 1.337 | 4.673 | 8440.74 | 2.073 | 97.8 | 77.7 | 1383 | 23.04 | 5486.5 | 2904.1 | 2809 | 4157.4 | 1196.1 | 0.68032 | 6.011
2024-12-09 | 17:23 | Data | 0 | 32.595 | 30.415 | 187.398 | 7.64 | 176.052 | 2128.52 | 25.99 | 45.908 | 6.35 | 1.355 | 4.671 | 8458.83 | 2.181 | 97.8 | 77.5 | 1383 | 22.95 | 5498.2 | 2884.1 | 2834.5 | 4166.6 | 1196.1 | 0.67715 | 6.026
2024-12-09 | 17:23 | Data | 0 | 32.494 | 30.475 | 187.443 | 7.64 | 176.097 | 2127.62 | 25.98 | 45.998 | 6.34 | 1.347 | 4.685 | 8445.26 | 2.052 | 97.8 | 77.7 | 1383 | 23 | 5489.4 | 2895 | 2818.4 | 4157.2 | 1196.1 | 0.67995 | 6.032
2024-12-09 | 17:23 | Data | 0 | 32.804 | 30.874 | 187.624 | 7.64 | 176.187 | 2132.14 | 25.98 | 45.998 | 6.35 | 1.342 | 4.674 | 8454.3 | 2.127 | 97.8 | 77.7 | 1385 | 22.95 | 5495.3 | 2907.6 | 2819.9 | 4165.3 | 1196.1 | 0.68168 | 6.017
2024-12-09 | 17:24 | Data | 0 | 32.393 | 30.219 | 187.398 | 7.64 | 176.187 | 2128.52 | 25.97 | 45.998 | 6.35 | 1.339 | 4.664 | 8458.83 | 2.019 | 97.8 | 77.7 | 1384 | 22.95 | 5498.2 | 2885.9 | 2808.1 | 4145.7 | 1196.1 | 0.67939 | 6.004
2024-12-09 | 17:24 | Data | 0 | 32.636 | 30.442 | 187.443 | 7.64 | 176.142 | 2128.52 | 25.98 | 45.998 | 6.35 | 1.352 | 4.691 | 8431.69 | 1.985 | 97.8 | 77.6 | 1384 | 23 | 5480.6 | 2902.2 | 2828.2 | 4169.4 | 1196.1 | 0.67994 | 6.042
2024-12-09 | 17:24 | Data | 0 | 32.291 | 30.327 | 187.398 | 7.64 | 176.007 | 2127.62 | 25.97 | 45.998 | 6.34 | 1.365 | 4.659 | 8467.87 | 1.978 | 97.8 | 77.3 | 1383 | 23 | 5504.1 | 2919.1 | 2811.8 | 4168.8 | 1196.1 | 0.68426 | 6.025
2024-12-09 | 17:24 | Data | 0 | 32.717 | 30.82 | 187.353 | 7.64 | 176.052 | 2123.1 | 25.98 | 45.998 | 6.35 | 1.348 | 4.647 | 8445.26 | 2.079 | 97.8 | 77.5 | 1380 | 22.95 | 5489.4 | 2905 | 2829.4 | 4171.3 | 1196.1 | 0.67968 | 5.995
2024-12-09 | 17:24 | Data | 0 | 32.494 | 30.415 | 187.353 | 7.64 | 176.097 | 2127.62 | 25.98 | 45.908 | 6.35 | 1.349 | 4.675 | 8440.74 | 2.079 | 97.8 | 77.6 | 1384 | 22.95 | 5486.5 | 2904.3 | 2823 | 4164.5 | 1196.1 | 0.67968 | 6.027
2024-12-09 | 17:24 | Data | 0 | 32.494 | 30.415 | 187.398 | 7.64 | 176.007 | 2128.52 | 25.98 | 45.998 | 6.35 | 1.345 | 4.677 | 8440.74 | 2.079 | 97.8 | 77.7 | 1383 | 23 | 5486.5 | 2912.1 | 2816.2 | 4169.8 | 1196.1 | 0.68179 | 6.024
2024-12-09 | 17:24 | Data | 0 | 32.561 | 30.421 | 187.489 | 7.64 | 176.187 | 2128.52 | 25.98 | 46.089 | 6.35 | 1.348 | 4.682 | 8440.74 | 2.079 | 97.8 | 77.6 | 1384 | 23.04 | 5486.5 | 2897.9 | 2802.1 | 4152.3 | 1196.1 | 0.68003 | 6.03
2024-12-09 | 17:24 | Data | 0 | 32.723 | 30.651 | 187.353 | 7.64 | 176.097 | 2129.43 | 25.97 | 45.998 | 6.35 | 1.346 | 4.666 | 8431.69 | 2.1 | 97.8 | 77.6 | 1384 | 23 | 5480.6 | 2911.4 | 2826 | 4171.8 | 1196.1 | 0.68101 | 6.012
2024-12-09 | 17:24 | Data | 0 | 32.514 | 30.448 | 187.398 | 7.64 | 176.187 | 2125.81 | 25.97 | 45.998 | 6.35 | 1.341 | 4.677 | 8445.26 | 2.025 | 97.8 | 77.7 | 1382 | 23 | 5489.4 | 2902.9 | 2821.8 | 4169.7 | 1196.1 | 0.67703 | 6.017
2024-12-09 | 17:24 | Data | 0 | 32.696 | 30.84 | 187.534 | 7.64 | 176.142 | 2120.39 | 25.98 | 46.45 | 6.35 | 1.354 | 4.684 | 8467.87 | 1.924 | 97.8 | 77.6 | 1378 | 23.22 | 5504.1 | 2927.3 | 2820.2 | 4183.4 | 1196.1 | 0.68195 | 6.039
2024-12-09 | 17:24 | Data | 0 | 32.663 | 30.847 | 187.534 | 7.64 | 176.142 | 2124.91 | 25.97 | 45.998 | 6.35 | 1.349 | 4.664 | 8454.3 | 1.965 | 97.8 | 77.5 | 1382 | 22.95 | 5495.3 | 2889.6 | 2824.7 | 4160.2 | 1196.1 | 0.67767 | 6.016
2024-12-09 | 17:24 | Data | 0 | 32.447 | 30.644 | 187.489 | 7.64 | 176.052 | 2126.72 | 25.98 | 45.908 | 6.34 | 1.339 | 4.67 | 8440.74 | 2.019 | 97.8 | 77.7 | 1382 | 23 | 5486.5 | 2907.1 | 2801 | 4154.7 | 1196.1 | 0.68408 | 6.01
2024-12-09 | 17:24 | Data | 0 | 32.696 | 30.475 | 187.534 | 7.64 | 176.142 | 2124.01 | 25.97 | 45.998 | 6.35 | 1.344 | 4.672 | 8445.26 | 2.187 | 97.8 | 77.7 | 1381 | 23 | 5489.4 | 2896.2 | 2818.9 | 4162 | 1196.1 | 0.6791 | 6.015
2024-12-09 | 17:24 | Data | 0 | 32.825 | 30.853 | 187.489 | 7.64 | 176.142 | 2123.1 | 25.97 | 45.998 | 6.35 | 1.355 | 4.707 | 8427.17 | 2.086 | 97.8 | 77.6 | 1380 | 23 | 5477.7 | 2892.4 | 2809.6 | 4152.8 | 1196.1 | 0.67981 | 6.063
2024-12-09 | 17:24 | Data | 0 | 32.838 | 30.921 | 187.624 | 7.64 | 176.233 | 2124.01 | 25.99 | 45.998 | 6.35 | 1.349 | 4.714 | 8427.17 | 2.019 | 97.8 | 77.7 | 1381 | 22.91 | 5477.7 | 2901.2 | 2827.8 | 4168.9 | 1196.1 | 0.67999 | 6.064
2024-12-09 | 17:24 | Data | 0 | 32.494 | 30.563 | 187.489 | 7.64 | 176.097 | 2123.1 | 25.97 | 45.998 | 6.35 | 1.355 | 4.679 | 8431.69 | 2.194 | 97.8 | 77.6 | 1379 | 23 | 5480.6 | 2901.1 | 2832.9 | 4169 | 1196.1 | 0.68081 | 6.033
2024-12-09 | 17:24 | Data | 0 | 32.507 | 30.637 | 187.489 | 7.65 | 176.142 | 2123.1 | 25.98 | 45.818 | 6.35 | 1.357 | 4.673 | 8440.74 | 1.877 | 97.8 | 77.5 | 1379 | 23 | 5486.5 | 2902.2 | 2831.5 | 4168.3 | 1196.1 | 0.67964 | 6.029
2024-12-09 | 17:24 | Data | 0 | 32.501 | 30.415 | 187.398 | 7.64 | 176.007 | 2122.2 | 25.97 | 45.908 | 6.34 | 1.353 | 4.687 | 8409.08 | 2.073 | 97.8 | 77.6 | 1379 | 22.95 | 5465.9 | 2900.6 | 2833.3 | 4170.7 | 1196.2 | 0.67749 | 6.043
2024-12-09 | 17:25 | Data | 0 | 32.926 | 30.556 | 187.489 | 7.64 | 176.233 | 2122.2 | 25.99 | 46.179 | 6.35 | 1.355 | 4.673 | 8427.17 | 2.106 | 97.8 | 77.5 | 1379 | 23 | 5477.7 | 2895.4 | 2841.8 | 4173.8 | 1196.2 | 0.6761 | 6.029
2024-12-09 | 17:25 | Data | 0 | 32.723 | 30.442 | 187.489 | 7.64 | 176.142 | 2122.2 | 25.98 | 45.998 | 6.35 | 1.357 | 4.685 | 8418.13 | 2.167 | 97.8 | 77.5 | 1380 | 23.04 | 5471.8 | 2901.2 | 2814 | 4158.6 | 1196.2 | 0.6812 | 6.042
2024-12-09 | 17:25 | Data | 0 | 32.494 | 30.415 | 187.398 | 7.64 | 176.142 | 2122.2 | 25.98 | 45.366 | 6.35 | 1.346 | 4.694 | 8422.65 | 2.079 | 97.9 | 77.7 | 1379 | 22.73 | 5474.7 | 2917.3 | 2800.5 | 4162.9 | 1196.2 | 0.68416 | 6.039
2024-12-09 | 17:25 | Data | 0 | 32.717 | 30.543 | 187.398 | 7.65 | 176.097 | 2123.1 | 25.98 | 45.908 | 6.34 | 1.341 | 4.686 | 8418.13 | 2.093 | 97.8 | 77.7 | 1380 | 22.95 | 5471.8 | 2899 | 2799.7 | 4147.3 | 1196.2 | 0.68319 | 6.026
2024-12-09 | 17:25 | Data | 0 | 32.494 | 30.624 | 187.443 | 7.64 | 176.142 | 2122.2 | 25.99 | 45.908 | 6.35 | 1.348 | 4.683 | 8409.08 | 2.046 | 97.8 | 77.6 | 1379 | 22.95 | 5465.9 | 2897.6 | 2814.4 | 4158.6 | 1196.2 | 0.68014 | 6.032
2024-12-09 | 17:25 | Data | 0 | 32.663 | 30.637 | 187.534 | 7.64 | 176.052 | 2122.2 | 25.98 | 45.998 | 6.35 | 1.358 | 4.693 | 8395.51 | 2.086 | 97.8 | 77.6 | 1379 | 23 | 5457.1 | 2905.4 | 2812.7 | 4144.3 | 1196.2 | 0.67979 | 6.053
2024-12-09 | 17:25 | Data | 0 | 32.501 | 30.442 | 187.534 | 7.64 | 176.097 | 2121.29 | 25.99 | 45.908 | 6.35 | 1.353 | 4.701 | 8422.65 | 1.971 | 97.8 | 77.7 | 1378 | 22.91 | 5474.7 | 2908.2 | 2797.5 | 4152 | 1196.2 | 0.68379 | 6.054
2024-12-09 | 17:25 | Data | 0 | 32.669 | 30.766 | 187.534 | 7.64 | 176.097 | 2120.39 | 25.98 | 45.998 | 6.36 | 1.344 | 4.656 | 8440.74 | 2.059 | 97.8 | 77.6 | 1377 | 23.04 | 5486.5 | 2906.3 | 2810.6 | 4157.8 | 1196.2 | 0.68287 | 6.002
2024-12-09 | 17:25 | Data | 0 | 32.609 | 30.853 | 187.398 | 7.64 | 176.097 | 2117.68 | 25.98 | 46.089 | 6.35 | 1.338 | 4.667 | 8445.26 | 1.904 | 97.8 | 77.7 | 1376 | 22.95 | 5489.4 | 2906.8 | 2786.5 | 4144.5 | 1196.2 | 0.68429 | 6.004
2024-12-09 | 17:25 | Data | 0 | 32.609 | 30.631 | 187.398 | 7.64 | 176.097 | 2114.06 | 25.96 | 45.998 | 6.35 | 1.337 | 4.683 | 8445.26 | 2.079 | 97.8 | 77.8 | 1375 | 23 | 5489.4 | 2900.5 | 2818.8 | 4165.6 | 1196.2 | 0.68048 | 6.019
2024-12-09 | 17:25 | Data | 0 | 32.71 | 30.651 | 187.489 | 7.64 | 176.052 | 2116.78 | 25.98 | 45.908 | 6.35 | 1.334 | 4.677 | 8440.74 | 2.073 | 97.8 | 77.8 | 1376 | 22.95 | 5486.5 | 2906.1 | 2826.6 | 4172.1 | 1196.2 | 0.67987 | 6.01
2024-12-09 | 17:25 | Data | 0 | 32.696 | 30.651 | 187.579 | 7.64 | 176.142 | 2119.49 | 25.98 | 45.818 | 6.35 | 1.355 | 4.676 | 8431.69 | 2.181 | 97.8 | 77.6 | 1378 | 22.86 | 5480.6 | 2893.7 | 2825.1 | 4163.9 | 1196.2 | 0.67754 | 6.031
2024-12-09 | 17:25 | Data | 0 | 32.717 | 30.597 | 187.443 | 7.64 | 176.187 | 2120.39 | 25.97 | 45.998 | 6.35 | 1.352 | 4.684 | 8454.3 | 2.295 | 97.8 | 77.6 | 1378 | 23 | 5495.3 | 2898.9 | 2813.7 | 4152.7 | 1196.2 | 0.68202 | 6.036
2024-12-09 | 17:25 | Data | 0 | 32.676 | 30.644 | 187.398 | 7.64 | 176.187 | 2123.1 | 25.98 | 45.908 | 6.35 | 1.349 | 4.702 | 8449.78 | 2.073 | 97.8 | 77.7 | 1379 | 23 | 5492.4 | 2903.2 | 2818.8 | 4167.2 | 1196.2 | 0.67972 | 6.053
2024-12-09 | 17:25 | Data | 0 | 32.501 | 30.759 | 187.489 | 7.64 | 176.142 | 2121.29 | 25.97 | 46.089 | 6.35 | 1.348 | 4.683 | 8449.78 | 1.87 | 97.8 | 77.6 | 1378 | 23 | 5492.4 | 2883.7 | 2820.5 | 4156.4 | 1196.2 | 0.67642 | 6.032
2024-12-09 | 17:25 | Data | 0 | 32.784 | 30.428 | 187.624 | 7.64 | 176.187 | 2123.1 | 25.97 | 46.179 | 6.35 | 1.348 | 4.679 | 8454.3 | 1.985 | 97.8 | 77.6 | 1380 | 23.13 | 5495.3 | 2875 | 2816.7 | 4158.5 | 1196.2 | 0.67568 | 6.03
2024-12-09 | 17:25 | Data | 0 | 32.521 | 31.177 | 187.579 | 7.64 | 176.142 | 2122.2 | 25.98 | 45.908 | 6.35 | 1.352 | 4.69 | 8449.78 | 1.985 | 97.8 | 77.6 | 1380 | 22.95 | 5492.4 | 2920.3 | 2828.5 | 4183 | 1196.2 | 0.68209 | 6.042
2024-12-09 | 17:25 | Data | 0 | 32.501 | 30.651 | 187.534 | 7.64 | 176.142 | 2123.1 | 25.98 | 45.998 | 6.35 | 1.343 | 4.687 | 8467.87 | 1.958 | 97.8 | 77.7 | 1380 | 23 | 5504.1 | 2909.9 | 2830 | 4174.6 | 1196.2 | 0.68017 | 6.031
2024-12-09 | 17:26 | Data | 0 | 32.561 | 30.624 | 187.489 | 7.64 | 176.142 | 2123.1 | 25.98 | 45.908 | 6.35 | 1.341 | 4.684 | 8467.87 | 1.904 | 97.8 | 77.7 | 1380 | 22.95 | 5504.1 | 2889.9 | 2801.3 | 4142.5 | 1196.2 | 0.67975 | 6.025
2024-12-09 | 17:26 | Data | 0 | 32.399 | 30.624 | 187.398 | 7.64 | 176.142 | 2123.1 | 25.97 | 45.998 | 6.35 | 1.345 | 4.693 | 8427.17 | 1.816 | 97.8 | 77.7 | 1380 | 22.95 | 5477.7 | 2889.7 | 2806.7 | 4147.6 | 1196.2 | 0.67991 | 6.038
2024-12-09 | 17:26 | Data | 0 | 32.717 | 30.651 | 187.489 | 7.64 | 176.097 | 2124.01 | 25.98 | 45.998 | 6.35 | 1.354 | 4.689 | 8400.04 | 2.073 | 97.8 | 77.6 | 1381 | 23 | 5460 | 2905 | 2824.6 | 4165.4 | 1196.2 | 0.68092 | 6.043
2024-12-09 | 17:26 | Data | 0 | 32.885 | 30.766 | 187.443 | 7.64 | 176.187 | 2123.1 | 25.98 | 45.998 | 6.35 | 1.349 | 4.703 | 8395.51 | 1.897 | 97.8 | 77.7 | 1380 | 23 | 5457.1 | 2919.2 | 2848.9 | 4196.6 | 1196.2 | 0.67863 | 6.053
2024-12-09 | 17:26 | Data | 0 | 32.271 | 30.415 | 187.534 | 7.64 | 176.142 | 2122.2 | 25.98 | 45.998 | 6.35 | 1.349 | 4.693 | 8390.99 | 2.025 | 97.8 | 77.7 | 1380 | 23 | 5454.1 | 2909.2 | 2812 | 4159.8 | 1196.2 | 0.68278 | 6.042
2024-12-09 | 17:26 | Data | 0 | 32.609 | 30.421 | 187.534 | 7.64 | 176.187 | 2123.1 | 25.97 | 45.908 | 6.35 | 1.352 | 4.653 | 8404.56 | 2.127 | 97.8 | 77.5 | 1380 | 22.95 | 5463 | 2902.9 | 2823.3 | 4169.6 | 1196.2 | 0.67919 | 6.005
2024-12-09 | 17:26 | Data | 0 | 32.73 | 30.442 | 187.579 | 7.64 | 176.142 | 2122.2 | 25.98 | 46.179 | 6.35 | 1.347 | 4.671 | 8386.47 | 2.025 | 97.8 | 77.6 | 1379 | 23.09 | 5451.2 | 2908.1 | 2825.5 | 4165.9 | 1196.2 | 0.6817 | 6.017
2024-12-09 | 17:26 | Data | 0 | 32.642 | 30.658 | 187.579 | 7.64 | 176.187 | 2120.39 | 25.98 | 45.998 | 6.35 | 1.349 | 4.67 | 8400.04 | 1.863 | 97.8 | 77.6 | 1379 | 22.91 | 5460 | 2893 | 2823.8 | 4162.4 | 1196.2 | 0.67883 | 6.019
2024-12-09 | 17:26 | Data | 0 | 32.764 | 30.651 | 187.579 | 7.64 | 176.097 | 2124.01 | 25.98 | 45.998 | 6.35 | 1.351 | 4.659 | 8418.13 | 1.877 | 97.8 | 77.5 | 1379 | 23.04 | 5471.8 | 2905.1 | 2835.7 | 4177.5 | 1196.2 | 0.67844 | 6.01
2024-12-09 | 17:26 | Data | 0 | 32.325 | 30.415 | 187.398 | 7.64 | 176.097 | 2126.72 | 25.97 | 45.998 | 6.35 | 1.349 | 4.683 | 8427.17 | 2.073 | 97.8 | 77.6 | 1381 | 22.95 | 5477.7 | 2887.6 | 2850.7 | 4174.1 | 1196.2 | 0.67575 | 6.031
2024-12-09 | 17:26 | Data | 0 | 32.568 | 30.421 | 187.579 | 7.64 | 176.233 | 2125.81 | 25.97 | 46.089 | 6.35 | 1.339 | 4.691 | 8422.65 | 1.978 | 97.8 | 77.8 | 1381 | 23 | 5474.7 | 2903 | 2832.7 | 4175 | 1196.2 | 0.67675 | 6.028
2024-12-09 | 17:26 | Data | 0 | 32.494 | 30.624 | 187.624 | 7.64 | 176.097 | 2128.52 | 25.99 | 45.998 | 6.35 | 1.348 | 4.673 | 8427.17 | 2.059 | 97.8 | 77.6 | 1383 | 23 | 5477.7 | 2924.6 | 2836.8 | 4189.6 | 1196.2 | 0.68126 | 6.021
2024-12-09 | 17:26 | Data | 0 | 32.501 | 30.475 | 187.398 | 7.64 | 176.142 | 2127.62 | 25.98 | 46.179 | 6.35 | 1.348 | 4.681 | 8431.69 | 2.14 | 97.8 | 77.6 | 1383 | 23.04 | 5480.6 | 2911.1 | 2823.1 | 4171.9 | 1196.2 | 0.68071 | 6.031
2024-12-09 | 17:26 | Data | 0 | 32.636 | 30.442 | 187.579 | 7.64 | 176.187 | 2127.62 | 25.98 | 45.998 | 6.34 | 1.358 | 4.698 | 8404.56 | 1.938 | 97.8 | 77.6 | 1383 | 23 | 5463 | 2915.5 | 2804.6 | 4158.5 | 1196.2 | 0.68502 | 6.055
2024-12-09 | 17:26 | Data | 0 | 32.723 | 30.597 | 187.489 | 7.64 | 176.097 | 2127.62 | 25.98 | 45.998 | 6.35 | 1.357 | 4.695 | 8400.04 | 2.174 | 97.8 | 77.6 | 1383 | 23 | 5460 | 2903 | 2798.1 | 4152.4 | 1196.2 | 0.68141 | 6.054
2024-12-09 | 17:26 | Data | 0 | 32.278 | 30.536 | 187.443 | 7.64 | 176.187 | 2129.43 | 25.97 | 46.269 | 6.35 | 1.356 | 4.697 | 8418.13 | 2.167 | 97.8 | 77.6 | 1384 | 23.18 | 5471.8 | 2901.9 | 2826 | 4166.3 | 1196.2 | 0.67891 | 6.053
2024-12-09 | 17:26 | Data | 0 | 32.892 | 30.678 | 187.489 | 7.64 | 176.142 | 2131.24 | 25.97 | 46.359 | 6.35 | 1.357 | 4.702 | 8418.13 | 2.059 | 97.8 | 77.6 | 1385 | 23.13 | 5471.8 | 2903.7 | 2847.7 | 4181.5 | 1196.2 | 0.67675 | 6.055
2024-12-09 | 17:26 | Data | 0 | 33.088 | 30.671 | 187.624 | 7.64 | 176.233 | 2130.33 | 25.98 | 45.908 | 6.35 | 1.347 | 4.705 | 8431.69 | 2.268 | 97.8 | 77.7 | 1385 | 22.95 | 5480.6 | 2890.7 | 2833.6 | 4168.2 | 1196.2 | 0.67606 | 6.052
2024-12-09 | 17:27 | Data | 0 | 32.838 | 30.948 | 187.67 | 7.64 | 176.233 | 2126.72 | 25.99 | 46.179 | 6.35 | 1.344 | 4.693 | 8445.26 | 2.025 | 97.8 | 77.7 | 1382 | 23.09 | 5489.4 | 2907.9 | 2847.7 | 4184.2 | 1196.3 | 0.67888 | 6.039
2024-12-09 | 17:27 | Data | 0 | 32.494 | 30.543 | 187.579 | 7.64 | 176.142 | 2128.52 | 25.98 | 45.998 | 6.35 | 1.348 | 4.674 | 8431.69 | 2.052 | 97.8 | 77.6 | 1384 | 23 | 5480.6 | 2897.6 | 2831.3 | 4170.5 | 1196.3 | 0.67901 | 6.023
2024-12-09 | 17:27 | Data | 0 | 32.696 | 30.766 | 187.579 | 7.64 | 176.233 | 2129.43 | 25.97 | 46.089 | 6.35 | 1.345 | 4.672 | 8427.17 | 2.066 | 97.8 | 77.6 | 1384 | 23 | 5477.7 | 2908.1 | 2815.2 | 4165.9 | 1196.3 | 0.67983 | 6.016
2024-12-09 | 17:27 | Data | 0 | 32.71 | 30.624 | 187.353 | 7.64 | 176.097 | 2128.52 | 25.98 | 46.089 | 6.35 | 1.337 | 4.683 | 8436.21 | 2.127 | 97.8 | 77.8 | 1384 | 23 | 5483.5 | 2882.2 | 2805.2 | 4141.9 | 1196.3 | 0.67938 | 6.02
2024-12-09 | 17:27 | Data | 0 | 32.777 | 30.853 | 187.67 | 7.64 | 176.233 | 2128.52 | 25.97 | 45.998 | 6.35 | 1.346 | 4.673 | 8463.35 | 1.877 | 97.8 | 77.6 | 1383 | 23 | 5501.2 | 2907.7 | 2825.8 | 4172.7 | 1196.3 | 0.68052 | 6.019
2024-12-09 | 17:27 | Data | 0 | 32.609 | 30.786 | 187.624 | 7.64 | 176.233 | 2127.62 | 25.98 | 45.998 | 6.35 | 1.356 | 4.67 | 8454.3 | 2.187 | 97.8 | 77.5 | 1383 | 23 | 5495.3 | 2902.3 | 2809.5 | 4160 | 1196.3 | 0.68204 | 6.026
2024-12-09 | 17:27 | Data | 0 | 32.723 | 30.536 | 187.624 | 7.64 | 176.233 | 2128.52 | 25.98 | 45.908 | 6.35 | 1.356 | 4.664 | 8472.39 | 2.066 | 97.8 | 77.5 | 1384 | 22.95 | 5507.1 | 2887.9 | 2799.7 | 4143.6 | 1196.3 | 0.68027 | 6.019
2024-12-09 | 17:27 | Data | 0 | 32.723 | 30.651 | 187.579 | 7.64 | 176.097 | 2128.52 | 25.98 | 45.908 | 6.35 | 1.344 | 4.701 | 8458.83 | 1.985 | 97.8 | 77.8 | 1384 | 23.04 | 5498.2 | 2900.2 | 2802.7 | 4154.8 | 1196.3 | 0.68046 | 6.044
2024-12-09 | 17:27 | Data | 0 | 32.494 | 30.644 | 187.489 | 7.64 | 176.142 | 2128.52 | 25.98 | 46.089 | 6.35 | 1.34 | 4.677 | 8467.87 | 2.052 | 97.8 | 77.7 | 1384 | 23 | 5504.1 | 2903.2 | 2815 | 4168 | 1196.3 | 0.6817 | 6.017
2024-12-09 | 17:27 | Data | 0 | 32.548 | 30.421 | 187.489 | 7.64 | 176.142 | 2127.62 | 25.98 | 45.998 | 6.34 | 1.344 | 4.66 | 8463.35 | 2.086 | 97.8 | 77.6 | 1383 | 23 | 5501.2 | 2923.8 | 2821 | 4180.1 | 1196.3 | 0.68275 | 6.003
2024-12-09 | 17:27 | Data | 0 | 32.771 | 30.874 | 187.579 | 7.64 | 176.233 | 2127.62 | 25.98 | 45.908 | 6.35 | 1.353 | 4.668 | 8454.3 | 1.857 | 97.8 | 77.5 | 1383 | 23 | 5495.3 | 2908.9 | 2820.4 | 4171.4 | 1196.3 | 0.68096 | 6.022
2024-12-09 | 17:27 | Data | 0 | 32.717 | 30.624 | 187.489 | 7.64 | 176.187 | 2127.62 | 25.98 | 45.908 | 6.35 | 1.346 | 4.669 | 8449.78 | 2.012 | 97.8 | 77.6 | 1384 | 22.95 | 5492.4 | 2912.2 | 2841.3 | 4172.3 | 1196.3 | 0.67875 | 6.015
2024-12-09 | 17:27 | Data | 0 | 32.94 | 30.766 | 187.579 | 7.64 | 176.278 | 2127.62 | 25.97 | 45.908 | 6.35 | 1.343 | 4.675 | 8467.87 | 2.073 | 97.8 | 77.7 | 1384 | 22.95 | 5504.1 | 2899.8 | 2818.8 | 4161.8 | 1196.3 | 0.67908 | 6.019
2024-12-09 | 17:27 | Data | 0 | 32.534 | 30.637 | 187.624 | 7.64 | 176.187 | 2128.52 | 25.98 | 45.998 | 6.35 | 1.343 | 4.68 | 8454.3 | 1.877 | 97.8 | 77.7 | 1383 | 22.95 | 5495.3 | 2898.8 | 2826 | 4169.4 | 1196.3 | 0.6778 | 6.023
2024-12-09 | 17:27 | Data | 0 | 32.494 | 30.624 | 187.579 | 7.64 | 176.142 | 2128.52 | 25.97 | 45.908 | 6.35 | 1.345 | 4.665 | 8454.3 | 2.019 | 97.8 | 77.6 | 1384 | 22.95 | 5495.3 | 2897.5 | 2823.6 | 4164.8 | 1196.3 | 0.67852 | 6.01
2024-12-09 | 17:27 | Data | 0 | 32.501 | 30.644 | 187.398 | 7.64 | 176.097 | 2127.62 | 25.97 | 45.998 | 6.35 | 1.346 | 4.704 | 8445.26 | 1.87 | 97.8 | 77.8 | 1383 | 23 | 5489.4 | 2884.6 | 2810.3 | 4153 | 1196.3 | 0.67804 | 6.05
2024-12-09 | 17:27 | Data | 0 | 32.865 | 30.887 | 187.624 | 7.64 | 176.278 | 2124.01 | 25.98 | 45.998 | 6.35 | 1.349 | 4.694 | 8454.3 | 2.302 | 97.8 | 77.7 | 1380 | 23 | 5495.3 | 2898.4 | 2817.3 | 4164.7 | 1196.3 | 0.68164 | 6.044
2024-12-09 | 17:28 | Data | 0 | 32.919 | 30.907 | 187.534 | 7.64 | 176.187 | 2127.62 | 25.99 | 46.089 | 6.35 | 1.356 | 4.693 | 8445.26 | 2.039 | 97.8 | 77.6 | 1384 | 23 | 5489.4 | 2905.6 | 2813 | 4162 | 1196.3 | 0.68184 | 6.049
2024-12-09 | 17:28 | Data | 0 | 33.156 | 30.793 | 187.715 | 7.64 | 176.323 | 2127.62 | 25.98 | 45.908 | 6.35 | 1.355 | 4.668 | 8454.3 | 1.931 | 97.8 | 77.5 | 1383 | 22.95 | 5495.3 | 2890.8 | 2823 | 4162 | 1196.3 | 0.67816 | 6.022
2024-12-09 | 17:28 | Data | 0 | 32.609 | 30.482 | 187.579 | 7.64 | 176.187 | 2125.81 | 25.96 | 46.089 | 6.35 | 1.354 | 4.656 | 8418.13 | 2.295 | 97.8 | 77.5 | 1381 | 23 | 5471.8 | 2924 | 2805.5 | 4160.5 | 1196.3 | 0.6818 | 6.009
2024-12-09 | 17:28 | Data | 0 | 32.636 | 30.421 | 187.624 | 7.64 | 176.233 | 2124.01 | 25.98 | 45.998 | 6.35 | 1.347 | 4.658 | 8440.74 | 2.079 | 97.8 | 77.6 | 1382 | 23 | 5486.5 | 2925.6 | 2817.4 | 4179.2 | 1196.3 | 0.68372 | 6.005
2024-12-09 | 17:28 | Data | 0 | 32.885 | 31.036 | 187.579 | 7.64 | 176.187 | 2128.52 | 25.98 | 45.998 | 6.35 | 1.349 | 4.677 | 8431.69 | 2.14 | 97.8 | 77.6 | 1383 | 23 | 5480.6 | 2919.2 | 2810.9 | 4169.4 | 1196.3 | 0.68297 | 6.026
2024-12-09 | 17:28 | Data | 0 | 32.636 | 30.853 | 187.443 | 7.64 | 176.187 | 2127.62 | 25.98 | 45.908 | 6.36 | 1.353 | 4.664 | 8431.69 | 1.938 | 97.8 | 77.5 | 1383 | 22.95 | 5480.6 | 2927.2 | 2830.9 | 4192.1 | 1196.3 | 0.68077 | 6.017
2024-12-09 | 17:28 | Data | 0 | 32.588 | 30.739 | 187.579 | 7.64 | 176.187 | 2128.52 | 25.98 | 45.908 | 6.34 | 1.342 | 4.643 | 8418.13 | 2.14 | 97.8 | 77.6 | 1384 | 23 | 5471.8 | 2912.1 | 2838.3 | 4190.3 | 1196.3 | 0.67785 | 5.986
2024-12-09 | 17:28 | Data | 0 | 32.609 | 30.86 | 187.579 | 7.64 | 176.233 | 2125.81 | 25.97 | 45.998 | 6.35 | 1.334 | 4.665 | 8395.51 | 2.073 | 97.8 | 77.8 | 1382 | 22.95 | 5457.1 | 2913.5 | 2810.6 | 4169.8 | 1196.3 | 0.68128 | 6.001
2024-12-09 | 17:28 | Data | 0 | 32.636 | 30.867 | 187.534 | 7.64 | 176.187 | 2126.72 | 25.97 | 45.998 | 6.35 | 1.346 | 4.671 | 8404.56 | 1.971 | 97.8 | 77.6 | 1382 | 23 | 5463 | 2932.7 | 2815.1 | 4180.3 | 1196.3 | 0.68541 | 6.017
2024-12-09 | 17:28 | Data | 0 | 33.061 | 30.442 | 187.624 | 7.64 | 176.323 | 2125.81 | 25.98 | 46.089 | 6.35 | 1.351 | 4.667 | 8400.04 | 2.133 | 97.8 | 77.6 | 1382 | 23 | 5460 | 2931.3 | 2798.5 | 4164.2 | 1196.3 | 0.68794 | 6.017
2024-12-09 | 17:28 | Data | 0 | 32.879 | 31.076 | 187.76 | 7.64 | 176.368 | 2125.81 | 25.98 | 45.998 | 6.35 | 1.347 | 4.666 | 8404.56 | 2.073 | 97.8 | 77.6 | 1382 | 22.95 | 5463 | 2944.1 | 2826.5 | 4200.2 | 1196.3 | 0.68504 | 6.012
2024-12-09 | 17:28 | Data | 0 | 32.609 | 30.651 | 187.579 | 7.64 | 176.187 | 2122.2 | 25.99 | 45.908 | 6.34 | 1.357 | 4.675 | 8436.21 | 1.857 | 97.8 | 77.5 | 1380 | 22.91 | 5483.5 | 2939.7 | 2794.8 | 4175.7 | 1196.3 | 0.68664 | 6.032
2024-12-09 | 17:28 | Data | 0 | 32.602 | 30.867 | 187.534 | 7.64 | 176.187 | 2122.2 | 25.98 | 45.998 | 6.35 | 1.358 | 4.692 | 8418.13 | 2.012 | 97.8 | 77.6 | 1379 | 23 | 5471.8 | 2930.9 | 2811.2 | 4178.9 | 1196.3 | 0.68466 | 6.049
2024-12-09 | 17:28 | Data | 0 | 32.507 | 30.678 | 187.624 | 7.64 | 176.323 | 2124.01 | 25.98 | 46.089 | 6.35 | 1.344 | 4.692 | 8404.56 | 2.167 | 97.8 | 77.7 | 1379 | 23 | 5463 | 2925.9 | 2810 | 4178.2 | 1196.3 | 0.68265 | 6.038
2024-12-09 | 17:28 | Data | 0 | 32.838 | 30.921 | 187.715 | 7.64 | 176.278 | 2123.1 | 25.97 | 45.998 | 6.35 | 1.345 | 4.666 | 8418.13 | 2.147 | 97.8 | 77.6 | 1380 | 23.04 | 5471.8 | 2927.3 | 2837.3 | 4196.6 | 1196.3 | 0.68223 | 6.011
2024-12-09 | 17:28 | Data | 0 | 32.453 | 30.536 | 187.624 | 7.64 | 176.278 | 2123.1 | 25.98 | 45.637 | 6.35 | 1.348 | 4.687 | 8418.13 | 1.749 | 97.8 | 77.7 | 1379 | 22.86 | 5471.8 | 2934.3 | 2809.8 | 4181.3 | 1196.3 | 0.68531 | 6.036
2024-12-09 | 17:28 | Data | 0 | 32.723 | 30.651 | 187.534 | 7.64 | 176.142 | 2122.2 | 25.97 | 45.908 | 6.35 | 1.345 | 4.686 | 8400.04 | 2.073 | 97.8 | 77.7 | 1379 | 22.95 | 5460 | 2921.8 | 2844.7 | 4195.9 | 1196.3 | 0.67807 | 6.031
2024-12-09 | 17:28 | Data | 0 | 33.048 | 30.435 | 187.67 | 7.64 | 176.233 | 2122.2 | 25.98 | 45.908 | 6.35 | 1.345 | 4.689 | 8404.56 | 2.093 | 97.8 | 77.7 | 1379 | 22.95 | 5463 | 2909.4 | 2845.1 | 4187.4 | 1196.3 | 0.67778 | 6.034
2024-12-09 | 17:29 | Data | 0 | 32.501 | 30.536 | 187.489 | 7.64 | 176.187 | 2123.1 | 25.98 | 45.908 | 6.34 | 1.351 | 4.685 | 8395.51 | 1.958 | 97.8 | 77.6 | 1380 | 23 | 5457.1 | 2918.9 | 2831.7 | 4188.3 | 1196.3 | 0.67798 | 6.036
2024-12-09 | 17:29 | Data | 0 | 32.494 | 30.55 | 187.624 | 7.64 | 176.187 | 2122.2 | 25.98 | 45.998 | 6.35 | 1.348 | 4.641 | 8390.99 | 2.12 | 97.8 | 77.5 | 1380 | 22.95 | 5454.1 | 2934.1 | 2841.1 | 4201.8 | 1196.4 | 0.68156 | 5.989
2024-12-09 | 17:29 | Data | 0 | 32.528 | 30.793 | 187.489 | 7.64 | 176.187 | 2123.1 | 25.98 | 45.908 | 6.35 | 1.341 | 4.654 | 8390.99 | 1.985 | 97.8 | 77.7 | 1379 | 23 | 5454.1 | 2923.5 | 2815.7 | 4176.3 | 1196.4 | 0.68342 | 5.994
2024-12-09 | 17:29 | Data | 0 | 33.081 | 30.934 | 187.67 | 7.64 | 176.233 | 2123.1 | 25.98 | 45.998 | 6.35 | 1.347 | 4.691 | 8386.47 | 2.235 | 97.8 | 77.7 | 1379 | 22.95 | 5451.2 | 2941.1 | 2815.7 | 4188.6 | 1196.4 | 0.68499 | 6.038
2024-12-09 | 17:29 | Data | 0 | 32.487 | 30.59 | 187.489 | 7.64 | 176.052 | 2123.1 | 25.97 | 45.998 | 6.35 | 1.343 | 4.666 | 8368.38 | 2.194 | 97.8 | 77.6 | 1380 | 23 | 5439.4 | 2944.3 | 2843.5 | 4214 | 1196.4 | 0.68119 | 6.008
2024-12-09 | 17:29 | Data | 0 | 32.325 | 30.415 | 187.443 | 7.64 | 176.187 | 2123.1 | 25.98 | 45.818 | 6.35 | 1.347 | 4.67 | 8390.99 | 1.884 | 97.8 | 77.6 | 1380 | 22.95 | 5454.1 | 2917 | 2842.7 | 4193.1 | 1196.4 | 0.68155 | 6.016
2024-12-09 | 17:29 | Data | 0 | 32.636 | 30.739 | 187.443 | 7.64 | 176.142 | 2123.1 | 25.98 | 45.998 | 6.35 | 1.346 | 4.679 | 8390.99 | 2.127 | 97.8 | 77.7 | 1379 | 23 | 5454.1 | 2936.3 | 2845 | 4208 | 1196.4 | 0.67954 | 6.025
2024-12-09 | 17:29 | Data | 0 | 32.696 | 30.59 | 187.398 | 7.64 | 176.142 | 2122.2 | 25.98 | 45.998 | 6.35 | 1.345 | 4.634 | 8404.56 | 2.133 | 97.8 | 77.5 | 1380 | 22.95 | 5463 | 2922.9 | 2860.3 | 4209.2 | 1196.4 | 0.6772 | 5.977
2024-12-09 | 17:29 | Data | 0 | 32.494 | 30.86 | 187.534 | 7.64 | 176.187 | 2123.1 | 25.98 | 45.908 | 6.35 | 1.348 | 4.655 | 8418.13 | 1.863 | 97.8 | 77.5 | 1380 | 23 | 5471.8 | 2935.2 | 2867.1 | 4224.1 | 1196.4 | 0.67657 | 6.002
2024-12-09 | 17:29 | Data | 0 | 32.636 | 30.523 | 187.534 | 7.64 | 176.233 | 2124.01 | 25.98 | 45.998 | 6.35 | 1.344 | 4.675 | 8400.04 | 1.904 | 97.8 | 77.7 | 1381 | 23 | 5460 | 2951.7 | 2820.2 | 4204.1 | 1196.4 | 0.68384 | 6.019
2024-12-09 | 17:29 | Data | 0 | 32.615 | 30.651 | 187.624 | 7.64 | 176.187 | 2127.62 | 25.98 | 45.908 | 6.35 | 1.354 | 4.657 | 8436.21 | 1.897 | 97.8 | 77.5 | 1383 | 23 | 5483.5 | 2848.7 | 2821.7 | 4124.6 | 1196.4 | 0.67574 | 6.011
2024-12-09 | 17:29 | Data | 0 | 32.507 | 30.475 | 187.443 | 7.64 | 176.142 | 2124.01 | 25.98 | 45.998 | 6.35 | 1.355 | 4.647 | 8422.65 | 1.965 | 97.8 | 77.4 | 1381 | 23 | 5474.7 | 2834.8 | 2801.2 | 4102.1 | 1196.4 | 0.67561 | 6.003
2024-12-09 | 17:29 | Data | 0 | 32.885 | 30.928 | 187.579 | 7.64 | 176.323 | 2120.39 | 25.99 | 45.908 | 6.35 | 1.348 | 4.67 | 8431.69 | 2.079 | 97.8 | 77.6 | 1378 | 22.95 | 5480.6 | 2873.4 | 2804 | 4134.1 | 1196.4 | 0.67831 | 6.019
2024-12-09 | 17:29 | Data | 0 | 32.777 | 30.536 | 187.489 | 7.64 | 176.233 | 2121.29 | 25.98 | 45.998 | 6.35 | 1.348 | 4.68 | 8386.47 | 2.059 | 97.8 | 77.6 | 1378 | 22.95 | 5451.2 | 2832.6 | 2794.7 | 4098.2 | 1196.4 | 0.67403 | 6.028
2024-12-09 | 17:29 | Data | 0 | 32.885 | 30.88 | 187.624 | 7.64 | 176.187 | 2124.01 | 25.97 | 45.998 | 6.35 | 1.358 | 4.664 | 8381.95 | 2.16 | 97.8 | 77.4 | 1380 | 23 | 5448.3 | 2871.2 | 2789.4 | 4114.3 | 1196.4 | 0.68343 | 6.021
2024-12-09 | 17:29 | Data | 0 | 32.568 | 30.651 | 187.489 | 7.64 | 176.187 | 2123.1 | 25.98 | 45.998 | 6.35 | 1.352 | 4.679 | 8404.56 | 1.85 | 97.8 | 77.6 | 1380 | 23 | 5463 | 2861 | 2797.9 | 4114.9 | 1196.4 | 0.67884 | 6.031
2024-12-09 | 17:29 | Data | 0 | 32.919 | 30.664 | 187.534 | 7.64 | 176.187 | 2120.39 | 25.99 | 45.998 | 6.35 | 1.342 | 4.688 | 8400.04 | 2.066 | 97.8 | 77.7 | 1378 | 23 | 5460 | 2861.2 | 2784.7 | 4108.7 | 1196.4 | 0.6809 | 6.031
2024-12-09 | 17:29 | Data | 0 | 32.501 | 30.529 | 187.398 | 7.64 | 176.142 | 2122.2 | 25.98 | 45.908 | 6.35 | 1.342 | 4.687 | 8458.83 | 2.14 | 97.8 | 77.7 | 1379 | 23 | 5498.2 | 2868.4 | 2788.4 | 4111.2 | 1196.4 | 0.68282 | 6.029
2024-12-09 | 17:30 | Data | 0 | 32.602 | 30.428 | 187.443 | 7.64 | 176.142 | 2120.39 | 25.97 | 45.908 | 6.35 | 1.345 | 4.682 | 8458.83 | 2.079 | 97.8 | 77.7 | 1378 | 22.95 | 5498.2 | 2904.2 | 2824.8 | 4169.4 | 1196.4 | 0.68127 | 6.027
2024-12-09 | 17:30 | Data | 0 | 32.892 | 30.921 | 187.489 | 7.64 | 176.278 | 2122.2 | 25.98 | 45.998 | 6.35 | 1.342 | 4.667 | 8454.3 | 2.073 | 97.8 | 77.7 | 1380 | 22.95 | 5495.3 | 2909.8 | 2801.1 | 4157.5 | 1196.4 | 0.68322 | 6.009
2024-12-09 | 17:30 | Data | 0 | 32.723 | 30.502 | 187.624 | 7.64 | 176.278 | 2120.39 | 25.98 | 45.908 | 6.36 | 1.342 | 4.685 | 8467.87 | 1.85 | 97.8 | 77.7 | 1378 | 22.95 | 5504.1 | 2929.3 | 2816.3 | 4180.8 | 1196.4 | 0.68192 | 6.026
2024-12-09 | 17:30 | Data | 0 | 32.48 | 30.415 | 187.443 | 7.64 | 176.142 | 2122.2 | 25.98 | 45.998 | 6.35 | 1.344 | 4.691 | 8436.21 | 2.073 | 97.8 | 77.7 | 1380 | 23 | 5483.5 | 2925.9 | 2809.4 | 4174.5 | 1196.4 | 0.68384 | 6.036
2024-12-09 | 17:30 | Data | 0 | 32.507 | 30.597 | 187.443 | 7.64 | 176.097 | 2123.1 | 25.97 | 45.818 | 6.35 | 1.354 | 4.693 | 8436.21 | 1.897 | 97.8 | 77.6 | 1380 | 22.91 | 5483.5 | 2920 | 2785.2 | 4153.4 | 1196.4 | 0.68588 | 6.048
2024-12-09 | 17:30 | Data | 0 | 32.453 | 30.644 | 187.398 | 7.64 | 176.097 | 2123.1 | 25.97 | 45.908 | 6.35 | 1.355 | 4.683 | 8449.78 | 2.14 | 97.8 | 77.6 | 1380 | 23.04 | 5492.4 | 2909.1 | 2815.8 | 4166.8 | 1196.4 | 0.68254 | 6.036
2024-12-09 | 17:30 | Data | 0 | 32.332 | 30.415 | 187.489 | 7.64 | 176.052 | 2122.2 | 25.98 | 45.908 | 6.35 | 1.348 | 4.673 | 8431.69 | 1.971 | 97.8 | 77.6 | 1380 | 22.95 | 5480.6 | 2894.6 | 2818.4 | 4158.9 | 1196.4 | 0.68006 | 6.022
2024-12-09 | 17:30 | Data | 0 | 32.669 | 30.84 | 187.443 | 7.64 | 176.097 | 2123.1 | 25.98 | 45.818 | 6.35 | 1.344 | 4.676 | 8467.87 | 1.992 | 97.8 | 77.7 | 1379 | 22.95 | 5504.1 | 2896.1 | 2806.7 | 4151.8 | 1196.4 | 0.68075 | 6.021
2024-12-09 | 17:30 | Data | 0 | 32.696 | 30.691 | 187.534 | 7.64 | 176.142 | 2122.2 | 25.98 | 45.998 | 6.35 | 1.354 | 4.673 | 8454.3 | 1.897 | 97.8 | 77.5 | 1379 | 23 | 5495.3 | 2915.7 | 2827.3 | 4177.8 | 1196.4 | 0.68233 | 6.027
2024-12-09 | 17:30 | Data | 0 | 32.777 | 30.658 | 187.534 | 7.64 | 176.233 | 2120.39 | 25.98 | 45.908 | 6.35 | 1.359 | 4.67 | 8454.3 | 1.965 | 97.8 | 77.5 | 1378 | 23 | 5495.3 | 2932.2 | 2805.3 | 4173.6 | 1196.4 | 0.6862 | 6.028
2024-12-09 | 17:30 | Data | 0 | 32.892 | 30.901 | 187.624 | 7.64 | 176.142 | 2120.39 | 25.98 | 45.908 | 6.35 | 1.345 | 4.691 | 8449.78 | 1.978 | 97.8 | 77.7 | 1378 | 23 | 5492.4 | 2910 | 2801.8 | 4159.9 | 1196.4 | 0.68294 | 6.036
2024-12-09 | 17:30 | Data | 0 | 32.744 | 30.448 | 187.489 | 7.64 | 176.187 | 2118.58 | 25.98 | 45.998 | 6.35 | 1.344 | 4.7 | 8445.26 | 2.066 | 97.8 | 77.8 | 1377 | 22.95 | 5489.4 | 2915.4 | 2809.8 | 4167.1 | 1196.4 | 0.68277 | 6.045
2024-12-09 | 17:30 | Data | 0 | 32.467 | 30.637 | 187.443 | 7.64 | 176.142 | 2117.68 | 25.98 | 45.998 | 6.35 | 1.348 | 4.681 | 8431.69 | 2.039 | 97.8 | 77.6 | 1376 | 23 | 5480.6 | 2900.4 | 2820.2 | 4169.7 | 1196.4 | 0.6844 | 6.031
2024-12-09 | 17:30 | Data | 0 | 32.75 | 30.34 | 187.489 | 7.64 | 176.097 | 2119.49 | 25.97 | 45.998 | 6.35 | 1.354 | 4.703 | 8431.69 | 2.032 | 97.8 | 77.6 | 1378 | 23 | 5480.6 | 2915.5 | 2836.3 | 4186.3 | 1196.4 | 0.67921 | 6.057
2024-12-09 | 17:30 | Data | 0 | 32.379 | 30.624 | 187.489 | 7.64 | 176.052 | 2120.39 | 25.98 | 45.908 | 6.34 | 1.348 | 4.683 | 8431.69 | 1.917 | 97.8 | 77.6 | 1378 | 23 | 5480.6 | 2899.6 | 2827.4 | 4167.6 | 1196.4 | 0.6795 | 6.029
2024-12-09 | 17:30 | Data | 0 | 32.602 | 30.752 | 187.579 | 7.64 | 176.142 | 2124.01 | 25.98 | 45.998 | 6.34 | 1.355 | 4.689 | 8409.08 | 2.086 | 97.8 | 77.6 | 1380 | 23 | 5465.9 | 2920.2 | 2841.6 | 4192.5 | 1196.4 | 0.68011 | 6.044
2024-12-09 | 17:30 | Data | 0 | 32.548 | 30.428 | 187.443 | 7.64 | 176.097 | 2122.2 | 25.98 | 45.908 | 6.35 | 1.355 | 4.692 | 8427.17 | 2.059 | 97.8 | 77.6 | 1380 | 23 | 5477.7 | 2904.8 | 2844.6 | 4181.8 | 1196.4 | 0.67782 | 6.045
2024-12-09 | 17:30 | Data | 0 | 32.723 | 30.806 | 187.443 | 7.64 | 176.142 | 2120.39 | 25.97 | 45.998 | 6.35 | 1.34 | 4.664 | 8404.56 | 1.917 | 97.8 | 77.7 | 1378 | 23 | 5463 | 2907.1 | 2838.7 | 4178.8 | 1196.4 | 0.67904 | 6.005
2024-12-09 | 17:31 | Data | 0 | 32.555 | 30.421 | 187.443 | 7.64 | 176.187 | 2122.2 | 25.98 | 45.908 | 6.34 | 1.355 | 4.689 | 8404.56 | 1.904 | 97.8 | 77.6 | 1379 | 22.95 | 5463 | 2903.2 | 2838.4 | 4176.4 | 1196.4 | 0.67891 | 6.043
2024-12-09 | 17:31 | Data | 0 | 32.264 | 30.401 | 187.217 | 7.64 | 176.007 | 2123.1 | 25.98 | 45.998 | 6.35 | 1.354 | 4.686 | 8395.51 | 2.066 | 97.8 | 77.6 | 1380 | 22.95 | 5457.1 | 2882.3 | 2826.7 | 4155.6 | 1196.4 | 0.67666 | 6.04
2024-12-09 | 17:31 | Data | 0 | 32.561 | 30.421 | 187.398 | 7.64 | 176.142 | 2123.1 | 25.98 | 45.998 | 6.35 | 1.352 | 4.672 | 8400.04 | 1.884 | 97.8 | 77.6 | 1380 | 23 | 5460 | 2901.1 | 2817.2 | 4164.3 | 1196.5 | 0.67997 | 6.023
2024-12-09 | 17:31 | Data | 0 | 32.885 | 30.685 | 187.489 | 7.64 | 176.187 | 2120.39 | 25.98 | 45.908 | 6.34 | 1.347 | 4.651 | 8404.56 | 2.14 | 97.8 | 77.5 | 1378 | 23 | 5463 | 2900.2 | 2801.3 | 4153.4 | 1196.5 | 0.68112 | 5.998
2024-12-09 | 17:31 | Data | 0 | 32.818 | 30.529 | 187.398 | 7.64 | 176.187 | 2117.68 | 25.97 | 45.908 | 6.35 | 1.351 | 4.673 | 8400.04 | 2.12 | 97.8 | 77.6 | 1376 | 22.95 | 5460 | 2913.1 | 2802.8 | 4157.2 | 1196.5 | 0.68571 | 6.025
2024-12-09 | 17:31 | Data | 0 | 32.494 | 30.415 | 187.398 | 7.64 | 176.142 | 2121.29 | 25.98 | 45.998 | 6.35 | 1.342 | 4.65 | 8454.3 | 2.079 | 97.8 | 77.6 | 1378 | 22.86 | 5495.3 | 2886.6 | 2802.6 | 4137.1 | 1196.5 | 0.68144 | 5.994
2024-12-09 | 17:31 | Data | 0 | 32.386 | 30.469 | 187.263 | 7.64 | 176.052 | 2122.2 | 25.97 | 45.908 | 6.35 | 1.342 | 4.666 | 8454.3 | 1.951 | 97.8 | 77.7 | 1379 | 23 | 5495.3 | 2918.5 | 2799.5 | 4157.8 | 1196.5 | 0.68524 | 6.009
2024-12-09 | 17:31 | Data | 0 | 32.507 | 30.739 | 187.489 | 7.64 | 176.142 | 2122.2 | 25.99 | 45.998 | 6.35 | 1.342 | 4.673 | 8458.83 | 1.958 | 97.8 | 77.7 | 1379 | 23 | 5498.2 | 2894.8 | 2805.1 | 4150 | 1196.5 | 0.67801 | 6.016
2024-12-09 | 17:31 | Data | 0 | 32.771 | 30.55 | 187.489 | 7.64 | 176.142 | 2123.1 | 26 | 45.818 | 6.35 | 1.344 | 4.652 | 8436.21 | 2.167 | 97.8 | 77.6 | 1380 | 22.95 | 5483.5 | 2913.9 | 2824 | 4173.1 | 1196.5 | 0.68188 | 5.996
2024-12-09 | 17:31 | Data | 0 | 32.528 | 30.442 | 187.579 | 7.64 | 176.142 | 2125.81 | 25.99 | 45.998 | 6.35 | 1.348 | 4.653 | 8454.3 | 1.857 | 97.8 | 77.5 | 1381 | 22.95 | 5495.3 | 2881.1 | 2811.7 | 4143.6 | 1196.5 | 0.67845 | 6.002
2024-12-09 | 17:31 | Data | 0 | 32.285 | 30.415 | 187.353 | 7.64 | 176.052 | 2124.91 | 25.99 | 45.998 | 6.35 | 1.343 | 4.669 | 8467.87 | 1.857 | 97.8 | 77.7 | 1381 | 23 | 5504.1 | 2904.7 | 2827.9 | 4174.5 | 1196.5 | 0.67915 | 6.012
2024-12-09 | 17:31 | Data | 0 | 32.831 | 30.536 | 187.534 | 7.64 | 176.187 | 2124.91 | 25.99 | 45.998 | 6.35 | 1.344 | 4.682 | 8454.3 | 1.958 | 97.8 | 77.7 | 1382 | 23 | 5495.3 | 2897 | 2803.1 | 4149.9 | 1196.5 | 0.68098 | 6.026
2024-12-09 | 17:31 | Data | 0 | 32.723 | 30.448 | 187.443 | 7.64 | 176.187 | 2124.01 | 25.99 | 46.089 | 6.35 | 1.353 | 4.669 | 8445.26 | 2.181 | 97.8 | 77.5 | 1381 | 23.04 | 5489.4 | 2887.6 | 2807.2 | 4147.3 | 1196.5 | 0.68062 | 6.023
2024-12-09 | 17:31 | Data | 0 | 32.494 | 30.536 | 187.579 | 7.64 | 176.052 | 2125.81 | 25.99 | 45.818 | 6.35 | 1.349 | 4.689 | 8422.65 | 2.248 | 97.8 | 77.6 | 1382 | 22.95 | 5474.7 | 2904.3 | 2809.7 | 4159.9 | 1196.5 | 0.68107 | 6.037
2024-12-09 | 17:31 | Data | 0 | 32.487 | 30.401 | 187.353 | 7.64 | 176.097 | 2124.01 | 26 | 46.179 | 6.35 | 1.346 | 4.697 | 8409.08 | 1.944 | 97.8 | 77.7 | 1381 | 23.13 | 5465.9 | 2903.9 | 2789 | 4155.9 | 1196.5 | 0.68725 | 6.044
2024-12-09 | 17:31 | Data | 0 | 32.271 | 30.415 | 187.443 | 7.64 | 176.097 | 2128.52 | 26.01 | 45.908 | 6.35 | 1.348 | 4.663 | 8404.56 | 2.032 | 97.8 | 77.6 | 1383 | 22.95 | 5463 | 2924 | 2793.1 | 4160 | 1196.5 | 0.68552 | 6.01
2024-12-09 | 17:31 | Data | 0 | 32.609 | 30.651 | 187.443 | 7.64 | 176.142 | 2128.52 | 25.99 | 45.998 | 6.35 | 1.351 | 4.669 | 8431.69 | 2.059 | 97.8 | 77.6 | 1384 | 23 | 5480.6 | 2896.9 | 2800.7 | 4146.2 | 1196.5 | 0.6835 | 6.02
2024-12-09 | 17:32 | Data | 0 | 32.663 | 30.651 | 187.534 | 7.64 | 176.007 | 2128.52 | 26.01 | 45.998 | 6.34 | 1.354 | 4.687 | 8427.17 | 2.073 | 97.8 | 77.6 | 1384 | 23 | 5477.7 | 2892.6 | 2808.2 | 4155.1 | 1196.5 | 0.67785 | 6.041
2024-12-09 | 17:32 | Data | 0 | 32.696 | 30.529 | 187.534 | 7.64 | 176.187 | 2128.52 | 25.99 | 46.179 | 6.35 | 1.349 | 4.698 | 8427.17 | 2.066 | 97.8 | 77.7 | 1384 | 23.09 | 5477.7 | 2886.1 | 2809.8 | 4149.5 | 1196.5 | 0.6782 | 6.047
2024-12-09 | 17:32 | Data | 0 | 32.723 | 30.529 | 187.489 | 7.64 | 176.097 | 2128.52 | 25.99 | 45.998 | 6.34 | 1.355 | 4.683 | 8436.21 | 1.897 | 97.8 | 77.6 | 1384 | 22.95 | 5483.5 | 2896.8 | 2818.8 | 4162.6 | 1196.5 | 0.67913 | 6.039
2024-12-09 | 17:32 | Data | 0 | 32.514 | 30.428 | 187.398 | 7.64 | 176.142 | 2128.52 | 25.99 | 46.179 | 6.35 | 1.358 | 4.675 | 8427.17 | 1.897 | 97.8 | 77.5 | 1384 | 23.09 | 5477.7 | 2908.8 | 2831.7 | 4175.2 | 1196.5 | 0.67989 | 6.032
2024-12-09 | 17:32 | Data | 0 | 32.865 | 30.759 | 187.534 | 7.64 | 176.187 | 2128.52 | 25.99 | 46.179 | 6.35 | 1.352 | 4.667 | 8635.19 | 2.073 | 97.8 | 77.5 | 1384 | 23.09 | 5612.9 | 2901.7 | 2797.5 | 4146.4 | 1196.5 | 0.68312 | 6.02
2024-12-09 | 17:32 | Data | 0 | 32.501 | 30.766 | 187.489 | 7.64 | 176.142 | 2128.52 | 25.99 | 46.269 | 6.35 | 1.344 | 4.674 | 8635.19 | 2.228 | 97.8 | 77.6 | 1384 | 23.09 | 5612.9 | 2891.3 | 2806.4 | 4146.6 | 1196.5 | 0.68111 | 6.02
2024-12-09 | 17:32 | Data | 0 | 32.494 | 30.509 | 187.398 | 7.64 | 176.052 | 2127.62 | 25.99 | 46.269 | 6.34 | 1.344 | 4.681 | 8626.15 | 2.181 | 97.8 | 77.7 | 1384 | 23.13 | 5607 | 2899.3 | 2826 | 4168.2 | 1196.5 | 0.67855 | 6.024
2024-12-09 | 17:32 | Data | 0 | 32.717 | 30.475 | 187.489 | 7.64 | 176.097 | 2131.24 | 25.99 | 46.269 | 6.35 | 1.345 | 4.697 | 8630.67 | 2.133 | 97.8 | 77.7 | 1384 | 23.13 | 5609.9 | 2902.4 | 2791.1 | 4143.7 | 1196.5 | 0.68427 | 6.043
2024-12-09 | 17:32 | Data | 0 | 32.723 | 30.651 | 187.443 | 7.64 | 176.142 | 2131.24 | 25.97 | 45.998 | 6.35 | 1.344 | 4.687 | 8445.26 | 1.87 | 97.8 | 77.7 | 1385 | 23 | 5489.4 | 2904.4 | 2787.1 | 4146.7 | 1196.5 | 0.68508 | 6.031
2024-12-09 | 17:32 | Data | 0 | 32.804 | 30.658 | 187.534 | 7.64 | 176.187 | 2130.33 | 25.98 | 45.998 | 6.35 | 1.352 | 4.684 | 8436.21 | 2.16 | 97.8 | 77.6 | 1385 | 23 | 5483.5 | 2906.3 | 2778.4 | 4140 | 1196.5 | 0.68454 | 6.036
2024-12-09 | 17:32 | Data | 0 | 32.703 | 30.853 | 187.579 | 7.64 | 176.142 | 2130.33 | 25.99 | 45.908 | 6.35 | 1.348 | 4.697 | 8418.13 | 1.89 | 97.8 | 77.7 | 1385 | 23 | 5471.8 | 2920.3 | 2805.4 | 4166.6 | 1196.5 | 0.68519 | 6.045
2024-12-09 | 17:32 | Data | 0 | 32.44 | 30.415 | 187.579 | 7.64 | 176.142 | 2124.91 | 25.96 | 45.998 | 6.35 | 1.343 | 4.683 | 8436.21 | 2.167 | 97.8 | 77.7 | 1382 | 23.04 | 5483.5 | 2898.2 | 2789.9 | 4136.8 | 1196.5 | 0.68446 | 6.023
2024-12-09 | 17:32 | Data | 0 | 32.501 | 30.415 | 187.489 | 7.64 | 176.187 | 2125.81 | 25.99 | 45.998 | 6.34 | 1.347 | 4.674 | 8436.21 | 2.073 | 97.8 | 77.6 | 1382 | 23 | 5483.5 | 2885.6 | 2791 | 4129.3 | 1196.5 | 0.68143 | 6.022
2024-12-09 | 17:32 | Data | 0 | 32.501 | 30.698 | 187.443 | 7.64 | 176.187 | 2123.1 | 25.98 | 45.998 | 6.35 | 1.346 | 4.654 | 8431.69 | 1.985 | 97.8 | 77.6 | 1380 | 23 | 5480.6 | 2909.4 | 2770 | 4137.5 | 1196.5 | 0.68614 | 5.999
2024-12-09 | 17:32 | Data | 0 | 33.041 | 30.543 | 187.534 | 7.64 | 176.187 | 2122.2 | 25.97 | 45.998 | 6.35 | 1.342 | 4.656 | 8445.26 | 2.113 | 97.8 | 77.6 | 1379 | 23 | 5489.4 | 2902.2 | 2786.2 | 4140.4 | 1196.5 | 0.68368 | 5.998
2024-12-09 | 17:32 | Data | 0 | 32.224 | 30.529 | 187.398 | 7.64 | 176.052 | 2119.49 | 25.98 | 45.908 | 6.35 | 1.344 | 4.647 | 8445.26 | 2.032 | 97.8 | 77.6 | 1378 | 22.95 | 5489.4 | 2911 | 2787.2 | 4147 | 1196.5 | 0.68616 | 5.99
2024-12-09 | 17:32 | Data | 0 | 32.717 | 30.651 | 187.489 | 7.64 | 176.142 | 2121.29 | 25.98 | 45.998 | 6.35 | 1.352 | 4.659 | 8458.83 | 1.958 | 97.8 | 77.5 | 1380 | 22.95 | 5498.2 | 2880.9 | 2788.2 | 4130.9 | 1196.5 | 0.68168 | 6.01
2024-12-09 | 17:32 | Data | 0 | 32.811 | 30.759 | 187.579 | 7.64 | 176.233 | 2124.01 | 25.97 | 45.998 | 6.35 | 1.346 | 4.677 | 8454.3 | 2.073 | 97.8 | 77.7 | 1380 | 23 | 5495.3 | 2897.1 | 2815.2 | 4155.3 | 1196.5 | 0.67981 | 6.022
2024-12-09 | 17:33 | Data | 0 | 32.494 | 30.374 | 187.353 | 7.64 | 176.007 | 2123.1 | 25.98 | 45.998 | 6.35 | 1.34 | 4.655 | 8445.26 | 1.965 | 97.8 | 77.6 | 1380 | 22.95 | 5489.4 | 2907.3 | 2820 | 4166.4 | 1196.5 | 0.68089 | 5.996
2024-12-09 | 17:33 | Data | 0 | 32.615 | 30.421 | 187.579 | 7.64 | 176.142 | 2120.39 | 25.98 | 45.998 | 6.35 | 1.359 | 4.664 | 8440.74 | 2.073 | 97.8 | 77.4 | 1378 | 23 | 5486.5 | 2903.4 | 2798.7 | 4151.1 | 1196.5 | 0.68342 | 6.023
2024-12-09 | 17:33 | Data | 0 | 32.521 | 30.651 | 187.443 | 7.64 | 176.233 | 2120.39 | 25.98 | 45.908 | 6.35 | 1.36 | 4.665 | 9087.41 | 1.857 | 97.8 | 77.4 | 1378 | 23 | 5906.8 | 2878 | 2790.8 | 4124.7 | 1196.5 | 0.67988 | 6.026
2024-12-09 | 17:33 | Data | 0 | 32.494 | 30.428 | 187.489 | 7.64 | 176.142 | 2119.49 | 25.98 | 45.908 | 6.35 | 1.346 | 4.664 | 8639.71 | 2.059 | 97.8 | 77.6 | 1378 | 23 | 5615.8 | 2900.3 | 2784 | 4136.2 | 1196.6 | 0.68592 | 6.009
2024-12-09 | 17:33 | Data | 0 | 32.723 | 30.651 | 187.353 | 7.64 | 176.187 | 2120.39 | 25.98 | 45.998 | 6.35 | 1.351 | 4.67 | 8626.15 | 2.073 | 97.8 | 77.6 | 1378 | 23.04 | 5607 | 2885.6 | 2783.4 | 4132.3 | 1196.6 | 0.68153 | 6.021
2024-12-09 | 17:33 | Data | 0 | 32.44 | 30.415 | 187.489 | 7.64 | 176.142 | 2124.91 | 25.98 | 45.998 | 6.35 | 1.347 | 4.676 | 8621.63 | 2.046 | 97.8 | 77.6 | 1381 | 23 | 5604.1 | 2911.8 | 2807.7 | 4156.5 | 1196.6 | 0.68492 | 6.023
2024-12-09 | 17:33 | Data | 0 | 32.44 | 30.59 | 187.534 | 7.64 | 176.007 | 2127.62 | 25.98 | 45.998 | 6.35 | 1.339 | 4.651 | 8259.85 | 2.073 | 97.8 | 77.6 | 1383 | 23 | 5368.9 | 2903.5 | 2787.7 | 4136 | 1196.6 | 0.68376 | 5.991
2024-12-09 | 17:33 | Data | 0 | 32.393 | 30.705 | 187.353 | 7.64 | 176.097 | 2129.43 | 25.98 | 45.998 | 6.35 | 1.341 | 4.671 | 8612.58 | 2.181 | 97.8 | 77.7 | 1384 | 22.95 | 5598.2 | 2902.3 | 2780.7 | 4132.7 | 1196.6 | 0.6838 | 6.012
2024-12-09 | 17:33 | Data | 0 | 32.494 | 30.415 | 187.398 | 7.64 | 176.142 | 2130.33 | 25.98 | 46.089 | 6.35 | 1.341 | 4.681 | 8608.06 | 2.079 | 97.8 | 77.7 | 1385 | 23 | 5595.2 | 2894.8 | 2776.5 | 4130.7 | 1196.6 | 0.68128 | 6.023
2024-12-09 | 17:33 | Data | 0 | 32.494 | 30.428 | 187.398 | 7.64 | 176.142 | 2132.14 | 25.98 | 45.998 | 6.35 | 1.334 | 4.665 | 8599.01 | 2.052 | 97.8 | 77.8 | 1387 | 22.95 | 5589.4 | 2914.1 | 2780.6 | 4147.4 | 1196.6 | 0.68549 | 5.999
2024-12-09 | 17:33 | Data | 0 | 32.771 | 30.658 | 187.534 | 7.64 | 176.142 | 2138.47 | 25.98 | 45.818 | 6.35 | 1.335 | 4.669 | 8585.45 | 2.073 | 97.9 | 77.7 | 1388 | 23 | 5580.5 | 2898.9 | 2778.6 | 4137.8 | 1196.6 | 0.68642 | 6.007
2024-12-09 | 17:33 | Data | 0 | 32.825 | 30.502 | 187.489 | 7.64 | 176.187 | 2137.56 | 25.97 | 45.998 | 6.35 | 1.337 | 4.645 | 8608.06 | 2.133 | 97.8 | 77.7 | 1389 | 23 | 5595.2 | 2912.4 | 2793.1 | 4151.7 | 1196.6 | 0.68562 | 5.985
2024-12-09 | 17:33 | Data | 0 | 32.94 | 30.678 | 187.534 | 7.64 | 176.233 | 2134.85 | 25.98 | 45.998 | 6.35 | 1.353 | 4.692 | 8585.45 | 2.133 | 97.8 | 77.6 | 1387 | 22.95 | 5580.5 | 2917.5 | 2810.3 | 4166.2 | 1196.6 | 0.68463 | 6.044
2024-12-09 | 17:33 | Data | 0 | 32.919 | 30.448 | 187.489 | 7.64 | 176.142 | 2136.66 | 25.99 | 45.908 | 6.34 | 1.343 | 4.662 | 8599.01 | 2.079 | 97.9 | 77.6 | 1389 | 23 | 5589.4 | 2911.1 | 2792.9 | 4147.9 | 1196.6 | 0.6861 | 6.004
2024-12-09 | 17:33 | Data | 0 | 32.885 | 30.88 | 187.67 | 7.64 | 176.187 | 2136.66 | 25.99 | 45.818 | 6.35 | 1.34 | 4.674 | 8599.01 | 2.066 | 97.9 | 77.7 | 1389 | 22.95 | 5589.4 | 2898.7 | 2769.8 | 4129.1 | 1196.6 | 0.68448 | 6.015
2024-12-09 | 17:33 | Data | 0 | 32.602 | 30.469 | 187.398 | 7.64 | 176.097 | 2137.56 | 25.99 | 45.998 | 6.35 | 1.343 | 4.674 | 8599.01 | 2.052 | 97.8 | 77.7 | 1389 | 23 | 5589.4 | 2915.3 | 2799.3 | 4156.4 | 1196.6 | 0.68444 | 6.017
2024-12-09 | 17:33 | Data | 0 | 32.71 | 30.867 | 187.624 | 7.64 | 176.233 | 2136.66 | 25.99 | 45.998 | 6.35 | 1.347 | 4.694 | 8576.4 | 2.059 | 97.8 | 77.7 | 1389 | 22.95 | 5574.7 | 2883.6 | 2803.5 | 4141.9 | 1196.6 | 0.68078 | 6.04
2024-12-09 | 17:33 | Data | 0 | 32.933 | 30.651 | 187.624 | 7.64 | 176.142 | 2139.37 | 25.98 | 45.998 | 6.35 | 1.347 | 4.663 | 8562.84 | 1.904 | 97.9 | 77.6 | 1390 | 23 | 5565.8 | 2905.2 | 2820.9 | 4167.4 | 1196.6 | 0.68101 | 6.009
2024-12-09 | 17:34 | Data | 0 | 32.298 | 30.415 | 187.353 | 7.64 | 176.097 | 2137.56 | 25.99 | 46.089 | 6.35 | 1.354 | 4.68 | 8259.85 | 1.971 | 97.8 | 77.6 | 1389 | 23 | 5368.9 | 2911 | 2787.4 | 4148.4 | 1196.6 | 0.68464 | 6.032
2024-12-09 | 17:34 | Data | 0 | 32.636 | 30.651 | 187.443 | 7.64 | 176.233 | 2136.66 | 25.99 | 45.908 | 6.35 | 1.345 | 4.682 | 8232.71 | 1.863 | 97.9 | 77.7 | 1389 | 22.95 | 5351.3 | 2912.7 | 2788 | 4149.6 | 1196.6 | 0.6848 | 6.026
2024-12-09 | 17:34 | Data | 0 | 32.501 | 30.421 | 187.443 | 7.64 | 176.187 | 2135.76 | 25.99 | 45.998 | 6.35 | 1.358 | 4.704 | 8255.33 | 2.187 | 97.8 | 77.6 | 1388 | 23 | 5366 | 2891.7 | 2809.6 | 4157.9 | 1196.6 | 0.68053 | 6.062
2024-12-09 | 17:34 | Data | 0 | 32.879 | 30.759 | 187.624 | 7.64 | 176.187 | 2137.56 | 25.99 | 45.908 | 6.35 | 1.349 | 4.692 | 8268.89 | 2.073 | 97.8 | 77.7 | 1389 | 22.95 | 5374.8 | 2913.8 | 2797.3 | 4158.8 | 1196.6 | 0.68291 | 6.039
2024-12-09 | 17:34 | Data | 0 | 32.919 | 30.988 | 187.579 | 7.64 | 176.142 | 2139.37 | 25.97 | 45.998 | 6.35 | 1.354 | 4.668 | 8223.67 | 1.958 | 97.9 | 77.5 | 1391 | 23 | 5345.4 | 2906.2 | 2804.6 | 4155.6 | 1196.6 | 0.68091 | 6.021
2024-12-09 | 17:34 | Data | 0 | 32.669 | 30.529 | 187.443 | 7.64 | 176.052 | 2137.56 | 25.98 | 45.998 | 6.35 | 1.344 | 4.664 | 8250.8 | 2.073 | 97.8 | 77.6 | 1389 | 23 | 5363 | 2889.6 | 2816.1 | 4151 | 1196.6 | 0.68145 | 6.008
2024-12-09 | 17:34 | Data | 0 | 32.494 | 30.644 | 187.534 | 7.64 | 176.142 | 2137.56 | 25.98 | 45.998 | 6.35 | 1.348 | 4.684 | 8259.85 | 1.985 | 97.8 | 77.6 | 1389 | 23 | 5368.9 | 2908.9 | 2816.6 | 4151.6 | 1196.6 | 0.67925 | 6.032
2024-12-09 | 17:34 | Data | 0 | 32.973 | 30.658 | 187.624 | 7.64 | 176.233 | 2136.66 | 25.98 | 45.908 | 6.34 | 1.349 | 4.693 | 8264.37 | 2.167 | 97.8 | 77.7 | 1389 | 23 | 5371.8 | 2901.5 | 2815.8 | 4157.8 | 1196.6 | 0.68154 | 6.043
2024-12-09 | 17:34 | Data | 0 | 32.602 | 30.651 | 187.534 | 7.64 | 176.187 | 2136.66 | 25.99 | 45.908 | 6.35 | 1.354 | 4.669 | 8314.11 | 2.025 | 97.9 | 77.5 | 1388 | 22.86 | 5404.2 | 2912.8 | 2815.5 | 4168.3 | 1196.6 | 0.68254 | 6.021
2024-12-09 | 17:34 | Data | 0 | 32.521 | 30.759 | 187.624 | 7.64 | 176.233 | 2133.95 | 25.98 | 45.998 | 6.35 | 1.349 | 4.674 | 8300.55 | 1.998 | 97.8 | 77.6 | 1387 | 23 | 5395.4 | 2916.5 | 2834.2 | 4183.3 | 1196.6 | 0.67956 | 6.024
2024-12-09 | 17:34 | Data | 0 | 32.737 | 30.651 | 187.579 | 7.64 | 176.278 | 2136.66 | 25.98 | 45.998 | 6.34 | 1.344 | 4.687 | 8300.55 | 2.066 | 97.8 | 77.7 | 1389 | 23 | 5395.4 | 2904.5 | 2841.5 | 4180.6 | 1196.6 | 0.67735 | 6.033
2024-12-09 | 17:34 | Data | 0 | 32.899 | 30.685 | 187.579 | 7.64 | 176.187 | 2133.95 | 25.98 | 45.998 | 6.35 | 1.349 | 4.69 | 8612.58 | 2.235 | 97.8 | 77.7 | 1388 | 23.04 | 5598.2 | 2897.6 | 2832.4 | 4169.4 | 1196.6 | 0.67751 | 6.039
2024-12-09 | 17:34 | Data | 0 | 32.528 | 30.624 | 187.443 | 7.64 | 176.278 | 2130.33 | 25.99 | 45.998 | 6.35 | 1.354 | 4.701 | 8621.63 | 1.904 | 97.8 | 77.6 | 1384 | 23.04 | 5604.1 | 2910.1 | 2836 | 4176.3 | 1196.6 | 0.67983 | 6.055
2024-12-09 | 17:34 | Data | 0 | 32.723 | 30.874 | 187.579 | 7.64 | 176.187 | 2131.24 | 25.98 | 45.908 | 6.35 | 1.354 | 4.67 | 8626.15 | 1.87 | 97.8 | 77.5 | 1385 | 22.95 | 5607 | 2901.9 | 2840.6 | 4177.6 | 1196.6 | 0.67857 | 6.024
2024-12-09 | 17:34 | Data | 0 | 32.609 | 30.637 | 187.579 | 7.63 | 176.097 | 2129.43 | 25.98 | 45.998 | 6.35 | 1.347 | 4.677 | 8626.15 | 2.073 | 97.8 | 77.6 | 1384 | 23 | 5607 | 2891.9 | 2818.7 | 4153.9 | 1196.6 | 0.67991 | 6.025
2024-12-09 | 17:34 | Data | 0 | 32.933 | 30.698 | 187.67 | 7.64 | 176.233 | 2130.33 | 25.98 | 45.908 | 6.35 | 1.344 | 4.675 | 8060.87 | 2.079 | 97.8 | 77.7 | 1385 | 23 | 5239.6 | 2901 | 2808.5 | 4156.5 | 1196.6 | 0.68532 | 6.019
2024-12-09 | 17:34 | Data | 0 | 32.494 | 30.624 | 187.353 | 7.64 | 176.142 | 2130.33 | 25.99 | 45.998 | 6.35 | 1.355 | 4.691 | 8418.13 | 2.079 | 97.8 | 77.6 | 1384 | 22.95 | 5471.8 | 2898 | 2806.3 | 4152.8 | 1196.6 | 0.68081 | 6.043
2024-12-09 | 17:34 | Data | 0 | 32.494 | 30.415 | 187.398 | 7.64 | 176.142 | 2127.62 | 25.98 | 46.089 | 6.35 | 1.359 | 4.668 | 8440.74 | 2.073 | 97.8 | 77.5 | 1384 | 23.04 | 5486.5 | 2915.4 | 2794.4 | 4159.1 | 1196.6 | 0.68393 | 6.026
2024-12-09 | 17:35 | Data | 0 | 32.494 | 30.624 | 187.534 | 7.64 | 176.187 | 2128.52 | 25.98 | 45.908 | 6.34 | 1.352 | 4.674 | 8449.78 | 2.127 | 97.8 | 77.6 | 1384 | 23 | 5492.4 | 2902 | 2812.5 | 4157.4 | 1196.6 | 0.68184 | 6.027
2024-12-09 | 17:35 | Data | 0 | 32.609 | 30.644 | 187.579 | 7.64 | 176.187 | 2126.72 | 25.98 | 45.998 | 6.35 | 1.348 | 4.695 | 8458.83 | 1.924 | 97.8 | 77.7 | 1384 | 23 | 5498.2 | 2909.9 | 2818.3 | 4172.3 | 1196.6 | 0.6812 | 6.044
2024-12-09 | 17:35 | Data | 0 | 32.494 | 30.624 | 187.489 | 7.64 | 176.187 | 2131.24 | 25.98 | 45.998 | 6.34 | 1.349 | 4.687 | 8445.26 | 2.079 | 97.8 | 77.6 | 1385 | 22.95 | 5489.4 | 2909.4 | 2824.5 | 4170.5 | 1196.6 | 0.68098 | 6.037
2024-12-09 | 17:35 | Data | 0 | 32.609 | 30.651 | 187.534 | 7.64 | 176.233 | 2133.95 | 25.98 | 45.998 | 6.35 | 1.353 | 4.653 | 8445.26 | 2.059 | 97.8 | 77.5 | 1387 | 23 | 5489.4 | 2914.2 | 2820.7 | 4171.6 | 1196.6 | 0.68259 | 6.006
2024-12-09 | 17:35 | Data | 0 | 32.548 | 30.597 | 187.534 | 7.64 | 176.187 | 2134.85 | 25.98 | 45.908 | 6.35 | 1.355 | 4.681 | 8440.74 | 2.079 | 97.8 | 77.5 | 1387 | 23 | 5486.5 | 2902.5 | 2806.5 | 4156.2 | 1196.7 | 0.68341 | 6.036
2024-12-09 | 17:35 | Data | 0 | 32.453 | 30.624 | 187.489 | 7.64 | 176.142 | 2131.24 | 25.98 | 45.998 | 6.35 | 1.341 | 4.673 | 8449.78 | 2.005 | 97.8 | 77.7 | 1385 | 23.04 | 5492.4 | 2897.3 | 2805.8 | 4149.8 | 1196.7 | 0.68216 | 6.014
2024-12-09 | 17:35 | Data | 0 | 32.501 | 30.752 | 187.579 | 7.64 | 176.187 | 2130.33 | 25.97 | 45.547 | 6.35 | 1.345 | 4.675 | 8436.21 | 2.073 | 97.9 | 77.7 | 1385 | 22.73 | 5483.5 | 2892.8 | 2796 | 4141.5 | 1196.7 | 0.68274 | 6.021
2024-12-09 | 17:35 | Data | 0 | 32.615 | 30.442 | 187.443 | 7.64 | 176.187 | 2131.24 | 25.98 | 45.908 | 6.35 | 1.353 | 4.689 | 8418.13 | 2.241 | 97.8 | 77.6 | 1385 | 22.95 | 5471.8 | 2892.5 | 2801 | 4146.3 | 1196.7 | 0.68134 | 6.041
2024-12-09 | 17:35 | Data | 0 | 32.946 | 30.455 | 187.579 | 7.64 | 176.187 | 2127.62 | 25.98 | 45.998 | 6.35 | 1.351 | 4.683 | 8427.17 | 1.978 | 97.8 | 77.6 | 1383 | 23 | 5477.7 | 2905.4 | 2795.9 | 4147.6 | 1196.7 | 0.68391 | 6.032
2024-12-09 | 17:35 | Data | 0 | 32.507 | 30.739 | 187.489 | 7.64 | 176.142 | 2124.91 | 25.98 | 45.908 | 6.35 | 1.346 | 4.67 | 8427.17 | 1.965 | 97.8 | 77.6 | 1381 | 23 | 5477.7 | 2908.1 | 2815.8 | 4170.7 | 1196.7 | 0.68073 | 6.016
2024-12-09 | 17:35 | Data | 0 | 32.906 | 30.88 | 187.624 | 7.64 | 176.278 | 2124.91 | 25.99 | 45.998 | 6.34 | 1.347 | 4.67 | 8449.78 | 2.066 | 97.8 | 77.6 | 1381 | 23 | 5492.4 | 2905.2 | 2802 | 4154 | 1196.7 | 0.68322 | 6.017
2024-12-09 | 17:35 | Data | 0 | 32.825 | 30.766 | 187.624 | 7.64 | 176.278 | 2125.81 | 25.98 | 45.998 | 6.35 | 1.352 | 4.666 | 8449.78 | 2.066 | 97.8 | 77.5 | 1382 | 23 | 5492.4 | 2895.1 | 2819.5 | 4158.3 | 1196.7 | 0.67946 | 6.017
2024-12-09 | 17:35 | Data | 0 | 32.723 | 30.442 | 187.67 | 7.64 | 176.233 | 2126.72 | 25.99 | 45.908 | 6.34 | 1.342 | 4.651 | 8449.78 | 2.248 | 97.8 | 77.6 | 1382 | 23 | 5492.4 | 2920.3 | 2807.8 | 4171.3 | 1196.7 | 0.68253 | 5.993
2024-12-09 | 17:35 | Data | 0 | 32.595 | 30.651 | 187.398 | 7.63 | 176.187 | 2124.91 | 25.98 | 45.998 | 6.35 | 1.346 | 4.668 | 8458.83 | 2.019 | 97.8 | 77.6 | 1381 | 23.04 | 5498.2 | 2923.3 | 2819.5 | 4177.7 | 1196.7 | 0.68293 | 6.013
2024-12-09 | 17:35 | Data | 0 | 32.723 | 30.651 | 187.443 | 7.64 | 176.187 | 2125.81 | 25.98 | 45.818 | 6.35 | 1.345 | 4.692 | 8467.87 | 2.073 | 97.8 | 77.7 | 1382 | 23 | 5504.1 | 2908.9 | 2819.1 | 4165.7 | 1196.7 | 0.68141 | 6.036
2024-12-09 | 17:35 | Data | 0 | 32.609 | 30.867 | 187.624 | 7.64 | 176.233 | 2125.81 | 25.97 | 45.908 | 6.35 | 1.342 | 4.665 | 8472.39 | 2.012 | 97.8 | 77.7 | 1381 | 22.95 | 5507.1 | 2902.7 | 2811.4 | 4157.7 | 1196.7 | 0.68127 | 6.007
2024-12-09 | 17:35 | Data | 0 | 32.548 | 30.475 | 187.534 | 7.64 | 176.142 | 2125.81 | 25.98 | 45.908 | 6.35 | 1.346 | 4.691 | 8476.91 | 2.1 | 97.8 | 77.7 | 1382 | 22.95 | 5510 | 2890 | 2803.1 | 4144.6 | 1196.7 | 0.67993 | 6.036
2024-12-09 | 17:36 | Data | 0 | 32.669 | 30.772 | 187.624 | 7.64 | 176.278 | 2125.81 | 25.98 | 45.998 | 6.34 | 1.348 | 4.702 | 8472.39 | 2.37 | 97.8 | 77.7 | 1382 | 23 | 5507.1 | 2907.9 | 2805.7 | 4154.2 | 1196.7 | 0.68314 | 6.05
2024-12-09 | 17:36 | Data | 0 | 32.737 | 30.651 | 187.443 | 7.64 | 176.187 | 2125.81 | 25.98 | 46.089 | 6.35 | 1.349 | 4.707 | 8454.3 | 2.079 | 97.8 | 77.7 | 1382 | 23 | 5495.3 | 2901.6 | 2804.6 | 4151.9 | 1196.7 | 0.68315 | 6.057
2024-12-09 | 17:36 | Data | 0 | 32.642 | 30.651 | 187.534 | 7.64 | 176.187 | 2125.81 | 25.97 | 45.998 | 6.35 | 1.353 | 4.692 | 8445.26 | 1.85 | 97.8 | 77.6 | 1382 | 22.95 | 5489.4 | 2903.5 | 2816.2 | 4163.6 | 1196.7 | 0.68016 | 6.047
2024-12-09 | 17:36 | Data | 0 | 32.507 | 30.536 | 187.534 | 7.63 | 176.187 | 2128.52 | 25.98 | 45.998 | 6.35 | 1.354 | 4.687 | 8445.26 | 1.85 | 97.8 | 77.6 | 1384 | 23 | 5489.4 | 2914.3 | 2797.9 | 4158.7 | 1196.7 | 0.68534 | 6.04
2024-12-09 | 17:36 | Data | 0 | 32.298 | 30.644 | 187.624 | 7.64 | 176.233 | 2125.81 | 25.99 | 46.54 | 6.35 | 1.353 | 4.692 | 8458.83 | 1.843 | 97.8 | 77.6 | 1382 | 23.27 | 5498.2 | 2919.2 | 2799.3 | 4160.5 | 1196.7 | 0.6851 | 6.046
2024-12-09 | 17:36 | Data | 0 | 32.501 | 30.624 | 187.489 | 7.64 | 176.278 | 2124.91 | 25.99 | 46.089 | 6.35 | 1.343 | 4.667 | 8454.3 | 2.106 | 97.8 | 77.6 | 1382 | 23 | 5495.3 | 2889.4 | 2794.5 | 4137.2 | 1196.7 | 0.68274 | 6.011
2024-12-09 | 17:36 | Data | 0 | 32.737 | 30.651 | 187.624 | 7.64 | 176.278 | 2122.2 | 25.98 | 45.998 | 6.34 | 1.345 | 4.688 | 8427.17 | 2.073 | 97.8 | 77.7 | 1379 | 23 | 5477.7 | 2897.2 | 2780.6 | 4136.6 | 1196.7 | 0.68331 | 6.034
2024-12-09 | 17:36 | Data | 0 | 32.528 | 30.421 | 187.443 | 7.64 | 176.142 | 2123.1 | 25.98 | 45.998 | 6.35 | 1.348 | 4.667 | 8431.69 | 1.897 | 97.8 | 77.6 | 1381 | 22.91 | 5480.6 | 2893 | 2796.3 | 4142.4 | 1196.7 | 0.68253 | 6.017
2024-12-09 | 17:36 | Data | 0 | 32.723 | 30.536 | 187.579 | 7.64 | 176.233 | 2121.29 | 25.97 | 45.998 | 6.35 | 1.346 | 4.673 | 8445.26 | 1.938 | 97.8 | 77.6 | 1379 | 23 | 5489.4 | 2901.8 | 2790.7 | 4141.1 | 1196.7 | 0.68444 | 6.02
2024-12-09 | 17:36 | Data | 0 | 32.723 | 30.421 | 187.534 | 7.64 | 176.142 | 2123.1 | 25.99 | 45.998 | 6.34 | 1.346 | 4.676 | 8418.13 | 2.133 | 97.8 | 77.7 | 1380 | 23 | 5471.8 | 2922.2 | 2802.5 | 4161.4 | 1196.7 | 0.68584 | 6.023
2024-12-09 | 17:36 | Data | 0 | 32.723 | 30.556 | 187.489 | 7.64 | 176.142 | 2120.39 | 25.99 | 45.908 | 6.35 | 1.34 | 4.676 | 8445.26 | 2.167 | 97.8 | 77.7 | 1378 | 22.95 | 5489.4 | 2885.5 | 2813.3 | 4147.4 | 1196.7 | 0.68046 | 6.017
2024-12-09 | 17:36 | Data | 0 | 32.825 | 30.482 | 187.715 | 7.63 | 176.278 | 2119.49 | 25.98 | 45.998 | 6.34 | 1.349 | 4.669 | 8458.83 | 2.127 | 97.8 | 77.6 | 1378 | 23 | 5498.2 | 2885.6 | 2803.8 | 4139.9 | 1196.7 | 0.68115 | 6.017
2024-12-09 | 17:36 | Data | 0 | 32.865 | 30.961 | 187.624 | 7.63 | 176.142 | 2123.1 | 25.97 | 45.998 | 6.35 | 1.349 | 4.692 | 8458.83 | 2.052 | 97.8 | 77.7 | 1380 | 23 | 5498.2 | 2884.3 | 2791.3 | 4147.6 | 1196.7 | 0.68108 | 6.042
2024-12-09 | 17:36 | Data | 0 | 32.717 | 30.624 | 187.534 | 7.64 | 176.278 | 2124.91 | 25.99 | 45.998 | 6.35 | 1.355 | 4.684 | 8458.83 | 2.127 | 97.8 | 77.6 | 1382 | 23 | 5498.2 | 2889.3 | 2809.6 | 4150.9 | 1196.7 | 0.67965 | 6.04
2024-12-09 | 17:36 | Data | 0 | 32.399 | 30.428 | 187.534 | 7.64 | 176.233 | 2128.52 | 25.98 | 45.998 | 6.35 | 1.348 | 4.692 | 8458.83 | 2.012 | 97.8 | 77.7 | 1384 | 22.95 | 5498.2 | 2897.5 | 2807 | 4149.2 | 1196.7 | 0.68225 | 6.04
2024-12-09 | 17:36 | Data | 0 | 32.494 | 30.766 | 187.534 | 7.64 | 176.187 | 2123.1 | 25.99 | 45.998 | 6.35 | 1.352 | 4.709 | 8454.3 | 2.167 | 97.8 | 77.7 | 1379 | 23 | 5495.3 | 2906.6 | 2799.1 | 4154.3 | 1196.7 | 0.68322 | 6.062
2024-12-09 | 17:36 | Data | 0 | 33.048 | 30.678 | 187.579 | 7.64 | 176.233 | 2127.62 | 25.98 | 45.908 | 6.35 | 1.346 | 4.699 | 8427.17 | 2.12 | 97.8 | 77.7 | 1383 | 23 | 5477.7 | 2880.5 | 2789.8 | 4126.5 | 1196.7 | 0.68084 | 6.045
2024-12-09 | 17:36 | Data | 0 | 32.717 | 30.826 | 187.579 | 7.64 | 176.233 | 2128.52 | 25.99 | 45.998 | 6.35 | 1.341 | 4.683 | 8440.74 | 2.187 | 97.8 | 77.7 | 1384 | 23 | 5486.5 | 2888.5 | 2807.1 | 4148.7 | 1196.7 | 0.67903 | 6.025
2024-12-09 | 17:37 | Data | 0 | 32.831 | 30.766 | 187.443 | 7.63 | 176.233 | 2131.24 | 25.97 | 45.727 | 6.35 | 1.34 | 4.664 | 8427.17 | 2.268 | 97.9 | 77.7 | 1384 | 22.86 | 5477.7 | 2900.7 | 2781.9 | 4137 | 1196.7 | 0.68449 | 6.004
2024-12-09 | 17:37 | Data | 0 | 33.054 | 30.651 | 187.76 | 7.64 | 176.278 | 2128.52 | 25.98 | 45.637 | 6.34 | 1.359 | 4.679 | 8431.69 | 1.911 | 97.9 | 77.5 | 1383 | 22.91 | 5480.6 | 2922 | 2787.4 | 4152.8 | 1196.7 | 0.685 | 6.038
2024-12-09 | 17:37 | Data | 0 | 33.054 | 30.772 | 187.67 | 7.64 | 176.323 | 2128.52 | 25.98 | 45.637 | 6.35 | 1.354 | 4.668 | 8440.74 | 2.1 | 97.9 | 77.5 | 1384 | 22.86 | 5486.5 | 2911.1 | 2802.5 | 4153.7 | 1196.7 | 0.68436 | 6.022
2024-12-09 | 17:37 | Data | 0 | 32.717 | 30.867 | 187.624 | 7.64 | 176.233 | 2128.52 | 25.99 | 45.908 | 6.35 | 1.34 | 4.683 | 8454.3 | 2.046 | 97.9 | 77.7 | 1383 | 22.86 | 5495.3 | 2899.6 | 2809.4 | 4152.9 | 1196.7 | 0.68154 | 6.023
2024-12-09 | 17:37 | Data | 0 | 32.919 | 30.88 | 187.579 | 7.64 | 176.233 | 2128.52 | 25.99 | 45.637 | 6.35 | 1.346 | 4.705 | 8418.13 | 2.066 | 97.9 | 77.8 | 1384 | 22.82 | 5471.8 | 2907.7 | 2788.9 | 4148 | 1196.7 | 0.68439 | 6.051
2024-12-09 | 17:37 | Data | 0 | 32.723 | 30.867 | 187.624 | 7.64 | 176.233 | 2127.62 | 25.99 | 45.727 | 6.34 | 1.334 | 4.656 | 8422.65 | 2.066 | 97.9 | 77.7 | 1383 | 22.86 | 5474.7 | 2892.2 | 2813.4 | 4153.5 | 1196.8 | 0.67923 | 5.99
2024-12-09 | 17:37 | Data | 0 | 32.994 | 30.732 | 187.67 | 7.64 | 176.323 | 2127.62 | 25.98 | 45.727 | 6.34 | 1.348 | 4.67 | 8390.99 | 2.16 | 97.9 | 77.6 | 1383 | 22.82 | 5454.1 | 2896.2 | 2725.6 | 4093.8 | 1196.8 | 0.69279 | 6.018
2024-12-09 | 17:37 | Data | 0 | 32.717 | 30.651 | 187.489 | 7.64 | 176.187 | 2124.91 | 25.99 | 45.727 | 6.35 | 1.354 | 4.668 | 8386.47 | 2.167 | 97.8 | 77.5 | 1382 | 22.86 | 5451.2 | 2910.9 | 2804 | 4155.9 | 1196.8 | 0.68368 | 6.022
2024-12-09 | 17:37 | Data | 0 | 32.723 | 30.658 | 187.624 | 7.64 | 176.187 | 2125.81 | 25.99 | 45.727 | 6.35 | 1.343 | 4.666 | 8404.56 | 2.059 | 97.9 | 77.7 | 1382 | 22.77 | 5463 | 2903.7 | 2785.7 | 4134 | 1196.8 | 0.68474 | 6.009
2024-12-09 | 17:37 | Data | 0 | 32.555 | 30.475 | 187.534 | 7.64 | 176.187 | 2122.2 | 25.97 | 45.998 | 6.34 | 1.349 | 4.687 | 8400.04 | 2.14 | 97.8 | 77.6 | 1379 | 22.95 | 5460 | 2899.6 | 2790 | 4132.7 | 1196.8 | 0.68446 | 6.036
2024-12-09 | 17:37 | Data | 0 | 33.169 | 30.718 | 187.624 | 7.64 | 176.323 | 2123.1 | 25.98 | 45.727 | 6.34 | 1.337 | 4.66 | 8395.51 | 2.147 | 97.8 | 77.7 | 1380 | 22.86 | 5457.1 | 2893.1 | 2773.3 | 4125.7 | 1196.8 | 0.68522 | 5.998
2024-12-09 | 17:37 | Data | 0 | 33.122 | 30.577 | 187.534 | 7.64 | 176.278 | 2123.1 | 25.98 | 45.727 | 6.35 | 1.336 | 4.668 | 8400.04 | 2.181 | 97.8 | 77.8 | 1380 | 22.86 | 5460 | 2917.9 | 2792.5 | 4157.7 | 1196.8 | 0.6859 | 6.004
2024-12-09 | 17:37 | Data | 0 | 32.723 | 30.651 | 187.579 | 7.64 | 176.187 | 2116.78 | 25.99 | 45.818 | 6.35 | 1.343 | 4.668 | 8400.04 | 2.1 | 97.8 | 77.7 | 1377 | 22.91 | 5460 | 2890.5 | 2785.1 | 4134.2 | 1196.8 | 0.68469 | 6.011
2024-12-09 | 17:37 | Data | 0 | 32.494 | 30.644 | 187.534 | 7.64 | 176.187 | 2123.1 | 25.99 | 45.818 | 6.35 | 1.345 | 4.68 | 8386.47 | 2.073 | 97.8 | 77.7 | 1380 | 22.91 | 5451.2 | 2887.1 | 2790 | 4132.3 | 1196.8 | 0.68294 | 6.026
2024-12-09 | 17:37 | Data | 0 | 32.514 | 30.644 | 187.624 | 7.64 | 176.233 | 2123.1 | 25.98 | 45.637 | 6.35 | 1.346 | 4.685 | 8390.99 | 1.87 | 97.8 | 77.7 | 1379 | 22.86 | 5454.1 | 2899.9 | 2776.5 | 4131.8 | 1196.8 | 0.68614 | 6.031
2024-12-09 | 17:37 | Data | 0 | 32.953 | 30.658 | 187.624 | 7.64 | 176.278 | 2123.1 | 25.98 | 45.818 | 6.35 | 1.348 | 4.675 | 8418.13 | 1.978 | 97.8 | 77.6 | 1380 | 22.91 | 5471.8 | 2904.4 | 2763.1 | 4124.6 | 1196.8 | 0.68873 | 6.025
2024-12-09 | 17:37 | Data | 0 | 32.737 | 30.658 | 187.534 | 7.63 | 176.323 | 2124.01 | 25.98 | 45.908 | 6.35 | 1.354 | 4.663 | 8409.08 | 1.958 | 97.8 | 77.5 | 1381 | 23 | 5465.9 | 2897.4 | 2776.5 | 4132.6 | 1196.8 | 0.68438 | 6.017
2024-12-09 | 17:38 | Data | 0 | 32.926 | 30.678 | 187.534 | 7.64 | 176.187 | 2121.29 | 25.98 | 45.998 | 6.35 | 1.347 | 4.673 | 8422.65 | 2.066 | 97.8 | 77.7 | 1379 | 23 | 5474.7 | 2897.2 | 2771.3 | 4127 | 1196.8 | 0.68582 | 6.017
2024-12-09 | 17:38 | Data | 0 | 32.413 | 30.536 | 187.624 | 7.64 | 176.233 | 2126.72 | 25.98 | 45.908 | 6.35 | 1.344 | 4.669 | 8427.17 | 1.978 | 97.8 | 77.6 | 1383 | 22.91 | 5477.7 | 2890.1 | 2789.7 | 4132.4 | 1196.8 | 0.68237 | 6.013
2024-12-09 | 17:38 | Data | 0 | 32.514 | 30.415 | 187.534 | 7.64 | 176.187 | 2122.2 | 25.96 | 45.998 | 6.34 | 1.347 | 4.674 | 8445.26 | 2.073 | 97.8 | 77.6 | 1381 | 23 | 5489.4 | 2917.1 | 2785.7 | 4148.8 | 1196.8 | 0.68658 | 6.021
2024-12-09 | 17:38 | Data | 0 | 32.723 | 30.637 | 187.624 | 7.64 | 176.278 | 2122.2 | 25.98 | 45.908 | 6.35 | 1.356 | 4.694 | 8476.91 | 2.12 | 97.8 | 77.6 | 1380 | 23 | 5510 | 2909 | 2810.9 | 4163.2 | 1196.8 | 0.68302 | 6.05
2024-12-09 | 17:38 | Data | 0 | 32.75 | 30.678 | 187.579 | 7.63 | 176.187 | 2122.2 | 25.98 | 45.908 | 6.34 | 1.358 | 4.692 | 8481.44 | 1.971 | 97.8 | 77.6 | 1380 | 23 | 5512.9 | 2899.6 | 2793.7 | 4144.7 | 1196.8 | 0.68342 | 6.049
2024-12-09 | 17:38 | Data | 0 | 32.696 | 30.428 | 187.443 | 7.63 | 176.187 | 2123.1 | 25.99 | 45.998 | 6.34 | 1.355 | 4.689 | 8481.44 | 2.16 | 97.8 | 77.6 | 1380 | 23 | 5512.9 | 2894.7 | 2785.4 | 4138 | 1196.8 | 0.68204 | 6.043
2024-12-09 | 17:38 | Data | 0 | 32.865 | 30.894 | 187.624 | 7.64 | 176.233 | 2122.2 | 25.98 | 45.998 | 6.34 | 1.351 | 4.693 | 8485.96 | 2.086 | 97.8 | 77.6 | 1379 | 23 | 5515.9 | 2903.5 | 2779.9 | 4136.3 | 1196.8 | 0.68647 | 6.045
2024-12-09 | 17:38 | Data | 0 | 32.494 | 30.421 | 187.624 | 7.64 | 176.142 | 2119.49 | 25.98 | 45.998 | 6.35 | 1.348 | 4.673 | 8467.87 | 2.073 | 97.8 | 77.6 | 1378 | 22.95 | 5504.1 | 2903.5 | 2777 | 4134.5 | 1196.8 | 0.68641 | 6.022
2024-12-09 | 17:38 | Data | 0 | 32.811 | 30.664 | 187.624 | 7.64 | 176.233 | 2122.2 | 25.98 | 45.998 | 6.35 | 1.353 | 4.645 | 8485.96 | 2.066 | 97.8 | 77.4 | 1381 | 23 | 5515.9 | 2916.3 | 2789.5 | 4150 | 1196.8 | 0.68655 | 5.998
2024-12-09 | 17:38 | Data | 0 | 32.615 | 30.678 | 187.534 | 7.63 | 176.323 | 2123.1 | 25.98 | 45.998 | 6.34 | 1.352 | 4.674 | 8481.44 | 2.005 | 97.8 | 77.6 | 1380 | 23 | 5512.9 | 2893 | 2790.2 | 4136.2 | 1196.8 | 0.68373 | 6.026
2024-12-09 | 17:38 | Data | 0 | 32.636 | 30.799 | 187.579 | 7.63 | 176.233 | 2124.91 | 25.98 | 45.998 | 6.34 | 1.352 | 4.666 | 8495 | 1.904 | 97.8 | 77.5 | 1381 | 23 | 5521.8 | 2881.2 | 2786.6 | 4139.5 | 1196.8 | 0.68397 | 6.018
2024-12-09 | 17:38 | Data | 0 | 32.723 | 30.671 | 187.579 | 7.63 | 176.187 | 2123.1 | 25.99 | 45.908 | 6.35 | 1.355 | 4.67 | 8508.57 | 2.052 | 97.8 | 77.5 | 1380 | 22.91 | 5530.6 | 2892.1 | 2796 | 4139 | 1196.8 | 0.68273 | 6.026
2024-12-09 | 17:38 | Data | 0 | 32.696 | 30.651 | 187.624 | 7.64 | 176.323 | 2123.1 | 25.98 | 45.908 | 6.35 | 1.355 | 4.701 | 8508.57 | 2.066 | 97.8 | 77.6 | 1380 | 23 | 5530.6 | 2915.3 | 2788.1 | 4153.3 | 1196.8 | 0.68597 | 6.056
2024-12-09 | 17:38 | Data | 0 | 33.095 | 30.772 | 187.715 | 7.64 | 176.323 | 2122.2 | 25.98 | 45.908 | 6.35 | 1.351 | 4.689 | 8508.57 | 2.228 | 97.8 | 77.6 | 1380 | 23.04 | 5530.6 | 2892.1 | 2770.6 | 4120.9 | 1196.8 | 0.6871 | 6.042
2024-12-09 | 17:38 | Data | 0 | 32.717 | 30.847 | 187.489 | 7.63 | 176.323 | 2123.1 | 25.96 | 45.908 | 6.35 | 1.356 | 4.673 | 8517.61 | 1.904 | 97.8 | 77.5 | 1379 | 22.95 | 5536.4 | 2896.1 | 2777.4 | 4132.5 | 1196.8 | 0.68415 | 6.027
2024-12-09 | 17:38 | Data | 0 | 33.108 | 30.941 | 187.579 | 7.63 | 176.368 | 2125.81 | 25.97 | 45.998 | 6.35 | 1.357 | 4.68 | 8495 | 2.106 | 97.8 | 77.5 | 1381 | 23.04 | 5521.8 | 2899.9 | 2791.7 | 4138.9 | 1196.8 | 0.68423 | 6.036
2024-12-09 | 17:38 | Data | 0 | 33.135 | 30.907 | 187.67 | 7.64 | 176.323 | 2128.52 | 25.98 | 45.908 | 6.34 | 1.354 | 4.684 | 8495 | 2.079 | 97.8 | 77.6 | 1383 | 22.95 | 5521.8 | 2890.3 | 2797.9 | 4143.5 | 1196.8 | 0.68247 | 6.038
2024-12-09 | 17:38 | Data | 0 | 32.946 | 30.732 | 187.624 | 7.63 | 176.323 | 2126.72 | 25.99 | 45.908 | 6.35 | 1.357 | 4.664 | 8495 | 1.978 | 97.8 | 77.5 | 1382 | 22.95 | 5521.8 | 2887.1 | 2785.9 | 4128.7 | 1196.8 | 0.68363 | 6.019
2024-12-09 | 17:38 | Data | 0 | 32.825 | 30.664 | 187.67 | 7.63 | 176.278 | 2127.62 | 25.98 | 46.269 | 6.35 | 1.351 | 4.685 | 8495 | 2.073 | 97.8 | 77.6 | 1384 | 23.18 | 5521.8 | 2918.4 | 2797.4 | 4158.6 | 1196.8 | 0.68381 | 6.036
2024-12-09 | 17:39 | Data | 0 | 32.494 | 30.921 | 187.534 | 7.64 | 176.278 | 2128.52 | 25.97 | 45.998 | 6.34 | 1.355 | 4.675 | 8472.39 | 2.073 | 97.8 | 77.5 | 1384 | 23 | 5507.1 | 2899.3 | 2795.1 | 4147.7 | 1196.8 | 0.68215 | 6.03
2024-12-09 | 17:39 | Data | 0 | 32.501 | 30.651 | 187.489 | 7.63 | 176.233 | 2128.52 | 25.99 | 45.998 | 6.35 | 1.347 | 4.689 | 8472.39 | 1.85 | 97.8 | 77.7 | 1384 | 22.95 | 5507.1 | 2892.9 | 2783.9 | 4135.6 | 1196.8 | 0.68353 | 6.036
2024-12-09 | 17:39 | Data | 0 | 33.034 | 30.887 | 187.67 | 7.64 | 176.187 | 2128.52 | 25.98 | 45.998 | 6.35 | 1.344 | 4.671 | 8458.83 | 2.241 | 97.8 | 77.7 | 1384 | 23 | 5498.2 | 2891.1 | 2781 | 4130 | 1196.8 | 0.68295 | 6.015
2024-12-09 | 17:39 | Data | 0 | 32.717 | 30.624 | 187.579 | 7.63 | 176.233 | 2124.01 | 25.99 | 45.908 | 6.35 | 1.348 | 4.662 | 8463.35 | 2.127 | 97.8 | 77.6 | 1381 | 23 | 5501.2 | 1823.1 | 2227.3 | 2890.2 | 1196.8 | 0.62772 | 6.007
2024-12-09 | 17:39 | Data | 0 | 32.723 | 30.651 | 187.534 | 7.64 | 176.142 | 2124.91 | 25.97 | 45.908 | 6.35 | 1.354 | 4.683 | 8458.83 | 2.079 | 97.8 | 77.6 | 1381 | 22.95 | 5498.2 | 1819.5 | 2238.1 | 2899.1 | 1196.8 | 0.62487 | 6.036
2024-12-09 | 17:39 | Data | 0 | 32.75 | 30.718 | 187.579 | 7.63 | 176.323 | 2124.91 | 25.98 | 45.998 | 6.34 | 1.345 | 4.675 | 8472.39 | 2.005 | 97.8 | 77.7 | 1381 | 22.95 | 5507.1 | 1809.2 | 2235.5 | 2920.1 | 1196.8 | 0.62523 | 6.019
2024-12-09 | 17:39 | Data | 0 | 32.946 | 30.712 | 187.579 | 7.63 | 176.368 | 2125.81 | 25.99 | 45.998 | 6.35 | 1.345 | 4.672 | 8458.83 | 2.052 | 97.8 | 77.6 | 1382 | 23 | 5498.2 | 1813.5 | 2236.5 | 2890.9 | 1196.8 | 0.62512 | 6.017
2024-12-09 | 17:39 | Data | 0 | 32.669 | 30.651 | 187.579 | 7.64 | 176.323 | 2125.81 | 25.97 | 45.998 | 6.34 | 1.344 | 4.684 | 8454.3 | 2.228 | 97.8 | 77.7 | 1382 | 23 | 5495.3 | 1821.4 | 2232.3 | 2893.3 | 1196.8 | 0.62667 | 6.028
2024-12-09 | 17:39 | Data | 0 | 32.723 | 30.428 | 187.579 | 7.64 | 176.278 | 2127.62 | 25.97 | 45.998 | 6.34 | 1.343 | 4.679 | 8467.87 | 2.241 | 97.8 | 77.7 | 1382 | 23 | 5504.1 | 1836.7 | 2235.3 | 2903.5 | 1196.8 | 0.63057 | 6.02
2024-12-09 | 17:39 | Data | 0 | 32.825 | 30.664 | 187.534 | 7.64 | 176.278 | 2127.62 | 25.98 | 45.908 | 6.34 | 1.354 | 4.675 | 8467.87 | 2.262 | 97.8 | 77.5 | 1384 | 22.95 | 5504.1 | 1811.4 | 2217.6 | 2875.3 | 1196.9 | 0.62754 | 6.029
2024-12-09 | 17:39 | Data | 0 | 32.582 | 30.55 | 187.579 | 7.63 | 176.233 | 2128.52 | 25.98 | 45.908 | 6.34 | 1.348 | 4.684 | 8458.83 | 2.437 | 97.8 | 77.7 | 1383 | 23 | 5498.2 | 1813 | 2216.5 | 2874.9 | 1196.9 | 0.62795 | 6.031
2024-12-09 | 17:39 | Data | 0 | 32.501 | 30.651 | 187.579 | 7.63 | 176.142 | 2127.62 | 25.97 | 45.908 | 6.35 | 1.347 | 4.689 | 8467.87 | 1.958 | 97.8 | 77.7 | 1383 | 23 | 5504.1 | 1817.6 | 2230.8 | 2890 | 1196.9 | 0.62582 | 6.034
2024-12-09 | 17:39 | Data | 0 | 32.75 | 30.421 | 187.534 | 7.64 | 176.233 | 2128.52 | 25.98 | 45.998 | 6.34 | 1.351 | 4.683 | 8472.39 | 2.12 | 97.8 | 77.6 | 1384 | 23 | 5507.1 | 1819.9 | 2245.6 | 2902.5 | 1196.9 | 0.62461 | 6.035
2024-12-09 | 17:39 | Data | 0 | 32.609 | 30.448 | 187.534 | 7.64 | 176.278 | 2128.52 | 25.97 | 45.908 | 6.34 | 1.36 | 4.658 | 8476.91 | 2.059 | 97.8 | 77.4 | 1384 | 23 | 5510 | 1822.4 | 2232.4 | 2893.5 | 1196.9 | 0.6276 | 6.017
2024-12-09 | 17:39 | Data | 0 | 32.507 | 30.421 | 187.489 | 7.63 | 176.142 | 2130.33 | 25.98 | 45.998 | 6.34 | 1.354 | 4.652 | 8463.35 | 2.025 | 97.8 | 77.4 | 1385 | 22.95 | 5501.2 | 1823.2 | 2247.1 | 2906.3 | 1196.9 | 0.62448 | 6.007
2024-12-09 | 17:39 | Data | 0 | 32.791 | 30.853 | 187.67 | 7.63 | 176.413 | 2130.33 | 25.98 | 45.998 | 6.34 | 1.353 | 4.653 | 8454.3 | 1.796 | 97.8 | 77.5 | 1385 | 22.95 | 5495.3 | 1819 | 2239.2 | 2896.6 | 1196.9 | 0.62667 | 6.006
2024-12-09 | 17:39 | Data | 0 | 32.879 | 31.09 | 187.715 | 7.64 | 176.323 | 2130.33 | 25.97 | 45.908 | 6.35 | 1.346 | 4.668 | 8449.78 | 2.052 | 97.8 | 77.6 | 1385 | 22.95 | 5492.4 | 1810.1 | 2220.2 | 2874.5 | 1196.9 | 0.62541 | 6.015
2024-12-09 | 17:40 | Data | 0 | 33.054 | 30.658 | 187.624 | 7.64 | 176.368 | 2124.91 | 25.97 | 45.998 | 6.34 | 1.356 | 4.674 | 8458.83 | 1.958 | 97.8 | 77.5 | 1381 | 23 | 5498.2 | 1803.8 | 2221 | 2874.3 | 1196.9 | 0.62412 | 6.03
2024-12-09 | 17:40 | Data | 0 | 32.501 | 30.651 | 187.534 | 7.63 | 176.233 | 2125.81 | 25.98 | 45.998 | 6.35 | 1.352 | 4.665 | 8467.87 | 2.046 | 97.8 | 77.5 | 1382 | 23 | 5504.1 | 1826.1 | 2205.7 | 2876.9 | 1196.9 | 0.63186 | 6.017
2024-12-09 | 17:40 | Data | 0 | 32.501 | 30.475 | 187.534 | 7.64 | 176.278 | 2125.81 | 25.98 | 45.908 | 6.35 | 1.346 | 4.66 | 8463.35 | 2.133 | 97.8 | 77.6 | 1382 | 22.95 | 5501.2 | 1805.6 | 2243 | 2890.6 | 1196.9 | 0.62256 | 6.006
2024-12-09 | 17:40 | Data | 0 | 32.723 | 30.651 | 187.489 | 7.64 | 176.187 | 2125.81 | 25.98 | 45.998 | 6.35 | 1.347 | 4.677 | 8481.44 | 2.066 | 97.8 | 77.6 | 1382 | 23 | 5512.9 | 1828.3 | 2216.1 | 2884.9 | 1196.9 | 0.63061 | 6.024
2024-12-09 | 17:40 | Data | 0 | 32.804 | 30.448 | 187.534 | 7.64 | 176.278 | 2125.81 | 25.98 | 45.998 | 6.35 | 1.346 | 4.683 | 8463.35 | 2.208 | 97.8 | 77.7 | 1382 | 23 | 5501.2 | 1819.2 | 2216.2 | 2870.6 | 1196.9 | 0.627 | 6.028
2024-12-09 | 17:40 | Data | 0 | 33.007 | 30.712 | 187.579 | 7.64 | 176.233 | 2129.43 | 25.98 | 45.998 | 6.35 | 1.353 | 4.676 | 8440.74 | 2.093 | 97.8 | 77.6 | 1384 | 22.95 | 5486.5 | 1837.9 | 2208.5 | 2882.7 | 1196.9 | 0.63119 | 6.028
2024-12-09 | 17:40 | Data | 0 | 32.717 | 30.766 | 187.579 | 7.64 | 176.233 | 2124.91 | 25.98 | 45.998 | 6.36 | 1.34 | 4.668 | 8454.3 | 2.073 | 97.8 | 77.7 | 1381 | 22.91 | 5495.3 | 1821.6 | 2193.9 | 2862.8 | 1196.9 | 0.63413 | 6.008
2024-12-09 | 17:40 | Data | 0 | 33.054 | 30.685 | 187.624 | 7.63 | 176.233 | 2128.52 | 25.97 | 45.908 | 6.35 | 1.344 | 4.673 | 8458.83 | 2.262 | 97.8 | 77.7 | 1384 | 22.95 | 5498.2 | 1814.8 | 2208.9 | 2871.2 | 1196.9 | 0.63145 | 6.017
2024-12-09 | 17:40 | Data | 0 | 32.885 | 30.59 | 187.67 | 7.64 | 176.278 | 2129.43 | 25.98 | 45.998 | 6.35 | 1.355 | 4.675 | 8454.3 | 2.066 | 97.8 | 77.5 | 1384 | 23 | 5495.3 | 1820.5 | 2224.5 | 2886.4 | 1196.9 | 0.62331 | 6.03
2024-12-09 | 17:40 | Data | 0 | 32.777 | 30.502 | 187.67 | 7.64 | 176.233 | 2129.43 | 25.98 | 45.998 | 6.34 | 1.351 | 4.68 | 8467.87 | 2.147 | 97.8 | 77.6 | 1384 | 22.91 | 5504.1 | 1824.1 | 2227.6 | 2889.9 | 1196.9 | 0.62875 | 6.032
2024-12-09 | 17:40 | Data | 0 | 32.831 | 30.867 | 187.67 | 7.64 | 176.233 | 2122.2 | 25.97 | 45.998 | 6.35 | 1.353 | 4.669 | 8481.44 | 2.073 | 97.8 | 77.5 | 1379 | 23 | 5512.9 | 1846.1 | 2246.4 | 2917.3 | 1196.9 | 0.6301 | 6.022
2024-12-09 | 17:40 | Data | 0 | 32.494 | 30.428 | 187.534 | 7.63 | 176.142 | 2129.43 | 25.98 | 45.818 | 6.34 | 1.352 | 4.675 | 8458.83 | 2.032 | 97.8 | 77.6 | 1384 | 22.95 | 5498.2 | 1801.5 | 2262.9 | 2904.7 | 1196.9 | 0.61773 | 6.027
2024-12-09 | 17:40 | Data | 0 | 32.723 | 30.536 | 187.579 | 7.64 | 176.278 | 2127.62 | 25.97 | 45.998 | 6.34 | 1.349 | 4.687 | 8445.26 | 1.87 | 97.8 | 77.6 | 1383 | 22.95 | 5489.4 | 1823.8 | 2264.5 | 2919.8 | 1196.9 | 0.61935 | 6.036
2024-12-09 | 17:40 | Data | 0 | 32.669 | 30.826 | 187.534 | 7.64 | 176.187 | 2127.62 | 25.97 | 45.908 | 6.35 | 1.356 | 4.677 | 8440.74 | 2.113 | 97.8 | 77.5 | 1383 | 23 | 5486.5 | 1823.3 | 2250 | 2925.2 | 1196.9 | 0.62469 | 6.033
2024-12-09 | 17:40 | Data | 0 | 32.669 | 30.644 | 187.534 | 7.64 | 176.142 | 2126.72 | 25.97 | 45.998 | 6.35 | 1.344 | 4.686 | 8445.26 | 2.073 | 97.8 | 77.7 | 1382 | 23.04 | 5489.4 | 1817.7 | 2243.9 | 2906.8 | 1196.9 | 0.62533 | 6.03
2024-12-09 | 17:40 | Data | 0 | 32.737 | 30.664 | 187.534 | 7.64 | 176.323 | 2128.52 | 25.97 | 45.998 | 6.35 | 1.337 | 4.689 | 8431.69 | 2.052 | 97.8 | 77.8 | 1384 | 22.95 | 5480.6 | 1812.8 | 2221.8 | 2879.9 | 1196.9 | 0.62737 | 6.025
2024-12-09 | 17:40 | Data | 0 | 32.521 | 30.82 | 187.443 | 7.64 | 176.187 | 2128.52 | 25.98 | 45.908 | 6.35 | 1.351 | 4.664 | 8454.3 | 1.965 | 97.8 | 77.5 | 1384 | 23 | 5495.3 | 1812.7 | 2233 | 2887.3 | 1196.9 | 0.62384 | 6.016
2024-12-09 | 17:40 | Data | 0 | 32.528 | 30.651 | 187.579 | 7.64 | 176.142 | 2126.72 | 25.96 | 45.908 | 6.35 | 1.345 | 4.655 | 8445.26 | 1.863 | 97.8 | 77.6 | 1383 | 22.95 | 5489.4 | 1814.5 | 2221.6 | 2905.5 | 1196.9 | 0.62902 | 6.001
2024-12-09 | 17:41 | Data | 0 | 32.892 | 30.651 | 187.534 | 7.63 | 176.233 | 2127.62 | 25.98 | 45.998 | 6.35 | 1.352 | 4.66 | 8445.26 | 2.093 | 97.8 | 77.5 | 1383 | 22.95 | 5489.4 | 1828.7 | 2229.8 | 2895.8 | 1196.9 | 0.62921 | 6.013
2024-12-09 | 17:41 | Data | 0 | 32.723 | 30.469 | 187.534 | 7.64 | 176.187 | 2128.52 | 25.98 | 45.457 | 6.35 | 1.348 | 4.664 | 8458.83 | 2.1 | 97.9 | 77.6 | 1384 | 22.68 | 5498.2 | 1816.1 | 2244.8 | 2900 | 1196.9 | 0.62344 | 6.012
2024-12-09 | 17:41 | Data | 0 | 32.723 | 30.651 | 187.534 | 7.63 | 176.233 | 2128.52 | 25.97 | 45.998 | 6.35 | 1.351 | 4.686 | 8454.3 | 2.073 | 97.8 | 77.6 | 1383 | 23 | 5495.3 | 1810.8 | 2220.8 | 2878.7 | 1196.9 | 0.62533 | 6.037
2024-12-09 | 17:41 | Data | 0 | 32.602 | 30.421 | 187.534 | 7.64 | 176.233 | 2127.62 | 25.98 | 45.998 | 6.35 | 1.354 | 4.666 | 8463.35 | 2.093 | 97.8 | 77.5 | 1384 | 22.95 | 5501.2 | 1825.5 | 2234.7 | 2899.5 | 1196.9 | 0.62606 | 6.02
2024-12-09 | 17:41 | Data | 0 | 32.953 | 30.421 | 187.579 | 7.63 | 176.233 | 2128.52 | 25.98 | 45.998 | 6.34 | 1.353 | 4.675 | 8449.78 | 2.093 | 97.8 | 77.6 | 1382 | 23 | 5492.4 | 1827.2 | 2242.7 | 2903.3 | 1196.9 | 0.62717 | 6.026
2024-12-09 | 17:41 | Data | 0 | 32.723 | 30.442 | 187.489 | 7.64 | 176.187 | 2127.62 | 25.97 | 45.998 | 6.35 | 1.351 | 4.683 | 8440.74 | 1.931 | 97.8 | 77.6 | 1384 | 22.95 | 5486.5 | 1823.6 | 2225.4 | 2891.4 | 1196.9 | 0.62726 | 6.034
2024-12-09 | 17:41 | Data | 0 | 32.696 | 30.901 | 187.534 | 7.64 | 176.233 | 2127.62 | 25.98 | 45.908 | 6.34 | 1.352 | 4.671 | 8454.3 | 2.019 | 97.8 | 77.5 | 1383 | 23 | 5495.3 | 1829.8 | 2257.4 | 2917.3 | 1196.9 | 0.62519 | 6.025
2024-12-09 | 17:41 | Data | 0 | 32.467 | 30.637 | 187.489 | 7.64 | 176.187 | 2127.62 | 25.98 | 45.998 | 6.35 | 1.355 | 4.673 | 8454.3 | 2.025 | 97.8 | 77.5 | 1384 | 23 | 5495.3 | 1825.1 | 2236.1 | 2896.2 | 1196.9 | 0.62794 | 6.029
2024-12-09 | 17:41 | Data | 0 | 32.609 | 30.867 | 187.534 | 7.64 | 176.233 | 2123.1 | 25.98 | 45.998 | 6.35 | 1.354 | 4.699 | 8449.78 | 1.85 | 97.8 | 77.6 | 1380 | 23 | 5492.4 | 1830.9 | 2245.4 | 2908.9 | 1196.9 | 0.62715 | 6.053
2024-12-09 | 17:41 | Data | 0 | 32.494 | 30.415 | 187.443 | 7.63 | 176.097 | 2128.52 | 25.98 | 45.908 | 6.34 | 1.348 | 4.675 | 8449.78 | 2.079 | 97.8 | 77.6 | 1384 | 22.95 | 5492.4 | 1812.2 | 2244.5 | 2904.1 | 1196.9 | 0.62448 | 6.024
2024-12-09 | 17:41 | Data | 0 | 32.906 | 30.455 | 187.534 | 7.63 | 176.187 | 2128.52 | 25.97 | 45.998 | 6.35 | 1.351 | 4.7 | 8458.83 | 2.16 | 97.8 | 77.7 | 1384 | 23.04 | 5498.2 | 1828.7 | 2255.9 | 2916 | 1196.9 | 0.62459 | 6.051
2024-12-09 | 17:41 | Data | 0 | 32.507 | 30.442 | 187.579 | 7.64 | 176.278 | 2125.81 | 25.98 | 45.998 | 6.34 | 1.351 | 4.699 | 8454.3 | 1.971 | 97.8 | 77.7 | 1382 | 23 | 5495.3 | 1834 | 2256.5 | 2919.9 | 1196.9 | 0.62558 | 6.049
2024-12-09 | 17:41 | Data | 0 | 32.946 | 30.55 | 187.624 | 7.63 | 176.233 | 2124.91 | 25.97 | 45.998 | 6.35 | 1.345 | 4.65 | 8427.17 | 2.106 | 97.8 | 77.6 | 1381 | 23 | 5477.7 | 1843.2 | 2243.3 | 2915.5 | 1196.9 | 0.6295 | 5.996
2024-12-09 | 17:41 | Data | 0 | 32.885 | 30.651 | 187.534 | 7.64 | 176.278 | 2127.62 | 25.97 | 45.908 | 6.35 | 1.343 | 4.657 | 8440.74 | 2.12 | 97.8 | 77.6 | 1382 | 23 | 5486.5 | 1813.7 | 2240 | 2894.9 | 1196.9 | 0.62836 | 5.999
2024-12-09 | 17:41 | Data | 0 | 32.494 | 30.597 | 187.489 | 7.63 | 176.142 | 2124.91 | 25.98 | 45.908 | 6.35 | 1.346 | 4.654 | 8431.69 | 2.147 | 97.8 | 77.6 | 1382 | 22.95 | 5480.6 | 1827.9 | 2233 | 2897.7 | 1196.9 | 0.62795 | 6
2024-12-09 | 17:41 | Data | 0 | 32.696 | 30.853 | 187.534 | 7.64 | 176.233 | 2124.91 | 25.98 | 45.908 | 6.35 | 1.356 | 4.679 | 8418.13 | 2.127 | 97.8 | 77.5 | 1382 | 22.95 | 5471.8 | 1810.7 | 2220.8 | 2879.4 | 1196.9 | 0.6261 | 6.036
2024-12-09 | 17:41 | Data | 0 | 32.494 | 30.739 | 187.489 | 7.63 | 176.142 | 2125.81 | 25.98 | 45.908 | 6.35 | 1.34 | 4.683 | 8431.69 | 2.039 | 97.8 | 77.7 | 1381 | 22.95 | 5480.6 | 1825.9 | 2243.7 | 2905.6 | 1196.9 | 0.62606 | 6.024
2024-12-09 | 17:42 | Data | 0 | 32.494 | 30.644 | 187.398 | 7.63 | 176.142 | 2125.81 | 25.98 | 45.908 | 6.35 | 1.353 | 4.672 | 8409.08 | 2.073 | 97.8 | 77.5 | 1382 | 23 | 5465.9 | 1812.2 | 2233.7 | 2888.5 | 1196.9 | 0.62625 | 6.025
2024-12-09 | 17:42 | Data | 0 | 32.777 | 30.421 | 187.489 | 7.64 | 176.233 | 2124.91 | 25.98 | 45.908 | 6.35 | 1.348 | 4.667 | 8418.13 | 2.113 | 97.8 | 77.6 | 1381 | 22.95 | 5471.8 | 1808.5 | 2215 | 2872.3 | 1196.9 | 0.62706 | 6.015
2024-12-09 | 17:42 | Data | 0 | 32.514 | 30.415 | 187.443 | 7.64 | 176.097 | 2124.91 | 25.98 | 45.998 | 6.35 | 1.342 | 4.669 | 8431.69 | 2.079 | 97.8 | 77.7 | 1381 | 23 | 5480.6 | 2163.8 | 3043.9 | 3765.5 | 1196.9 | 0.60108 | 6.01
2024-12-09 | 17:42 | Data | 0 | 32.494 | 30.583 | 187.534 | 7.64 | 176.097 | 2124.91 | 25.98 | 45.908 | 6.35 | 1.349 | 4.684 | 8431.69 | 2.12 | 97.8 | 77.7 | 1381 | 22.91 | 5480.6 | 2906 | 2814.4 | 4164.9 | 1196.9 | 0.68051 | 6.035
2024-12-09 | 17:42 | Data | 0 | 32.48 | 30.536 | 187.489 | 7.63 | 176.097 | 2124.91 | 25.97 | 45.998 | 6.35 | 1.363 | 4.685 | 8427.17 | 2.194 | 97.8 | 77.5 | 1381 | 23 | 5477.7 | 2904 | 2818.6 | 4168.9 | 1196.9 | 0.67999 | 6.049
2024-12-09 | 17:42 | Data | 0 | 32.386 | 30.583 | 187.489 | 7.63 | 176.097 | 2124.91 | 25.98 | 45.908 | 6.35 | 1.354 | 4.674 | 8418.13 | 1.944 | 97.8 | 77.5 | 1382 | 22.95 | 5471.8 | 2906.3 | 2836.1 | 4180 | 1196.9 | 0.67941 | 6.028
2024-12-09 | 17:42 | Data | 0 | 32.561 | 30.428 | 187.534 | 7.64 | 176.233 | 2125.81 | 25.98 | 45.998 | 6.34 | 1.346 | 4.671 | 8431.69 | 1.951 | 97.8 | 77.6 | 1381 | 22.95 | 5480.6 | 2899.6 | 2853.4 | 4188.4 | 1196.9 | 0.67656 | 6.017
2024-12-09 | 17:42 | Data | 0 | 32.467 | 30.246 | 187.398 | 7.64 | 176.097 | 2126.72 | 25.98 | 45.998 | 6.35 | 1.354 | 4.686 | 8431.69 | 2.066 | 97.8 | 77.6 | 1382 | 22.95 | 5480.6 | 2890.1 | 2845.3 | 4184.3 | 1196.9 | 0.67652 | 6.041
2024-12-09 | 17:42 | Data | 0 | 32.838 | 30.448 | 187.534 | 7.63 | 176.278 | 2125.81 | 25.98 | 45.998 | 6.35 | 1.355 | 4.683 | 8445.26 | 2.059 | 97.8 | 77.6 | 1382 | 22.95 | 5489.4 | 2908.5 | 2839.4 | 4179.9 | 1196.9 | 0.68003 | 6.037
2024-12-09 | 17:42 | Data | 0 | 32.521 | 30.421 | 187.443 | 7.64 | 176.187 | 2126.72 | 25.97 | 45.908 | 6.34 | 1.343 | 4.673 | 8440.74 | 1.944 | 97.8 | 77.7 | 1382 | 23 | 5486.5 | 2903.3 | 2841.2 | 4182.5 | 1196.9 | 0.67721 | 6.016
2024-12-09 | 17:42 | Data | 0 | 32.507 | 30.415 | 187.443 | 7.63 | 176.187 | 2124.91 | 25.98 | 45.908 | 6.35 | 1.349 | 4.683 | 8445.26 | 2.079 | 97.8 | 77.6 | 1381 | 22.95 | 5489.4 | 2892.5 | 2853.3 | 4181.1 | 1197 | 0.67506 | 6.033
2024-12-09 | 17:42 | Data | 0 | 32.521 | 30.826 | 187.579 | 7.63 | 176.233 | 2128.52 | 25.97 | 45.998 | 6.35 | 1.358 | 4.666 | 8445.26 | 1.971 | 97.8 | 77.5 | 1384 | 22.95 | 5489.4 | 2902.3 | 2837.1 | 4179.8 | 1197 | 0.6784 | 6.025
2024-12-09 | 17:42 | Data | 0 | 32.548 | 30.536 | 187.534 | 7.63 | 176.187 | 2127.62 | 25.98 | 46.089 | 6.34 | 1.36 | 4.645 | 8472.39 | 1.917 | 97.8 | 77.4 | 1384 | 23 | 5507.1 | 2897.3 | 2815.2 | 4161.8 | 1197 | 0.67973 | 6.001
2024-12-09 | 17:42 | Data | 0 | 32.602 | 30.523 | 187.534 | 7.64 | 176.187 | 2128.52 | 25.97 | 45.998 | 6.35 | 1.353 | 4.669 | 8454.3 | 2.167 | 97.8 | 77.5 | 1384 | 22.95 | 5495.3 | 2886.8 | 2799.4 | 4144.5 | 1197 | 0.68092 | 6.022
2024-12-09 | 17:42 | Data | 0 | 32.487 | 30.415 | 187.579 | 7.64 | 176.097 | 2127.62 | 25.97 | 45.998 | 6.35 | 1.345 | 4.674 | 8458.83 | 2.079 | 97.8 | 77.6 | 1384 | 23 | 5498.2 | 2908.6 | 2809.2 | 4161.4 | 1197 | 0.68359 | 6.02
2024-12-09 | 17:42 | Data | 0 | 32.291 | 30.367 | 187.489 | 7.64 | 176.097 | 2129.43 | 25.96 | 45.908 | 6.34 | 1.341 | 4.673 | 8454.3 | 2.059 | 97.8 | 77.7 | 1384 | 22.95 | 5495.3 | 2897.1 | 2800.7 | 4149.2 | 1197 | 0.68244 | 6.015
2024-12-09 | 17:42 | Data | 0 | 32.71 | 30.705 | 187.534 | 7.64 | 176.187 | 2129.43 | 25.93 | 45.998 | 6.35 | 1.341 | 4.698 | 8458.83 | 2.052 | 97.8 | 77.8 | 1382 | 23 | 5498.2 | 2898.7 | 2821.6 | 4164.8 | 1197 | 0.67804 | 6.042
2024-12-09 | 17:42 | Data | 0 | 32.48 | 30.644 | 187.579 | 7.63 | 176.142 | 2127.62 | 25.95 | 45.908 | 6.34 | 1.342 | 4.709 | 8458.83 | 2.039 | 97.8 | 77.8 | 1383 | 22.95 | 5498.2 | 2902.5 | 2857.7 | 4193.7 | 1197 | 0.67467 | 6.05
2024-12-09 | 17:43 | Data | 0 | 32.663 | 30.867 | 187.443 | 7.64 | 176.233 | 2128.52 | 25.94 | 45.998 | 6.35 | 1.341 | 4.682 | 8467.87 | 2.052 | 97.8 | 77.7 | 1382 | 23 | 5504.1 | 2898.5 | 2883.3 | 4204.2 | 1197 | 0.67178 | 6.023
2024-12-09 | 17:43 | Data | 0 | 32.494 | 30.624 | 187.398 | 7.64 | 176.007 | 2127.62 | 25.95 | 46.089 | 6.35 | 1.349 | 4.652 | 8467.87 | 1.87 | 97.8 | 77.5 | 1383 | 23 | 5504.1 | 2913.6 | 2904.1 | 4226.8 | 1197 | 0.67234 | 6.001
2024-12-09 | 17:43 | Data | 0 | 32.548 | 30.806 | 187.489 | 7.63 | 176.187 | 2128.52 | 25.95 | 45.998 | 6.35 | 1.348 | 4.667 | 8440.74 | 1.998 | 97.8 | 77.6 | 1384 | 23.04 | 5486.5 | 2919.4 | 2900.3 | 4232.9 | 1197 | 0.67283 | 6.016
2024-12-09 | 17:43 | Data | 0 | 32.561 | 30.624 | 187.579 | 7.64 | 176.142 | 2128.52 | 25.96 | 45.998 | 6.35 | 1.345 | 4.63 | 8458.83 | 1.985 | 97.8 | 77.5 | 1383 | 22.95 | 5498.2 | 2920.5 | 2880.9 | 4214.4 | 1197 | 0.6742 | 5.977
2024-12-09 | 17:43 | Data | 0 | 32.548 | 30.752 | 187.489 | 7.64 | 176.142 | 2127.62 | 25.96 | 46.089 | 6.35 | 1.351 | 4.664 | 8458.83 | 1.985 | 97.8 | 77.6 | 1383 | 22.95 | 5498.2 | 2906.8 | 2851 | 4189.4 | 1197 | 0.67675 | 6.014
2024-12-09 | 17:43 | Data | 0 | 32.717 | 30.651 | 187.489 | 7.63 | 176.142 | 2131.24 | 25.96 | 45.998 | 6.35 | 1.352 | 4.676 | 8467.87 | 2.073 | 97.8 | 77.6 | 1385 | 23 | 5504.1 | 2927.5 | 2834.8 | 4194.2 | 1197 | 0.68238 | 6.028
2024-12-09 | 17:43 | Data | 0 | 32.723 | 30.435 | 187.398 | 7.63 | 176.142 | 2130.33 | 25.98 | 45.998 | 6.35 | 1.349 | 4.692 | 8463.35 | 1.958 | 97.8 | 77.6 | 1385 | 22.95 | 5501.2 | 2911.5 | 2816.7 | 4169.3 | 1197 | 0.68134 | 6.044
2024-12-09 | 17:43 | Data | 0 | 32.723 | 30.489 | 187.443 | 7.64 | 176.187 | 2131.24 | 25.98 | 45.998 | 6.34 | 1.347 | 4.699 | 8481.44 | 2.025 | 97.8 | 77.7 | 1385 | 23 | 5512.9 | 2899 | 2804.6 | 4147.5 | 1197 | 0.68142 | 6.045
2024-12-09 | 17:43 | Data | 0 | 32.717 | 30.644 | 187.534 | 7.64 | 176.142 | 2130.33 | 25.96 | 45.998 | 6.35 | 1.348 | 4.69 | 8476.91 | 2.079 | 97.8 | 77.7 | 1386 | 23 | 5510 | 2897 | 2830 | 4167.4 | 1197 | 0.67873 | 6.039
2024-12-09 | 17:43 | Data | 0 | 32.696 | 30.86 | 187.353 | 7.63 | 176.187 | 2130.33 | 25.96 | 45.998 | 6.35 | 1.356 | 4.679 | 8485.96 | 1.924 | 97.8 | 77.5 | 1385 | 22.95 | 5515.9 | 2918.6 | 2821 | 4162.8 | 1197 | 0.68259 | 6.036
2024-12-09 | 17:43 | Data | 0 | 32.494 | 30.624 | 187.534 | 7.64 | 176.187 | 2130.33 | 25.96 | 45.908 | 6.34 | 1.351 | 4.695 | 8485.96 | 1.958 | 97.8 | 77.7 | 1385 | 23 | 5515.9 | 2910.9 | 2829 | 4196.9 | 1197 | 0.68028 | 6.046
2024-12-09 | 17:43 | Data | 0 | 32.507 | 30.59 | 187.443 | 7.64 | 176.097 | 2130.33 | 25.98 | 46.089 | 6.34 | 1.344 | 4.697 | 8463.35 | 1.965 | 97.8 | 77.8 | 1385 | 23 | 5501.2 | 2892.6 | 2847.7 | 4177 | 1197 | 0.67513 | 6.041
2024-12-09 | 17:43 | Data | 0 | 32.325 | 30.415 | 187.443 | 7.64 | 176.187 | 2130.33 | 25.98 | 45.998 | 6.36 | 1.353 | 4.666 | 8481.44 | 2.039 | 97.8 | 77.5 | 1385 | 23 | 5512.9 | 2896.4 | 2862.7 | 4189.7 | 1197 | 0.6746 | 6.02
2024-12-09 | 17:43 | Data | 0 | 32.379 | 30.401 | 187.489 | 7.63 | 176.142 | 2128.52 | 25.98 | 45.998 | 6.35 | 1.352 | 4.683 | 8476.91 | 1.944 | 97.8 | 77.6 | 1383 | 22.95 | 5510 | 2889.2 | 2843.1 | 4172.3 | 1197 | 0.67586 | 6.034
2024-12-09 | 17:43 | Data | 0 | 32.777 | 30.597 | 187.534 | 7.63 | 176.323 | 2130.33 | 25.98 | 46.089 | 6.35 | 1.358 | 4.69 | 8467.87 | 2.093 | 97.8 | 77.5 | 1385 | 23 | 5504.1 | 2922.4 | 2859.8 | 4203.6 | 1197 | 0.67686 | 6.046
2024-12-09 | 17:43 | Data | 0 | 32.717 | 30.739 | 187.534 | 7.64 | 176.142 | 2128.52 | 25.98 | 45.998 | 6.35 | 1.349 | 4.676 | 8445.26 | 2.127 | 97.8 | 77.6 | 1384 | 23.04 | 5489.4 | 2905.7 | 2860.9 | 4196.3 | 1197 | 0.67488 | 6.024
2024-12-09 | 17:43 | Data | 0 | 32.669 | 30.806 | 187.715 | 7.64 | 176.323 | 2128.52 | 25.98 | 45.998 | 6.34 | 1.342 | 4.682 | 8431.69 | 2.073 | 97.8 | 77.7 | 1384 | 23 | 5480.6 | 2902 | 2859.2 | 4190.5 | 1197 | 0.67713 | 6.024
2024-12-09 | 17:43 | Data | 0 | 32.494 | 30.766 | 187.624 | 7.63 | 176.187 | 2127.62 | 25.97 | 46.089 | 6.35 | 1.352 | 4.662 | 8449.78 | 1.958 | 97.8 | 77.5 | 1383 | 23 | 5492.4 | 2908.6 | 2821.6 | 4169.4 | 1197 | 0.68068 | 6.015
2024-12-09 | 17:44 | Data | 0 | 32.393 | 30.59 | 187.579 | 7.64 | 176.142 | 2125.81 | 25.98 | 45.908 | 6.35 | 1.353 | 4.673 | 8418.13 | 1.992 | 97.8 | 77.5 | 1381 | 23 | 5471.8 | 2900.8 | 2828.1 | 4171.8 | 1197 | 0.67923 | 6.026
2024-12-09 | 17:44 | Data | 0 | 32.278 | 30.617 | 187.443 | 7.64 | 176.142 | 2128.52 | 25.99 | 45.818 | 6.35 | 1.346 | 4.683 | 8431.69 | 2.019 | 97.8 | 77.7 | 1384 | 23.04 | 5480.6 | 2891.9 | 2804.2 | 4143.6 | 1197 | 0.6813 | 6.027
2024-12-09 | 17:44 | Data | 0 | 32.44 | 30.921 | 187.579 | 7.64 | 176.233 | 2129.43 | 25.97 | 45.998 | 6.35 | 1.348 | 4.672 | 8422.65 | 1.992 | 97.8 | 77.6 | 1385 | 23 | 5474.7 | 2896.5 | 2831 | 4164.8 | 1197 | 0.6787 | 6.021
2024-12-09 | 17:44 | Data | 0 | 32.723 | 30.489 | 187.489 | 7.63 | 176.233 | 2127.62 | 25.98 | 45.998 | 6.34 | 1.348 | 4.689 | 8427.17 | 2.12 | 97.8 | 77.7 | 1383 | 23 | 5477.7 | 2905.7 | 2816.2 | 4164.7 | 1197 | 0.68184 | 6.037
2024-12-09 | 17:44 | Data | 0 | 32.777 | 30.651 | 187.489 | 7.64 | 176.233 | 2126.72 | 25.97 | 45.998 | 6.35 | 1.348 | 4.698 | 8431.69 | 1.971 | 97.8 | 77.7 | 1382 | 23 | 5480.6 | 2902.2 | 2828.7 | 4171.6 | 1197 | 0.67933 | 6.045
2024-12-09 | 17:44 | Data | 0 | 32.507 | 30.651 | 187.534 | 7.64 | 176.187 | 2131.24 | 25.98 | 45.998 | 6.34 | 1.343 | 4.694 | 8445.26 | 2.025 | 97.8 | 77.8 | 1385 | 23 | 5489.4 | 2930.8 | 2823.5 | 4182.3 | 1197 | 0.68426 | 6.036
2024-12-09 | 17:44 | Data | 0 | 32.845 | 30.658 | 187.624 | 7.63 | 176.278 | 2131.24 | 25.98 | 45.998 | 6.35 | 1.346 | 4.674 | 8038.26 | 1.924 | 97.8 | 77.6 | 1385 | 23.04 | 5224.9 | 2914.6 | 2839.7 | 4182 | 1197 | 0.67998 | 6.019
2024-12-09 | 17:44 | Data | 0 | 32.339 | 30.421 | 187.443 | 7.64 | 176.187 | 2130.33 | 25.99 | 45.998 | 6.35 | 1.346 | 4.662 | 8422.65 | 1.877 | 97.8 | 77.6 | 1385 | 23 | 5474.7 | 2896 | 2821.8 | 4159.1 | 1197 | 0.6802 | 6.007
2024-12-09 | 17:44 | Data | 0 | 32.723 | 30.86 | 187.534 | 7.64 | 176.233 | 2125.81 | 25.98 | 45.908 | 6.35 | 1.344 | 4.639 | 8431.69 | 2.066 | 97.8 | 77.5 | 1382 | 23 | 5480.6 | 2900.7 | 2839.7 | 4177.1 | 1197 | 0.67695 | 5.982
2024-12-09 | 17:44 | Data | 0 | 32.933 | 30.421 | 187.579 | 7.64 | 176.323 | 2125.81 | 25.97 | 45.908 | 6.35 | 1.349 | 4.671 | 8427.17 | 2.106 | 97.8 | 77.6 | 1382 | 23 | 5477.7 | 2904.4 | 2832.1 | 4175.9 | 1197 | 0.67803 | 6.021
2024-12-09 | 17:44 | Data | 0 | 32.663 | 30.86 | 187.579 | 7.63 | 176.233 | 2131.24 | 25.99 | 45.998 | 6.34 | 1.348 | 4.681 | 8431.69 | 2.059 | 97.8 | 77.6 | 1385 | 22.95 | 5480.6 | 2909.4 | 2842.3 | 4178 | 1197 | 0.68062 | 6.029
2024-12-09 | 17:44 | Data | 0 | 32.379 | 30.415 | 187.443 | 7.64 | 176.142 | 2120.39 | 25.98 | 45.908 | 6.34 | 1.346 | 4.687 | 8427.17 | 2.181 | 97.8 | 77.7 | 1378 | 23 | 5477.7 | 2884.1 | 2860.1 | 4182.4 | 1197.1 | 0.67272 | 6.032
2024-12-09 | 17:44 | Data | 0 | 32.717 | 30.428 | 187.579 | 7.64 | 176.187 | 2127.62 | 25.98 | 45.998 | 6.34 | 1.341 | 4.683 | 8436.21 | 1.965 | 97.8 | 77.7 | 1382 | 23 | 5483.5 | 2901.2 | 2838.7 | 4173.5 | 1197.1 | 0.67933 | 6.024
2024-12-09 | 17:44 | Data | 0 | 32.521 | 30.536 | 187.534 | 7.64 | 176.142 | 2127.62 | 25.98 | 45.818 | 6.35 | 1.352 | 4.654 | 8422.65 | 2.086 | 97.8 | 77.5 | 1384 | 22.91 | 5474.7 | 2906.1 | 2850.3 | 4191.1 | 1197.1 | 0.67659 | 6.007
2024-12-09 | 17:44 | Data | 0 | 32.501 | 30.523 | 187.443 | 7.63 | 176.142 | 2126.72 | 25.98 | 45.908 | 6.34 | 1.355 | 4.666 | 8418.13 | 2.012 | 97.8 | 77.5 | 1383 | 23.04 | 5471.8 | 2904.9 | 2829.7 | 4172.5 | 1197.1 | 0.67944 | 6.021
2024-12-09 | 17:44 | Data | 0 | 32.494 | 30.651 | 187.489 | 7.64 | 176.097 | 2128.52 | 25.98 | 45.998 | 6.35 | 1.349 | 4.666 | 8431.69 | 1.863 | 97.8 | 77.6 | 1383 | 23.04 | 5480.6 | 2917.5 | 2817.2 | 4169.1 | 1197.1 | 0.68083 | 6.015
2024-12-09 | 17:44 | Data | 0 | 33.027 | 30.597 | 187.67 | 7.64 | 176.323 | 2125.81 | 25.97 | 45.998 | 6.34 | 1.346 | 4.669 | 8422.65 | 2.093 | 97.8 | 77.6 | 1382 | 23 | 5474.7 | 2888.1 | 2847.4 | 4174.9 | 1197.1 | 0.67409 | 6.014
2024-12-09 | 17:44 | Data | 0 | 32.609 | 30.597 | 187.489 | 7.63 | 176.187 | 2124.91 | 25.97 | 46.089 | 6.35 | 1.34 | 4.685 | 8458.83 | 2.174 | 97.8 | 77.8 | 1382 | 23 | 5498.2 | 2911.4 | 2838.5 | 4185.2 | 1197.1 | 0.67874 | 6.026
2024-12-09 | 17:45 | Data | 0 | 32.561 | 30.523 | 187.579 | 7.64 | 176.278 | 2122.2 | 25.99 | 45.908 | 6.34 | 1.353 | 4.65 | 8454.3 | 1.978 | 97.8 | 77.5 | 1379 | 23 | 5495.3 | 2894 | 2819.6 | 4160.9 | 1197.1 | 0.67785 | 6.003
2024-12-09 | 17:45 | Data | 0 | 32.723 | 30.651 | 187.579 | 7.64 | 176.233 | 2122.2 | 25.98 | 45.908 | 6.35 | 1.351 | 4.663 | 8458.83 | 2.073 | 97.8 | 77.5 | 1379 | 22.95 | 5498.2 | 2896.5 | 2813.2 | 4154 | 1197.1 | 0.68033 | 6.013
2024-12-09 | 17:45 | Data | 0 | 32.838 | 30.435 | 187.67 | 7.63 | 176.278 | 2124.91 | 25.99 | 45.908 | 6.35 | 1.358 | 4.651 | 8440.74 | 1.978 | 97.8 | 77.4 | 1381 | 22.95 | 5486.5 | 2891.6 | 2800.3 | 4147.4 | 1197.1 | 0.68086 | 6.008
2024-12-09 | 17:45 | Data | 0 | 32.919 | 30.482 | 187.489 | 7.63 | 176.323 | 2124.01 | 25.98 | 45.998 | 6.35 | 1.346 | 4.669 | 8440.74 | 2.133 | 97.8 | 77.6 | 1380 | 23 | 5486.5 | 2925.6 | 2815.9 | 4168 | 1197.1 | 0.6831 | 6.015
2024-12-09 | 17:45 | Data | 0 | 32.764 | 30.421 | 187.579 | 7.64 | 176.278 | 2120.39 | 25.98 | 45.998 | 6.34 | 1.348 | 4.683 | 8870.35 | 2.181 | 97.8 | 77.6 | 1378 | 23 | 5765.7 | 2916.1 | 2832.4 | 4182.6 | 1197.1 | 0.68061 | 6.032
2024-12-09 | 17:45 | Data | 0 | 32.521 | 30.421 | 187.489 | 7.64 | 176.142 | 2125.81 | 25.97 | 45.908 | 6.34 | 1.346 | 4.682 | 8431.69 | 1.897 | 97.8 | 77.7 | 1382 | 23 | 5480.6 | 2888.5 | 2835 | 4164.6 | 1197.1 | 0.67184 | 6.027
2024-12-09 | 17:45 | Data | 0 | 32.507 | 30.475 | 187.579 | 7.63 | 176.187 | 2078.81 | 25.97 | 45.998 | 6.34 | 1.339 | 4.667 | 8418.13 | 1.85 | 97.8 | 77.7 | 1351 | 23 | 5471.8 | 2887.6 | 2849.9 | 4175.5 | 1197.1 | 0.67444 | 6.007
2024-12-09 | 17:45 | Data | 0 | 32.69 | 30.516 | 187.489 | 7.64 | 176.142 | 2069.78 | 25.98 | 45.818 | 6.35 | 1.347 | 4.677 | 8395.51 | 2.005 | 97.8 | 77.6 | 1346 | 22.95 | 5457.1 | 2900.6 | 2830.1 | 4171.9 | 1197.1 | 0.6777 | 6.024
2024-12-09 | 17:45 | Data | 0 | 32.953 | 30.678 | 187.624 | 7.64 | 176.278 | 2069.78 | 25.98 | 45.908 | 6.35 | 1.346 | 4.664 | 8390.99 | 2.073 | 97.8 | 77.6 | 1346 | 23 | 5454.1 | 2898.5 | 2837.1 | 4172.4 | 1197.1 | 0.67909 | 6.01
2024-12-09 | 17:45 | Data | 0 | 32.804 | 30.766 | 187.579 | 7.64 | 176.187 | 2069.78 | 25.98 | 45.998 | 6.34 | 1.344 | 4.664 | 8372.9 | 2.154 | 97.8 | 77.6 | 1346 | 22.95 | 5442.4 | 2882.8 | 2825.1 | 4155.8 | 1197.1 | 0.6766 | 6.008
2024-12-09 | 17:45 | Data | 0 | 32.494 | 30.374 | 187.353 | 7.63 | 176.052 | 2105.03 | 25.97 | 45.998 | 6.34 | 1.352 | 4.687 | 8372.9 | 2.12 | 97.8 | 77.6 | 1369 | 22.95 | 5442.4 | 2887 | 2836.7 | 4168.6 | 1197.1 | 0.67572 | 6.04
2024-12-09 | 17:45 | Data | 0 | 32.946 | 30.766 | 187.579 | 7.64 | 176.278 | 2125.81 | 25.98 | 45.998 | 6.34 | 1.348 | 4.69 | 8431.69 | 1.958 | 97.8 | 77.7 | 1381 | 23 | 5480.6 | 2909 | 2827.3 | 4173.8 | 1197.1 | 0.68189 | 6.036
2024-12-09 | 17:45 | Data | 0 | 32.609 | 30.732 | 187.534 | 7.64 | 176.233 | 2123.1 | 25.98 | 45.908 | 6.35 | 1.353 | 4.648 | 8409.08 | 2.012 | 97.8 | 77.5 | 1380 | 22.95 | 5465.9 | 2888.9 | 2815.5 | 4153.6 | 1197.1 | 0.68088 | 6.001
2024-12-09 | 17:45 | Data | 0 | 32.892 | 30.907 | 187.67 | 7.63 | 176.278 | 2123.1 | 25.98 | 45.998 | 6.34 | 1.354 | 4.667 | 8409.08 | 1.965 | 97.8 | 77.5 | 1381 | 22.95 | 5465.9 | 2903 | 2834.2 | 4168.4 | 1197.1 | 0.68 | 6.022
2024-12-09 | 17:45 | Data | 0 | 32.494 | 30.624 | 187.489 | 7.64 | 176.278 | 2124.91 | 25.98 | 45.998 | 6.35 | 1.346 | 4.68 | 8418.13 | 2.073 | 97.8 | 77.7 | 1381 | 23 | 5471.8 | 2875.1 | 2808.3 | 4144.1 | 1197.1 | 0.67574 | 6.026
2024-12-09 | 17:45 | Data | 0 | 32.723 | 30.82 | 187.579 | 7.63 | 176.142 | 2128.52 | 25.97 | 45.908 | 6.34 | 1.349 | 4.67 | 8418.13 | 2.073 | 97.8 | 77.6 | 1384 | 22.95 | 5471.8 | 2908 | 2842.7 | 4186.3 | 1197.1 | 0.67925 | 6.019
2024-12-09 | 17:45 | Data | 0 | 32.696 | 30.604 | 187.624 | 7.64 | 176.187 | 2129.43 | 25.97 | 45.998 | 6.35 | 1.36 | 4.649 | 8409.08 | 2.201 | 97.8 | 77.4 | 1384 | 23.04 | 5465.9 | 2886.2 | 2835 | 4162.6 | 1197.1 | 0.67725 | 6.012
2024-12-09 | 17:46 | Data | 0 | 32.838 | 30.664 | 187.67 | 7.64 | 176.323 | 2129.43 | 25.98 | 45.998 | 6.34 | 1.355 | 4.665 | 8395.51 | 1.998 | 97.8 | 77.5 | 1384 | 22.95 | 5457.1 | 2897.2 | 2803.6 | 4148.1 | 1197.1 | 0.68119 | 6.021
2024-12-09 | 17:46 | Data | 0 | 32.696 | 30.529 | 187.534 | 7.63 | 176.187 | 2127.62 | 25.99 | 45.998 | 6.35 | 1.348 | 4.669 | 8400.04 | 1.951 | 97.8 | 77.6 | 1383 | 22.95 | 5460 | 2923.3 | 2839.8 | 4177.5 | 1197.1 | 0.67941 | 6.018
2024-12-09 | 17:46 | Data | 0 | 32.494 | 30.597 | 187.443 | 7.63 | 176.233 | 2128.52 | 25.98 | 45.908 | 6.35 | 1.357 | 4.676 | 8422.65 | 2.066 | 97.8 | 77.5 | 1384 | 23 | 5474.7 | 2907.6 | 2824.1 | 4168 | 1197.1 | 0.67955 | 6.033
2024-12-09 | 17:46 | Data | 0 | 32.494 | 30.59 | 187.398 | 7.64 | 176.187 | 2124.91 | 25.97 | 45.908 | 6.35 | 1.358 | 4.688 | 8431.69 | 2.079 | 97.8 | 77.5 | 1381 | 22.95 | 5480.6 | 2915.9 | 2830.6 | 4181.2 | 1197.1 | 0.67897 | 6.044
2024-12-09 | 17:46 | Data | 0 | 32.494 | 30.624 | 187.534 | 7.64 | 176.187 | 2127.62 | 25.97 | 45.998 | 6.35 | 1.353 | 4.686 | 8418.13 | 2.073 | 97.8 | 77.6 | 1383 | 22.95 | 5471.8 | 2916.6 | 2839.8 | 4186.5 | 1197.1 | 0.67856 | 6.039
2024-12-09 | 17:46 | Data | 0 | 32.723 | 30.529 | 187.624 | 7.64 | 176.278 | 2128.52 | 25.97 | 45.998 | 6.35 | 1.344 | 4.685 | 8440.74 | 2.079 | 97.8 | 77.7 | 1384 | 22.95 | 5486.5 | 2875.7 | 2833.2 | 4160 | 1197.1 | 0.67287 | 6.029
2024-12-09 | 17:46 | Data | 0 | 32.723 | 30.806 | 187.398 | 7.64 | 176.187 | 2127.62 | 25.97 | 45.998 | 6.35 | 1.345 | 4.677 | 8431.69 | 1.917 | 97.8 | 77.7 | 1383 | 23 | 5480.6 | 2901.1 | 2828.4 | 4170.7 | 1197.1 | 0.67822 | 6.022
2024-12-09 | 17:46 | Data | 0 | 32.501 | 30.624 | 187.624 | 7.64 | 176.278 | 2128.52 | 25.98 | 45.998 | 6.35 | 1.36 | 4.675 | 8427.17 | 1.985 | 97.8 | 77.5 | 1384 | 22.95 | 5477.7 | 2897.7 | 2792.8 | 4150.1 | 1197.1 | 0.68162 | 6.036
2024-12-09 | 17:46 | Data | 0 | 32.582 | 30.421 | 187.489 | 7.63 | 176.233 | 2127.62 | 25.98 | 45.998 | 6.35 | 1.363 | 4.664 | 8427.17 | 1.863 | 97.8 | 77.4 | 1383 | 23 | 5477.7 | 2895.2 | 2805.7 | 4150.5 | 1197.1 | 0.68154 | 6.028
2024-12-09 | 17:46 | Data | 0 | 32.413 | 30.523 | 187.534 | 7.64 | 176.187 | 2127.62 | 25.98 | 45.908 | 6.34 | 1.353 | 4.669 | 8431.69 | 2.032 | 97.8 | 77.5 | 1383 | 23 | 5480.6 | 2887.8 | 2808.4 | 4150.2 | 1197.1 | 0.68034 | 6.02
2024-12-09 | 17:46 | Data | 0 | 32.467 | 30.617 | 187.489 | 7.64 | 176.142 | 2127.62 | 25.98 | 45.908 | 6.35 | 1.351 | 4.664 | 8445.26 | 2.073 | 97.8 | 77.5 | 1384 | 23 | 5489.4 | 2898.7 | 2805.1 | 4142.4 | 1197.1 | 0.68136 | 6.017
2024-12-09 | 17:46 | Data | 0 | 33 | 30.874 | 187.67 | 7.64 | 176.368 | 2128.52 | 25.97 | 45.998 | 6.35 | 1.353 | 4.665 | 8463.35 | 2.093 | 97.8 | 77.5 | 1384 | 23 | 5501.2 | 2905.4 | 2845.8 | 4183.8 | 1197.1 | 0.67749 | 6.019
2024-12-09 | 17:46 | Data | 0 | 32.723 | 30.664 | 187.624 | 7.64 | 176.278 | 2128.52 | 25.98 | 45.818 | 6.35 | 1.359 | 4.659 | 8445.26 | 2.059 | 97.8 | 77.4 | 1383 | 22.95 | 5489.4 | 2878 | 2819 | 4145.6 | 1197.1 | 0.67674 | 6.017
2024-12-09 | 17:46 | Data | 0 | 32.507 | 30.543 | 187.624 | 7.64 | 176.368 | 2127.62 | 25.97 | 45.998 | 6.35 | 1.354 | 4.654 | 8463.35 | 2.066 | 97.8 | 77.5 | 1383 | 23 | 5501.2 | 2916.8 | 2812.6 | 4172.8 | 1197.2 | 0.681 | 6.007
2024-12-09 | 17:46 | Data | 0 | 32.602 | 30.84 | 187.579 | 7.63 | 176.233 | 2127.62 | 25.98 | 45.908 | 6.35 | 1.356 | 4.668 | 8431.69 | 2.005 | 97.8 | 77.5 | 1384 | 22.95 | 5480.6 | 2900 | 2852.7 | 4184.6 | 1197.2 | 0.67635 | 6.025
2024-12-09 | 17:46 | Data | 0 | 32.696 | 30.82 | 187.579 | 7.64 | 176.233 | 2128.52 | 25.97 | 45.998 | 6.35 | 1.359 | 4.667 | 8431.69 | 2.086 | 97.8 | 77.4 | 1383 | 23 | 5480.6 | 2900.2 | 2826.4 | 4164.3 | 1197.2 | 0.67968 | 6.026
2024-12-09 | 17:46 | Data | 0 | 32.494 | 30.604 | 187.489 | 7.64 | 176.142 | 2127.62 | 25.98 | 45.998 | 6.35 | 1.352 | 4.656 | 8427.17 | 2.194 | 97.8 | 77.5 | 1382 | 23 | 5477.7 | 2897.6 | 2837.6 | 4174 | 1197.2 | 0.6808 | 6.008
2024-12-09 | 17:46 | Data | 0 | 32.919 | 30.651 | 187.624 | 7.64 | 176.323 | 2128.52 | 25.97 | 45.908 | 6.35 | 1.356 | 4.679 | 8422.65 | 2.174 | 97.8 | 77.5 | 1384 | 22.91 | 5474.7 | 2892.1 | 2813.1 | 4150.9 | 1197.2 | 0.68046 | 6.032
2024-12-09 | 17:47 | Data | 0 | 32.521 | 30.739 | 187.534 | 7.64 | 176.187 | 2123.1 | 25.97 | 45.998 | 6.35 | 1.348 | 4.687 | 8436.21 | 1.904 | 97.8 | 77.7 | 1380 | 23.04 | 5483.5 | 2886.7 | 2813 | 4150.3 | 1197.2 | 0.67907 | 6.035
2024-12-09 | 17:47 | Data | 0 | 32.69 | 30.482 | 187.443 | 7.63 | 176.187 | 2127.62 | 25.98 | 45.908 | 6.34 | 1.352 | 4.679 | 8445.26 | 1.971 | 97.8 | 77.6 | 1384 | 23 | 5489.4 | 2928 | 2824.5 | 4187.6 | 1197.2 | 0.68309 | 6.031
2024-12-09 | 17:47 | Data | 0 | 32.501 | 30.502 | 187.398 | 7.63 | 176.142 | 2128.52 | 25.97 | 45.998 | 6.35 | 1.352 | 4.664 | 8445.26 | 1.992 | 97.8 | 77.5 | 1383 | 23 | 5489.4 | 2895.9 | 2791.7 | 4141.3 | 1197.2 | 0.68334 | 6.017
2024-12-09 | 17:47 | Data | 0 | 32.696 | 30.597 | 187.534 | 7.64 | 176.233 | 2128.52 | 25.98 | 45.998 | 6.34 | 1.352 | 4.645 | 8445.26 | 2.174 | 97.8 | 77.5 | 1384 | 23.04 | 5489.4 | 2890.5 | 2813.3 | 4153.9 | 1197.2 | 0.67841 | 5.998
2024-12-09 | 17:47 | Data | 0 | 32.494 | 30.415 | 187.489 | 7.63 | 176.142 | 2125.81 | 25.98 | 45.908 | 6.35 | 1.347 | 4.657 | 8445.26 | 2.079 | 97.8 | 77.6 | 1382 | 22.95 | 5489.4 | 2895.1 | 2808.8 | 4150.1 | 1197.2 | 0.68135 | 6.004
2024-12-09 | 17:47 | Data | 0 | 32.555 | 30.475 | 187.579 | 7.64 | 176.278 | 2127.62 | 25.98 | 45.998 | 6.34 | 1.339 | 4.66 | 8445.26 | 1.85 | 97.8 | 77.7 | 1383 | 23 | 5489.4 | 2914.9 | 2835.2 | 4179.2 | 1197.2 | 0.68188 | 5.998
2024-12-09 | 17:47 | Data | 0 | 32.44 | 30.759 | 187.534 | 7.63 | 176.187 | 2127.62 | 25.98 | 45.908 | 6.35 | 1.341 | 4.668 | 8454.3 | 2.052 | 97.8 | 77.7 | 1383 | 23 | 5495.3 | 2904.6 | 2845 | 4180.1 | 1197.2 | 0.67742 | 6.007
2024-12-09 | 17:47 | Data | 0 | 32.312 | 30.415 | 187.534 | 7.64 | 176.278 | 2129.43 | 25.97 | 45.998 | 6.35 | 1.347 | 4.681 | 8449.78 | 1.863 | 97.8 | 77.7 | 1384 | 23 | 5492.4 | 2907.9 | 2853.4 | 4187.1 | 1197.2 | 0.67735 | 6.027
2024-12-09 | 17:47 | Data | 0 | 32.494 | 30.624 | 187.67 | 7.64 | 176.278 | 2128.52 | 25.98 | 45.998 | 6.34 | 1.336 | 4.694 | 8454.3 | 2.073 | 97.8 | 77.8 | 1383 | 23 | 5495.3 | 2900.6 | 2850.5 | 4181.2 | 1197.2 | 0.67757 | 6.03
2024-12-09 | 17:47 | Data | 0 | 32.44 | 30.644 | 187.624 | 7.64 | 176.233 | 2129.43 | 25.98 | 45.908 | 6.35 | 1.352 | 4.689 | 8458.83 | 2.052 | 97.8 | 77.6 | 1384 | 23 | 5498.2 | 2880.4 | 2833.4 | 4145.6 | 1197.2 | 0.67685 | 6.041
2024-12-09 | 17:47 | Data | 0 | 32.494 | 30.806 | 187.67 | 7.63 | 176.323 | 2127.62 | 25.99 | 45.998 | 6.34 | 1.353 | 4.675 | 8449.78 | 2.012 | 97.8 | 77.6 | 1383 | 23 | 5492.4 | 2893.7 | 2852.5 | 4179.3 | 1197.2 | 0.67587 | 6.027
2024-12-09 | 17:47 | Data | 0 | 32.467 | 30.752 | 187.579 | 7.64 | 176.233 | 2134.85 | 25.97 | 45.908 | 6.35 | 1.349 | 4.657 | 8454.3 | 2.1 | 97.8 | 77.5 | 1387 | 23 | 5495.3 | 2895.6 | 2804.7 | 4151.6 | 1197.2 | 0.68029 | 6.007
2024-12-09 | 17:47 | Data | 0 | 32.494 | 30.847 | 187.489 | 7.64 | 176.187 | 2127.62 | 25.97 | 45.998 | 6.35 | 1.348 | 4.664 | 8440.74 | 1.87 | 97.8 | 77.6 | 1384 | 23 | 5486.5 | 2892.2 | 2814.3 | 4151 | 1197.2 | 0.68076 | 6.012
2024-12-09 | 17:47 | Data | 0 | 32.467 | 30.421 | 187.715 | 7.63 | 176.278 | 2128.52 | 25.98 | 45.908 | 6.35 | 1.341 | 4.673 | 8445.26 | 1.87 | 97.8 | 77.7 | 1384 | 22.95 | 5489.4 | 2905.1 | 2801.8 | 4155.7 | 1197.2 | 0.6823 | 6.015
2024-12-09 | 17:47 | Data | 0 | 32.609 | 30.867 | 187.624 | 7.64 | 176.233 | 2127.62 | 25.98 | 45.998 | 6.35 | 1.343 | 4.656 | 8440.74 | 2.066 | 97.8 | 77.6 | 1383 | 23 | 5486.5 | 2905 | 2789.6 | 4138.9 | 1197.2 | 0.68448 | 6.001
2024-12-09 | 17:47 | Data | 0 | 32.926 | 30.685 | 187.67 | 7.64 | 176.368 | 2127.62 | 25.98 | 46.089 | 6.34 | 1.336 | 4.666 | 8445.26 | 2.019 | 97.8 | 77.7 | 1383 | 23 | 5489.4 | 2895.6 | 2815.2 | 4158.3 | 1197.2 | 0.679 | 6.001
2024-12-09 | 17:47 | Data | 0 | 32.858 | 30.502 | 187.76 | 7.64 | 176.278 | 2128.52 | 25.97 | 45.998 | 6.35 | 1.341 | 4.676 | 8440.74 | 2.025 | 97.8 | 77.7 | 1384 | 23 | 5486.5 | 2905.9 | 2844 | 4184.9 | 1197.2 | 0.67693 | 6.017
2024-12-09 | 17:47 | Data | 0 | 32.696 | 30.644 | 187.489 | 7.63 | 176.233 | 2128.52 | 25.98 | 45.998 | 6.35 | 1.353 | 4.662 | 8418.13 | 1.904 | 97.8 | 77.5 | 1384 | 23 | 5471.8 | 2904.7 | 2874.4 | 4200.2 | 1197.2 | 0.67412 | 6.015
2024-12-09 | 17:48 | Data | 0 | 32.494 | 30.705 | 187.443 | 7.64 | 176.187 | 2130.33 | 25.99 | 45.908 | 6.35 | 1.358 | 4.684 | 8431.69 | 2.079 | 97.8 | 77.5 | 1385 | 23.04 | 5480.6 | 2897.9 | 2872 | 4199.1 | 1197.2 | 0.67276 | 6.043
2024-12-09 | 17:48 | Data | 0 | 32.555 | 30.604 | 187.624 | 7.63 | 176.278 | 2130.33 | 25.98 | 46.089 | 6.35 | 1.353 | 4.645 | 8431.69 | 1.897 | 97.8 | 77.4 | 1385 | 23 | 5480.6 | 2904 | 2852.2 | 4185.1 | 1197.2 | 0.67585 | 5.998
2024-12-09 | 17:48 | Data | 0 | 32.561 | 30.428 | 187.579 | 7.63 | 176.233 | 2136.66 | 25.97 | 46.269 | 6.34 | 1.348 | 4.646 | 8431.69 | 1.89 | 97.8 | 77.5 | 1389 | 23.13 | 5480.6 | 2892.7 | 2878.1 | 4196.5 | 1197.2 | 0.67223 | 5.994
2024-12-09 | 17:48 | Data | 0 | 32.838 | 30.921 | 187.624 | 7.64 | 176.278 | 2134.85 | 25.98 | 46.179 | 6.35 | 1.354 | 4.666 | 8431.69 | 1.924 | 97.8 | 77.5 | 1388 | 23.04 | 5480.6 | 2894.2 | 2854.3 | 4182.6 | 1197.2 | 0.67388 | 6.02
2024-12-09 | 17:48 | Data | 0 | 32.919 | 30.664 | 187.67 | 7.64 | 176.323 | 2134.85 | 25.97 | 46.269 | 6.34 | 1.358 | 4.664 | 8445.26 | 2.127 | 97.8 | 77.5 | 1388 | 23.09 | 5489.4 | 2896.6 | 2827.8 | 4164.6 | 1197.2 | 0.679 | 6.022
2024-12-09 | 17:48 | Data | 0 | 32.717 | 30.637 | 187.624 | 7.64 | 176.278 | 2133.95 | 25.97 | 46.269 | 6.34 | 1.348 | 4.651 | 8440.74 | 2.113 | 97.8 | 77.5 | 1388 | 23.09 | 5486.5 | 2902.3 | 2795.6 | 4148.7 | 1197.2 | 0.68387 | 6
2024-12-09 | 17:48 | Data | 0 | 32.723 | 30.766 | 187.624 | 7.64 | 176.233 | 2135.76 | 25.96 | 46.269 | 6.34 | 1.343 | 4.668 | 8431.69 | 2.073 | 97.8 | 77.7 | 1388 | 23.13 | 5480.6 | 2910.4 | 2812.6 | 4162.2 | 1197.2 | 0.68187 | 6.011
2024-12-09 | 17:48 | Data | 0 | 32.75 | 30.536 | 187.579 | 7.63 | 176.413 | 2136.66 | 25.98 | 46.179 | 6.34 | 1.34 | 4.68 | 8418.13 | 1.992 | 97.8 | 77.7 | 1389 | 23.09 | 5471.8 | 2889 | 2808.8 | 4144.3 | 1197.2 | 0.68064 | 6.02
2024-12-09 | 17:48 | Data | 0 | 32.683 | 30.853 | 187.489 | 7.64 | 176.278 | 2136.66 | 25.99 | 46.179 | 6.35 | 1.346 | 4.695 | 8418.13 | 1.971 | 97.8 | 77.7 | 1389 | 23.09 | 5471.8 | 2907.5 | 2827.6 | 4175.1 | 1197.2 | 0.67834 | 6.041
2024-12-09 | 17:48 | Data | 0 | 32.717 | 30.637 | 187.579 | 7.63 | 176.187 | 2136.66 | 25.98 | 46.269 | 6.34 | 1.345 | 4.693 | 8400.04 | 2.187 | 97.8 | 77.7 | 1389 | 23.18 | 5460 | 2913.6 | 2831.4 | 4178.7 | 1197.2 | 0.67858 | 6.038
2024-12-09 | 17:48 | Data | 0 | 32.899 | 30.597 | 187.579 | 7.63 | 176.323 | 2136.66 | 25.97 | 46.179 | 6.35 | 1.345 | 4.672 | 8395.51 | 2.025 | 97.8 | 77.6 | 1389 | 23.13 | 5457.1 | 2896.8 | 2841.3 | 4172.8 | 1197.2 | 0.67871 | 6.017
2024-12-09 | 17:48 | Data | 0 | 32.703 | 30.712 | 187.579 | 7.63 | 176.233 | 2132.14 | 25.98 | 46.269 | 6.35 | 1.346 | 4.663 | 8400.04 | 2.174 | 97.8 | 77.6 | 1386 | 23.13 | 5460 | 2902.2 | 2856.1 | 4186.1 | 1197.2 | 0.67656 | 6.007
2024-12-09 | 17:48 | Data | 0 | 32.723 | 30.475 | 187.489 | 7.64 | 176.233 | 2136.66 | 25.98 | 46.63 | 6.35 | 1.336 | 4.666 | 8395.51 | 2.073 | 97.8 | 77.8 | 1389 | 23.22 | 5457.1 | 2898 | 2849.6 | 4179.4 | 1197.2 | 0.67628 | 6.001
2024-12-09 | 17:48 | Data | 0 | 32.879 | 30.651 | 187.624 | 7.63 | 176.323 | 2142.08 | 25.99 | 46.179 | 6.35 | 1.343 | 4.676 | 8400.04 | 2.181 | 97.8 | 77.7 | 1392 | 23.09 | 5460 | 2905.2 | 2854 | 4199.8 | 1197.3 | 0.67558 | 6.018
2024-12-09 | 17:48 | Data | 0 | 32.71 | 30.529 | 187.534 | 7.64 | 176.233 | 2135.76 | 25.99 | 46.269 | 6.35 | 1.343 | 4.664 | 8400.04 | 2.073 | 97.8 | 77.6 | 1388 | 23.13 | 5460 | 2922.4 | 2851.4 | 4193.7 | 1197.3 | 0.67889 | 6.007
2024-12-09 | 17:48 | Data | 0 | 32.636 | 30.86 | 187.624 | 7.63 | 176.278 | 2139.37 | 25.97 | 46.179 | 6.35 | 1.349 | 4.666 | 8427.17 | 2.066 | 97.8 | 77.6 | 1391 | 23.13 | 5477.7 | 2899.8 | 2834.5 | 4170.7 | 1197.3 | 0.67893 | 6.017
2024-12-09 | 17:48 | Data | 0 | 32.838 | 30.435 | 187.624 | 7.63 | 176.323 | 2141.18 | 25.98 | 45.727 | 6.35 | 1.347 | 4.667 | 8418.13 | 2.127 | 97.9 | 77.6 | 1392 | 22.86 | 5471.8 | 2902.8 | 2818.5 | 4162.5 | 1197.3 | 0.68186 | 6.014
2024-12-09 | 17:48 | Data | 0 | 32.494 | 30.739 | 187.579 | 7.64 | 176.233 | 2142.08 | 25.98 | 46.179 | 6.35 | 1.349 | 4.686 | 8409.08 | 2.127 | 97.8 | 77.6 | 1393 | 23.13 | 5465.9 | 2907.1 | 2799.4 | 4148.9 | 1197.3 | 0.68329 | 6.037
2024-12-09 | 17:49 | Data | 0 | 32.879 | 30.678 | 187.715 | 7.64 | 176.278 | 2137.56 | 25.97 | 46.269 | 6.35 | 1.342 | 4.664 | 8436.21 | 2.1 | 97.8 | 77.7 | 1389 | 23.09 | 5483.5 | 2895.8 | 2809.5 | 4155.3 | 1197.3 | 0.67979 | 6.007
2024-12-09 | 17:49 | Data | 0 | 32.494 | 30.624 | 187.443 | 7.63 | 176.233 | 2141.18 | 25.97 | 46.269 | 6.35 | 1.341 | 4.658 | 8404.56 | 2.012 | 97.8 | 77.6 | 1392 | 23.13 | 5463 | 2914.2 | 2827.1 | 4171.9 | 1197.3 | 0.68299 | 5.999
2024-12-09 | 17:49 | Data | 0 | 32.696 | 30.82 | 187.534 | 7.64 | 176.187 | 2139.37 | 25.98 | 46.179 | 6.35 | 1.354 | 4.645 | 8409.08 | 2.073 | 97.8 | 77.4 | 1391 | 23.09 | 5465.9 | 2890 | 2819.3 | 4155.9 | 1197.3 | 0.67811 | 6
2024-12-09 | 17:49 | Data | 0 | 32.332 | 30.205 | 187.579 | 7.64 | 176.233 | 2138.47 | 25.98 | 46.179 | 6.35 | 1.342 | 4.645 | 8418.13 | 2.181 | 97.8 | 77.6 | 1391 | 23.09 | 5471.8 | 2874 | 2854.9 | 4168.5 | 1197.3 | 0.67294 | 5.988
2024-12-09 | 17:49 | Data | 0 | 32.494 | 30.536 | 187.534 | 7.64 | 176.278 | 2139.37 | 25.98 | 45.998 | 6.34 | 1.347 | 4.655 | 8418.13 | 2.073 | 97.9 | 77.6 | 1391 | 23.04 | 5471.8 | 2895.8 | 2895.2 | 4212.7 | 1197.3 | 0.67065 | 6.002
2024-12-09 | 17:49 | Data | 0 | 32.73 | 30.739 | 187.579 | 7.63 | 176.368 | 2137.56 | 25.98 | 45.998 | 6.34 | 1.348 | 4.676 | 8440.74 | 1.897 | 97.8 | 77.6 | 1391 | 23.04 | 5486.5 | 2905.5 | 2843.7 | 4184 | 1197.3 | 0.67684 | 6.026
2024-12-09 | 17:49 | Data | 0 | 32.534 | 30.415 | 187.579 | 7.63 | 176.278 | 2139.37 | 25.98 | 45.998 | 6.34 | 1.352 | 4.668 | 8463.35 | 1.877 | 97.8 | 77.5 | 1391 | 23 | 5501.2 | 2916.4 | 2865.5 | 4201.7 | 1197.3 | 0.67485 | 6.019
2024-12-09 | 17:49 | Data | 0 | 32.555 | 30.421 | 187.579 | 7.63 | 176.368 | 2140.27 | 25.97 | 45.908 | 6.35 | 1.353 | 4.698 | 8445.26 | 2.079 | 97.9 | 77.6 | 1391 | 22.95 | 5489.4 | 2897.1 | 2863.6 | 4189.8 | 1197.3 | 0.67423 | 6.051
2024-12-09 | 17:49 | Data | 0 | 32.494 | 30.725 | 187.579 | 7.63 | 176.187 | 2134.85 | 25.98 | 45.998 | 6.35 | 1.347 | 4.684 | 8445.26 | 2.1 | 97.8 | 77.7 | 1388 | 23 | 5489.4 | 2916.4 | 2842.7 | 4188.6 | 1197.3 | 0.67928 | 6.031
2024-12-09 | 17:49 | Data | 0 | 32.98 | 30.793 | 187.76 | 7.64 | 176.413 | 2133.95 | 25.98 | 45.727 | 6.35 | 1.348 | 4.677 | 8431.69 | 2.012 | 97.9 | 77.6 | 1387 | 22.86 | 5480.6 | 2893.9 | 2859.9 | 4184.6 | 1197.3 | 0.6739 | 6.026
2024-12-09 | 17:49 | Data | 0 | 32.555 | 30.624 | 187.534 | 7.63 | 176.187 | 2133.95 | 25.98 | 45.998 | 6.35 | 1.352 | 4.679 | 8445.26 | 2.025 | 97.8 | 77.6 | 1387 | 23 | 5489.4 | 2890.1 | 2844.3 | 4179.4 | 1197.3 | 0.67687 | 6.031
2024-12-09 | 17:49 | Data | 0 | 32.73 | 30.651 | 187.67 | 7.64 | 176.368 | 2133.95 | 25.98 | 45.908 | 6.35 | 1.359 | 4.659 | 8445.26 | 2.073 | 97.8 | 77.4 | 1387 | 23 | 5489.4 | 2912.5 | 2847 | 4194.3 | 1197.3 | 0.67901 | 6.017
2024-12-09 | 17:49 | Data | 0 | 32.723 | 30.651 | 187.624 | 7.63 | 176.278 | 2126.72 | 25.97 | 45.998 | 6.35 | 1.357 | 4.672 | 8431.69 | 2.241 | 97.8 | 77.5 | 1382 | 22.95 | 5480.6 | 2905.4 | 2861.4 | 4193.3 | 1197.3 | 0.67633 | 6.028
2024-12-09 | 17:49 | Data | 0 | 32.777 | 30.563 | 187.624 | 7.63 | 176.368 | 2134.85 | 25.97 | 45.998 | 6.35 | 1.356 | 4.646 | 8463.35 | 2.012 | 97.8 | 77.4 | 1387 | 23 | 5501.2 | 2889.8 | 2872.2 | 4193.9 | 1197.3 | 0.67229 | 6.002
2024-12-09 | 17:49 | Data | 0 | 32.507 | 30.637 | 187.534 | 7.63 | 176.233 | 2133.95 | 25.97 | 45.998 | 6.35 | 1.358 | 4.662 | 8485.96 | 1.911 | 97.8 | 77.4 | 1388 | 23 | 5515.9 | 2899.9 | 2849.6 | 4178.5 | 1197.3 | 0.67534 | 6.019
2024-12-09 | 17:49 | Data | 0 | 32.723 | 30.705 | 187.67 | 7.64 | 176.323 | 2133.95 | 25.98 | 45.727 | 6.35 | 1.349 | 4.684 | 8467.87 | 2.046 | 97.9 | 77.6 | 1387 | 22.82 | 5504.1 | 2888.2 | 2854 | 4176.5 | 1197.3 | 0.67382 | 6.036
2024-12-09 | 17:49 | Data | 0 | 32.507 | 30.428 | 187.489 | 7.64 | 176.187 | 2133.95 | 25.98 | 45.818 | 6.35 | 1.349 | 4.666 | 8467.87 | 2.167 | 97.8 | 77.6 | 1388 | 22.95 | 5504.1 | 2908.1 | 2830.5 | 4179.5 | 1197.3 | 0.68125 | 6.016
2024-12-09 | 17:50 | Data | 0 | 32.723 | 30.55 | 187.579 | 7.64 | 176.278 | 2134.85 | 25.97 | 45.998 | 6.35 | 1.353 | 4.665 | 8454.3 | 2.241 | 97.8 | 77.5 | 1387 | 22.95 | 5495.3 | 2894 | 2824.2 | 4160.5 | 1197.3 | 0.67809 | 6.018
2024-12-09 | 17:50 | Data | 0 | 32.73 | 30.475 | 187.624 | 7.64 | 176.278 | 2127.62 | 25.98 | 45.998 | 6.35 | 1.353 | 4.682 | 8472.39 | 1.985 | 97.8 | 77.6 | 1383 | 23.04 | 5507.1 | 2894.8 | 2836.2 | 4166 | 1197.3 | 0.67737 | 6.033
2024-12-09 | 17:50 | Data | 0 | 32.507 | 30.624 | 187.534 | 7.64 | 176.323 | 2125.81 | 25.97 | 45.998 | 6.35 | 1.352 | 4.683 | 8454.3 | 1.87 | 97.8 | 77.6 | 1382 | 23 | 5495.3 | 2923.5 | 2820.1 | 4174.8 | 1197.3 | 0.6825 | 6.036
2024-12-09 | 17:50 | Data | 0 | 32.723 | 30.556 | 187.579 | 7.63 | 176.278 | 2124.91 | 25.98 | 45.998 | 6.35 | 1.348 | 4.692 | 8458.83 | 1.978 | 97.8 | 77.7 | 1382 | 23 | 5498.2 | 2905.9 | 2832.9 | 4174.9 | 1197.3 | 0.67894 | 6.04
2024-12-09 | 17:50 | Data | 0 | 32.831 | 31.036 | 187.579 | 7.64 | 176.368 | 2124.91 | 25.98 | 45.908 | 6.35 | 1.346 | 4.692 | 8436.21 | 1.971 | 97.8 | 77.7 | 1381 | 22.91 | 5483.5 | 2904.8 | 2842.7 | 4182.5 | 1197.3 | 0.67739 | 6.038
2024-12-09 | 17:50 | Data | 0 | 32.71 | 30.658 | 187.579 | 7.64 | 176.278 | 2130.33 | 25.98 | 45.998 | 6.35 | 1.354 | 4.675 | 8440.74 | 1.985 | 97.8 | 77.5 | 1384 | 22.95 | 5486.5 | 2904.9 | 2861.6 | 4196.6 | 1197.3 | 0.67578 | 6.028
2024-12-09 | 17:50 | Data | 0 | 32.642 | 30.597 | 187.624 | 7.63 | 176.323 | 2130.33 | 25.98 | 45.998 | 6.35 | 1.355 | 4.682 | 8427.17 | 2.127 | 97.8 | 77.6 | 1384 | 23 | 5477.7 | 2900.8 | 2852.4 | 4182.9 | 1197.3 | 0.67541 | 6.036
2024-12-09 | 17:50 | Data | 0 | 32.447 | 30.536 | 187.579 | 7.63 | 176.278 | 2134.85 | 25.97 | 48.436 | 6.35 | 1.353 | 4.67 | 8445.26 | 2.127 | 97.7 | 77.5 | 1387 | 24.26 | 5489.4 | 2902.8 | 2869.6 | 4198.9 | 1197.3 | 0.67422 | 6.023
2024-12-09 | 17:50 | Data | 0 | 32.723 | 30.712 | 187.805 | 7.64 | 176.413 | 2134.85 | 25.98 | 46.089 | 6.34 | 1.354 | 4.669 | 8467.87 | 1.944 | 97.8 | 77.5 | 1388 | 23 | 5504.1 | 2926.6 | 2859 | 4204.9 | 1197.3 | 0.67849 | 6.021
2024-12-09 | 17:50 | Data | 0 | 32.676 | 30.543 | 187.579 | 7.64 | 176.278 | 2133.95 | 25.98 | 45.908 | 6.35 | 1.353 | 4.674 | 8436.21 | 1.904 | 97.8 | 77.6 | 1388 | 23 | 5483.5 | 2903.3 | 2845 | 4183.1 | 1197.3 | 0.67666 | 6.027
2024-12-09 | 17:50 | Data | 0 | 32.723 | 30.651 | 187.624 | 7.63 | 176.323 | 2133.95 | 25.98 | 45.998 | 6.35 | 1.349 | 4.64 | 8472.39 | 2.073 | 97.8 | 77.5 | 1387 | 22.95 | 5507.1 | 2909.5 | 2852.6 | 4189 | 1197.3 | 0.6781 | 5.988
2024-12-09 | 17:50 | Data | 0 | 32.723 | 30.651 | 187.534 | 7.64 | 176.278 | 2135.76 | 25.98 | 45.998 | 6.35 | 1.345 | 4.668 | 8458.83 | 2.073 | 97.9 | 77.6 | 1389 | 22.91 | 5498.2 | 2899.8 | 2834.5 | 4173.7 | 1197.3 | 0.67802 | 6.014
2024-12-09 | 17:50 | Data | 0 | 32.723 | 30.651 | 187.624 | 7.64 | 176.278 | 2139.37 | 25.97 | 45.908 | 6.34 | 1.347 | 4.676 | 8431.69 | 2.073 | 97.9 | 77.6 | 1391 | 23 | 5480.6 | 2907.2 | 2838.3 | 4181.9 | 1197.3 | 0.67703 | 6.024
2024-12-09 | 17:50 | Data | 0 | 33.061 | 30.658 | 187.67 | 7.64 | 176.413 | 2140.27 | 25.98 | 45.998 | 6.35 | 1.348 | 4.654 | 8431.69 | 2.005 | 97.9 | 77.5 | 1391 | 22.95 | 5480.6 | 2906.8 | 2845.1 | 4183.5 | 1197.3 | 0.67856 | 6.001
2024-12-09 | 17:50 | Data | 0 | 32.723 | 30.448 | 187.67 | 7.64 | 176.233 | 2140.27 | 25.98 | 45.908 | 6.35 | 1.354 | 4.687 | 8445.26 | 2.025 | 97.9 | 77.6 | 1391 | 23 | 5489.4 | 2909.1 | 2847.7 | 4190.1 | 1197.3 | 0.67706 | 6.041
2024-12-09 | 17:50 | Data | 0 | 32.723 | 30.644 | 187.579 | 7.64 | 176.323 | 2134.85 | 25.98 | 46.089 | 6.35 | 1.348 | 4.686 | 8431.69 | 2.079 | 97.8 | 77.7 | 1386 | 23.04 | 5480.6 | 2551.4 | 2640.8 | 3756.2 | 1197.4 | 0.65738 | 6.035
2024-12-09 | 17:50 | Data | 0 | 32.696 | 30.475 | 187.534 | 7.64 | 176.233 | 2142.08 | 25.98 | 46.089 | 6.35 | 1.341 | 4.691 | 8440.74 | 1.958 | 97.9 | 77.8 | 1392 | 22.91 | 5486.5 | 1807.4 | 2294.9 | 2931.6 | 1197.4 | 0.6138 | 6.033
2024-12-09 | 17:50 | Data | 0 | 32.75 | 30.543 | 187.805 | 7.64 | 176.368 | 2142.08 | 25.98 | 45.998 | 6.34 | 1.351 | 4.685 | 8431.69 | 2.187 | 97.9 | 77.6 | 1392 | 23 | 5480.6 | 1834.2 | 2291 | 2938.7 | 1197.4 | 0.61956 | 6.037
2024-12-09 | 17:51 | Data | 0 | 32.777 | 30.678 | 187.76 | 7.64 | 176.323 | 2142.08 | 25.99 | 45.998 | 6.34 | 1.358 | 4.689 | 8445.26 | 2.032 | 97.9 | 77.5 | 1392 | 23 | 5489.4 | 1823.6 | 2283.4 | 2932.9 | 1197.4 | 0.62 | 6.046
2024-12-09 | 17:51 | Data | 0 | 32.777 | 30.435 | 187.624 | 7.63 | 176.278 | 2136.66 | 25.97 | 45.998 | 6.35 | 1.353 | 4.683 | 8440.74 | 1.971 | 97.8 | 77.6 | 1389 | 23 | 5486.5 | 1820.9 | 2276.5 | 2926.4 | 1197.4 | 0.61984 | 6.036
2024-12-09 | 17:51 | Data | 0 | 32.636 | 30.421 | 187.624 | 7.64 | 176.323 | 2142.99 | 25.97 | 45.998 | 6.35 | 1.347 | 4.697 | 8467.87 | 1.985 | 97.9 | 77.7 | 1394 | 23 | 5504.1 | 1832.7 | 2273.5 | 2931.3 | 1197.4 | 0.62304 | 6.045
2024-12-09 | 17:51 | Data | 0 | 32.501 | 30.651 | 187.67 | 7.64 | 176.233 | 2142.08 | 25.97 | 46.269 | 6.35 | 1.341 | 4.671 | 8458.83 | 1.958 | 97.8 | 77.7 | 1392 | 23.04 | 5498.2 | 1821.7 | 2269.4 | 2919.2 | 1197.4 | 0.62004 | 6.012
2024-12-09 | 17:51 | Data | 0 | 32.723 | 30.705 | 187.624 | 7.63 | 176.323 | 2142.08 | 25.98 | 46.179 | 6.34 | 1.348 | 4.673 | 8458.83 | 2.079 | 97.8 | 77.6 | 1393 | 23.13 | 5498.2 | 1825.1 | 2254.3 | 2912.1 | 1197.4 | 0.62348 | 6.02
2024-12-09 | 17:51 | Data | 0 | 32.332 | 30.421 | 187.624 | 7.63 | 176.233 | 2139.37 | 25.97 | 46.359 | 6.34 | 1.355 | 4.666 | 8431.69 | 1.877 | 97.8 | 77.5 | 1391 | 23.13 | 5480.6 | 1826.1 | 2241 | 2903.1 | 1197.4 | 0.6268 | 6.022
2024-12-09 | 17:51 | Data | 0 | 33 | 30.779 | 187.624 | 7.63 | 176.368 | 2140.27 | 25.99 | 46.179 | 6.35 | 1.352 | 4.672 | 8458.83 | 2.012 | 97.8 | 77.6 | 1391 | 23.13 | 5498.2 | 1821.6 | 2248.5 | 2905.9 | 1197.4 | 0.62457 | 6.024
2024-12-09 | 17:51 | Data | 0 | 32.73 | 30.813 | 187.624 | 7.63 | 176.233 | 2138.47 | 25.97 | 46.269 | 6.35 | 1.355 | 4.675 | 8467.87 | 1.924 | 97.8 | 77.5 | 1390 | 23.09 | 5504.1 | 1807.4 | 2227.1 | 2879.8 | 1197.4 | 0.62754 | 6.03
2024-12-09 | 17:51 | Data | 0 | 32.669 | 30.651 | 187.76 | 7.64 | 176.278 | 2137.56 | 25.98 | 46.089 | 6.34 | 1.349 | 4.683 | 8472.39 | 2.066 | 97.8 | 77.6 | 1389 | 23.09 | 5507.1 | 1835 | 2233.7 | 2902.1 | 1197.4 | 0.62978 | 6.032
2024-12-09 | 17:51 | Data | 0 | 32.717 | 30.752 | 187.534 | 7.63 | 176.233 | 2135.76 | 25.98 | 46.54 | 6.35 | 1.348 | 4.654 | 8467.87 | 2.039 | 97.8 | 77.5 | 1388 | 23.22 | 5504.1 | 1861.3 | 2268.5 | 2946.9 | 1197.4 | 0.62937 | 6
2024-12-09 | 17:51 | Data | 0 | 32.507 | 30.421 | 187.534 | 7.64 | 176.233 | 2133.95 | 25.96 | 46.179 | 6.34 | 1.358 | 4.669 | 8440.74 | 2.073 | 97.8 | 77.5 | 1387 | 23.09 | 5486.5 | 1838 | 2260.3 | 2926.2 | 1197.4 | 0.62527 | 6.026
2024-12-09 | 17:51 | Data | 0 | 32.71 | 30.651 | 187.715 | 7.63 | 176.323 | 2133.95 | 25.96 | 46.269 | 6.34 | 1.347 | 4.682 | 8458.83 | 2.073 | 97.8 | 77.7 | 1388 | 23.09 | 5498.2 | 1841.8 | 2288.5 | 2949.1 | 1197.4 | 0.62171 | 6.028
2024-12-09 | 17:51 | Data | 0 | 32.669 | 30.928 | 187.76 | 7.64 | 176.278 | 2133.95 | 25.98 | 46.269 | 6.35 | 1.348 | 4.658 | 8440.74 | 1.998 | 97.8 | 77.6 | 1387 | 23.13 | 5486.5 | 1836.8 | 2273.6 | 2934.9 | 1197.4 | 0.62263 | 6.005
2024-12-09 | 17:51 | Data | 0 | 32.71 | 30.752 | 187.534 | 7.63 | 176.187 | 2133.95 | 25.98 | 46.269 | 6.35 | 1.348 | 4.666 | 8440.74 | 2.093 | 97.8 | 77.6 | 1387 | 23.13 | 5486.5 | 1841.3 | 2260.5 | 2928.5 | 1197.4 | 0.62453 | 6.013
2024-12-09 | 17:51 | Data | 0 | 32.838 | 30.536 | 187.76 | 7.64 | 176.413 | 2134.85 | 25.97 | 46.269 | 6.35 | 1.338 | 4.669 | 8445.26 | 1.965 | 97.8 | 77.8 | 1387 | 23.13 | 5489.4 | 1832.2 | 2232.9 | 2903.9 | 1197.4 | 0.62809 | 6.004
2024-12-09 | 17:51 | Data | 0 | 32.609 | 30.759 | 187.624 | 7.63 | 176.278 | 2134.85 | 25.98 | 45.908 | 6.35 | 1.346 | 4.652 | 8485.96 | 2.032 | 97.9 | 77.6 | 1388 | 22.95 | 5515.9 | 1831.5 | 2233.4 | 2900.9 | 1197.4 | 0.6289 | 5.998
2024-12-09 | 17:51 | Data | 0 | 32.507 | 30.563 | 187.579 | 7.63 | 176.323 | 2131.24 | 25.98 | 45.998 | 6.34 | 1.356 | 4.702 | 8472.39 | 1.965 | 97.8 | 77.7 | 1387 | 23 | 5507.1 | 1834.3 | 2225.7 | 2899 | 1197.4 | 0.62976 | 6.058
2024-12-09 | 17:51 | Data | 0 | 32.467 | 30.428 | 187.489 | 7.64 | 176.278 | 2127.62 | 25.98 | 46.269 | 6.34 | 1.358 | 4.682 | 8445.26 | 2.248 | 97.8 | 77.5 | 1383 | 23.09 | 5489.4 | 1848.3 | 2217.5 | 2898.1 | 1197.4 | 0.63508 | 6.039
2024-12-09 | 17:52 | Data | 0 | 32.717 | 30.651 | 187.579 | 7.64 | 176.323 | 2133.95 | 25.97 | 45.998 | 6.34 | 1.349 | 4.66 | 8440.74 | 2.073 | 97.8 | 77.6 | 1388 | 23 | 5486.5 | 1852.1 | 2238.2 | 2917.5 | 1197.4 | 0.6322 | 6.007
2024-12-09 | 17:52 | Data | 0 | 32.285 | 30.475 | 187.67 | 7.64 | 176.233 | 2136.66 | 25.98 | 46.269 | 6.35 | 1.342 | 4.626 | 8445.26 | 1.971 | 97.8 | 77.5 | 1389 | 23.09 | 5489.4 | 1835.5 | 2254.7 | 2921.8 | 1197.4 | 0.62674 | 5.97
2024-12-09 | 17:52 | Data | 0 | 32.744 | 30.651 | 187.624 | 7.63 | 176.323 | 2131.24 | 25.98 | 46.179 | 6.35 | 1.351 | 4.664 | 8449.78 | 2.079 | 97.8 | 77.5 | 1385 | 23.13 | 5492.4 | 1834.9 | 2248.7 | 2915.2 | 1197.4 | 0.62439 | 6.017
2024-12-09 | 17:52 | Data | 0 | 32.94 | 30.556 | 187.67 | 7.63 | 176.323 | 2125.81 | 25.96 | 46.269 | 6.35 | 1.348 | 4.663 | 8436.21 | 2.106 | 97.8 | 77.6 | 1381 | 23.13 | 5483.5 | 1827.9 | 2277.9 | 2934.3 | 1197.4 | 0.62044 | 6.011
2024-12-09 | 17:52 | Data | 0 | 32.69 | 30.82 | 187.534 | 7.63 | 176.278 | 2130.33 | 25.98 | 45.998 | 6.35 | 1.357 | 4.641 | 8440.74 | 2.133 | 97.8 | 77.4 | 1385 | 23 | 5486.5 | 1850.8 | 2256.5 | 2920.1 | 1197.4 | 0.62831 | 5.998
2024-12-09 | 17:52 | Data | 0 | 32.723 | 30.678 | 187.624 | 7.63 | 176.233 | 2126.72 | 25.98 | 46.179 | 6.35 | 1.354 | 4.673 | 8431.69 | 2.012 | 97.8 | 77.5 | 1383 | 23.09 | 5480.6 | 1839.7 | 2239.6 | 2909.3 | 1197.4 | 0.62961 | 6.028
2024-12-09 | 17:52 | Data | 0 | 32.717 | 30.82 | 187.624 | 7.64 | 176.323 | 2128.52 | 25.98 | 46.089 | 6.34 | 1.346 | 4.673 | 8418.13 | 1.965 | 97.8 | 77.6 | 1384 | 23.04 | 5471.8 | 1839 | 2269.1 | 2934.9 | 1197.4 | 0.62414 | 6.018
2024-12-09 | 17:52 | Data | 0 | 32.494 | 30.421 | 187.67 | 7.63 | 176.233 | 2127.62 | 25.97 | 45.908 | 6.34 | 1.358 | 4.671 | 8418.13 | 2.1 | 97.8 | 77.5 | 1384 | 22.91 | 5471.8 | 1830.2 | 2272.7 | 2931.7 | 1197.4 | 0.62124 | 6.029
2024-12-09 | 17:52 | Data | 0 | 32.278 | 30.806 | 187.624 | 7.64 | 176.278 | 2137.56 | 25.98 | 45.998 | 6.35 | 1.349 | 4.665 | 8422.65 | 1.843 | 97.8 | 77.5 | 1388 | 23 | 5474.7 | 1837 | 2262.9 | 2926.3 | 1197.4 | 0.62294 | 6.017
2024-12-09 | 17:52 | Data | 0 | 32.973 | 30.59 | 187.534 | 7.64 | 176.278 | 2130.33 | 25.97 | 45.908 | 6.35 | 1.356 | 4.684 | 8422.65 | 2.052 | 97.8 | 77.6 | 1385 | 22.95 | 5474.7 | 1820.4 | 2255.9 | 2911.3 | 1197.4 | 0.6231 | 6.04
2024-12-09 | 17:52 | Data | 0 | 32.507 | 30.624 | 187.805 | 7.64 | 176.278 | 2132.14 | 25.98 | 46.359 | 6.35 | 1.348 | 4.668 | 8422.65 | 2.012 | 97.8 | 77.6 | 1386 | 23.13 | 5474.7 | 1836.2 | 2277.6 | 2936.4 | 1197.4 | 0.62307 | 6.018
2024-12-09 | 17:52 | Data | 0 | 32.71 | 30.88 | 187.851 | 7.63 | 176.278 | 2131.24 | 25.98 | 46.179 | 6.34 | 1.349 | 4.64 | 8431.69 | 1.971 | 97.8 | 77.5 | 1385 | 23.13 | 5480.6 | 1826.5 | 2258.6 | 2935.2 | 1197.4 | 0.62092 | 5.988
2024-12-09 | 17:52 | Data | 0 | 32.521 | 30.415 | 187.624 | 7.64 | 176.233 | 2131.24 | 25.99 | 46.269 | 6.35 | 1.352 | 4.665 | 8418.13 | 2.079 | 97.8 | 77.5 | 1385 | 23.09 | 5471.8 | 1816.4 | 2283.6 | 2929.4 | 1197.4 | 0.61949 | 6.017
2024-12-09 | 17:52 | Data | 0 | 32.94 | 30.658 | 187.67 | 7.63 | 176.413 | 2130.33 | 25.96 | 46.269 | 6.35 | 1.357 | 4.685 | 8422.65 | 2.113 | 97.8 | 77.5 | 1385 | 23.13 | 5474.7 | 1815.9 | 2250.1 | 2903.3 | 1197.4 | 0.62368 | 6.043
2024-12-09 | 17:52 | Data | 0 | 32.879 | 30.705 | 187.579 | 7.63 | 176.278 | 2130.33 | 25.97 | 46.359 | 6.35 | 1.347 | 4.672 | 8418.13 | 2.127 | 97.8 | 77.6 | 1385 | 23.22 | 5471.8 | 1835 | 2251 | 2915.9 | 1197.4 | 0.62357 | 6.017
2024-12-09 | 17:52 | Data | 0 | 32.575 | 30.415 | 187.715 | 7.64 | 176.233 | 2130.33 | 25.97 | 46.179 | 6.35 | 1.351 | 4.641 | 8409.08 | 1.857 | 97.8 | 77.4 | 1385 | 23.13 | 5465.9 | 1820 | 2261.2 | 2914.8 | 1197.4 | 0.62163 | 5.994
2024-12-09 | 17:52 | Data | 0 | 32.278 | 30.415 | 187.489 | 7.63 | 176.278 | 2130.33 | 25.98 | 46.179 | 6.33 | 1.338 | 4.653 | 8418.13 | 1.857 | 97.8 | 77.7 | 1385 | 23.09 | 5471.8 | 1818.2 | 2263.6 | 2919.6 | 1197.4 | 0.62072 | 5.99
2024-12-09 | 17:52 | Data | 0 | 32.44 | 30.415 | 187.534 | 7.64 | 176.233 | 2131.24 | 25.98 | 46.359 | 6.35 | 1.339 | 4.657 | 8431.69 | 2.066 | 97.8 | 77.7 | 1385 | 23.13 | 5480.6 | 1832.3 | 2270.9 | 2930 | 1197.4 | 0.62302 | 5.997
2024-12-09 | 17:53 | Data | 0 | 32.71 | 30.475 | 187.489 | 7.63 | 176.233 | 2130.33 | 25.97 | 46.179 | 6.35 | 1.348 | 4.675 | 8418.13 | 1.958 | 97.8 | 77.6 | 1385 | 23.13 | 5471.8 | 1830 | 2265.4 | 2923.9 | 1197.4 | 0.62321 | 6.023
2024-12-09 | 17:53 | Data | 0 | 32.696 | 30.421 | 187.489 | 7.63 | 176.187 | 2123.1 | 25.96 | 46.179 | 6.35 | 1.351 | 4.699 | 8418.13 | 2.12 | 97.8 | 77.7 | 1380 | 23.09 | 5471.8 | 1845.7 | 2277.4 | 2944.7 | 1197.4 | 0.62581 | 6.048
2024-12-09 | 17:53 | Data | 0 | 32.494 | 30.415 | 187.624 | 7.64 | 176.233 | 2127.62 | 25.96 | 46.269 | 6.34 | 1.348 | 4.673 | 8404.56 | 2.079 | 97.8 | 77.6 | 1382 | 23.09 | 5463 | 1834.4 | 2253.7 | 2918.3 | 1197.4 | 0.626 | 6.021
2024-12-09 | 17:53 | Data | 0 | 32.622 | 30.421 | 187.534 | 7.63 | 176.233 | 2127.62 | 25.96 | 46.179 | 6.34 | 1.347 | 4.656 | 8427.17 | 1.911 | 97.8 | 77.6 | 1383 | 23.13 | 5477.7 | 1828.5 | 2294.6 | 2931 | 1197.4 | 0.61679 | 6.003
2024-12-09 | 17:53 | Data | 0 | 32.696 | 30.86 | 187.579 | 7.63 | 176.233 | 2125.81 | 25.95 | 46.179 | 6.35 | 1.341 | 4.658 | 8431.69 | 2.039 | 97.8 | 77.6 | 1382 | 23.09 | 5480.6 | 1832.8 | 2287 | 2946.3 | 1197.4 | 0.62007 | 6
2024-12-09 | 17:53 | Data | 0 | 32.852 | 30.658 | 187.76 | 7.64 | 176.413 | 2125.81 | 25.95 | 46.179 | 6.35 | 1.36 | 4.654 | 8431.69 | 1.971 | 97.8 | 77.4 | 1382 | 23.13 | 5480.6 | 3152 | 3487.8 | 4816.9 | 1197.4 | 0.63527 | 6.014
2024-12-09 | 17:53 | Data | 0 | 32.879 | 30.489 | 187.67 | 7.64 | 176.233 | 2129.43 | 25.98 | 46.089 | 6.35 | 1.348 | 4.645 | 8445.26 | 2.208 | 97.8 | 77.5 | 1384 | 23.09 | 5489.4 | 2909.8 | 2901.5 | 4232.7 | 1197.4 | 0.66908 | 5.994
2024-12-09 | 17:53 | Data | 0 | 32.717 | 30.442 | 187.443 | 7.64 | 176.187 | 2128.52 | 25.97 | 46.179 | 6.34 | 1.338 | 4.666 | 8458.83 | 2.073 | 97.8 | 77.7 | 1384 | 23.13 | 5498.2 | 2897.1 | 2892.6 | 4215.1 | 1197.4 | 0.66963 | 6.004
2024-12-09 | 17:53 | Data | 0 | 32.325 | 30.205 | 187.489 | 7.64 | 176.233 | 2130.33 | 25.96 | 46.269 | 6.35 | 1.338 | 4.674 | 8472.39 | 2.336 | 97.8 | 77.7 | 1385 | 23 | 5507.1 | 2915.4 | 2910.5 | 4237.2 | 1197.4 | 0.67074 | 6.012
2024-12-09 | 17:53 | Data | 0 | 32.379 | 30.415 | 187.67 | 7.64 | 176.233 | 2132.14 | 25.96 | 45.998 | 6.35 | 1.34 | 4.676 | 8481.44 | 1.992 | 97.8 | 77.7 | 1386 | 23 | 5512.9 | 2911.2 | 2876.5 | 4210.1 | 1197.4 | 0.67409 | 6.017
2024-12-09 | 17:53 | Data | 0 | 32.298 | 30.415 | 187.443 | 7.63 | 176.142 | 2133.95 | 25.97 | 45.998 | 6.34 | 1.34 | 4.672 | 8485.96 | 1.971 | 97.8 | 77.7 | 1387 | 22.95 | 5515.9 | 2917 | 2864.4 | 4206.5 | 1197.4 | 0.67699 | 6.012
2024-12-09 | 17:53 | Data | 0 | 32.359 | 30.415 | 187.579 | 7.63 | 176.233 | 2134.85 | 25.96 | 45.908 | 6.35 | 1.338 | 4.685 | 8440.74 | 1.863 | 97.8 | 77.8 | 1388 | 22.95 | 5486.5 | 2923 | 2820.9 | 4184.7 | 1197.4 | 0.68159 | 6.022
2024-12-09 | 17:53 | Data | 0 | 32.298 | 30.394 | 187.443 | 7.64 | 176.142 | 2136.66 | 25.97 | 46.089 | 6.35 | 1.335 | 4.663 | 8445.26 | 1.897 | 97.8 | 77.7 | 1389 | 23.04 | 5489.4 | 2923.5 | 2804.5 | 4171.1 | 1197.4 | 0.68495 | 5.998
2024-12-09 | 17:53 | Data | 0 | 32.318 | 30.415 | 187.443 | 7.63 | 176.142 | 2136.66 | 25.96 | 46.179 | 6.35 | 1.351 | 4.676 | 8440.74 | 1.863 | 97.8 | 77.6 | 1389 | 22.91 | 5486.5 | 2889.6 | 2800.7 | 4147.6 | 1197.4 | 0.68006 | 6.028
2024-12-09 | 17:53 | Data | 0 | 32.494 | 30.583 | 187.489 | 7.64 | 176.187 | 2134.85 | 25.95 | 45.998 | 6.34 | 1.352 | 4.681 | 8458.83 | 2.106 | 97.8 | 77.6 | 1388 | 23 | 5498.2 | 2926.5 | 2830.9 | 4184.1 | 1197.5 | 0.68252 | 6.034
2024-12-09 | 17:53 | Data | 0 | 32.582 | 30.415 | 187.579 | 7.63 | 176.233 | 2133.95 | 25.96 | 45.908 | 6.35 | 1.349 | 4.645 | 8454.3 | 2.14 | 97.8 | 77.5 | 1387 | 23 | 5495.3 | 2920.4 | 2838.6 | 4184.7 | 1197.5 | 0.679 | 5.994
2024-12-09 | 17:53 | Data | 0 | 32.615 | 30.415 | 187.624 | 7.64 | 176.233 | 2133.95 | 25.96 | 45.998 | 6.35 | 1.355 | 4.655 | 8458.83 | 1.917 | 97.8 | 77.5 | 1387 | 23 | 5498.2 | 2915.2 | 2866.6 | 4204.3 | 1197.5 | 0.6751 | 6.009
2024-12-09 | 17:54 | Data | 0 | 32.663 | 30.644 | 187.624 | 7.64 | 176.278 | 2133.95 | 25.98 | 45.908 | 6.35 | 1.349 | 4.674 | 8458.83 | 2.174 | 97.8 | 77.6 | 1386 | 23 | 5498.2 | 2916.2 | 2873.5 | 4208.2 | 1197.5 | 0.67584 | 6.023
2024-12-09 | 17:54 | Data | 0 | 32.582 | 30.671 | 187.489 | 7.64 | 176.142 | 2131.24 | 25.97 | 45.998 | 6.35 | 1.352 | 4.68 | 8445.26 | 2.093 | 97.8 | 77.6 | 1385 | 22.95 | 5489.4 | 2908.4 | 2894.8 | 4219.7 | 1197.5 | 0.6724 | 6.032
2024-12-09 | 17:54 | Data | 0 | 32.467 | 30.212 | 187.443 | 7.64 | 176.142 | 2134.85 | 25.98 | 45.998 | 6.35 | 1.351 | 4.636 | 8400.04 | 2.127 | 97.8 | 77.4 | 1387 | 23 | 5460 | 2877.6 | 2865.2 | 4176.5 | 1197.5 | 0.67079 | 5.988
2024-12-09 | 17:54 | Data | 0 | 32.507 | 30.739 | 187.353 | 7.63 | 176.097 | 2133.95 | 25.97 | 45.998 | 6.35 | 1.353 | 4.683 | 8395.51 | 1.904 | 97.8 | 77.6 | 1388 | 22.95 | 5457.1 | 2924.5 | 2866.2 | 4211.8 | 1197.5 | 0.67632 | 6.035
2024-12-09 | 17:54 | Data | 0 | 32.379 | 30.59 | 187.534 | 7.63 | 176.187 | 2133.95 | 25.98 | 45.998 | 6.36 | 1.346 | 4.668 | 8395.51 | 2.167 | 97.8 | 77.6 | 1387 | 23 | 5457.1 | 2878.2 | 2829.1 | 4157.1 | 1197.5 | 0.67408 | 6.013
2024-12-09 | 17:54 | Data | 0 | 32.278 | 30.165 | 187.398 | 7.63 | 176.097 | 2137.56 | 25.98 | 45.908 | 6.35 | 1.351 | 4.671 | 8395.51 | 2.127 | 97.9 | 77.6 | 1388 | 23 | 5457.1 | 2892.9 | 2801 | 4146.7 | 1197.5 | 0.68044 | 6.021
2024-12-09 | 17:54 | Data | 0 | 32.467 | 30.415 | 187.353 | 7.63 | 176.097 | 2133.95 | 25.98 | 45.818 | 6.35 | 1.342 | 4.649 | 8363.86 | 2.079 | 97.8 | 77.6 | 1387 | 22.95 | 5436.5 | 2906.1 | 2817.1 | 4171.4 | 1197.5 | 0.68284 | 5.991
2024-12-09 | 17:54 | Data | 0 | 32.609 | 30.307 | 187.443 | 7.64 | 176.233 | 2133.95 | 25.98 | 45.908 | 6.34 | 1.345 | 4.673 | 8368.38 | 2.086 | 97.8 | 77.7 | 1387 | 23 | 5439.4 | 2909.6 | 2783.6 | 4143.1 | 1197.5 | 0.68572 | 6.017
2024-12-09 | 17:54 | Data | 0 | 32.433 | 30.435 | 187.489 | 7.64 | 176.142 | 2130.33 | 25.98 | 45.908 | 6.35 | 1.344 | 4.677 | 8359.34 | 2.187 | 97.8 | 77.7 | 1385 | 23.09 | 5433.6 | 2895.7 | 2797.8 | 4144.8 | 1197.5 | 0.68233 | 6.021
2024-12-09 | 17:54 | Data | 0 | 32.494 | 30.415 | 187.443 | 7.63 | 176.142 | 2131.24 | 25.96 | 45.998 | 6.35 | 1.348 | 4.674 | 8372.9 | 2.079 | 97.8 | 77.6 | 1386 | 22.95 | 5442.4 | 2891.4 | 2816.2 | 4154.8 | 1197.5 | 0.67871 | 6.022
2024-12-09 | 17:54 | Data | 0 | 32.622 | 30.448 | 187.443 | 7.63 | 176.187 | 2127.62 | 25.98 | 45.908 | 6.35 | 1.349 | 4.665 | 8395.51 | 1.965 | 97.8 | 77.5 | 1383 | 23 | 5457.1 | 2889.1 | 2821.7 | 4155.3 | 1197.5 | 0.67761 | 6.017
2024-12-09 | 17:54 | Data | 0 | 32.663 | 30.421 | 187.489 | 7.63 | 176.142 | 2128.52 | 25.99 | 45.908 | 6.35 | 1.348 | 4.648 | 8386.47 | 2.1 | 97.8 | 77.5 | 1384 | 22.95 | 5451.2 | 2889.7 | 2829.1 | 4160.9 | 1197.5 | 0.67724 | 5.995
2024-12-09 | 17:54 | Data | 0 | 32.264 | 30.388 | 187.443 | 7.64 | 176.142 | 2127.62 | 25.99 | 45.998 | 6.34 | 1.353 | 4.65 | 8409.08 | 1.897 | 97.8 | 77.5 | 1383 | 23 | 5465.9 | 2908.1 | 2862.2 | 4199.1 | 1197.5 | 0.67533 | 6.003
2024-12-09 | 17:54 | Data | 0 | 32.913 | 30.482 | 187.579 | 7.63 | 176.278 | 2124.91 | 25.98 | 45.908 | 6.35 | 1.348 | 4.673 | 8874.87 | 2.073 | 97.8 | 77.6 | 1381 | 22.95 | 5768.7 | 2874.6 | 2852 | 4167.4 | 1197.5 | 0.67326 | 6.02
2024-12-09 | 17:54 | Data | 0 | 32.285 | 30.307 | 187.534 | 7.63 | 176.233 | 2125.81 | 25.98 | 45.998 | 6.35 | 1.344 | 4.665 | 8409.08 | 2.073 | 97.8 | 77.6 | 1381 | 22.95 | 5465.9 | 2903.4 | 2835.6 | 4174.7 | 1197.5 | 0.67833 | 6.009
2024-12-09 | 17:54 | Data | 0 | 32.339 | 30.536 | 187.534 | 7.63 | 176.233 | 2034.53 | 25.97 | 46.179 | 6.35 | 1.346 | 4.645 | 8409.08 | 1.87 | 97.7 | 77.5 | 1322 | 23.13 | 5465.9 | 2893.2 | 2844.8 | 4173.7 | 1197.5 | 0.67599 | 5.991
2024-12-09 | 17:54 | Data | 0 | 32.71 | 30.428 | 187.353 | 7.63 | 176.233 | 2132.14 | 25.96 | 46.089 | 6.35 | 1.351 | 4.66 | 8418.13 | 2.133 | 97.8 | 77.5 | 1385 | 22.95 | 5471.8 | 2909.2 | 2830.7 | 4164.9 | 1197.5 | 0.67992 | 6.013
2024-12-09 | 17:54 | Data | 0 | 32.764 | 30.455 | 187.579 | 7.64 | 176.233 | 2135.76 | 25.97 | 45.998 | 6.35 | 1.344 | 4.685 | 8409.08 | 2.1 | 97.8 | 77.7 | 1389 | 22.95 | 5465.9 | 2906.5 | 2847.9 | 4183.5 | 1197.5 | 0.67755 | 6.027
2024-12-09 | 17:55 | Data | 0 | 32.69 | 30.739 | 187.624 | 7.63 | 176.187 | 2136.66 | 25.98 | 45.908 | 6.36 | 1.343 | 4.682 | 8458.83 | 1.897 | 97.8 | 77.7 | 1389 | 23 | 5498.2 | 2915.6 | 2819.1 | 4170.4 | 1197.5 | 0.68321 | 6.026
2024-12-09 | 17:55 | Data | 0 | 32.48 | 30.624 | 187.489 | 7.64 | 176.142 | 2135.76 | 25.98 | 45.908 | 6.34 | 1.336 | 4.673 | 8431.69 | 2.079 | 97.8 | 77.8 | 1389 | 23 | 5480.6 | 2913.9 | 2836.7 | 4182.1 | 1197.5 | 0.67843 | 6.008
2024-12-09 | 17:55 | Data | 0 | 32.386 | 30.442 | 187.534 | 7.64 | 176.142 | 2137.56 | 25.98 | 45.998 | 6.34 | 1.339 | 4.671 | 8427.17 | 1.877 | 97.8 | 77.7 | 1389 | 23 | 5477.7 | 2906.7 | 2809.4 | 4160.1 | 1197.5 | 0.68183 | 6.01
2024-12-09 | 17:55 | Data | 0 | 32.555 | 30.448 | 187.534 | 7.63 | 176.278 | 2137.56 | 25.98 | 45.998 | 6.34 | 1.342 | 4.668 | 8431.69 | 1.836 | 97.8 | 77.7 | 1389 | 23 | 5480.6 | 2908.3 | 2848.4 | 4185.5 | 1197.5 | 0.67825 | 6.01
2024-12-09 | 17:55 | Data | 0 | 32.271 | 30.415 | 187.534 | 7.63 | 176.187 | 2134.85 | 25.97 | 45.998 | 6.34 | 1.346 | 4.654 | 8431.69 | 1.85 | 97.8 | 77.6 | 1388 | 23.04 | 5480.6 | 2904.7 | 2837.6 | 4171.8 | 1197.5 | 0.67923 | 5.999
2024-12-09 | 17:55 | Data | 0 | 32.71 | 30.475 | 187.489 | 7.63 | 176.142 | 2136.66 | 25.97 | 45.908 | 6.35 | 1.351 | 4.675 | 8440.74 | 2.059 | 97.9 | 77.6 | 1389 | 23 | 5486.5 | 2926.9 | 2844.8 | 4198.5 | 1197.5 | 0.67908 | 6.028
2024-12-09 | 17:55 | Data | 0 | 32.696 | 30.259 | 187.489 | 7.64 | 176.233 | 2136.66 | 25.99 | 45.727 | 6.35 | 1.351 | 4.665 | 8888.44 | 2.262 | 97.9 | 77.5 | 1389 | 22.86 | 5777.5 | 2893.2 | 2834.3 | 4150.4 | 1197.5 | 0.6783 | 6.017
2024-12-09 | 17:55 | Data | 0 | 32.723 | 30.651 | 187.534 | 7.64 | 176.278 | 2137.56 | 25.99 | 46.089 | 6.35 | 1.356 | 4.656 | 8463.35 | 2.073 | 97.9 | 77.4 | 1389 | 23 | 5501.2 | 2895.9 | 2824.9 | 4172.4 | 1197.5 | 0.6788 | 6.01
2024-12-09 | 17:55 | Data | 0 | 32.548 | 30.415 | 187.579 | 7.63 | 176.142 | 2137.56 | 25.97 | 45.998 | 6.35 | 1.358 | 4.675 | 8449.78 | 2.086 | 97.9 | 77.5 | 1388 | 23 | 5492.4 | 2904.3 | 2859.8 | 4192 | 1197.5 | 0.67572 | 6.033
2024-12-09 | 17:55 | Data | 0 | 32.555 | 30.442 | 187.443 | 7.63 | 176.233 | 2136.66 | 25.98 | 45.998 | 6.35 | 1.351 | 4.667 | 8472.39 | 2.032 | 97.8 | 77.5 | 1388 | 23.04 | 5507.1 | 2908.2 | 2867.1 | 4202.6 | 1197.5 | 0.67432 | 6.018
2024-12-09 | 17:55 | Data | 0 | 32.663 | 30.469 | 187.579 | 7.63 | 176.233 | 2134.85 | 25.98 | 45.998 | 6.35 | 1.353 | 4.677 | 8467.87 | 2.046 | 97.8 | 77.6 | 1388 | 23 | 5504.1 | 2908.8 | 2853.4 | 4189.9 | 1197.5 | 0.67736 | 6.032
2024-12-09 | 17:55 | Data | 0 | 32.494 | 30.516 | 187.489 | 7.64 | 176.233 | 2135.76 | 25.97 | 45.998 | 6.35 | 1.34 | 4.673 | 8467.87 | 1.87 | 97.8 | 77.7 | 1389 | 23 | 5504.1 | 2894.4 | 2853 | 4183 | 1197.5 | 0.67449 | 6.014
2024-12-09 | 17:55 | Data | 0 | 32.278 | 30.637 | 187.489 | 7.64 | 176.187 | 2133.95 | 25.98 | 45.908 | 6.34 | 1.34 | 4.675 | 8902 | 1.938 | 97.9 | 77.7 | 1388 | 22.95 | 5786.3 | 2913.7 | 2855.6 | 4191.6 | 1197.5 | 0.67666 | 6.015
2024-12-09 | 17:55 | Data | 0 | 32.366 | 30.421 | 187.579 | 7.64 | 176.278 | 2134.85 | 25.98 | 46.089 | 6.35 | 1.351 | 4.67 | 8476.91 | 1.695 | 97.8 | 77.6 | 1388 | 22.95 | 5510 | 2917.9 | 2850.6 | 4192.9 | 1197.5 | 0.67903 | 6.02
2024-12-09 | 17:55 | Data | 0 | 32.764 | 30.543 | 187.443 | 7.64 | 176.187 | 2134.85 | 25.97 | 45.998 | 6.34 | 1.344 | 4.668 | 8458.83 | 2.093 | 97.8 | 77.6 | 1387 | 23.04 | 5498.2 | 2890.1 | 2867.2 | 4190.2 | 1197.6 | 0.67358 | 6.011
2024-12-09 | 17:55 | Data | 0 | 32.379 | 30.59 | 187.443 | 7.63 | 176.142 | 2133.95 | 25.97 | 45.998 | 6.35 | 1.339 | 4.682 | 8445.26 | 1.985 | 97.8 | 77.8 | 1388 | 23.09 | 5489.4 | 2904 | 2845 | 4180.4 | 1197.6 | 0.67775 | 6.022
2024-12-09 | 17:56 | Data | 0 | 32.379 | 30.415 | 187.398 | 7.64 | 176.187 | 2133.95 | 25.96 | 45.998 | 6.34 | 1.344 | 4.663 | 8440.74 | 2.181 | 97.8 | 77.6 | 1388 | 22.95 | 5486.5 | 2911.6 | 2863.8 | 4199.3 | 1197.6 | 0.6763 | 6.006
2024-12-09 | 17:56 | Data | 0 | 32.521 | 30.401 | 187.534 | 7.64 | 176.233 | 2133.95 | 25.98 | 46.089 | 6.35 | 1.346 | 4.64 | 8449.78 | 1.884 | 97.8 | 77.5 | 1387 | 23 | 5492.4 | 2910.5 | 2833 | 4175.7 | 1197.6 | 0.68071 | 5.986
2024-12-09 | 17:56 | Data | 0 | 32.494 | 30.516 | 187.443 | 7.63 | 176.187 | 2133.95 | 25.98 | 45.908 | 6.35 | 1.351 | 4.677 | 8454.3 | 2.073 | 97.8 | 77.6 | 1387 | 23.04 | 5495.3 | 2904.7 | 2820.4 | 4168.1 | 1197.6 | 0.67972 | 6.028
2024-12-09 | 17:56 | Data | 0 | 32.501 | 30.624 | 187.579 | 7.63 | 176.278 | 2132.14 | 25.98 | 45.998 | 6.35 | 1.358 | 4.659 | 8481.44 | 2.073 | 97.8 | 77.4 | 1387 | 23 | 5512.9 | 2911.6 | 2824.1 | 4173.3 | 1197.6 | 0.68171 | 6.017
2024-12-09 | 17:56 | Data | 0 | 32.17 | 30.388 | 187.534 | 7.63 | 176.233 | 2131.24 | 25.98 | 46.269 | 6.34 | 1.359 | 4.673 | 8481.44 | 1.836 | 97.8 | 77.5 | 1384 | 23.09 | 5512.9 | 2928 | 2860.9 | 4210.1 | 1197.6 | 0.67754 | 6.033
2024-12-09 | 17:56 | Data | 0 | 32.393 | 30.415 | 187.579 | 7.64 | 176.233 | 2134.85 | 25.98 | 46.089 | 6.34 | 1.336 | 4.639 | 8495 | 2.039 | 97.8 | 77.6 | 1388 | 23.04 | 5521.8 | 2919.2 | 2838.7 | 4189 | 1197.6 | 0.67913 | 5.974
2024-12-09 | 17:56 | Data | 0 | 32.339 | 30.415 | 187.534 | 7.63 | 176.233 | 2138.47 | 25.98 | 46.179 | 6.35 | 1.352 | 4.654 | 8476.91 | 1.863 | 97.8 | 77.5 | 1391 | 23.13 | 5510 | 2908.5 | 2849 | 4185.9 | 1197.6 | 0.67798 | 6.005
2024-12-09 | 17:56 | Data | 0 | 32.609 | 30.259 | 187.579 | 7.63 | 176.278 | 2133.95 | 25.98 | 46.179 | 6.35 | 1.354 | 4.672 | 8481.44 | 2.066 | 97.8 | 77.5 | 1387 | 23.09 | 5512.9 | 2898.5 | 2869.1 | 4192.5 | 1197.6 | 0.67527 | 6.025
2024-12-09 | 17:56 | Data | 0 | 32.723 | 30.691 | 187.489 | 7.63 | 176.187 | 2133.95 | 25.98 | 46.269 | 6.34 | 1.352 | 4.677 | 8467.87 | 2.032 | 97.8 | 77.6 | 1387 | 23.13 | 5504.1 | 2909.8 | 2855.9 | 4193.6 | 1197.6 | 0.6762 | 6.028
2024-12-09 | 17:56 | Data | 0 | 32.75 | 30.225 | 187.579 | 7.63 | 176.278 | 2134.85 | 25.98 | 46.269 | 6.35 | 1.349 | 4.67 | 8476.91 | 2.208 | 97.8 | 77.6 | 1388 | 23.09 | 5510 | 2898.8 | 2870.1 | 4196.7 | 1197.6 | 0.67304 | 6.019
2024-12-09 | 17:56 | Data | 0 | 32.501 | 30.651 | 187.67 | 7.64 | 176.233 | 2134.85 | 25.97 | 46.179 | 6.36 | 1.346 | 4.651 | 8481.44 | 1.931 | 97.8 | 77.6 | 1387 | 23.13 | 5512.9 | 2911.7 | 2861 | 4195 | 1197.6 | 0.67583 | 5.998
2024-12-09 | 17:56 | Data | 0 | 32.71 | 30.529 | 187.398 | 7.63 | 176.187 | 2134.85 | 25.98 | 46.269 | 6.35 | 1.348 | 4.628 | 8495 | 1.904 | 97.8 | 77.4 | 1388 | 23.13 | 5521.8 | 2903.2 | 2824.6 | 4168.2 | 1197.6 | 0.67952 | 5.978
2024-12-09 | 17:56 | Data | 0 | 32.278 | 30.523 | 187.489 | 7.64 | 176.233 | 2134.85 | 25.95 | 46.269 | 6.35 | 1.348 | 4.651 | 8463.35 | 2.079 | 97.8 | 77.5 | 1388 | 23.09 | 5501.2 | 2905.6 | 2826.8 | 4168.3 | 1197.6 | 0.68014 | 6
2024-12-09 | 17:56 | Data | 0 | 32.278 | 30.624 | 187.443 | 7.63 | 176.278 | 2139.37 | 25.98 | 45.727 | 6.35 | 1.345 | 4.655 | 8458.83 | 2.066 | 97.9 | 77.6 | 1391 | 22.86 | 5498.2 | 2906.2 | 2832.9 | 4174.8 | 1197.6 | 0.67925 | 5.999
2024-12-09 | 17:56 | Data | 0 | 32.507 | 30.415 | 187.624 | 7.64 | 176.233 | 2130.33 | 25.97 | 46.089 | 6.35 | 1.349 | 4.682 | 8454.3 | 2.079 | 97.8 | 77.6 | 1385 | 23.13 | 5495.3 | 2903 | 2820.5 | 4166.6 | 1197.6 | 0.67947 | 6.031
2024-12-09 | 17:56 | Data | 0 | 32.548 | 30.637 | 187.624 | 7.64 | 176.278 | 2133.95 | 25.98 | 46.269 | 6.35 | 1.348 | 4.68 | 8237.24 | 1.924 | 97.8 | 77.6 | 1388 | 23.13 | 5354.2 | 2905.8 | 2830.6 | 4175 | 1197.6 | 0.67619 | 6.027
2024-12-09 | 17:56 | Data | 0 | 32.561 | 30.421 | 187.624 | 7.64 | 176.323 | 2136.66 | 25.98 | 46.269 | 6.35 | 1.348 | 4.664 | 8246.28 | 1.904 | 97.8 | 77.6 | 1388 | 23.18 | 5360.1 | 2898.2 | 2855.5 | 4187.5 | 1197.6 | 0.67405 | 6.012
2024-12-09 | 17:56 | Data | 0 | 32.345 | 30.367 | 187.534 | 7.64 | 176.368 | 2136.66 | 25.96 | 46.359 | 6.35 | 1.353 | 4.645 | 8223.67 | 1.904 | 97.8 | 77.5 | 1389 | 23.09 | 5345.4 | 2915.8 | 2854.4 | 4193.5 | 1197.6 | 0.67787 | 5.998
2024-12-09 | 17:57 | Data | 0 | 32.494 | 30.536 | 187.489 | 7.64 | 176.278 | 2136.66 | 25.98 | 46.179 | 6.35 | 1.343 | 4.645 | 8232.71 | 2.079 | 97.8 | 77.6 | 1388 | 23.13 | 5351.3 | 2898.2 | 2880.5 | 4199.8 | 1197.6 | 0.67234 | 5.988
2024-12-09 | 17:57 | Data | 0 | 32.467 | 30.637 | 187.579 | 7.63 | 176.278 | 2137.56 | 25.99 | 45.908 | 6.35 | 1.348 | 4.664 | 8458.83 | 2.167 | 97.9 | 77.6 | 1389 | 22.95 | 5498.2 | 2911.7 | 2880.2 | 4208.2 | 1197.6 | 0.67487 | 6.011
2024-12-09 | 17:57 | Data | 0 | 32.906 | 30.752 | 187.624 | 7.63 | 176.233 | 2136.66 | 25.97 | 46.179 | 6.34 | 1.351 | 4.635 | 8445.26 | 2.079 | 97.8 | 77.4 | 1389 | 23.09 | 5489.4 | 2916 | 2887.3 | 4214.4 | 1197.6 | 0.674 | 5.987
2024-12-09 | 17:57 | Data | 0 | 32.494 | 30.745 | 187.579 | 7.63 | 176.187 | 2033.62 | 25.98 | 46.269 | 6.35 | 1.348 | 4.635 | 8458.83 | 1.897 | 97.7 | 77.5 | 1322 | 23.09 | 5498.2 | 2901.5 | 2889.2 | 4207.7 | 1197.6 | 0.67163 | 5.982
2024-12-09 | 17:57 | Data | 0 | 32.386 | 30.536 | 187.715 | 7.63 | 176.278 | 2136.66 | 25.98 | 45.998 | 6.35 | 1.353 | 4.673 | 8454.3 | 2.039 | 97.8 | 77.5 | 1389 | 23 | 5495.3 | 2897.4 | 2847.5 | 4175.4 | 1197.6 | 0.67567 | 6.026
2024-12-09 | 17:57 | Data | 0 | 32.838 | 30.88 | 187.76 | 7.64 | 176.323 | 2136.66 | 25.97 | 45.908 | 6.34 | 1.349 | 4.67 | 8454.3 | 2.052 | 97.8 | 77.6 | 1389 | 23 | 5495.3 | 2889.9 | 2833.3 | 4186.6 | 1197.6 | 0.67536 | 6.019
2024-12-09 | 17:57 | Data | 0 | 32.717 | 30.671 | 187.67 | 7.63 | 176.233 | 2136.66 | 25.97 | 45.998 | 6.34 | 1.348 | 4.669 | 8445.26 | 1.978 | 97.8 | 77.6 | 1389 | 22.95 | 5489.4 | 2895.8 | 2846.2 | 4184.8 | 1197.6 | 0.67736 | 6.017
2024-12-09 | 17:57 | Data | 0 | 32.71 | 30.651 | 187.534 | 7.63 | 176.323 | 2135.76 | 25.98 | 46.089 | 6.35 | 1.339 | 4.659 | 8458.83 | 2.066 | 97.8 | 77.7 | 1389 | 23 | 5498.2 | 2911.6 | 2829 | 4178.6 | 1197.6 | 0.67881 | 5.997
2024-12-09 | 17:57 | Data | 0 | 32.494 | 30.442 | 187.579 | 7.63 | 176.233 | 2136.66 | 25.97 | 45.908 | 6.35 | 1.338 | 4.647 | 8431.69 | 1.971 | 97.8 | 77.7 | 1389 | 23 | 5480.6 | 2913.1 | 2831.7 | 4179 | 1197.6 | 0.68022 | 5.986
2024-12-09 | 17:57 | Data | 0 | 32.71 | 30.671 | 187.67 | 7.63 | 176.278 | 2137.56 | 25.96 | 45.998 | 6.35 | 1.339 | 4.686 | 8467.87 | 2.052 | 97.8 | 77.8 | 1389 | 23 | 5504.1 | 2912.6 | 2832.4 | 4176.6 | 1197.6 | 0.67991 | 6.025
2024-12-09 | 17:57 | Data | 0 | 32.521 | 30.415 | 187.624 | 7.63 | 176.233 | 2133.95 | 25.98 | 46.269 | 6.35 | 1.352 | 4.664 | 8467.87 | 1.884 | 97.8 | 77.5 | 1388 | 23.13 | 5504.1 | 2912.4 | 2857.7 | 4195.8 | 1197.6 | 0.67727 | 6.016
2024-12-09 | 17:57 | Data | 0 | 32.879 | 30.664 | 187.534 | 7.64 | 176.233 | 2133.95 | 25.98 | 46.269 | 6.35 | 1.346 | 4.638 | 8454.3 | 2.248 | 97.8 | 77.5 | 1387 | 23.09 | 5495.3 | 2926.4 | 2858.5 | 4205.1 | 1197.6 | 0.67865 | 5.986
2024-12-09 | 17:57 | Data | 0 | 32.494 | 30.536 | 187.443 | 7.63 | 176.187 | 2132.14 | 25.97 | 46.269 | 6.35 | 1.345 | 4.642 | 8454.3 | 2.073 | 97.8 | 77.5 | 1388 | 23.13 | 5495.3 | 2897.4 | 2880.6 | 4200.5 | 1197.6 | 0.67239 | 5.987
2024-12-09 | 17:57 | Data | 0 | 32.494 | 30.415 | 187.534 | 7.63 | 176.187 | 2134.85 | 25.98 | 46.179 | 6.35 | 1.344 | 4.643 | 8431.69 | 2.079 | 97.8 | 77.6 | 1388 | 23.04 | 5480.6 | 2893.8 | 2873.9 | 4193.9 | 1197.6 | 0.67303 | 5.987
2024-12-09 | 17:57 | Data | 0 | 32.906 | 30.489 | 187.67 | 7.64 | 176.368 | 2133.95 | 25.98 | 46.269 | 6.35 | 1.347 | 4.654 | 8440.74 | 2.343 | 97.8 | 77.6 | 1387 | 23.13 | 5486.5 | 2902.3 | 2883.7 | 4206 | 1197.6 | 0.67171 | 6.001
2024-12-09 | 17:57 | Data | 0 | 32.764 | 30.415 | 187.624 | 7.63 | 176.323 | 2133.95 | 25.98 | 46.179 | 6.35 | 1.352 | 4.672 | 8440.74 | 1.917 | 97.8 | 77.6 | 1387 | 23.09 | 5486.5 | 2903.9 | 2854.6 | 4195.8 | 1197.6 | 0.67323 | 6.024
2024-12-09 | 17:57 | Data | 0 | 32.494 | 30.651 | 187.715 | 7.63 | 176.278 | 2131.24 | 25.97 | 46.269 | 6.35 | 1.344 | 4.675 | 8427.17 | 2.052 | 97.8 | 77.7 | 1385 | 23.09 | 5477.7 | 2885 | 2858.3 | 4180.4 | 1197.7 | 0.6717 | 6.02
2024-12-09 | 17:57 | Data | 0 | 32.487 | 30.415 | 187.398 | 7.63 | 176.233 | 2130.33 | 25.98 | 46.179 | 6.35 | 1.344 | 4.689 | 8458.83 | 2.079 | 97.8 | 77.7 | 1385 | 23.13 | 5498.2 | 2896.9 | 2854.8 | 4187.2 | 1197.7 | 0.67871 | 6.032
2024-12-09 | 17:58 | Data | 0 | 32.453 | 30.367 | 187.534 | 7.64 | 176.233 | 2131.24 | 25.98 | 46.179 | 6.35 | 1.342 | 4.677 | 8454.3 | 1.965 | 97.8 | 77.7 | 1385 | 23.04 | 5495.3 | 2923.4 | 2844.6 | 4192.3 | 1197.7 | 0.67866 | 6.02
2024-12-09 | 17:58 | Data | 0 | 32.973 | 30.664 | 187.67 | 7.63 | 176.368 | 2129.43 | 25.97 | 46.269 | 6.35 | 1.342 | 4.689 | 8051.82 | 2.106 | 97.8 | 77.7 | 1384 | 23.13 | 5233.7 | 2900.2 | 2822.1 | 4162.6 | 1197.7 | 0.67971 | 6.031
2024-12-09 | 17:58 | Data | 0 | 32.501 | 30.529 | 187.624 | 7.64 | 176.187 | 2133.95 | 25.98 | 46.269 | 6.35 | 1.351 | 4.645 | 8662.33 | 1.85 | 97.8 | 77.5 | 1387 | 23.13 | 5630.5 | 2907.5 | 2817.9 | 4167.3 | 1197.7 | 0.68012 | 5.995
2024-12-09 | 17:58 | Data | 0 | 32.865 | 30.806 | 187.715 | 7.63 | 176.413 | 2134.85 | 25.98 | 46.269 | 6.35 | 1.339 | 4.635 | 8621.63 | 2.059 | 97.8 | 77.6 | 1388 | 23.09 | 5604.1 | 2896.6 | 2830.2 | 4166 | 1197.7 | 0.67773 | 5.975
2024-12-09 | 17:58 | Data | 0 | 32.386 | 30.577 | 187.443 | 7.63 | 176.278 | 2134.85 | 25.96 | 46.089 | 6.35 | 1.338 | 4.67 | 8621.63 | 2.046 | 97.8 | 77.7 | 1388 | 23.04 | 5604.1 | 2909.5 | 2821.4 | 4167.2 | 1197.7 | 0.68204 | 6.007
2024-12-09 | 17:58 | Data | 0 | 32.636 | 30.428 | 187.534 | 7.64 | 176.323 | 2131.24 | 25.99 | 46.269 | 6.34 | 1.339 | 4.649 | 8621.63 | 2.093 | 97.8 | 77.6 | 1386 | 23.13 | 5604.1 | 2891 | 2856.3 | 4178.4 | 1197.7 | 0.67451 | 5.988
2024-12-09 | 17:58 | Data | 0 | 32.723 | 30.421 | 187.579 | 7.63 | 176.278 | 2128.52 | 25.98 | 46.269 | 6.34 | 1.341 | 4.645 | 8599.01 | 2.093 | 97.8 | 77.6 | 1383 | 23.09 | 5589.4 | 2893.2 | 2863.3 | 4182.5 | 1197.7 | 0.67439 | 5.987
2024-12-09 | 17:58 | Data | 0 | 32.723 | 30.651 | 187.624 | 7.64 | 176.323 | 2124.91 | 25.98 | 46.179 | 6.35 | 1.348 | 4.659 | 8232.71 | 1.958 | 97.8 | 77.5 | 1381 | 23.09 | 5351.3 | 2906.6 | 2880.2 | 4204.4 | 1197.7 | 0.67484 | 6.008
2024-12-09 | 17:58 | Data | 0 | 32.75 | 30.435 | 187.579 | 7.63 | 176.323 | 2125.81 | 25.97 | 46.179 | 6.34 | 1.358 | 4.676 | 8232.71 | 2.059 | 97.8 | 77.5 | 1382 | 23.09 | 5351.3 | 2890.6 | 2852.7 | 4176 | 1197.7 | 0.67497 | 6.036
2024-12-09 | 17:58 | Data | 0 | 32.609 | 30.415 | 187.624 | 7.64 | 176.323 | 2125.81 | 25.97 | 46.359 | 6.35 | 1.349 | 4.653 | 8255.33 | 2.248 | 97.8 | 77.5 | 1381 | 23.18 | 5366 | 2896.9 | 2850.2 | 4176.1 | 1197.7 | 0.67581 | 6.002
2024-12-09 | 17:58 | Data | 0 | 32.413 | 30.563 | 187.624 | 7.64 | 176.323 | 2125.81 | 25.98 | 46.269 | 6.34 | 1.348 | 4.67 | 8237.24 | 1.796 | 97.8 | 77.6 | 1382 | 23.18 | 5354.2 | 2913.3 | 2858.6 | 4196.4 | 1197.7 | 0.6775 | 6.017
2024-12-09 | 17:58 | Data | 0 | 32.885 | 30.651 | 187.624 | 7.64 | 176.278 | 2124.91 | 25.98 | 46.179 | 6.35 | 1.348 | 4.679 | 8273.41 | 2.113 | 97.8 | 77.6 | 1382 | 23.13 | 5377.7 | 2907.9 | 2827.4 | 4171.3 | 1197.7 | 0.68083 | 6.026
2024-12-09 | 17:58 | Data | 0 | 32.696 | 30.475 | 187.624 | 7.64 | 176.278 | 2125.81 | 25.99 | 46.179 | 6.35 | 1.344 | 4.65 | 8291.5 | 2.248 | 97.8 | 77.6 | 1381 | 23.09 | 5389.5 | 2904.9 | 2824.4 | 4167.8 | 1197.7 | 0.68104 | 5.993
2024-12-09 | 17:58 | Data | 0 | 32.285 | 30.59 | 187.579 | 7.64 | 176.187 | 2127.62 | 25.98 | 46.269 | 6.35 | 1.349 | 4.654 | 8291.5 | 1.843 | 97.8 | 77.5 | 1384 | 23.09 | 5389.5 | 2897.1 | 2824.3 | 4168.8 | 1197.7 | 0.67885 | 6.003
2024-12-09 | 17:58 | Data | 0 | 32.825 | 30.225 | 187.624 | 7.63 | 176.323 | 2128.52 | 25.98 | 46.179 | 6.35 | 1.354 | 4.663 | 8314.11 | 2.295 | 97.8 | 77.5 | 1384 | 23.09 | 5404.2 | 2887.5 | 2835.4 | 4163.7 | 1197.7 | 0.6763 | 6.017
2024-12-09 | 17:58 | Data | 0 | 32.069 | 30.415 | 187.67 | 7.63 | 176.233 | 2127.62 | 25.97 | 46.269 | 6.34 | 1.351 | 4.668 | 8318.64 | 1.938 | 97.8 | 77.6 | 1383 | 23.13 | 5407.1 | 2911.5 | 2873.5 | 4204.3 | 1197.7 | 0.67479 | 6.019
2024-12-09 | 17:58 | Data | 0 | 32.615 | 30.651 | 187.67 | 7.63 | 176.278 | 2128.52 | 25.98 | 46.269 | 6.34 | 1.336 | 4.667 | 8318.64 | 1.87 | 97.8 | 77.8 | 1383 | 23.13 | 5407.1 | 2909.7 | 2882 | 4209.2 | 1197.7 | 0.67472 | 6.004
2024-12-09 | 17:58 | Data | 0 | 32.494 | 30.82 | 187.67 | 7.64 | 176.323 | 2131.24 | 25.96 | 46.179 | 6.35 | 1.351 | 4.659 | 8336.72 | 2.025 | 97.8 | 77.6 | 1385 | 23.13 | 5418.9 | 2895.3 | 2885.7 | 4208.6 | 1197.7 | 0.66945 | 6.007
2024-12-09 | 17:59 | Data | 0 | 32.501 | 30.813 | 187.579 | 7.63 | 176.323 | 2128.52 | 25.98 | 46.269 | 6.35 | 1.353 | 4.689 | 8323.16 | 2.046 | 97.8 | 77.6 | 1384 | 23.13 | 5410.1 | 2900.2 | 2869 | 4196.2 | 1197.7 | 0.67238 | 6.041
2024-12-09 | 17:59 | Data | 0 | 32.804 | 30.536 | 187.67 | 7.63 | 176.278 | 2133.95 | 25.98 | 46.359 | 6.34 | 1.343 | 4.68 | 8363.86 | 2.079 | 97.8 | 77.7 | 1387 | 23.13 | 5436.5 | 2902.7 | 2890 | 4212.2 | 1197.7 | 0.67209 | 6.023
2024-12-09 | 17:59 | Data | 0 | 32.521 | 30.421 | 187.489 | 7.64 | 176.187 | 2133.95 | 25.98 | 46.179 | 6.35 | 1.347 | 4.684 | 8372.9 | 2.073 | 97.8 | 77.7 | 1386 | 23.13 | 5442.4 | 2901.9 | 2880.3 | 4201.6 | 1197.7 | 0.6727 | 6.031
2024-12-09 | 17:59 | Data | 0 | 32.723 | 30.232 | 187.715 | 7.63 | 176.323 | 2137.56 | 25.97 | 45.998 | 6.35 | 1.356 | 4.651 | 8372.9 | 2.052 | 97.8 | 77.4 | 1389 | 23 | 5442.4 | 2906.8 | 2810.6 | 4163.2 | 1197.7 | 0.6818 | 6.007
2024-12-09 | 17:59 | Data | 0 | 32.696 | 30.752 | 187.489 | 7.63 | 176.278 | 2137.56 | 25.97 | 46.089 | 6.35 | 1.345 | 4.632 | 8390.99 | 1.897 | 97.8 | 77.5 | 1389 | 23 | 5454.1 | 2904.5 | 2787.4 | 4142.4 | 1197.7 | 0.68468 | 5.977
2024-12-09 | 17:59 | Data | 0 | 32.271 | 30.59 | 187.489 | 7.63 | 176.187 | 2136.66 | 25.98 | 45.998 | 6.34 | 1.344 | 4.674 | 8400.04 | 2.025 | 97.8 | 77.7 | 1389 | 23 | 5460 | 2911.4 | 2804.8 | 4160.3 | 1197.7 | 0.68561 | 6.018
2024-12-09 | 17:59 | Data | 0 | 33.108 | 30.597 | 187.76 | 7.63 | 176.413 | 2131.24 | 25.98 | 45.908 | 6.35 | 1.354 | 4.686 | 8395.51 | 2.106 | 97.8 | 77.6 | 1386 | 22.91 | 5457.1 | 2888.1 | 2816 | 4146.9 | 1197.7 | 0.67915 | 6.04
2024-12-09 | 17:59 | Data | 0 | 32.703 | 30.536 | 187.624 | 7.63 | 176.278 | 2135.76 | 25.98 | 46.269 | 6.34 | 1.36 | 4.66 | 8409.08 | 2.295 | 97.8 | 77.4 | 1389 | 23.13 | 5465.9 | 2901.1 | 2828.3 | 4170.8 | 1197.7 | 0.68036 | 6.019
2024-12-09 | 17:59 | Data | 0 | 32.764 | 30.631 | 187.534 | 7.63 | 176.323 | 2134.85 | 25.98 | 46.179 | 6.34 | 1.348 | 4.625 | 8400.04 | 1.992 | 97.8 | 77.4 | 1387 | 23.09 | 5460 | 2900.2 | 2870.1 | 4197.7 | 1197.7 | 0.67346 | 5.974
2024-12-09 | 17:59 | Data | 0 | 32.582 | 30.475 | 187.534 | 7.64 | 176.323 | 2137.56 | 25.97 | 46.359 | 6.35 | 1.351 | 4.656 | 8436.21 | 1.985 | 97.8 | 77.5 | 1389 | 23.13 | 5483.5 | 2908.9 | 2868.3 | 4198.5 | 1197.7 | 0.67661 | 6.006
2024-12-09 | 17:59 | Data | 0 | 32.555 | 30.442 | 187.67 | 7.63 | 176.278 | 2135.76 | 25.98 | 46.359 | 6.35 | 1.348 | 4.662 | 8458.83 | 1.971 | 97.8 | 77.5 | 1389 | 23.18 | 5498.2 | 2886.4 | 2861.2 | 4181 | 1197.7 | 0.67199 | 6.008
2024-12-09 | 17:59 | Data | 0 | 32.838 | 30.415 | 187.624 | 7.63 | 176.278 | 2140.27 | 25.97 | 46.179 | 6.35 | 1.347 | 4.651 | 8467.87 | 1.884 | 97.8 | 77.5 | 1391 | 23.09 | 5504.1 | 2912.8 | 2869.2 | 4203.7 | 1197.7 | 0.67546 | 5.998
2024-12-09 | 17:59 | Data | 0 | 32.973 | 30.435 | 187.715 | 7.63 | 176.413 | 2138.47 | 25.98 | 46.179 | 6.35 | 1.347 | 4.639 | 8467.87 | 2.181 | 97.8 | 77.5 | 1390 | 23.13 | 5504.1 | 2904.3 | 2845.4 | 4184.1 | 1197.7 | 0.6768 | 5.986
2024-12-09 | 17:59 | Data | 0 | 32.507 | 30.475 | 187.534 | 7.63 | 176.187 | 2136.66 | 25.98 | 46.269 | 6.35 | 1.355 | 4.656 | 8458.83 | 2.019 | 97.8 | 77.5 | 1389 | 23.18 | 5498.2 | 2885.2 | 2788.8 | 4129.7 | 1197.7 | 0.68192 | 6.01
2024-12-09 | 17:59 | Data | 0 | 32.501 | 30.536 | 187.624 | 7.63 | 176.368 | 2139.37 | 25.98 | 46.269 | 6.35 | 1.349 | 4.672 | 8458.83 | 2.052 | 97.8 | 77.6 | 1391 | 23.18 | 5498.2 | 2905.3 | 2817.9 | 4165.6 | 1197.7 | 0.68013 | 6.022
2024-12-09 | 17:59 | Data | 0 | 32.494 | 30.421 | 187.489 | 7.64 | 176.278 | 2140.27 | 25.98 | 45.998 | 6.34 | 1.34 | 4.663 | 8458.83 | 2.066 | 97.9 | 77.7 | 1391 | 23 | 5498.2 | 2892.8 | 2814.8 | 4154.9 | 1197.7 | 0.67863 | 6.002
2024-12-09 | 17:59 | Data | 0 | 32.696 | 30.597 | 187.534 | 7.64 | 176.278 | 2140.27 | 25.97 | 46.089 | 6.35 | 1.348 | 4.65 | 8458.83 | 2.16 | 97.9 | 77.5 | 1391 | 22.95 | 5498.2 | 2907.5 | 2815.1 | 4162.8 | 1197.7 | 0.68074 | 5.998
2024-12-09 | 18:00 | Data | 0 | 32.534 | 30.421 | 187.67 | 7.63 | 176.368 | 2188.18 | 25.98 | 46.269 | 6.35 | 1.356 | 4.654 | 8440.74 | 2.066 | 97.9 | 77.4 | 1423 | 23.13 | 5486.5 | 2907.7 | 2877.3 | 4206.4 | 1197.8 | 0.67382 | 6.009
2024-12-09 | 18:00 | Data | 0 | 32.717 | 30.475 | 187.624 | 7.64 | 176.368 | 2189.08 | 25.97 | 46.179 | 6.36 | 1.351 | 4.635 | 8445.26 | 1.897 | 97.9 | 77.4 | 1423 | 23.09 | 5489.4 | 2907.6 | 2866.5 | 4193.1 | 1197.8 | 0.67319 | 5.987
2024-12-09 | 18:00 | Data | 0 | 32.649 | 30.415 | 187.534 | 7.64 | 176.278 | 2194.5 | 25.98 | 46.269 | 6.35 | 1.348 | 4.637 | 8445.26 | 1.857 | 97.9 | 77.5 | 1426 | 23.09 | 5489.4 | 2923.4 | 2883.1 | 4206.8 | 1197.8 | 0.67222 | 5.986
2024-12-09 | 18:00 | Data | 0 | 32.777 | 30.435 | 187.67 | 7.64 | 176.413 | 2189.08 | 25.98 | 46.179 | 6.35 | 1.342 | 4.656 | 8440.74 | 1.978 | 97.9 | 77.6 | 1423 | 23.13 | 5486.5 | 2898.8 | 2883.1 | 4206.5 | 1197.8 | 0.67192 | 5.999
2024-12-09 | 18:00 | Data | 0 | 32.609 | 30.651 | 187.67 | 7.64 | 176.233 | 2140.27 | 25.98 | 46.179 | 6.35 | 1.329 | 4.664 | 8472.39 | 2.066 | 97.8 | 77.8 | 1391 | 23.09 | 5507.1 | 2899.8 | 2883.2 | 4207.4 | 1197.8 | 0.67236 | 5.994
2024-12-09 | 18:00 | Data | 0 | 32.94 | 30.455 | 187.67 | 7.64 | 176.278 | 2135.76 | 25.97 | 46.269 | 6.34 | 1.339 | 4.652 | 8485.96 | 2.046 | 97.8 | 77.6 | 1389 | 23.13 | 5515.9 | 2920.1 | 2842.6 | 4189.9 | 1197.8 | 0.68087 | 5.99
2024-12-09 | 18:00 | Data | 0 | 32.696 | 30.651 | 187.624 | 7.64 | 176.368 | 2134.85 | 25.98 | 46.179 | 6.35 | 1.347 | 4.68 | 8485.96 | 2.059 | 97.8 | 77.7 | 1388 | 23.13 | 5515.9 | 2894.8 | 2823.4 | 4166.4 | 1197.8 | 0.67705 | 6.026
2024-12-09 | 18:00 | Data | 0 | 32.386 | 30.705 | 187.624 | 7.63 | 176.323 | 2133.95 | 25.97 | 46.269 | 6.35 | 1.353 | 4.668 | 8485.96 | 1.992 | 97.8 | 77.5 | 1387 | 23.09 | 5515.9 | 2898.2 | 2851.1 | 4180.7 | 1197.8 | 0.67697 | 6.021
2024-12-09 | 18:00 | Data | 0 | 32.494 | 30.428 | 187.624 | 7.63 | 176.323 | 2133.95 | 25.98 | 46.179 | 6.35 | 1.337 | 4.675 | 8467.87 | 2.181 | 97.8 | 77.8 | 1388 | 23.18 | 5504.1 | 2895.3 | 2866.2 | 4194.1 | 1197.8 | 0.67191 | 6.012
2024-12-09 | 18:00 | Data | 0 | 32.494 | 30.651 | 187.624 | 7.63 | 176.278 | 2128.52 | 25.98 | 45.998 | 6.35 | 1.346 | 4.628 | 8472.39 | 2.046 | 97.8 | 77.5 | 1384 | 23.04 | 5507.1 | 2890.8 | 2848.4 | 4176.5 | 1197.8 | 0.67495 | 5.974
2024-12-09 | 18:00 | Data | 0 | 32.717 | 30.442 | 187.624 | 7.63 | 176.323 | 2133.95 | 25.98 | 46.179 | 6.34 | 1.349 | 4.623 | 8472.39 | 2.059 | 97.8 | 77.4 | 1388 | 23.13 | 5507.1 | 2897 | 2896.6 | 4214.2 | 1197.8 | 0.66973 | 5.971
2024-12-09 | 18:00 | Data | 0 | 32.399 | 30.428 | 187.76 | 7.63 | 176.459 | 2132.14 | 25.98 | 46.269 | 6.35 | 1.338 | 4.654 | 8481.44 | 1.85 | 97.8 | 77.7 | 1385 | 23.13 | 5512.9 | 2895 | 2904.4 | 4220.3 | 1197.8 | 0.66776 | 5.99
2024-12-09 | 18:00 | Data | 0 | 32.919 | 30.678 | 187.851 | 7.63 | 176.459 | 2132.14 | 25.98 | 46.269 | 6.35 | 1.347 | 4.674 | 8481.44 | 2.154 | 97.8 | 77.6 | 1387 | 23.13 | 5512.9 | 2890.8 | 2892.7 | 4203.6 | 1197.8 | 0.66992 | 6.021
2024-12-09 | 18:00 | Data | 0 | 32.494 | 30.658 | 187.67 | 7.63 | 176.413 | 2134.85 | 25.98 | 46.179 | 6.35 | 1.344 | 4.671 | 8495 | 2.248 | 97.8 | 77.7 | 1387 | 23.09 | 5521.8 | 2911.4 | 2906.9 | 4225.3 | 1197.8 | 0.67063 | 6.017
2024-12-09 | 18:00 | Data | 0 | 32.278 | 30.415 | 187.624 | 7.64 | 176.368 | 2132.14 | 25.99 | 46.179 | 6.35 | 1.339 | 4.664 | 8481.44 | 1.857 | 97.8 | 77.7 | 1387 | 23.09 | 5512.9 | 2924.3 | 2890.1 | 4225.9 | 1197.8 | 0.6741 | 6.005
2024-12-09 | 18:00 | Data | 0 | 32.609 | 30.637 | 187.715 | 7.63 | 176.323 | 2133.95 | 25.98 | 46.269 | 6.34 | 1.347 | 4.66 | 8485.96 | 2.106 | 97.8 | 77.6 | 1387 | 23.09 | 5515.9 | 2899.5 | 2903.9 | 4217.6 | 1197.8 | 0.66999 | 6.007
2024-12-09 | 18:00 | Data | 0 | 32.811 | 30.698 | 187.67 | 7.63 | 176.323 | 2133.95 | 25.97 | 46.179 | 6.35 | 1.351 | 4.67 | 8644.24 | 2.167 | 97.8 | 77.6 | 1388 | 23.13 | 5618.8 | 2918.8 | 2892.4 | 4218.8 | 1197.8 | 0.67183 | 6.02
2024-12-09 | 18:00 | Data | 0 | 32.953 | 30.543 | 187.624 | 7.63 | 176.459 | 2136.66 | 25.97 | 46.269 | 6.35 | 1.347 | 4.697 | 8662.33 | 2.093 | 97.8 | 77.7 | 1389 | 23.09 | 5630.5 | 2906 | 2880.7 | 4208.4 | 1197.8 | 0.67306 | 6.044
2024-12-09 | 18:01 | Data | 0 | 32.879 | 30.651 | 187.579 | 7.63 | 176.368 | 2134.85 | 25.98 | 46.269 | 6.35 | 1.358 | 4.672 | 8648.76 | 2.262 | 97.8 | 77.5 | 1388 | 23.18 | 5621.7 | 2876.2 | 2840.2 | 4163.1 | 1197.8 | 0.6759 | 6.031
2024-12-09 | 18:01 | Data | 0 | 32.582 | 30.415 | 187.579 | 7.63 | 176.278 | 2133.95 | 25.97 | 46.269 | 6.35 | 1.356 | 4.664 | 8662.33 | 2.113 | 97.8 | 77.5 | 1387 | 23.18 | 5630.5 | 2906.8 | 2828.9 | 4175.3 | 1197.8 | 0.67818 | 6.019
2024-12-09 | 18:01 | Data | 0 | 32.507 | 30.624 | 187.715 | 7.64 | 176.323 | 2134.85 | 25.98 | 46.179 | 6.35 | 1.353 | 4.639 | 8472.39 | 2.012 | 97.8 | 77.4 | 1387 | 23.09 | 5507.1 | 2906.6 | 2827.7 | 4170 | 1197.8 | 0.67954 | 5.992
2024-12-09 | 18:01 | Data | 0 | 32.669 | 30.874 | 187.624 | 7.63 | 176.278 | 2134.85 | 25.97 | 46.179 | 6.36 | 1.357 | 4.656 | 8476.91 | 2.032 | 97.8 | 77.4 | 1388 | 23.13 | 5510 | 2887.1 | 2830.9 | 4163.3 | 1197.8 | 0.6761 | 6.013
2024-12-09 | 18:01 | Data | 0 | 32.386 | 30.415 | 187.67 | 7.63 | 176.323 | 2133.95 | 25.98 | 46.179 | 6.35 | 1.352 | 4.656 | 8467.87 | 2.019 | 97.8 | 77.5 | 1387 | 23.13 | 5504.1 | 2883.8 | 2837.7 | 4163.3 | 1197.8 | 0.67629 | 6.008
2024-12-09 | 18:01 | Data | 0 | 32.737 | 30.475 | 187.67 | 7.63 | 176.278 | 2133.95 | 25.98 | 46.269 | 6.35 | 1.34 | 4.664 | 8467.87 | 2.079 | 97.8 | 77.7 | 1387 | 23.13 | 5504.1 | 2894 | 2869.2 | 4190.4 | 1197.8 | 0.67256 | 6.004
2024-12-09 | 18:01 | Data | 0 | 32.555 | 30.624 | 187.67 | 7.64 | 176.413 | 2133.95 | 25.98 | 46.269 | 6.35 | 1.354 | 4.683 | 8445.26 | 1.971 | 97.8 | 77.6 | 1387 | 23.13 | 5489.4 | 2889.8 | 2874.7 | 4198.2 | 1197.8 | 0.67163 | 6.036
2024-12-09 | 18:01 | Data | 0 | 32.703 | 30.651 | 187.579 | 7.63 | 176.323 | 2137.56 | 25.98 | 46.269 | 6.35 | 1.359 | 4.64 | 8445.26 | 2.066 | 97.8 | 77.3 | 1389 | 23.18 | 5489.4 | 2882.7 | 2883.8 | 4194 | 1197.8 | 0.67247 | 5.999
2024-12-09 | 18:01 | Data | 0 | 32.298 | 30.644 | 187.579 | 7.63 | 176.323 | 2136.66 | 25.98 | 46.269 | 6.34 | 1.357 | 4.674 | 8427.17 | 1.803 | 97.8 | 77.5 | 1389 | 23.13 | 5477.7 | 2904.3 | 2891.2 | 4218 | 1197.8 | 0.67073 | 6.032
2024-12-09 | 18:01 | Data | 0 | 32.825 | 30.543 | 187.67 | 7.63 | 176.323 | 2133.95 | 25.98 | 46.269 | 6.35 | 1.354 | 4.652 | 8440.74 | 2.073 | 97.8 | 77.5 | 1388 | 23.13 | 5486.5 | 2871.2 | 2896.7 | 4199 | 1197.8 | 0.66629 | 6.006
2024-12-09 | 18:01 | Data | 0 | 32.723 | 30.637 | 187.67 | 7.64 | 176.278 | 2134.85 | 25.99 | 46.269 | 6.35 | 1.345 | 4.664 | 8449.78 | 1.951 | 97.8 | 77.6 | 1388 | 23.13 | 5492.4 | 2903.9 | 2873.9 | 4202.5 | 1197.8 | 0.6729 | 6.009
2024-12-09 | 18:01 | Data | 0 | 32.588 | 30.745 | 187.715 | 7.63 | 176.323 | 2135.76 | 25.97 | 46.179 | 6.35 | 1.347 | 4.672 | 8454.3 | 1.965 | 97.8 | 77.6 | 1388 | 23.13 | 5495.3 | 2895.5 | 2891.9 | 4207.5 | 1197.8 | 0.6713 | 6.017
2024-12-09 | 18:01 | Data | 0 | 32.609 | 30.428 | 187.67 | 7.63 | 176.278 | 2134.85 | 25.98 | 46.089 | 6.35 | 1.351 | 4.667 | 8463.35 | 2.066 | 97.8 | 77.5 | 1388 | 23.09 | 5501.2 | 2909.2 | 2875.2 | 4207.4 | 1197.8 | 0.67433 | 6.019
2024-12-09 | 18:01 | Data | 0 | 32.494 | 30.421 | 187.579 | 7.63 | 176.278 | 2130.33 | 25.98 | 46.269 | 6.35 | 1.355 | 4.673 | 8458.83 | 2.066 | 97.8 | 77.5 | 1385 | 23.09 | 5498.2 | 2891.5 | 2869.4 | 4187.8 | 1197.8 | 0.67379 | 6.027
2024-12-09 | 18:01 | Data | 0 | 32.507 | 30.536 | 187.624 | 7.63 | 176.323 | 2132.14 | 25.98 | 46.269 | 6.35 | 1.343 | 4.663 | 8449.78 | 2.079 | 97.8 | 77.6 | 1386 | 23.13 | 5492.4 | 2892.1 | 2867.8 | 4191.3 | 1197.8 | 0.67259 | 6.006
2024-12-09 | 18:01 | Data | 0 | 32.609 | 30.624 | 187.67 | 7.63 | 176.278 | 2139.37 | 25.98 | 46.269 | 6.34 | 1.349 | 4.654 | 8440.74 | 2.12 | 97.8 | 77.5 | 1391 | 23.13 | 5486.5 | 2875 | 2844.6 | 4166.1 | 1197.8 | 0.67277 | 6.004
2024-12-09 | 18:01 | Data | 0 | 32.494 | 30.415 | 187.534 | 7.63 | 176.278 | 2133.95 | 25.98 | 46.269 | 6.35 | 1.337 | 4.683 | 8445.26 | 2.079 | 97.8 | 77.8 | 1387 | 23.13 | 5489.4 | 2897.7 | 2838.8 | 4173.6 | 1197.8 | 0.67629 | 6.018
2024-12-09 | 18:02 | Data | 0 | 32.811 | 30.651 | 187.805 | 7.63 | 176.323 | 2134.85 | 25.97 | 46.179 | 6.35 | 1.348 | 4.656 | 8440.74 | 1.985 | 97.8 | 77.6 | 1388 | 23.09 | 5486.5 | 2901.9 | 2867.3 | 4194.9 | 1197.8 | 0.67407 | 6.003
2024-12-09 | 18:02 | Data | 0 | 32.669 | 30.651 | 187.715 | 7.63 | 176.323 | 2132.14 | 25.98 | 46.269 | 6.35 | 1.355 | 4.656 | 8454.3 | 2.066 | 97.8 | 77.5 | 1386 | 23.13 | 5495.3 | 2903.3 | 2850 | 4182.2 | 1197.8 | 0.67611 | 6.011
2024-12-09 | 18:02 | Data | 0 | 32.723 | 30.982 | 187.67 | 7.63 | 176.323 | 2136.66 | 25.98 | 46.269 | 6.35 | 1.348 | 4.667 | 8485.96 | 2.039 | 97.8 | 77.6 | 1389 | 23.09 | 5515.9 | 2908 | 2880.9 | 4208.1 | 1197.9 | 0.67411 | 6.013
2024-12-09 | 18:02 | Data | 0 | 33.048 | 30.658 | 187.715 | 7.63 | 176.459 | 2136.66 | 25.97 | 46.179 | 6.35 | 1.354 | 4.663 | 8485.96 | 2.005 | 97.8 | 77.5 | 1389 | 23.13 | 5515.9 | 2887.8 | 2895.4 | 4207.6 | 1197.9 | 0.66751 | 6.016
2024-12-09 | 18:02 | Data | 0 | 32.507 | 30.698 | 187.67 | 7.63 | 176.413 | 2136.66 | 25.98 | 46.269 | 6.35 | 1.347 | 4.669 | 8495 | 1.904 | 97.8 | 77.6 | 1389 | 23.13 | 5521.8 | 2897.2 | 2888.5 | 4217.3 | 1197.9 | 0.6726 | 6.017
2024-12-09 | 18:02 | Data | 0 | 32.298 | 30.415 | 187.624 | 7.63 | 176.459 | 2136.66 | 25.97 | 46.269 | 6.35 | 1.348 | 4.681 | 8472.39 | 1.978 | 97.8 | 77.6 | 1389 | 23.13 | 5507.1 | 2891.7 | 2849.3 | 4184.2 | 1197.9 | 0.6757 | 6.027
2024-12-09 | 18:02 | Data | 0 | 32.507 | 30.597 | 187.624 | 7.63 | 176.368 | 2139.37 | 25.98 | 46.269 | 6.34 | 1.344 | 4.657 | 8472.39 | 1.965 | 97.8 | 77.6 | 1391 | 23.09 | 5507.1 | 2900 | 2853.7 | 4180.4 | 1197.9 | 0.67481 | 6.001
2024-12-09 | 18:02 | Data | 0 | 32.548 | 30.475 | 187.534 | 7.63 | 176.323 | 2132.14 | 25.98 | 46.45 | 6.35 | 1.354 | 4.656 | 8472.39 | 1.971 | 97.8 | 77.5 | 1387 | 23.13 | 5507.1 | 2904.3 | 2859.6 | 4184.7 | 1197.9 | 0.67488 | 6.009
2024-12-09 | 18:02 | Data | 0 | 33.048 | 30.563 | 187.624 | 7.63 | 176.368 | 2134.85 | 25.98 | 46.179 | 6.35 | 1.357 | 4.673 | 8490.48 | 2.14 | 97.8 | 77.5 | 1387 | 23.09 | 5518.8 | 2894.6 | 2842.7 | 4188.8 | 1197.9 | 0.67508 | 6.029
2024-12-09 | 18:02 | Data | 0 | 32.494 | 30.624 | 187.624 | 7.63 | 176.278 | 2133.95 | 25.98 | 46.269 | 6.35 | 1.344 | 4.68 | 8472.39 | 1.985 | 97.8 | 77.7 | 1387 | 23.13 | 5507.1 | 2901.2 | 2835.4 | 4175.6 | 1197.9 | 0.67679 | 6.024
2024-12-09 | 18:02 | Data | 0 | 32.507 | 30.651 | 187.624 | 7.63 | 176.413 | 2130.33 | 25.98 | 46.269 | 6.34 | 1.343 | 4.645 | 8467.87 | 1.85 | 97.8 | 77.6 | 1385 | 23.13 | 5504.1 | 2892.4 | 2846.5 | 4177.3 | 1197.9 | 0.67536 | 5.988
2024-12-09 | 18:02 | Data | 0 | 32.568 | 30.428 | 187.76 | 7.63 | 176.413 | 2130.33 | 25.97 | 46.269 | 6.35 | 1.349 | 4.65 | 8467.87 | 2.046 | 97.8 | 77.5 | 1385 | 23.09 | 5504.1 | 2889.9 | 2874.6 | 4196.2 | 1197.9 | 0.67245 | 5.998
2024-12-09 | 18:02 | Data | 0 | 32.609 | 30.651 | 187.805 | 7.63 | 176.413 | 2128.52 | 25.97 | 46.179 | 6.35 | 1.342 | 4.62 | 8467.87 | 2.019 | 97.8 | 77.5 | 1384 | 23.13 | 5504.1 | 2897.9 | 2858.5 | 4186.8 | 1197.9 | 0.67566 | 5.962
2024-12-09 | 18:02 | Data | 0 | 32.858 | 30.651 | 187.624 | 7.64 | 176.323 | 2133.95 | 25.98 | 46.179 | 6.35 | 1.348 | 4.651 | 8476.91 | 2.093 | 97.8 | 77.5 | 1387 | 23.13 | 5510 | 2896.2 | 2890.6 | 4206.5 | 1197.9 | 0.67127 | 5.998
2024-12-09 | 18:02 | Data | 0 | 32.75 | 30.651 | 187.624 | 7.63 | 176.278 | 2132.14 | 25.98 | 46.179 | 6.35 | 1.342 | 4.656 | 8467.87 | 2.073 | 97.8 | 77.6 | 1387 | 23.13 | 5504.1 | 2910.8 | 2895.9 | 4222 | 1197.9 | 0.67296 | 5.998
2024-12-09 | 18:02 | Data | 0 | 32.723 | 30.61 | 187.67 | 7.63 | 176.278 | 2133.95 | 25.96 | 46.269 | 6.35 | 1.347 | 4.643 | 8449.78 | 2.241 | 97.8 | 77.5 | 1386 | 23.09 | 5492.4 | 2901 | 2893.2 | 4211.4 | 1197.9 | 0.67151 | 5.989
2024-12-09 | 18:02 | Data | 0 | 32.494 | 30.637 | 187.624 | 7.63 | 176.323 | 2136.66 | 25.98 | 46.179 | 6.35 | 1.348 | 4.653 | 8458.83 | 2.059 | 97.8 | 77.5 | 1389 | 23.13 | 5498.2 | 2908.5 | 2905.7 | 4229.9 | 1197.9 | 0.66965 | 6.002
2024-12-09 | 18:02 | Data | 0 | 32.521 | 30.651 | 187.715 | 7.63 | 176.413 | 2141.18 | 25.98 | 46.269 | 6.35 | 1.352 | 4.645 | 8467.87 | 2.046 | 97.8 | 77.4 | 1391 | 23.13 | 5504.1 | 2887.7 | 2911.1 | 4218.5 | 1197.9 | 0.6662 | 5.998
2024-12-09 | 18:03 | Data | 0 | 32.723 | 30.651 | 187.624 | 7.63 | 176.368 | 2138.47 | 25.98 | 46.269 | 6.35 | 1.355 | 4.676 | 8463.35 | 2.073 | 97.8 | 77.5 | 1391 | 23.09 | 5501.2 | 2896 | 2910.9 | 4221.2 | 1197.9 | 0.66721 | 6.031
2024-12-09 | 18:03 | Data | 0 | 32.723 | 30.482 | 187.67 | 7.63 | 176.368 | 2140.27 | 25.98 | 46.269 | 6.35 | 1.358 | 4.667 | 8485.96 | 2.066 | 97.8 | 77.5 | 1391 | 23.13 | 5515.9 | 2910.7 | 2875.8 | 4199 | 1197.9 | 0.67002 | 6.026
2024-12-09 | 18:03 | Data | 0 | 32.953 | 30.88 | 187.805 | 7.63 | 176.459 | 2139.37 | 25.97 | 46.179 | 6.35 | 1.353 | 4.667 | 8499.53 | 2.073 | 97.8 | 77.5 | 1391 | 23.09 | 5524.7 | 2895.3 | 2858.6 | 4186 | 1197.9 | 0.67536 | 6.022
2024-12-09 | 18:03 | Data | 0 | 32.825 | 30.664 | 187.624 | 7.63 | 176.368 | 2138.47 | 25.98 | 46.179 | 6.36 | 1.352 | 4.68 | 8499.53 | 2.16 | 97.8 | 77.6 | 1391 | 23.13 | 5524.7 | 2916.6 | 2890.5 | 4218.4 | 1197.9 | 0.67535 | 6.032
2024-12-09 | 18:03 | Data | 0 | 32.669 | 30.82 | 187.67 | 7.63 | 176.323 | 2140.27 | 25.98 | 46.179 | 6.35 | 1.348 | 4.637 | 8490.48 | 1.944 | 97.8 | 77.5 | 1391 | 23.09 | 5518.8 | 2909.6 | 2838.2 | 4179.1 | 1197.9 | 0.67854 | 5.986
2024-12-09 | 18:03 | Data | 0 | 32.933 | 30.664 | 187.76 | 7.63 | 176.323 | 2139.37 | 25.97 | 46.269 | 6.35 | 1.354 | 4.663 | 8481.44 | 2.086 | 97.8 | 77.5 | 1390 | 23.13 | 5512.9 | 2908.5 | 2858.7 | 4194.3 | 1197.9 | 0.67632 | 6.017
2024-12-09 | 18:03 | Data | 0 | 32.723 | 30.651 | 187.715 | 7.63 | 176.368 | 2139.37 | 25.98 | 46.179 | 6.35 | 1.342 | 4.679 | 8490.48 | 2.073 | 97.8 | 77.7 | 1391 | 23.13 | 5518.8 | 2907.4 | 2881.7 | 4212.6 | 1197.9 | 0.67209 | 6.024
2024-12-09 | 18:03 | Data | 0 | 32.393 | 30.421 | 187.579 | 7.63 | 176.413 | 2134.85 | 25.96 | 46.269 | 6.35 | 1.34 | 4.662 | 8467.87 | 2.032 | 97.8 | 77.7 | 1388 | 23.13 | 5504.1 | 2895.5 | 2919.7 | 4231.6 | 1197.9 | 0.66686 | 6.002
2024-12-09 | 18:03 | Data | 0 | 32.399 | 30.651 | 187.76 | 7.63 | 176.413 | 2140.27 | 25.98 | 46.269 | 6.34 | 1.357 | 4.699 | 8467.87 | 2.005 | 97.8 | 77.6 | 1391 | 23.13 | 5504.1 | 2892.2 | 2924.9 | 4229.7 | 1197.9 | 0.66535 | 6.055
2024-12-09 | 18:03 | Data | 0 | 32.44 | 30.732 | 187.67 | 7.63 | 176.368 | 2141.18 | 25.97 | 46.179 | 6.35 | 1.346 | 4.687 | 8485.96 | 1.904 | 97.8 | 77.7 | 1391 | 23.13 | 5515.9 | 2899.6 | 2947.7 | 4254.8 | 1197.9 | 0.66291 | 6.035
2024-12-09 | 18:03 | Data | 0 | 32.717 | 30.651 | 187.715 | 7.63 | 176.278 | 2141.18 | 25.98 | 46.179 | 6.35 | 1.353 | 4.643 | 8454.3 | 2.073 | 97.8 | 77.4 | 1391 | 23.13 | 5495.3 | 2905.5 | 2943 | 4251 | 1197.9 | 0.66616 | 5.996
2024-12-09 | 18:03 | Data | 0 | 32.744 | 30.752 | 187.67 | 7.63 | 176.413 | 2142.99 | 25.98 | 46.179 | 6.35 | 1.342 | 4.631 | 8458.83 | 1.985 | 97.8 | 77.5 | 1392 | 23.09 | 5498.2 | 2915.4 | 2899.3 | 4228.7 | 1197.9 | 0.66858 | 5.973
2024-12-09 | 18:03 | Data | 0 | 32.737 | 30.833 | 187.76 | 7.63 | 176.459 | 2141.18 | 25.96 | 46.269 | 6.35 | 1.341 | 4.654 | 8481.44 | 2.052 | 97.8 | 77.6 | 1391 | 23.13 | 5512.9 | 2897.9 | 2906.8 | 4226.9 | 1197.9 | 0.66744 | 5.995
2024-12-09 | 18:03 | Data | 0 | 32.453 | 30.597 | 187.715 | 7.63 | 176.323 | 2139.37 | 25.98 | 46.179 | 6.34 | 1.354 | 4.669 | 8495 | 2.066 | 97.8 | 77.5 | 1391 | 23.13 | 5521.8 | 2886.2 | 2860.8 | 4184.7 | 1197.9 | 0.67336 | 6.024
2024-12-09 | 18:03 | Data | 0 | 32.723 | 30.651 | 187.67 | 7.63 | 176.368 | 2139.37 | 25.97 | 46.359 | 6.35 | 1.352 | 4.676 | 8499.53 | 2.073 | 97.8 | 77.6 | 1390 | 23.13 | 5524.7 | 2895.4 | 2860.5 | 4187.8 | 1197.9 | 0.67417 | 6.029
2024-12-09 | 18:03 | Data | 0 | 32.696 | 30.766 | 187.67 | 7.63 | 176.413 | 2144.79 | 25.98 | 46.179 | 6.35 | 1.357 | 4.666 | 8499.53 | 2.268 | 97.8 | 77.5 | 1394 | 23.13 | 5524.7 | 2889.9 | 2868.1 | 4195.2 | 1197.9 | 0.6708 | 6.023
2024-12-09 | 18:03 | Data | 0 | 32.494 | 30.536 | 187.624 | 7.63 | 176.233 | 2139.37 | 25.98 | 46.179 | 6.35 | 1.359 | 4.664 | 8526.66 | 1.958 | 97.8 | 77.4 | 1391 | 23.04 | 5542.3 | 2909.9 | 2880.9 | 4215 | 1197.9 | 0.67442 | 6.023
2024-12-09 | 18:03 | Data | 0 | 32.723 | 30.651 | 187.67 | 7.63 | 176.413 | 2139.37 | 25.98 | 46.269 | 6.35 | 1.354 | 4.672 | 8540.22 | 2.046 | 97.8 | 77.5 | 1391 | 23.09 | 5551.1 | 2920 | 2903.6 | 4238.4 | 1197.9 | 0.6726 | 6.026
2024-12-09 | 18:04 | Data | 0 | 32.696 | 30.651 | 187.715 | 7.63 | 176.413 | 2139.37 | 25.98 | 46.359 | 6.35 | 1.349 | 4.681 | 8522.14 | 2.073 | 97.8 | 77.6 | 1390 | 23.13 | 5539.4 | 2910.1 | 2907.2 | 4229.3 | 1197.9 | 0.67007 | 6.028
2024-12-09 | 18:04 | Data | 0 | 32.919 | 30.651 | 187.67 | 7.63 | 176.368 | 2140.27 | 25.97 | 46.54 | 6.34 | 1.351 | 4.684 | 8513.09 | 2.12 | 97.8 | 77.6 | 1391 | 23.27 | 5533.5 | 2913.9 | 2884 | 4218 | 1197.9 | 0.67361 | 6.036
2024-12-09 | 18:04 | Data | 0 | 32.723 | 30.428 | 187.624 | 7.63 | 176.368 | 2140.27 | 25.97 | 46.54 | 6.35 | 1.343 | 4.664 | 8495 | 2.106 | 97.8 | 77.6 | 1391 | 23.22 | 5521.8 | 2898.4 | 2881.6 | 4205.3 | 1198 | 0.67175 | 6.008
2024-12-09 | 18:04 | Data | 0 | 32.71 | 30.482 | 187.76 | 7.63 | 176.413 | 2140.27 | 25.99 | 46.45 | 6.34 | 1.335 | 4.668 | 8472.39 | 2.241 | 97.8 | 77.8 | 1391 | 23.22 | 5507.1 | 2921.5 | 2876.2 | 4217.8 | 1198 | 0.67617 | 6.002
2024-12-09 | 18:04 | Data | 0 | 32.94 | 30.88 | 187.76 | 7.63 | 176.413 | 2138.47 | 25.99 | 46.54 | 6.35 | 1.349 | 4.671 | 8467.87 | 2.154 | 97.8 | 77.6 | 1390 | 23.27 | 5504.1 | 2909.6 | 2875.7 | 4202.1 | 1198 | 0.67443 | 6.02
2024-12-09 | 18:04 | Data | 0 | 32.865 | 30.658 | 187.715 | 7.63 | 176.459 | 2139.37 | 25.98 | 46.359 | 6.35 | 1.343 | 4.681 | 8472.39 | 2.106 | 97.8 | 77.7 | 1391 | 23.22 | 5507.1 | 2915.8 | 2873.8 | 4210 | 1198 | 0.67544 | 6.023
2024-12-09 | 18:04 | Data | 0 | 32.501 | 30.651 | 187.76 | 7.63 | 176.323 | 2140.27 | 25.97 | 46.54 | 6.35 | 1.349 | 4.687 | 8476.91 | 1.958 | 97.8 | 77.6 | 1391 | 23.27 | 5510 | 2898 | 2876.1 | 4201.3 | 1198 | 0.67358 | 6.036
2024-12-09 | 18:04 | Data | 0 | 32.501 | 30.536 | 187.715 | 7.64 | 176.459 | 2140.27 | 25.98 | 46.45 | 6.35 | 1.352 | 4.677 | 8481.44 | 1.958 | 97.8 | 77.6 | 1391 | 23.22 | 5512.9 | 2889.9 | 2864.5 | 4188.9 | 1198 | 0.67294 | 6.03
2024-12-09 | 18:04 | Data | 0 | 32.521 | 30.624 | 187.579 | 7.63 | 176.323 | 2142.08 | 25.96 | 46.721 | 6.34 | 1.358 | 4.656 | 8485.96 | 1.958 | 97.8 | 77.4 | 1392 | 23.32 | 5515.9 | 2894.9 | 2873.1 | 4200.5 | 1198 | 0.67201 | 6.013
2024-12-09 | 18:04 | Data | 0 | 32.953 | 30.509 | 187.76 | 7.63 | 176.459 | 2141.18 | 25.98 | 46.179 | 6.35 | 1.36 | 4.673 | 8481.44 | 1.931 | 97.8 | 77.5 | 1392 | 23.13 | 5512.9 | 2902 | 2870.1 | 4204.2 | 1198 | 0.67331 | 6.033
2024-12-09 | 18:04 | Data | 0 | 32.69 | 30.536 | 187.67 | 7.63 | 176.413 | 2139.37 | 25.98 | 46.45 | 6.35 | 1.358 | 4.675 | 8476.91 | 2.106 | 97.8 | 77.5 | 1391 | 23.22 | 5510 | 2893.4 | 2899.3 | 4215.3 | 1198 | 0.67044 | 6.033
2024-12-09 | 18:04 | Data | 0 | 32.514 | 30.637 | 187.67 | 7.63 | 176.323 | 2142.08 | 25.98 | 46.54 | 6.35 | 1.351 | 4.686 | 8485.96 | 1.965 | 97.8 | 77.6 | 1392 | 23.22 | 5515.9 | 2904.8 | 2869.6 | 4216.3 | 1198 | 0.67479 | 6.04
2024-12-09 | 18:04 | Data | 0 | 33.034 | 30.975 | 187.896 | 7.63 | 176.639 | 2138.47 | 25.98 | 46.54 | 6.35 | 1.348 | 4.663 | 8485.96 | 2.066 | 97.8 | 77.6 | 1390 | 23.32 | 5515.9 | 2910.5 | 2897.1 | 4225.1 | 1198 | 0.67113 | 6.009
2024-12-09 | 18:04 | Data | 0 | 32.723 | 30.766 | 187.715 | 7.63 | 176.368 | 2142.08 | 25.98 | 46.54 | 6.35 | 1.338 | 4.658 | 8485.96 | 2.187 | 97.8 | 77.7 | 1393 | 23.27 | 5515.9 | 2912.5 | 2872.6 | 4205.6 | 1198 | 0.67381 | 5.996
2024-12-09 | 18:04 | Data | 0 | 32.906 | 30.691 | 187.851 | 7.63 | 176.549 | 2137.56 | 25.98 | 46.54 | 6.34 | 1.345 | 4.651 | 8495 | 2.14 | 97.8 | 77.6 | 1389 | 23.22 | 5521.8 | 2908.7 | 2862 | 4199.8 | 1198 | 0.67486 | 5.997
2024-12-09 | 18:04 | Data | 0 | 32.933 | 30.705 | 187.67 | 7.63 | 176.368 | 2145.7 | 25.98 | 46.45 | 6.35 | 1.348 | 4.674 | 8485.96 | 2.073 | 97.8 | 77.6 | 1394 | 23.22 | 5515.9 | 2908.2 | 2857.9 | 4186.9 | 1198 | 0.67542 | 6.022
2024-12-09 | 18:04 | Data | 0 | 32.696 | 30.651 | 187.715 | 7.63 | 176.549 | 2143.89 | 25.99 | 46.45 | 6.36 | 1.353 | 4.664 | 8495 | 2.059 | 97.8 | 77.5 | 1394 | 23.22 | 5521.8 | 2910.9 | 2859.5 | 4200 | 1198 | 0.67608 | 6.017
2024-12-09 | 18:04 | Data | 0 | 32.946 | 30.88 | 187.76 | 7.63 | 176.368 | 2144.79 | 25.98 | 46.45 | 6.35 | 1.357 | 4.673 | 8490.48 | 2.073 | 97.8 | 77.5 | 1394 | 23.32 | 5518.8 | 2919.9 | 2861.2 | 4201.7 | 1198 | 0.67805 | 6.03
2024-12-09 | 18:05 | Data | 0 | 32.447 | 30.536 | 187.624 | 7.63 | 176.368 | 2145.7 | 25.97 | 46.45 | 6.35 | 1.354 | 4.664 | 8481.44 | 2.248 | 97.8 | 77.5 | 1394 | 23.22 | 5512.9 | 2907.2 | 2862.6 | 4195.7 | 1198 | 0.67513 | 6.017
2024-12-09 | 18:05 | Data | 0 | 32.838 | 30.651 | 187.76 | 7.63 | 176.459 | 2142.08 | 25.98 | 46.179 | 6.34 | 1.347 | 4.663 | 8476.91 | 2.079 | 97.8 | 77.6 | 1392 | 23.13 | 5510 | 2913.7 | 2876.9 | 4211.7 | 1198 | 0.675 | 6.011
2024-12-09 | 18:05 | Data | 0 | 32.899 | 30.705 | 187.76 | 7.63 | 176.459 | 2142.99 | 25.98 | 46.359 | 6.35 | 1.345 | 4.674 | 8481.44 | 2.066 | 97.8 | 77.7 | 1392 | 23.22 | 5512.9 | 2913.9 | 2900.9 | 4231.7 | 1198 | 0.67049 | 6.019
2024-12-09 | 18:05 | Data | 0 | 32.528 | 30.651 | 187.76 | 7.63 | 176.459 | 2141.18 | 25.98 | 46.179 | 6.35 | 1.355 | 4.671 | 8481.44 | 1.857 | 97.8 | 77.5 | 1392 | 23.13 | 5512.9 | 2904.9 | 2896.6 | 4217 | 1198 | 0.67235 | 6.026
2024-12-09 | 18:05 | Data | 0 | 32.723 | 30.88 | 187.851 | 7.63 | 176.459 | 2142.08 | 25.98 | 46.359 | 6.35 | 1.352 | 4.655 | 8472.39 | 2.059 | 97.8 | 77.5 | 1392 | 23.09 | 5507.1 | 2912.6 | 2905.3 | 4232.8 | 1198 | 0.67106 | 6.006
2024-12-09 | 18:05 | Data | 0 | 32.615 | 30.651 | 187.76 | 7.63 | 176.413 | 2142.08 | 25.98 | 46.45 | 6.35 | 1.341 | 4.635 | 8467.87 | 2.046 | 97.8 | 77.6 | 1392 | 23.22 | 5504.1 | 2906.9 | 2882.3 | 4212.2 | 1198 | 0.67348 | 5.978
2024-12-09 | 18:05 | Data | 0 | 33.027 | 30.894 | 187.76 | 7.63 | 176.413 | 2137.56 | 25.98 | 46.359 | 6.35 | 1.343 | 4.663 | 8906.53 | 2.127 | 97.8 | 77.6 | 1389 | 23.13 | 5789.2 | 2887.8 | 2877.4 | 4192.8 | 1198 | 0.67101 | 6.006
2024-12-09 | 18:05 | Data | 0 | 32.75 | 30.61 | 187.805 | 7.63 | 176.413 | 2139.37 | 25.97 | 46.269 | 6.35 | 1.344 | 4.665 | 8472.39 | 1.992 | 97.8 | 77.6 | 1391 | 23.13 | 5507.1 | 2900.7 | 2872.4 | 4200.3 | 1198 | 0.67404 | 6.01
2024-12-09 | 18:05 | Data | 0 | 33.149 | 31.096 | 187.851 | 7.63 | 176.459 | 2137.56 | 25.98 | 46.359 | 6.35 | 1.345 | 4.654 | 8467.87 | 1.978 | 97.8 | 77.6 | 1389 | 23.13 | 5504.1 | 2898.1 | 2850.9 | 4190.9 | 1198 | 0.67687 | 5.999
2024-12-09 | 18:05 | Data | 0 | 32.94 | 30.705 | 187.851 | 7.63 | 176.459 | 2135.76 | 25.98 | 46.269 | 6.35 | 1.342 | 4.629 | 8454.3 | 2.073 | 97.8 | 77.5 | 1389 | 23.09 | 5495.3 | 2916.7 | 2841.8 | 4202 | 1198 | 0.68307 | 5.972
2024-12-09 | 18:05 | Data | 0 | 32.892 | 30.968 | 187.851 | 7.63 | 176.459 | 2135.76 | 25.98 | 46.269 | 6.35 | 1.356 | 4.653 | 8440.74 | 1.917 | 97.8 | 77.4 | 1388 | 23.09 | 5486.5 | 1824.4 | 2271 | 2914.6 | 1198 | 0.62322 | 6.007
2024-12-09 | 18:05 | Data | 0 | 32.94 | 30.712 | 187.941 | 7.63 | 176.459 | 2136.66 | 25.98 | 46.269 | 6.35 | 1.346 | 4.673 | 8440.74 | 2.005 | 97.8 | 77.6 | 1389 | 23.13 | 5486.5 | 1824.9 | 2279.1 | 2931.8 | 1198 | 0.62114 | 6.019
2024-12-09 | 18:05 | Data | 0 | 32.494 | 30.644 | 187.76 | 7.63 | 176.323 | 2135.76 | 25.98 | 46.359 | 6.35 | 1.337 | 4.664 | 8454.3 | 2.093 | 97.8 | 77.7 | 1389 | 23.09 | 5495.3 | 1831.4 | 2279.2 | 2935.6 | 1198 | 0.62266 | 6.001
2024-12-09 | 18:05 | Data | 0 | 32.953 | 30.907 | 187.896 | 7.63 | 176.549 | 2039.05 | 25.97 | 45.998 | 6.35 | 1.342 | 4.624 | 8906.53 | 1.971 | 97.7 | 77.5 | 1325 | 23 | 5789.2 | 1832.4 | 2286.8 | 2940.8 | 1198 | 0.61983 | 5.966
2024-12-09 | 18:05 | Data | 0 | 32.892 | 30.894 | 187.805 | 7.63 | 176.549 | 2142.99 | 25.97 | 46.179 | 6.35 | 1.353 | 4.637 | 8472.39 | 1.944 | 97.8 | 77.4 | 1392 | 23.09 | 5507.1 | 1821.2 | 2300.9 | 2946.9 | 1198 | 0.61595 | 5.992
2024-12-09 | 18:05 | Data | 0 | 32.804 | 30.563 | 187.805 | 7.63 | 176.549 | 2142.08 | 25.98 | 46.269 | 6.34 | 1.334 | 4.687 | 8458.83 | 1.951 | 97.8 | 77.8 | 1392 | 23.13 | 5498.2 | 1813.9 | 2302.1 | 2942.2 | 1198 | 0.61365 | 6.021
2024-12-09 | 18:05 | Data | 0 | 32.453 | 30.428 | 187.579 | 7.63 | 176.278 | 2142.08 | 25.96 | 46.089 | 6.35 | 1.341 | 4.702 | 8481.44 | 2.127 | 97.8 | 77.8 | 1392 | 23.04 | 5512.9 | 1804.3 | 2286.3 | 2924.4 | 1198 | 0.61412 | 6.042
2024-12-09 | 18:06 | Data | 0 | 32.501 | 30.428 | 187.624 | 7.63 | 176.368 | 2142.08 | 25.97 | 46.269 | 6.35 | 1.357 | 4.687 | 8481.44 | 2.066 | 97.8 | 77.6 | 1392 | 23.09 | 5512.9 | 1819.7 | 2320 | 2960.6 | 1198 | 0.61216 | 6.044
2024-12-09 | 18:06 | Data | 0 | 33.081 | 30.988 | 187.896 | 7.63 | 176.549 | 2144.79 | 25.97 | 46.269 | 6.35 | 1.349 | 4.638 | 8472.39 | 2.181 | 97.8 | 77.5 | 1394 | 23.13 | 5507.1 | 1817.1 | 2298.5 | 2941 | 1198 | 0.61484 | 5.988
2024-12-09 | 18:06 | Data | 0 | 32.669 | 30.766 | 187.76 | 7.64 | 176.413 | 2142.08 | 25.97 | 46.269 | 6.35 | 1.345 | 4.655 | 8467.87 | 2.181 | 97.8 | 77.6 | 1393 | 23.09 | 5504.1 | 1812.8 | 2281 | 2924.8 | 1198 | 0.61706 | 6
2024-12-09 | 18:06 | Data | 0 | 32.332 | 30.415 | 187.534 | 7.63 | 176.368 | 2141.18 | 25.97 | 46.269 | 6.35 | 1.355 | 4.673 | 8463.35 | 1.857 | 97.8 | 77.5 | 1392 | 23.09 | 5501.2 | 1823 | 2278.8 | 2925.5 | 1198 | 0.61831 | 6.028
2024-12-09 | 18:06 | Data | 0 | 32.669 | 30.442 | 187.67 | 7.63 | 176.368 | 2142.08 | 25.97 | 46.269 | 6.35 | 1.352 | 4.665 | 8467.87 | 2.241 | 97.8 | 77.5 | 1392 | 23.09 | 5504.1 | 1814.8 | 2259.7 | 2910 | 1198 | 0.62144 | 6.018
2024-12-09 | 18:06 | Data | 0 | 32.75 | 30.651 | 187.624 | 7.63 | 176.323 | 2139.37 | 25.96 | 46.359 | 6.35 | 1.344 | 4.631 | 8481.44 | 2.073 | 97.8 | 77.5 | 1391 | 23.09 | 5512.9 | 1800.6 | 2213.6 | 2864.6 | 1198 | 0.62669 | 5.977
2024-12-09 | 18:06 | Data | 0 | 32.669 | 30.968 | 187.67 | 7.63 | 176.413 | 2139.37 | 25.96 | 46.179 | 6.35 | 1.346 | 4.635 | 8481.44 | 1.971 | 97.8 | 77.5 | 1391 | 23.09 | 5512.9 | 1819.2 | 2206.8 | 2871.9 | 1198 | 0.6306 | 5.981
2024-12-09 | 18:06 | Data | 0 | 32.94 | 30.705 | 187.579 | 7.63 | 176.368 | 2144.79 | 25.96 | 46.179 | 6.35 | 1.346 | 4.639 | 8454.3 | 2.066 | 97.8 | 77.5 | 1394 | 23.13 | 5495.3 | 1811.1 | 2214.2 | 2872.5 | 1198 | 0.62786 | 5.984
2024-12-09 | 18:06 | Data | 0 | 32.501 | 30.637 | 187.624 | 7.63 | 176.368 | 2136.66 | 25.96 | 46.269 | 6.35 | 1.357 | 4.654 | 8458.83 | 1.897 | 97.8 | 77.4 | 1388 | 23.13 | 5498.2 | 1819.8 | 2241.5 | 2897.2 | 1198 | 0.62621 | 6.01
2024-12-09 | 18:06 | Data | 0 | 33.169 | 30.766 | 187.896 | 7.63 | 176.549 | 2136.66 | 25.96 | 46.179 | 6.35 | 1.348 | 4.686 | 8458.83 | 1.971 | 97.8 | 77.6 | 1389 | 23.09 | 5498.2 | 1805 | 2271.4 | 2912.6 | 1198 | 0.61764 | 6.032
2024-12-09 | 18:06 | Data | 0 | 32.541 | 30.421 | 187.67 | 7.63 | 176.368 | 2136.66 | 25.96 | 46.269 | 6.35 | 1.341 | 4.666 | 8431.69 | 2.187 | 97.8 | 77.7 | 1389 | 23.09 | 5480.6 | 1796.1 | 2273.3 | 2909.4 | 1198.1 | 0.61561 | 6.007
2024-12-09 | 18:06 | Data | 0 | 32.663 | 30.813 | 187.715 | 7.63 | 176.323 | 2136.66 | 25.97 | 46.179 | 6.34 | 1.351 | 4.68 | 8092.52 | 2.086 | 97.8 | 77.6 | 1389 | 23.09 | 5260.1 | 1821.5 | 2281.6 | 2926.5 | 1198.1 | 0.62008 | 6.031
2024-12-09 | 18:06 | Data | 0 | 32.919 | 30.928 | 187.76 | 7.63 | 176.459 | 2135.76 | 25.96 | 46.269 | 6.35 | 1.356 | 4.663 | 8431.69 | 2.019 | 97.8 | 77.5 | 1389 | 23.13 | 5480.6 | 1828.4 | 2261.8 | 2920 | 1198.1 | 0.62305 | 6.018
2024-12-09 | 18:06 | Data | 0 | 32.501 | 30.536 | 187.805 | 7.63 | 176.323 | 2135.76 | 25.96 | 46.359 | 6.36 | 1.355 | 4.645 | 8431.69 | 1.843 | 97.8 | 77.4 | 1388 | 23.09 | 5480.6 | 1821.9 | 2228.6 | 2889.5 | 1198.1 | 0.62833 | 5.999
2024-12-09 | 18:06 | Data | 0 | 32.75 | 30.435 | 187.67 | 7.63 | 176.368 | 2133.95 | 25.95 | 46.269 | 6.35 | 1.352 | 4.658 | 8458.83 | 2.12 | 97.8 | 77.5 | 1388 | 23.13 | 5498.2 | 1807.9 | 2205 | 2863.2 | 1198.1 | 0.62893 | 6.008
2024-12-09 | 18:06 | Data | 0 | 32.838 | 30.543 | 187.579 | 7.63 | 176.413 | 2132.14 | 25.97 | 45.727 | 6.35 | 1.353 | 4.667 | 8445.26 | 2.079 | 97.9 | 77.5 | 1387 | 22.86 | 5489.4 | 1823.3 | 2207.6 | 2875 | 1198.1 | 0.63199 | 6.019
2024-12-09 | 18:06 | Data | 0 | 32.933 | 30.678 | 187.67 | 7.63 | 176.413 | 2134.85 | 25.96 | 46.179 | 6.35 | 1.355 | 4.672 | 8485.96 | 2.187 | 97.8 | 77.5 | 1387 | 23.09 | 5515.9 | 1830.7 | 2205.1 | 2878.1 | 1198.1 | 0.63336 | 6.026
2024-12-09 | 18:06 | Data | 0 | 32.777 | 30.651 | 187.76 | 7.63 | 176.459 | 2133.95 | 25.96 | 46.179 | 6.35 | 1.351 | 4.686 | 8495 | 1.971 | 97.8 | 77.6 | 1388 | 23.18 | 5521.8 | 1832 | 2228 | 2897.4 | 1198.1 | 0.63013 | 6.039
2024-12-09 | 18:07 | Data | 0 | 32.946 | 30.874 | 187.76 | 7.63 | 176.368 | 2134.85 | 25.96 | 46.269 | 6.35 | 1.356 | 4.649 | 8481.44 | 1.87 | 97.8 | 77.4 | 1388 | 23.13 | 5512.9 | 1815.5 | 2222.7 | 2893.6 | 1198.1 | 0.63145 | 6.005
2024-12-09 | 18:07 | Data | 0 | 32.494 | 30.637 | 187.67 | 7.63 | 176.278 | 2134.85 | 25.95 | 46.179 | 6.35 | 1.354 | 4.647 | 8481.44 | 2.046 | 97.8 | 77.4 | 1387 | 23.13 | 5512.9 | 1810.7 | 2224.8 | 2880.6 | 1198.1 | 0.62619 | 6.001
2024-12-09 | 18:07 | Data | 0 | 32.94 | 31.049 | 187.851 | 7.63 | 176.594 | 2134.85 | 25.97 | 46.179 | 6.35 | 1.344 | 4.638 | 8467.87 | 2.086 | 97.8 | 77.5 | 1388 | 23.13 | 5504.1 | 1818.5 | 2229.7 | 2890.2 | 1198.1 | 0.6272 | 5.979
2024-12-09 | 18:07 | Data | 0 | 32.723 | 30.442 | 187.579 | 7.63 | 176.323 | 2133.95 | 25.96 | 46.269 | 6.35 | 1.348 | 4.685 | 8481.44 | 2.073 | 97.8 | 77.7 | 1387 | 23.09 | 5512.9 | 1800.4 | 2245.4 | 2890.2 | 1198.1 | 0.62016 | 6.033
2024-12-09 | 18:07 | Data | 0 | 32.494 | 30.415 | 187.67 | 7.64 | 176.368 | 2133.95 | 25.96 | 46.269 | 6.35 | 1.335 | 4.654 | 8481.44 | 2.079 | 97.8 | 77.7 | 1387 | 23.13 | 5512.9 | 1816.8 | 2250.9 | 2905.7 | 1198.1 | 0.62283 | 5.988
2024-12-09 | 18:07 | Data | 0 | 32.831 | 30.664 | 187.715 | 7.63 | 176.323 | 2136.66 | 25.94 | 46.269 | 6.34 | 1.358 | 4.654 | 8472.39 | 1.904 | 97.8 | 77.4 | 1389 | 23.13 | 5507.1 | 1811.4 | 2258.1 | 2908.1 | 1198.1 | 0.61983 | 6.012
2024-12-09 | 18:07 | Data | 0 | 32.332 | 30.536 | 187.805 | 7.63 | 176.368 | 2137.56 | 25.94 | 46.179 | 6.34 | 1.345 | 4.67 | 8481.44 | 1.971 | 97.8 | 77.6 | 1389 | 23.09 | 5512.9 | 1813 | 2259 | 2909.9 | 1198.1 | 0.62012 | 6.016
2024-12-09 | 18:07 | Data | 0 | 32.494 | 30.529 | 187.715 | 7.63 | 176.459 | 2137.56 | 25.96 | 46.179 | 6.35 | 1.357 | 4.669 | 8472.39 | 1.965 | 97.8 | 77.5 | 1389 | 23.13 | 5507.1 | 1801.4 | 2229.5 | 2877.6 | 1198.1 | 0.62331 | 6.025
2024-12-09 | 18:07 | Data | 0 | 33.081 | 30.968 | 187.624 | 7.63 | 176.368 | 2136.66 | 25.96 | 46.269 | 6.34 | 1.358 | 4.647 | 8476.91 | 2.073 | 97.8 | 77.4 | 1389 | 23.09 | 5510 | 1807.5 | 2234 | 2885.1 | 1198.1 | 0.6242 | 6.006
2024-12-09 | 18:07 | Data | 0 | 32.501 | 30.651 | 187.67 | 7.63 | 176.323 | 2136.66 | 25.94 | 46.359 | 6.35 | 1.342 | 4.637 | 8458.83 | 1.85 | 97.8 | 77.6 | 1388 | 23.13 | 5498.2 | 1808.6 | 2222.4 | 2876.5 | 1198.1 | 0.6261 | 5.979
2024-12-09 | 18:07 | Data | 0 | 32.818 | 30.448 | 187.715 | 7.63 | 176.368 | 2132.14 | 25.96 | 45.908 | 6.35 | 1.346 | 4.656 | 8440.74 | 2.154 | 97.8 | 77.6 | 1386 | 23 | 5486.5 | 1819.2 | 2254.8 | 2907 | 1198.1 | 0.62337 | 6.002
2024-12-09 | 18:07 | Data | 0 | 32.642 | 30.644 | 187.624 | 7.63 | 176.323 | 2140.27 | 25.95 | 46.179 | 6.35 | 1.349 | 4.645 | 8454.3 | 2.046 | 97.8 | 77.5 | 1391 | 23.13 | 5495.3 | 1816 | 2248.2 | 2901.1 | 1198.1 | 0.62411 | 5.992
2024-12-09 | 18:07 | Data | 0 | 32.494 | 30.624 | 187.579 | 7.63 | 176.323 | 2141.18 | 25.96 | 46.269 | 6.35 | 1.348 | 4.637 | 8458.83 | 1.87 | 97.8 | 77.5 | 1392 | 23.13 | 5498.2 | 1829.6 | 2245.8 | 2908.8 | 1198.1 | 0.62384 | 5.986
2024-12-09 | 18:07 | Data | 0 | 32.771 | 30.327 | 187.715 | 7.63 | 176.368 | 2143.89 | 25.95 | 46.269 | 6.34 | 1.348 | 4.664 | 8481.44 | 2.032 | 97.8 | 77.6 | 1393 | 23.13 | 5512.9 | 1815.7 | 2242.2 | 2897.5 | 1198.1 | 0.62366 | 6.01
2024-12-09 | 18:07 | Data | 0 | 32.393 | 30.408 | 187.715 | 7.64 | 176.413 | 2136.66 | 25.96 | 46.269 | 6.35 | 1.349 | 4.673 | 8472.39 | 1.904 | 97.8 | 77.6 | 1389 | 23.13 | 5507.1 | 1827.7 | 2237.9 | 2899.5 | 1198.1 | 0.62731 | 6.022
2024-12-09 | 18:07 | Data | 0 | 32.501 | 30.59 | 187.579 | 7.63 | 176.278 | 2143.89 | 25.96 | 46.179 | 6.35 | 1.343 | 4.685 | 8481.44 | 1.958 | 97.8 | 77.7 | 1394 | 23.13 | 5512.9 | 1814.1 | 2208.8 | 2869.4 | 1198.1 | 0.63016 | 6.028
2024-12-09 | 18:07 | Data | 0 | 32.75 | 30.766 | 187.715 | 7.63 | 176.459 | 2146.6 | 25.96 | 46.269 | 6.35 | 1.355 | 4.683 | 8481.44 | 1.965 | 97.8 | 77.6 | 1396 | 23.13 | 5512.9 | 1811.6 | 2202.1 | 2862.7 | 1198.1 | 0.63068 | 6.038
2024-12-09 | 18:07 | Data | 0 | 32.521 | 30.469 | 187.579 | 7.64 | 176.323 | 2147.51 | 25.96 | 46.269 | 6.34 | 1.357 | 4.664 | 8485.96 | 2.025 | 97.8 | 77.5 | 1395 | 23.09 | 5515.9 | 1813.5 | 2187.5 | 2853.9 | 1198.1 | 0.63306 | 6.021
2024-12-09 | 18:08 | Data | 0 | 32.494 | 30.59 | 187.624 | 7.63 | 176.323 | 2148.41 | 25.96 | 46.179 | 6.35 | 1.353 | 4.635 | 8490.48 | 1.958 | 97.9 | 77.4 | 1396 | 23.09 | 5518.8 | 1817 | 2182.7 | 2853.1 | 1198.1 | 0.63464 | 5.988
2024-12-09 | 18:08 | Data | 0 | 32.467 | 30.543 | 187.67 | 7.63 | 176.413 | 2146.6 | 25.97 | 46.269 | 6.35 | 1.347 | 4.625 | 8485.96 | 2.255 | 97.9 | 77.5 | 1396 | 23.09 | 5515.9 | 1824.5 | 2182.9 | 2857.3 | 1198.1 | 0.63631 | 5.969
2024-12-09 | 18:08 | Data | 0 | 32.75 | 30.658 | 187.715 | 7.63 | 176.459 | 2147.51 | 25.96 | 46.269 | 6.35 | 1.354 | 4.669 | 8472.39 | 2.059 | 97.8 | 77.5 | 1396 | 23.18 | 5507.1 | 1832.2 | 2217.5 | 2886.9 | 1198.1 | 0.6327 | 6.022
2024-12-09 | 18:08 | Data | 0 | 32.393 | 30.536 | 187.534 | 7.63 | 176.278 | 2147.51 | 25.96 | 46.359 | 6.35 | 1.348 | 4.69 | 8485.96 | 2.059 | 97.8 | 77.7 | 1396 | 23.13 | 5515.9 | 1828.1 | 2215 | 2870.3 | 1198.1 | 0.62766 | 6.035
2024-12-09 | 18:08 | Data | 0 | 32.71 | 30.691 | 187.624 | 7.63 | 176.323 | 2142.99 | 25.97 | 46.269 | 6.35 | 1.351 | 4.655 | 8508.57 | 1.911 | 97.8 | 77.5 | 1392 | 23.13 | 5530.6 | 1809.9 | 2235.3 | 2887.6 | 1198.1 | 0.62366 | 6.007
2024-12-09 | 18:08 | Data | 0 | 32.804 | 30.435 | 187.579 | 7.63 | 176.368 | 2146.6 | 25.98 | 46.179 | 6.35 | 1.347 | 4.664 | 8495 | 2.046 | 97.8 | 77.6 | 1396 | 23.09 | 5521.8 | 1831.6 | 2207.5 | 2879.7 | 1198.1 | 0.6311 | 6.011
2024-12-09 | 18:08 | Data | 0 | 32.264 | 30.529 | 187.579 | 7.63 | 176.278 | 2143.89 | 25.95 | 46.269 | 6.35 | 1.341 | 4.651 | 8499.53 | 2.066 | 97.8 | 77.6 | 1394 | 23.13 | 5524.7 | 1821 | 2201.1 | 2869.7 | 1198.1 | 0.63189 | 5.991
2024-12-09 | 18:08 | Data | 0 | 32.494 | 30.759 | 187.579 | 7.63 | 176.278 | 2144.79 | 25.96 | 46.179 | 6.35 | 1.341 | 4.673 | 8522.14 | 1.971 | 97.8 | 77.7 | 1394 | 23.13 | 5539.4 | 1815.6 | 2216.1 | 2877.1 | 1198.1 | 0.62855 | 6.015
2024-12-09 | 18:08 | Data | 0 | 32.602 | 30.651 | 187.624 | 7.63 | 176.323 | 2144.79 | 25.95 | 46.269 | 6.35 | 1.347 | 4.682 | 8508.57 | 2.214 | 97.8 | 77.7 | 1394 | 23.13 | 5530.6 | 2161.9 | 3012.1 | 3740.2 | 1198.1 | 0.60453 | 6.027
2024-12-09 | 18:08 | Data | 0 | 32.494 | 30.415 | 187.443 | 7.63 | 176.278 | 2145.7 | 25.95 | 46.45 | 6.35 | 1.346 | 4.668 | 8490.48 | 2.073 | 97.8 | 77.6 | 1395 | 23.22 | 5518.8 | 2894.5 | 2795.7 | 4140.4 | 1198.1 | 0.68358 | 6.014
2024-12-09 | 18:08 | Data | 0 | 32.285 | 30.59 | 187.624 | 7.63 | 176.323 | 2143.89 | 25.96 | 46.359 | 6.35 | 1.348 | 4.66 | 8495 | 1.877 | 97.8 | 77.6 | 1394 | 23.27 | 5521.8 | 2903.1 | 2783.1 | 4141.2 | 1198.1 | 0.68479 | 6.007
2024-12-09 | 18:08 | Data | 0 | 32.71 | 30.421 | 187.67 | 7.63 | 176.278 | 2142.99 | 25.97 | 46.269 | 6.35 | 1.348 | 4.66 | 8495 | 2.12 | 97.8 | 77.6 | 1394 | 23.18 | 5521.8 | 2905.8 | 2788.4 | 4144 | 1198.1 | 0.68549 | 6.007
2024-12-09 | 18:08 | Data | 0 | 32.494 | 30.415 | 187.624 | 7.63 | 176.278 | 2144.79 | 25.95 | 46.359 | 6.34 | 1.351 | 4.656 | 8495 | 1.877 | 97.8 | 77.5 | 1394 | 23.18 | 5521.8 | 2892.9 | 2775.2 | 4127.9 | 1198.1 | 0.68446 | 6.006
2024-12-09 | 18:08 | Data | 0 | 32.811 | 30.759 | 187.715 | 7.63 | 176.368 | 2143.89 | 25.95 | 46.54 | 6.35 | 1.353 | 4.677 | 8490.48 | 2.073 | 97.8 | 77.6 | 1394 | 23.22 | 5518.8 | 2875.9 | 2805 | 4139.2 | 1198.1 | 0.67805 | 6.03
2024-12-09 | 18:08 | Data | 0 | 32.696 | 30.806 | 187.534 | 7.63 | 176.278 | 2143.89 | 25.94 | 46.089 | 6.35 | 1.354 | 4.659 | 8499.53 | 2.127 | 97.8 | 77.5 | 1393 | 23.09 | 5524.7 | 2880.8 | 2804.5 | 4139.5 | 1198.1 | 0.68088 | 6.014
2024-12-09 | 18:08 | Data | 0 | 32.44 | 30.415 | 187.715 | 7.63 | 176.368 | 2142.08 | 25.94 | 46.45 | 6.35 | 1.352 | 4.635 | 8490.48 | 1.863 | 97.8 | 77.4 | 1392 | 23.22 | 5518.8 | 2901.2 | 2790.2 | 4143.2 | 1198.1 | 0.68374 | 5.988
2024-12-09 | 18:08 | Data | 0 | 32.609 | 30.442 | 187.715 | 7.63 | 176.368 | 2142.08 | 25.94 | 46.269 | 6.35 | 1.348 | 4.648 | 8490.48 | 1.917 | 97.8 | 77.5 | 1392 | 23.13 | 5518.8 | 2902.7 | 2810.6 | 4158.3 | 1198.1 | 0.6816 | 5.997
2024-12-09 | 18:08 | Data | 0 | 32.467 | 30.502 | 187.579 | 7.63 | 176.323 | 2142.08 | 25.94 | 46.45 | 6.35 | 1.341 | 4.645 | 8495 | 2.1 | 97.8 | 77.6 | 1392 | 23.22 | 5521.8 | 2902.1 | 2801.3 | 4149.8 | 1198.1 | 0.68269 | 5.987
2024-12-09 | 18:09 | Data | 0 | 32.298 | 30.637 | 187.67 | 7.63 | 176.323 | 2142.08 | 25.94 | 46.45 | 6.34 | 1.342 | 4.656 | 8499.53 | 1.843 | 97.8 | 77.6 | 1392 | 23.22 | 5524.7 | 2898.8 | 2779.6 | 4132.1 | 1198.1 | 0.68579 | 5.999
2024-12-09 | 18:09 | Data | 0 | 32.453 | 30.415 | 187.67 | 7.63 | 176.368 | 2144.79 | 25.93 | 46.45 | 6.35 | 1.344 | 4.666 | 8513.09 | 1.863 | 97.8 | 77.7 | 1394 | 23.22 | 5533.5 | 2901.1 | 2784.7 | 4136.7 | 1198.1 | 0.68587 | 6.009
2024-12-09 | 18:09 | Data | 0 | 32.717 | 30.651 | 187.76 | 7.63 | 176.323 | 2144.79 | 25.92 | 46.359 | 6.35 | 1.351 | 4.671 | 8472.39 | 2.073 | 97.8 | 77.6 | 1395 | 23.13 | 5507.1 | 2905.1 | 2768 | 4134.7 | 1198.1 | 0.68697 | 6.021
2024-12-09 | 18:09 | Data | 0 | 32.501 | 30.415 | 187.579 | 7.63 | 176.413 | 2137.56 | 25.92 | 46.45 | 6.35 | 1.348 | 4.673 | 8467.87 | 1.911 | 97.8 | 77.6 | 1389 | 23.27 | 5504.1 | 2916.7 | 2780.4 | 4149.9 | 1198.1 | 0.68579 | 6.021
2024-12-09 | 18:09 | Data | 0 | 32.818 | 30.907 | 187.624 | 7.63 | 176.368 | 2142.99 | 25.93 | 46.45 | 6.35 | 1.346 | 4.64 | 8458.83 | 2.073 | 97.8 | 77.5 | 1393 | 23.27 | 5498.2 | 2871.7 | 2785.9 | 4125.9 | 1198.1 | 0.6853 | 5.986
2024-12-09 | 18:09 | Data | 0 | 32.494 | 30.523 | 187.624 | 7.63 | 176.278 | 2142.08 | 25.93 | 46.45 | 6.35 | 1.345 | 4.649 | 8472.39 | 1.971 | 97.8 | 77.6 | 1392 | 23.27 | 5507.1 | 2895 | 2789.8 | 4136.9 | 1198.1 | 0.68345 | 5.994
2024-12-09 | 18:09 | Data | 0 | 32.521 | 30.469 | 187.715 | 7.63 | 176.368 | 2141.18 | 25.93 | 46.179 | 6.35 | 1.344 | 4.65 | 8472.39 | 1.863 | 97.8 | 77.6 | 1392 | 23.13 | 5507.1 | 2899.3 | 2782.2 | 4137.2 | 1198.2 | 0.68425 | 5.995
2024-12-09 | 18:09 | Data | 0 | 32.44 | 30.847 | 187.715 | 7.63 | 176.459 | 2141.18 | 25.91 | 46.45 | 6.35 | 1.346 | 4.676 | 8476.91 | 2.066 | 97.8 | 77.6 | 1393 | 23.27 | 5510 | 2900.6 | 2785.8 | 4141.6 | 1198.2 | 0.68417 | 6.021
2024-12-09 | 18:09 | Data | 0 | 32.386 | 30.637 | 187.67 | 7.63 | 176.278 | 2142.08 | 25.93 | 46.179 | 6.35 | 1.343 | 4.686 | 8481.44 | 1.782 | 97.8 | 77.7 | 1393 | 23.13 | 5512.9 | 2903.9 | 2785.7 | 4149.5 | 1198.2 | 0.68195 | 6.029
2024-12-09 | 18:09 | Data | 0 | 32.494 | 30.415 | 187.489 | 7.63 | 176.278 | 2148.41 | 25.92 | 46.179 | 6.34 | 1.34 | 4.682 | 8467.87 | 2.059 | 97.8 | 77.7 | 1396 | 23.13 | 5504.1 | 2890.3 | 2792.6 | 4138 | 1198.2 | 0.68248 | 6.023
2024-12-09 | 18:09 | Data | 0 | 32.521 | 30.644 | 187.67 | 7.63 | 176.368 | 2152.02 | 25.93 | 46.269 | 6.35 | 1.352 | 4.645 | 8458.83 | 1.863 | 97.8 | 77.5 | 1398 | 23.13 | 5498.2 | 2909.7 | 2775.7 | 4140.1 | 1198.2 | 0.68627 | 5.999
2024-12-09 | 18:09 | Data | 0 | 32.339 | 30.631 | 187.579 | 7.63 | 176.368 | 2151.12 | 25.93 | 46.179 | 6.35 | 1.349 | 4.649 | 8472.39 | 1.87 | 97.9 | 77.5 | 1399 | 23.09 | 5507.1 | 2895.8 | 2765.8 | 4125.1 | 1198.2 | 0.6859 | 5.998
2024-12-09 | 18:09 | Data | 0 | 32.595 | 30.435 | 187.579 | 7.63 | 176.368 | 2149.31 | 25.93 | 46.179 | 6.35 | 1.351 | 4.677 | 8454.3 | 2.019 | 97.8 | 77.6 | 1398 | 23.13 | 5495.3 | 2898.7 | 2784.3 | 4135.5 | 1198.2 | 0.68399 | 6.031
2024-12-09 | 18:09 | Data | 0 | 32.825 | 30.874 | 187.67 | 7.63 | 176.323 | 2152.93 | 25.93 | 46.179 | 6.35 | 1.363 | 4.645 | 8458.83 | 2.066 | 97.8 | 77.3 | 1399 | 23.13 | 5498.2 | 2898.7 | 2791.3 | 4143 | 1198.2 | 0.68299 | 6.01
2024-12-09 | 18:09 | Data | 0 | 32.291 | 30.415 | 187.624 | 7.63 | 176.233 | 2153.83 | 25.92 | 46.269 | 6.35 | 1.344 | 4.684 | 8440.74 | 2.032 | 97.9 | 77.7 | 1400 | 23.09 | 5486.5 | 2899.3 | 2774.7 | 4129.7 | 1198.2 | 0.6864 | 6.028
2024-12-09 | 18:09 | Data | 0 | 32.94 | 30.563 | 187.715 | 7.63 | 176.459 | 2153.83 | 25.93 | 46.179 | 6.35 | 1.345 | 4.66 | 8445.26 | 2.073 | 97.8 | 77.6 | 1401 | 23.18 | 5489.4 | 2903 | 2783.6 | 4140.5 | 1198.2 | 0.68433 | 6.007
2024-12-09 | 18:09 | Data | 0 | 33.054 | 30.685 | 187.805 | 7.63 | 176.413 | 2151.12 | 25.92 | 46.359 | 6.35 | 1.348 | 4.654 | 8445.26 | 2.214 | 97.8 | 77.5 | 1398 | 23.13 | 5489.4 | 2911 | 2820.3 | 4172.7 | 1198.2 | 0.68148 | 6.003
2024-12-09 | 18:10 | Data | 0 | 32.717 | 30.59 | 187.579 | 7.63 | 176.278 | 2153.83 | 25.93 | 46.269 | 6.35 | 1.347 | 4.654 | 8458.83 | 2.187 | 97.9 | 77.6 | 1400 | 23.18 | 5498.2 | 2904.6 | 2790.6 | 4144.8 | 1198.2 | 0.68429 | 6.002
2024-12-09 | 18:10 | Data | 0 | 32.264 | 30.536 | 187.579 | 7.63 | 176.323 | 2153.83 | 25.94 | 46.269 | 6.35 | 1.347 | 4.669 | 8463.35 | 1.85 | 97.9 | 77.6 | 1399 | 23.04 | 5501.2 | 2896.4 | 2785.6 | 4135.7 | 1198.2 | 0.68455 | 6.015
2024-12-09 | 18:10 | Data | 0 | 32.919 | 30.705 | 187.67 | 7.63 | 176.368 | 2152.93 | 25.93 | 46.721 | 6.35 | 1.348 | 4.675 | 8472.39 | 2.241 | 97.8 | 77.6 | 1399 | 23.36 | 5507.1 | 2896.4 | 2787.4 | 4138.3 | 1198.2 | 0.68377 | 6.024
2024-12-09 | 18:10 | Data | 0 | 32.825 | 30.678 | 187.805 | 7.63 | 176.459 | 2153.83 | 25.93 | 46.269 | 6.35 | 1.342 | 4.671 | 8454.3 | 2.181 | 97.9 | 77.7 | 1401 | 23.09 | 5495.3 | 2901.6 | 2776.7 | 4136.1 | 1198.2 | 0.68455 | 6.013
2024-12-09 | 18:10 | Data | 0 | 32.71 | 30.853 | 187.624 | 7.64 | 176.368 | 2151.12 | 25.92 | 46.269 | 6.35 | 1.352 | 4.654 | 8458.83 | 1.951 | 97.8 | 77.5 | 1398 | 23.09 | 5498.2 | 2894.7 | 2784.2 | 4134.3 | 1198.2 | 0.68371 | 6.007
2024-12-09 | 18:10 | Data | 0 | 32.379 | 30.739 | 187.715 | 7.63 | 176.368 | 2149.31 | 25.92 | 46.269 | 6.35 | 1.354 | 4.664 | 8458.83 | 2.046 | 97.8 | 77.5 | 1397 | 23.13 | 5498.2 | 2893.5 | 2793 | 4142 | 1198.2 | 0.68162 | 6.019
2024-12-09 | 18:10 | Data | 0 | 32.494 | 30.59 | 187.624 | 7.63 | 176.323 | 2147.51 | 25.94 | 46.179 | 6.35 | 1.353 | 4.666 | 8458.83 | 2.073 | 97.9 | 77.5 | 1396 | 23.09 | 5498.2 | 2900.9 | 2793.1 | 4146.3 | 1198.2 | 0.68387 | 6.02
2024-12-09 | 18:10 | Data | 0 | 32.453 | 30.624 | 187.624 | 7.64 | 176.278 | 2146.6 | 25.93 | 46.269 | 6.35 | 1.356 | 4.666 | 8467.87 | 1.884 | 97.8 | 77.5 | 1395 | 23.13 | 5504.1 | 2881 | 2817.3 | 4147.1 | 1198.2 | 0.67882 | 6.022
2024-12-09 | 18:10 | Data | 0 | 32.514 | 30.651 | 187.67 | 7.63 | 176.323 | 2144.79 | 25.93 | 46.269 | 6.35 | 1.347 | 4.654 | 8472.39 | 2.019 | 97.8 | 77.6 | 1394 | 23.13 | 5507.1 | 2897.3 | 2812.7 | 4157.6 | 1198.2 | 0.67962 | 6
2024-12-09 | 18:10 | Data | 0 | 32.271 | 30.523 | 187.534 | 7.63 | 176.323 | 2146.6 | 25.94 | 46.179 | 6.35 | 1.339 | 4.652 | 8458.83 | 1.911 | 97.8 | 77.7 | 1396 | 23.13 | 5498.2 | 2916.9 | 2825.6 | 4169 | 1198.2 | 0.68292 | 5.993
2024-12-09 | 18:10 | Data | 0 | 32.507 | 30.421 | 187.67 | 7.63 | 176.323 | 2147.51 | 25.92 | 46.179 | 6.35 | 1.346 | 4.648 | 8445.26 | 2.073 | 97.8 | 77.6 | 1396 | 23.13 | 5489.4 | 2903.6 | 2813.9 | 4160 | 1198.2 | 0.68133 | 5.993
2024-12-09 | 18:10 | Data | 0 | 32.507 | 30.637 | 187.715 | 7.63 | 176.413 | 2151.12 | 25.92 | 46.359 | 6.35 | 1.348 | 4.672 | 8440.74 | 1.877 | 97.8 | 77.6 | 1398 | 23.13 | 5486.5 | 2913.6 | 2815.8 | 4166.9 | 1198.2 | 0.68442 | 6.02
2024-12-09 | 18:10 | Data | 0 | 32.669 | 30.421 | 187.67 | 7.63 | 176.323 | 2146.6 | 25.93 | 46.269 | 6.35 | 1.348 | 4.655 | 8440.74 | 2.079 | 97.8 | 77.6 | 1395 | 23.13 | 5486.5 | 2915.7 | 2792.6 | 4152.8 | 1198.2 | 0.68511 | 6.005
2024-12-09 | 18:10 | Data | 0 | 32.723 | 30.651 | 187.715 | 7.63 | 176.323 | 2145.7 | 25.92 | 46.179 | 6.35 | 1.334 | 4.679 | 8454.3 | 1.958 | 97.8 | 77.8 | 1394 | 23.13 | 5495.3 | 2910.7 | 2782.4 | 4142.8 | 1198.2 | 0.68608 | 6.014
2024-12-09 | 18:10 | Data | 0 | 32.723 | 30.867 | 187.851 | 7.63 | 176.413 | 2143.89 | 25.93 | 46.179 | 6.35 | 1.347 | 4.659 | 8463.35 | 1.985 | 97.8 | 77.6 | 1394 | 23.13 | 5501.2 | 2923.8 | 2789.7 | 4157.8 | 1198.2 | 0.68802 | 6.005
2024-12-09 | 18:10 | Data | 0 | 32.622 | 30.225 | 187.67 | 7.63 | 176.368 | 2143.89 | 25.94 | 46.269 | 6.35 | 1.342 | 4.636 | 8458.83 | 2.214 | 97.8 | 77.6 | 1394 | 23.09 | 5498.2 | 2912.4 | 2798.3 | 4150.9 | 1198.2 | 0.68559 | 5.977
2024-12-09 | 18:10 | Data | 0 | 32.771 | 30.421 | 187.624 | 7.63 | 176.413 | 2144.79 | 25.91 | 46.359 | 6.35 | 1.348 | 4.677 | 8449.78 | 1.978 | 97.8 | 77.6 | 1395 | 23.18 | 5492.4 | 2888.3 | 2801.2 | 4144.6 | 1198.2 | 0.68043 | 6.026
2024-12-09 | 18:10 | Data | 0 | 32.48 | 30.415 | 187.579 | 7.63 | 176.278 | 2142.08 | 25.94 | 46.269 | 6.35 | 1.348 | 4.655 | 8445.26 | 2.079 | 97.8 | 77.6 | 1392 | 23.13 | 5489.4 | 2909.4 | 2812.2 | 4164.9 | 1198.2 | 0.68194 | 6.003
2024-12-09 | 18:11 | Data | 0 | 32.541 | 30.847 | 187.67 | 7.63 | 176.413 | 2142.99 | 25.95 | 46.179 | 6.35 | 1.351 | 4.655 | 8467.87 | 1.931 | 97.8 | 77.5 | 1392 | 23.09 | 5504.1 | 2910.2 | 2794.3 | 4155.8 | 1198.2 | 0.6837 | 6.007
2024-12-09 | 18:11 | Data | 0 | 32.501 | 30.651 | 187.624 | 7.63 | 176.459 | 2141.18 | 25.94 | 46.269 | 6.35 | 1.348 | 4.632 | 8445.26 | 2.046 | 97.8 | 77.5 | 1392 | 23.09 | 5489.4 | 2888.8 | 2788.2 | 4130.2 | 1198.2 | 0.68088 | 5.979
2024-12-09 | 18:11 | Data | 0 | 32.507 | 30.806 | 187.67 | 7.63 | 176.368 | 2142.08 | 25.95 | 46.359 | 6.35 | 1.347 | 4.657 | 8445.26 | 2.073 | 97.8 | 77.6 | 1392 | 23.18 | 5489.4 | 2891.2 | 2793.5 | 4135 | 1198.2 | 0.6827 | 6.005
2024-12-09 | 18:11 | Data | 0 | 32.494 | 30.82 | 187.715 | 7.63 | 176.368 | 2147.51 | 25.92 | 46.269 | 6.35 | 1.346 | 4.674 | 8440.74 | 2.025 | 97.8 | 77.6 | 1396 | 23.13 | 5486.5 | 2904.5 | 2782.4 | 4139.7 | 1198.2 | 0.68511 | 6.021
2024-12-09 | 18:11 | Data | 0 | 32.723 | 30.448 | 187.715 | 7.63 | 176.368 | 2146.6 | 25.92 | 46.269 | 6.35 | 1.357 | 4.68 | 8454.3 | 2.241 | 97.8 | 77.5 | 1396 | 23.09 | 5495.3 | 2903.4 | 2790.9 | 4147.4 | 1198.2 | 0.68418 | 6.035
2024-12-09 | 18:11 | Data | 0 | 32.777 | 30.448 | 187.76 | 7.63 | 176.368 | 2144.79 | 25.94 | 46.179 | 6.35 | 1.351 | 4.687 | 8892.96 | 2.073 | 97.8 | 77.6 | 1394 | 23.09 | 5780.4 | 2892.8 | 2783.4 | 4132.7 | 1198.2 | 0.6829 | 6.037
2024-12-09 | 18:11 | Data | 0 | 32.946 | 30.766 | 187.67 | 7.63 | 176.549 | 2144.79 | 25.93 | 46.269 | 6.35 | 1.347 | 4.681 | 8463.35 | 1.985 | 97.8 | 77.7 | 1394 | 23.18 | 5501.2 | 2913.6 | 2786.1 | 4147.8 | 1198.2 | 0.68518 | 6.027
2024-12-09 | 18:11 | Data | 0 | 32.561 | 30.712 | 187.805 | 7.63 | 176.594 | 2144.79 | 25.94 | 46.089 | 6.34 | 1.349 | 4.662 | 8485.96 | 1.998 | 97.8 | 77.6 | 1394 | 23.09 | 5515.9 | 2900.3 | 2794.6 | 4144.3 | 1198.3 | 0.68176 | 6.011
2024-12-09 | 18:11 | Data | 0 | 32.717 | 30.759 | 187.76 | 7.63 | 176.368 | 2144.79 | 25.93 | 46.269 | 6.35 | 1.344 | 4.669 | 8490.48 | 2.086 | 97.8 | 77.7 | 1394 | 23.13 | 5518.8 | 2903.6 | 2789 | 4147 | 1198.3 | 0.68201 | 6.013
2024-12-09 | 18:11 | Data | 0 | 33.108 | 30.516 | 187.67 | 7.63 | 176.459 | 2147.51 | 25.95 | 46.269 | 6.35 | 1.348 | 4.688 | 8485.96 | 2.241 | 97.8 | 77.7 | 1396 | 23.13 | 5515.9 | 2895.3 | 2786.2 | 4131.1 | 1198.3 | 0.6853 | 6.036
2024-12-09 | 18:11 | Data | 0 | 32.501 | 30.651 | 187.67 | 7.63 | 176.368 | 2147.51 | 25.93 | 46.45 | 6.35 | 1.343 | 4.673 | 8485.96 | 1.958 | 97.8 | 77.7 | 1396 | 23.27 | 5515.9 | 2903.2 | 2787.2 | 4143.5 | 1198.3 | 0.68505 | 6.016
2024-12-09 | 18:11 | Data | 0 | 32.325 | 30.415 | 187.67 | 7.63 | 176.459 | 2144.79 | 25.93 | 46.54 | 6.35 | 1.352 | 4.666 | 8472.39 | 1.857 | 97.8 | 77.5 | 1394 | 23.27 | 5507.1 | 2925.1 | 2772 | 4146.3 | 1198.3 | 0.68979 | 6.018
2024-12-09 | 18:11 | Data | 0 | 32.413 | 30.415 | 187.715 | 7.63 | 176.368 | 2145.7 | 25.94 | 46.45 | 6.35 | 1.353 | 4.66 | 8458.83 | 2.039 | 97.8 | 77.5 | 1394 | 23.22 | 5498.2 | 2915.2 | 2793 | 4151.9 | 1198.3 | 0.68672 | 6.014
2024-12-09 | 18:11 | Data | 0 | 32.507 | 30.597 | 187.67 | 7.63 | 176.368 | 2143.89 | 25.93 | 46.45 | 6.34 | 1.353 | 4.655 | 8463.35 | 1.904 | 97.8 | 77.5 | 1394 | 23.22 | 5501.2 | 2904.1 | 2787.4 | 4150.5 | 1198.3 | 0.68452 | 6.008
2024-12-09 | 18:11 | Data | 0 | 32.838 | 30.874 | 187.715 | 7.63 | 176.413 | 2142.08 | 25.94 | 46.45 | 6.34 | 1.341 | 4.665 | 8467.87 | 2.059 | 97.8 | 77.7 | 1392 | 23.27 | 5504.1 | 2901.9 | 2773.6 | 4129.9 | 1198.3 | 0.6869 | 6.007
2024-12-09 | 18:11 | Data | 0 | 32.94 | 30.88 | 187.805 | 7.63 | 176.549 | 2144.79 | 25.94 | 46.54 | 6.35 | 1.339 | 4.665 | 8508.57 | 2.073 | 97.8 | 77.7 | 1394 | 23.22 | 5530.6 | 2900.6 | 2783.1 | 4137.9 | 1198.3 | 0.6846 | 6.003
2024-12-09 | 18:11 | Data | 0 | 32.831 | 30.853 | 187.715 | 7.63 | 176.413 | 2144.79 | 25.94 | 46.54 | 6.35 | 1.34 | 4.679 | 8495 | 2.154 | 97.8 | 77.7 | 1394 | 23.27 | 5521.8 | 2893.2 | 2775.5 | 4133.4 | 1198.3 | 0.68235 | 6.017
2024-12-09 | 18:11 | Data | 0 | 32.494 | 30.415 | 187.715 | 7.63 | 176.368 | 2144.79 | 25.94 | 46.45 | 6.35 | 1.348 | 4.688 | 8495 | 2.079 | 97.8 | 77.7 | 1394 | 23.22 | 5521.8 | 2909.6 | 2783.8 | 4150.2 | 1198.3 | 0.68645 | 6.036
2024-12-09 | 18:12 | Data | 0 | 32.494 | 30.421 | 187.715 | 7.63 | 176.413 | 2143.89 | 25.94 | 46.45 | 6.35 | 1.349 | 4.681 | 8495 | 2.073 | 97.8 | 77.6 | 1394 | 23.22 | 5521.8 | 2902.3 | 2781.3 | 4137.9 | 1198.3 | 0.68405 | 6.03
2024-12-09 | 18:12 | Data | 0 | 32.946 | 30.651 | 187.579 | 7.63 | 176.549 | 2142.08 | 25.94 | 46.45 | 6.35 | 1.349 | 4.655 | 8481.44 | 2.093 | 97.8 | 77.5 | 1393 | 23.22 | 5512.9 | 2901.9 | 2779.2 | 4136.2 | 1198.3 | 0.68472 | 6.005
2024-12-09 | 18:12 | Data | 0 | 32.723 | 30.705 | 187.805 | 7.63 | 176.459 | 2141.18 | 25.93 | 46.45 | 6.35 | 1.347 | 4.657 | 8449.78 | 2.019 | 97.8 | 77.6 | 1392 | 23.22 | 5492.4 | 2902.1 | 2777 | 4131.5 | 1198.3 | 0.6851 | 6.004
2024-12-09 | 18:12 | Data | 0 | 33.054 | 31.157 | 187.76 | 7.63 | 176.459 | 2142.08 | 25.92 | 46.54 | 6.35 | 1.348 | 4.656 | 8458.83 | 1.938 | 97.8 | 77.5 | 1392 | 23.27 | 5498.2 | 2896.5 | 2779.4 | 4139.9 | 1198.3 | 0.68622 | 6.006
2024-12-09 | 18:12 | Data | 0 | 32.663 | 30.651 | 187.715 | 7.63 | 176.459 | 2140.27 | 25.92 | 46.54 | 6.35 | 1.349 | 4.643 | 8485.96 | 1.884 | 97.8 | 77.5 | 1391 | 23.22 | 5515.9 | 2910.9 | 2770.4 | 4137.7 | 1198.3 | 0.68716 | 5.992
2024-12-09 | 18:12 | Data | 0 | 32.669 | 30.82 | 187.76 | 7.63 | 176.368 | 2138.47 | 25.94 | 46.45 | 6.35 | 1.348 | 4.659 | 8513.09 | 2.066 | 97.8 | 77.6 | 1391 | 23.22 | 5533.5 | 2895.7 | 2803.3 | 4148.6 | 1198.3 | 0.6787 | 6.006
2024-12-09 | 18:12 | Data | 0 | 32.501 | 30.597 | 187.579 | 7.63 | 176.323 | 2139.37 | 25.93 | 46.359 | 6.35 | 1.356 | 4.649 | 8526.66 | 1.958 | 97.8 | 77.4 | 1391 | 23.22 | 5542.3 | 2899.6 | 2831.4 | 4174.4 | 1198.3 | 0.67969 | 6.004
2024-12-09 | 18:12 | Data | 0 | 32.858 | 30.455 | 187.805 | 7.63 | 176.459 | 2139.37 | 25.92 | 46.54 | 6.35 | 1.348 | 4.648 | 8517.61 | 1.978 | 97.8 | 77.5 | 1391 | 23.32 | 5536.4 | 2882.4 | 2829.9 | 4167.3 | 1198.3 | 0.67552 | 5.996
2024-12-09 | 18:12 | Data | 0 | 32.298 | 30.421 | 187.76 | 7.63 | 176.413 | 2142.99 | 25.94 | 46.54 | 6.35 | 1.349 | 4.655 | 8495 | 1.958 | 97.8 | 77.5 | 1392 | 23.22 | 5521.8 | 2880.7 | 2821.1 | 4146.7 | 1198.3 | 0.68136 | 6.005
2024-12-09 | 18:12 | Data | 0 | 33.061 | 30.57 | 187.76 | 7.63 | 176.549 | 2140.27 | 25.94 | 46.54 | 6.35 | 1.345 | 4.677 | 8499.53 | 2.086 | 97.8 | 77.7 | 1390 | 23.27 | 5524.7 | 2887 | 2811.2 | 4151.7 | 1198.3 | 0.67863 | 6.022
2024-12-09 | 18:12 | Data | 0 | 32.521 | 30.752 | 187.76 | 7.64 | 176.413 | 2138.47 | 25.94 | 46.54 | 6.35 | 1.355 | 4.656 | 8526.66 | 1.89 | 97.8 | 77.5 | 1391 | 23.27 | 5542.3 | 2909.6 | 2806.9 | 4156.6 | 1198.3 | 0.68268 | 6.011
2024-12-09 | 18:12 | Data | 0 | 32.946 | 30.88 | 187.805 | 7.63 | 176.549 | 2139.37 | 25.94 | 46.269 | 6.34 | 1.348 | 4.688 | 8531.18 | 1.87 | 97.8 | 77.7 | 1391 | 23.18 | 5545.3 | 2903.4 | 2776.7 | 4137.5 | 1198.3 | 0.68479 | 6.036
2024-12-09 | 18:12 | Data | 0 | 32.44 | 30.691 | 187.67 | 7.63 | 176.323 | 2139.37 | 25.94 | 46.179 | 6.35 | 1.346 | 4.677 | 8522.14 | 2.127 | 97.8 | 77.7 | 1391 | 23.09 | 5539.4 | 2883.1 | 2804.6 | 4144.3 | 1198.3 | 0.67924 | 6.021
2024-12-09 | 18:12 | Data | 0 | 32.609 | 30.624 | 187.76 | 7.63 | 176.413 | 2138.47 | 25.93 | 46.179 | 6.35 | 1.359 | 4.65 | 8513.09 | 1.911 | 97.8 | 77.4 | 1391 | 23.13 | 5533.5 | 2890.1 | 2796.6 | 4143.1 | 1198.3 | 0.68053 | 6.009
2024-12-09 | 18:12 | Data | 0 | 32.696 | 30.813 | 187.624 | 7.63 | 176.368 | 2139.37 | 25.94 | 46.269 | 6.35 | 1.344 | 4.628 | 8495 | 2.113 | 97.8 | 77.5 | 1391 | 23.09 | 5521.8 | 2890.3 | 2794 | 4131.4 | 1198.3 | 0.67979 | 5.971
2024-12-09 | 18:12 | Data | 0 | 32.669 | 30.874 | 187.715 | 7.63 | 176.549 | 2139.37 | 25.93 | 46.269 | 6.35 | 1.352 | 4.667 | 8499.53 | 1.965 | 97.8 | 77.5 | 1391 | 23.13 | 5524.7 | 2884.6 | 2781.2 | 4125.2 | 1198.3 | 0.68311 | 6.019
2024-12-09 | 18:12 | Data | 0 | 32.967 | 30.712 | 187.76 | 7.63 | 176.639 | 2140.27 | 25.94 | 46.269 | 6.35 | 1.348 | 4.65 | 8490.48 | 1.924 | 97.8 | 77.5 | 1392 | 23.04 | 5518.8 | 2902.1 | 2785.9 | 4140.4 | 1198.3 | 0.6852 | 5.998
2024-12-09 | 18:12 | Data | 0 | 32.494 | 30.624 | 187.67 | 7.63 | 176.368 | 2142.99 | 25.94 | 46.269 | 6.35 | 1.348 | 4.66 | 8454.3 | 1.938 | 97.8 | 77.6 | 1392 | 23.13 | 5495.3 | 2901.4 | 2768 | 4125.7 | 1198.3 | 0.68656 | 6.01
2024-12-09 | 18:13 | Data | 0 | 32.568 | 30.435 | 187.805 | 7.63 | 176.549 | 2142.08 | 25.95 | 46.179 | 6.35 | 1.343 | 4.656 | 8440.74 | 2.066 | 97.8 | 77.6 | 1392 | 23.09 | 5486.5 | 2887.3 | 2788.4 | 4133.6 | 1198.3 | 0.68352 | 5.998
2024-12-09 | 18:13 | Data | 0 | 32.568 | 30.543 | 187.67 | 7.64 | 176.459 | 2145.7 | 25.95 | 46.269 | 6.35 | 1.338 | 4.681 | 8458.83 | 1.87 | 97.8 | 77.8 | 1395 | 23.13 | 5498.2 | 2893.6 | 2804.6 | 4146.9 | 1198.3 | 0.68361 | 6.018
2024-12-09 | 18:13 | Data | 0 | 32.582 | 30.874 | 187.67 | 7.63 | 176.459 | 2141.18 | 25.95 | 46.179 | 6.35 | 1.346 | 4.669 | 8458.83 | 2.066 | 97.8 | 77.6 | 1392 | 23.09 | 5498.2 | 2898.5 | 2783 | 4132.9 | 1198.3 | 0.68483 | 6.015
2024-12-09 | 18:13 | Data | 0 | 32.609 | 30.637 | 187.715 | 7.63 | 176.459 | 2148.41 | 25.94 | 46.269 | 6.35 | 1.349 | 4.629 | 8485.96 | 2.086 | 97.8 | 77.4 | 1396 | 23.13 | 5515.9 | 2895.7 | 2780.8 | 4132.5 | 1198.3 | 0.68475 | 5.979
2024-12-09 | 18:13 | Data | 0 | 32.568 | 30.421 | 187.76 | 7.63 | 176.368 | 2142.08 | 25.94 | 46.269 | 6.35 | 1.358 | 4.616 | 8495 | 2.052 | 97.8 | 77.3 | 1392 | 23.13 | 5521.8 | 2909.1 | 2779 | 4139 | 1198.3 | 0.68665 | 5.973
2024-12-09 | 18:13 | Data | 0 | 32.629 | 30.435 | 187.896 | 7.63 | 176.549 | 2141.18 | 25.94 | 46.179 | 6.35 | 1.358 | 4.655 | 8490.48 | 2.073 | 97.8 | 77.4 | 1392 | 23.09 | 5518.8 | 2905.4 | 2792.9 | 4138.2 | 1198.3 | 0.68315 | 6.012
2024-12-09 | 18:13 | Data | 0 | 32.501 | 30.529 | 187.76 | 7.63 | 176.459 | 2142.08 | 25.94 | 46.269 | 6.35 | 1.353 | 4.631 | 8481.44 | 2.079 | 97.8 | 77.4 | 1392 | 23.13 | 5512.9 | 2887.8 | 2788.5 | 4133.7 | 1198.3 | 0.68314 | 5.985
2024-12-09 | 18:13 | Data | 0 | 32.656 | 31.015 | 187.896 | 7.63 | 176.459 | 2144.79 | 25.95 | 46.179 | 6.35 | 1.343 | 4.672 | 8499.53 | 2.1 | 97.8 | 77.7 | 1394 | 23.13 | 5524.7 | 2887.6 | 2788.6 | 4136.2 | 1198.3 | 0.68115 | 6.014
2024-12-09 | 18:13 | Data | 0 | 32.44 | 30.82 | 187.76 | 7.63 | 176.459 | 2144.79 | 25.94 | 46.179 | 6.35 | 1.351 | 4.654 | 8508.57 | 2.012 | 97.8 | 77.5 | 1395 | 23.09 | 5530.6 | 2909.1 | 2777.4 | 4138.2 | 1198.4 | 0.68642 | 6.006
2024-12-09 | 18:13 | Data | 0 | 32.723 | 30.698 | 187.67 | 7.63 | 176.413 | 2144.79 | 25.95 | 46.269 | 6.35 | 1.356 | 4.662 | 8522.14 | 2.12 | 97.8 | 77.5 | 1394 | 23.13 | 5539.4 | 2907.4 | 2805.4 | 4160.8 | 1198.4 | 0.68187 | 6.018
2024-12-09 | 18:13 | Data | 0 | 33.108 | 30.57 | 187.896 | 7.63 | 176.594 | 2144.79 | 25.94 | 46.179 | 6.35 | 1.348 | 4.684 | 8513.09 | 2.167 | 97.8 | 77.7 | 1394 | 23.18 | 5533.5 | 2904.9 | 2773.5 | 4132.7 | 1198.4 | 0.68624 | 6.031
2024-12-09 | 18:13 | Data | 0 | 32.541 | 30.597 | 187.76 | 7.64 | 176.459 | 2140.27 | 25.93 | 46.269 | 6.35 | 1.349 | 4.671 | 8513.09 | 1.965 | 97.8 | 77.6 | 1391 | 23.18 | 5533.5 | 2887.8 | 2786 | 4134.6 | 1198.4 | 0.68207 | 6.022
2024-12-09 | 18:13 | Data | 0 | 32.723 | 30.455 | 187.67 | 7.64 | 176.459 | 2144.79 | 25.95 | 46.179 | 6.35 | 1.359 | 4.676 | 8883.91 | 2.113 | 97.8 | 77.5 | 1394 | 23.18 | 5774.5 | 2900.3 | 2780.3 | 4139.8 | 1198.4 | 0.68423 | 6.036
2024-12-09 | 18:13 | Data | 0 | 32.757 | 30.982 | 187.896 | 7.63 | 176.639 | 2145.7 | 25.94 | 46.269 | 6.35 | 1.357 | 4.674 | 8911.05 | 1.877 | 97.8 | 77.5 | 1394 | 23.09 | 5792.2 | 2906.8 | 2792.3 | 4137.9 | 1198.4 | 0.68383 | 6.03
2024-12-09 | 18:13 | Data | 0 | 32.501 | 30.597 | 187.851 | 7.63 | 176.594 | 2144.79 | 25.95 | 46.269 | 6.35 | 1.344 | 4.676 | 8341.25 | 1.951 | 97.8 | 77.7 | 1394 | 23.13 | 5421.8 | 2909.9 | 2785.2 | 4141.6 | 1198.4 | 0.68711 | 6.019
2024-12-09 | 18:13 | Data | 0 | 32.609 | 30.988 | 187.76 | 7.63 | 176.549 | 2147.51 | 25.94 | 46.269 | 6.35 | 1.348 | 4.683 | 8291.5 | 2.012 | 97.8 | 77.7 | 1396 | 23.13 | 5389.5 | 2885.8 | 2785.5 | 4130.4 | 1198.4 | 0.68263 | 6.03
2024-12-09 | 18:13 | Data | 0 | 32.528 | 30.853 | 187.715 | 7.63 | 176.413 | 2143.89 | 25.94 | 46.269 | 6.35 | 1.352 | 4.666 | 8277.94 | 1.789 | 97.8 | 77.5 | 1393 | 23.13 | 5380.7 | 2895.7 | 2775.8 | 4130.8 | 1198.4 | 0.68408 | 6.019
2024-12-09 | 18:14 | Data | 0 | 32.494 | 30.536 | 187.624 | 7.63 | 176.413 | 2145.7 | 25.94 | 46.179 | 6.35 | 1.351 | 4.639 | 8291.5 | 2.073 | 97.8 | 77.4 | 1395 | 23.09 | 5389.5 | 2896.7 | 2771.4 | 4129.1 | 1198.4 | 0.68407 | 5.99
2024-12-09 | 18:14 | Data | 0 | 32.528 | 30.813 | 187.851 | 7.63 | 176.549 | 2144.79 | 25.95 | 46.179 | 6.35 | 1.345 | 4.662 | 8300.55 | 1.857 | 97.8 | 77.6 | 1394 | 23.09 | 5395.4 | 2912.3 | 2792.7 | 4157 | 1198.4 | 0.68755 | 6.007
2024-12-09 | 18:14 | Data | 0 | 32.737 | 30.442 | 187.76 | 7.63 | 176.459 | 2143.89 | 25.93 | 46.269 | 6.35 | 1.343 | 4.691 | 8314.11 | 2.046 | 97.8 | 77.7 | 1394 | 23.09 | 5404.2 | 2909.2 | 2754.2 | 4128.6 | 1198.4 | 0.68796 | 6.034
2024-12-09 | 18:14 | Data | 0 | 32.345 | 30.415 | 187.67 | 7.63 | 176.549 | 2147.51 | 25.94 | 46.179 | 6.35 | 1.341 | 4.667 | 8332.2 | 1.884 | 97.8 | 77.7 | 1396 | 23.09 | 5415.9 | 2907.3 | 2784 | 4144.5 | 1198.4 | 0.68558 | 6.008
2024-12-09 | 18:14 | Data | 0 | 32.71 | 30.651 | 187.715 | 7.63 | 176.549 | 2148.41 | 25.94 | 46.179 | 6.35 | 1.332 | 4.662 | 8345.77 | 2.086 | 97.8 | 77.8 | 1396 | 23.09 | 5424.8 | 2919.2 | 2780.7 | 4147.9 | 1198.4 | 0.6874 | 5.994
2024-12-09 | 18:14 | Data | 0 | 32.71 | 30.482 | 187.624 | 7.63 | 176.459 | 2146.6 | 25.94 | 46.179 | 6.35 | 1.353 | 4.647 | 8345.77 | 2.066 | 97.8 | 77.5 | 1395 | 23.13 | 5424.8 | 2921.2 | 2798.3 | 4165.6 | 1198.4 | 0.68532 | 6
2024-12-09 | 18:14 | Data | 0 | 32.285 | 30.637 | 187.76 | 7.63 | 176.323 | 2146.6 | 25.93 | 46.269 | 6.34 | 1.362 | 4.639 | 8372.9 | 1.877 | 97.8 | 77.3 | 1396 | 23.13 | 5442.4 | 2937 | 2782.6 | 4162.4 | 1198.4 | 0.68926 | 6.001
2024-12-09 | 18:14 | Data | 0 | 32.723 | 30.448 | 187.624 | 7.63 | 176.459 | 2147.51 | 25.94 | 46.269 | 6.35 | 1.344 | 4.647 | 8730.16 | 2.066 | 97.8 | 77.6 | 1395 | 23.13 | 5674.6 | 2918.9 | 2796.9 | 4167.7 | 1198.4 | 0.68524 | 5.992
2024-12-09 | 18:14 | Data | 0 | 32.94 | 30.678 | 187.76 | 7.63 | 176.413 | 2144.79 | 25.92 | 46.179 | 6.35 | 1.354 | 4.662 | 8703.03 | 2.059 | 97.8 | 77.5 | 1394 | 23.13 | 5657 | 2897.1 | 2781.5 | 4140.4 | 1198.4 | 0.68347 | 6.018
2024-12-09 | 18:14 | Data | 0 | 33 | 30.678 | 187.851 | 7.63 | 176.549 | 2143.89 | 25.95 | 46.179 | 6.34 | 1.344 | 4.641 | 8684.94 | 2.255 | 97.8 | 77.5 | 1394 | 23.13 | 5645.2 | 2961.7 | 2807.1 | 4214.1 | 1198.4 | 0.68947 | 5.985
2024-12-09 | 18:14 | Data | 0 | 32.723 | 30.874 | 187.805 | 7.63 | 176.549 | 2144.79 | 25.94 | 46.359 | 6.35 | 1.348 | 4.631 | 8662.33 | 1.992 | 97.8 | 77.5 | 1394 | 23.27 | 5630.5 | 2940.4 | 2798.2 | 4183.1 | 1198.4 | 0.68596 | 5.978
2024-12-09 | 18:14 | Data | 0 | 32.663 | 30.543 | 187.715 | 7.63 | 176.459 | 2144.79 | 25.94 | 46.54 | 6.35 | 1.343 | 4.652 | 8264.37 | 2.079 | 97.8 | 77.6 | 1394 | 23.22 | 5371.8 | 2908.4 | 2795.3 | 4155 | 1198.4 | 0.68353 | 5.996
2024-12-09 | 18:14 | Data | 0 | 32.48 | 30.637 | 187.805 | 7.63 | 176.413 | 2145.7 | 25.93 | 46.359 | 6.35 | 1.345 | 4.649 | 8264.37 | 2.073 | 97.8 | 77.6 | 1394 | 23.18 | 5371.8 | 2930.4 | 2748.1 | 4147 | 1198.4 | 0.69267 | 5.993
2024-12-09 | 18:14 | Data | 0 | 32.42 | 30.55 | 187.715 | 7.64 | 176.549 | 2144.79 | 25.94 | 46.45 | 6.35 | 1.355 | 4.672 | 8273.41 | 1.924 | 97.8 | 77.5 | 1394 | 23.27 | 5377.7 | 2926.7 | 2772.8 | 4153.2 | 1198.4 | 0.6892 | 6.026
2024-12-09 | 18:14 | Data | 0 | 32.494 | 30.415 | 187.715 | 7.63 | 176.368 | 2143.89 | 25.94 | 46.45 | 6.35 | 1.347 | 4.673 | 8273.41 | 2.079 | 97.8 | 77.6 | 1394 | 23.27 | 5377.7 | 2925.8 | 2788.3 | 4148.6 | 1198.4 | 0.68477 | 6.02
2024-12-09 | 18:14 | Data | 0 | 32.919 | 30.766 | 187.805 | 7.63 | 176.459 | 2145.7 | 25.94 | 45.998 | 6.35 | 1.342 | 4.655 | 8291.5 | 2.181 | 97.9 | 77.6 | 1394 | 22.95 | 5389.5 | 2909.3 | 2797.1 | 4157.2 | 1198.4 | 0.68289 | 5.998
2024-12-09 | 18:14 | Data | 0 | 32.507 | 30.671 | 187.76 | 7.63 | 176.368 | 2144.79 | 25.94 | 46.45 | 6.35 | 1.342 | 4.659 | 8318.64 | 1.978 | 97.8 | 77.6 | 1395 | 23.18 | 5407.1 | 2919.3 | 2769.3 | 4141.1 | 1198.4 | 0.68835 | 6.001
2024-12-09 | 18:14 | Data | 0 | 32.48 | 30.415 | 187.67 | 7.63 | 176.368 | 2144.79 | 25.92 | 46.54 | 6.35 | 1.352 | 4.663 | 8318.64 | 2.079 | 97.8 | 77.5 | 1394 | 23.22 | 5407.1 | 2923.7 | 2786.9 | 4162.2 | 1198.4 | 0.68605 | 6.015
2024-12-09 | 18:15 | Data | 0 | 32.696 | 30.651 | 187.624 | 7.63 | 176.413 | 2145.7 | 25.93 | 46.54 | 6.35 | 1.348 | 4.652 | 8314.11 | 1.951 | 97.8 | 77.5 | 1395 | 23.27 | 5404.2 | 2918.1 | 2771.8 | 4147.6 | 1198.4 | 0.6868 | 5.999
2024-12-09 | 18:15 | Data | 0 | 32.723 | 30.658 | 187.851 | 7.63 | 176.368 | 2145.7 | 25.94 | 46.54 | 6.35 | 1.348 | 4.677 | 8345.77 | 2.046 | 97.8 | 77.6 | 1395 | 23.27 | 5424.8 | 2930.1 | 2772.6 | 4150.3 | 1198.4 | 0.68908 | 6.026
2024-12-09 | 18:15 | Data | 0 | 32.777 | 30.448 | 187.851 | 7.63 | 176.594 | 2144.79 | 25.94 | 46.45 | 6.35 | 1.353 | 4.675 | 8363.86 | 2.019 | 97.8 | 77.6 | 1394 | 23.27 | 5436.5 | 2919.3 | 2774.8 | 4149.8 | 1198.4 | 0.68698 | 6.027
2024-12-09 | 18:15 | Data | 0 | 32.548 | 30.536 | 187.715 | 7.63 | 176.459 | 2143.89 | 25.93 | 46.54 | 6.35 | 1.358 | 4.641 | 8377.43 | 2.079 | 97.8 | 77.4 | 1393 | 23.27 | 5445.3 | 2927.6 | 2781.7 | 4157.7 | 1198.4 | 0.68866 | 5.998
2024-12-09 | 18:15 | Data | 0 | 32.723 | 30.651 | 187.76 | 7.63 | 176.368 | 2144.79 | 25.92 | 46.54 | 6.35 | 1.347 | 4.704 | 8359.34 | 2.066 | 97.8 | 77.7 | 1395 | 23.27 | 5433.6 | 2909.6 | 2752.3 | 4129.3 | 1198.4 | 0.68823 | 6.051
2024-12-09 | 18:15 | Data | 0 | 32.879 | 30.489 | 187.805 | 7.63 | 176.459 | 2147.51 | 25.92 | 46.54 | 6.35 | 1.358 | 4.704 | 8372.9 | 2.282 | 97.8 | 77.6 | 1396 | 23.22 | 5442.4 | 2925.3 | 2775 | 4152.9 | 1198.4 | 0.68817 | 6.063
2024-12-09 | 18:15 | Data | 0 | 32.723 | 30.759 | 187.76 | 7.63 | 176.459 | 2142.08 | 25.92 | 46.54 | 6.35 | 1.367 | 4.663 | 8386.47 | 1.857 | 97.8 | 77.3 | 1392 | 23.22 | 5451.2 | 2904.9 | 2775.4 | 4138.2 | 1198.4 | 0.68551 | 6.029
2024-12-09 | 18:15 | Data | 0 | 33.048 | 30.894 | 187.805 | 7.63 | 176.549 | 2142.08 | 25.94 | 46.54 | 6.35 | 1.358 | 4.685 | 8427.17 | 2.187 | 97.8 | 77.5 | 1393 | 23.27 | 5477.7 | 2928.3 | 2783 | 4145.6 | 1198.4 | 0.68909 | 6.043
2024-12-09 | 18:15 | Data | 0 | 32.386 | 30.502 | 187.76 | 7.63 | 176.413 | 2141.18 | 25.94 | 46.54 | 6.35 | 1.344 | 4.676 | 8440.74 | 1.877 | 97.8 | 77.7 | 1392 | 23.27 | 5486.5 | 2852.1 | 2753.5 | 4078.8 | 1198.5 | 0.68346 | 6.019
2024-12-09 | 18:15 | Data | 0 | 32.669 | 30.536 | 187.579 | 7.63 | 176.413 | 2144.79 | 25.95 | 46.54 | 6.35 | 1.353 | 4.659 | 8445.26 | 2.174 | 97.8 | 77.5 | 1394 | 23.27 | 5489.4 | 2859.8 | 2773.1 | 4099.1 | 1198.5 | 0.68319 | 6.011
2024-12-09 | 18:15 | Data | 0 | 32.919 | 30.766 | 187.76 | 7.63 | 176.549 | 2144.79 | 25.94 | 46.45 | 6.35 | 1.344 | 4.688 | 8449.78 | 2.073 | 97.8 | 77.7 | 1394 | 23.22 | 5492.4 | 2841.7 | 2785.5 | 4092.7 | 1198.5 | 0.67829 | 6.031
2024-12-09 | 18:15 | Data | 0 | 32.345 | 30.421 | 187.67 | 7.63 | 176.459 | 2143.89 | 25.92 | 46.45 | 6.35 | 1.345 | 4.656 | 8458.83 | 1.877 | 97.8 | 77.6 | 1394 | 23.22 | 5498.2 | 2836.2 | 2770.4 | 4084.6 | 1198.5 | 0.67777 | 6
2024-12-09 | 18:15 | Data | 0 | 32.507 | 30.86 | 187.715 | 7.63 | 176.368 | 2143.89 | 25.93 | 46.54 | 6.35 | 1.347 | 4.621 | 8472.39 | 1.83 | 97.8 | 77.4 | 1394 | 23.27 | 5507.1 | 2853.5 | 2770.6 | 4089.8 | 1198.5 | 0.68226 | 5.968
2024-12-09 | 18:15 | Data | 0 | 32.501 | 30.415 | 187.624 | 7.63 | 176.368 | 2141.18 | 25.92 | 46.179 | 6.35 | 1.351 | 4.671 | 8472.39 | 2.086 | 97.8 | 77.6 | 1391 | 23.13 | 5507.1 | 2867.6 | 2770.6 | 4096.8 | 1198.5 | 0.68257 | 6.022
2024-12-09 | 18:15 | Data | 0 | 32.393 | 30.421 | 187.715 | 7.63 | 176.278 | 2140.27 | 25.93 | 46.45 | 6.35 | 1.363 | 4.687 | 8472.39 | 1.877 | 97.8 | 77.5 | 1391 | 23.27 | 5507.1 | 2860.9 | 2768.5 | 4085.5 | 1198.5 | 0.68299 | 6.05
2024-12-09 | 18:15 | Data | 0 | 32.494 | 30.435 | 187.624 | 7.64 | 176.368 | 2142.99 | 25.93 | 46.45 | 6.35 | 1.359 | 4.662 | 8856.78 | 2.147 | 97.8 | 77.4 | 1393 | 23.27 | 5756.9 | 2864.4 | 2749.9 | 4079.2 | 1198.5 | 0.68479 | 6.021
2024-12-09 | 18:16 | Data | 0 | 32.994 | 30.664 | 187.851 | 7.63 | 176.594 | 2141.18 | 25.92 | 46.54 | 6.34 | 1.352 | 4.67 | 8599.01 | 2.106 | 97.8 | 77.5 | 1392 | 23.27 | 5589.4 | 2877 | 2770.2 | 4106.2 | 1198.5 | 0.68535 | 6.022
2024-12-09 | 18:16 | Data | 0 | 32.494 | 30.536 | 187.624 | 7.63 | 176.413 | 2142.08 | 25.93 | 46.179 | 6.35 | 1.351 | 4.66 | 8508.57 | 1.877 | 97.8 | 77.5 | 1392 | 23.18 | 5530.6 | 2895.2 | 2778.1 | 4132 | 1198.5 | 0.68444 | 6.012
2024-12-09 | 18:16 | Data | 0 | 32.474 | 30.847 | 187.715 | 7.63 | 176.368 | 2142.08 | 25.92 | 46.269 | 6.35 | 1.358 | 4.666 | 8513.09 | 2.12 | 97.8 | 77.5 | 1392 | 23.09 | 5533.5 | 2916.4 | 2770.7 | 4136.7 | 1198.5 | 0.68756 | 6.024
2024-12-09 | 18:16 | Data | 0 | 32.804 | 30.482 | 187.67 | 7.63 | 176.549 | 2142.08 | 25.93 | 46.179 | 6.35 | 1.353 | 4.677 | 8472.39 | 2.093 | 97.8 | 77.6 | 1392 | 23.09 | 5507.1 | 2909.1 | 2784.5 | 4149.8 | 1198.5 | 0.68472 | 6.032
2024-12-09 | 18:16 | Data | 0 | 32.494 | 30.624 | 187.624 | 7.63 | 176.323 | 2142.08 | 25.93 | 46.269 | 6.35 | 1.351 | 4.666 | 8467.87 | 2.073 | 97.8 | 77.5 | 1393 | 23.09 | 5504.1 | 2899.4 | 2807.4 | 4151 | 1198.5 | 0.68389 | 6.017
2024-12-09 | 18:16 | Data | 0 | 32.447 | 30.415 | 187.805 | 7.63 | 176.323 | 2139.37 | 25.93 | 46.179 | 6.35 | 1.348 | 4.653 | 8481.44 | 2.052 | 97.8 | 77.5 | 1391 | 23.13 | 5512.9 | 2922.5 | 2814.7 | 4173.4 | 1198.5 | 0.68408 | 6
2024-12-09 | 18:16 | Data | 0 | 32.332 | 30.705 | 187.715 | 7.63 | 176.323 | 2140.27 | 25.93 | 46.179 | 6.35 | 1.349 | 4.664 | 8481.44 | 1.904 | 97.8 | 77.6 | 1391 | 23.13 | 5512.9 | 2906.6 | 2783.7 | 4142.6 | 1198.5 | 0.68637 | 6.014
2024-12-09 | 18:16 | Data | 0 | 32.69 | 30.529 | 187.67 | 7.63 | 176.413 | 2138.47 | 25.93 | 46.269 | 6.35 | 1.345 | 4.688 | 8508.57 | 2.066 | 97.8 | 77.7 | 1392 | 23.09 | 5530.6 | 2896.7 | 2769 | 4124.5 | 1198.5 | 0.68627 | 6.032
2024-12-09 | 18:16 | Data | 0 | 32.609 | 30.806 | 187.67 | 7.63 | 176.323 | 2139.37 | 25.92 | 46.179 | 6.35 | 1.34 | 4.664 | 8495 | 2.079 | 97.8 | 77.7 | 1391 | 23.18 | 5521.8 | 2902.8 | 2794.7 | 4151.4 | 1198.5 | 0.68276 | 6.005
2024-12-09 | 18:16 | Data | 0 | 32.379 | 30.415 | 187.579 | 7.63 | 176.368 | 2142.08 | 25.91 | 46.269 | 6.35 | 1.342 | 4.684 | 8495 | 2.066 | 97.8 | 77.7 | 1393 | 23.09 | 5521.8 | 2899.2 | 2769 | 4127.9 | 1198.5 | 0.68631 | 6.028
2024-12-09 | 18:16 | Data | 0 | 32.514 | 30.59 | 187.851 | 7.63 | 176.368 | 2144.79 | 25.93 | 46.359 | 6.35 | 1.356 | 4.681 | 8485.96 | 1.958 | 97.8 | 77.5 | 1394 | 23.13 | 5515.9 | 2920.5 | 2769.7 | 4146.4 | 1198.5 | 0.68889 | 6.037
2024-12-09 | 18:16 | Data | 0 | 32.723 | 30.428 | 187.67 | 7.63 | 176.413 | 2143.89 | 25.94 | 46.179 | 6.35 | 1.347 | 4.684 | 8517.61 | 2.1 | 97.9 | 77.7 | 1394 | 23.09 | 5536.4 | 2909.9 | 2780.7 | 4145.7 | 1198.5 | 0.68592 | 6.031
2024-12-09 | 18:16 | Data | 0 | 32.494 | 30.415 | 187.534 | 7.63 | 176.323 | 2144.79 | 25.93 | 45.998 | 6.35 | 1.358 | 4.675 | 8522.14 | 2.079 | 97.9 | 77.5 | 1394 | 23 | 5539.4 | 2924.3 | 2786.2 | 4156.8 | 1198.5 | 0.68598 | 6.032
2024-12-09 | 18:16 | Data | 0 | 32.494 | 30.732 | 187.805 | 7.63 | 176.459 | 2144.79 | 25.93 | 46.179 | 6.35 | 1.36 | 4.687 | 8526.66 | 1.978 | 97.8 | 77.5 | 1394 | 23.09 | 5542.3 | 2896.3 | 2776.7 | 4130.3 | 1198.5 | 0.68485 | 6.047
2024-12-09 | 18:16 | Data | 0 | 32.285 | 30.509 | 187.489 | 7.63 | 176.278 | 2142.99 | 25.92 | 46.269 | 6.35 | 1.352 | 4.667 | 8531.18 | 1.87 | 97.8 | 77.5 | 1393 | 23.09 | 5545.3 | 2905.3 | 2786 | 4145.5 | 1198.5 | 0.68446 | 6.019
2024-12-09 | 18:16 | Data | 0 | 32.494 | 30.442 | 187.579 | 7.63 | 176.323 | 2144.79 | 25.93 | 46.269 | 6.36 | 1.342 | 4.662 | 8522.14 | 2.005 | 97.8 | 77.6 | 1394 | 23.13 | 5539.4 | 2897.7 | 2780.1 | 4139.1 | 1198.5 | 0.6819 | 6.003
2024-12-09 | 18:16 | Data | 0 | 32.575 | 30.428 | 187.76 | 7.63 | 176.368 | 2148.41 | 25.93 | 46.179 | 6.34 | 1.341 | 4.656 | 8513.09 | 1.904 | 97.9 | 77.6 | 1396 | 23.09 | 5533.5 | 2906.9 | 2791.2 | 4151.3 | 1198.5 | 0.68306 | 5.997
2024-12-09 | 18:16 | Data | 0 | 32.879 | 30.489 | 187.624 | 7.63 | 176.368 | 2147.51 | 25.93 | 46.269 | 6.34 | 1.355 | 4.645 | 8508.57 | 2.214 | 97.8 | 77.4 | 1395 | 23.13 | 5530.6 | 2905.3 | 2822.7 | 4169 | 1198.5 | 0.67873 | 5.999
2024-12-09 | 18:17 | Data | 0 | 32.44 | 30.624 | 187.579 | 7.63 | 176.323 | 2146.6 | 25.93 | 46.179 | 6.35 | 1.351 | 4.664 | 8517.61 | 2.059 | 97.8 | 77.5 | 1396 | 23.09 | 5536.4 | 2895 | 2777.8 | 4132.5 | 1198.5 | 0.68299 | 6.015
2024-12-09 | 18:17 | Data | 0 | 32.494 | 30.415 | 187.579 | 7.63 | 176.323 | 2147.51 | 25.92 | 46.179 | 6.36 | 1.342 | 4.654 | 8513.09 | 1.877 | 97.8 | 77.6 | 1396 | 23.13 | 5533.5 | 2909.5 | 2782.1 | 4142.3 | 1198.5 | 0.68515 | 5.997
2024-12-09 | 18:17 | Data | 0 | 32.561 | 30.3 | 187.67 | 7.63 | 176.368 | 2147.51 | 25.92 | 46.269 | 6.35 | 1.343 | 4.653 | 8513.09 | 1.992 | 97.8 | 77.6 | 1396 | 23.13 | 5533.5 | 2897 | 2799.1 | 4145 | 1198.5 | 0.68349 | 5.997
2024-12-09 | 18:17 | Data | 0 | 32.494 | 30.469 | 187.67 | 7.63 | 176.413 | 2147.51 | 25.94 | 46.721 | 6.35 | 1.352 | 4.647 | 8522.14 | 1.863 | 97.8 | 77.5 | 1396 | 23.36 | 5539.4 | 2886.3 | 2780.8 | 4126.7 | 1198.5 | 0.6831 | 5.998
2024-12-09 | 18:17 | Data | 0 | 32.379 | 30.415 | 187.534 | 7.63 | 176.233 | 2147.51 | 25.92 | 46.179 | 6.35 | 1.357 | 4.654 | 8513.09 | 2.073 | 97.8 | 77.4 | 1396 | 23.13 | 5533.5 | 2904.1 | 2788.1 | 4146.5 | 1198.5 | 0.68292 | 6.012
2024-12-09 | 18:17 | Data | 0 | 32.669 | 30.482 | 187.76 | 7.63 | 176.459 | 2147.51 | 25.94 | 46.269 | 6.35 | 1.354 | 4.645 | 8526.66 | 2.14 | 97.8 | 77.5 | 1396 | 23.13 | 5542.3 | 2909.2 | 2786 | 4149 | 1198.5 | 0.68545 | 5.997
2024-12-09 | 18:17 | Data | 0 | 32.393 | 30.192 | 187.489 | 7.63 | 176.323 | 2144.79 | 25.94 | 46.269 | 6.34 | 1.341 | 4.645 | 8513.09 | 1.911 | 97.8 | 77.6 | 1394 | 23.13 | 5533.5 | 2889.8 | 2790.1 | 4132.8 | 1198.5 | 0.68274 | 5.987
2024-12-09 | 18:17 | Data | 0 | 32.494 | 30.59 | 187.579 | 7.63 | 176.323 | 2141.18 | 25.95 | 46.179 | 6.35 | 1.348 | 4.624 | 8513.09 | 2.079 | 97.8 | 77.4 | 1392 | 23.13 | 5533.5 | 2889.9 | 2801.4 | 4141.1 | 1198.5 | 0.68149 | 5.972
2024-12-09 | 18:17 | Data | 0 | 32.656 | 30.705 | 187.67 | 7.63 | 176.368 | 2139.37 | 25.94 | 46.269 | 6.35 | 1.354 | 4.646 | 8499.53 | 2.073 | 97.8 | 77.4 | 1391 | 23.09 | 5524.7 | 2912.5 | 2792.9 | 4150.9 | 1198.5 | 0.68542 | 6
2024-12-09 | 18:17 | Data | 0 | 32.494 | 30.415 | 187.624 | 7.63 | 176.323 | 2139.37 | 25.96 | 46.269 | 6.35 | 1.356 | 4.657 | 8467.87 | 2.133 | 97.8 | 77.5 | 1391 | 23.13 | 5504.1 | 2910.8 | 2806.1 | 4158.7 | 1198.5 | 0.68371 | 6.012
2024-12-09 | 18:17 | Data | 0 | 32.521 | 30.469 | 187.624 | 7.63 | 176.413 | 2136.66 | 25.96 | 46.179 | 6.35 | 1.351 | 4.679 | 8454.3 | 1.884 | 97.8 | 77.6 | 1389 | 23.04 | 5495.3 | 2901.7 | 2800.8 | 4148.4 | 1198.6 | 0.68252 | 6.032
2024-12-09 | 18:17 | Data | 0 | 32.366 | 30.415 | 187.579 | 7.63 | 176.368 | 2137.56 | 25.96 | 46.179 | 6.35 | 1.344 | 4.654 | 8440.74 | 1.749 | 97.8 | 77.6 | 1389 | 23.13 | 5486.5 | 2901.3 | 2802.3 | 4151.5 | 1198.6 | 0.68123 | 5.998
2024-12-09 | 18:17 | Data | 0 | 32.777 | 30.556 | 187.715 | 7.63 | 176.549 | 2137.56 | 25.97 | 46.179 | 6.34 | 1.345 | 4.643 | 8445.26 | 2.059 | 97.8 | 77.5 | 1389 | 23.13 | 5489.4 | 2902.5 | 2793.7 | 4148.4 | 1198.6 | 0.68408 | 5.989
2024-12-09 | 18:17 | Data | 0 | 32.285 | 30.469 | 187.489 | 7.63 | 176.278 | 2131.24 | 25.96 | 46.269 | 6.35 | 1.354 | 4.654 | 8458.83 | 1.85 | 97.8 | 77.5 | 1385 | 23.13 | 5498.2 | 2881.1 | 2776.6 | 4117.8 | 1198.6 | 0.68472 | 6.008
2024-12-09 | 18:17 | Data | 0 | 32.879 | 30.543 | 187.715 | 7.63 | 176.413 | 2133.95 | 25.96 | 46.269 | 6.35 | 1.338 | 4.652 | 8558.31 | 2.093 | 97.8 | 77.7 | 1386 | 23.13 | 5562.9 | 2913.2 | 2792 | 4146.9 | 1198.6 | 0.68699 | 5.99
2024-12-09 | 18:17 | Data | 0 | 32.42 | 30.766 | 187.805 | 7.63 | 176.413 | 2137.56 | 25.94 | 46.179 | 6.35 | 1.347 | 4.636 | 8540.22 | 1.803 | 97.8 | 77.5 | 1389 | 23.09 | 5551.1 | 2901.7 | 2774.1 | 4131.1 | 1198.6 | 0.68447 | 5.984
2024-12-09 | 18:17 | Data | 0 | 32.494 | 30.624 | 187.67 | 7.63 | 176.368 | 2136.66 | 25.96 | 46.179 | 6.35 | 1.354 | 4.635 | 8517.61 | 2.079 | 97.8 | 77.4 | 1389 | 23.09 | 5536.4 | 2916.6 | 2779.7 | 4139.2 | 1198.6 | 0.68288 | 5.988
2024-12-09 | 18:18 | Data | 0 | 32.723 | 30.651 | 187.715 | 7.63 | 176.413 | 2136.66 | 25.96 | 46.359 | 6.35 | 1.351 | 4.667 | 8544.75 | 2.073 | 97.8 | 77.6 | 1389 | 23.18 | 5554.1 | 2897 | 2796.4 | 4146.7 | 1198.6 | 0.68177 | 6.016
2024-12-09 | 18:18 | Data | 0 | 32.595 | 30.921 | 187.76 | 7.63 | 176.459 | 2136.66 | 25.95 | 46.269 | 6.35 | 1.348 | 4.645 | 8513.09 | 1.985 | 97.8 | 77.5 | 1389 | 23.13 | 5533.5 | 2893.4 | 2798.6 | 4140.3 | 1198.6 | 0.68287 | 5.993
2024-12-09 | 18:18 | Data | 0 | 32.561 | 30.543 | 187.67 | 7.63 | 176.459 | 2134.85 | 25.96 | 46.269 | 6.35 | 1.34 | 4.645 | 8513.09 | 2.079 | 97.8 | 77.6 | 1388 | 23.13 | 5533.5 | 2896.5 | 2786.3 | 4125.7 | 1198.6 | 0.6833 | 5.986
2024-12-09 | 18:18 | Data | 0 | 32.494 | 30.415 | 187.624 | 7.63 | 176.142 | 2133.95 | 25.96 | 46.359 | 6.35 | 1.349 | 4.646 | 8535.7 | 2.039 | 97.8 | 77.5 | 1388 | 23.09 | 5548.2 | 2908 | 2797.5 | 4151.9 | 1198.6 | 0.68375 | 5.998
2024-12-09 | 18:18 | Data | 0 | 32.933 | 30.766 | 187.851 | 7.63 | 176.594 | 2132.14 | 25.96 | 46.269 | 6.35 | 1.345 | 4.662 | 8531.18 | 2.1 | 97.8 | 77.6 | 1386 | 23.13 | 5545.3 | 2897.7 | 2795.3 | 4144.3 | 1198.6 | 0.68236 | 6.007
2024-12-09 | 18:18 | Data | 0 | 32.514 | 30.462 | 187.67 | 7.63 | 176.459 | 2133.95 | 25.96 | 46.089 | 6.35 | 1.352 | 4.659 | 8549.27 | 2.032 | 97.8 | 77.5 | 1387 | 23.09 | 5557 | 2905.7 | 2799.2 | 4145.8 | 1198.6 | 0.6839 | 6.011
2024-12-09 | 18:18 | Data | 0 | 32.494 | 30.374 | 187.76 | 7.63 | 176.323 | 2136.66 | 25.97 | 46.269 | 6.35 | 1.355 | 4.645 | 8535.7 | 2.16 | 97.8 | 77.4 | 1389 | 23.13 | 5548.2 | 2890.8 | 2819.9 | 4152.6 | 1198.6 | 0.68025 | 5.999
2024-12-09 | 18:18 | Data | 0 | 32.609 | 30.482 | 187.67 | 7.63 | 176.413 | 2139.37 | 25.95 | 46.269 | 6.35 | 1.355 | 4.617 | 8544.75 | 2.248 | 97.8 | 77.3 | 1391 | 23.13 | 5554.1 | 2895.2 | 2814.6 | 4153.8 | 1198.6 | 0.68004 | 5.972
2024-12-09 | 18:18 | Data | 0 | 32.636 | 30.421 | 187.805 | 7.64 | 176.459 | 2140.27 | 25.96 | 46.54 | 6.35 | 1.346 | 4.648 | 8513.09 | 1.911 | 97.8 | 77.5 | 1392 | 23.22 | 5533.5 | 2888.8 | 2813.5 | 4149.8 | 1198.6 | 0.68137 | 5.994
2024-12-09 | 18:18 | Data | 0 | 32.602 | 30.421 | 187.579 | 7.63 | 176.368 | 2140.27 | 25.96 | 46.45 | 6.35 | 1.339 | 4.648 | 8703.03 | 1.904 | 97.8 | 77.6 | 1391 | 23.27 | 5657 | 2895.4 | 2829.7 | 4164.4 | 1198.6 | 0.67875 | 5.988
2024-12-09 | 18:18 | Data | 0 | 32.278 | 30.637 | 187.67 | 7.63 | 176.368 | 2142.08 | 25.97 | 46.179 | 6.35 | 1.344 | 4.668 | 8277.94 | 2.039 | 97.8 | 77.6 | 1393 | 23.09 | 5380.7 | 2907.8 | 2794.7 | 4148.9 | 1198.6 | 0.68499 | 6.012
2024-12-09 | 18:18 | Data | 0 | 32.717 | 30.651 | 187.624 | 7.63 | 176.368 | 2143.89 | 25.95 | 46.179 | 6.35 | 1.345 | 4.654 | 8924.61 | 2.066 | 97.8 | 77.6 | 1394 | 23.09 | 5801 | 2900.1 | 2795.9 | 4144.2 | 1198.6 | 0.68313 | 5.998
2024-12-09 | 18:18 | Data | 0 | 32.595 | 30.651 | 187.579 | 7.63 | 176.413 | 2147.51 | 25.95 | 46.269 | 6.35 | 1.337 | 4.676 | 8911.05 | 2.059 | 97.8 | 77.8 | 1396 | 23.04 | 5792.2 | 2922.7 | 2796.8 | 4163.5 | 1198.6 | 0.68519 | 6.013
2024-12-09 | 18:18 | Data | 0 | 32.717 | 30.867 | 187.67 | 7.63 | 176.368 | 2148.41 | 25.96 | 46.269 | 6.35 | 1.354 | 4.667 | 8693.98 | 1.877 | 97.8 | 77.5 | 1395 | 23.09 | 5651.1 | 2903 | 2814.7 | 4161.3 | 1198.6 | 0.68354 | 6.021
2024-12-09 | 18:18 | Data | 0 | 32.494 | 30.637 | 187.534 | 7.63 | 176.368 | 2149.31 | 25.94 | 46.269 | 6.35 | 1.355 | 4.662 | 8698.5 | 1.971 | 97.9 | 77.5 | 1399 | 23.13 | 5654 | 2876.1 | 2782.4 | 4120.5 | 1198.6 | 0.68098 | 6.016
2024-12-09 | 18:18 | Data | 0 | 32.507 | 30.421 | 187.624 | 7.63 | 176.368 | 2152.93 | 25.94 | 46.269 | 6.35 | 1.352 | 4.676 | 8666.85 | 2.079 | 97.9 | 77.6 | 1399 | 23.09 | 5633.5 | 2893.3 | 2814.6 | 4151.1 | 1198.6 | 0.68461 | 6.028
2024-12-09 | 18:18 | Data | 0 | 32.494 | 30.502 | 187.579 | 7.63 | 176.323 | 2152.93 | 25.95 | 46.179 | 6.35 | 1.343 | 4.656 | 8653.28 | 2.133 | 97.9 | 77.6 | 1399 | 23.09 | 5624.6 | 2896.7 | 2812.9 | 4155.9 | 1198.6 | 0.6796 | 5.999
2024-12-09 | 18:18 | Data | 0 | 33.021 | 30.786 | 187.805 | 7.63 | 176.413 | 2152.93 | 25.96 | 45.998 | 6.35 | 1.339 | 4.645 | 8648.76 | 2.147 | 97.9 | 77.6 | 1399 | 23.13 | 5621.7 | 2895.1 | 2802.6 | 4146.8 | 1198.6 | 0.68181 | 5.981
2024-12-09 | 18:19 | Data | 0 | 32.71 | 30.442 | 187.534 | 7.63 | 176.278 | 2152.93 | 25.94 | 46.269 | 6.35 | 1.335 | 4.664 | 8630.67 | 2.079 | 97.9 | 77.7 | 1399 | 23.09 | 5609.9 | 2869.7 | 2798.4 | 4130.3 | 1198.6 | 0.6773 | 5.999
2024-12-09 | 18:19 | Data | 0 | 32.831 | 30.421 | 187.579 | 7.63 | 176.459 | 2151.12 | 25.96 | 46.811 | 6.35 | 1.334 | 4.641 | 8639.71 | 2.214 | 97.8 | 77.7 | 1398 | 23.5 | 5615.8 | 2900.4 | 2777.9 | 4135.3 | 1198.6 | 0.68506 | 5.975
2024-12-09 | 18:19 | Data | 0 | 32.737 | 30.475 | 187.76 | 7.63 | 176.413 | 2152.02 | 25.95 | 46.269 | 6.35 | 1.354 | 4.654 | 8621.63 | 2.046 | 97.8 | 77.5 | 1398 | 23.13 | 5604.1 | 2914.5 | 2791.2 | 4147.5 | 1198.6 | 0.68548 | 6.008
2024-12-09 | 18:19 | Data | 0 | 32.271 | 30.415 | 187.624 | 7.63 | 176.368 | 2152.93 | 25.95 | 46.179 | 6.35 | 1.347 | 4.676 | 8626.15 | 1.85 | 97.9 | 77.6 | 1400 | 23.09 | 5607 | 2902.1 | 2772.8 | 4128.5 | 1198.6 | 0.68637 | 6.022
2024-12-09 | 18:19 | Data | 0 | 32.332 | 30.334 | 187.624 | 7.63 | 176.368 | 2153.83 | 25.96 | 46.269 | 6.35 | 1.345 | 4.662 | 8612.58 | 1.944 | 97.9 | 77.6 | 1400 | 23.13 | 5598.2 | 2899.7 | 2767.3 | 4124.8 | 1198.6 | 0.68463 | 6.007
2024-12-09 | 18:19 | Data | 0 | 32.467 | 30.624 | 187.67 | 7.63 | 176.368 | 2149.31 | 25.95 | 46.269 | 6.35 | 1.348 | 4.654 | 8608.06 | 2.012 | 97.8 | 77.5 | 1398 | 23.13 | 5595.2 | 2889.6 | 2779.9 | 4128.7 | 1198.6 | 0.68519 | 6.004
2024-12-09 | 18:19 | Data | 0 | 32.494 | 30.516 | 187.624 | 7.63 | 176.413 | 2151.12 | 25.96 | 46.45 | 6.35 | 1.348 | 4.675 | 8571.88 | 2.039 | 97.8 | 77.6 | 1397 | 23.18 | 5571.7 | 2896.2 | 2766.3 | 4120.6 | 1198.6 | 0.6863 | 6.024
2024-12-09 | 18:19 | Data | 0 | 32.717 | 30.651 | 187.67 | 7.63 | 176.413 | 2152.02 | 25.94 | 46.54 | 6.35 | 1.346 | 4.675 | 8567.36 | 2.073 | 97.8 | 77.6 | 1397 | 23.27 | 5568.8 | 2881.3 | 2781.4 | 4123.4 | 1198.6 | 0.68446 | 6.022
2024-12-09 | 18:19 | Data | 0 | 32.386 | 30.415 | 187.624 | 7.63 | 176.459 | 2146.6 | 25.97 | 46.54 | 6.35 | 1.344 | 4.633 | 8567.36 | 1.863 | 97.8 | 77.5 | 1396 | 23.32 | 5568.8 | 2894.8 | 2798.1 | 4145.4 | 1198.6 | 0.68178 | 5.977
2024-12-09 | 18:19 | Data | 0 | 32.696 | 30.644 | 187.67 | 7.63 | 176.413 | 2151.12 | 25.94 | 46.359 | 6.35 | 1.352 | 4.658 | 8553.79 | 2.066 | 97.8 | 77.5 | 1398 | 23.13 | 5560 | 2895.5 | 2762.6 | 4120.6 | 1198.6 | 0.68564 | 6.011
2024-12-09 | 18:19 | Data | 0 | 32.555 | 30.82 | 187.941 | 7.63 | 176.549 | 2149.31 | 25.96 | 46.269 | 6.35 | 1.352 | 4.635 | 8522.14 | 1.884 | 97.8 | 77.4 | 1397 | 23.09 | 5539.4 | 2888.3 | 2786.5 | 4126.5 | 1198.6 | 0.6828 | 5.987
2024-12-09 | 18:19 | Data | 0 | 32.285 | 30.475 | 187.67 | 7.63 | 176.368 | 2149.31 | 25.95 | 46.45 | 6.35 | 1.346 | 4.624 | 8526.66 | 2.025 | 97.8 | 77.5 | 1398 | 23.18 | 5542.3 | 2901 | 2789.6 | 4139.3 | 1198.6 | 0.68322 | 5.97
2024-12-09 | 18:19 | Data | 0 | 32.717 | 30.469 | 187.715 | 7.63 | 176.413 | 2149.31 | 25.95 | 46.45 | 6.35 | 1.346 | 4.655 | 8513.09 | 2.025 | 97.8 | 77.6 | 1397 | 23.27 | 5533.5 | 2903.4 | 2806.6 | 4153 | 1198.7 | 0.68273 | 6.001
2024-12-09 | 18:19 | Data | 0 | 32.507 | 30.59 | 187.624 | 7.63 | 176.323 | 2151.12 | 25.96 | 46.359 | 6.35 | 1.358 | 4.665 | 8499.53 | 1.958 | 97.8 | 77.5 | 1398 | 23.18 | 5524.7 | 2905.8 | 2789.5 | 4149.6 | 1198.7 | 0.68368 | 6.022
2024-12-09 | 18:19 | Data | 0 | 32.582 | 30.88 | 187.715 | 7.63 | 176.459 | 2151.12 | 25.94 | 46.359 | 6.35 | 1.349 | 4.652 | 8495 | 2.032 | 97.8 | 77.5 | 1398 | 23.18 | 5521.8 | 2917.9 | 2780.1 | 4139.7 | 1198.7 | 0.6889 | 6.002
2024-12-09 | 18:19 | Data | 0 | 32.838 | 30.536 | 187.76 | 7.63 | 176.549 | 2151.12 | 25.95 | 46.359 | 6.35 | 1.348 | 4.659 | 8495 | 1.931 | 97.8 | 77.6 | 1398 | 23.22 | 5521.8 | 2913.8 | 2797.7 | 4156.3 | 1198.7 | 0.68427 | 6.006
2024-12-09 | 18:19 | Data | 0 | 32.71 | 30.624 | 187.805 | 7.63 | 176.323 | 2151.12 | 25.96 | 46.45 | 6.35 | 1.352 | 4.687 | 8499.53 | 2.127 | 97.8 | 77.6 | 1398 | 23.13 | 5524.7 | 2888.7 | 2807.7 | 4145.1 | 1198.7 | 0.68019 | 6.039
2024-12-09 | 18:19 | Data | 0 | 32.285 | 30.421 | 187.76 | 7.63 | 176.594 | 2148.41 | 25.94 | 46.54 | 6.35 | 1.348 | 4.673 | 8481.44 | 2.019 | 97.8 | 77.6 | 1397 | 23.22 | 5512.9 | 2887.1 | 2792.7 | 4135.7 | 1198.7 | 0.68172 | 6.019
2024-12-09 | 18:20 | Data | 0 | 32.723 | 30.867 | 187.805 | 7.63 | 176.549 | 2149.31 | 25.96 | 46.63 | 6.35 | 1.342 | 4.68 | 8485.96 | 1.87 | 97.8 | 77.7 | 1397 | 23.22 | 5515.9 | 2891.6 | 2776.7 | 4125.7 | 1198.7 | 0.68365 | 6.023
2024-12-09 | 18:20 | Data | 0 | 32.609 | 30.529 | 187.624 | 7.63 | 176.413 | 2151.12 | 25.93 | 46.54 | 6.34 | 1.347 | 4.67 | 8485.96 | 1.944 | 97.8 | 77.6 | 1398 | 23.22 | 5515.9 | 2904.9 | 2799.2 | 4152.4 | 1198.7 | 0.68242 | 6.017
2024-12-09 | 18:20 | Data | 0 | 32.494 | 30.847 | 187.805 | 7.63 | 176.368 | 2149.31 | 25.96 | 46.54 | 6.35 | 1.351 | 4.681 | 8485.96 | 2.005 | 97.8 | 77.6 | 1397 | 23.27 | 5515.9 | 2897.3 | 2810.6 | 4150.2 | 1198.7 | 0.68179 | 6.033
2024-12-09 | 18:20 | Data | 0 | 32.298 | 30.415 | 187.715 | 7.63 | 176.459 | 2144.79 | 25.96 | 46.45 | 6.35 | 1.351 | 4.666 | 8485.96 | 1.857 | 97.8 | 77.5 | 1394 | 23.27 | 5515.9 | 2896 | 2815.6 | 4158.8 | 1198.7 | 0.67887 | 6.017
2024-12-09 | 18:20 | Data | 0 | 32.561 | 30.752 | 187.579 | 7.63 | 176.323 | 2149.31 | 25.96 | 46.45 | 6.35 | 1.344 | 4.677 | 8490.48 | 1.985 | 97.8 | 77.7 | 1398 | 23.27 | 5518.8 | 2885.5 | 2769.8 | 4113 | 1198.7 | 0.68305 | 6.023
2024-12-09 | 18:20 | Data | 0 | 32.494 | 30.631 | 187.624 | 7.63 | 176.413 | 2151.12 | 25.94 | 46.45 | 6.35 | 1.348 | 4.662 | 8467.87 | 1.931 | 97.8 | 77.6 | 1398 | 23.27 | 5504.1 | 2900.2 | 2756 | 4110.5 | 1198.7 | 0.68583 | 6.008
2024-12-09 | 18:20 | Data | 0 | 32.75 | 30.428 | 187.715 | 7.63 | 176.549 | 2149.31 | 25.96 | 46.45 | 6.35 | 1.351 | 4.672 | 8467.87 | 2.147 | 97.8 | 77.6 | 1398 | 23.22 | 5504.1 | 2897.7 | 2777.5 | 4129.8 | 1198.7 | 0.6866 | 6.023
2024-12-09 | 18:20 | Data | 0 | 32.521 | 30.651 | 187.715 | 7.63 | 176.459 | 2152.93 | 25.95 | 46.54 | 6.35 | 1.341 | 4.667 | 8467.87 | 1.85 | 97.8 | 77.7 | 1397 | 23.27 | 5504.1 | 2888.5 | 2774.9 | 4121 | 1198.7 | 0.68488 | 6.008
2024-12-09 | 18:20 | Data | 0 | 32.771 | 30.678 | 187.76 | 7.63 | 176.413 | 2149.31 | 25.96 | 46.45 | 6.35 | 1.345 | 4.662 | 8472.39 | 1.843 | 97.8 | 77.6 | 1398 | 23.27 | 5507.1 | 2889 | 2756.7 | 4114.8 | 1198.7 | 0.68635 | 6.007
2024-12-09 | 18:20 | Data | 0 | 32.494 | 30.793 | 187.715 | 7.63 | 176.413 | 2149.31 | 25.96 | 46.54 | 6.35 | 1.348 | 4.669 | 8454.3 | 1.958 | 97.8 | 77.6 | 1395 | 23.27 | 5495.3 | 2902.8 | 2772.5 | 4128.2 | 1198.7 | 0.68735 | 6.016
2024-12-09 | 18:20 | Data | 0 | 32.555 | 30.806 | 187.715 | 7.63 | 176.549 | 2151.12 | 25.96 | 46.45 | 6.35 | 1.348 | 4.672 | 8454.3 | 2.066 | 97.8 | 77.6 | 1398 | 23.22 | 5495.3 | 2894.4 | 2755.4 | 4111.8 | 1198.7 | 0.68768 | 6.019
2024-12-09 | 18:20 | Data | 0 | 32.71 | 30.651 | 187.805 | 7.63 | 176.413 | 2151.12 | 25.95 | 46.45 | 6.35 | 1.354 | 4.672 | 8454.3 | 2.073 | 97.8 | 77.5 | 1396 | 23.27 | 5495.3 | 2890.7 | 2785.4 | 4132.1 | 1198.7 | 0.68342 | 6.026
2024-12-09 | 18:20 | Data | 0 | 32.501 | 30.536 | 187.715 | 7.63 | 176.459 | 2032.72 | 25.96 | 46.54 | 6.35 | 1.343 | 4.653 | 8467.87 | 2.073 | 97.7 | 77.6 | 1321 | 23.22 | 5504.1 | 2906.2 | 2786.1 | 4136.8 | 1198.7 | 0.6877 | 5.996
2024-12-09 | 18:20 | Data | 0 | 32.271 | 30.536 | 187.579 | 7.63 | 176.549 | 2030.01 | 25.93 | 46.54 | 6.35 | 1.348 | 4.659 | 8490.48 | 2.14 | 97.7 | 77.6 | 1319 | 23.22 | 5518.8 | 2873.9 | 2783.7 | 4115.1 | 1198.7 | 0.6829 | 6.007
2024-12-09 | 18:20 | Data | 0 | 32.528 | 30.536 | 187.76 | 7.63 | 176.549 | 2133.95 | 25.95 | 46.45 | 6.35 | 1.351 | 4.658 | 8485.96 | 1.965 | 97.8 | 77.5 | 1387 | 23.27 | 5515.9 | 2903 | 2792.5 | 4144.2 | 1198.7 | 0.68359 | 6.009
2024-12-09 | 18:20 | Data | 0 | 32.541 | 30.529 | 187.76 | 7.63 | 176.368 | 2134.85 | 25.94 | 46.45 | 6.35 | 1.346 | 4.647 | 8495 | 1.863 | 97.8 | 77.5 | 1387 | 23.22 | 5521.8 | 2889.5 | 2816.7 | 4153.9 | 1198.7 | 0.67831 | 5.993
2024-12-09 | 18:20 | Data | 0 | 32.933 | 30.88 | 187.76 | 7.63 | 176.459 | 2145.7 | 25.95 | 46.63 | 6.35 | 1.34 | 4.654 | 8508.57 | 1.958 | 97.8 | 77.6 | 1395 | 23.32 | 5530.6 | 2909.9 | 2812.2 | 4160.9 | 1198.7 | 0.68261 | 5.995
2024-12-09 | 18:20 | Data | 0 | 32.48 | 30.428 | 187.579 | 7.63 | 176.413 | 2151.12 | 25.96 | 46.45 | 6.35 | 1.344 | 4.654 | 8495 | 2.221 | 97.8 | 77.6 | 1398 | 23.18 | 5521.8 | 2897.8 | 2789.2 | 4140.7 | 1198.7 | 0.68441 | 5.998
2024-12-09 | 18:21 | Data | 0 | 33.108 | 30.496 | 187.76 | 7.63 | 176.549 | 2152.02 | 25.94 | 46.54 | 6.35 | 1.348 | 4.658 | 8495 | 2.127 | 97.8 | 77.6 | 1397 | 23.22 | 5521.8 | 2884.1 | 2764.9 | 4114.5 | 1198.7 | 0.6847 | 6.007
2024-12-09 | 18:21 | Data | 0 | 32.494 | 30.428 | 187.624 | 7.63 | 176.459 | 2151.12 | 25.97 | 46.54 | 6.35 | 1.354 | 4.667 | 8495 | 2.032 | 97.8 | 77.5 | 1398 | 23.27 | 5521.8 | 2903.6 | 2778.9 | 4133 | 1198.7 | 0.68581 | 6.019
2024-12-09 | 18:21 | Data | 0 | 32.494 | 30.637 | 187.534 | 7.63 | 176.368 | 2151.12 | 25.95 | 46.45 | 6.35 | 1.352 | 4.671 | 8490.48 | 1.985 | 97.8 | 77.6 | 1398 | 23.27 | 5518.8 | 2890.6 | 2772.6 | 4121.5 | 1198.7 | 0.68555 | 6.021
2024-12-09 | 18:21 | Data | 0 | 32.663 | 30.469 | 187.624 | 7.63 | 176.368 | 2149.31 | 25.96 | 46.45 | 6.35 | 1.349 | 4.658 | 8485.96 | 2.079 | 97.8 | 77.5 | 1398 | 23.22 | 5515.9 | 2901.8 | 2777.3 | 4136.5 | 1198.7 | 0.68491 | 6.008
2024-12-09 | 18:21 | Data | 0 | 32.696 | 30.442 | 187.579 | 7.63 | 176.368 | 2153.83 | 25.96 | 46.45 | 6.35 | 1.348 | 4.643 | 8481.44 | 2.005 | 97.8 | 77.5 | 1400 | 23.22 | 5512.9 | 2899.1 | 2759.4 | 4117.1 | 1198.7 | 0.68826 | 5.99
2024-12-09 | 18:21 | Data | 0 | 32.723 | 30.678 | 187.851 | 7.63 | 176.594 | 2148.41 | 25.96 | 46.45 | 6.35 | 1.345 | 4.653 | 8481.44 | 2.046 | 97.8 | 77.6 | 1396 | 23.22 | 5512.9 | 2900.2 | 2785.9 | 4136 | 1198.7 | 0.68603 | 5.998
2024-12-09 | 18:21 | Data | 0 | 32.723 | 30.651 | 187.715 | 7.63 | 176.459 | 2144.79 | 25.96 | 46.45 | 6.35 | 1.347 | 4.649 | 8485.96 | 2.073 | 97.8 | 77.5 | 1394 | 23.27 | 5515.9 | 2899.7 | 2790.6 | 4140.4 | 1198.7 | 0.68265 | 5.996
2024-12-09 | 18:21 | Data | 0 | 32.501 | 30.59 | 187.624 | 7.63 | 176.549 | 2133.95 | 25.96 | 46.54 | 6.35 | 1.353 | 4.648 | 8495 | 1.958 | 97.8 | 77.5 | 1387 | 23.27 | 5521.8 | 2903.8 | 2779 | 4133.3 | 1198.7 | 0.68664 | 6.001
2024-12-09 | 18:21 | Data | 0 | 32.663 | 30.752 | 187.805 | 7.63 | 176.459 | 2134.85 | 25.96 | 46.54 | 6.35 | 1.345 | 4.635 | 8513.09 | 2.093 | 97.8 | 77.5 | 1388 | 23.27 | 5533.5 | 2892.7 | 2786.9 | 4133.3 | 1198.7 | 0.68409 | 5.98
2024-12-09 | 18:21 | Data | 0 | 32.305 | 30.415 | 187.715 | 7.63 | 176.459 | 2140.27 | 25.95 | 46.359 | 6.35 | 1.354 | 4.649 | 8938.18 | 1.971 | 97.8 | 77.4 | 1391 | 23.27 | 5809.8 | 2879.8 | 2785.1 | 4123.1 | 1198.7 | 0.68101 | 6.003
2024-12-09 | 18:21 | Data | 0 | 32.285 | 30.361 | 187.715 | 7.63 | 176.413 | 2139.37 | 25.95 | 46.45 | 6.35 | 1.354 | 4.64 | 8508.57 | 1.965 | 97.8 | 77.4 | 1390 | 23.22 | 5530.6 | 2897.6 | 2803.2 | 4146.1 | 1198.7 | 0.68283 | 5.993
2024-12-09 | 18:21 | Data | 0 | 32.386 | 30.631 | 187.76 | 7.63 | 176.413 | 2139.37 | 25.96 | 46.45 | 6.35 | 1.357 | 4.684 | 8495 | 2.019 | 97.8 | 77.5 | 1391 | 23.22 | 5521.8 | 2891.9 | 2812.9 | 4150.7 | 1198.7 | 0.68023 | 6.041
2024-12-09 | 18:21 | Data | 0 | 32.94 | 30.536 | 187.715 | 7.63 | 176.459 | 2140.27 | 25.94 | 46.54 | 6.35 | 1.345 | 4.673 | 8495 | 2.012 | 97.8 | 77.7 | 1391 | 23.27 | 5521.8 | 2896.8 | 2774.1 | 4125.8 | 1198.7 | 0.68431 | 6.018
2024-12-09 | 18:21 | Data | 0 | 33.007 | 30.685 | 187.941 | 7.63 | 176.639 | 2140.27 | 25.96 | 46.54 | 6.35 | 1.343 | 4.673 | 8508.57 | 2.14 | 97.8 | 77.7 | 1391 | 23.27 | 5530.6 | 2892.4 | 2779.5 | 4127.6 | 1198.8 | 0.68297 | 6.015
2024-12-09 | 18:21 | Data | 0 | 32.501 | 30.475 | 187.624 | 7.63 | 176.413 | 2137.56 | 25.96 | 46.45 | 6.35 | 1.34 | 4.672 | 8513.09 | 2.019 | 97.8 | 77.7 | 1389 | 23.27 | 5533.5 | 2893.3 | 2791.1 | 4135.8 | 1198.8 | 0.6835 | 6.012
2024-12-09 | 18:21 | Data | 0 | 32.75 | 30.658 | 187.941 | 7.63 | 176.594 | 2136.66 | 25.96 | 46.54 | 6.35 | 1.345 | 4.654 | 8513.09 | 2.066 | 97.8 | 77.6 | 1389 | 23.27 | 5533.5 | 2895 | 2793.6 | 4135.9 | 1198.8 | 0.68381 | 5.998
2024-12-09 | 18:21 | Data | 0 | 32.784 | 30.448 | 187.76 | 7.63 | 176.549 | 2136.66 | 25.96 | 46.45 | 6.35 | 1.339 | 4.646 | 8508.57 | 2.046 | 97.8 | 77.6 | 1389 | 23.18 | 5530.6 | 2890 | 2809.3 | 4150.5 | 1198.8 | 0.67928 | 5.985
2024-12-09 | 18:22 | Data | 0 | 33.048 | 30.988 | 187.941 | 7.63 | 176.639 | 2136.66 | 25.97 | 46.45 | 6.35 | 1.344 | 4.646 | 8517.61 | 2.073 | 97.8 | 77.6 | 1389 | 23.22 | 5536.4 | 2917.9 | 2804 | 4161 | 1198.8 | 0.68529 | 5.991
2024-12-09 | 18:22 | Data | 0 | 32.548 | 30.428 | 187.579 | 7.63 | 176.368 | 2139.37 | 25.94 | 46.54 | 6.36 | 1.354 | 4.657 | 8513.09 | 2.059 | 97.8 | 77.5 | 1391 | 23.22 | 5533.5 | 2895.7 | 2788.9 | 4138.7 | 1198.8 | 0.68218 | 6.012
2024-12-09 | 18:22 | Data | 0 | 32.919 | 30.88 | 187.941 | 7.63 | 176.594 | 2139.37 | 25.96 | 46.54 | 6.35 | 1.351 | 4.657 | 8499.53 | 2.066 | 97.8 | 77.5 | 1391 | 23.22 | 5524.7 | 2906.8 | 2771.2 | 4134.6 | 1198.8 | 0.68571 | 6.008
2024-12-09 | 18:22 | Data | 0 | 32.811 | 30.874 | 187.805 | 7.63 | 176.413 | 2138.47 | 25.95 | 46.45 | 6.34 | 1.343 | 4.646 | 8495 | 2.167 | 97.8 | 77.6 | 1391 | 23.27 | 5521.8 | 2911.1 | 2791.7 | 4149.6 | 1198.8 | 0.68628 | 5.989
2024-12-09 | 18:22 | Data | 0 | 32.669 | 30.766 | 187.715 | 7.63 | 176.549 | 2139.37 | 25.96 | 46.45 | 6.35 | 1.348 | 4.642 | 8513.09 | 2.221 | 97.8 | 77.5 | 1391 | 23.22 | 5533.5 | 2896 | 2791.3 | 4138 | 1198.8 | 0.6849 | 5.99
2024-12-09 | 18:22 | Data | 0 | 32.926 | 30.88 | 187.896 | 7.63 | 176.639 | 2139.37 | 25.96 | 46.54 | 6.35 | 1.358 | 4.648 | 8513.09 | 2.059 | 97.8 | 77.4 | 1390 | 23.27 | 5533.5 | 2893.7 | 2772.5 | 4119.6 | 1198.8 | 0.68693 | 6.005
2024-12-09 | 18:22 | Data | 0 | 32.534 | 30.766 | 187.76 | 7.63 | 176.459 | 2139.37 | 25.95 | 46.269 | 6.35 | 1.356 | 4.675 | 8540.22 | 1.857 | 97.8 | 77.5 | 1391 | 23.09 | 5551.1 | 2894.4 | 2755.3 | 4114.2 | 1198.8 | 0.68749 | 6.031
2024-12-09 | 18:22 | Data | 0 | 32.494 | 30.637 | 187.67 | 7.63 | 176.413 | 2137.56 | 25.95 | 46.269 | 6.35 | 1.356 | 4.667 | 8540.22 | 1.985 | 97.8 | 77.5 | 1389 | 23.13 | 5551.1 | 2898.5 | 2759 | 4125.1 | 1198.8 | 0.6867 | 6.023
2024-12-09 | 18:22 | Data | 0 | 32.494 | 30.651 | 187.76 | 7.63 | 176.549 | 2133.95 | 25.96 | 46.269 | 6.35 | 1.348 | 4.667 | 8535.7 | 2.046 | 97.8 | 77.6 | 1387 | 23.13 | 5548.2 | 2879.6 | 2775.2 | 4141.2 | 1198.8 | 0.68479 | 6.016
2024-12-09 | 18:22 | Data | 0 | 32.777 | 30.658 | 187.805 | 7.63 | 176.549 | 2140.27 | 25.96 | 46.269 | 6.35 | 1.349 | 4.636 | 8535.7 | 2.073 | 97.8 | 77.5 | 1391 | 23.04 | 5548.2 | 2893.6 | 2785.2 | 4132.1 | 1198.8 | 0.68359 | 5.986
2024-12-09 | 18:22 | Data | 0 | 32.501 | 30.529 | 187.624 | 7.63 | 176.459 | 2142.99 | 25.96 | 46.179 | 6.35 | 1.348 | 4.666 | 8485.96 | 1.85 | 97.8 | 77.6 | 1392 | 23.09 | 5515.9 | 2876.4 | 2804.3 | 4135 | 1198.8 | 0.6787 | 6.015
2024-12-09 | 18:22 | Data | 0 | 32.595 | 30.597 | 187.624 | 7.63 | 176.413 | 2144.79 | 25.96 | 46.45 | 6.35 | 1.346 | 4.682 | 8531.18 | 2.241 | 97.8 | 77.7 | 1394 | 23.22 | 5545.3 | 2911.7 | 2805.2 | 4158.6 | 1198.8 | 0.68323 | 6.027
2024-12-09 | 18:22 | Data | 0 | 33.169 | 30.489 | 187.896 | 7.63 | 176.639 | 2143.89 | 25.97 | 46.45 | 6.35 | 1.351 | 4.673 | 8526.66 | 2.147 | 97.8 | 77.6 | 1394 | 23.22 | 5542.3 | 2899.8 | 2825.2 | 4165.5 | 1198.8 | 0.67998 | 6.025
2024-12-09 | 18:22 | Data | 0 | 32.919 | 30.867 | 187.67 | 7.63 | 176.549 | 2145.7 | 25.96 | 46.54 | 6.35 | 1.347 | 4.673 | 8522.14 | 2.093 | 97.8 | 77.6 | 1394 | 23.27 | 5539.4 | 2882.8 | 2777.4 | 4120.2 | 1198.8 | 0.68303 | 6.021
2024-12-09 | 18:22 | Data | 0 | 32.501 | 30.651 | 187.715 | 7.63 | 176.413 | 2147.51 | 25.95 | 46.45 | 6.35 | 1.339 | 4.652 | 8540.22 | 1.85 | 97.8 | 77.6 | 1396 | 23.22 | 5551.1 | 2904.5 | 2789.1 | 4141.3 | 1198.8 | 0.68488 | 5.99
2024-12-09 | 18:22 | Data | 0 | 32.501 | 30.651 | 187.76 | 7.63 | 176.413 | 2147.51 | 25.96 | 46.54 | 6.35 | 1.347 | 4.655 | 8535.7 | 1.958 | 97.8 | 77.6 | 1396 | 23.22 | 5548.2 | 2885.6 | 2776.2 | 4137.7 | 1198.8 | 0.68751 | 6.003
2024-12-09 | 18:22 | Data | 0 | 32.636 | 30.658 | 187.76 | 7.63 | 176.594 | 2147.51 | 25.96 | 46.54 | 6.35 | 1.358 | 4.635 | 8553.79 | 1.857 | 97.8 | 77.3 | 1395 | 23.27 | 5560 | 2906.5 | 2750.5 | 4122.4 | 1198.8 | 0.68912 | 5.994
2024-12-09 | 18:22 | Data | 0 | 32.514 | 30.651 | 187.805 | 7.63 | 176.549 | 2149.31 | 25.96 | 46.45 | 6.34 | 1.356 | 4.672 | 8553.79 | 1.85 | 97.8 | 77.5 | 1397 | 23.27 | 5560 | 2920 | 2780.8 | 4150.5 | 1198.8 | 0.68717 | 6.026
2024-12-09 | 18:23 | Data | 0 | 32.501 | 30.651 | 187.76 | 7.63 | 176.459 | 2201.74 | 25.96 | 46.45 | 6.35 | 1.352 | 4.671 | 8576.4 | 2.059 | 97.9 | 77.6 | 1432 | 23.27 | 5574.7 | 2895 | 2795.8 | 4142.7 | 1198.8 | 0.68212 | 6.026
2024-12-09 | 18:23 | Data | 0 | 32.723 | 30.651 | 187.805 | 7.63 | 176.459 | 2203.54 | 25.97 | 46.54 | 6.35 | 1.352 | 4.654 | 8558.31 | 2.066 | 97.9 | 77.5 | 1432 | 23.22 | 5562.9 | 2896.6 | 2805.5 | 4159.7 | 1198.8 | 0.68084 | 6.005
2024-12-09 | 18:23 | Data | 0 | 32.723 | 30.948 | 187.805 | 7.63 | 176.549 | 2201.74 | 25.95 | 46.54 | 6.35 | 1.355 | 4.664 | 8558.31 | 1.877 | 97.9 | 77.5 | 1431 | 23.27 | 5562.9 | 2901.2 | 2830.5 | 4169.5 | 1198.8 | 0.68088 | 6.019
2024-12-09 | 18:23 | Data | 0 | 32.892 | 30.712 | 187.76 | 7.63 | 176.549 | 2204.45 | 25.96 | 46.54 | 6.35 | 1.353 | 4.633 | 8567.36 | 2.046 | 97.9 | 77.4 | 1432 | 23.27 | 5568.8 | 2922.1 | 2851.9 | 4193.9 | 1198.8 | 0.67777 | 5.985
2024-12-09 | 18:23 | Data | 0 | 33.034 | 30.685 | 187.851 | 7.63 | 176.594 | 2152.93 | 25.96 | 46.54 | 6.35 | 1.352 | 4.642 | 8549.27 | 2.133 | 97.8 | 77.4 | 1400 | 23.22 | 5557 | 2887.6 | 2851.1 | 4169.9 | 1198.8 | 0.67592 | 5.995
2024-12-09 | 18:23 | Data | 0 | 32.94 | 30.685 | 187.805 | 7.63 | 176.594 | 2151.12 | 25.96 | 46.45 | 6.35 | 1.341 | 4.656 | 8540.22 | 1.978 | 97.8 | 77.6 | 1398 | 23.22 | 5551.1 | 2902.2 | 2808.4 | 4154.6 | 1198.8 | 0.68115 | 5.998
2024-12-09 | 18:23 | Data | 0 | 32.44 | 30.651 | 187.851 | 7.63 | 176.459 | 2151.12 | 25.96 | 46.45 | 6.36 | 1.339 | 4.647 | 8558.31 | 2.005 | 97.8 | 77.6 | 1398 | 23.27 | 5562.9 | 2883.1 | 2789.8 | 4130.3 | 1198.8 | 0.6824 | 5.987
2024-12-09 | 18:23 | Data | 0 | 32.737 | 30.55 | 187.67 | 7.63 | 176.639 | 2155.64 | 25.96 | 46.45 | 6.35 | 1.342 | 4.634 | 8544.75 | 1.938 | 97.8 | 77.5 | 1401 | 23.27 | 5554.1 | 2901.3 | 2771.8 | 4128.2 | 1198.8 | 0.68763 | 5.977
2024-12-09 | 18:23 | Data | 0 | 32.717 | 30.651 | 187.76 | 7.64 | 176.549 | 2152.02 | 25.95 | 46.45 | 6.35 | 1.352 | 4.647 | 8508.57 | 2.073 | 97.8 | 77.4 | 1398 | 23.22 | 5530.6 | 2889.7 | 2767.3 | 4122 | 1198.8 | 0.68462 | 5.999
2024-12-09 | 18:23 | Data | 0 | 32.892 | 30.766 | 187.896 | 7.63 | 176.594 | 2152.93 | 25.96 | 46.54 | 6.35 | 1.354 | 4.668 | 8513.09 | 2.046 | 97.8 | 77.5 | 1399 | 23.27 | 5533.5 | 2899 | 2768.6 | 4128 | 1198.8 | 0.68589 | 6.022
2024-12-09 | 18:23 | Data | 0 | 32.717 | 30.475 | 187.805 | 7.63 | 176.413 | 2153.83 | 25.96 | 46.45 | 6.36 | 1.345 | 4.645 | 8526.66 | 2.073 | 97.8 | 77.5 | 1400 | 23.22 | 5542.3 | 2907.7 | 2763.2 | 4128.6 | 1198.8 | 0.68889 | 5.99
2024-12-09 | 18:23 | Data | 0 | 32.663 | 30.644 | 187.76 | 7.63 | 176.413 | 2153.83 | 25.97 | 46.54 | 6.35 | 1.349 | 4.652 | 8526.66 | 2.093 | 97.8 | 77.5 | 1400 | 23.27 | 5542.3 | 2888.8 | 2775.9 | 4129.5 | 1198.8 | 0.68336 | 6.001
2024-12-09 | 18:23 | Data | 0 | 32.723 | 30.597 | 187.67 | 7.63 | 176.549 | 2147.51 | 25.96 | 46.54 | 6.35 | 1.348 | 4.667 | 8549.27 | 2.302 | 97.8 | 77.6 | 1396 | 23.27 | 5557 | 2902.9 | 2785.7 | 4133.5 | 1198.8 | 0.6864 | 6.017
2024-12-09 | 18:23 | Data | 0 | 32.723 | 30.766 | 187.579 | 7.63 | 176.459 | 2153.83 | 25.96 | 46.45 | 6.35 | 1.347 | 4.675 | 8553.79 | 2.073 | 97.8 | 77.7 | 1399 | 23.22 | 5560 | 2888.9 | 2770.4 | 4122.6 | 1198.8 | 0.68218 | 6.022
2024-12-09 | 18:23 | Data | 0 | 32.919 | 30.874 | 187.805 | 7.63 | 176.549 | 2153.83 | 25.96 | 46.45 | 6.35 | 1.352 | 4.673 | 8553.79 | 2.079 | 97.8 | 77.6 | 1399 | 23.22 | 5560 | 2892.4 | 2815.3 | 4150.7 | 1198.8 | 0.6808 | 6.025
2024-12-09 | 18:23 | Data | 0 | 32.629 | 30.421 | 187.715 | 7.63 | 176.549 | 2153.83 | 25.96 | 46.54 | 6.34 | 1.351 | 4.651 | 8549.27 | 2.12 | 97.8 | 77.5 | 1400 | 23.27 | 5557 | 2899.1 | 2791.1 | 4137.7 | 1198.9 | 0.68485 | 6.002
2024-12-09 | 18:23 | Data | 0 | 32.609 | 30.644 | 187.76 | 7.63 | 176.368 | 2158.35 | 25.95 | 46.45 | 6.35 | 1.352 | 4.629 | 8562.84 | 2.073 | 97.9 | 77.4 | 1404 | 23.13 | 5565.8 | 2896.4 | 2800.8 | 4141.9 | 1198.9 | 0.68318 | 5.981
2024-12-09 | 18:23 | Data | 0 | 32.669 | 30.651 | 187.715 | 7.63 | 176.413 | 2159.26 | 25.95 | 46.179 | 6.35 | 1.354 | 4.659 | 8576.4 | 2.066 | 97.9 | 77.5 | 1403 | 23.09 | 5574.7 | 2889.5 | 2809.6 | 4145.6 | 1198.9 | 0.68044 | 6.012
2024-12-09 | 18:24 | Data | 0 | 32.946 | 30.691 | 187.805 | 7.63 | 176.594 | 2158.35 | 25.96 | 46.359 | 6.35 | 1.355 | 4.673 | 8562.84 | 2.14 | 97.9 | 77.5 | 1403 | 23.18 | 5565.8 | 2908.7 | 2780.1 | 4127.5 | 1198.9 | 0.68605 | 6.029
2024-12-09 | 18:24 | Data | 0 | 32.494 | 30.644 | 187.76 | 7.63 | 176.459 | 2155.64 | 25.96 | 46.45 | 6.35 | 1.353 | 4.635 | 8571.88 | 2.032 | 97.8 | 77.4 | 1402 | 23.27 | 5571.7 | 2884.1 | 2794.1 | 4132.1 | 1198.9 | 0.68185 | 5.988
2024-12-09 | 18:24 | Data | 0 | 32.669 | 30.826 | 187.805 | 7.63 | 176.594 | 2153.83 | 25.96 | 46.359 | 6.35 | 1.356 | 4.635 | 8553.79 | 2.16 | 97.8 | 77.4 | 1400 | 23.22 | 5560 | 2890.8 | 2764.5 | 4115 | 1198.9 | 0.68652 | 5.992
2024-12-09 | 18:24 | Data | 0 | 32.804 | 30.651 | 187.851 | 7.63 | 176.459 | 2152.02 | 25.96 | 46.269 | 6.35 | 1.353 | 4.619 | 8571.88 | 2.113 | 97.8 | 77.3 | 1399 | 23.13 | 5571.7 | 2882.2 | 2759.5 | 4107.8 | 1198.9 | 0.68454 | 5.972
2024-12-09 | 18:24 | Data | 0 | 32.609 | 30.968 | 187.986 | 7.63 | 176.459 | 2151.12 | 25.96 | 46.269 | 6.35 | 1.351 | 4.641 | 8558.31 | 2.025 | 97.8 | 77.5 | 1398 | 23.13 | 5562.9 | 2881.4 | 2783.9 | 4127 | 1198.9 | 0.68172 | 5.992
2024-12-09 | 18:24 | Data | 0 | 32.528 | 30.637 | 187.715 | 7.63 | 176.459 | 2153.83 | 25.96 | 46.179 | 6.35 | 1.353 | 4.654 | 8558.31 | 2.046 | 97.9 | 77.5 | 1400 | 23.13 | 5562.9 | 2889.8 | 2814.4 | 4152.7 | 1198.9 | 0.67992 | 6.006
2024-12-09 | 18:24 | Data | 0 | 32.615 | 30.651 | 187.76 | 7.63 | 176.549 | 2153.83 | 25.97 | 46.269 | 6.35 | 1.347 | 4.655 | 8544.75 | 2.046 | 97.9 | 77.6 | 1400 | 23.13 | 5554.1 | 2883.9 | 2854.6 | 4170.9 | 1198.9 | 0.67513 | 6
2024-12-09 | 18:24 | Data | 0 | 32.548 | 30.644 | 187.67 | 7.63 | 176.459 | 2155.64 | 25.96 | 46.179 | 6.35 | 1.347 | 4.65 | 8540.22 | 1.857 | 97.9 | 77.5 | 1402 | 23.09 | 5551.1 | 2903.5 | 2814.7 | 4156.3 | 1198.9 | 0.68268 | 5.997
2024-12-09 | 18:24 | Data | 0 | 32.717 | 30.651 | 187.76 | 7.63 | 176.459 | 2155.64 | 25.96 | 46.089 | 6.35 | 1.358 | 4.649 | 8549.27 | 2.073 | 97.9 | 77.4 | 1401 | 23.09 | 5557 | 2908.8 | 2811 | 4158.5 | 1198.9 | 0.68326 | 6.006
2024-12-09 | 18:24 | Data | 0 | 32.798 | 30.86 | 187.941 | 7.63 | 176.594 | 2156.54 | 25.95 | 46.179 | 6.35 | 1.347 | 4.656 | 8535.7 | 2.066 | 97.9 | 77.6 | 1401 | 23.09 | 5548.2 | 2898.2 | 2836.1 | 4170.8 | 1198.9 | 0.67794 | 6.003
2024-12-09 | 18:24 | Data | 0 | 32.609 | 30.752 | 187.896 | 7.63 | 176.459 | 2155.64 | 25.94 | 46.721 | 6.35 | 1.344 | 4.658 | 8535.7 | 2.1 | 97.8 | 77.6 | 1401 | 23.41 | 5548.2 | 2897.5 | 2793.9 | 4137.5 | 1198.9 | 0.68428 | 6.002
2024-12-09 | 18:24 | Data | 0 | 32.737 | 31.056 | 187.896 | 7.63 | 176.639 | 2156.54 | 25.97 | 46.269 | 6.35 | 1.354 | 4.647 | 8576.4 | 1.904 | 97.9 | 77.4 | 1402 | 23.13 | 5574.7 | 2900.6 | 2813.6 | 4154.1 | 1198.9 | 0.682 | 6.001
2024-12-09 | 18:24 | Data | 0 | 32.717 | 30.664 | 187.805 | 7.63 | 176.549 | 2161.97 | 25.96 | 46.179 | 6.35 | 1.351 | 4.629 | 8567.36 | 2.046 | 97.9 | 77.4 | 1405 | 23.09 | 5568.8 | 2888.1 | 2814.3 | 4146.9 | 1198.9 | 0.67998 | 5.98
2024-12-09 | 18:24 | Data | 0 | 32.453 | 30.644 | 187.896 | 7.63 | 176.459 | 2158.35 | 25.97 | 46.269 | 6.35 | 1.353 | 4.667 | 8567.36 | 2.16 | 97.9 | 77.5 | 1404 | 23.13 | 5568.8 | 2914.5 | 2796 | 4150.1 | 1198.9 | 0.68521 | 6.019
2024-12-09 | 18:24 | Data | 0 | 32.528 | 30.637 | 187.805 | 7.63 | 176.549 | 2154.74 | 25.97 | 46.179 | 6.35 | 1.345 | 4.658 | 8558.31 | 1.776 | 97.9 | 77.6 | 1401 | 23.09 | 5562.9 | 2896.7 | 2782.8 | 4129.2 | 1198.9 | 0.68473 | 6.003
2024-12-09 | 18:24 | Data | 0 | 32.717 | 30.529 | 187.67 | 7.63 | 176.459 | 2156.54 | 25.95 | 46.089 | 6.35 | 1.355 | 4.676 | 8540.22 | 2.16 | 97.9 | 77.5 | 1402 | 23.09 | 5551.1 | 2899.2 | 2805.6 | 4145.9 | 1198.9 | 0.68237 | 6.03
2024-12-09 | 18:24 | Data | 0 | 32.71 | 30.651 | 187.67 | 7.63 | 176.549 | 2156.54 | 25.96 | 46.269 | 6.35 | 1.356 | 4.673 | 8526.66 | 2.066 | 97.9 | 77.5 | 1402 | 23.13 | 5542.3 | 2912.8 | 2822.8 | 4172.7 | 1198.9 | 0.68089 | 6.028
2024-12-09 | 18:24 | Data | 0 | 32.636 | 30.968 | 187.896 | 7.63 | 176.594 | 2156.54 | 25.94 | 46.179 | 6.35 | 1.352 | 4.646 | 8526.66 | 1.917 | 97.9 | 77.5 | 1402 | 23.18 | 5542.3 | 2900 | 2839.9 | 4173.4 | 1198.9 | 0.67824 | 5.998
2024-12-09 | 18:25 | Data | 0 | 32.636 | 30.651 | 187.805 | 7.63 | 176.549 | 2155.64 | 25.96 | 46.269 | 6.35 | 1.342 | 4.646 | 8499.53 | 1.85 | 97.9 | 77.6 | 1401 | 23.13 | 5524.7 | 2901.4 | 2792.8 | 4146.7 | 1198.9 | 0.68275 | 5.989
2024-12-09 | 18:25 | Data | 0 | 33.108 | 31.103 | 187.896 | 7.63 | 176.549 | 2153.83 | 25.95 | 46.269 | 6.35 | 1.341 | 4.658 | 8540.22 | 2.059 | 97.9 | 77.6 | 1400 | 23.09 | 5551.1 | 2908.8 | 2799.9 | 4155 | 1198.9 | 0.68431 | 6
2024-12-09 | 18:25 | Data | 0 | 32.919 | 30.867 | 187.805 | 7.63 | 176.549 | 2149.31 | 25.96 | 45.998 | 6.35 | 1.351 | 4.683 | 8535.7 | 2.12 | 97.9 | 77.6 | 1398 | 23 | 5548.2 | 2919.5 | 2803 | 4160.7 | 1198.9 | 0.68547 | 6.03
2024-12-09 | 18:25 | Data | 0 | 32.521 | 30.685 | 187.715 | 7.63 | 176.549 | 2152.02 | 25.96 | 46.179 | 6.35 | 1.345 | 4.656 | 8540.22 | 1.769 | 97.8 | 77.6 | 1398 | 23.18 | 5551.1 | 2884.7 | 2795.7 | 4134.7 | 1198.9 | 0.67962 | 6.002
2024-12-09 | 18:25 | Data | 0 | 32.906 | 31.144 | 187.986 | 7.63 | 176.594 | 2152.02 | 25.96 | 46.269 | 6.35 | 1.355 | 4.648 | 8513.09 | 2.032 | 97.9 | 77.4 | 1398 | 23.13 | 5533.5 | 2909.3 | 2801.8 | 4152.7 | 1198.9 | 0.68459 | 6.003
2024-12-09 | 18:25 | Data | 0 | 32.507 | 30.428 | 187.624 | 7.63 | 176.413 | 2151.12 | 25.94 | 46.179 | 6.35 | 1.357 | 4.642 | 8495 | 1.958 | 97.8 | 77.4 | 1398 | 23.09 | 5521.8 | 2888.3 | 2790.5 | 4129.8 | 1198.9 | 0.68427 | 5.998
2024-12-09 | 18:25 | Data | 0 | 33.115 | 30.577 | 187.941 | 7.63 | 176.594 | 2144.79 | 25.96 | 46.179 | 6.36 | 1.354 | 4.666 | 8495 | 2.268 | 97.8 | 77.5 | 1395 | 23.09 | 5521.8 | 2897.9 | 2801.7 | 4148.7 | 1198.9 | 0.68311 | 6.019
2024-12-09 | 18:25 | Data | 0 | 32.568 | 30.421 | 187.67 | 7.63 | 176.413 | 2143.89 | 25.96 | 46.269 | 6.35 | 1.358 | 4.631 | 8513.09 | 2.073 | 97.8 | 77.3 | 1394 | 23.09 | 5533.5 | 2896.2 | 2781.2 | 4131.5 | 1198.9 | 0.6845 | 5.988
2024-12-09 | 18:25 | Data | 0 | 32.514 | 30.867 | 187.715 | 7.63 | 176.594 | 2143.89 | 25.98 | 46.179 | 6.34 | 1.356 | 4.647 | 8938.18 | 1.897 | 97.9 | 77.4 | 1394 | 23.09 | 5809.8 | 2908.5 | 2804.5 | 4154.6 | 1198.9 | 0.68407 | 6.004
2024-12-09 | 18:25 | Data | 0 | 33.088 | 30.982 | 187.851 | 7.63 | 176.594 | 2144.79 | 25.96 | 46.54 | 6.36 | 1.354 | 4.679 | 8499.53 | 2.174 | 97.8 | 77.6 | 1394 | 23.22 | 5524.7 | 2936.8 | 2806.9 | 4176.6 | 1198.9 | 0.68558 | 6.032
2024-12-09 | 18:25 | Data | 0 | 32.926 | 30.766 | 187.941 | 7.63 | 176.639 | 2143.89 | 25.96 | 46.54 | 6.35 | 1.349 | 4.662 | 8495 | 2.073 | 97.8 | 77.6 | 1394 | 23.22 | 5521.8 | 2896.5 | 2826.1 | 4161.1 | 1198.9 | 0.67936 | 6.013
2024-12-09 | 18:25 | Data | 0 | 32.723 | 30.766 | 187.805 | 7.63 | 176.549 | 2144.79 | 25.96 | 46.45 | 6.36 | 1.346 | 4.654 | 8485.96 | 2.073 | 97.8 | 77.6 | 1395 | 23.27 | 5515.9 | 2897.1 | 2789 | 4137.7 | 1198.9 | 0.68292 | 6
2024-12-09 | 18:25 | Data | 0 | 32.75 | 30.867 | 187.896 | 7.63 | 176.639 | 2144.79 | 25.96 | 46.54 | 6.35 | 1.344 | 4.634 | 8481.44 | 1.911 | 97.8 | 77.5 | 1394 | 23.27 | 5512.9 | 2914.5 | 2804 | 4159.6 | 1198.9 | 0.68334 | 5.978
2024-12-09 | 18:25 | Data | 0 | 32.831 | 30.664 | 187.851 | 7.63 | 176.549 | 2145.7 | 25.97 | 46.45 | 6.35 | 1.348 | 4.64 | 8499.53 | 2.012 | 97.8 | 77.5 | 1394 | 23.22 | 5524.7 | 2905.2 | 2800.6 | 4147.7 | 1198.9 | 0.67986 | 5.988
2024-12-09 | 18:25 | Data | 0 | 32.737 | 30.705 | 187.896 | 7.63 | 176.639 | 2143.89 | 25.96 | 46.54 | 6.35 | 1.351 | 4.659 | 8495 | 2.241 | 97.8 | 77.5 | 1393 | 23.27 | 5521.8 | 2914.8 | 2813.3 | 4166.2 | 1198.9 | 0.68227 | 6.01
2024-12-09 | 18:25 | Data | 0 | 32.994 | 30.705 | 187.941 | 7.63 | 176.73 | 2142.08 | 25.96 | 46.45 | 6.35 | 1.348 | 4.653 | 8513.09 | 2.093 | 97.8 | 77.5 | 1392 | 23.27 | 5533.5 | 2899.3 | 2822.7 | 4160.3 | 1199 | 0.68051 | 5.999
2024-12-09 | 18:25 | Data | 0 | 32.669 | 30.705 | 187.851 | 7.63 | 176.639 | 2144.79 | 25.95 | 46.54 | 6.35 | 1.347 | 4.629 | 8495 | 1.951 | 97.8 | 77.5 | 1394 | 23.27 | 5521.8 | 2904.4 | 2802.8 | 4151.6 | 1199 | 0.68205 | 5.977
2024-12-09 | 18:26 | Data | 0 | 32.777 | 30.658 | 187.76 | 7.63 | 176.549 | 2144.79 | 25.95 | 46.45 | 6.35 | 1.34 | 4.659 | 8513.09 | 1.87 | 97.8 | 77.7 | 1394 | 23.22 | 5533.5 | 2893.1 | 2837.6 | 4168.2 | 1199 | 0.6777 | 5.999
2024-12-09 | 18:26 | Data | 0 | 33.054 | 30.671 | 187.941 | 7.63 | 176.685 | 2144.79 | 25.96 | 46.54 | 6.35 | 1.346 | 4.659 | 8508.57 | 2.289 | 97.8 | 77.6 | 1394 | 23.27 | 5530.6 | 2905.3 | 2828.8 | 4168.8 | 1199 | 0.68077 | 6.005
2024-12-09 | 18:26 | Data | 0 | 32.75 | 30.658 | 187.805 | 7.63 | 176.594 | 2144.79 | 25.95 | 46.54 | 6.35 | 1.351 | 4.657 | 8517.61 | 2.059 | 97.8 | 77.5 | 1394 | 23.27 | 5536.4 | 2874.1 | 2831.9 | 4159.3 | 1199 | 0.67234 | 6.008
2024-12-09 | 18:26 | Data | 0 | 32.919 | 30.874 | 187.805 | 7.63 | 176.639 | 2143.89 | 25.96 | 46.45 | 6.35 | 1.349 | 4.65 | 8517.61 | 2.073 | 97.8 | 77.5 | 1394 | 23.22 | 5536.4 | 2902 | 2846.3 | 4176.8 | 1199 | 0.67821 | 6.001
2024-12-09 | 18:26 | Data | 0 | 32.926 | 30.921 | 188.031 | 7.63 | 176.639 | 2145.7 | 25.96 | 46.54 | 6.35 | 1.348 | 4.657 | 8531.18 | 2.019 | 97.8 | 77.6 | 1394 | 23.27 | 5545.3 | 2899.5 | 2805 | 4146.5 | 1199 | 0.68187 | 6.005
2024-12-09 | 18:26 | Data | 0 | 32.723 | 30.853 | 187.851 | 7.63 | 176.459 | 2144.79 | 25.97 | 46.54 | 6.35 | 1.358 | 4.662 | 8495 | 2.039 | 97.8 | 77.4 | 1394 | 23.27 | 5521.8 | 2912.9 | 2795.4 | 4153.6 | 1199 | 0.68467 | 6.02
2024-12-09 | 18:26 | Data | 0 | 32.609 | 30.691 | 187.805 | 7.63 | 176.639 | 2147.51 | 25.95 | 46.45 | 6.35 | 1.346 | 4.664 | 8522.14 | 1.897 | 97.8 | 77.6 | 1396 | 23.32 | 5539.4 | 2892.1 | 2789.1 | 4134.9 | 1199 | 0.68443 | 6.009
2024-12-09 | 18:26 | Data | 0 | 32.737 | 30.543 | 187.851 | 7.63 | 176.594 | 2147.51 | 25.96 | 46.54 | 6.36 | 1.342 | 4.672 | 8513.09 | 1.863 | 97.8 | 77.7 | 1396 | 23.27 | 5533.5 | 2875.5 | 2777.8 | 4115.1 | 1199 | 0.68306 | 6.014
2024-12-09 | 18:26 | Data | 0 | 32.696 | 30.651 | 187.851 | 7.63 | 176.594 | 2148.41 | 25.96 | 46.359 | 6.35 | 1.348 | 4.666 | 8481.44 | 2.073 | 97.8 | 77.6 | 1396 | 23.13 | 5512.9 | 2897.8 | 2767.6 | 4123.2 | 1199 | 0.68609 | 6.016
2024-12-09 | 18:26 | Data | 0 | 32.622 | 30.651 | 187.941 | 7.63 | 176.639 | 2147.51 | 25.95 | 46.54 | 6.35 | 1.353 | 4.663 | 8495 | 2.059 | 97.8 | 77.5 | 1396 | 23.22 | 5521.8 | 2909.6 | 2781 | 4139.3 | 1199 | 0.688 | 6.016
2024-12-09 | 18:26 | Data | 0 | 33 | 30.982 | 187.941 | 7.63 | 176.639 | 2149.31 | 25.95 | 46.54 | 6.35 | 1.355 | 4.671 | 8513.09 | 1.931 | 97.8 | 77.5 | 1398 | 23.22 | 5533.5 | 2911.3 | 2803.2 | 4158.9 | 1199 | 0.68405 | 6.026
2024-12-09 | 18:26 | Data | 0 | 32.879 | 31.049 | 187.805 | 7.63 | 176.549 | 2151.12 | 25.95 | 46.179 | 6.35 | 1.352 | 4.647 | 8485.96 | 2.059 | 97.8 | 77.5 | 1398 | 23.13 | 5515.9 | 2871.5 | 2808.9 | 4134.2 | 1199 | 0.6775 | 5.999
2024-12-09 | 18:26 | Data | 0 | 32.507 | 30.428 | 187.805 | 7.63 | 176.594 | 2151.12 | 25.95 | 46.54 | 6.35 | 1.348 | 4.623 | 8526.66 | 2.066 | 97.8 | 77.4 | 1397 | 23.27 | 5542.3 | 2904.3 | 2803.1 | 4153.9 | 1199 | 0.68119 | 5.972
2024-12-09 | 18:26 | Data | 0 | 32.946 | 30.658 | 187.896 | 7.63 | 176.594 | 2153.83 | 25.95 | 46.45 | 6.35 | 1.353 | 4.634 | 8508.57 | 2.113 | 97.8 | 77.4 | 1399 | 23.27 | 5530.6 | 2918.2 | 2813.3 | 4168 | 1199 | 0.68325 | 5.987
2024-12-09 | 18:26 | Data | 0 | 32.528 | 30.82 | 187.805 | 7.63 | 176.549 | 2152.02 | 25.96 | 46.269 | 6.35 | 1.351 | 4.641 | 8513.09 | 1.951 | 97.9 | 77.5 | 1400 | 23.13 | 5533.5 | 2922.1 | 2825.3 | 4181.7 | 1199 | 0.68164 | 5.992
2024-12-09 | 18:26 | Data | 0 | 32.723 | 30.651 | 187.851 | 7.63 | 176.594 | 2153.83 | 25.96 | 46.54 | 6.35 | 1.349 | 4.651 | 8513.09 | 2.066 | 97.8 | 77.5 | 1400 | 23.22 | 5533.5 | 2906.1 | 2827.3 | 4169.9 | 1199 | 0.68058 | 6.001
2024-12-09 | 18:26 | Data | 0 | 32.723 | 30.88 | 187.805 | 7.63 | 176.639 | 2153.83 | 25.95 | 46.54 | 6.35 | 1.356 | 4.659 | 8540.22 | 2.019 | 97.8 | 77.5 | 1399 | 23.27 | 5551.1 | 2897.6 | 2810 | 4148.7 | 1199 | 0.68187 | 6.015
2024-12-09 | 18:26 | Data | 0 | 32.926 | 30.705 | 187.896 | 7.63 | 176.639 | 2157.45 | 25.96 | 46.54 | 6.35 | 1.351 | 4.66 | 8531.18 | 2.012 | 97.8 | 77.5 | 1402 | 23.27 | 5545.3 | 2898.8 | 2795.1 | 4138.9 | 1199 | 0.68566 | 6.01
2024-12-09 | 18:27 | Data | 0 | 32.723 | 30.874 | 187.805 | 7.63 | 176.549 | 2153.83 | 25.97 | 46.45 | 6.35 | 1.343 | 4.654 | 8526.66 | 2.066 | 97.8 | 77.6 | 1399 | 23.18 | 5542.3 | 2906.2 | 2779.8 | 4136.7 | 1199 | 0.68594 | 5.997
2024-12-09 | 18:27 | Data | 0 | 32.777 | 30.867 | 187.896 | 7.63 | 176.685 | 2152.93 | 25.96 | 46.45 | 6.35 | 1.338 | 4.654 | 8531.18 | 1.958 | 97.8 | 77.7 | 1399 | 23.27 | 5545.3 | 2895.6 | 2808.8 | 4155.8 | 1199 | 0.67948 | 5.994
2024-12-09 | 18:27 | Data | 0 | 32.892 | 31.09 | 187.805 | 7.63 | 176.594 | 2152.02 | 25.96 | 46.45 | 6.35 | 1.341 | 4.665 | 8526.66 | 2.025 | 97.8 | 77.7 | 1399 | 23.22 | 5542.3 | 2901 | 2780.4 | 4137.9 | 1199 | 0.68441 | 6.007
2024-12-09 | 18:27 | Data | 0 | 32.561 | 30.543 | 187.805 | 7.63 | 176.594 | 2153.83 | 25.96 | 46.179 | 6.34 | 1.339 | 4.673 | 8517.61 | 1.958 | 97.9 | 77.7 | 1399 | 23.09 | 5536.4 | 2892.8 | 2767.7 | 4122.4 | 1199 | 0.68471 | 6.013
2024-12-09 | 18:27 | Data | 0 | 32.946 | 30.705 | 187.896 | 7.63 | 176.594 | 2151.12 | 25.96 | 46.269 | 6.35 | 1.345 | 4.637 | 8526.66 | 2.073 | 97.8 | 77.5 | 1398 | 23.13 | 5542.3 | 2896.2 | 2794.6 | 4138.9 | 1199 | 0.68375 | 5.981
2024-12-09 | 18:27 | Data | 0 | 32.514 | 30.867 | 187.941 | 7.63 | 176.639 | 2148.41 | 25.97 | 46.45 | 6.36 | 1.339 | 4.66 | 8531.18 | 1.904 | 97.8 | 77.7 | 1396 | 23.22 | 5545.3 | 2883.1 | 2802 | 4137.9 | 1199 | 0.67933 | 5.999
2024-12-09 | 18:27 | Data | 0 | 32.879 | 30.88 | 187.896 | 7.63 | 176.639 | 2146.6 | 25.96 | 46.54 | 6.35 | 1.339 | 4.68 | 8522.14 | 2.052 | 97.8 | 77.8 | 1395 | 23.27 | 5539.4 | 2913.2 | 2769.2 | 4129.4 | 1199 | 0.68883 | 6.02
2024-12-09 | 18:27 | Data | 0 | 32.98 | 30.772 | 187.851 | 7.63 | 176.685 | 2149.31 | 25.96 | 46.359 | 6.35 | 1.356 | 4.664 | 8522.14 | 2.12 | 97.8 | 77.5 | 1398 | 23.27 | 5539.4 | 1817.8 | 2210.3 | 2866.4 | 1199 | 0.62941 | 6.019
2024-12-09 | 18:27 | Data | 0 | 32.831 | 30.867 | 187.851 | 7.63 | 176.639 | 2151.12 | 25.97 | 46.45 | 6.35 | 1.356 | 4.645 | 8513.09 | 1.904 | 97.8 | 77.4 | 1397 | 23.27 | 5533.5 | 1818.2 | 2227.4 | 2887.4 | 1199 | 0.62518 | 6.001
2024-12-09 | 18:27 | Data | 0 | 32.953 | 30.691 | 187.805 | 7.63 | 176.639 | 2151.12 | 25.96 | 46.63 | 6.35 | 1.36 | 4.65 | 8526.66 | 2.086 | 97.8 | 77.4 | 1397 | 23.27 | 5542.3 | 1817 | 2234.6 | 2890.7 | 1199 | 0.62614 | 6.009
2024-12-09 | 18:27 | Data | 0 | 32.75 | 30.651 | 187.805 | 7.63 | 176.594 | 2144.79 | 25.96 | 46.811 | 6.35 | 1.345 | 4.654 | 8508.57 | 2.066 | 97.8 | 77.6 | 1394 | 23.36 | 5530.6 | 1814.2 | 2249.6 | 2900.3 | 1199 | 0.62371 | 5.998
2024-12-09 | 18:27 | Data | 0 | 33.169 | 30.995 | 187.851 | 7.63 | 176.639 | 2152.93 | 25.96 | 46.269 | 6.35 | 1.345 | 4.637 | 8508.57 | 2.012 | 97.9 | 77.5 | 1400 | 23.13 | 5530.6 | 1793.1 | 2236.6 | 2877.9 | 1199 | 0.62029 | 5.982
2024-12-09 | 18:27 | Data | 0 | 32.953 | 30.509 | 187.941 | 7.63 | 176.685 | 2147.51 | 25.95 | 46.179 | 6.35 | 1.348 | 4.654 | 8513.09 | 1.85 | 97.8 | 77.5 | 1396 | 23.09 | 5533.5 | 1812.6 | 2252.2 | 2889.2 | 1199 | 0.62397 | 6.004
2024-12-09 | 18:27 | Data | 0 | 33.149 | 30.793 | 187.986 | 7.63 | 176.639 | 2146.6 | 25.94 | 46.179 | 6.35 | 1.355 | 4.666 | 8495 | 2.127 | 97.8 | 77.5 | 1395 | 23.09 | 5521.8 | 1817.7 | 2238.6 | 2902.6 | 1199 | 0.62759 | 6.022
2024-12-09 | 18:27 | Data | 0 | 32.723 | 30.678 | 187.76 | 7.63 | 176.639 | 2147.51 | 25.96 | 46.179 | 6.35 | 1.336 | 4.655 | 8513.09 | 2.046 | 97.8 | 77.7 | 1395 | 23.09 | 5533.5 | 1821.3 | 2232.3 | 2893.8 | 1199 | 0.62623 | 5.992
2024-12-09 | 18:27 | Data | 0 | 32.669 | 30.982 | 187.851 | 7.63 | 176.594 | 2149.31 | 25.94 | 46.179 | 6.35 | 1.346 | 4.663 | 8495 | 2.113 | 97.9 | 77.6 | 1397 | 23.09 | 5521.8 | 1819.8 | 2256.4 | 2911.1 | 1199 | 0.62241 | 6.008
2024-12-09 | 18:27 | Data | 0 | 33.034 | 30.907 | 187.941 | 7.63 | 176.639 | 2146.6 | 25.94 | 46.269 | 6.35 | 1.348 | 4.664 | 8495 | 2.046 | 97.8 | 77.6 | 1395 | 23.09 | 5521.8 | 1820.9 | 2257.2 | 2909.8 | 1199 | 0.62178 | 6.012
2024-12-09 | 18:28 | Data | 0 | 32.885 | 30.968 | 187.941 | 7.64 | 176.639 | 2151.12 | 25.93 | 46.269 | 6.36 | 1.341 | 4.677 | 8517.61 | 2.154 | 97.9 | 77.7 | 1398 | 23.13 | 5536.4 | 1818.7 | 2298 | 2940.1 | 1199 | 0.61459 | 6.017
2024-12-09 | 18:28 | Data | 0 | 32.494 | 30.59 | 187.76 | 7.63 | 176.549 | 2149.31 | 25.94 | 46.269 | 6.35 | 1.339 | 4.671 | 8513.09 | 2.133 | 97.8 | 77.7 | 1396 | 23.18 | 5533.5 | 1818 | 2326.8 | 2964.2 | 1199 | 0.61051 | 6.008
2024-12-09 | 18:28 | Data | 0 | 32.609 | 30.853 | 187.805 | 7.63 | 176.459 | 2149.31 | 25.95 | 46.359 | 6.35 | 1.347 | 4.669 | 8513.09 | 2.025 | 97.8 | 77.6 | 1396 | 23.13 | 5533.5 | 1804.4 | 2316.9 | 2948.6 | 1199 | 0.60833 | 6.017
2024-12-09 | 18:28 | Data | 0 | 32.831 | 31.096 | 187.986 | 7.63 | 176.639 | 2147.51 | 25.94 | 46.269 | 6.35 | 1.352 | 4.683 | 8517.61 | 2.066 | 97.8 | 77.6 | 1395 | 23.09 | 5536.4 | 1820 | 2319.1 | 2947.1 | 1199 | 0.60799 | 6.034
2024-12-09 | 18:28 | Data | 0 | 32.723 | 30.82 | 187.715 | 7.63 | 176.549 | 2143.89 | 25.94 | 46.179 | 6.35 | 1.359 | 4.669 | 8513.09 | 2.019 | 97.8 | 77.5 | 1394 | 23.09 | 5533.5 | 1830.5 | 2307.3 | 2956.6 | 1199 | 0.61575 | 6.028
2024-12-09 | 18:28 | Data | 0 | 32.507 | 30.651 | 187.896 | 7.63 | 176.685 | 2147.51 | 25.94 | 46.359 | 6.35 | 1.348 | 4.647 | 8526.66 | 2.019 | 97.8 | 77.5 | 1396 | 23.18 | 5542.3 | 1819.1 | 2312.2 | 2951.1 | 1199 | 0.61427 | 5.996
2024-12-09 | 18:28 | Data | 0 | 32.548 | 30.543 | 187.851 | 7.63 | 176.459 | 2146.6 | 25.94 | 46.359 | 6.35 | 1.348 | 4.655 | 8522.14 | 2.127 | 97.8 | 77.5 | 1396 | 23.22 | 5539.4 | 1820.1 | 2307.2 | 2949 | 1199.1 | 0.61373 | 6.005
2024-12-09 | 18:28 | Data | 0 | 32.73 | 30.766 | 187.986 | 7.63 | 176.594 | 2151.12 | 25.94 | 46.359 | 6.35 | 1.348 | 4.656 | 8526.66 | 1.958 | 97.8 | 77.6 | 1398 | 23.09 | 5542.3 | 1820 | 2284 | 2931 | 1199.1 | 0.61864 | 6.004
2024-12-09 | 18:28 | Data | 0 | 32.973 | 30.718 | 187.805 | 7.63 | 176.639 | 2149.31 | 25.94 | 46.179 | 6.35 | 1.348 | 4.66 | 8531.18 | 2.066 | 97.8 | 77.6 | 1397 | 23.13 | 5545.3 | 1824.9 | 2273.6 | 2927.4 | 1199.1 | 0.62049 | 6.008
2024-12-09 | 18:28 | Data | 0 | 32.892 | 30.88 | 187.851 | 7.63 | 176.639 | 2153.83 | 25.94 | 46.179 | 6.35 | 1.345 | 4.651 | 8540.22 | 2.073 | 97.9 | 77.6 | 1400 | 23.09 | 5551.1 | 1813.3 | 2277.9 | 2925.1 | 1199.1 | 0.61736 | 5.998
2024-12-09 | 18:28 | Data | 0 | 32.602 | 30.442 | 187.76 | 7.63 | 176.549 | 2152.93 | 25.92 | 46.179 | 6.35 | 1.351 | 4.662 | 8540.22 | 2.066 | 97.9 | 77.6 | 1399 | 23.13 | 5551.1 | 1807.2 | 2249.6 | 2898.6 | 1199.1 | 0.62117 | 6.011
2024-12-09 | 18:28 | Data | 0 | 33.149 | 30.907 | 187.941 | 7.63 | 176.685 | 2146.6 | 25.95 | 46.269 | 6.35 | 1.356 | 4.658 | 8553.79 | 2.066 | 97.8 | 77.5 | 1396 | 23.13 | 5560 | 1813.6 | 2264.2 | 2911.9 | 1199.1 | 0.62135 | 6.014
2024-12-09 | 18:28 | Data | 0 | 32.825 | 30.759 | 187.805 | 7.63 | 176.594 | 2148.41 | 25.94 | 46.269 | 6.35 | 1.341 | 4.681 | 8544.75 | 2.032 | 97.9 | 77.7 | 1396 | 23.13 | 5554.1 | 1819.7 | 2289.8 | 2936.3 | 1199.1 | 0.61714 | 6.02
2024-12-09 | 18:28 | Data | 0 | 32.494 | 30.536 | 187.715 | 7.63 | 176.459 | 2148.41 | 25.94 | 46.45 | 6.35 | 1.351 | 4.639 | 8535.7 | 2.073 | 97.8 | 77.4 | 1396 | 23.22 | 5548.2 | 1819.6 | 2323.9 | 2962.4 | 1199.1 | 0.6118 | 5.992
2024-12-09 | 18:28 | Data | 0 | 32.723 | 30.651 | 187.805 | 7.63 | 176.459 | 2146.6 | 25.95 | 46.269 | 6.35 | 1.355 | 4.654 | 8553.79 | 1.897 | 97.8 | 77.5 | 1395 | 23.13 | 5560 | 1811.5 | 2309.8 | 2946.1 | 1199.1 | 0.61228 | 6.009
2024-12-09 | 18:28 | Data | 0 | 32.723 | 30.745 | 187.896 | 7.63 | 176.594 | 2149.31 | 25.95 | 46.179 | 6.35 | 1.358 | 4.659 | 8544.75 | 1.877 | 97.9 | 77.4 | 1398 | 23.09 | 5554.1 | 1814.4 | 2326 | 2961.1 | 1199.1 | 0.60971 | 6.017
2024-12-09 | 18:28 | Data | 0 | 32.609 | 30.644 | 187.67 | 7.63 | 176.459 | 2148.41 | 25.94 | 46.269 | 6.35 | 1.348 | 4.627 | 8540.22 | 2.046 | 97.8 | 77.4 | 1396 | 23.13 | 5551.1 | 1821.3 | 2302.5 | 2945.7 | 1199.1 | 0.61555 | 5.976
2024-12-09 | 18:28 | Data | 0 | 32.946 | 30.475 | 187.805 | 7.63 | 176.639 | 2148.41 | 25.92 | 46.179 | 6.35 | 1.339 | 4.648 | 8526.66 | 1.985 | 97.9 | 77.6 | 1396 | 23.09 | 5542.3 | 1820.2 | 2281.2 | 2929.7 | 1199.1 | 0.61876 | 5.986
2024-12-09 | 18:29 | Data | 0 | 32.501 | 30.442 | 187.851 | 7.63 | 176.594 | 2145.7 | 25.93 | 46.269 | 6.35 | 1.361 | 4.668 | 8540.22 | 2.268 | 97.8 | 77.4 | 1395 | 23.13 | 5551.1 | 1815.8 | 2264 | 2912.6 | 1199.1 | 0.62063 | 6.029
2024-12-09 | 18:29 | Data | 0 | 32.777 | 30.475 | 187.805 | 7.63 | 176.639 | 2147.51 | 25.93 | 46.269 | 6.35 | 1.353 | 4.677 | 8522.14 | 1.971 | 97.8 | 77.6 | 1396 | 23.18 | 5539.4 | 1813.1 | 2251.1 | 2901.2 | 1199.1 | 0.62238 | 6.029
2024-12-09 | 18:29 | Data | 0 | 32.609 | 30.428 | 187.67 | 7.63 | 176.549 | 2147.51 | 25.95 | 46.179 | 6.35 | 1.349 | 4.64 | 8526.66 | 2.032 | 97.8 | 77.5 | 1395 | 23.04 | 5542.3 | 1808.6 | 2264.3 | 2909.6 | 1199.1 | 0.61921 | 5.989
2024-12-09 | 18:29 | Data | 0 | 32.892 | 30.752 | 187.76 | 7.63 | 176.459 | 2146.6 | 25.94 | 46.179 | 6.35 | 1.358 | 4.616 | 8526.66 | 2.16 | 97.8 | 77.3 | 1396 | 23.13 | 5542.3 | 1809.8 | 2253.4 | 2904.1 | 1199.1 | 0.62049 | 5.971
2024-12-09 | 18:29 | Data | 0 | 32.919 | 30.766 | 187.805 | 7.63 | 176.639 | 2145.7 | 25.95 | 46.269 | 6.35 | 1.357 | 4.632 | 8526.66 | 2.1 | 97.8 | 77.3 | 1395 | 23.13 | 5542.3 | 1793.7 | 2288.1 | 2920 | 1199.1 | 0.61124 | 5.988
2024-12-09 | 18:29 | Data | 0 | 32.71 | 30.536 | 187.805 | 7.63 | 176.549 | 2147.51 | 25.95 | 46.179 | 6.35 | 1.355 | 4.647 | 8553.79 | 2.133 | 97.8 | 77.4 | 1395 | 23.13 | 5560 | 1801.5 | 2305.8 | 2935.7 | 1199.1 | 0.61089 | 6.001
2024-12-09 | 18:29 | Data | 0 | 32.514 | 30.739 | 187.805 | 7.63 | 176.594 | 2144.79 | 25.94 | 46.269 | 6.34 | 1.337 | 4.638 | 8553.79 | 2.012 | 97.8 | 77.6 | 1394 | 23.13 | 5560 | 1816.8 | 2329.1 | 2965.8 | 1199.1 | 0.61014 | 5.975
2024-12-09 | 18:29 | Data | 0 | 32.379 | 30.577 | 187.805 | 7.63 | 176.549 | 2144.79 | 25.94 | 46.269 | 6.35 | 1.355 | 4.654 | 8513.09 | 1.931 | 97.8 | 77.4 | 1395 | 23.09 | 5533.5 | 1829.8 | 2336.8 | 2978.6 | 1199.1 | 0.61132 | 6.007
2024-12-09 | 18:29 | Data | 0 | 32.561 | 30.651 | 187.76 | 7.63 | 176.549 | 2144.79 | 25.95 | 46.269 | 6.35 | 1.363 | 4.668 | 8495 | 1.85 | 97.8 | 77.4 | 1395 | 23.09 | 5521.8 | 1807.4 | 2329.7 | 2960.3 | 1199.1 | 0.60769 | 6.031
2024-12-09 | 18:29 | Data | 0 | 32.494 | 30.644 | 187.624 | 7.63 | 176.368 | 2143.89 | 25.95 | 46.179 | 6.36 | 1.348 | 4.672 | 8495 | 1.965 | 97.8 | 77.6 | 1394 | 23.09 | 5521.8 | 1838.5 | 2295.3 | 2950.7 | 1199.1 | 0.62049 | 6.02
2024-12-09 | 18:29 | Data | 0 | 32.494 | 30.651 | 187.805 | 7.63 | 176.459 | 2143.89 | 25.94 | 46.179 | 6.35 | 1.346 | 4.641 | 8490.48 | 2.174 | 97.8 | 77.5 | 1395 | 23.13 | 5518.8 | 1829.6 | 2254 | 2913.9 | 1199.1 | 0.62544 | 5.989
2024-12-09 | 18:29 | Data | 0 | 32.494 | 30.644 | 187.76 | 7.63 | 176.549 | 2144.79 | 25.93 | 46.179 | 6.35 | 1.353 | 4.636 | 8472.39 | 1.965 | 97.8 | 77.4 | 1394 | 23.09 | 5507.1 | 1823.2 | 2250.2 | 2908.1 | 1199.1 | 0.62411 | 5.988
2024-12-09 | 18:29 | Data | 0 | 32.609 | 30.475 | 187.805 | 7.63 | 176.549 | 2142.08 | 25.93 | 46.269 | 6.35 | 1.356 | 4.629 | 8485.96 | 2.032 | 97.8 | 77.3 | 1393 | 23.13 | 5515.9 | 1809 | 2293.3 | 2932.4 | 1199.1 | 0.61463 | 5.985
2024-12-09 | 18:29 | Data | 0 | 32.474 | 30.529 | 187.67 | 7.63 | 176.549 | 2143.89 | 25.94 | 46.269 | 6.35 | 1.358 | 4.655 | 8467.87 | 2.16 | 97.8 | 77.4 | 1394 | 23.18 | 5504.1 | 1825.7 | 2313.1 | 2957.9 | 1199.1 | 0.61422 | 6.013
2024-12-09 | 18:29 | Data | 0 | 32.494 | 30.813 | 187.76 | 7.63 | 176.549 | 2144.79 | 25.94 | 46.359 | 6.35 | 1.359 | 4.668 | 8436.21 | 2.052 | 97.8 | 77.4 | 1394 | 23.18 | 5483.5 | 1823.3 | 2312.9 | 2956.1 | 1199.1 | 0.61627 | 6.026
2024-12-09 | 18:29 | Data | 0 | 32.494 | 30.644 | 187.67 | 7.63 | 176.413 | 2145.7 | 25.94 | 46.179 | 6.35 | 1.347 | 4.654 | 8467.87 | 2.052 | 97.8 | 77.6 | 1394 | 23.13 | 5504.1 | 1812.9 | 2315.1 | 2951.9 | 1199.1 | 0.61169 | 6
2024-12-09 | 18:29 | Data | 0 | 32.723 | 30.651 | 187.76 | 7.63 | 176.459 | 2145.7 | 25.92 | 46.179 | 6.36 | 1.358 | 4.656 | 8454.3 | 2.073 | 97.8 | 77.4 | 1394 | 23.09 | 5495.3 | 1828.9 | 2313.4 | 2959.2 | 1199.1 | 0.61546 | 6.013
2024-12-09 | 18:29 | Data | 0 | 32.285 | 30.644 | 187.715 | 7.63 | 176.413 | 2143.89 | 25.96 | 46.179 | 6.35 | 1.351 | 4.662 | 8458.83 | 1.83 | 97.8 | 77.5 | 1394 | 23.09 | 5498.2 | 1827.4 | 2293.2 | 2942.9 | 1199.1 | 0.6166 | 6.013
2024-12-09 | 18:30 | Data | 0 | 32.831 | 30.813 | 187.896 | 7.63 | 176.459 | 2144.79 | 25.94 | 46.269 | 6.35 | 1.349 | 4.652 | 8449.78 | 1.83 | 97.8 | 77.5 | 1394 | 23.13 | 5492.4 | 1810.3 | 2285.9 | 2928.4 | 1199.1 | 0.61501 | 6
2024-12-09 | 18:30 | Data | 0 | 32.696 | 30.651 | 187.715 | 7.63 | 176.549 | 2144.79 | 25.94 | 46.54 | 6.35 | 1.352 | 4.656 | 8472.39 | 2.059 | 97.8 | 77.5 | 1395 | 23.22 | 5507.1 | 1812.9 | 2266.9 | 2915 | 1199.1 | 0.61955 | 6.007
2024-12-09 | 18:30 | Data | 0 | 32.312 | 30.415 | 187.805 | 7.63 | 176.459 | 2144.79 | 25.95 | 46.54 | 6.35 | 1.357 | 4.664 | 8467.87 | 1.857 | 97.8 | 77.5 | 1394 | 23.22 | 5504.1 | 1811.8 | 2260.7 | 2907.5 | 1199.1 | 0.62086 | 6.02
2024-12-09 | 18:30 | Data | 0 | 32.609 | 30.82 | 187.715 | 7.63 | 176.413 | 2144.79 | 25.92 | 46.45 | 6.35 | 1.351 | 4.641 | 8458.83 | 2.025 | 97.8 | 77.5 | 1394 | 23.22 | 5498.2 | 1816.5 | 2289.1 | 2934 | 1199.1 | 0.61639 | 5.992
2024-12-09 | 18:30 | Data | 0 | 32.555 | 30.624 | 187.76 | 7.63 | 176.459 | 2144.79 | 25.93 | 46.45 | 6.35 | 1.348 | 4.657 | 8445.26 | 1.965 | 97.8 | 77.6 | 1394 | 23.22 | 5489.4 | 1819.1 | 2286.8 | 2934.6 | 1199.1 | 0.61567 | 6.002
2024-12-09 | 18:30 | Data | 0 | 32.413 | 30.644 | 187.715 | 7.63 | 176.459 | 2143.89 | 25.93 | 46.45 | 6.35 | 1.345 | 4.659 | 8436.21 | 1.836 | 97.8 | 77.6 | 1394 | 23.18 | 5483.5 | 1818.6 | 2313 | 2951.9 | 1199.1 | 0.61382 | 6.005
2024-12-09 | 18:30 | Data | 0 | 32.339 | 30.374 | 187.805 | 7.63 | 176.459 | 2144.79 | 25.92 | 46.45 | 6.34 | 1.344 | 4.672 | 8458.83 | 1.897 | 97.8 | 77.6 | 1394 | 23.27 | 5498.2 | 3210.6 | 3216.5 | 4198.4 | 1199.1 | 0.6597 | 6.017
2024-12-09 | 18:30 | Data | 0 | 32.75 | 30.874 | 187.805 | 7.63 | 176.549 | 2145.7 | 25.93 | 46.45 | 6.35 | 1.352 | 4.673 | 8445.26 | 2.228 | 97.8 | 77.5 | 1394 | 23.22 | 5489.4 | 2882.4 | 2860.5 | 4180.8 | 1199.1 | 0.67158 | 6.026
2024-12-09 | 18:30 | Data | 0 | 32.582 | 30.428 | 187.715 | 7.63 | 176.368 | 2145.7 | 25.92 | 46.63 | 6.35 | 1.359 | 4.663 | 8467.87 | 2.066 | 97.8 | 77.4 | 1395 | 23.22 | 5504.1 | 2880.8 | 2864.5 | 4180.5 | 1199.1 | 0.67094 | 6.021
2024-12-09 | 18:30 | Data | 0 | 32.946 | 30.502 | 187.76 | 7.63 | 176.594 | 2147.51 | 25.93 | 46.54 | 6.35 | 1.351 | 4.662 | 8440.74 | 2.133 | 97.8 | 77.5 | 1395 | 23.32 | 5486.5 | 2896.2 | 2886.3 | 4205 | 1199.1 | 0.67191 | 6.013
2024-12-09 | 18:30 | Data | 0 | 32.75 | 30.705 | 187.805 | 7.63 | 176.549 | 2147.51 | 25.93 | 46.45 | 6.35 | 1.348 | 4.666 | 8445.26 | 1.857 | 97.8 | 77.6 | 1395 | 23.22 | 5489.4 | 2908.6 | 2873.8 | 4206 | 1199.1 | 0.67423 | 6.015
2024-12-09 | 18:30 | Data | 0 | 32.696 | 30.853 | 187.76 | 7.63 | 176.459 | 2146.6 | 25.92 | 46.45 | 6.35 | 1.349 | 4.656 | 8440.74 | 2.019 | 97.8 | 77.5 | 1396 | 23.22 | 5486.5 | 2901.4 | 2902 | 4222.4 | 1199.1 | 0.67053 | 6.006
2024-12-09 | 18:30 | Data | 0 | 32.946 | 30.88 | 187.851 | 7.63 | 176.594 | 2148.41 | 25.93 | 46.54 | 6.35 | 1.351 | 4.643 | 8458.83 | 2.073 | 97.8 | 77.5 | 1396 | 23.27 | 5498.2 | 2889.5 | 2852.7 | 4180.9 | 1199.1 | 0.67374 | 5.994
2024-12-09 | 18:30 | Data | 0 | 32.69 | 30.556 | 187.76 | 7.63 | 176.459 | 2147.51 | 25.93 | 46.54 | 6.35 | 1.348 | 4.671 | 8454.3 | 2.086 | 97.8 | 77.6 | 1395 | 23.27 | 5495.3 | 2897.6 | 2872.7 | 4197.3 | 1199.1 | 0.673 | 6.017
2024-12-09 | 18:30 | Data | 0 | 32.494 | 30.867 | 187.76 | 7.63 | 176.549 | 2143.89 | 25.92 | 46.54 | 6.35 | 1.349 | 4.645 | 8449.78 | 1.998 | 97.8 | 77.5 | 1394 | 23.27 | 5492.4 | 2896.5 | 2868.4 | 4196.3 | 1199.1 | 0.67276 | 5.996
2024-12-09 | 18:30 | Data | 0 | 32.298 | 30.86 | 187.896 | 7.63 | 176.459 | 2147.51 | 25.92 | 46.45 | 6.35 | 1.348 | 4.687 | 8449.78 | 1.789 | 97.8 | 77.6 | 1396 | 23.22 | 5492.4 | 2897.6 | 2869.3 | 4195.1 | 1199.1 | 0.66922 | 6.036
2024-12-09 | 18:30 | Data | 0 | 32.494 | 30.415 | 187.67 | 7.63 | 176.413 | 2146.6 | 25.93 | 46.45 | 6.34 | 1.36 | 4.673 | 8485.96 | 2.079 | 97.8 | 77.5 | 1395 | 23.22 | 5515.9 | 2908.9 | 2848.1 | 4183.7 | 1199.1 | 0.67799 | 6.035
2024-12-09 | 18:30 | Data | 0 | 32.474 | 31.009 | 187.715 | 7.63 | 176.459 | 2147.51 | 25.92 | 46.269 | 6.35 | 1.349 | 4.635 | 8495 | 1.87 | 97.8 | 77.4 | 1396 | 23.09 | 5521.8 | 2899.9 | 2850.7 | 4182 | 1199.1 | 0.67594 | 5.986
2024-12-09 | 18:31 | Data | 0 | 32.069 | 30.415 | 187.851 | 7.63 | 176.459 | 2148.41 | 25.91 | 46.45 | 6.35 | 1.352 | 4.645 | 8684.94 | 1.823 | 97.8 | 77.5 | 1396 | 23.22 | 5645.2 | 2904.2 | 2868.8 | 4197.5 | 1199.1 | 0.67447 | 5.997
2024-12-09 | 18:31 | Data | 0 | 32.879 | 30.597 | 187.896 | 7.63 | 176.594 | 2147.51 | 25.91 | 46.269 | 6.35 | 1.352 | 4.666 | 8693.98 | 2.025 | 97.8 | 77.5 | 1396 | 23.13 | 5651.1 | 2894.5 | 2897.2 | 4213.1 | 1199.1 | 0.66957 | 6.018
2024-12-09 | 18:31 | Data | 0 | 32.595 | 30.536 | 187.76 | 7.63 | 176.368 | 2147.51 | 25.91 | 46.269 | 6.34 | 1.345 | 4.654 | 8689.46 | 2.275 | 97.8 | 77.6 | 1396 | 23.13 | 5648.1 | 2892.9 | 2885.4 | 4200.2 | 1199.2 | 0.6717 | 5.998
2024-12-09 | 18:31 | Data | 0 | 32.609 | 30.739 | 187.76 | 7.63 | 176.549 | 2146.6 | 25.92 | 45.998 | 6.35 | 1.356 | 4.643 | 8680.41 | 1.992 | 97.9 | 77.4 | 1396 | 22.95 | 5642.3 | 2924.7 | 2879.8 | 4216.4 | 1199.2 | 0.67599 | 5.998
2024-12-09 | 18:31 | Data | 0 | 32.561 | 30.415 | 187.715 | 7.63 | 176.413 | 2147.51 | 25.9 | 46.179 | 6.35 | 1.346 | 4.633 | 8481.44 | 1.978 | 97.8 | 77.5 | 1396 | 23.13 | 5512.9 | 2894.9 | 2897.2 | 4209.3 | 1199.2 | 0.67054 | 5.979
2024-12-09 | 18:31 | Data | 0 | 32.413 | 30.421 | 187.715 | 7.63 | 176.459 | 2147.51 | 25.9 | 46.179 | 6.35 | 1.343 | 4.659 | 8490.48 | 1.863 | 97.8 | 77.6 | 1395 | 23.13 | 5518.8 | 2906.5 | 2861.8 | 4197.3 | 1199.2 | 0.67486 | 6.002
2024-12-09 | 18:31 | Data | 0 | 32.494 | 30.637 | 187.67 | 7.63 | 176.413 | 2147.51 | 25.92 | 46.089 | 6.34 | 1.345 | 4.663 | 8499.53 | 1.931 | 97.8 | 77.6 | 1396 | 23.13 | 5524.7 | 2877.1 | 2857.4 | 4172 | 1199.2 | 0.6713 | 6.007
2024-12-09 | 18:31 | Data | 0 | 32.953 | 30.651 | 187.805 | 7.63 | 176.639 | 2147.51 | 25.89 | 46.269 | 6.35 | 1.353 | 4.68 | 8490.48 | 1.877 | 97.8 | 77.6 | 1396 | 23.13 | 5518.8 | 2884.7 | 2877.9 | 4194.8 | 1199.2 | 0.66963 | 6.031
2024-12-09 | 18:31 | Data | 0 | 32.663 | 30.489 | 187.851 | 7.63 | 176.639 | 2146.6 | 25.92 | 46.269 | 6.35 | 1.363 | 4.672 | 8499.53 | 2.046 | 97.8 | 77.4 | 1395 | 23.13 | 5524.7 | 2897.8 | 2842.6 | 4176.8 | 1199.2 | 0.67742 | 6.034
2024-12-09 | 18:31 | Data | 0 | 32.94 | 30.867 | 187.76 | 7.63 | 176.549 | 2147.51 | 25.93 | 46.089 | 6.35 | 1.358 | 4.659 | 8495 | 1.971 | 97.8 | 77.4 | 1396 | 23.09 | 5521.8 | 2903.6 | 2846.2 | 4181 | 1199.2 | 0.67705 | 6.017
2024-12-09 | 18:31 | Data | 0 | 32.933 | 30.664 | 187.76 | 7.63 | 176.459 | 2146.6 | 25.92 | 46.179 | 6.35 | 1.346 | 4.646 | 8467.87 | 2.154 | 97.8 | 77.5 | 1396 | 23.13 | 5504.1 | 2905 | 2877.4 | 4187.6 | 1199.2 | 0.67683 | 5.993
2024-12-09 | 18:31 | Data | 0 | 32.44 | 30.529 | 187.715 | 7.63 | 176.413 | 2143.89 | 25.93 | 46.359 | 6.35 | 1.348 | 4.625 | 8481.44 | 2.073 | 97.8 | 77.4 | 1394 | 23.13 | 5512.9 | 2894.6 | 2871 | 4194.5 | 1199.2 | 0.67638 | 5.975
2024-12-09 | 18:31 | Data | 0 | 32.818 | 30.651 | 187.715 | 7.63 | 176.459 | 2144.79 | 25.92 | 46.179 | 6.35 | 1.347 | 4.635 | 8481.44 | 2.12 | 97.8 | 77.5 | 1394 | 23.13 | 5512.9 | 2893.1 | 2896.7 | 4212.2 | 1199.2 | 0.66933 | 5.981
2024-12-09 | 18:31 | Data | 0 | 32.723 | 30.428 | 187.624 | 7.63 | 176.549 | 2144.79 | 25.92 | 46.269 | 6.35 | 1.343 | 4.653 | 8467.87 | 2.133 | 97.8 | 77.6 | 1395 | 23.13 | 5504.1 | 2906.6 | 2871.7 | 4201.9 | 1199.2 | 0.67493 | 5.996
2024-12-09 | 18:31 | Data | 0 | 33.122 | 30.55 | 187.851 | 7.63 | 176.639 | 2152.93 | 25.93 | 46.179 | 6.35 | 1.347 | 4.662 | 8472.39 | 2.154 | 97.9 | 77.6 | 1399 | 23.09 | 5507.1 | 2908.4 | 2883.7 | 4211.5 | 1199.2 | 0.67339 | 6.007
2024-12-09 | 18:31 | Data | 0 | 32.696 | 30.651 | 187.715 | 7.63 | 176.549 | 2143.89 | 25.93 | 46.269 | 6.35 | 1.355 | 4.672 | 8472.39 | 2.066 | 97.8 | 77.5 | 1394 | 23.13 | 5507.1 | 2904.4 | 2904.1 | 4224.8 | 1199.2 | 0.66973 | 6.026
2024-12-09 | 18:31 | Data | 0 | 32.548 | 30.651 | 187.715 | 7.63 | 176.459 | 2152.93 | 25.93 | 46.089 | 6.35 | 1.346 | 4.649 | 8454.3 | 1.87 | 97.9 | 77.6 | 1399 | 23.04 | 5495.3 | 2877.4 | 2893.6 | 4197.6 | 1199.2 | 0.67022 | 5.995
2024-12-09 | 18:32 | Data | 0 | 32.48 | 30.536 | 187.851 | 7.63 | 176.459 | 2146.6 | 25.92 | 46.269 | 6.35 | 1.354 | 4.663 | 8467.87 | 2.073 | 97.8 | 77.5 | 1396 | 23.09 | 5504.1 | 2909.6 | 2871.3 | 4202.4 | 1199.2 | 0.67546 | 6.017
2024-12-09 | 18:32 | Data | 0 | 32.521 | 30.475 | 187.76 | 7.63 | 176.413 | 2147.51 | 25.92 | 46.269 | 6.35 | 1.342 | 4.683 | 8458.83 | 1.958 | 97.8 | 77.7 | 1396 | 23.13 | 5498.2 | 2899.1 | 2897 | 4209.1 | 1199.2 | 0.67126 | 6.026
2024-12-09 | 18:32 | Data | 0 | 32.271 | 30.536 | 187.896 | 7.63 | 176.459 | 2147.51 | 25.92 | 46.269 | 6.35 | 1.346 | 4.662 | 8454.3 | 2.046 | 97.8 | 77.6 | 1396 | 23.13 | 5495.3 | 2897.3 | 2895.6 | 4214 | 1199.2 | 0.67169 | 6.007
2024-12-09 | 18:32 | Data | 0 | 32.933 | 30.664 | 187.805 | 7.63 | 176.639 | 2146.6 | 25.93 | 46.269 | 6.35 | 1.348 | 4.628 | 8495 | 2.174 | 97.8 | 77.4 | 1395 | 23.13 | 5521.8 | 2894.3 | 2888.3 | 4207.5 | 1199.2 | 0.66899 | 5.976
2024-12-09 | 18:32 | Data | 0 | 32.669 | 30.428 | 187.76 | 7.63 | 176.413 | 2147.51 | 25.93 | 46.089 | 6.35 | 1.341 | 4.632 | 8499.53 | 2.079 | 97.8 | 77.6 | 1396 | 23.09 | 5524.7 | 2896.5 | 2874.9 | 4200.2 | 1199.2 | 0.67185 | 5.973
2024-12-09 | 18:32 | Data | 0 | 32.386 | 30.651 | 187.715 | 7.63 | 176.459 | 2146.6 | 25.92 | 46.269 | 6.36 | 1.354 | 4.635 | 8499.53 | 2.12 | 97.8 | 77.4 | 1396 | 23.09 | 5524.7 | 2908.1 | 2870.1 | 4198.7 | 1199.2 | 0.67594 | 5.988
2024-12-09 | 18:32 | Data | 0 | 32.501 | 30.259 | 187.76 | 7.63 | 176.459 | 2144.79 | 25.92 | 46.269 | 6.35 | 1.353 | 4.638 | 8495 | 2.025 | 97.9 | 77.4 | 1395 | 23.09 | 5521.8 | 2882.6 | 2877.7 | 4190.6 | 1199.2 | 0.6733 | 5.99
2024-12-09 | 18:32 | Data | 0 | 32.723 | 30.536 | 187.805 | 7.63 | 176.413 | 2145.7 | 25.92 | 46.269 | 6.35 | 1.346 | 4.645 | 8431.69 | 1.985 | 97.8 | 77.5 | 1395 | 23.09 | 5480.6 | 2924.9 | 2867.2 | 4209 | 1199.2 | 0.67828 | 5.99
2024-12-09 | 18:32 | Data | 0 | 32.352 | 30.415 | 187.715 | 7.63 | 176.459 | 2145.7 | 25.92 | 46.269 | 6.36 | 1.354 | 4.667 | 8445.26 | 1.863 | 97.8 | 77.5 | 1395 | 23.13 | 5489.4 | 2904.2 | 2874.6 | 4201.7 | 1199.2 | 0.67312 | 6.021
2024-12-09 | 18:32 | Data | 0 | 32.609 | 30.793 | 187.851 | 7.63 | 176.639 | 2144.79 | 25.94 | 46.179 | 6.35 | 1.358 | 4.66 | 8436.21 | 2.005 | 97.9 | 77.4 | 1394 | 23.09 | 5483.5 | 2891.5 | 2874.9 | 4195 | 1199.2 | 0.67037 | 6.017
2024-12-09 | 18:32 | Data | 0 | 32.622 | 30.543 | 187.805 | 7.63 | 176.594 | 2146.6 | 25.92 | 46.179 | 6.35 | 1.349 | 4.651 | 8445.26 | 2.079 | 97.8 | 77.5 | 1396 | 23.13 | 5489.4 | 2913.9 | 2883.4 | 4213.7 | 1199.2 | 0.67381 | 6
2024-12-09 | 18:32 | Data | 0 | 32.528 | 30.624 | 187.67 | 7.63 | 176.459 | 2146.6 | 25.93 | 46.179 | 6.35 | 1.345 | 4.647 | 8463.35 | 1.85 | 97.8 | 77.6 | 1396 | 23.09 | 5501.2 | 2914.4 | 2883.7 | 4217.7 | 1199.2 | 0.67407 | 5.992
2024-12-09 | 18:32 | Data | 0 | 32.312 | 30.806 | 187.851 | 7.63 | 176.639 | 2147.51 | 25.92 | 46.179 | 6.35 | 1.343 | 4.654 | 8467.87 | 1.85 | 97.8 | 77.6 | 1396 | 23.09 | 5504.1 | 2920.1 | 2915.6 | 4242.7 | 1199.2 | 0.67095 | 5.997
2024-12-09 | 18:32 | Data | 0 | 32.784 | 30.651 | 187.851 | 7.63 | 176.459 | 2141.18 | 25.93 | 46.359 | 6.35 | 1.341 | 4.682 | 8481.44 | 2.086 | 97.8 | 77.7 | 1392 | 23.18 | 5512.9 | 2907.7 | 2887.7 | 4211.8 | 1199.2 | 0.67349 | 6.023
2024-12-09 | 18:32 | Data | 0 | 32.717 | 30.428 | 187.805 | 7.63 | 176.459 | 2144.79 | 25.93 | 46.269 | 6.34 | 1.344 | 4.655 | 8467.87 | 2.106 | 97.8 | 77.6 | 1394 | 23.13 | 5504.1 | 2897.4 | 2868.2 | 4195.3 | 1199.2 | 0.67362 | 6.001
2024-12-09 | 18:32 | Data | 0 | 32.494 | 30.421 | 187.624 | 7.63 | 176.549 | 2142.99 | 25.93 | 46.269 | 6.35 | 1.345 | 4.642 | 8445.26 | 2.167 | 97.8 | 77.5 | 1394 | 23.09 | 5489.4 | 2912.2 | 2868.4 | 4202.2 | 1199.2 | 0.67607 | 5.987
2024-12-09 | 18:32 | Data | 0 | 32.494 | 30.415 | 187.715 | 7.63 | 176.549 | 2146.6 | 25.93 | 46.359 | 6.35 | 1.347 | 4.67 | 8454.3 | 2.079 | 97.8 | 77.6 | 1396 | 23.18 | 5495.3 | 2906.1 | 2830 | 4174 | 1199.2 | 0.67911 | 6.017
2024-12-09 | 18:32 | Data | 0 | 32.892 | 30.678 | 187.805 | 7.63 | 176.549 | 2142.99 | 25.93 | 46.45 | 6.35 | 1.348 | 4.657 | 8454.3 | 2.039 | 97.8 | 77.5 | 1394 | 23.27 | 5495.3 | 2904.1 | 2878.7 | 4206.7 | 1199.2 | 0.66893 | 6.006
2024-12-09 | 18:33 | Data | 0 | 32.453 | 30.705 | 187.851 | 7.63 | 176.459 | 2147.51 | 25.92 | 46.359 | 6.35 | 1.342 | 4.66 | 8472.39 | 2.059 | 97.8 | 77.6 | 1395 | 23.13 | 5507.1 | 2908 | 2857.3 | 4191.2 | 1199.2 | 0.67636 | 6.002
2024-12-09 | 18:33 | Data | 0 | 32.501 | 30.421 | 187.715 | 7.63 | 176.459 | 2152.02 | 25.92 | 46.45 | 6.35 | 1.357 | 4.635 | 8481.44 | 2.066 | 97.8 | 77.4 | 1398 | 23.18 | 5512.9 | 2913 | 2882.1 | 4211.4 | 1199.2 | 0.67597 | 5.991
2024-12-09 | 18:33 | Data | 0 | 32.696 | 30.651 | 187.896 | 7.63 | 176.685 | 2147.51 | 25.93 | 46.54 | 6.35 | 1.358 | 4.665 | 8490.48 | 2.059 | 97.8 | 77.5 | 1395 | 23.27 | 5518.8 | 2904.7 | 2884.1 | 4210.5 | 1199.2 | 0.67171 | 6.02
2024-12-09 | 18:33 | Data | 0 | 32.656 | 30.604 | 187.67 | 7.63 | 176.413 | 2154.74 | 25.93 | 46.269 | 6.35 | 1.343 | 4.695 | 8472.39 | 2.113 | 97.9 | 77.7 | 1401 | 23.13 | 5507.1 | 2888 | 2864.7 | 4188.3 | 1199.2 | 0.6725 | 6.039
2024-12-09 | 18:33 | Data | 0 | 32.501 | 30.847 | 187.851 | 7.63 | 176.594 | 2149.31 | 25.92 | 46.269 | 6.35 | 1.347 | 4.673 | 8467.87 | 1.87 | 97.8 | 77.6 | 1396 | 23.13 | 5504.1 | 2890.5 | 2886.8 | 4203.6 | 1199.3 | 0.66997 | 6.02
2024-12-09 | 18:33 | Data | 0 | 32.946 | 30.712 | 187.851 | 7.63 | 176.594 | 2151.12 | 25.93 | 46.269 | 6.35 | 1.349 | 4.667 | 8490.48 | 2.066 | 97.9 | 77.6 | 1398 | 23.09 | 5518.8 | 2894.1 | 2855.6 | 4183.1 | 1199.3 | 0.67367 | 6.017
2024-12-09 | 18:33 | Data | 0 | 32.663 | 30.475 | 187.715 | 7.63 | 176.549 | 2149.31 | 25.93 | 46.089 | 6.35 | 1.351 | 4.652 | 8485.96 | 2.073 | 97.9 | 77.5 | 1398 | 23.09 | 5515.9 | 2902.7 | 2867.5 | 4199.6 | 1199.3 | 0.6722 | 6.004
2024-12-09 | 18:33 | Data | 0 | 32.399 | 30.415 | 187.805 | 7.63 | 176.549 | 2149.31 | 25.92 | 46.269 | 6.35 | 1.351 | 4.65 | 8495 | 1.884 | 97.8 | 77.5 | 1398 | 23.13 | 5521.8 | 2893.9 | 2877.6 | 4196.2 | 1199.3 | 0.67296 | 6.001
2024-12-09 | 18:33 | Data | 0 | 32.717 | 30.219 | 187.67 | 7.63 | 176.459 | 2147.51 | 25.93 | 46.179 | 6.34 | 1.358 | 4.667 | 8472.39 | 2.079 | 97.8 | 77.5 | 1396 | 23.13 | 5507.1 | 2886.4 | 2831 | 4162.1 | 1199.3 | 0.67637 | 6.026
2024-12-09 | 18:33 | Data | 0 | 32.811 | 30.874 | 187.76 | 7.63 | 176.639 | 2146.6 | 25.92 | 46.269 | 6.35 | 1.344 | 4.64 | 8508.57 | 2.039 | 97.8 | 77.5 | 1395 | 23.13 | 5530.6 | 2882.3 | 2839.2 | 4162.1 | 1199.3 | 0.67528 | 5.983
2024-12-09 | 18:33 | Data | 0 | 32.629 | 30.421 | 187.76 | 7.63 | 176.549 | 2147.51 | 25.93 | 46.269 | 6.35 | 1.357 | 4.634 | 8513.09 | 1.965 | 97.8 | 77.4 | 1396 | 23.09 | 5533.5 | 2890.4 | 2866.9 | 4188.9 | 1199.3 | 0.67185 | 5.99
2024-12-09 | 18:33 | Data | 0 | 32.514 | 30.651 | 187.851 | 7.63 | 176.594 | 2146.6 | 25.92 | 46.269 | 6.35 | 1.347 | 4.65 | 8490.48 | 1.958 | 97.8 | 77.6 | 1395 | 23.09 | 5518.8 | 2889.2 | 2847 | 4175.5 | 1199.3 | 0.67508 | 5.996
2024-12-09 | 18:33 | Data | 0 | 32.609 | 30.637 | 187.76 | 7.63 | 176.549 | 2146.6 | 25.94 | 46.269 | 6.35 | 1.348 | 4.679 | 8490.48 | 1.863 | 97.8 | 77.6 | 1395 | 23.09 | 5518.8 | 2900.2 | 2872.3 | 4201.8 | 1199.3 | 0.67279 | 6.028
2024-12-09 | 18:33 | Data | 0 | 32.94 | 30.563 | 187.851 | 7.63 | 176.594 | 2147.51 | 25.93 | 46.179 | 6.35 | 1.34 | 4.649 | 8458.83 | 2.187 | 97.8 | 77.6 | 1395 | 23.09 | 5498.2 | 2898.8 | 2895.9 | 4213.1 | 1199.3 | 0.6704 | 5.989
2024-12-09 | 18:33 | Data | 0 | 32.494 | 30.536 | 187.67 | 7.63 | 176.549 | 2144.79 | 25.93 | 46.269 | 6.35 | 1.352 | 4.646 | 8463.35 | 2.167 | 97.8 | 77.5 | 1394 | 23.13 | 5501.2 | 2896.3 | 2898.3 | 4213.2 | 1199.3 | 0.66969 | 5.998
2024-12-09 | 18:33 | Data | 0 | 32.723 | 30.644 | 187.805 | 7.63 | 176.459 | 2144.79 | 25.92 | 46.089 | 6.35 | 1.348 | 4.663 | 8467.87 | 1.884 | 97.9 | 77.6 | 1394 | 23 | 5504.1 | 2902.5 | 2880.6 | 4210.4 | 1199.3 | 0.67791 | 6.01
2024-12-09 | 18:33 | Data | 0 | 32.717 | 30.651 | 187.805 | 7.63 | 176.549 | 2145.7 | 25.92 | 46.179 | 6.35 | 1.344 | 4.67 | 8463.35 | 1.87 | 97.8 | 77.7 | 1394 | 23.13 | 5501.2 | 2899.6 | 2896.2 | 4211.9 | 1199.3 | 0.6712 | 6.013
2024-12-09 | 18:33 | Data | 0 | 32.723 | 30.536 | 187.805 | 7.63 | 176.459 | 2142.08 | 25.93 | 46.269 | 6.35 | 1.358 | 4.684 | 8490.48 | 2.187 | 97.8 | 77.5 | 1392 | 23.09 | 5518.8 | 2907.1 | 2865.8 | 4197.4 | 1199.3 | 0.67525 | 6.042
2024-12-09 | 18:34 | Data | 0 | 32.703 | 30.867 | 187.76 | 7.63 | 176.594 | 2142.08 | 25.93 | 46.179 | 6.35 | 1.353 | 4.658 | 8499.53 | 2.032 | 97.8 | 77.5 | 1392 | 23.09 | 5524.7 | 2911.1 | 2865.9 | 4200.9 | 1199.3 | 0.67601 | 6.011
2024-12-09 | 18:34 | Data | 0 | 32.723 | 30.874 | 187.76 | 7.63 | 176.685 | 2144.79 | 25.93 | 46.179 | 6.35 | 1.344 | 4.675 | 8481.44 | 1.857 | 97.8 | 77.7 | 1394 | 23.09 | 5512.9 | 2887.2 | 2870.6 | 4187.5 | 1199.3 | 0.67212 | 6.018
2024-12-09 | 18:34 | Data | 0 | 32.669 | 30.867 | 187.986 | 7.63 | 176.594 | 2142.08 | 25.92 | 46.179 | 6.35 | 1.342 | 4.647 | 8481.44 | 1.978 | 97.8 | 77.6 | 1392 | 23.13 | 5512.9 | 2922.5 | 2842.2 | 4195.8 | 1199.3 | 0.68115 | 5.989
2024-12-09 | 18:34 | Data | 0 | 32.494 | 30.59 | 187.805 | 7.63 | 176.459 | 2142.99 | 25.92 | 46.269 | 6.35 | 1.349 | 4.657 | 8951.75 | 2.187 | 97.8 | 77.5 | 1394 | 23.09 | 5818.6 | 2912.1 | 2855.6 | 4192.9 | 1199.3 | 0.67799 | 6.008
2024-12-09 | 18:34 | Data | 0 | 32.501 | 30.435 | 187.805 | 7.63 | 176.549 | 2143.89 | 25.92 | 46.179 | 6.35 | 1.353 | 4.643 | 8499.53 | 2.032 | 97.8 | 77.4 | 1394 | 23.09 | 5524.7 | 2910.5 | 2865.5 | 4204.2 | 1199.3 | 0.67578 | 5.996
2024-12-09 | 18:34 | Data | 0 | 32.48 | 30.624 | 187.805 | 7.63 | 176.549 | 2143.89 | 25.92 | 46.179 | 6.35 | 1.348 | 4.662 | 8495 | 2.073 | 97.8 | 77.6 | 1394 | 23.13 | 5521.8 | 2873.9 | 2865.7 | 4189.2 | 1199.3 | 0.67106 | 6.01
2024-12-09 | 18:34 | Data | 0 | 32.568 | 30.651 | 187.851 | 7.63 | 176.594 | 2143.89 | 25.93 | 46.269 | 6.35 | 1.358 | 4.647 | 8495 | 2.025 | 97.8 | 77.4 | 1394 | 23.13 | 5521.8 | 2903 | 2872.1 | 4200.3 | 1199.3 | 0.67407 | 6.007
2024-12-09 | 18:34 | Data | 0 | 32.528 | 30.853 | 187.941 | 7.63 | 176.594 | 2144.79 | 25.92 | 46.089 | 6.35 | 1.354 | 4.638 | 8513.09 | 1.843 | 97.8 | 77.4 | 1394 | 23.04 | 5533.5 | 2889.6 | 2880.2 | 4195.6 | 1199.3 | 0.67044 | 5.992
2024-12-09 | 18:34 | Data | 0 | 32.501 | 30.462 | 187.715 | 7.63 | 176.594 | 2144.79 | 25.92 | 46.269 | 6.35 | 1.345 | 4.645 | 8495 | 2.046 | 97.8 | 77.5 | 1394 | 23.09 | 5521.8 | 2897.5 | 2875.3 | 4198.9 | 1199.3 | 0.67224 | 5.99
2024-12-09 | 18:34 | Data | 0 | 32.501 | 30.651 | 187.851 | 7.63 | 176.549 | 2143.89 | 25.93 | 46.179 | 6.35 | 1.346 | 4.662 | 8517.61 | 2.019 | 97.8 | 77.6 | 1394 | 23.09 | 5536.4 | 2898.2 | 2875.9 | 4200.6 | 1199.3 | 0.67156 | 6.007
2024-12-09 | 18:34 | Data | 0 | 32.669 | 30.678 | 187.76 | 7.63 | 176.594 | 2144.79 | 25.92 | 46.179 | 6.35 | 1.361 | 4.664 | 8517.61 | 1.971 | 97.8 | 77.4 | 1394 | 23.09 | 5536.4 | 2910.2 | 2865.9 | 4196.1 | 1199.3 | 0.67636 | 6.025
2024-12-09 | 18:34 | Data | 0 | 32.838 | 30.874 | 187.851 | 7.63 | 176.594 | 2143.89 | 25.93 | 46.179 | 6.36 | 1.355 | 4.649 | 8481.44 | 2.052 | 97.8 | 77.4 | 1394 | 23.09 | 5512.9 | 2901.5 | 2874 | 4201.3 | 1199.3 | 0.674 | 6.005
2024-12-09 | 18:34 | Data | 0 | 32.831 | 30.651 | 187.896 | 7.63 | 176.549 | 2144.79 | 25.93 | 46.179 | 6.35 | 1.352 | 4.675 | 8906.53 | 1.958 | 97.8 | 77.6 | 1394 | 23.09 | 5789.2 | 2902.5 | 2820.1 | 4158.5 | 1199.3 | 0.68052 | 6.026
2024-12-09 | 18:34 | Data | 0 | 32.305 | 30.637 | 187.715 | 7.63 | 176.549 | 2143.89 | 25.93 | 46.179 | 6.35 | 1.341 | 4.664 | 8490.48 | 1.823 | 97.8 | 77.7 | 1394 | 23.13 | 5518.8 | 2902.1 | 2818.7 | 4164.5 | 1199.3 | 0.68021 | 6.006
2024-12-09 | 18:34 | Data | 0 | 32.953 | 30.718 | 187.986 | 7.63 | 176.73 | 2144.79 | 25.93 | 46.179 | 6.35 | 1.351 | 4.652 | 8485.96 | 2.12 | 97.9 | 77.5 | 1394 | 23.04 | 5515.9 | 2901.1 | 2846.8 | 4180.9 | 1199.3 | 0.67773 | 6.004
2024-12-09 | 18:34 | Data | 0 | 32.71 | 30.421 | 187.715 | 7.63 | 176.549 | 2146.6 | 25.92 | 46.269 | 6.35 | 1.353 | 4.673 | 8481.44 | 2.079 | 97.8 | 77.5 | 1395 | 23.13 | 5512.9 | 2886.8 | 2850.1 | 4175.6 | 1199.3 | 0.67421 | 6.025
2024-12-09 | 18:34 | Data | 0 | 32.71 | 30.739 | 187.851 | 7.63 | 176.594 | 2147.51 | 25.92 | 46.269 | 6.35 | 1.357 | 4.664 | 8454.3 | 1.985 | 97.8 | 77.5 | 1396 | 23.13 | 5495.3 | 2885.5 | 2858.9 | 4181 | 1199.3 | 0.67235 | 6.022
2024-12-09 | 18:34 | Data | 0 | 32.507 | 30.82 | 187.715 | 7.63 | 176.459 | 2152.02 | 25.9 | 46.269 | 6.35 | 1.351 | 4.655 | 8458.83 | 1.85 | 97.8 | 77.5 | 1398 | 23.13 | 5498.2 | 2900.7 | 2847.9 | 4188.1 | 1199.3 | 0.67288 | 6.007
2024-12-09 | 18:35 | Data | 0 | 32.696 | 30.421 | 187.851 | 7.63 | 176.594 | 2149.31 | 25.92 | 46.179 | 6.35 | 1.343 | 4.662 | 8458.83 | 2.127 | 97.8 | 77.6 | 1396 | 23.13 | 5498.2 | 2903.2 | 2868.1 | 4199.4 | 1199.3 | 0.67431 | 6.005
2024-12-09 | 18:35 | Data | 0 | 32.669 | 31.029 | 187.76 | 7.63 | 176.549 | 2151.12 | 25.94 | 46.179 | 6.35 | 1.348 | 4.645 | 8449.78 | 2.012 | 97.9 | 77.5 | 1398 | 23.09 | 5492.4 | 2910.8 | 2876.9 | 4207.2 | 1199.3 | 0.67399 | 5.995
2024-12-09 | 18:35 | Data | 0 | 32.946 | 30.428 | 187.941 | 7.63 | 176.594 | 2149.31 | 25.93 | 46.269 | 6.35 | 1.354 | 4.673 | 8458.83 | 1.985 | 97.8 | 77.5 | 1397 | 23.09 | 5498.2 | 2894.8 | 2873.3 | 4200.7 | 1199.3 | 0.67205 | 6.027
2024-12-09 | 18:35 | Data | 0 | 32.831 | 30.651 | 187.851 | 7.63 | 176.549 | 2151.12 | 25.92 | 46.269 | 6.35 | 1.349 | 4.665 | 8449.78 | 2.086 | 97.8 | 77.5 | 1398 | 23.09 | 5492.4 | 2895.8 | 2859 | 4187.5 | 1199.3 | 0.67366 | 6.017
2024-12-09 | 18:35 | Data | 0 | 32.602 | 30.631 | 187.851 | 7.63 | 176.639 | 2151.12 | 25.92 | 46.179 | 6.35 | 1.354 | 4.662 | 8445.26 | 2.066 | 97.8 | 77.5 | 1398 | 23.13 | 5489.4 | 2888.2 | 2852.6 | 4175.8 | 1199.4 | 0.67429 | 6.016
2024-12-09 | 18:35 | Data | 0 | 32.933 | 30.563 | 187.76 | 7.63 | 176.549 | 2151.12 | 25.92 | 46.269 | 6.35 | 1.343 | 4.665 | 8495 | 2.16 | 97.8 | 77.7 | 1398 | 23.13 | 5521.8 | 2885.3 | 2840.9 | 4175.3 | 1199.4 | 0.6758 | 6.007
2024-12-09 | 18:35 | Data | 0 | 32.71 | 30.421 | 187.851 | 7.63 | 176.685 | 2151.12 | 25.93 | 46.179 | 6.35 | 1.348 | 4.667 | 8495 | 2.086 | 97.9 | 77.6 | 1398 | 23.13 | 5521.8 | 2884 | 2856.7 | 4180.9 | 1199.4 | 0.66927 | 6.017
2024-12-09 | 18:35 | Data | 0 | 32.426 | 30.448 | 187.851 | 7.63 | 176.685 | 2149.31 | 25.93 | 46.269 | 6.35 | 1.342 | 4.664 | 8481.44 | 1.836 | 97.8 | 77.7 | 1398 | 23.13 | 5512.9 | 2896.7 | 2865.2 | 4190.3 | 1199.4 | 0.67392 | 6.006
2024-12-09 | 18:35 | Data | 0 | 32.636 | 30.543 | 187.805 | 7.63 | 176.594 | 2152.02 | 25.92 | 46.179 | 6.35 | 1.344 | 4.664 | 8490.48 | 2.079 | 97.8 | 77.6 | 1398 | 23.13 | 5518.8 | 2890.1 | 2845.1 | 4171.4 | 1199.4 | 0.6743 | 6.007
2024-12-09 | 18:35 | Data | 0 | 32.501 | 30.529 | 187.67 | 7.63 | 176.594 | 2151.12 | 25.91 | 46.269 | 6.35 | 1.353 | 4.662 | 8513.09 | 1.85 | 97.8 | 77.5 | 1398 | 23.18 | 5533.5 | 2894.5 | 2867.3 | 4192.3 | 1199.4 | 0.67382 | 6.016
2024-12-09 | 18:35 | Data | 0 | 32.946 | 30.88 | 187.941 | 7.63 | 176.639 | 2153.83 | 25.93 | 46.269 | 6.35 | 1.345 | 4.669 | 8508.57 | 1.897 | 97.9 | 77.6 | 1399 | 23.13 | 5530.6 | 2900.4 | 2857 | 4190.5 | 1199.4 | 0.67472 | 6.014
2024-12-09 | 18:35 | Data | 0 | 32.696 | 30.826 | 187.805 | 7.63 | 176.594 | 2152.93 | 25.93 | 46.269 | 6.35 | 1.339 | 4.675 | 8495 | 2.174 | 97.9 | 77.7 | 1400 | 23.09 | 5521.8 | 2913.3 | 2866.1 | 4199.8 | 1199.4 | 0.67313 | 6.014
2024-12-09 | 18:35 | Data | 0 | 32.71 | 30.759 | 187.941 | 7.63 | 176.594 | 2152.93 | 25.93 | 46.269 | 6.35 | 1.346 | 4.655 | 8513.09 | 1.917 | 97.9 | 77.6 | 1399 | 23.13 | 5533.5 | 2885.4 | 2869.6 | 4188.5 | 1199.4 | 0.67 | 6.001
2024-12-09 | 18:35 | Data | 0 | 32.615 | 30.482 | 187.805 | 7.63 | 176.549 | 2153.83 | 25.93 | 46.269 | 6.35 | 1.349 | 4.64 | 8513.09 | 2.039 | 97.9 | 77.5 | 1400 | 23.13 | 5533.5 | 2913.8 | 2878.8 | 4209.7 | 1199.4 | 0.67493 | 5.989
2024-12-09 | 18:35 | Data | 0 | 32.737 | 30.874 | 187.941 | 7.63 | 176.685 | 2153.83 | 25.92 | 46.179 | 6.35 | 1.348 | 4.662 | 8540.22 | 1.87 | 97.9 | 77.6 | 1401 | 23.09 | 5551.1 | 2901.4 | 2894.3 | 4211.4 | 1199.4 | 0.67436 | 6.009
2024-12-09 | 18:35 | Data | 0 | 32.582 | 30.651 | 187.851 | 7.63 | 176.639 | 2147.51 | 25.93 | 46.269 | 6.35 | 1.346 | 4.646 | 8540.22 | 1.884 | 97.8 | 77.5 | 1396 | 23.09 | 5551.1 | 2917.1 | 2874.8 | 4210.3 | 1199.4 | 0.6764 | 5.992
2024-12-09 | 18:35 | Data | 0 | 32.757 | 30.651 | 187.851 | 7.63 | 176.73 | 2147.51 | 25.92 | 46.179 | 6.36 | 1.348 | 4.642 | 8544.75 | 1.87 | 97.8 | 77.5 | 1396 | 23.13 | 5554.1 | 2885.1 | 2873.9 | 4191 | 1199.4 | 0.672 | 5.996
2024-12-09 | 18:36 | Data | 0 | 32.507 | 30.543 | 187.896 | 7.63 | 176.459 | 2151.12 | 25.93 | 46.269 | 6.35 | 1.362 | 4.625 | 8526.66 | 2.066 | 97.8 | 77.3 | 1397 | 23.13 | 5542.3 | 2892 | 2872.6 | 4191.5 | 1199.4 | 0.67312 | 5.986
2024-12-09 | 18:36 | Data | 0 | 32.804 | 30.664 | 187.941 | 7.63 | 176.639 | 2147.51 | 25.93 | 46.089 | 6.35 | 1.343 | 4.67 | 8540.22 | 1.931 | 97.8 | 77.7 | 1396 | 23.13 | 5551.1 | 2893.9 | 2904.1 | 4220.9 | 1199.4 | 0.67036 | 6.014
2024-12-09 | 18:36 | Data | 0 | 32.696 | 30.671 | 187.76 | 7.63 | 176.549 | 2147.51 | 25.92 | 45.998 | 6.36 | 1.336 | 4.669 | 8526.66 | 2.046 | 97.9 | 77.7 | 1396 | 23 | 5542.3 | 2878.8 | 2882.1 | 4190.2 | 1199.4 | 0.66922 | 6.006
2024-12-09 | 18:36 | Data | 0 | 32.831 | 30.428 | 188.122 | 7.63 | 177.046 | 2147.51 | 25.93 | 46.089 | 6.35 | 1.342 | 4.656 | 8540.22 | 2.228 | 97.9 | 77.6 | 1396 | 23 | 5551.1 | 2883.7 | 2876.1 | 4192.3 | 1199.4 | 0.66957 | 5.999
2024-12-09 | 18:36 | Data | 0 | 32.555 | 30.543 | 190.972 | 7.63 | 179.532 | 2148.41 | 25.93 | 46.089 | 6.35 | 1.349 | 4.664 | 8540.22 | 2.039 | 97.9 | 77.6 | 1396 | 23.04 | 5551.1 | 2922.6 | 2913.2 | 4240.9 | 1199.4 | 0.6726 | 6.011
2024-12-09 | 18:36 | Data | 0 | 32.521 | 30.185 | 193.098 | 7.63 | 181.385 | 2145.7 | 25.93 | 46.269 | 6.35 | 1.356 | 4.735 | 8540.22 | 2.086 | 97.8 | 77.7 | 1396 | 23.13 | 5551.1 | 2960.7 | 2935.3 | 4283.2 | 1199.4 | 0.67386 | 6.09
2024-12-09 | 18:36 | Data | 0 | 32.575 | 30.32 | 194.952 | 7.63 | 183.102 | 2145.7 | 25.93 | 46.359 | 6.35 | 1.366 | 4.768 | 8522.14 | 2.154 | 97.8 | 77.7 | 1394 | 23.13 | 5539.4 | 2967.7 | 2931.4 | 4284.2 | 1199.4 | 0.67541 | 6.134
2024-12-09 | 18:36 | Data | 0 | 32.089 | 30.225 | 196.445 | 7.63 | 184.503 | 2147.51 | 25.92 | 45.998 | 6.35 | 1.369 | 4.794 | 8481.44 | 2.052 | 97.9 | 77.8 | 1396 | 23 | 5512.9 | 2995 | 2971 | 4329.5 | 1199.4 | 0.67349 | 6.163
2024-12-09 | 18:36 | Data | 0 | 32.264 | 30.07 | 197.756 | 7.63 | 185.543 | 2151.12 | 25.92 | 45.998 | 6.35 | 1.381 | 4.872 | 8472.39 | 2.194 | 97.9 | 77.9 | 1398 | 23 | 5507.1 | 2993.8 | 2984.2 | 4339.7 | 1199.4 | 0.67225 | 6.253
2024-12-09 | 18:36 | Data | 0 | 32.264 | 30.408 | 197.937 | 7.63 | 185.769 | 2151.12 | 25.93 | 45.637 | 6.35 | 1.377 | 4.877 | 8495 | 2.066 | 97.9 | 78 | 1397 | 22.82 | 5521.8 | 2999.2 | 2974.9 | 4335 | 1199.4 | 0.67489 | 6.253
2024-12-09 | 18:36 | Data | 0 | 32.075 | 30.158 | 198.254 | 7.63 | 186.22 | 2149.31 | 25.92 | 45.727 | 6.35 | 1.381 | 4.844 | 8490.48 | 1.971 | 97.9 | 77.8 | 1397 | 22.86 | 5518.8 | 3014.5 | 2993.9 | 4358.1 | 1199.4 | 0.67569 | 6.226
2024-12-09 | 18:36 | Data | 0 | 32.474 | 30.009 | 198.933 | 7.63 | 186.627 | 2136.66 | 25.93 | 45.457 | 6.34 | 1.383 | 4.887 | 8513.09 | 2.309 | 97.9 | 77.9 | 1389 | 22.68 | 5533.5 | 3000.3 | 2994 | 4349.6 | 1199.4 | 0.67533 | 6.269
2024-12-09 | 18:36 | Data | 0 | 32.048 | 29.955 | 198.842 | 7.63 | 186.672 | 2147.51 | 25.93 | 45.005 | 6.34 | 1.381 | 4.908 | 8535.7 | 2.079 | 97.9 | 78 | 1396 | 22.59 | 5548.2 | 3012.8 | 2986.2 | 4353.3 | 1199.4 | 0.67614 | 6.289
2024-12-09 | 18:36 | Data | 0 | 32.312 | 29.942 | 198.616 | 7.63 | 186.627 | 2048.99 | 25.92 | 45.186 | 6.33 | 1.388 | 4.898 | 8553.79 | 2.133 | 97.8 | 77.9 | 1332 | 22.59 | 5560 | 3025.7 | 2982 | 4357.9 | 1199.4 | 0.67805 | 6.287
2024-12-09 | 18:36 | Data | 0 | 32.035 | 29.901 | 198.842 | 7.63 | 186.537 | 2152.02 | 25.93 | 44.825 | 6.34 | 1.383 | 4.902 | 7970.42 | 2.248 | 97.9 | 78 | 1399 | 22.37 | 5180.8 | 3000 | 2979.6 | 4339.2 | 1199.4 | 0.67451 | 6.283
2024-12-09 | 18:36 | Data | 0 | 32.602 | 30.023 | 198.933 | 7.63 | 186.763 | 2147.51 | 25.93 | 44.825 | 6.34 | 1.376 | 4.912 | 8580.93 | 2.262 | 97.9 | 78.1 | 1396 | 22.41 | 5577.6 | 3009.6 | 2997.7 | 4359.7 | 1199.4 | 0.673 | 6.289
2024-12-09 | 18:36 | Data | 0 | 32.143 | 30.07 | 198.887 | 7.63 | 186.672 | 2153.83 | 25.92 | 44.825 | 6.34 | 1.378 | 4.917 | 8599.01 | 2.275 | 97.9 | 78.1 | 1399 | 22.37 | 5589.4 | 3018.9 | 2985.9 | 4360.3 | 1199.4 | 0.67469 | 6.295
2024-12-09 | 18:37 | Data | 0 | 32.062 | 29.928 | 198.933 | 7.63 | 186.627 | 2153.83 | 25.92 | 44.825 | 6.34 | 1.38 | 4.905 | 8594.49 | 2.295 | 97.9 | 78 | 1400 | 22.41 | 5586.4 | 3045.4 | 2998.3 | 4386.2 | 1199.4 | 0.67736 | 6.283
2024-12-09 | 18:37 | Data | 0 | 32.48 | 30.212 | 198.887 | 7.63 | 186.718 | 2153.83 | 25.93 | 44.825 | 6.34 | 1.384 | 4.911 | 8626.15 | 2.282 | 97.9 | 78 | 1399 | 22.46 | 5607 | 3039.7 | 2971.9 | 4364.4 | 1199.4 | 0.68004 | 6.296
2024-12-09 | 18:37 | Data | 0 | 32.534 | 30.077 | 198.933 | 7.63 | 186.718 | 2153.83 | 25.92 | 44.915 | 6.34 | 1.397 | 4.903 | 8576.4 | 2.457 | 97.9 | 77.8 | 1400 | 22.46 | 5574.7 | 3034 | 2940.4 | 4340.6 | 1199.4 | 0.68159 | 6.301
2024-12-09 | 18:37 | Data | 0 | 32.264 | 30.408 | 198.933 | 7.63 | 186.718 | 2153.83 | 25.92 | 45.186 | 6.34 | 1.389 | 4.905 | 8576.4 | 2.086 | 97.9 | 77.9 | 1399 | 22.59 | 5574.7 | 3033.2 | 2934.9 | 4334 | 1199.4 | 0.68298 | 6.294
2024-12-09 | 18:37 | Data | 0 | 32.035 | 29.841 | 198.752 | 7.63 | 186.627 | 2152.93 | 25.92 | 45.186 | 6.33 | 1.384 | 4.915 | 8594.49 | 2.079 | 97.9 | 78 | 1400 | 22.64 | 5586.4 | 3026.8 | 2969.6 | 4355.4 | 1199.4 | 0.67794 | 6.3
2024-12-09 | 18:37 | Data | 0 | 31.839 | 29.901 | 198.797 | 7.63 | 186.718 | 2153.83 | 25.94 | 45.186 | 6.33 | 1.384 | 4.907 | 8599.01 | 2.019 | 97.9 | 78 | 1399 | 22.59 | 5589.4 | 3037.2 | 2982 | 4370.1 | 1199.5 | 0.67847 | 6.291
2024-12-09 | 18:37 | Data | 0 | 32.278 | 30.009 | 198.887 | 7.63 | 186.808 | 2147.51 | 25.93 | 45.186 | 6.34 | 1.382 | 4.89 | 8621.63 | 2.201 | 97.9 | 78 | 1396 | 22.5 | 5604.1 | 3039.5 | 2992.2 | 4374.5 | 1199.5 | 0.6772 | 6.272
2024-12-09 | 18:37 | Data | 0 | 32.15 | 29.955 | 198.842 | 7.63 | 186.672 | 2153.83 | 25.92 | 45.186 | 6.34 | 1.381 | 4.904 | 8617.1 | 2.295 | 97.9 | 78 | 1400 | 22.59 | 5601.1 | 3025.8 | 3012.9 | 4384.7 | 1199.5 | 0.67649 | 6.286
2024-12-09 | 18:37 | Data | 0 | 32.237 | 30.043 | 198.752 | 7.63 | 186.582 | 2153.83 | 25.92 | 45.276 | 6.33 | 1.387 | 4.903 | 8635.19 | 2.127 | 97.9 | 77.9 | 1399 | 22.59 | 5612.9 | 3031.4 | 3011.1 | 4384.7 | 1199.5 | 0.67336 | 6.291
2024-12-09 | 18:37 | Data | 0 | 32.487 | 30.354 | 199.023 | 7.63 | 186.718 | 2153.83 | 25.93 | 45.005 | 6.33 | 1.38 | 4.918 | 8653.28 | 2.14 | 97.9 | 78.1 | 1400 | 22.5 | 5624.6 | 3046.5 | 3016.6 | 4399.6 | 1199.5 | 0.67481 | 6.298
2024-12-09 | 18:37 | Data | 0 | 32.15 | 29.955 | 198.797 | 7.63 | 186.582 | 2152.93 | 25.93 | 45.186 | 6.33 | 1.384 | 4.916 | 8662.33 | 2.086 | 97.9 | 78 | 1397 | 22.5 | 5630.5 | 3058 | 3008.8 | 4403.2 | 1199.5 | 0.67716 | 6.3
2024-12-09 | 18:37 | Data | 0 | 32.069 | 29.753 | 198.887 | 7.63 | 186.718 | 2153.83 | 25.93 | 45.276 | 6.34 | 1.385 | 4.91 | 8662.33 | 2.187 | 97.9 | 78 | 1400 | 22.59 | 5630.5 | 3050.5 | 3024 | 4408 | 1199.5 | 0.6732 | 6.294
2024-12-09 | 18:37 | Data | 0 | 32.487 | 30.185 | 198.978 | 7.63 | 186.763 | 2152.93 | 25.93 | 45.276 | 6.34 | 1.385 | 4.883 | 8653.28 | 2.194 | 97.9 | 77.9 | 1399 | 22.59 | 5624.6 | 3045 | 2992 | 4381.4 | 1199.5 | 0.67829 | 6.267
2024-12-09 | 18:37 | Data | 0 | 32.494 | 30.185 | 199.023 | 7.63 | 186.763 | 2153.83 | 25.93 | 45.186 | 6.34 | 1.383 | 4.87 | 8662.33 | 2.106 | 97.9 | 77.9 | 1400 | 22.59 | 5630.5 | 3039.2 | 2987.5 | 4380 | 1199.5 | 0.67641 | 6.251
2024-12-09 | 18:37 | Data | 0 | 32.15 | 29.908 | 198.752 | 7.63 | 186.672 | 2153.83 | 25.92 | 45.186 | 6.33 | 1.391 | 4.9 | 8657.8 | 2.187 | 97.9 | 77.9 | 1400 | 22.64 | 5627.6 | 3037.5 | 2972.1 | 4364.2 | 1199.5 | 0.67836 | 6.291
2024-12-09 | 18:37 | Data | 0 | 32.325 | 29.847 | 198.978 | 7.63 | 186.763 | 2161.06 | 25.92 | 44.734 | 6.34 | 1.394 | 4.883 | 8662.33 | 2.133 | 97.9 | 77.8 | 1405 | 22.28 | 5630.5 | 3039.3 | 2979.6 | 4365.7 | 1199.5 | 0.67807 | 6.278
2024-12-09 | 18:37 | Data | 0 | 32.258 | 29.955 | 198.842 | 7.63 | 186.627 | 2156.54 | 25.92 | 45.186 | 6.33 | 1.384 | 4.883 | 8689.46 | 2.309 | 97.9 | 77.9 | 1402 | 22.59 | 5648.1 | 3039.4 | 2990.8 | 4379 | 1199.5 | 0.67593 | 6.266
2024-12-09 | 18:38 | Data | 0 | 32.264 | 30.07 | 198.933 | 7.63 | 186.808 | 2155.64 | 25.93 | 45.186 | 6.33 | 1.38 | 4.893 | 8693.98 | 2.079 | 97.9 | 78 | 1401 | 22.59 | 5651.1 | 3048.1 | 2994.4 | 4390.3 | 1199.5 | 0.67602 | 6.272
2024-12-09 | 18:38 | Data | 0 | 32.102 | 29.949 | 198.842 | 7.63 | 186.672 | 2156.54 | 25.93 | 45.005 | 6.34 | 1.383 | 4.908 | 8666.85 | 2.106 | 97.9 | 78 | 1402 | 22.64 | 5633.5 | 3040.3 | 3011.9 | 4393.7 | 1199.5 | 0.67214 | 6.29
2024-12-09 | 18:38 | Data | 0 | 31.819 | 29.901 | 198.797 | 7.63 | 186.672 | 2153.83 | 25.92 | 45.276 | 6.33 | 1.386 | 4.901 | 8657.8 | 2.079 | 97.9 | 78 | 1399 | 22.5 | 5627.6 | 3039.8 | 3020.3 | 4395.1 | 1199.5 | 0.67495 | 6.288
2024-12-09 | 18:38 | Data | 0 | 32.204 | 29.733 | 198.752 | 7.63 | 186.672 | 2151.12 | 25.92 | 45.186 | 6.34 | 1.386 | 4.891 | 8671.37 | 2.525 | 97.9 | 77.9 | 1398 | 22.59 | 5636.4 | 3067.7 | 3011.3 | 4410.9 | 1199.5 | 0.67786 | 6.277
2024-12-09 | 18:38 | Data | 0 | 32.264 | 29.962 | 198.933 | 7.63 | 186.627 | 2151.12 | 25.92 | 45.005 | 6.34 | 1.389 | 4.887 | 8671.37 | 2.302 | 97.9 | 77.9 | 1399 | 22.64 | 5636.4 | 3051.4 | 2996.8 | 4390 | 1199.5 | 0.6763 | 6.276
2024-12-09 | 18:38 | Data | 0 | 32.264 | 30.063 | 198.887 | 7.63 | 186.763 | 2151.12 | 25.9 | 45.276 | 6.33 | 1.388 | 4.91 | 8662.33 | 2.093 | 97.9 | 78 | 1398 | 22.59 | 5630.5 | 3057.2 | 3026.8 | 4413.5 | 1199.5 | 0.67609 | 6.297
2024-12-09 | 18:38 | Data | 0 | 32.487 | 30.198 | 198.933 | 7.63 | 186.763 | 2153.83 | 25.92 | 45.186 | 6.34 | 1.384 | 4.896 | 8671.37 | 2.248 | 97.9 | 78 | 1399 | 22.59 | 5636.4 | 3035.9 | 2966.5 | 4358.3 | 1199.5 | 0.67959 | 6.279
2024-12-09 | 18:38 | Data | 0 | 32.028 | 29.949 | 198.797 | 7.63 | 186.672 | 2152.93 | 25.92 | 45.005 | 6.34 | 1.383 | 4.911 | 8671.37 | 2.262 | 97.9 | 78 | 1400 | 22.59 | 5636.4 | 3046.8 | 2989.8 | 4384.4 | 1199.5 | 0.67656 | 6.294
2024-12-09 | 18:38 | Data | 0 | 31.805 | 30.347 | 198.933 | 7.63 | 186.718 | 2149.31 | 25.93 | 45.186 | 6.33 | 1.379 | 4.872 | 8680.41 | 2.235 | 97.9 | 77.9 | 1396 | 22.5 | 5642.3 | 3026.7 | 2948 | 4340.7 | 1199.5 | 0.68081 | 6.252
2024-12-09 | 18:38 | Data | 0 | 32.352 | 29.854 | 198.797 | 7.63 | 186.672 | 2147.51 | 25.92 | 44.915 | 6.33 | 1.377 | 4.907 | 8689.46 | 2.302 | 97.9 | 78.1 | 1396 | 22.64 | 5648.1 | 3045.6 | 3000.1 | 4388.6 | 1199.5 | 0.67599 | 6.285
2024-12-09 | 18:38 | Data | 0 | 32.406 | 30.158 | 198.978 | 7.63 | 186.582 | 2145.7 | 25.91 | 45.186 | 6.33 | 1.388 | 4.926 | 8703.03 | 2.343 | 97.9 | 78 | 1394 | 22.59 | 5657 | 2964.7 | 2961.7 | 4299.1 | 1199.5 | 0.67235 | 6.315
2024-12-09 | 18:38 | Data | 0 | 32.514 | 29.955 | 198.842 | 7.63 | 186.763 | 2142.99 | 25.92 | 45.186 | 6.34 | 1.388 | 4.907 | 8707.55 | 2.14 | 97.9 | 78 | 1392 | 22.64 | 5659.9 | 2986.9 | 2963.8 | 4316.8 | 1199.5 | 0.6752 | 6.296
2024-12-09 | 18:38 | Data | 0 | 32.204 | 29.854 | 198.797 | 7.63 | 186.672 | 2145.7 | 25.91 | 45.276 | 6.34 | 1.384 | 4.909 | 8721.11 | 2.451 | 97.9 | 78 | 1394 | 22.59 | 5668.7 | 2974.1 | 2973.5 | 4314.9 | 1199.5 | 0.67251 | 6.292
2024-12-09 | 18:38 | Data | 0 | 32.028 | 29.949 | 198.797 | 7.63 | 186.627 | 2143.89 | 25.91 | 45.005 | 6.33 | 1.381 | 4.909 | 8716.59 | 2.1 | 97.9 | 78 | 1394 | 22.59 | 5665.8 | 2972.1 | 2982.1 | 4317.7 | 1199.5 | 0.67131 | 6.291
2024-12-09 | 18:38 | Data | 0 | 32.062 | 29.955 | 199.068 | 7.63 | 186.627 | 2141.18 | 25.92 | 45.005 | 6.34 | 1.39 | 4.904 | 8671.37 | 2.073 | 97.9 | 77.9 | 1392 | 22.59 | 5636.4 | 2973.7 | 2973.5 | 4317 | 1199.5 | 0.67261 | 6.294
2024-12-09 | 18:38 | Data | 0 | 32.143 | 29.962 | 198.706 | 7.63 | 186.672 | 2144.79 | 25.92 | 45.005 | 6.34 | 1.386 | 4.911 | 8693.98 | 2.079 | 97.9 | 78 | 1394 | 22.5 | 5651.1 | 2990 | 2979.6 | 4329.8 | 1199.5 | 0.67459 | 6.298
2024-12-09 | 18:38 | Data | 0 | 32.325 | 29.955 | 199.023 | 7.63 | 186.763 | 2144.79 | 25.91 | 45.276 | 6.33 | 1.39 | 4.918 | 8680.41 | 2.14 | 97.9 | 78 | 1394 | 22.5 | 5642.3 | 2973.2 | 2977.2 | 4315.9 | 1199.5 | 0.67387 | 6.308
2024-12-09 | 18:38 | Data | 0 | 32.143 | 29.955 | 198.933 | 7.63 | 186.672 | 2143.89 | 25.9 | 45.186 | 6.33 | 1.38 | 4.895 | 8693.98 | 2.086 | 97.9 | 78 | 1394 | 22.59 | 5651.1 | 2980 | 2967.9 | 4311 | 1199.5 | 0.67433 | 6.275
2024-12-09 | 18:39 | Data | 0 | 32.028 | 29.901 | 198.797 | 7.63 | 186.718 | 2148.41 | 25.9 | 45.276 | 6.34 | 1.382 | 4.882 | 8648.76 | 2.302 | 97.9 | 77.9 | 1396 | 22.64 | 5621.7 | 3038.5 | 2957.8 | 4353.4 | 1199.5 | 0.68157 | 6.264
2024-12-09 | 18:39 | Data | 0 | 32.069 | 29.787 | 198.797 | 7.63 | 186.718 | 2147.51 | 25.89 | 45.005 | 6.34 | 1.4 | 4.895 | 8648.76 | 2.194 | 97.9 | 77.8 | 1396 | 22.59 | 5621.7 | 3019.6 | 2971.1 | 4353.2 | 1199.5 | 0.6761 | 6.292
2024-12-09 | 18:39 | Data | 0 | 32.278 | 30.131 | 198.887 | 7.63 | 186.718 | 2146.6 | 25.89 | 45.186 | 6.33 | 1.395 | 4.9 | 8639.71 | 2.106 | 97.9 | 77.8 | 1395 | 22.59 | 5615.8 | 3032.9 | 2979.2 | 4368.9 | 1199.5 | 0.6769 | 6.296
2024-12-09 | 18:39 | Data | 0 | 32.237 | 29.955 | 198.842 | 7.63 | 186.627 | 2147.51 | 25.91 | 45.186 | 6.34 | 1.387 | 4.88 | 8626.15 | 2.302 | 97.9 | 77.9 | 1396 | 22.5 | 5607 | 3024.4 | 2954.3 | 4338.8 | 1199.5 | 0.67974 | 6.267
2024-12-09 | 18:39 | Data | 0 | 31.974 | 30.394 | 198.797 | 7.63 | 186.672 | 2145.7 | 25.9 | 45.186 | 6.33 | 1.385 | 4.888 | 8662.33 | 2.289 | 97.9 | 77.9 | 1395 | 22.59 | 5630.5 | 3034.8 | 3013.3 | 4390.7 | 1199.5 | 0.67324 | 6.273
2024-12-09 | 18:39 | Data | 0 | 32.035 | 30.124 | 198.752 | 7.63 | 186.627 | 2146.6 | 25.9 | 44.915 | 6.34 | 1.397 | 4.882 | 8648.76 | 2.133 | 97.9 | 77.7 | 1396 | 22.46 | 5621.7 | 3035.7 | 2988.7 | 4372.6 | 1199.6 | 0.67636 | 6.279
2024-12-09 | 18:39 | Data | 0 | 32.055 | 29.942 | 198.752 | 7.63 | 186.672 | 2148.41 | 25.89 | 45.186 | 6.34 | 1.38 | 4.893 | 8648.76 | 2.106 | 97.9 | 78 | 1396 | 22.59 | 5621.7 | 3010.1 | 2990.8 | 4371.1 | 1199.6 | 0.6739 | 6.273
2024-12-09 | 18:39 | Data | 0 | 32.318 | 29.955 | 198.933 | 7.63 | 186.718 | 2151.12 | 25.91 | 45.276 | 6.33 | 1.376 | 4.913 | 8639.71 | 2.093 | 97.9 | 78.1 | 1398 | 22.64 | 5615.8 | 3035.6 | 2986.7 | 4370 | 1199.6 | 0.67726 | 6.289
2024-12-09 | 18:39 | Data | 0 | 32.035 | 30.111 | 198.887 | 7.63 | 186.672 | 2152.02 | 25.89 | 45.186 | 6.34 | 1.379 | 4.892 | 8635.19 | 2.127 | 97.9 | 78 | 1399 | 22.59 | 5612.9 | 3022.6 | 2976.2 | 4356.6 | 1199.6 | 0.67602 | 6.272
2024-12-09 | 18:39 | Data | 0 | 32.028 | 30.07 | 198.797 | 7.63 | 186.627 | 2151.12 | 25.89 | 44.825 | 6.33 | 1.385 | 4.904 | 8630.67 | 2.194 | 97.9 | 78 | 1396 | 22.41 | 5609.9 | 3017.2 | 2982.8 | 4357.2 | 1199.6 | 0.67542 | 6.289
2024-12-09 | 18:39 | Data | 0 | 32.237 | 30.158 | 198.752 | 7.63 | 186.627 | 2154.74 | 25.9 | 44.825 | 6.34 | 1.385 | 4.913 | 8621.63 | 2.302 | 97.9 | 78 | 1401 | 22.46 | 5604.1 | 3043.9 | 2986.2 | 4369.2 | 1199.6 | 0.68012 | 6.299
2024-12-09 | 18:39 | Data | 0 | 32.318 | 29.955 | 198.887 | 7.63 | 186.672 | 2156.54 | 25.88 | 45.186 | 6.34 | 1.386 | 4.879 | 8639.71 | 2.086 | 97.9 | 77.9 | 1401 | 22.59 | 5615.8 | 3033.8 | 3025.4 | 4392 | 1199.6 | 0.67331 | 6.267
2024-12-09 | 18:39 | Data | 0 | 32.237 | 29.969 | 198.842 | 7.63 | 186.627 | 2159.26 | 25.89 | 45.186 | 6.33 | 1.404 | 4.887 | 8635.19 | 2.275 | 97.9 | 77.7 | 1404 | 22.59 | 5612.9 | 3014.5 | 2996.7 | 4365.4 | 1199.6 | 0.67352 | 6.291
2024-12-09 | 18:39 | Data | 0 | 32.237 | 29.949 | 198.842 | 7.63 | 186.672 | 2161.06 | 25.89 | 45.186 | 6.33 | 1.394 | 4.876 | 8626.15 | 2.309 | 97.9 | 77.8 | 1405 | 22.59 | 5607 | 3021.3 | 2963.4 | 4347 | 1199.6 | 0.67833 | 6.269
2024-12-09 | 18:39 | Data | 0 | 32.116 | 30.266 | 198.887 | 7.63 | 186.627 | 2161.06 | 25.89 | 45.186 | 6.33 | 1.383 | 4.887 | 8617.1 | 2.262 | 97.9 | 77.9 | 1405 | 22.59 | 5601.1 | 3034.2 | 3010.8 | 4387 | 1199.6 | 0.67592 | 6.269
2024-12-09 | 18:39 | Data | 0 | 31.805 | 29.901 | 198.571 | 7.63 | 186.492 | 2158.35 | 25.89 | 45.005 | 6.33 | 1.385 | 4.878 | 8635.19 | 2.214 | 97.9 | 77.9 | 1403 | 22.59 | 5612.9 | 3026.9 | 3006.4 | 4381.5 | 1199.6 | 0.67314 | 6.263
2024-12-09 | 18:39 | Data | 0 | 31.886 | 29.901 | 198.797 | 7.63 | 186.537 | 2158.35 | 25.89 | 44.825 | 6.33 | 1.381 | 4.9 | 8653.28 | 2.403 | 97.9 | 78 | 1404 | 22.41 | 5624.6 | 3034.9 | 3008.3 | 4385 | 1199.6 | 0.67553 | 6.28
2024-12-09 | 18:40 | Data | 0 | 32.244 | 29.955 | 198.752 | 7.63 | 186.537 | 2158.35 | 25.89 | 44.825 | 6.33 | 1.388 | 4.876 | 8657.8 | 1.971 | 97.9 | 77.8 | 1404 | 22.41 | 5627.6 | 3011.3 | 3005.3 | 4373 | 1199.6 | 0.67116 | 6.264
2024-12-09 | 18:40 | Data | 0 | 32.372 | 29.571 | 199.611 | 7.63 | 187.26 | 2161.97 | 25.89 | 44.825 | 6.33 | 1.381 | 4.844 | 8657.8 | 2.302 | 97.9 | 77.8 | 1405 | 22.37 | 5627.6 | 3027 | 3010.6 | 4381.8 | 1199.6 | 0.67354 | 6.225
2024-12-09 | 18:40 | Data | 0 | 32.372 | 29.51 | 199.475 | 7.63 | 187.305 | 2155.64 | 25.89 | 44.825 | 6.33 | 1.38 | 4.91 | 8653.28 | 2.133 | 97.9 | 78.1 | 1401 | 22.46 | 5624.6 | 3016.1 | 3019.5 | 4377.3 | 1199.6 | 0.67174 | 6.291
2024-12-09 | 18:40 | Data | 0 | 32.028 | 30.063 | 199.611 | 7.63 | 187.305 | 2153.83 | 25.89 | 44.734 | 6.33 | 1.385 | 4.895 | 8648.76 | 2.106 | 97.9 | 78 | 1400 | 22.37 | 5621.7 | 3030.8 | 2999.5 | 4377.3 | 1199.6 | 0.67525 | 6.279
2024-12-09 | 18:40 | Data | 0 | 32.15 | 29.733 | 199.611 | 7.63 | 187.35 | 2153.83 | 25.89 | 44.825 | 6.33 | 1.391 | 4.902 | 8630.67 | 2.208 | 97.9 | 77.9 | 1400 | 22.41 | 5609.9 | 3021 | 2996.3 | 4369.8 | 1199.6 | 0.67516 | 6.294
2024-12-09 | 18:40 | Data | 0 | 32.028 | 29.901 | 199.611 | 7.63 | 187.395 | 2148.41 | 25.92 | 44.825 | 6.33 | 1.382 | 4.9 | 8648.76 | 2.187 | 97.9 | 78 | 1396 | 22.46 | 5621.7 | 3024.5 | 2985.3 | 4362.9 | 1199.6 | 0.6763 | 6.282
2024-12-09 | 18:40 | Data | 0 | 32.015 | 29.773 | 199.611 | 7.63 | 187.35 | 2154.74 | 25.92 | 44.825 | 6.34 | 1.387 | 4.867 | 8644.24 | 2.201 | 97.9 | 77.8 | 1401 | 22.41 | 5618.8 | 3013.2 | 2980.6 | 4356.2 | 1199.6 | 0.67432 | 6.253
2024-12-09 | 18:40 | Data | 0 | 32.413 | 29.996 | 199.656 | 7.63 | 187.441 | 2153.83 | 25.92 | 44.915 | 6.35 | 1.385 | 4.89 | 8635.19 | 2.329 | 97.9 | 77.9 | 1399 | 22.46 | 5612.9 | 3013 | 2982.9 | 4354.9 | 1199.6 | 0.67542 | 6.274
2024-12-09 | 18:40 | Data | 0 | 32.143 | 29.955 | 199.656 | 7.63 | 187.35 | 2203.54 | 25.94 | 44.825 | 6.33 | 1.384 | 4.9 | 8648.76 | 2.1 | 98 | 78 | 1432 | 22.41 | 5621.7 | 3026.1 | 2990.4 | 4364.9 | 1199.6 | 0.67702 | 6.284
2024-12-09 | 18:40 | Data | 0 | 32.082 | 29.901 | 199.701 | 7.63 | 187.486 | 2206.25 | 25.93 | 44.825 | 6.33 | 1.379 | 4.905 | 8648.76 | 2.322 | 98 | 78.1 | 1434 | 22.46 | 5621.7 | 3043.3 | 2990.9 | 4377.5 | 1199.6 | 0.67804 | 6.284
2024-12-09 | 18:40 | Data | 0 | 32.028 | 29.739 | 199.521 | 7.63 | 187.531 | 2199.02 | 25.93 | 44.734 | 6.33 | 1.385 | 4.891 | 8635.19 | 2.275 | 98 | 77.9 | 1430 | 22.41 | 5612.9 | 3028.4 | 2997.6 | 4371.6 | 1199.6 | 0.67673 | 6.275
2024-12-09 | 18:40 | Data | 0 | 32.264 | 29.962 | 199.701 | 7.63 | 187.395 | 2196.31 | 25.93 | 44.734 | 6.33 | 1.395 | 4.872 | 8644.24 | 2.282 | 98 | 77.8 | 1429 | 22.41 | 5618.8 | 3032.4 | 2989.3 | 4369.3 | 1199.6 | 0.67706 | 6.268
2024-12-09 | 18:40 | Data | 0 | 32.001 | 29.841 | 199.611 | 7.63 | 187.35 | 2147.51 | 25.93 | 44.734 | 6.34 | 1.376 | 4.911 | 8648.76 | 2.289 | 97.9 | 78.1 | 1396 | 22.37 | 5621.7 | 3017.2 | 3001.7 | 4369 | 1199.6 | 0.67345 | 6.288
2024-12-09 | 18:40 | Data | 0 | 32.291 | 30.178 | 199.792 | 7.63 | 187.441 | 2145.7 | 25.92 | 44.825 | 6.33 | 1.375 | 4.932 | 8648.76 | 2.1 | 97.9 | 78.2 | 1394 | 22.41 | 5621.7 | 3030.5 | 2983.9 | 4364.3 | 1199.6 | 0.67647 | 6.308
2024-12-09 | 18:40 | Data | 0 | 32.021 | 29.625 | 199.475 | 7.63 | 187.395 | 2143.89 | 25.93 | 44.915 | 6.33 | 1.392 | 4.92 | 8635.19 | 2.471 | 97.9 | 77.9 | 1394 | 22.41 | 5612.9 | 3039.6 | 2972.6 | 4361.9 | 1199.6 | 0.67994 | 6.311
2024-12-09 | 18:40 | Data | 0 | 32.136 | 29.895 | 199.611 | 7.63 | 187.35 | 2136.66 | 25.93 | 44.734 | 6.34 | 1.387 | 4.873 | 8644.24 | 2.106 | 97.9 | 77.8 | 1389 | 22.41 | 5618.8 | 3019.1 | 2983 | 4359.4 | 1199.6 | 0.67586 | 6.262
2024-12-09 | 18:40 | Data | 0 | 32.028 | 29.753 | 200.063 | 7.63 | 187.757 | 2142.08 | 25.92 | 44.825 | 6.33 | 1.383 | 4.877 | 8635.19 | 2.194 | 97.9 | 77.9 | 1392 | 22.46 | 5612.9 | 3033.7 | 3023 | 4394.3 | 1199.6 | 0.67315 | 6.26
2024-12-09 | 18:40 | Data | 0 | 31.988 | 29.726 | 200.018 | 7.63 | 187.712 | 2145.7 | 25.93 | 44.825 | 6.34 | 1.377 | 4.912 | 8653.28 | 2.295 | 97.9 | 78.1 | 1394 | 22.41 | 5624.6 | 3044.2 | 2990.6 | 4378.2 | 1199.6 | 0.67806 | 6.289
2024-12-09 | 18:41 | Data | 0 | 31.819 | 29.564 | 199.973 | 7.63 | 187.667 | 2144.79 | 25.93 | 44.825 | 6.34 | 1.382 | 4.891 | 8657.8 | 2.039 | 97.9 | 78 | 1394 | 22.46 | 5627.6 | 3032.8 | 3011.3 | 4385 | 1199.6 | 0.67446 | 6.273
2024-12-09 | 18:41 | Data | 0 | 32.028 | 29.901 | 199.973 | 7.63 | 187.621 | 2143.89 | 25.93 | 44.825 | 6.34 | 1.383 | 4.92 | 8639.71 | 2.302 | 97.9 | 78.1 | 1394 | 22.46 | 5615.8 | 3036.6 | 3010.7 | 4378.6 | 1199.6 | 0.67618 | 6.303
2024-12-09 | 18:41 | Data | 0 | 31.799 | 29.726 | 199.837 | 7.63 | 187.576 | 2142.99 | 25.92 | 44.825 | 6.33 | 1.395 | 4.898 | 8580.93 | 2.39 | 97.9 | 77.8 | 1392 | 22.41 | 5577.6 | 3032.2 | 3023.9 | 4374.7 | 1199.6 | 0.67495 | 6.292
2024-12-09 | 18:41 | Data | 0 | 32.028 | 29.503 | 199.792 | 7.63 | 187.576 | 2141.18 | 25.93 | 44.825 | 6.34 | 1.381 | 4.884 | 8571.88 | 2.397 | 97.9 | 77.9 | 1392 | 22.46 | 5571.7 | 3034.9 | 3021.4 | 4395.8 | 1199.6 | 0.67364 | 6.267
2024-12-09 | 18:41 | Data | 0 | 31.927 | 29.679 | 200.063 | 7.63 | 187.757 | 2142.08 | 25.93 | 44.825 | 6.33 | 1.373 | 4.882 | 8553.79 | 2.282 | 97.9 | 78.1 | 1392 | 22.41 | 5560 | 3030.8 | 2989.4 | 4368.7 | 1199.6 | 0.67703 | 6.254
2024-12-09 | 18:41 | Data | 0 | 31.805 | 29.726 | 199.882 | 7.63 | 187.667 | 2142.08 | 25.92 | 44.825 | 6.33 | 1.386 | 4.882 | 8562.84 | 2.187 | 97.9 | 77.9 | 1392 | 22.41 | 5565.8 | 3037.6 | 3003.3 | 4379.9 | 1199.7 | 0.67739 | 6.27
2024-12-09 | 18:41 | Data | 0 | 31.805 | 30.111 | 200.063 | 7.63 | 187.667 | 2140.27 | 25.93 | 44.825 | 6.33 | 1.395 | 4.926 | 8576.4 | 2.302 | 97.9 | 77.9 | 1391 | 22.46 | 5574.7 | 3031.3 | 3004.1 | 4377 | 1199.7 | 0.67533 | 6.32
2024-12-09 | 18:41 | Data | 0 | 31.913 | 29.726 | 199.882 | 7.63 | 187.621 | 2144.79 | 25.93 | 44.825 | 6.33 | 1.392 | 4.92 | 8562.84 | 2.248 | 97.9 | 77.9 | 1394 | 22.41 | 5565.8 | 3027.9 | 2986.7 | 4371.2 | 1199.7 | 0.67499 | 6.313
2024-12-09 | 18:41 | Data | 0 | 31.819 | 30.03 | 199.973 | 7.63 | 187.712 | 2144.79 | 25.92 | 44.825 | 6.33 | 1.389 | 4.91 | 8580.93 | 1.944 | 97.9 | 77.9 | 1394 | 22.41 | 5577.6 | 3038.7 | 3006.7 | 4386.4 | 1199.7 | 0.67552 | 6.298
2024-12-09 | 18:41 | Data | 0 | 32.042 | 29.793 | 199.928 | 7.63 | 187.621 | 2145.7 | 25.93 | 44.825 | 6.33 | 1.382 | 4.901 | 8576.4 | 2.174 | 97.9 | 78 | 1395 | 22.46 | 5574.7 | 3017.4 | 2960.2 | 4339.8 | 1199.7 | 0.67946 | 6.283
2024-12-09 | 18:41 | Data | 0 | 32.096 | 29.625 | 199.973 | 7.63 | 187.712 | 2147.51 | 25.91 | 44.825 | 6.34 | 1.383 | 4.897 | 8580.93 | 2.349 | 97.9 | 78 | 1396 | 22.46 | 5577.6 | 3031.5 | 2985.2 | 4364.1 | 1199.7 | 0.67747 | 6.281
2024-12-09 | 18:41 | Data | 0 | 32.204 | 29.854 | 200.063 | 7.63 | 187.802 | 2151.12 | 25.93 | 44.915 | 6.34 | 1.382 | 4.925 | 8562.84 | 2.221 | 97.9 | 78.1 | 1399 | 22.41 | 5565.8 | 3025.3 | 2995.6 | 4369.9 | 1199.7 | 0.67561 | 6.306
2024-12-09 | 18:41 | Data | 0 | 32.028 | 29.942 | 200.018 | 7.63 | 187.667 | 2144.79 | 25.93 | 44.825 | 6.33 | 1.387 | 4.916 | 8580.93 | 2.295 | 97.9 | 78 | 1395 | 22.41 | 5577.6 | 3023.4 | 3010.4 | 4377.9 | 1199.7 | 0.67329 | 6.302
2024-12-09 | 18:41 | Data | 0 | 32.366 | 29.847 | 200.063 | 7.63 | 187.712 | 2152.93 | 25.93 | 44.825 | 6.33 | 1.379 | 4.919 | 8576.4 | 2.444 | 97.9 | 78.1 | 1399 | 22.41 | 5574.7 | 3028.3 | 3006.2 | 4382.6 | 1199.7 | 0.67312 | 6.297
2024-12-09 | 18:41 | Data | 0 | 32.123 | 29.78 | 200.018 | 7.63 | 187.712 | 2151.12 | 25.93 | 44.734 | 6.34 | 1.387 | 4.924 | 8621.63 | 2.471 | 97.9 | 78 | 1397 | 22.37 | 5604.1 | 3010.2 | 3001.1 | 4364.6 | 1199.7 | 0.67192 | 6.312
2024-12-09 | 18:41 | Data | 0 | 32.136 | 29.814 | 200.018 | 7.63 | 187.712 | 2149.31 | 25.92 | 44.825 | 6.33 | 1.388 | 4.931 | 8630.67 | 2.444 | 97.9 | 78 | 1397 | 22.41 | 5609.9 | 3045.8 | 3023.2 | 4393.4 | 1199.7 | 0.67436 | 6.32
2024-12-09 | 18:41 | Data | 0 | 32.001 | 29.942 | 199.973 | 7.63 | 187.667 | 2152.02 | 25.92 | 44.825 | 6.34 | 1.38 | 4.92 | 8648.76 | 2.262 | 97.9 | 78.1 | 1399 | 22.46 | 5621.7 | 3021.1 | 2981 | 4355.7 | 1199.7 | 0.67623 | 6.3
2024-12-09 | 18:41 | Data | 0 | 32.204 | 30.185 | 200.018 | 7.63 | 187.757 | 2144.79 | 25.92 | 44.825 | 6.34 | 1.382 | 4.89 | 8648.76 | 2.397 | 97.9 | 78 | 1395 | 22.41 | 5621.7 | 3023.2 | 2972.5 | 4355.9 | 1199.7 | 0.67701 | 6.272
2024-12-09 | 18:42 | Data | 0 | 31.805 | 29.841 | 199.973 | 7.63 | 187.712 | 2153.83 | 25.93 | 44.825 | 6.34 | 1.395 | 4.881 | 8648.76 | 2.073 | 97.9 | 77.8 | 1400 | 22.41 | 5621.7 | 3026.8 | 2974.4 | 4358.6 | 1199.7 | 0.67786 | 6.275
2024-12-09 | 18:42 | Data | 0 | 31.805 | 29.726 | 199.928 | 7.63 | 187.757 | 2156.54 | 25.93 | 44.825 | 6.33 | 1.38 | 4.915 | 8657.8 | 2.073 | 97.9 | 78.1 | 1401 | 22.41 | 5627.6 | 3046.3 | 2970.1 | 4367.6 | 1199.7 | 0.68178 | 6.296
2024-12-09 | 18:42 | Data | 0 | 31.805 | 29.699 | 199.882 | 7.63 | 187.576 | 2155.64 | 25.93 | 44.734 | 6.33 | 1.386 | 4.931 | 8653.28 | 2.127 | 97.9 | 78.1 | 1401 | 22.41 | 5624.6 | 3048.2 | 2988.6 | 4377.5 | 1199.7 | 0.6795 | 6.316
2024-12-09 | 18:42 | Data | 0 | 31.846 | 29.901 | 199.973 | 7.63 | 187.712 | 2155.64 | 25.93 | 44.825 | 6.33 | 1.384 | 4.927 | 8657.8 | 1.971 | 97.9 | 78.1 | 1401 | 22.41 | 5627.6 | 3041.2 | 3010.7 | 4389.5 | 1199.7 | 0.6769 | 6.311
2024-12-09 | 18:42 | Data | 0 | 32.042 | 29.733 | 199.973 | 7.63 | 187.712 | 2156.54 | 25.92 | 44.734 | 6.33 | 1.378 | 4.892 | 8666.85 | 2.167 | 97.9 | 78 | 1401 | 22.41 | 5633.5 | 3034.2 | 3003.7 | 4377.5 | 1199.7 | 0.67626 | 6.272
2024-12-09 | 18:42 | Data | 0 | 32.258 | 29.78 | 199.928 | 7.63 | 187.667 | 2156.54 | 25.93 | 44.915 | 6.33 | 1.384 | 4.892 | 8644.24 | 2.187 | 97.9 | 78 | 1401 | 22.46 | 5618.8 | 3031.3 | 3002.1 | 4377.7 | 1199.7 | 0.67559 | 6.276
2024-12-09 | 18:42 | Data | 0 | 32.251 | 30.178 | 200.063 | 7.63 | 187.712 | 2156.54 | 25.92 | 45.276 | 6.33 | 1.39 | 4.9 | 8635.19 | 2.282 | 97.9 | 77.9 | 1402 | 22.59 | 5612.9 | 3039 | 3003.6 | 4382.5 | 1199.7 | 0.67699 | 6.291
2024-12-09 | 18:42 | Data | 0 | 32.264 | 29.638 | 200.018 | 7.63 | 187.757 | 2152.93 | 25.92 | 44.915 | 6.33 | 1.393 | 4.917 | 8666.85 | 2.275 | 97.9 | 77.9 | 1402 | 22.41 | 5633.5 | 3022 | 2971.8 | 4354.5 | 1199.7 | 0.67623 | 6.31
2024-12-09 | 18:42 | Data | 0 | 32.008 | 29.726 | 199.792 | 7.63 | 187.621 | 2156.54 | 25.93 | 44.825 | 6.34 | 1.395 | 4.934 | 8662.33 | 2.302 | 97.9 | 78 | 1402 | 22.37 | 5630.5 | 3024.5 | 2984.4 | 4373.1 | 1199.7 | 0.67662 | 6.329
2024-12-09 | 18:42 | Data | 0 | 32.096 | 29.942 | 199.973 | 7.63 | 187.847 | 2153.83 | 25.93 | 44.825 | 6.34 | 1.39 | 4.92 | 8680.41 | 2.127 | 97.9 | 78 | 1400 | 22.41 | 5642.3 | 3036.1 | 2958.8 | 4352.9 | 1199.7 | 0.68038 | 6.31
2024-12-09 | 18:42 | Data | 0 | 32.021 | 29.726 | 199.973 | 7.63 | 187.667 | 2154.74 | 25.92 | 44.825 | 6.34 | 1.386 | 4.912 | 8666.85 | 2.302 | 97.9 | 78 | 1400 | 22.41 | 5633.5 | 3037.6 | 2963.2 | 4356.3 | 1199.7 | 0.68098 | 6.298
2024-12-09 | 18:42 | Data | 0 | 32.028 | 29.733 | 199.973 | 7.63 | 187.712 | 2153.83 | 25.92 | 44.825 | 6.33 | 1.389 | 4.909 | 8662.33 | 2.275 | 97.9 | 77.9 | 1400 | 22.41 | 5630.5 | 3031.3 | 2947.8 | 4343.3 | 1199.7 | 0.68163 | 6.298
2024-12-09 | 18:42 | Data | 0 | 32.258 | 29.733 | 199.882 | 7.63 | 187.802 | 2153.83 | 25.92 | 44.825 | 6.33 | 1.388 | 4.921 | 8635.19 | 2.147 | 97.9 | 78 | 1399 | 22.41 | 5612.9 | 3026.3 | 2941.6 | 4337.4 | 1199.7 | 0.68141 | 6.309
2024-12-09 | 18:42 | Data | 0 | 32.042 | 29.942 | 200.063 | 7.63 | 187.712 | 2144.79 | 25.92 | 44.825 | 6.33 | 1.38 | 4.932 | 8657.8 | 1.971 | 97.9 | 78.1 | 1395 | 22.46 | 5627.6 | 3023.2 | 2970.5 | 4350.2 | 1199.7 | 0.67974 | 6.314
2024-12-09 | 18:42 | Data | 0 | 32.028 | 29.841 | 200.018 | 7.63 | 187.621 | 2149.31 | 25.93 | 44.734 | 6.34 | 1.392 | 4.913 | 8693.98 | 2.295 | 97.9 | 77.9 | 1396 | 22.41 | 5651.1 | 3047.8 | 2983.7 | 4376.4 | 1199.7 | 0.67969 | 6.304
2024-12-09 | 18:42 | Data | 0 | 32.082 | 30.043 | 200.154 | 7.63 | 187.802 | 2151.12 | 25.93 | 45.457 | 6.34 | 1.377 | 4.897 | 8693.98 | 2.127 | 97.9 | 78.1 | 1397 | 22.68 | 5651.1 | 3037.7 | 2974.6 | 4364.1 | 1199.7 | 0.67961 | 6.274
2024-12-09 | 18:42 | Data | 0 | 32.042 | 29.928 | 200.063 | 7.63 | 187.757 | 2152.93 | 25.93 | 44.825 | 6.34 | 1.386 | 4.891 | 8693.98 | 2.187 | 97.9 | 77.9 | 1400 | 22.37 | 5651.1 | 3041.2 | 2980.6 | 4370.3 | 1199.7 | 0.67892 | 6.278
2024-12-09 | 18:42 | Data | 0 | 32.028 | 29.78 | 199.928 | 7.63 | 187.667 | 2153.83 | 25.92 | 44.825 | 6.34 | 1.388 | 4.899 | 8693.98 | 2.194 | 97.9 | 77.9 | 1399 | 22.41 | 5651.1 | 3017 | 2971.7 | 4343.8 | 1199.7 | 0.67723 | 6.287
2024-12-09 | 18:43 | Data | 0 | 32.028 | 29.928 | 199.882 | 7.63 | 187.712 | 2153.83 | 25.92 | 44.915 | 6.34 | 1.383 | 4.93 | 8703.03 | 2.187 | 97.9 | 78.1 | 1400 | 22.5 | 5657 | 3032.1 | 2997 | 4373.1 | 1199.7 | 0.67747 | 6.315
2024-12-09 | 18:43 | Data | 0 | 32.237 | 30.063 | 200.063 | 7.63 | 187.802 | 2158.35 | 25.92 | 44.915 | 6.34 | 1.377 | 4.926 | 8707.55 | 2.268 | 97.9 | 78.1 | 1404 | 22.41 | 5659.9 | 3026.2 | 3023.4 | 4390.4 | 1199.7 | 0.67247 | 6.303
2024-12-09 | 18:43 | Data | 0 | 32.204 | 30.063 | 200.063 | 7.63 | 187.757 | 2153.83 | 25.93 | 44.825 | 6.34 | 1.377 | 4.907 | 8703.03 | 2.228 | 97.9 | 78.1 | 1401 | 22.46 | 5657 | 3047.5 | 2995.8 | 4378.3 | 1199.7 | 0.67715 | 6.283
2024-12-09 | 18:43 | Data | 0 | 31.819 | 29.841 | 200.018 | 7.63 | 187.712 | 2155.64 | 25.93 | 44.825 | 6.34 | 1.383 | 4.929 | 8703.03 | 2.079 | 97.9 | 78.1 | 1401 | 22.46 | 5657 | 3028.7 | 2984.5 | 4365.2 | 1199.7 | 0.67709 | 6.311
2024-12-09 | 18:43 | Data | 0 | 31.92 | 29.726 | 199.973 | 7.63 | 187.667 | 2155.64 | 25.92 | 44.825 | 6.34 | 1.38 | 4.937 | 8707.55 | 2.208 | 97.9 | 78.2 | 1401 | 22.41 | 5659.9 | 3014.6 | 2950.6 | 4336.1 | 1199.8 | 0.6787 | 6.319
2024-12-09 | 18:43 | Data | 0 | 32.055 | 29.726 | 199.928 | 7.63 | 187.757 | 2156.54 | 25.93 | 44.825 | 6.33 | 1.39 | 4.927 | 8671.37 | 2.127 | 97.9 | 78 | 1401 | 22.41 | 5636.4 | 3040.2 | 2968.4 | 4360.4 | 1199.8 | 0.68007 | 6.316
2024-12-09 | 18:43 | Data | 0 | 32.204 | 29.733 | 200.063 | 7.63 | 187.802 | 2154.74 | 25.93 | 44.825 | 6.34 | 1.394 | 4.91 | 8693.98 | 2.241 | 97.9 | 77.9 | 1400 | 22.41 | 5651.1 | 3017.1 | 2968.1 | 4343.1 | 1199.8 | 0.67882 | 6.304
2024-12-09 | 18:43 | Data | 0 | 32.116 | 29.928 | 200.109 | 7.63 | 187.712 | 2152.93 | 25.93 | 44.734 | 6.33 | 1.386 | 4.94 | 8680.41 | 2.113 | 97.9 | 78.1 | 1399 | 22.41 | 5642.3 | 3020.3 | 2951.3 | 4335.6 | 1199.8 | 0.67848 | 6.329
2024-12-09 | 18:43 | Data | 0 | 32.264 | 30.07 | 200.018 | 7.63 | 187.757 | 2147.51 | 25.92 | 44.825 | 6.33 | 1.391 | 4.911 | 8689.46 | 2.309 | 97.9 | 77.9 | 1396 | 22.41 | 5648.1 | 3022.7 | 2934.2 | 4325.8 | 1199.8 | 0.68252 | 6.303
2024-12-09 | 18:43 | Data | 0 | 32.001 | 29.706 | 199.882 | 7.63 | 187.576 | 2151.12 | 25.92 | 44.825 | 6.33 | 1.387 | 4.904 | 8228.19 | 2.336 | 97.9 | 78 | 1397 | 22.41 | 5348.3 | 3044.1 | 2976.2 | 4369.2 | 1199.8 | 0.67938 | 6.292
2024-12-09 | 18:43 | Data | 0 | 32.372 | 29.766 | 199.973 | 7.63 | 187.712 | 2151.12 | 25.93 | 44.734 | 6.33 | 1.394 | 4.892 | 8630.67 | 2.302 | 97.9 | 77.8 | 1398 | 22.41 | 5609.9 | 3007.8 | 2985.5 | 4349.4 | 1199.8 | 0.67498 | 6.286
2024-12-09 | 18:43 | Data | 0 | 32.028 | 29.726 | 199.928 | 7.63 | 187.667 | 2149.31 | 25.92 | 44.825 | 6.34 | 1.383 | 4.891 | 8662.33 | 2.302 | 97.9 | 78 | 1397 | 22.41 | 5630.5 | 3012.8 | 2961.4 | 4341.4 | 1199.8 | 0.67985 | 6.273
2024-12-09 | 18:43 | Data | 0 | 32.055 | 29.503 | 199.747 | 7.63 | 187.712 | 2151.12 | 25.92 | 44.644 | 6.34 | 1.372 | 4.911 | 8644.24 | 2.289 | 97.9 | 78.2 | 1397 | 22.46 | 5618.8 | 3027.7 | 2970.9 | 4352.9 | 1199.8 | 0.67826 | 6.282
2024-12-09 | 18:43 | Data | 0 | 32.028 | 29.726 | 199.882 | 7.63 | 187.712 | 2151.12 | 25.93 | 44.915 | 6.33 | 1.371 | 4.931 | 8657.8 | 2.363 | 97.9 | 78.2 | 1397 | 22.41 | 5627.6 | 3019.6 | 2942.5 | 4326.9 | 1199.8 | 0.68179 | 6.304
2024-12-09 | 18:43 | Data | 0 | 32.028 | 30.111 | 200.018 | 7.63 | 187.757 | 2151.12 | 25.92 | 44.825 | 6.34 | 1.382 | 4.902 | 8662.33 | 2.241 | 97.9 | 78 | 1397 | 22.41 | 5630.5 | 3029.3 | 2953.1 | 4346.3 | 1199.8 | 0.67938 | 6.285
2024-12-09 | 18:43 | Data | 0 | 31.974 | 30.34 | 199.928 | 7.63 | 187.712 | 2144.79 | 25.92 | 45.186 | 6.33 | 1.395 | 4.915 | 8648.76 | 2.289 | 97.9 | 77.9 | 1395 | 22.59 | 5621.7 | 3020.5 | 2957.2 | 4339.4 | 1199.8 | 0.68077 | 6.309
2024-12-09 | 18:43 | Data | 0 | 32.15 | 29.733 | 200.109 | 7.63 | 187.802 | 2152.93 | 25.93 | 44.915 | 6.34 | 1.394 | 4.928 | 8648.76 | 2.289 | 97.9 | 78 | 1399 | 22.41 | 5621.7 | 3035.2 | 2984.6 | 4369.7 | 1199.8 | 0.67745 | 6.32
2024-12-09 | 18:44 | Data | 0 | 32.021 | 29.834 | 199.928 | 7.63 | 187.712 | 2152.93 | 25.92 | 44.915 | 6.34 | 1.389 | 4.901 | 8621.63 | 2.194 | 97.9 | 77.9 | 1399 | 22.37 | 5604.1 | 3014.6 | 2976.1 | 4350.8 | 1199.8 | 0.67641 | 6.291
2024-12-09 | 18:44 | Data | 0 | 32.028 | 29.942 | 199.973 | 7.63 | 187.757 | 2153.83 | 25.93 | 44.825 | 6.34 | 1.395 | 4.907 | 8635.19 | 2.127 | 97.9 | 77.9 | 1400 | 22.41 | 5612.9 | 3016.2 | 2985.5 | 4356.7 | 1199.8 | 0.67634 | 6.301
2024-12-09 | 18:44 | Data | 0 | 32.028 | 30.084 | 200.018 | 7.63 | 187.712 | 2148.41 | 25.92 | 44.825 | 6.35 | 1.395 | 4.932 | 8626.15 | 2.16 | 97.9 | 78 | 1396 | 22.41 | 5607 | 3027.7 | 2992.7 | 4370.4 | 1199.8 | 0.67635 | 6.327
2024-12-09 | 18:44 | Data | 0 | 32.015 | 29.726 | 200.018 | 7.63 | 187.712 | 2153.83 | 25.92 | 44.825 | 6.34 | 1.388 | 4.911 | 8630.67 | 2.302 | 97.9 | 78 | 1400 | 22.46 | 5609.9 | 3023.7 | 2970.3 | 4352.3 | 1199.8 | 0.67781 | 6.301
2024-12-09 | 18:44 | Data | 0 | 32.359 | 29.847 | 200.199 | 7.63 | 187.712 | 2152.93 | 25.93 | 44.825 | 6.33 | 1.384 | 4.904 | 8630.67 | 2.356 | 97.9 | 78 | 1400 | 22.46 | 5609.9 | 3030.6 | 2962.2 | 4350.5 | 1199.8 | 0.67997 | 6.288
2024-12-09 | 18:44 | Data | 0 | 32.204 | 29.949 | 200.109 | 7.63 | 187.757 | 2152.93 | 25.92 | 44.734 | 6.33 | 1.386 | 4.91 | 8644.24 | 1.944 | 97.9 | 78 | 1399 | 22.41 | 5618.8 | 3016.7 | 2954.2 | 4343.5 | 1199.8 | 0.67758 | 6.297
2024-12-09 | 18:44 | Data | 0 | 32.028 | 29.726 | 200.018 | 7.63 | 187.712 | 2153.83 | 25.92 | 44.734 | 6.34 | 1.391 | 4.927 | 8630.67 | 2.302 | 97.9 | 78 | 1399 | 22.41 | 5609.9 | 3019.9 | 2964.4 | 4334.7 | 1199.8 | 0.6781 | 6.319
2024-12-09 | 18:44 | Data | 0 | 32.048 | 29.949 | 199.973 | 7.63 | 187.712 | 2153.83 | 25.92 | 44.734 | 6.34 | 1.384 | 4.902 | 8594.49 | 2.005 | 97.9 | 78 | 1400 | 22.41 | 5586.4 | 3018.5 | 2968.8 | 4344.1 | 1199.8 | 0.6799 | 6.288
2024-12-09 | 18:44 | Data | 0 | 32.055 | 29.955 | 199.973 | 7.63 | 187.712 | 2151.12 | 25.9 | 44.825 | 6.34 | 1.384 | 4.884 | 8580.93 | 2.086 | 97.9 | 77.9 | 1399 | 22.46 | 5577.6 | 3025.9 | 2980.5 | 4361.1 | 1199.8 | 0.68064 | 6.271
2024-12-09 | 18:44 | Data | 0 | 32.028 | 29.901 | 200.063 | 7.63 | 187.802 | 2153.83 | 25.92 | 44.915 | 6.33 | 1.388 | 4.892 | 8599.01 | 2.187 | 97.9 | 77.9 | 1400 | 22.41 | 5589.4 | 3037.9 | 2972.2 | 4359 | 1199.8 | 0.67944 | 6.281
2024-12-09 | 18:44 | Data | 0 | 32.143 | 29.901 | 199.973 | 7.63 | 187.712 | 2157.45 | 25.92 | 44.915 | 6.34 | 1.381 | 4.887 | 8594.49 | 2.302 | 97.9 | 78 | 1402 | 22.41 | 5586.4 | 3026 | 3008.1 | 4379.4 | 1199.8 | 0.67456 | 6.269
2024-12-09 | 18:44 | Data | 0 | 32.318 | 29.746 | 200.063 | 7.63 | 187.802 | 2155.64 | 25.92 | 45.276 | 6.34 | 1.397 | 4.896 | 8657.8 | 2.181 | 97.9 | 77.8 | 1401 | 22.59 | 5627.6 | 3046.1 | 3006.1 | 4389.2 | 1199.8 | 0.67711 | 6.292
2024-12-09 | 18:44 | Data | 0 | 32.352 | 30.178 | 200.244 | 7.63 | 187.802 | 2156.54 | 25.93 | 45.186 | 6.33 | 1.39 | 4.918 | 8662.33 | 2.295 | 97.9 | 78 | 1402 | 22.59 | 5630.5 | 3013.1 | 2988.3 | 4355.2 | 1199.8 | 0.67565 | 6.308
2024-12-09 | 18:44 | Data | 0 | 32.028 | 30.057 | 200.018 | 7.63 | 187.712 | 2154.74 | 25.93 | 45.186 | 6.34 | 1.382 | 4.911 | 8657.8 | 2.012 | 97.9 | 78 | 1401 | 22.59 | 5627.6 | 3031.4 | 2944 | 4334.3 | 1199.8 | 0.68388 | 6.293
2024-12-09 | 18:44 | Data | 0 | 32.028 | 29.949 | 200.063 | 7.63 | 187.802 | 2155.64 | 25.93 | 45.005 | 6.33 | 1.38 | 4.913 | 8662.33 | 2.079 | 97.9 | 78.1 | 1402 | 22.5 | 5630.5 | 3026.9 | 2959.4 | 4346.9 | 1199.8 | 0.67866 | 6.293
2024-12-09 | 18:44 | Data | 0 | 32.528 | 29.8 | 200.154 | 7.63 | 187.847 | 2156.54 | 25.92 | 45.186 | 6.34 | 1.386 | 4.911 | 8594.49 | 2.322 | 97.9 | 78 | 1402 | 22.59 | 5586.4 | 3036.5 | 2941.8 | 4343.7 | 1199.8 | 0.68239 | 6.296
2024-12-09 | 18:44 | Data | 0 | 32.251 | 30.124 | 200.018 | 7.62 | 187.847 | 2156.54 | 25.93 | 45.186 | 6.34 | 1.389 | 4.911 | 8576.4 | 2.309 | 97.9 | 77.9 | 1401 | 22.59 | 5574.7 | 3020.6 | 2928.3 | 4322.1 | 1199.8 | 0.68332 | 6.3
2024-12-09 | 18:44 | Data | 0 | 32.386 | 29.969 | 200.063 | 7.63 | 187.847 | 2155.64 | 25.92 | 45.186 | 6.34 | 1.375 | 4.905 | 8576.4 | 2.221 | 97.9 | 78.1 | 1402 | 22.59 | 5574.7 | 3029.9 | 2939.6 | 4338.1 | 1199.8 | 0.68488 | 6.282
2024-12-09 | 18:45 | Data | 0 | 32.028 | 29.726 | 199.928 | 7.63 | 187.757 | 2157.45 | 25.92 | 45.276 | 6.34 | 1.373 | 4.92 | 8585.45 | 2.302 | 97.9 | 78.2 | 1400 | 22.59 | 5580.5 | 3049.8 | 2934.8 | 4341.2 | 1199.8 | 0.68753 | 6.292
2024-12-09 | 18:45 | Data | 0 | 32.204 | 29.78 | 200.018 | 7.63 | 187.757 | 2155.64 | 25.92 | 45.186 | 6.34 | 1.379 | 4.945 | 8580.93 | 2.417 | 97.9 | 78.2 | 1402 | 22.64 | 5577.6 | 3033.5 | 2954.2 | 4347.1 | 1199.8 | 0.6843 | 6.324
2024-12-09 | 18:45 | Data | 0 | 31.927 | 29.733 | 200.154 | 7.63 | 187.847 | 2156.54 | 25.92 | 44.734 | 6.34 | 1.389 | 4.91 | 8585.45 | 2.262 | 97.9 | 77.9 | 1401 | 22.46 | 5580.5 | 3021 | 2964.9 | 4346.7 | 1199.8 | 0.67802 | 6.299
2024-12-09 | 18:45 | Data | 0 | 32.494 | 30.185 | 200.063 | 7.63 | 187.847 | 2153.83 | 25.93 | 45.005 | 6.34 | 1.381 | 4.884 | 8599.01 | 2.194 | 97.9 | 78 | 1400 | 22.59 | 5589.4 | 3028 | 2971.4 | 4354.2 | 1199.8 | 0.67943 | 6.266
2024-12-09 | 18:45 | Data | 0 | 32.204 | 30.232 | 199.973 | 7.63 | 187.938 | 2153.83 | 25.92 | 44.825 | 6.34 | 1.378 | 4.908 | 8594.49 | 2.201 | 97.9 | 78 | 1400 | 22.41 | 5586.4 | 3021.1 | 2964.1 | 4347.6 | 1199.9 | 0.67875 | 6.287
2024-12-09 | 18:45 | Data | 0 | 32.028 | 30.07 | 200.063 | 7.63 | 187.757 | 2153.83 | 25.92 | 44.915 | 6.34 | 1.389 | 4.92 | 8617.1 | 2.248 | 97.9 | 78 | 1400 | 22.41 | 5601.1 | 3023.9 | 2968.2 | 4353.5 | 1199.9 | 0.67749 | 6.31
2024-12-09 | 18:45 | Data | 0 | 32.042 | 29.841 | 200.109 | 7.63 | 187.802 | 2156.54 | 25.93 | 44.734 | 6.33 | 1.38 | 4.929 | 8621.63 | 2.187 | 97.9 | 78.1 | 1402 | 22.41 | 5604.1 | 3041.9 | 2978 | 4370.3 | 1199.9 | 0.67888 | 6.309
2024-12-09 | 18:45 | Data | 0 | 32.028 | 29.726 | 200.063 | 7.63 | 187.757 | 2153.83 | 25.93 | 44.825 | 6.33 | 1.387 | 4.936 | 9096.46 | 2.302 | 97.9 | 78.1 | 1400 | 22.41 | 5912.7 | 3010.4 | 2963.5 | 4339.8 | 1199.9 | 0.67745 | 6.322
2024-12-09 | 18:45 | Data | 0 | 32.352 | 30.009 | 200.018 | 7.63 | 187.802 | 2152.93 | 25.93 | 44.825 | 6.33 | 1.389 | 4.937 | 8666.85 | 2.41 | 97.9 | 78 | 1400 | 22.46 | 5633.5 | 3016.3 | 2940.7 | 4327.5 | 1199.9 | 0.67988 | 6.325
2024-12-09 | 18:45 | Data | 0 | 32.312 | 29.874 | 200.063 | 7.63 | 187.802 | 2156.54 | 25.92 | 44.825 | 6.33 | 1.391 | 4.914 | 8648.76 | 2.417 | 97.9 | 77.9 | 1402 | 22.46 | 5621.7 | 3014.6 | 2919.8 | 4322.5 | 1199.9 | 0.68428 | 6.305
2024-12-09 | 18:45 | Data | 0 | 32.062 | 29.841 | 199.973 | 7.63 | 187.712 | 2155.64 | 25.93 | 44.915 | 6.35 | 1.379 | 4.913 | 8644.24 | 2.208 | 97.9 | 78.1 | 1401 | 22.41 | 5618.8 | 3017 | 2947.4 | 4331.4 | 1199.9 | 0.68041 | 6.292
2024-12-09 | 18:45 | Data | 0 | 31.859 | 29.928 | 199.973 | 7.63 | 187.667 | 2161.97 | 25.93 | 44.283 | 6.34 | 1.381 | 4.897 | 8630.67 | 2.255 | 98 | 78 | 1405 | 22.14 | 5609.9 | 3040 | 2962.3 | 4357.2 | 1199.9 | 0.68137 | 6.277
2024-12-09 | 18:45 | Data | 0 | 32.46 | 30.171 | 200.018 | 7.63 | 187.938 | 2151.12 | 25.93 | 44.915 | 6.33 | 1.386 | 4.913 | 8635.19 | 2.201 | 97.9 | 78 | 1397 | 22.41 | 5612.9 | 3027.1 | 2938.8 | 4329.3 | 1199.9 | 0.68319 | 6.3
2024-12-09 | 18:45 | Data | 0 | 32.231 | 29.955 | 200.063 | 7.63 | 187.712 | 2158.35 | 25.93 | 44.825 | 6.34 | 1.386 | 4.894 | 8621.63 | 2.295 | 97.9 | 77.9 | 1403 | 22.41 | 5604.1 | 3031.9 | 2995.8 | 4376.2 | 1199.9 | 0.67682 | 6.282
2024-12-09 | 18:45 | Data | 0 | 32.028 | 29.928 | 200.109 | 7.63 | 187.757 | 2152.93 | 25.91 | 44.915 | 6.33 | 1.38 | 4.905 | 8648.76 | 2.302 | 97.9 | 78 | 1400 | 22.46 | 5621.7 | 3055.7 | 3026.9 | 4398.5 | 1199.9 | 0.67321 | 6.285
2024-12-09 | 18:45 | Data | 0 | 32.291 | 29.733 | 200.063 | 7.63 | 187.802 | 2152.02 | 25.93 | 44.825 | 6.33 | 1.383 | 4.911 | 8635.19 | 2.255 | 97.9 | 78 | 1399 | 22.41 | 5612.9 | 3037.2 | 2988.8 | 4371.1 | 1199.9 | 0.67803 | 6.295
2024-12-09 | 18:45 | Data | 0 | 32.035 | 29.726 | 200.063 | 7.63 | 187.667 | 2152.93 | 25.93 | 44.734 | 6.34 | 1.38 | 4.914 | 8635.19 | 2.302 | 97.9 | 78.1 | 1399 | 22.37 | 5612.9 | 3058.7 | 3015.9 | 4401.9 | 1199.9 | 0.67868 | 6.295
2024-12-09 | 18:45 | Data | 0 | 32.291 | 29.962 | 200.109 | 7.63 | 187.938 | 2152.93 | 25.93 | 44.825 | 6.34 | 1.39 | 4.903 | 8974.36 | 2.302 | 97.9 | 77.9 | 1399 | 22.46 | 5833.3 | 3021.4 | 2986.5 | 4383.3 | 1199.9 | 0.68003 | 6.292
2024-12-09 | 18:46 | Data | 0 | 32.264 | 30.158 | 200.154 | 7.63 | 187.983 | 2155.64 | 25.92 | 44.825 | 6.34 | 1.384 | 4.916 | 8562.84 | 2.181 | 97.9 | 78 | 1401 | 22.46 | 5565.8 | 3047 | 2965.2 | 4357.6 | 1199.9 | 0.68308 | 6.3
2024-12-09 | 18:46 | Data | 0 | 32.345 | 29.969 | 200.018 | 7.63 | 187.712 | 2155.64 | 25.93 | 44.915 | 6.34 | 1.395 | 4.897 | 8427.17 | 2.295 | 97.9 | 77.8 | 1401 | 22.41 | 5477.7 | 3065.5 | 2979.4 | 4384.2 | 1199.9 | 0.68357 | 6.292
2024-12-09 | 18:46 | Data | 0 | 32.177 | 29.76 | 200.154 | 7.63 | 187.802 | 2156.54 | 25.93 | 44.825 | 6.33 | 1.395 | 4.915 | 8418.13 | 2.262 | 97.9 | 77.9 | 1401 | 22.41 | 5471.8 | 3044.1 | 2953.3 | 4350.9 | 1199.9 | 0.68266 | 6.31
2024-12-09 | 18:46 | Data | 0 | 32.197 | 29.955 | 200.109 | 7.63 | 187.802 | 2152.93 | 25.93 | 44.734 | 6.34 | 1.377 | 4.918 | 8440.74 | 2.302 | 97.9 | 78.1 | 1399 | 22.37 | 5486.5 | 3033.1 | 2939.9 | 4334.3 | 1199.9 | 0.6832 | 6.295
2024-12-09 | 18:46 | Data | 0 | 32.318 | 30.171 | 200.063 | 7.63 | 187.938 | 2152.02 | 25.92 | 44.825 | 6.33 | 1.375 | 4.914 | 8454.3 | 1.978 | 97.9 | 78.2 | 1399 | 22.41 | 5495.3 | 3043.4 | 2949.9 | 4351.7 | 1199.9 | 0.6826 | 6.288
2024-12-09 | 18:46 | Data | 0 | 32.028 | 29.841 | 200.109 | 7.63 | 187.757 | 2154.74 | 25.93 | 44.464 | 6.34 | 1.393 | 4.921 | 8458.83 | 2.302 | 97.9 | 77.9 | 1399 | 22.23 | 5498.2 | 3024.4 | 2941.1 | 4332.1 | 1199.9 | 0.68055 | 6.314
2024-12-09 | 18:46 | Data | 0 | 32.474 | 29.969 | 200.109 | 7.63 | 187.847 | 2156.54 | 25.93 | 44.644 | 6.34 | 1.393 | 4.903 | 8472.39 | 2.201 | 97.9 | 77.9 | 1401 | 22.28 | 5507.1 | 3042.1 | 2954 | 4349.5 | 1199.9 | 0.68281 | 6.296
2024-12-09 | 18:46 | Data | 0 | 32.345 | 30.171 | 199.973 | 7.63 | 187.712 | 2160.16 | 25.93 | 44.554 | 6.34 | 1.385 | 4.938 | 8476.91 | 2.302 | 97.9 | 78.1 | 1404 | 22.28 | 5510 | 3062.9 | 2952 | 4361.3 | 1199.9 | 0.68554 | 6.325
2024-12-09 | 18:46 | Data | 0 | 31.893 | 29.841 | 200.018 | 7.63 | 187.757 | 2156.54 | 25.91 | 44.644 | 6.33 | 1.404 | 4.928 | 8508.57 | 2.086 | 97.9 | 77.8 | 1402 | 22.32 | 5530.6 | 3039.6 | 2990.7 | 4377.1 | 1199.9 | 0.67791 | 6.331
2024-12-09 | 18:46 | Data | 0 | 32.264 | 30.07 | 200.154 | 7.63 | 187.847 | 2155.64 | 25.93 | 44.825 | 6.33 | 1.397 | 4.908 | 8495 | 2.262 | 97.9 | 77.8 | 1401 | 22.46 | 5521.8 | 3021.9 | 2982.4 | 4356.1 | 1199.9 | 0.67761 | 6.304
2024-12-09 | 18:46 | Data | 0 | 32.318 | 29.861 | 200.199 | 7.63 | 187.938 | 2158.35 | 25.93 | 44.825 | 6.34 | 1.389 | 4.907 | 8495 | 2.262 | 97.9 | 77.9 | 1404 | 22.32 | 5521.8 | 3021.1 | 2962.1 | 4344.5 | 1199.9 | 0.67887 | 6.296
2024-12-09 | 18:46 | Data | 0 | 32.258 | 29.753 | 199.837 | 7.63 | 187.757 | 2144.79 | 25.92 | 44.554 | 6.34 | 1.393 | 4.907 | 8870.35 | 2.329 | 97.9 | 77.9 | 1394 | 22.28 | 5765.7 | 3033.5 | 2968.7 | 4357.5 | 1199.9 | 0.68077 | 6.3
2024-12-09 | 18:46 | Data | 0 | 32.474 | 29.996 | 200.109 | 7.62 | 187.847 | 2155.64 | 25.93 | 44.554 | 6.33 | 1.388 | 4.879 | 8395.51 | 2.336 | 97.9 | 77.9 | 1401 | 22.28 | 5457.1 | 3036.7 | 2948 | 4347.8 | 1199.9 | 0.68368 | 6.265
2024-12-09 | 18:46 | Data | 0 | 32.487 | 29.847 | 200.018 | 7.63 | 187.802 | 2156.54 | 25.92 | 44.644 | 6.33 | 1.39 | 4.898 | 8400.04 | 2.356 | 97.9 | 77.9 | 1402 | 22.28 | 5460 | 3026.1 | 2943.7 | 4334.3 | 1199.9 | 0.68205 | 6.288
2024-12-09 | 18:46 | Data | 0 | 32.366 | 29.982 | 199.973 | 7.63 | 187.757 | 2155.64 | 25.92 | 44.554 | 6.33 | 1.384 | 4.916 | 8431.69 | 2.363 | 97.9 | 78 | 1402 | 22.28 | 5480.6 | 3017.3 | 2925 | 4314.8 | 1199.9 | 0.68219 | 6.3
2024-12-09 | 18:46 | Data | 0 | 32.035 | 29.901 | 199.973 | 7.63 | 187.757 | 2153.83 | 25.93 | 44.373 | 6.34 | 1.38 | 4.925 | 8431.69 | 2.187 | 97.9 | 78.1 | 1399 | 22.28 | 5480.6 | 3034.3 | 2943.9 | 4342.5 | 1199.9 | 0.68203 | 6.305
2024-12-09 | 18:46 | Data | 0 | 32.156 | 29.733 | 199.973 | 7.63 | 187.757 | 2154.74 | 25.93 | 44.644 | 6.34 | 1.383 | 4.93 | 8454.3 | 2.133 | 97.9 | 78.1 | 1401 | 22.28 | 5495.3 | 3033.3 | 2939.1 | 4337.6 | 1199.9 | 0.68257 | 6.312
2024-12-09 | 18:46 | Data | 0 | 32.102 | 29.868 | 200.063 | 7.63 | 187.938 | 2155.64 | 25.93 | 44.554 | 6.34 | 1.377 | 4.93 | 8467.87 | 2.167 | 97.9 | 78.2 | 1401 | 22.28 | 5504.1 | 3035 | 2954.6 | 4349.9 | 1199.9 | 0.68216 | 6.308
2024-12-09 | 18:47 | Data | 0 | 32.116 | 29.733 | 199.928 | 7.63 | 187.847 | 2155.64 | 25.92 | 44.554 | 6.33 | 1.376 | 4.917 | 8481.44 | 2.316 | 97.9 | 78.1 | 1401 | 22.28 | 5512.9 | 3043.7 | 2954.3 | 4356 | 1199.9 | 0.68306 | 6.293
2024-12-09 | 18:47 | Data | 0 | 32.595 | 30.205 | 199.973 | 7.63 | 187.802 | 2155.64 | 25.93 | 44.554 | 6.33 | 1.377 | 4.938 | 8485.96 | 2.329 | 97.9 | 78.2 | 1401 | 22.32 | 5515.9 | 3016.3 | 2941.7 | 4325.5 | 1199.9 | 0.67987 | 6.315
2024-12-09 | 18:47 | Data | 0 | 32.251 | 29.861 | 200.018 | 7.63 | 187.757 | 2190.89 | 25.93 | 44.464 | 6.33 | 1.387 | 4.912 | 8513.09 | 2.262 | 98 | 78 | 1426 | 22.28 | 5533.5 | 3022.9 | 2961.5 | 4341.3 | 1199.9 | 0.68039 | 6.298
2024-12-09 | 18:47 | Data | 0 | 32.136 | 29.949 | 200.063 | 7.62 | 187.802 | 2208.06 | 25.92 | 44.644 | 6.34 | 1.391 | 4.921 | 8526.66 | 2.106 | 98 | 78 | 1435 | 22.32 | 5542.3 | 3044.3 | 2962.8 | 4359.3 | 1200 | 0.68217 | 6.311
2024-12-09 | 18:47 | Data | 0 | 32.062 | 29.915 | 200.154 | 7.63 | 187.847 | 2207.16 | 25.93 | 44.554 | 6.33 | 1.378 | 4.925 | 8879.39 | 2.167 | 98 | 78.1 | 1435 | 22.28 | 5771.6 | 3041 | 2953.1 | 4349.5 | 1200 | 0.68289 | 6.304
2024-12-09 | 18:47 | Data | 0 | 32.035 | 29.949 | 200.199 | 7.63 | 187.802 | 2212.58 | 25.93 | 44.554 | 6.34 | 1.378 | 4.909 | 8440.74 | 2.106 | 98 | 78.1 | 1439 | 22.28 | 5486.5 | 3054.5 | 2966.1 | 4365.5 | 1200 | 0.6833 | 6.288
2024-12-09 | 18:47 | Data | 0 | 32.15 | 29.949 | 199.973 | 7.63 | 187.802 | 2201.74 | 25.93 | 44.464 | 6.34 | 1.379 | 4.891 | 8277.94 | 2.322 | 98 | 78 | 1428 | 22.23 | 5380.7 | 3033.3 | 2934.5 | 4337.2 | 1200 | 0.68233 | 6.269
2024-12-09 | 18:47 | Data | 0 | 32.359 | 29.955 | 200.289 | 7.63 | 187.802 | 2163.77 | 25.92 | 44.644 | 6.34 | 1.39 | 4.92 | 8264.37 | 2.322 | 97.9 | 78 | 1406 | 22.32 | 5371.8 | 3026.6 | 2951.4 | 4341.7 | 1200 | 0.68125 | 6.311
2024-12-09 | 18:47 | Data | 0 | 32.251 | 30.165 | 200.199 | 7.63 | 187.757 | 2163.77 | 25.92 | 44.554 | 6.33 | 1.376 | 4.94 | 8282.46 | 2.113 | 97.9 | 78.2 | 1406 | 22.28 | 5383.6 | 3041.6 | 2937.5 | 4338.3 | 1200 | 0.68471 | 6.316
2024-12-09 | 18:47 | Data | 0 | 32.204 | 29.955 | 200.109 | 7.63 | 187.757 | 2163.77 | 25.93 | 44.554 | 6.34 | 1.377 | 4.922 | 8277.94 | 2.302 | 97.9 | 78.1 | 1407 | 22.28 | 5380.7 | 3040.8 | 2941.2 | 4346.7 | 1200 | 0.68439 | 6.3
2024-12-09 | 18:47 | Data | 0 | 32.258 | 29.955 | 200.109 | 7.63 | 187.802 | 2165.58 | 25.93 | 44.825 | 6.35 | 1.386 | 4.92 | 8472.39 | 2.133 | 97.9 | 78 | 1406 | 22.41 | 5507.1 | 3026.5 | 2943 | 4333.7 | 1200 | 0.68302 | 6.31
2024-12-09 | 18:47 | Data | 0 | 32.251 | 29.955 | 200.063 | 7.63 | 187.802 | 2162.87 | 25.93 | 44.825 | 6.34 | 1.389 | 4.91 | 8508.57 | 2.302 | 97.9 | 77.9 | 1406 | 22.41 | 5530.6 | 3028.7 | 2928.3 | 4321.2 | 1200 | 0.68449 | 6.299
2024-12-09 | 18:47 | Data | 0 | 32.251 | 29.787 | 200.244 | 7.63 | 187.802 | 2053.51 | 25.93 | 44.825 | 6.33 | 1.391 | 4.909 | 8526.66 | 2.302 | 97.8 | 77.9 | 1335 | 22.41 | 5542.3 | 3043.4 | 2962.1 | 4342.9 | 1200 | 0.68156 | 6.3
2024-12-09 | 18:47 | Data | 0 | 32.278 | 30.185 | 200.018 | 7.62 | 187.847 | 2158.35 | 25.93 | 44.825 | 6.33 | 1.391 | 4.9 | 8517.61 | 2.194 | 97.9 | 77.9 | 1404 | 22.41 | 5536.4 | 3028.8 | 2928.5 | 4321.1 | 1200 | 0.68535 | 6.291
2024-12-09 | 18:47 | Data | 0 | 31.805 | 29.726 | 200.109 | 7.63 | 187.802 | 2156.54 | 25.93 | 44.915 | 6.34 | 1.384 | 4.92 | 8517.61 | 2.073 | 97.9 | 78 | 1402 | 22.41 | 5536.4 | 3012.1 | 2965.3 | 4342.2 | 1200 | 0.67748 | 6.304
2024-12-09 | 18:47 | Data | 0 | 32.089 | 29.841 | 199.973 | 7.63 | 187.757 | 2153.83 | 25.92 | 45.005 | 6.34 | 1.402 | 4.926 | 8508.57 | 2.322 | 97.9 | 77.8 | 1399 | 22.46 | 5530.6 | 3052.9 | 2953 | 4361 | 1200 | 0.68324 | 6.329
2024-12-09 | 18:47 | Data | 0 | 32.123 | 29.982 | 200.063 | 7.63 | 187.938 | 2153.83 | 25.93 | 44.825 | 6.34 | 1.388 | 4.911 | 8526.66 | 2.579 | 97.9 | 78 | 1400 | 22.41 | 5542.3 | 3037.9 | 2939.9 | 4341.1 | 1200 | 0.68122 | 6.298
2024-12-09 | 18:48 | Data | 0 | 32.48 | 29.874 | 200.109 | 7.63 | 187.938 | 2153.83 | 25.91 | 44.825 | 6.34 | 1.384 | 4.885 | 8558.31 | 2.282 | 97.9 | 77.9 | 1400 | 22.41 | 5562.9 | 3043.8 | 2941.5 | 4339.9 | 1200 | 0.68299 | 6.268
2024-12-09 | 18:48 | Data | 0 | 32.258 | 29.901 | 200.063 | 7.63 | 187.847 | 2155.64 | 25.93 | 44.825 | 6.34 | 1.392 | 4.894 | 8571.88 | 2.133 | 97.9 | 77.9 | 1401 | 22.41 | 5571.7 | 3018.6 | 2922.3 | 4315.3 | 1200 | 0.68372 | 6.286
2024-12-09 | 18:48 | Data | 0 | 32.055 | 29.901 | 199.973 | 7.63 | 187.712 | 2160.16 | 25.92 | 44.825 | 6.34 | 1.387 | 4.9 | 8576.4 | 2.309 | 97.9 | 77.9 | 1404 | 22.41 | 5574.7 | 3021.6 | 2913.1 | 4312.9 | 1200 | 0.68478 | 6.288
2024-12-09 | 18:48 | Data | 0 | 32.028 | 29.841 | 200.063 | 7.63 | 187.757 | 2160.16 | 25.92 | 44.915 | 6.33 | 1.385 | 4.918 | 8594.49 | 2.187 | 97.9 | 78 | 1403 | 22.46 | 5586.4 | 3036.2 | 2939.2 | 4336.3 | 1200 | 0.68411 | 6.301
2024-12-09 | 18:48 | Data | 0 | 32.372 | 30.144 | 200.063 | 7.63 | 187.847 | 2159.26 | 25.92 | 44.915 | 6.33 | 1.39 | 4.929 | 8585.45 | 2.268 | 97.9 | 78 | 1404 | 22.41 | 5580.5 | 3042.1 | 2918.7 | 4327.4 | 1200 | 0.68646 | 6.32
2024-12-09 | 18:48 | Data | 0 | 32.426 | 29.982 | 200.063 | 7.63 | 187.757 | 2156.54 | 25.92 | 44.825 | 6.34 | 1.393 | 4.909 | 8580.93 | 2.295 | 97.9 | 77.9 | 1402 | 22.41 | 5577.6 | 3031.2 | 2961.3 | 4351.6 | 1200 | 0.68091 | 6.302
2024-12-09 | 18:48 | Data | 0 | 32.102 | 30.003 | 200.154 | 7.63 | 187.983 | 2157.45 | 25.93 | 44.825 | 6.33 | 1.385 | 4.912 | 8553.79 | 1.992 | 97.9 | 78 | 1402 | 22.41 | 5560 | 3040.5 | 2950.5 | 4343.5 | 1200 | 0.68294 | 6.297
2024-12-09 | 18:48 | Data | 0 | 32.001 | 29.928 | 199.973 | 7.63 | 187.712 | 2154.74 | 25.93 | 44.825 | 6.34 | 1.382 | 4.936 | 8549.27 | 2.181 | 97.9 | 78.1 | 1401 | 22.41 | 5557 | 3033 | 2962.5 | 4346.9 | 1200 | 0.68203 | 6.318
2024-12-09 | 18:48 | Data | 0 | 32.102 | 29.942 | 199.973 | 7.63 | 187.757 | 2158.35 | 25.93 | 44.825 | 6.34 | 1.384 | 4.927 | 8553.79 | 2.025 | 97.9 | 78.1 | 1403 | 22.41 | 5560 | 3021.4 | 2974.8 | 4349.8 | 1200 | 0.67785 | 6.31
2024-12-09 | 18:48 | Data | 0 | 32.048 | 29.955 | 200.244 | 7.63 | 187.802 | 2159.26 | 25.92 | 44.915 | 6.34 | 1.393 | 4.9 | 8567.36 | 2.073 | 97.9 | 77.9 | 1403 | 22.41 | 5568.8 | 3014.9 | 2961.7 | 4339 | 1200 | 0.6783 | 6.294
2024-12-09 | 18:48 | Data | 0 | 31.92 | 30.057 | 200.063 | 7.63 | 187.802 | 2161.06 | 25.92 | 44.825 | 6.33 | 1.392 | 4.909 | 8635.19 | 2.073 | 97.9 | 77.9 | 1405 | 22.41 | 5612.9 | 3040.6 | 2932.2 | 4336.8 | 1200 | 0.68433 | 6.301
2024-12-09 | 18:48 | Data | 0 | 32.372 | 30.171 | 200.063 | 7.63 | 187.847 | 2161.97 | 25.92 | 44.915 | 6.34 | 1.383 | 4.909 | 8635.19 | 2.16 | 97.9 | 78 | 1405 | 22.41 | 5612.9 | 3027.1 | 2939.1 | 4328.2 | 1200 | 0.68266 | 6.292
2024-12-09 | 18:48 | Data | 0 | 32.028 | 29.955 | 199.973 | 7.63 | 187.757 | 2058.03 | 25.93 | 44.825 | 6.33 | 1.378 | 4.92 | 8626.15 | 2.282 | 97.8 | 78.1 | 1337 | 22.41 | 5607 | 3040.5 | 2916 | 4306.7 | 1200 | 0.68747 | 6.298
2024-12-09 | 18:48 | Data | 0 | 32.258 | 29.955 | 200.154 | 7.63 | 187.847 | 2155.64 | 25.93 | 44.825 | 6.33 | 1.394 | 4.921 | 8630.67 | 2.309 | 97.9 | 77.9 | 1402 | 22.41 | 5609.9 | 3022.7 | 2919.9 | 4334.3 | 1200 | 0.68359 | 6.315
2024-12-09 | 18:48 | Data | 0 | 32.264 | 30.124 | 200.154 | 7.63 | 187.757 | 2156.54 | 25.93 | 44.825 | 6.33 | 1.39 | 4.93 | 8630.67 | 2.14 | 97.9 | 78 | 1402 | 22.41 | 5609.9 | 3014.8 | 2943.1 | 4325.6 | 1200 | 0.68059 | 6.32
2024-12-09 | 18:48 | Data | 0 | 32.136 | 29.901 | 200.018 | 7.63 | 187.712 | 2155.64 | 25.93 | 44.825 | 6.33 | 1.396 | 4.908 | 8594.49 | 2.302 | 97.9 | 77.8 | 1401 | 22.41 | 5586.4 | 3035.5 | 2959.3 | 4351.9 | 1200 | 0.68072 | 6.303
2024-12-09 | 18:48 | Data | 0 | 32.352 | 29.982 | 200.018 | 7.63 | 187.847 | 2151.12 | 25.93 | 44.825 | 6.33 | 1.395 | 4.908 | 8621.63 | 2.397 | 97.9 | 77.8 | 1398 | 22.41 | 5604.1 | 3012.3 | 2943.1 | 4326.2 | 1200 | 0.67965 | 6.304
2024-12-09 | 18:48 | Data | 0 | 32.271 | 29.955 | 200.154 | 7.63 | 187.802 | 2155.64 | 25.92 | 44.915 | 6.33 | 1.395 | 4.891 | 8635.19 | 2.194 | 97.9 | 77.8 | 1402 | 22.41 | 5612.9 | 3017.7 | 2926.3 | 4319.4 | 1200 | 0.68038 | 6.286
2024-12-09 | 18:49 | Data | 0 | 32.264 | 29.868 | 200.063 | 7.63 | 187.757 | 2155.64 | 25.92 | 44.644 | 6.34 | 1.395 | 4.899 | 8648.76 | 2.1 | 97.9 | 77.8 | 1401 | 22.32 | 5621.7 | 3018.6 | 2938.1 | 4317.7 | 1200 | 0.68476 | 6.294
2024-12-09 | 18:49 | Data | 0 | 32.649 | 30.212 | 200.335 | 7.62 | 187.983 | 2155.64 | 25.92 | 44.825 | 6.34 | 1.391 | 4.919 | 8648.76 | 2.41 | 97.9 | 77.9 | 1401 | 22.41 | 5621.7 | 3014.8 | 2933.2 | 4323.1 | 1200 | 0.6806 | 6.31
2024-12-09 | 18:49 | Data | 0 | 32.264 | 29.982 | 200.063 | 7.63 | 187.802 | 2155.64 | 25.93 | 44.825 | 6.34 | 1.384 | 4.919 | 8639.71 | 2.262 | 97.9 | 78 | 1402 | 22.41 | 5615.8 | 3027.5 | 2934.9 | 4333.9 | 1200 | 0.68202 | 6.301
2024-12-09 | 18:49 | Data | 0 | 32.264 | 30.043 | 200.199 | 7.63 | 187.802 | 2157.45 | 25.92 | 44.825 | 6.33 | 1.387 | 4.957 | 8626.15 | 2.194 | 97.9 | 78.1 | 1402 | 22.41 | 5607 | 3019.3 | 2910.8 | 4304.1 | 1200.1 | 0.68453 | 6.344
2024-12-09 | 18:49 | Data | 0 | 32.379 | 30.374 | 200.109 | 7.63 | 187.847 | 2158.35 | 25.91 | 44.825 | 6.33 | 1.393 | 4.948 | 8635.19 | 2.106 | 97.9 | 78 | 1403 | 22.41 | 5612.9 | 3034.7 | 2928.8 | 4311.9 | 1200.1 | 0.68576 | 6.34
2024-12-09 | 18:49 | Data | 0 | 32.406 | 30.394 | 200.154 | 7.63 | 187.938 | 2159.26 | 25.92 | 44.825 | 6.34 | 1.388 | 4.921 | 8608.06 | 2.302 | 97.9 | 78 | 1404 | 22.46 | 5595.2 | 3035.4 | 2944.4 | 4323.6 | 1200.1 | 0.68042 | 6.31
2024-12-09 | 18:49 | Data | 0 | 32.433 | 29.868 | 200.018 | 7.63 | 187.847 | 2158.35 | 25.93 | 44.825 | 6.34 | 1.392 | 4.946 | 8594.49 | 2.309 | 97.9 | 78 | 1404 | 22.46 | 5586.4 | 3017.9 | 2942.5 | 4325.2 | 1200.1 | 0.68152 | 6.338
2024-12-09 | 18:49 | Data | 0 | 32.285 | 29.874 | 200.063 | 7.63 | 187.802 | 2155.64 | 25.93 | 44.825 | 6.34 | 1.392 | 4.936 | 8608.06 | 2.424 | 97.9 | 78 | 1401 | 22.46 | 5595.2 | 3024.1 | 2960.1 | 4345.1 | 1200.1 | 0.67768 | 6.327
2024-12-09 | 18:49 | Data | 0 | 32.433 | 30.185 | 200.154 | 7.63 | 187.847 | 2159.26 | 25.93 | 44.825 | 6.33 | 1.392 | 4.928 | 8223.67 | 2.295 | 97.9 | 78 | 1403 | 22.41 | 5345.4 | 3031.6 | 2974.9 | 4359 | 1200.1 | 0.67916 | 6.32
2024-12-09 | 18:49 | Data | 0 | 32.19 | 29.955 | 200.063 | 7.63 | 187.847 | 2159.26 | 25.93 | 44.825 | 6.34 | 1.386 | 4.92 | 8576.4 | 2.106 | 97.9 | 78 | 1403 | 22.41 | 5574.7 | 3026.6 | 2940.4 | 4334.2 | 1200.1 | 0.68015 | 6.307
2024-12-09 | 18:49 | Data | 0 | 32.494 | 30.239 | 200.199 | 7.63 | 187.847 | 2159.26 | 25.93 | 44.825 | 6.33 | 1.383 | 4.928 | 8594.49 | 2.194 | 97.9 | 78.1 | 1404 | 22.41 | 5586.4 | 3023.1 | 2946 | 4331.9 | 1200.1 | 0.68063 | 6.31
2024-12-09 | 18:49 | Data | 0 | 32.028 | 30.381 | 200.063 | 7.62 | 187.983 | 2161.06 | 25.93 | 44.915 | 6.33 | 1.388 | 4.912 | 8567.36 | 2.329 | 97.9 | 78 | 1405 | 22.41 | 5568.8 | 3028 | 2937.5 | 4331.7 | 1200.1 | 0.68304 | 6.301
2024-12-09 | 18:49 | Data | 0 | 32.035 | 29.841 | 200.109 | 7.63 | 187.802 | 2161.06 | 25.92 | 44.825 | 6.34 | 1.388 | 4.904 | 8594.49 | 2.187 | 97.9 | 77.9 | 1405 | 22.41 | 5586.4 | 3035.2 | 2918.4 | 4324.2 | 1200.1 | 0.68572 | 6.293
2024-12-09 | 18:49 | Data | 0 | 32.264 | 30.07 | 200.154 | 7.63 | 187.847 | 2161.06 | 25.92 | 44.734 | 6.34 | 1.393 | 4.928 | 8635.19 | 2.194 | 97.9 | 78 | 1405 | 22.41 | 5612.9 | 3018.8 | 2926.6 | 4311.6 | 1200.1 | 0.68406 | 6.32
2024-12-09 | 18:49 | Data | 0 | 32.258 | 29.955 | 200.109 | 7.63 | 187.802 | 2158.35 | 25.93 | 44.825 | 6.33 | 1.391 | 4.935 | 8635.19 | 2.309 | 97.9 | 78 | 1404 | 22.41 | 5612.9 | 3028.8 | 2961.5 | 4347.5 | 1200.1 | 0.68086 | 6.326
2024-12-09 | 18:49 | Data | 0 | 32.035 | 29.942 | 200.109 | 7.63 | 187.938 | 2158.35 | 25.92 | 44.734 | 6.34 | 1.392 | 4.934 | 8621.63 | 2.133 | 97.9 | 78 | 1403 | 22.41 | 5604.1 | 3015.1 | 2961.6 | 4328.6 | 1200.1 | 0.67755 | 6.326
2024-12-09 | 18:49 | Data | 0 | 32.433 | 29.746 | 200.154 | 7.62 | 187.847 | 2156.54 | 25.92 | 44.825 | 6.34 | 1.392 | 4.899 | 8644.24 | 2.106 | 97.9 | 77.9 | 1402 | 22.41 | 5618.8 | 3034.7 | 2971.1 | 4360.5 | 1200.1 | 0.6787 | 6.291
2024-12-09 | 18:49 | Data | 0 | 32.487 | 29.962 | 200.154 | 7.62 | 187.983 | 2156.54 | 25.93 | 44.825 | 6.34 | 1.382 | 4.929 | 8662.33 | 2.329 | 97.9 | 78.1 | 1402 | 22.41 | 5630.5 | 3005.2 | 2933 | 4318.6 | 1200.1 | 0.67886 | 6.311
2024-12-09 | 18:50 | Data | 0 | 32.514 | 29.969 | 200.199 | 7.63 | 187.938 | 2159.26 | 25.92 | 44.644 | 6.33 | 1.39 | 4.905 | 8680.41 | 2.208 | 97.9 | 77.9 | 1404 | 22.28 | 5642.3 | 3022.3 | 2957.8 | 4341.8 | 1200.1 | 0.68257 | 6.295
2024-12-09 | 18:50 | Data | 0 | 32.258 | 30.178 | 200.289 | 7.62 | 187.938 | 2152.93 | 25.93 | 44.825 | 6.34 | 1.388 | 4.903 | 8671.37 | 2.106 | 97.9 | 77.9 | 1400 | 22.46 | 5636.4 | 3010.1 | 2959.2 | 4337.2 | 1200.1 | 0.67656 | 6.291
2024-12-09 | 18:50 | Data | 0 | 32.028 | 30.124 | 200.063 | 7.63 | 187.938 | 2158.35 | 25.93 | 44.825 | 6.33 | 1.384 | 4.902 | 8689.46 | 2.127 | 97.9 | 78 | 1403 | 22.41 | 5648.1 | 3017 | 2952.9 | 4331.9 | 1200.1 | 0.67931 | 6.286
2024-12-09 | 18:50 | Data | 0 | 32.467 | 30.212 | 200.154 | 7.63 | 188.028 | 2158.35 | 25.93 | 44.825 | 6.34 | 1.389 | 4.914 | 8693.98 | 2.363 | 97.9 | 78 | 1403 | 22.41 | 5651.1 | 3019.2 | 2940.8 | 4330.5 | 1200.1 | 0.68345 | 6.303
2024-12-09 | 18:50 | Data | 0 | 32.588 | 30.185 | 200.244 | 7.63 | 187.983 | 2158.35 | 25.93 | 44.825 | 6.33 | 1.383 | 4.913 | 8693.98 | 2.356 | 97.9 | 78 | 1403 | 22.41 | 5651.1 | 3038.6 | 2921.8 | 4330.3 | 1200.1 | 0.68417 | 6.295
2024-12-09 | 18:50 | Data | 0 | 32.062 | 29.955 | 200.063 | 7.62 | 187.938 | 2155.64 | 25.92 | 45.005 | 6.33 | 1.377 | 4.918 | 8693.98 | 2.079 | 97.9 | 78.1 | 1401 | 22.59 | 5651.1 | 3035.5 | 2920.8 | 4324 | 1200.1 | 0.68578 | 6.294
2024-12-09 | 18:50 | Data | 0 | 32.433 | 29.969 | 200.154 | 7.63 | 187.847 | 2157.45 | 25.93 | 44.915 | 6.34 | 1.38 | 4.892 | 8684.94 | 2.282 | 97.9 | 78 | 1402 | 22.46 | 5645.2 | 3018.5 | 2934.4 | 4327.6 | 1200.1 | 0.68369 | 6.272
2024-12-09 | 18:50 | Data | 0 | 32.629 | 29.982 | 200.289 | 7.62 | 188.028 | 2159.26 | 25.92 | 44.734 | 6.34 | 1.385 | 4.904 | 8662.33 | 2.464 | 97.9 | 78 | 1404 | 22.41 | 5630.5 | 3014 | 2927.2 | 4316.5 | 1200.1 | 0.6815 | 6.289
2024-12-09 | 18:50 | Data | 0 | 32.433 | 30.266 | 200.154 | 7.63 | 187.983 | 2157.45 | 25.92 | 44.825 | 6.34 | 1.388 | 4.934 | 8657.8 | 2.302 | 97.9 | 78 | 1402 | 22.41 | 5627.6 | 3032.9 | 2943.4 | 4339.9 | 1200.1 | 0.68014 | 6.322
2024-12-09 | 18:50 | Data | 0 | 32.372 | 30.009 | 200.109 | 7.63 | 187.847 | 2155.64 | 25.93 | 44.915 | 6.34 | 1.381 | 4.921 | 8662.33 | 2.282 | 97.9 | 78.1 | 1402 | 22.41 | 5630.5 | 3020.7 | 2941.4 | 4329 | 1200.1 | 0.68096 | 6.303
2024-12-09 | 18:50 | Data | 0 | 32.42 | 29.962 | 200.199 | 7.63 | 188.028 | 2156.54 | 25.93 | 44.825 | 6.34 | 1.384 | 4.915 | 8680.41 | 2.147 | 97.9 | 78 | 1401 | 22.41 | 5642.3 | 3027.2 | 2967.2 | 4346.8 | 1200.1 | 0.68067 | 6.299
2024-12-09 | 18:50 | Data | 0 | 31.9 | 29.901 | 200.109 | 7.63 | 187.802 | 2156.54 | 25.92 | 44.825 | 6.34 | 1.386 | 4.915 | 8671.37 | 2.073 | 97.9 | 78 | 1402 | 22.41 | 5636.4 | 3041.6 | 2959.8 | 4356.1 | 1200.1 | 0.68285 | 6.301
2024-12-09 | 18:50 | Data | 0 | 32.177 | 29.733 | 200.199 | 7.63 | 187.938 | 2156.54 | 25.93 | 44.825 | 6.33 | 1.383 | 4.901 | 8680.41 | 2.336 | 97.9 | 78 | 1401 | 22.41 | 5642.3 | 3024.1 | 2952.7 | 4335.1 | 1200.1 | 0.68109 | 6.283
2024-12-09 | 18:50 | Data | 0 | 32.474 | 30.347 | 200.154 | 7.63 | 187.938 | 2156.54 | 25.93 | 44.825 | 6.33 | 1.379 | 4.946 | 8693.98 | 2.214 | 97.9 | 78.2 | 1401 | 22.41 | 5651.1 | 3027.7 | 2942.8 | 4332.5 | 1200.1 | 0.68202 | 6.325
2024-12-09 | 18:50 | Data | 0 | 32.271 | 29.982 | 200.109 | 7.63 | 187.847 | 2152.93 | 25.93 | 44.915 | 6.34 | 1.377 | 4.916 | 8680.41 | 2.255 | 97.9 | 78.1 | 1400 | 22.46 | 5642.3 | 3040.2 | 2954.6 | 4345 | 1200.1 | 0.68312 | 6.293
2024-12-09 | 18:50 | Data | 0 | 32.237 | 29.955 | 200.109 | 7.62 | 187.802 | 2155.64 | 25.92 | 44.825 | 6.34 | 1.384 | 4.913 | 8657.8 | 2.302 | 97.9 | 78 | 1401 | 22.41 | 5627.6 | 3030.3 | 2951.7 | 4342.2 | 1200.1 | 0.68227 | 6.298
2024-12-09 | 18:50 | Data | 0 | 32.291 | 30.077 | 200.063 | 7.63 | 187.983 | 2158.35 | 25.92 | 44.825 | 6.34 | 1.388 | 4.926 | 8662.33 | 2.302 | 97.9 | 78 | 1403 | 22.41 | 5630.5 | 3036.2 | 2944.8 | 4339.7 | 1200.1 | 0.68201 | 6.313
2024-12-09 | 18:50 | Data | 0 | 32.602 | 30.097 | 200.289 | 7.63 | 187.983 | 2161.97 | 25.92 | 44.734 | 6.34 | 1.394 | 4.917 | 8657.8 | 2.451 | 97.9 | 77.9 | 1405 | 22.41 | 5627.6 | 3026 | 2920.1 | 4319.2 | 1200.1 | 0.68423 | 6.31
2024-12-09 | 18:51 | Data | 0 | 32.264 | 29.955 | 200.199 | 7.63 | 187.757 | 2158.35 | 25.93 | 44.825 | 6.34 | 1.391 | 4.91 | 8680.41 | 2.309 | 97.9 | 77.9 | 1403 | 22.41 | 5642.3 | 3038.8 | 2925.3 | 4326.3 | 1200.1 | 0.68488 | 6.301
2024-12-09 | 18:51 | Data | 0 | 32.042 | 29.942 | 200.109 | 7.63 | 187.712 | 2159.26 | 25.92 | 44.825 | 6.33 | 1.395 | 4.937 | 8635.19 | 2.187 | 97.9 | 78 | 1403 | 22.41 | 5612.9 | 3034.1 | 2918.6 | 4322.8 | 1200.1 | 0.6853 | 6.331
2024-12-09 | 18:51 | Data | 0 | 31.988 | 29.955 | 200.063 | 7.63 | 187.757 | 2151.12 | 25.92 | 44.915 | 6.34 | 1.391 | 4.911 | 8621.63 | 2.241 | 97.9 | 77.9 | 1398 | 22.46 | 5604.1 | 3028.4 | 2925.2 | 4325.4 | 1200.2 | 0.68296 | 6.302
2024-12-09 | 18:51 | Data | 0 | 32.048 | 29.996 | 200.109 | 7.63 | 187.847 | 2156.54 | 25.92 | 44.825 | 6.34 | 1.379 | 4.903 | 8621.63 | 1.992 | 97.9 | 78 | 1402 | 22.37 | 5604.1 | 3013.9 | 2937.6 | 4321 | 1200.2 | 0.68179 | 6.282
2024-12-09 | 18:51 | Data | 0 | 32.372 | 29.989 | 200.199 | 7.63 | 187.983 | 2156.54 | 25.93 | 44.825 | 6.34 | 1.384 | 4.907 | 8626.15 | 2.221 | 97.9 | 78 | 1402 | 22.46 | 5607 | 3040.5 | 2955 | 4351.8 | 1200.2 | 0.68256 | 6.291
2024-12-09 | 18:51 | Data | 0 | 32.703 | 30.259 | 200.289 | 7.62 | 188.028 | 2159.26 | 25.93 | 44.644 | 6.34 | 1.386 | 4.907 | 8680.41 | 2.214 | 97.9 | 78 | 1404 | 22.32 | 5642.3 | 3016.2 | 2927.7 | 4327.6 | 1200.2 | 0.68087 | 6.293
2024-12-09 | 18:51 | Data | 0 | 32.372 | 29.955 | 200.154 | 7.63 | 188.028 | 2158.35 | 25.93 | 44.734 | 6.33 | 1.397 | 4.929 | 8689.46 | 2.214 | 97.9 | 77.9 | 1403 | 22.37 | 5648.1 | 3024.4 | 2959.6 | 4342.7 | 1200.2 | 0.68065 | 6.327
2024-12-09 | 18:51 | Data | 0 | 32.062 | 30.286 | 200.244 | 7.62 | 187.983 | 2158.35 | 25.93 | 44.825 | 6.33 | 1.396 | 4.926 | 8689.46 | 2.194 | 97.9 | 77.9 | 1403 | 22.41 | 5648.1 | 3043.7 | 2971.8 | 4366.5 | 1200.2 | 0.68048 | 6.322
2024-12-09 | 18:51 | Data | 0 | 32.089 | 29.982 | 200.154 | 7.63 | 187.983 | 2158.35 | 25.93 | 44.734 | 6.34 | 1.387 | 4.911 | 8684.94 | 2.255 | 97.9 | 78 | 1402 | 22.41 | 5645.2 | 3025.6 | 2940.4 | 4329.6 | 1200.2 | 0.68119 | 6.299
2024-12-09 | 18:51 | Data | 0 | 32.487 | 30.185 | 200.244 | 7.63 | 187.983 | 2178.24 | 25.92 | 44.825 | 6.34 | 1.382 | 4.92 | 8666.85 | 2.086 | 97.9 | 78.1 | 1420 | 22.41 | 5633.5 | 3011 | 2949.8 | 4326.8 | 1200.2 | 0.68072 | 6.301
2024-12-09 | 18:51 | Data | 0 | 32.102 | 29.955 | 200.244 | 7.63 | 187.938 | 2206.25 | 25.93 | 44.825 | 6.33 | 1.387 | 4.903 | 8680.41 | 2.073 | 98 | 78 | 1433 | 22.46 | 5642.3 | 3047.5 | 2953 | 4353.4 | 1200.2 | 0.67977 | 6.29
2024-12-09 | 18:51 | Data | 0 | 32.244 | 30.009 | 200.289 | 7.63 | 187.802 | 2207.16 | 25.92 | 44.825 | 6.33 | 1.38 | 4.917 | 8693.98 | 2.113 | 98 | 78.1 | 1435 | 22.41 | 5651.1 | 3037.7 | 2916.5 | 4320.7 | 1200.2 | 0.68599 | 6.297
2024-12-09 | 18:51 | Data | 0 | 32.352 | 29.982 | 200.154 | 7.63 | 187.712 | 2208.06 | 25.92 | 44.734 | 6.34 | 1.382 | 4.911 | 8666.85 | 2.464 | 98 | 78 | 1436 | 22.41 | 5633.5 | 3049.3 | 2943.1 | 4345.6 | 1200.2 | 0.68636 | 6.293
2024-12-09 | 18:51 | Data | 0 | 32.062 | 29.955 | 200.199 | 7.62 | 187.847 | 2203.54 | 25.92 | 44.734 | 6.34 | 1.386 | 4.903 | 8693.98 | 2.079 | 98 | 78 | 1432 | 22.37 | 5651.1 | 3015 | 2902.2 | 4297.8 | 1200.2 | 0.68507 | 6.29
2024-12-09 | 18:51 | Data | 0 | 32.264 | 29.962 | 200.109 | 7.62 | 187.802 | 2159.26 | 25.93 | 44.825 | 6.34 | 1.402 | 4.927 | 8689.46 | 2.302 | 97.9 | 77.8 | 1403 | 22.41 | 5648.1 | 1952.1 | 2399.4 | 3104.2 | 1200.2 | 0.62808 | 6.329
2024-12-09 | 18:51 | Data | 0 | 32.629 | 30.232 | 200.244 | 7.62 | 188.073 | 2159.26 | 25.92 | 44.825 | 6.33 | 1.393 | 4.94 | 8693.98 | 2.424 | 97.9 | 78 | 1403 | 22.41 | 5651.1 | 1955.6 | 2402.8 | 3107.9 | 1200.2 | 0.62425 | 6.333
2024-12-09 | 18:51 | Data | 0 | 32.136 | 29.739 | 200.109 | 7.63 | 187.938 | 2158.35 | 25.92 | 44.825 | 6.34 | 1.396 | 4.928 | 8693.98 | 2.417 | 97.9 | 77.9 | 1403 | 22.41 | 5651.1 | 1942.2 | 2381.1 | 3083.8 | 1200.2 | 0.62733 | 6.323
2024-12-09 | 18:52 | Data | 0 | 31.846 | 29.928 | 200.154 | 7.63 | 187.847 | 2155.64 | 25.93 | 42.658 | 6.34 | 1.387 | 4.912 | 8680.41 | 2.025 | 98 | 78 | 1402 | 21.33 | 5642.3 | 1940.2 | 2380.6 | 3083.3 | 1200.2 | 0.62635 | 6.301
2024-12-09 | 18:52 | Data | 0 | 32.588 | 29.753 | 200.109 | 7.63 | 187.938 | 2153.83 | 25.93 | 42.297 | 6.34 | 1.381 | 4.875 | 8680.41 | 2.39 | 98 | 77.9 | 1399 | 21.15 | 5642.3 | 1934.8 | 2412.2 | 3102.8 | 1200.2 | 0.62126 | 6.257
2024-12-09 | 18:52 | Data | 0 | 32.156 | 29.955 | 200.154 | 7.63 | 187.802 | 2149.31 | 25.92 | 45.727 | 6.34 | 1.385 | 4.899 | 8689.46 | 2.106 | 97.9 | 77.9 | 1397 | 22.86 | 5648.1 | 1937 | 2402.6 | 3097.4 | 1200.2 | 0.62459 | 6.285
2024-12-09 | 18:52 | Data | 0 | 32.487 | 29.8 | 200.154 | 7.63 | 187.938 | 2145.7 | 25.91 | 45.727 | 6.33 | 1.388 | 4.898 | 8680.41 | 2.329 | 97.9 | 77.9 | 1394 | 22.86 | 5642.3 | 1934.4 | 2415 | 3104.8 | 1200.2 | 0.62038 | 6.285
2024-12-09 | 18:52 | Data | 0 | 32.237 | 29.915 | 200.154 | 7.63 | 187.802 | 2152.02 | 25.92 | 45.547 | 6.34 | 1.382 | 4.925 | 8662.33 | 2.464 | 97.9 | 78.1 | 1398 | 22.77 | 5630.5 | 1942.6 | 2392.8 | 3092.9 | 1200.2 | 0.62321 | 6.307
2024-12-09 | 18:52 | Data | 0 | 32.042 | 29.955 | 200.154 | 7.63 | 187.983 | 2151.12 | 25.91 | 45.818 | 6.34 | 1.381 | 4.932 | 8680.41 | 2.073 | 97.9 | 78.1 | 1398 | 22.91 | 5642.3 | 1956.7 | 2365.9 | 3080.1 | 1200.2 | 0.63287 | 6.313
2024-12-09 | 18:52 | Data | 0 | 32.487 | 30.09 | 200.199 | 7.63 | 188.028 | 2147.51 | 25.92 | 45.908 | 6.33 | 1.389 | 4.901 | 8671.37 | 2.268 | 97.9 | 77.9 | 1396 | 23 | 5636.4 | 1948.7 | 2384.9 | 3089.8 | 1200.2 | 0.62855 | 6.291
2024-12-09 | 18:52 | Data | 0 | 31.954 | 29.76 | 200.109 | 7.62 | 187.983 | 2146.6 | 25.91 | 45.727 | 6.33 | 1.385 | 4.91 | 8680.41 | 2.059 | 97.9 | 78 | 1395 | 22.86 | 5642.3 | 1928.7 | 2370.3 | 3068.6 | 1200.2 | 0.62734 | 6.293
2024-12-09 | 18:52 | Data | 0 | 32.237 | 29.969 | 200.109 | 7.63 | 187.847 | 2145.7 | 25.9 | 45.727 | 6.33 | 1.385 | 4.914 | 8693.98 | 2.289 | 97.9 | 78 | 1395 | 22.86 | 5651.1 | 1955.1 | 2370 | 3081 | 1200.2 | 0.63233 | 6.299
2024-12-09 | 18:52 | Data | 0 | 31.819 | 29.901 | 200.199 | 7.63 | 187.938 | 2143.89 | 25.89 | 45.637 | 6.33 | 1.377 | 4.92 | 8693.98 | 2.194 | 97.9 | 78.1 | 1394 | 22.82 | 5651.1 | 1939.2 | 2362.6 | 3065.1 | 1200.2 | 0.63299 | 6.297
2024-12-09 | 18:52 | Data | 0 | 32.129 | 29.935 | 199.973 | 7.63 | 187.757 | 2143.89 | 25.91 | 45.727 | 6.34 | 1.388 | 4.911 | 8698.5 | 2.147 | 97.9 | 78 | 1395 | 22.86 | 5654 | 1934.8 | 2365.7 | 3067 | 1200.2 | 0.62856 | 6.3
2024-12-09 | 18:52 | Data | 0 | 32.325 | 29.955 | 200.244 | 7.63 | 187.847 | 2147.51 | 25.9 | 45.457 | 6.33 | 1.377 | 4.946 | 8680.41 | 2.1 | 97.9 | 78.2 | 1395 | 22.77 | 5642.3 | 1947.8 | 2383.6 | 3090.4 | 1200.2 | 0.62528 | 6.322
2024-12-09 | 18:52 | Data | 0 | 32.278 | 29.955 | 200.018 | 7.63 | 187.847 | 2148.41 | 25.9 | 45.457 | 6.33 | 1.384 | 4.912 | 8671.37 | 2.079 | 97.9 | 78 | 1396 | 22.77 | 5636.4 | 1951 | 2401.2 | 3105 | 1200.2 | 0.6262 | 6.297
2024-12-09 | 18:52 | Data | 0 | 32.028 | 29.942 | 199.973 | 7.63 | 187.802 | 2151.12 | 25.92 | 45.366 | 6.33 | 1.384 | 4.931 | 8662.33 | 2.214 | 97.9 | 78.1 | 1398 | 22.68 | 5630.5 | 1956.9 | 2403.9 | 3109 | 1200.2 | 0.62579 | 6.314
2024-12-09 | 18:52 | Data | 0 | 32.258 | 30.178 | 200.154 | 7.62 | 188.028 | 2151.12 | 25.91 | 45.547 | 6.34 | 1.385 | 4.921 | 8657.8 | 2.295 | 97.9 | 78 | 1397 | 22.77 | 5627.6 | 1947.2 | 2414 | 3112.3 | 1200.2 | 0.62381 | 6.305
2024-12-09 | 18:52 | Data | 0 | 32.237 | 29.841 | 200.063 | 7.63 | 187.847 | 2149.31 | 25.91 | 45.457 | 6.33 | 1.391 | 4.922 | 8662.33 | 2.451 | 97.9 | 78 | 1397 | 22.73 | 5630.5 | 1940.7 | 2393.7 | 3091.3 | 1200.2 | 0.62555 | 6.313
2024-12-09 | 18:52 | Data | 0 | 32.703 | 29.807 | 200.063 | 7.63 | 187.847 | 2151.12 | 25.89 | 45.186 | 6.33 | 1.384 | 4.87 | 8662.33 | 2.464 | 97.9 | 77.9 | 1398 | 22.59 | 5630.5 | 1945.6 | 2400.9 | 3102.5 | 1200.2 | 0.62467 | 6.253
2024-12-09 | 18:52 | Data | 0 | 32.366 | 29.982 | 200.063 | 7.62 | 187.938 | 2151.12 | 25.91 | 45.186 | 6.33 | 1.381 | 4.901 | 8662.33 | 2.397 | 97.9 | 78 | 1398 | 22.59 | 5630.5 | 1941.7 | 2398 | 3095.8 | 1200.2 | 0.62469 | 6.282
2024-12-09 | 18:53 | Data | 0 | 32.143 | 29.955 | 200.109 | 7.63 | 187.847 | 2151.12 | 25.91 | 45.186 | 6.34 | 1.387 | 4.877 | 8671.37 | 2.073 | 97.9 | 77.8 | 1398 | 22.5 | 5636.4 | 1927.4 | 2403.5 | 3098 | 1200.2 | 0.61956 | 6.265
2024-12-09 | 18:53 | Data | 0 | 32.028 | 29.942 | 200.018 | 7.62 | 187.802 | 2155.64 | 25.92 | 45.186 | 6.33 | 1.396 | 4.888 | 8662.33 | 2.275 | 97.9 | 77.8 | 1401 | 22.59 | 5630.5 | 1939.6 | 2400.8 | 3095.6 | 1200.2 | 0.62404 | 6.284
2024-12-09 | 18:53 | Data | 0 | 32.372 | 29.868 | 200.109 | 7.62 | 187.938 | 2151.12 | 25.91 | 45.186 | 6.33 | 1.382 | 4.894 | 8666.85 | 2.255 | 97.9 | 78 | 1398 | 22.5 | 5633.5 | 1938.5 | 2402.9 | 3097.2 | 1200.2 | 0.62393 | 6.276
2024-12-09 | 18:53 | Data | 0 | 32.359 | 29.955 | 200.109 | 7.63 | 187.938 | 2155.64 | 25.89 | 45.005 | 6.33 | 1.385 | 4.894 | 8662.33 | 2.194 | 97.9 | 77.9 | 1401 | 22.59 | 5630.5 | 1940.9 | 2412.2 | 3107.6 | 1200.2 | 0.62602 | 6.279
2024-12-09 | 18:53 | Data | 0 | 32.285 | 29.753 | 200.109 | 7.63 | 187.802 | 2152.93 | 25.89 | 44.915 | 6.34 | 1.395 | 4.891 | 8657.8 | 2.309 | 97.9 | 77.8 | 1400 | 22.41 | 5627.6 | 1951.5 | 2420 | 3118.9 | 1200.2 | 0.62342 | 6.284
2024-12-09 | 18:53 | Data | 0 | 32.379 | 29.962 | 200.109 | 7.63 | 188.028 | 2152.93 | 25.89 | 44.825 | 6.34 | 1.39 | 4.911 | 8648.76 | 2.295 | 97.9 | 77.9 | 1400 | 22.41 | 5621.7 | 1937.5 | 2397.3 | 3093.1 | 1200.2 | 0.62465 | 6.301
2024-12-09 | 18:53 | Data | 0 | 32.48 | 29.874 | 200.289 | 7.63 | 187.938 | 2158.35 | 25.89 | 44.825 | 6.34 | 1.386 | 4.926 | 8666.85 | 2.289 | 97.9 | 78 | 1402 | 22.41 | 5633.5 | 1946.7 | 2410 | 3109.5 | 1200.2 | 0.62388 | 6.312
2024-12-09 | 18:53 | Data | 0 | 31.947 | 29.726 | 200.109 | 7.63 | 187.847 | 2153.83 | 25.89 | 44.825 | 6.33 | 1.384 | 4.935 | 8173.92 | 2.086 | 97.9 | 78.1 | 1400 | 22.41 | 5313.1 | 1963.4 | 2386.6 | 3101.5 | 1200.2 | 0.62999 | 6.318
2024-12-09 | 18:53 | Data | 0 | 31.866 | 29.726 | 199.973 | 7.63 | 187.712 | 2157.45 | 25.89 | 44.825 | 6.33 | 1.377 | 4.899 | 8562.84 | 2.086 | 97.9 | 78.1 | 1402 | 22.41 | 5565.8 | 1943.3 | 2402.1 | 3100.7 | 1200.2 | 0.62656 | 6.276
2024-12-09 | 18:53 | Data | 0 | 32.089 | 29.645 | 199.973 | 7.63 | 187.802 | 2156.54 | 25.91 | 44.825 | 6.33 | 1.381 | 4.886 | 8580.93 | 2.349 | 97.9 | 78 | 1402 | 22.41 | 5577.6 | 1931.9 | 2404.5 | 3096.8 | 1200.2 | 0.62135 | 6.266
2024-12-09 | 18:53 | Data | 0 | 32.15 | 29.841 | 200.063 | 7.63 | 187.847 | 2157.45 | 25.89 | 44.825 | 6.33 | 1.388 | 4.919 | 8562.84 | 2.248 | 97.9 | 78 | 1403 | 22.41 | 5565.8 | 1957.9 | 2409.9 | 3115.3 | 1200.2 | 0.62633 | 6.307
2024-12-09 | 18:53 | Data | 0 | 32.062 | 29.787 | 200.109 | 7.62 | 187.847 | 2158.35 | 25.89 | 44.915 | 6.34 | 1.39 | 4.934 | 8680.41 | 2.093 | 97.9 | 78 | 1404 | 22.41 | 5642.3 | 1950.2 | 2398.4 | 3101 | 1200.2 | 0.62656 | 6.324
2024-12-09 | 18:53 | Data | 0 | 31.873 | 29.874 | 199.973 | 7.62 | 187.802 | 2158.35 | 25.89 | 44.825 | 6.34 | 1.385 | 4.881 | 8662.33 | 2.012 | 97.9 | 77.9 | 1403 | 22.41 | 5630.5 | 1945.4 | 2399.8 | 3100 | 1200.2 | 0.62569 | 6.265
2024-12-09 | 18:53 | Data | 0 | 32.028 | 29.949 | 199.973 | 7.62 | 187.847 | 2156.54 | 25.9 | 44.915 | 6.33 | 1.388 | 4.866 | 8657.8 | 2.086 | 97.9 | 77.8 | 1402 | 22.41 | 5627.6 | 1938.1 | 2377.1 | 3080.1 | 1200.2 | 0.62951 | 6.256
2024-12-09 | 18:53 | Data | 0 | 32.028 | 29.739 | 200.063 | 7.63 | 187.712 | 2155.64 | 25.89 | 44.915 | 6.33 | 1.39 | 4.91 | 8644.24 | 2.289 | 97.9 | 77.9 | 1401 | 22.46 | 5618.8 | 1952 | 2390.4 | 3096.7 | 1200.2 | 0.62833 | 6.3
2024-12-09 | 18:53 | Data | 0 | 31.819 | 29.942 | 200.063 | 7.63 | 187.847 | 2156.54 | 25.89 | 44.915 | 6.33 | 1.393 | 4.908 | 8608.06 | 2.019 | 97.9 | 77.9 | 1401 | 22.46 | 5595.2 | 1949.5 | 2397.1 | 3101.7 | 1200.2 | 0.62653 | 6.3
2024-12-09 | 18:53 | Data | 0 | 32.352 | 30.28 | 200.063 | 7.62 | 187.847 | 2153.83 | 25.89 | 44.915 | 6.33 | 1.387 | 4.925 | 8608.06 | 2.255 | 97.9 | 78 | 1400 | 22.41 | 5595.2 | 1953.3 | 2380.1 | 3089 | 1200.3 | 0.63008 | 6.313
2024-12-09 | 18:54 | Data | 0 | 32.015 | 29.949 | 200.063 | 7.63 | 187.757 | 2153.83 | 25.89 | 44.825 | 6.33 | 1.389 | 4.901 | 8612.58 | 2.309 | 97.9 | 77.9 | 1400 | 22.41 | 5598.2 | 1951.2 | 2371.7 | 3082.5 | 1200.3 | 0.63074 | 6.29
2024-12-09 | 18:54 | Data | 0 | 32.055 | 29.739 | 200.063 | 7.62 | 187.712 | 2155.64 | 25.89 | 44.915 | 6.34 | 1.397 | 4.895 | 8599.01 | 2.248 | 97.9 | 77.8 | 1401 | 22.46 | 5589.4 | 1945.9 | 2381.2 | 3086.9 | 1200.3 | 0.62763 | 6.291
2024-12-09 | 18:54 | Data | 0 | 32.028 | 29.901 | 200.018 | 7.63 | 187.802 | 2156.54 | 25.9 | 44.825 | 6.33 | 1.394 | 4.913 | 8599.01 | 2.302 | 97.9 | 77.9 | 1401 | 22.41 | 5589.4 | 1948.8 | 2396.1 | 3099.5 | 1200.3 | 0.62666 | 6.307
2024-12-09 | 18:54 | Data | 0 | 32.028 | 29.78 | 199.928 | 7.63 | 187.757 | 2158.35 | 25.9 | 44.825 | 6.33 | 1.386 | 4.902 | 8594.49 | 2.086 | 97.9 | 78 | 1403 | 22.41 | 5586.4 | 1948.6 | 2382.5 | 3088.6 | 1200.3 | 0.62865 | 6.289
2024-12-09 | 18:54 | Data | 0 | 31.974 | 29.726 | 199.837 | 7.63 | 187.757 | 2159.26 | 25.9 | 44.825 | 6.34 | 1.377 | 4.898 | 8594.49 | 2.289 | 97.9 | 78.1 | 1403 | 22.41 | 5586.4 | 1957.6 | 2371.5 | 3085.7 | 1200.3 | 0.63263 | 6.274
2024-12-09 | 18:54 | Data | 0 | 32.028 | 29.733 | 200.063 | 7.62 | 187.757 | 2271.33 | 25.89 | 44.825 | 6.34 | 1.388 | 4.883 | 8594.49 | 2.295 | 98 | 77.9 | 1478 | 22.41 | 5586.4 | 1940.4 | 2408.2 | 3107.2 | 1200.3 | 0.62567 | 6.272
2024-12-09 | 18:54 | Data | 0 | 32.015 | 29.942 | 199.928 | 7.63 | 187.757 | 2155.64 | 25.89 | 44.915 | 6.33 | 1.396 | 4.888 | 8775.38 | 2.181 | 97.9 | 77.8 | 1401 | 22.41 | 5704 | 1948.7 | 2387.9 | 3092.5 | 1200.3 | 0.62795 | 6.283
2024-12-09 | 18:54 | Data | 0 | 32.386 | 29.746 | 200.018 | 7.63 | 187.938 | 2156.54 | 25.89 | 44.915 | 6.34 | 1.393 | 4.92 | 8784.42 | 2.154 | 97.9 | 77.9 | 1402 | 22.41 | 5709.9 | 1945.8 | 2382.1 | 3087.2 | 1200.3 | 0.62807 | 6.313
2024-12-09 | 18:54 | Data | 0 | 32.318 | 30.185 | 200.199 | 7.62 | 187.983 | 2156.54 | 25.91 | 44.554 | 6.34 | 1.386 | 4.919 | 8775.38 | 2.39 | 97.9 | 78 | 1402 | 22.28 | 5704 | 1939.3 | 2384.1 | 3087.7 | 1200.3 | 0.6273 | 6.304
2024-12-09 | 18:54 | Data | 0 | 32.102 | 29.928 | 200.063 | 7.63 | 187.712 | 2159.26 | 25.9 | 44.554 | 6.34 | 1.379 | 4.916 | 8784.42 | 2.174 | 97.9 | 78.1 | 1404 | 22.23 | 5709.9 | 3157.1 | 3005 | 4785.2 | 1200.3 | 0.66741 | 6.295
2024-12-09 | 18:54 | Data | 0 | 32.035 | 29.955 | 200.063 | 7.62 | 187.802 | 2158.35 | 25.91 | 44.554 | 6.33 | 1.389 | 4.894 | 8580.93 | 2.194 | 97.9 | 77.9 | 1403 | 22.32 | 5577.6 | 3041.7 | 2916.3 | 4330.1 | 1200.3 | 0.68357 | 6.282
2024-12-09 | 18:54 | Data | 0 | 32.035 | 30.151 | 200.109 | 7.62 | 187.757 | 2152.02 | 25.89 | 44.644 | 6.34 | 1.383 | 4.877 | 8576.4 | 2.235 | 97.9 | 77.9 | 1399 | 22.28 | 5574.7 | 3051 | 2928.5 | 4342 | 1200.3 | 0.68645 | 6.259
2024-12-09 | 18:54 | Data | 0 | 32.042 | 29.901 | 199.973 | 7.62 | 187.757 | 2155.64 | 25.91 | 44.464 | 6.33 | 1.371 | 4.893 | 8567.36 | 2.127 | 97.9 | 78.1 | 1401 | 22.23 | 5568.8 | 3044.1 | 2948.3 | 4348.8 | 1200.3 | 0.68401 | 6.264
2024-12-09 | 18:54 | Data | 0 | 32.028 | 29.726 | 200.063 | 7.62 | 187.757 | 2155.64 | 25.89 | 44.554 | 6.34 | 1.377 | 4.873 | 8580.93 | 2.302 | 97.9 | 78 | 1402 | 22.28 | 5577.6 | 3034.6 | 2954.7 | 4345 | 1200.3 | 0.68298 | 6.25
2024-12-09 | 18:54 | Data | 0 | 32.028 | 29.733 | 199.928 | 7.62 | 187.712 | 2153.83 | 25.91 | 44.554 | 6.33 | 1.389 | 4.892 | 8626.15 | 2.282 | 97.9 | 77.9 | 1400 | 22.37 | 5607 | 3034.9 | 2952.7 | 4349.9 | 1200.3 | 0.6816 | 6.281
2024-12-09 | 18:54 | Data | 0 | 32.062 | 29.753 | 200.109 | 7.62 | 187.802 | 2153.83 | 25.89 | 44.644 | 6.34 | 1.388 | 4.91 | 8635.19 | 2.019 | 97.9 | 78 | 1400 | 22.32 | 5612.9 | 3033.8 | 2947.3 | 4335.3 | 1200.3 | 0.68212 | 6.297
2024-12-09 | 18:54 | Data | 0 | 32.15 | 30.165 | 200.109 | 7.63 | 187.757 | 2152.93 | 25.89 | 44.554 | 6.34 | 1.389 | 4.896 | 8648.76 | 2.194 | 97.9 | 77.9 | 1400 | 22.32 | 5621.7 | 3034.3 | 2954.8 | 4349.5 | 1200.3 | 0.68076 | 6.285
2024-12-09 | 18:54 | Data | 0 | 31.819 | 29.733 | 199.882 | 7.63 | 187.802 | 2152.93 | 25.89 | 44.464 | 6.34 | 1.393 | 4.926 | 8657.8 | 2.073 | 97.9 | 78 | 1400 | 22.28 | 5627.6 | 3034.6 | 2952.8 | 4348.8 | 1200.3 | 0.68122 | 6.318
2024-12-09 | 18:55 | Data | 0 | 31.812 | 29.928 | 200.063 | 7.63 | 187.757 | 2152.02 | 25.89 | 44.644 | 6.34 | 1.387 | 4.913 | 8689.46 | 2.201 | 97.9 | 78 | 1399 | 22.28 | 5648.1 | 3036.2 | 2969.4 | 4360 | 1200.3 | 0.67925 | 6.301
2024-12-09 | 18:55 | Data | 0 | 32.129 | 29.955 | 200.244 | 7.63 | 187.847 | 2152.93 | 25.9 | 44.554 | 6.33 | 1.386 | 4.894 | 8689.46 | 2.113 | 97.9 | 77.9 | 1399 | 22.28 | 5648.1 | 3034.5 | 2933.1 | 4333.1 | 1200.3 | 0.68469 | 6.281
2024-12-09 | 18:55 | Data | 0 | 32.089 | 29.51 | 199.973 | 7.63 | 187.712 | 2153.83 | 25.89 | 44.825 | 6.34 | 1.383 | 4.901 | 8689.46 | 2.174 | 97.9 | 78 | 1400 | 22.41 | 5648.1 | 3032.5 | 2943.3 | 4337 | 1200.3 | 0.68307 | 6.284
2024-12-09 | 18:55 | Data | 0 | 32.372 | 29.868 | 200.018 | 7.63 | 187.757 | 2153.83 | 25.89 | 44.825 | 6.34 | 1.378 | 4.904 | 8703.03 | 2.309 | 97.9 | 78.1 | 1401 | 22.41 | 5657 | 3044.6 | 2957.6 | 4354 | 1200.3 | 0.68369 | 6.283
2024-12-09 | 18:55 | Data | 0 | 32.015 | 29.726 | 199.973 | 7.63 | 187.621 | 2153.83 | 25.89 | 44.825 | 6.33 | 1.375 | 4.9 | 8662.33 | 2.316 | 97.9 | 78.1 | 1400 | 22.46 | 5630.5 | 3053.7 | 2891.6 | 4317.9 | 1200.3 | 0.69072 | 6.274
2024-12-09 | 18:55 | Data | 0 | 31.812 | 29.841 | 200.063 | 7.63 | 187.757 | 2153.83 | 25.9 | 44.825 | 6.33 | 1.39 | 4.905 | 8671.37 | 2.268 | 97.9 | 77.9 | 1400 | 22.41 | 5636.4 | 3032.3 | 2945.6 | 4338.9 | 1200.3 | 0.68282 | 6.294
2024-12-09 | 18:55 | Data | 0 | 32.028 | 29.523 | 200.109 | 7.63 | 187.712 | 2153.83 | 25.89 | 44.825 | 6.33 | 1.382 | 4.91 | 8680.41 | 2.41 | 97.9 | 78 | 1399 | 22.37 | 5642.3 | 3045 | 2948.7 | 4355.2 | 1200.3 | 0.68339 | 6.293
2024-12-09 | 18:55 | Data | 0 | 32.352 | 30.07 | 200.063 | 7.63 | 187.938 | 2152.93 | 25.89 | 44.825 | 6.33 | 1.383 | 4.912 | 8666.85 | 2.106 | 97.9 | 78 | 1400 | 22.41 | 5633.5 | 3034.4 | 2946 | 4342.2 | 1200.3 | 0.68274 | 6.295
2024-12-09 | 18:55 | Data | 0 | 32.17 | 29.746 | 199.973 | 7.63 | 187.802 | 2152.93 | 25.89 | 44.644 | 6.34 | 1.385 | 4.881 | 8680.41 | 2.194 | 97.9 | 77.9 | 1400 | 22.28 | 5642.3 | 3030.7 | 2996.8 | 4372.4 | 1200.3 | 0.6764 | 6.264
2024-12-09 | 18:55 | Data | 0 | 32.001 | 30.178 | 200.109 | 7.63 | 187.938 | 2153.83 | 25.89 | 44.825 | 6.34 | 1.399 | 4.882 | 8680.41 | 2.322 | 97.9 | 77.7 | 1400 | 22.37 | 5642.3 | 3031.4 | 2978.6 | 4362.7 | 1200.3 | 0.67805 | 6.28
2024-12-09 | 18:55 | Data | 0 | 32.237 | 30.063 | 200.109 | 7.63 | 187.847 | 2153.83 | 25.89 | 44.915 | 6.34 | 1.393 | 4.899 | 8666.85 | 2.1 | 97.9 | 77.9 | 1400 | 22.46 | 5633.5 | 3025.1 | 2978.5 | 4357.7 | 1200.3 | 0.67794 | 6.291
2024-12-09 | 18:55 | Data | 0 | 32.028 | 29.901 | 200.018 | 7.63 | 187.757 | 2151.12 | 25.89 | 44.915 | 6.34 | 1.39 | 4.894 | 8671.37 | 2.187 | 97.9 | 77.9 | 1398 | 22.41 | 5636.4 | 3016.9 | 2951.5 | 4332.2 | 1200.3 | 0.67949 | 6.284
2024-12-09 | 18:55 | Data | 0 | 32.042 | 29.739 | 200.018 | 7.63 | 187.802 | 2153.83 | 25.89 | 44.373 | 6.34 | 1.387 | 4.903 | 8657.8 | 2.194 | 97.9 | 77.9 | 1400 | 22.14 | 5627.6 | 3038.7 | 2974 | 4364.6 | 1200.3 | 0.68028 | 6.291
2024-12-09 | 18:55 | Data | 0 | 31.799 | 29.719 | 200.018 | 7.62 | 187.802 | 2156.54 | 25.9 | 44.825 | 6.34 | 1.385 | 4.909 | 8689.46 | 2.086 | 97.9 | 78 | 1402 | 22.41 | 5648.1 | 3050.6 | 2952.8 | 4355.3 | 1200.3 | 0.68375 | 6.292
2024-12-09 | 18:55 | Data | 0 | 32.042 | 30.111 | 200.018 | 7.63 | 187.847 | 2161.06 | 25.89 | 44.825 | 6.34 | 1.395 | 4.913 | 8689.46 | 2.248 | 97.9 | 77.9 | 1405 | 22.46 | 5648.1 | 3037.6 | 2948 | 4346.7 | 1200.3 | 0.68168 | 6.308
2024-12-09 | 18:55 | Data | 0 | 32.15 | 29.753 | 200.154 | 7.63 | 187.847 | 2161.06 | 25.89 | 44.915 | 6.34 | 1.394 | 4.902 | 8671.37 | 2.498 | 97.9 | 77.9 | 1404 | 22.46 | 5636.4 | 3037.6 | 2935.2 | 4340.1 | 1200.3 | 0.68361 | 6.296
2024-12-09 | 18:55 | Data | 0 | 32.17 | 29.739 | 200.109 | 7.62 | 188.028 | 2158.35 | 25.89 | 44.825 | 6.33 | 1.381 | 4.916 | 8680.41 | 2.12 | 97.9 | 78.1 | 1404 | 22.41 | 5642.3 | 3030.9 | 2944.1 | 4335 | 1200.3 | 0.68307 | 6.296
2024-12-09 | 18:55 | Data | 0 | 32.028 | 29.976 | 199.973 | 7.62 | 187.757 | 2161.97 | 25.9 | 44.825 | 6.34 | 1.384 | 4.92 | 8680.41 | 2.052 | 97.9 | 78.1 | 1405 | 22.41 | 5642.3 | 3035.1 | 2939.9 | 4341.5 | 1200.3 | 0.68283 | 6.303
2024-12-09 | 18:56 | Data | 0 | 32.345 | 30.293 | 200.109 | 7.62 | 187.938 | 2161.97 | 25.9 | 44.825 | 6.34 | 1.387 | 4.901 | 8029.21 | 2.275 | 97.9 | 77.9 | 1405 | 22.41 | 5219 | 3018.3 | 2955.8 | 4340.3 | 1200.3 | 0.67988 | 6.288
2024-12-09 | 18:56 | Data | 0 | 31.799 | 30.009 | 200.018 | 7.63 | 187.757 | 2161.06 | 25.89 | 44.825 | 6.34 | 1.377 | 4.892 | 8644.24 | 2.302 | 97.9 | 78 | 1405 | 22.41 | 5618.8 | 3030.8 | 2933.4 | 4328.9 | 1200.4 | 0.68377 | 6.269
2024-12-09 | 18:56 | Data | 0 | 32.015 | 29.942 | 200.018 | 7.63 | 187.802 | 2161.97 | 25.9 | 44.825 | 6.33 | 1.376 | 4.91 | 8648.76 | 2.086 | 97.9 | 78.1 | 1405 | 22.41 | 5621.7 | 3028.4 | 2954.5 | 4345.5 | 1200.4 | 0.68039 | 6.285
2024-12-09 | 18:56 | Data | 0 | 32.028 | 30.057 | 200.018 | 7.63 | 187.757 | 2164.68 | 25.89 | 44.825 | 6.34 | 1.378 | 4.919 | 8635.19 | 2.214 | 97.9 | 78.1 | 1406 | 22.41 | 5612.9 | 3034.4 | 2947.6 | 4351.2 | 1200.4 | 0.68159 | 6.295
2024-12-09 | 18:56 | Data | 0 | 32.332 | 29.773 | 200.244 | 7.63 | 188.028 | 2035.43 | 25.89 | 44.825 | 6.34 | 1.385 | 4.935 | 8635.19 | 2.275 | 97.8 | 78.1 | 1323 | 22.41 | 5612.9 | 3037.1 | 2948.5 | 4346.5 | 1200.4 | 0.68128 | 6.32
2024-12-09 | 18:56 | Data | 0 | 32.197 | 29.949 | 200.018 | 7.63 | 187.938 | 2196.31 | 25.89 | 44.825 | 6.34 | 1.386 | 4.905 | 8612.58 | 2.289 | 98 | 78 | 1428 | 22.46 | 5598.2 | 3043.3 | 2973 | 4363.5 | 1200.4 | 0.68215 | 6.291
2024-12-09 | 18:56 | Data | 0 | 31.799 | 29.888 | 200.018 | 7.63 | 187.802 | 2189.99 | 25.89 | 44.825 | 6.34 | 1.395 | 4.91 | 8617.1 | 2.16 | 98 | 77.9 | 1423 | 22.41 | 5601.1 | 3006.8 | 2947.3 | 4327.1 | 1200.4 | 0.67689 | 6.303
2024-12-09 | 18:56 | Data | 0 | 32.264 | 29.753 | 200.063 | 7.63 | 187.938 | 2194.5 | 25.89 | 44.825 | 6.33 | 1.386 | 4.913 | 8639.71 | 2.309 | 98 | 78 | 1426 | 22.41 | 5615.8 | 3027.9 | 2949.1 | 4342.2 | 1200.4 | 0.68369 | 6.3
2024-12-09 | 18:56 | Data | 0 | 32.588 | 29.982 | 200.154 | 7.63 | 187.938 | 2205.35 | 25.9 | 44.825 | 6.34 | 1.386 | 4.888 | 8635.19 | 2.383 | 98 | 77.9 | 1434 | 22.46 | 5612.9 | 3031.9 | 2946.3 | 4343.8 | 1200.4 | 0.68176 | 6.276
2024-12-09 | 18:56 | Data | 0 | 32.129 | 30.266 | 200.063 | 7.63 | 187.847 | 2205.35 | 25.89 | 44.825 | 6.33 | 1.391 | 4.895 | 8635.19 | 2.309 | 98 | 77.9 | 1433 | 22.41 | 5612.9 | 3021 | 2941.2 | 4334.5 | 1200.4 | 0.67992 | 6.286
2024-12-09 | 18:56 | Data | 0 | 32.156 | 29.739 | 200.109 | 7.62 | 187.847 | 2105.93 | 25.9 | 44.825 | 6.34 | 1.393 | 4.92 | 8639.71 | 2.336 | 97.9 | 77.9 | 1369 | 22.41 | 5615.8 | 3009.1 | 2929.9 | 4313.2 | 1200.4 | 0.68076 | 6.313
2024-12-09 | 18:56 | Data | 0 | 32.271 | 30.07 | 200.199 | 7.63 | 188.028 | 2109.54 | 25.89 | 44.915 | 6.33 | 1.387 | 4.912 | 8635.19 | 2.302 | 97.9 | 78 | 1371 | 22.46 | 5612.9 | 3030.5 | 2961.7 | 4352.6 | 1200.4 | 0.681 | 6.301
2024-12-09 | 18:56 | Data | 0 | 31.954 | 30.05 | 200.154 | 7.62 | 187.938 | 2108.64 | 25.9 | 44.825 | 6.34 | 1.393 | 4.884 | 8635.19 | 1.998 | 97.9 | 77.8 | 1370 | 22.41 | 5612.9 | 3027.2 | 2963.1 | 4346 | 1200.4 | 0.67932 | 6.277
2024-12-09 | 18:56 | Data | 0 | 32.541 | 29.969 | 200.199 | 7.62 | 187.938 | 2103.22 | 25.89 | 44.825 | 6.33 | 1.389 | 4.91 | 8657.8 | 2.397 | 97.9 | 77.9 | 1368 | 22.46 | 5627.6 | 3037.9 | 2991.3 | 4377.4 | 1200.4 | 0.67977 | 6.298
2024-12-09 | 18:56 | Data | 0 | 32.028 | 30.043 | 200.154 | 7.63 | 187.847 | 2106.83 | 25.9 | 44.825 | 6.33 | 1.394 | 4.936 | 8648.76 | 2.302 | 97.9 | 78 | 1369 | 22.41 | 5621.7 | 3034.7 | 2952.6 | 4341.1 | 1200.4 | 0.68271 | 6.329
2024-12-09 | 18:56 | Data | 0 | 32.204 | 30.144 | 200.199 | 7.63 | 187.847 | 2106.83 | 25.9 | 44.734 | 6.33 | 1.387 | 4.919 | 8621.63 | 2.106 | 97.9 | 78 | 1369 | 22.37 | 5604.1 | 3021 | 2974.3 | 4357.3 | 1200.4 | 0.67632 | 6.305
2024-12-09 | 18:56 | Data | 0 | 32.021 | 29.841 | 200.109 | 7.62 | 187.757 | 2113.16 | 25.89 | 44.734 | 6.33 | 1.383 | 4.915 | 8648.76 | 2.187 | 97.9 | 78 | 1374 | 22.41 | 5621.7 | 3042.3 | 2983.7 | 4370 | 1200.4 | 0.6803 | 6.298
2024-12-09 | 18:56 | Data | 0 | 32.028 | 30.165 | 199.973 | 7.63 | 187.847 | 2111.35 | 25.89 | 44.825 | 6.34 | 1.384 | 4.885 | 8626.15 | 2.309 | 97.9 | 77.9 | 1372 | 22.41 | 5607 | 3028.5 | 2965.7 | 4349.6 | 1200.4 | 0.68066 | 6.269
2024-12-09 | 18:57 | Data | 0 | 32.089 | 29.618 | 200.154 | 7.63 | 187.847 | 2114.06 | 25.89 | 44.915 | 6.34 | 1.388 | 4.9 | 8630.67 | 2.167 | 97.9 | 77.9 | 1374 | 22.46 | 5609.9 | 3023.9 | 2957.2 | 4340.8 | 1200.4 | 0.6828 | 6.289
2024-12-09 | 18:57 | Data | 0 | 32.028 | 29.739 | 200.018 | 7.63 | 187.712 | 2117.68 | 25.89 | 44.825 | 6.33 | 1.392 | 4.897 | 8635.19 | 2.282 | 97.9 | 77.9 | 1376 | 22.41 | 5612.9 | 3018.6 | 2947.9 | 4334.3 | 1200.4 | 0.6796 | 6.29
2024-12-09 | 18:57 | Data | 0 | 32.345 | 29.746 | 200.154 | 7.63 | 188.028 | 2120.39 | 25.89 | 44.825 | 6.34 | 1.392 | 4.912 | 8630.67 | 2.12 | 97.9 | 77.9 | 1378 | 22.37 | 5609.9 | 3037.8 | 2948.9 | 4348.3 | 1200.4 | 0.68276 | 6.305
2024-12-09 | 18:57 | Data | 0 | 32.035 | 30.111 | 200.154 | 7.62 | 187.938 | 2124.91 | 25.9 | 44.825 | 6.33 | 1.389 | 4.919 | 8639.71 | 2.093 | 97.9 | 78 | 1382 | 22.46 | 5615.8 | 3030.7 | 2964.7 | 4350.6 | 1200.4 | 0.68059 | 6.308
2024-12-09 | 18:57 | Data | 0 | 32.042 | 29.942 | 200.063 | 7.62 | 187.802 | 2127.62 | 25.89 | 44.825 | 6.34 | 1.385 | 4.901 | 8644.24 | 2.133 | 97.9 | 78 | 1383 | 22.41 | 5618.8 | 3019.1 | 2960.9 | 4344 | 1200.4 | 0.67855 | 6.285
2024-12-09 | 18:57 | Data | 0 | 31.819 | 29.733 | 200.154 | 7.63 | 187.938 | 2130.33 | 25.89 | 44.825 | 6.33 | 1.382 | 4.899 | 8662.33 | 2.073 | 97.9 | 78 | 1385 | 22.41 | 5630.5 | 3024.4 | 2964.4 | 4349.9 | 1200.4 | 0.67839 | 6.281
2024-12-09 | 18:57 | Data | 0 | 31.92 | 29.928 | 200.063 | 7.63 | 187.757 | 2131.24 | 25.89 | 44.825 | 6.33 | 1.391 | 4.911 | 8693.98 | 2.113 | 97.9 | 77.9 | 1385 | 22.46 | 5651.1 | 3026.8 | 2983.6 | 4363.6 | 1200.4 | 0.6776 | 6.302
2024-12-09 | 18:57 | Data | 0 | 31.92 | 29.942 | 199.928 | 7.63 | 187.757 | 2133.95 | 25.89 | 44.825 | 6.34 | 1.395 | 4.917 | 8693.98 | 2.235 | 97.9 | 77.9 | 1388 | 22.41 | 5651.1 | 3032.6 | 2974.9 | 4360.8 | 1200.4 | 0.67869 | 6.312
2024-12-09 | 18:57 | Data | 0 | 32.258 | 29.847 | 200.018 | 7.63 | 187.938 | 2135.76 | 25.89 | 44.825 | 6.34 | 1.395 | 4.908 | 8707.55 | 2.282 | 97.9 | 77.9 | 1389 | 22.41 | 5659.9 | 3031.7 | 2955.2 | 4349.8 | 1200.4 | 0.68119 | 6.303
2024-12-09 | 18:57 | Data | 0 | 32.028 | 29.577 | 199.837 | 7.63 | 187.757 | 2139.37 | 25.89 | 44.825 | 6.33 | 1.387 | 4.911 | 8693.98 | 2.194 | 97.9 | 78 | 1391 | 22.37 | 5651.1 | 3033.8 | 2954 | 4347.7 | 1200.4 | 0.68165 | 6.3
2024-12-09 | 18:57 | Data | 0 | 32.197 | 30.178 | 199.973 | 7.62 | 187.938 | 2138.47 | 25.9 | 44.734 | 6.34 | 1.376 | 4.926 | 8693.98 | 2.309 | 97.9 | 78.2 | 1390 | 22.41 | 5651.1 | 3024.8 | 2944 | 4340.1 | 1200.4 | 0.6829 | 6.301
2024-12-09 | 18:57 | Data | 0 | 31.805 | 29.618 | 199.928 | 7.63 | 187.847 | 2142.99 | 25.89 | 44.734 | 6.34 | 1.389 | 4.92 | 8703.03 | 2.289 | 97.9 | 78 | 1393 | 22.41 | 5657 | 3033.4 | 2940.6 | 4339.5 | 1200.4 | 0.68281 | 6.309
2024-12-09 | 18:57 | Data | 0 | 32.467 | 30.036 | 200.199 | 7.63 | 187.938 | 2146.6 | 25.89 | 44.825 | 6.34 | 1.384 | 4.888 | 8689.46 | 2.201 | 97.9 | 77.9 | 1395 | 22.41 | 5648.1 | 3022.1 | 2946.7 | 4331.6 | 1200.4 | 0.68199 | 6.272
2024-12-09 | 18:57 | Data | 0 | 32.129 | 30.165 | 200.063 | 7.62 | 187.938 | 2147.51 | 25.89 | 44.825 | 6.33 | 1.393 | 4.935 | 8671.37 | 2.302 | 97.9 | 78 | 1396 | 22.41 | 5636.4 | 3026.8 | 2937.4 | 4333.2 | 1200.4 | 0.68287 | 6.327
2024-12-09 | 18:57 | Data | 0 | 32.474 | 30.07 | 200.154 | 7.63 | 187.938 | 2148.41 | 25.89 | 44.825 | 6.34 | 1.391 | 4.926 | 8657.8 | 2.309 | 97.9 | 78 | 1396 | 22.41 | 5627.6 | 3036.5 | 2933.5 | 4333.8 | 1200.4 | 0.68495 | 6.317
2024-12-09 | 18:57 | Data | 0 | 32.042 | 29.726 | 200.063 | 7.63 | 187.802 | 2155.64 | 25.89 | 44.825 | 6.33 | 1.391 | 4.922 | 8662.33 | 2.302 | 97.9 | 78 | 1401 | 22.41 | 5630.5 | 3036.8 | 2923.1 | 4330 | 1200.4 | 0.68567 | 6.312
2024-12-09 | 18:57 | Data | 0 | 32.042 | 29.955 | 200.063 | 7.63 | 187.938 | 2153.83 | 25.89 | 44.825 | 6.33 | 1.386 | 4.92 | 8657.8 | 2.079 | 97.9 | 78 | 1400 | 22.41 | 5627.6 | 3033.9 | 2930.3 | 4327.3 | 1200.4 | 0.68503 | 6.307
2024-12-09 | 18:58 | Data | 0 | 31.988 | 29.962 | 199.973 | 7.63 | 187.983 | 2155.64 | 25.89 | 44.825 | 6.33 | 1.394 | 4.928 | 8703.03 | 2.221 | 97.9 | 78 | 1401 | 22.41 | 5657 | 3035.9 | 2943.5 | 4342.1 | 1200.4 | 0.68303 | 6.321
2024-12-09 | 18:58 | Data | 0 | 32.055 | 30.151 | 200.38 | 7.63 | 187.938 | 2159.26 | 25.89 | 44.915 | 6.33 | 1.397 | 4.924 | 8716.59 | 2.025 | 97.9 | 77.9 | 1403 | 22.41 | 5665.8 | 3025.7 | 2939.4 | 4331.5 | 1200.5 | 0.68163 | 6.32
2024-12-09 | 18:58 | Data | 0 | 32.17 | 30.158 | 200.109 | 7.63 | 187.847 | 2159.26 | 25.89 | 44.554 | 6.34 | 1.388 | 4.912 | 8703.03 | 2.214 | 97.9 | 78 | 1404 | 22.28 | 5657 | 3028.3 | 2950.5 | 4341.3 | 1200.5 | 0.68157 | 6.301
2024-12-09 | 18:58 | Data | 0 | 31.947 | 29.901 | 200.063 | 7.63 | 187.938 | 2158.35 | 25.89 | 44.915 | 6.34 | 1.384 | 4.894 | 8703.03 | 2.235 | 97.9 | 78 | 1403 | 22.46 | 5657 | 3023.1 | 2944 | 4331.6 | 1200.5 | 0.68143 | 6.278
2024-12-09 | 18:58 | Data | 0 | 31.934 | 29.537 | 199.973 | 7.63 | 187.847 | 2159.26 | 25.9 | 44.825 | 6.34 | 1.387 | 4.897 | 8666.85 | 2.262 | 97.9 | 77.9 | 1404 | 22.37 | 5633.5 | 3041.7 | 2914.4 | 4322.7 | 1200.5 | 0.68732 | 6.284
2024-12-09 | 18:58 | Data | 0 | 31.812 | 29.955 | 199.973 | 7.62 | 187.983 | 2158.35 | 25.9 | 44.825 | 6.34 | 1.381 | 4.931 | 8657.8 | 2.133 | 97.9 | 78.1 | 1403 | 22.41 | 5627.6 | 3037.9 | 2910.8 | 4319.6 | 1200.5 | 0.68671 | 6.313
2024-12-09 | 18:58 | Data | 0 | 32.028 | 29.955 | 200.199 | 7.63 | 187.847 | 2159.26 | 25.89 | 44.554 | 6.34 | 1.381 | 4.915 | 8987.93 | 2.248 | 97.9 | 78.1 | 1404 | 22.28 | 5842.2 | 3042 | 2930.4 | 4334.8 | 1200.5 | 0.68603 | 6.296
2024-12-09 | 18:58 | Data | 0 | 32.028 | 29.955 | 200.018 | 7.63 | 187.802 | 2159.26 | 25.89 | 44.644 | 6.34 | 1.378 | 4.921 | 8788.95 | 2.073 | 97.9 | 78.1 | 1403 | 22.32 | 5712.8 | 3051.4 | 2939.3 | 4345.7 | 1200.5 | 0.68777 | 6.299
2024-12-09 | 18:58 | Data | 0 | 32.318 | 29.76 | 200.109 | 7.62 | 187.983 | 2158.35 | 25.89 | 44.554 | 6.33 | 1.375 | 4.92 | 8644.24 | 2.43 | 97.9 | 78.2 | 1403 | 22.28 | 5618.8 | 3022.1 | 2920.3 | 4316.5 | 1200.5 | 0.6834 | 6.294
2024-12-09 | 18:58 | Data | 0 | 32.028 | 30.165 | 200.109 | 7.63 | 187.983 | 2155.64 | 25.89 | 44.644 | 6.33 | 1.375 | 4.92 | 8662.33 | 2.106 | 97.9 | 78.2 | 1402 | 22.28 | 5630.5 | 3027.8 | 2915.2 | 4318.7 | 1200.5 | 0.68535 | 6.296
2024-12-09 | 18:58 | Data | 0 | 32.278 | 30.158 | 200.199 | 7.62 | 187.983 | 2152.02 | 25.89 | 44.734 | 6.34 | 1.385 | 4.913 | 8653.28 | 2.133 | 97.9 | 78 | 1399 | 22.37 | 5624.6 | 3042.4 | 2910.5 | 4320.8 | 1200.5 | 0.68788 | 6.298
2024-12-09 | 18:58 | Data | 0 | 31.805 | 29.841 | 200.109 | 7.63 | 187.847 | 2155.64 | 25.89 | 44.734 | 6.34 | 1.387 | 4.942 | 8662.33 | 2.275 | 97.9 | 78.1 | 1402 | 22.37 | 5630.5 | 3023.4 | 2947.1 | 4338.1 | 1200.5 | 0.68143 | 6.329
2024-12-09 | 18:58 | Data | 0 | 32.136 | 30.171 | 200.244 | 7.62 | 187.983 | 2156.54 | 25.89 | 44.915 | 6.34 | 1.378 | 4.916 | 8648.76 | 2.174 | 97.9 | 78.1 | 1401 | 22.46 | 5621.7 | 3037.8 | 2924.2 | 4332.8 | 1200.5 | 0.68402 | 6.294
2024-12-09 | 18:58 | Data | 0 | 32.102 | 29.739 | 200.199 | 7.63 | 187.847 | 2156.54 | 25.9 | 44.734 | 6.33 | 1.38 | 4.93 | 8594.49 | 2.052 | 97.9 | 78.1 | 1402 | 22.41 | 5586.4 | 3043.8 | 2925.4 | 4331.8 | 1200.5 | 0.68636 | 6.311
2024-12-09 | 18:58 | Data | 0 | 32.251 | 29.739 | 200.063 | 7.63 | 187.802 | 2159.26 | 25.89 | 44.825 | 6.33 | 1.392 | 4.924 | 8594.49 | 2.484 | 97.9 | 78 | 1404 | 22.41 | 5586.4 | 3042.5 | 2937.4 | 4340.4 | 1200.5 | 0.68557 | 6.317
2024-12-09 | 18:58 | Data | 0 | 32.42 | 30.185 | 200.199 | 7.63 | 187.938 | 2153.83 | 25.89 | 44.825 | 6.34 | 1.397 | 4.901 | 8608.06 | 2.309 | 97.9 | 77.8 | 1400 | 22.46 | 5595.2 | 3008 | 2913.1 | 4301.1 | 1200.5 | 0.68319 | 6.299
2024-12-09 | 18:58 | Data | 0 | 32.258 | 29.841 | 200.109 | 7.62 | 187.938 | 2160.16 | 25.89 | 44.825 | 6.33 | 1.395 | 4.92 | 8594.49 | 2.187 | 97.9 | 77.9 | 1404 | 22.41 | 5586.4 | 3030.3 | 2929.6 | 4327.6 | 1200.5 | 0.68502 | 6.315
2024-12-09 | 18:58 | Data | 0 | 32.345 | 29.982 | 200.109 | 7.63 | 188.028 | 2159.26 | 25.89 | 44.825 | 6.34 | 1.38 | 4.898 | 8662.33 | 2.248 | 97.9 | 78 | 1404 | 22.41 | 5630.5 | 3025.8 | 2913.6 | 4312.8 | 1200.5 | 0.68568 | 6.278
2024-12-09 | 18:59 | Data | 0 | 32.055 | 29.928 | 200.154 | 7.63 | 187.938 | 2155.64 | 25.89 | 44.825 | 6.33 | 1.392 | 4.891 | 8693.98 | 2.282 | 97.9 | 77.8 | 1401 | 22.46 | 5651.1 | 3019.1 | 2925.9 | 4317.7 | 1200.5 | 0.6826 | 6.282
2024-12-09 | 18:59 | Data | 0 | 32.042 | 29.625 | 200.109 | 7.63 | 187.847 | 2155.64 | 25.89 | 44.825 | 6.34 | 1.378 | 4.895 | 8657.8 | 2.282 | 97.9 | 78 | 1402 | 22.46 | 5627.6 | 3022.3 | 2931.4 | 4325 | 1200.5 | 0.68418 | 6.273
2024-12-09 | 18:59 | Data | 0 | 31.873 | 29.726 | 200.063 | 7.63 | 187.847 | 2156.54 | 25.89 | 44.825 | 6.33 | 1.385 | 4.91 | 8671.37 | 2.079 | 97.9 | 78 | 1401 | 22.41 | 5636.4 | 3032.6 | 2916.2 | 4319.5 | 1200.5 | 0.68507 | 6.295
2024-12-09 | 18:59 | Data | 0 | 31.805 | 29.928 | 200.018 | 7.63 | 187.983 | 2156.54 | 25.89 | 44.734 | 6.34 | 1.385 | 4.902 | 8662.33 | 2.275 | 97.9 | 78 | 1402 | 22.41 | 5630.5 | 3025.3 | 2937.3 | 4328.9 | 1200.5 | 0.68155 | 6.287
2024-12-09 | 18:59 | Data | 0 | 32.237 | 29.955 | 200.018 | 7.63 | 187.983 | 2151.12 | 25.89 | 44.915 | 6.34 | 1.384 | 4.912 | 8662.33 | 2.201 | 97.9 | 78 | 1398 | 22.46 | 5630.5 | 3016.3 | 2926.1 | 4319.7 | 1200.5 | 0.68188 | 6.296
2024-12-09 | 18:59 | Data | 0 | 32.035 | 29.827 | 199.973 | 7.63 | 187.802 | 2155.64 | 25.89 | 44.734 | 6.34 | 1.383 | 4.899 | 8657.8 | 2.127 | 97.9 | 78 | 1402 | 22.41 | 5627.6 | 3035.3 | 2910.1 | 4312.6 | 1200.5 | 0.68227 | 6.282
2024-12-09 | 18:59 | Data | 0 | 31.981 | 29.827 | 199.973 | 7.63 | 188.028 | 2156.54 | 25.89 | 44.825 | 6.34 | 1.393 | 4.863 | 8671.37 | 2.208 | 97.9 | 77.7 | 1401 | 22.41 | 5636.4 | 3017.1 | 2926.5 | 4316.5 | 1200.5 | 0.68157 | 6.256
2024-12-09 | 18:59 | Data | 0 | 32.143 | 29.733 | 200.516 | 7.63 | 188.119 | 2156.54 | 25.9 | 44.825 | 6.34 | 1.385 | 4.89 | 8703.03 | 2.241 | 97.9 | 77.9 | 1401 | 22.41 | 5657 | 3026.1 | 2933.1 | 4330 | 1200.5 | 0.6823 | 6.272
2024-12-09 | 18:59 | Data | 0 | 31.913 | 29.78 | 200.289 | 7.63 | 188.164 | 2154.74 | 25.89 | 44.825 | 6.34 | 1.386 | 4.912 | 8716.59 | 2.444 | 97.9 | 78 | 1401 | 22.41 | 5665.8 | 3037.7 | 2923 | 4332 | 1200.5 | 0.68675 | 6.299
2024-12-09 | 18:59 | Data | 0 | 32.055 | 29.928 | 200.335 | 7.63 | 188.164 | 2155.64 | 25.89 | 44.825 | 6.34 | 1.38 | 4.914 | 8707.55 | 2.106 | 97.9 | 78.1 | 1401 | 22.41 | 5659.9 | 3014.7 | 2920.2 | 4314.3 | 1200.5 | 0.68227 | 6.294
2024-12-09 | 18:59 | Data | 0 | 32.028 | 29.949 | 200.335 | 7.63 | 188.073 | 2156.54 | 25.89 | 44.734 | 6.34 | 1.382 | 4.883 | 8721.11 | 2.086 | 97.9 | 77.9 | 1401 | 22.41 | 5668.7 | 3031.7 | 2927.2 | 4327.6 | 1200.5 | 0.68426 | 6.265
2024-12-09 | 18:59 | Data | 0 | 32.258 | 30.124 | 200.47 | 7.63 | 188.119 | 2157.45 | 25.89 | 44.825 | 6.34 | 1.385 | 4.886 | 8689.46 | 2.208 | 97.9 | 77.9 | 1402 | 22.41 | 5648.1 | 3029.2 | 2924.1 | 4324.5 | 1200.5 | 0.6837 | 6.271
2024-12-09 | 18:59 | Data | 0 | 32.028 | 30.151 | 200.289 | 7.63 | 188.119 | 2160.16 | 25.9 | 44.915 | 6.34 | 1.395 | 4.929 | 8693.98 | 2.106 | 97.9 | 77.9 | 1405 | 22.46 | 5651.1 | 3030.4 | 2935.8 | 4330.3 | 1200.5 | 0.68338 | 6.325
2024-12-09 | 18:59 | Data | 0 | 32.568 | 29.793 | 200.38 | 7.63 | 188.164 | 2163.77 | 25.89 | 44.825 | 6.34 | 1.393 | 4.915 | 8693.98 | 2.248 | 97.9 | 77.9 | 1407 | 22.41 | 5651.1 | 3063.9 | 2973.3 | 4377.4 | 1200.5 | 0.68465 | 6.308
2024-12-09 | 18:59 | Data | 0 | 32.386 | 29.955 | 200.561 | 7.63 | 188.209 | 2163.77 | 25.9 | 44.915 | 6.34 | 1.394 | 4.913 | 8703.03 | 2.086 | 97.9 | 77.9 | 1406 | 22.46 | 5657 | 3040.8 | 2942.5 | 4337.9 | 1200.5 | 0.68443 | 6.306
2024-12-09 | 18:59 | Data | 0 | 32.46 | 29.82 | 200.335 | 7.63 | 188.119 | 2166.49 | 25.9 | 44.825 | 6.35 | 1.398 | 4.937 | 8716.59 | 2.376 | 97.9 | 77.9 | 1408 | 22.41 | 5665.8 | 3037.1 | 2867.6 | 4267 | 1200.5 | 0.6926 | 6.335
2024-12-09 | 18:59 | Data | 0 | 32.264 | 29.733 | 200.335 | 7.63 | 188.164 | 2166.49 | 25.89 | 44.825 | 6.33 | 1.396 | 4.945 | 8721.11 | 2.343 | 97.9 | 78 | 1408 | 22.41 | 5668.7 | 3040.8 | 2946.3 | 4348.4 | 1200.5 | 0.68466 | 6.341
2024-12-09 | 18:59 | Data | 0 | 32.258 | 30.009 | 200.335 | 7.63 | 188.164 | 2163.77 | 25.89 | 44.915 | 6.34 | 1.387 | 4.904 | 8730.16 | 2.214 | 97.9 | 77.9 | 1406 | 22.41 | 5674.6 | 3045.3 | 2909.4 | 4323.5 | 1200.5 | 0.68782 | 6.293
2024-12-09 | 19:00 | Data | 0 | 32.042 | 29.888 | 200.335 | 7.62 | 188.028 | 2163.77 | 25.89 | 44.915 | 6.34 | 1.387 | 4.882 | 8282.46 | 2.349 | 97.9 | 77.9 | 1406 | 22.41 | 5383.6 | 3045.8 | 2935 | 4343.1 | 1200.6 | 0.685 | 6.271
2024-12-09 | 19:00 | Data | 0 | 32.264 | 30.34 | 200.697 | 7.63 | 188.345 | 2161.06 | 25.89 | 44.825 | 6.33 | 1.385 | 4.856 | 8657.8 | 2.255 | 97.9 | 77.8 | 1405 | 22.41 | 5627.6 | 3047 | 2924.5 | 4334.8 | 1200.6 | 0.6854 | 6.242
2024-12-09 | 19:00 | Data | 0 | 32.028 | 29.726 | 200.651 | 7.63 | 188.345 | 2161.06 | 25.89 | 44.825 | 6.34 | 1.389 | 4.897 | 8657.8 | 2.302 | 97.9 | 77.9 | 1405 | 22.46 | 5627.6 | 3067 | 2938.8 | 4361.6 | 1200.6 | 0.68688 | 6.287
2024-12-09 | 19:00 | Data | 0 | 31.988 | 29.733 | 200.832 | 7.63 | 188.39 | 2163.77 | 25.89 | 44.825 | 6.34 | 1.387 | 4.9 | 8648.76 | 2.268 | 97.9 | 77.9 | 1406 | 22.41 | 5621.7 | 3047.2 | 2923.7 | 4340.9 | 1200.6 | 0.68528 | 6.287
2024-12-09 | 19:00 | Data | 0 | 32.028 | 30.043 | 200.651 | 7.63 | 188.435 | 2161.06 | 25.89 | 44.825 | 6.34 | 1.377 | 4.897 | 8644.24 | 2.295 | 97.9 | 78 | 1405 | 22.41 | 5618.8 | 3045.3 | 2931.4 | 4339.7 | 1200.6 | 0.68546 | 6.275
2024-12-09 | 19:00 | Data | 0 | 32.15 | 29.753 | 200.697 | 7.62 | 188.435 | 2161.06 | 25.89 | 44.825 | 6.34 | 1.393 | 4.901 | 8635.19 | 2.262 | 97.9 | 77.9 | 1405 | 22.46 | 5612.9 | 3057 | 2929 | 4345.3 | 1200.6 | 0.68671 | 6.292
2024-12-09 | 19:00 | Data | 0 | 32.318 | 29.739 | 200.651 | 7.63 | 188.435 | 2161.97 | 25.89 | 44.825 | 6.34 | 1.395 | 4.92 | 8635.19 | 2.302 | 97.9 | 77.9 | 1405 | 22.46 | 5612.9 | 3080.6 | 2944.5 | 4374 | 1200.6 | 0.68836 | 6.316
2024-12-09 | 19:00 | Data | 0 | 32.035 | 29.631 | 200.651 | 7.62 | 188.39 | 2039.95 | 25.89 | 44.825 | 6.34 | 1.388 | 4.924 | 8653.28 | 2.457 | 97.8 | 78 | 1326 | 22.46 | 5624.6 | 3067.6 | 2959.4 | 4372.6 | 1200.6 | 0.68611 | 6.312
2024-12-09 | 19:00 | Data | 0 | 32.251 | 29.955 | 200.742 | 7.63 | 188.48 | 2141.18 | 25.89 | 44.825 | 6.34 | 1.391 | 4.907 | 8635.19 | 2.309 | 97.9 | 77.9 | 1392 | 22.41 | 5612.9 | 3062.8 | 2948.9 | 4372.2 | 1200.6 | 0.68375 | 6.298
2024-12-09 | 19:00 | Data | 0 | 32.035 | 30.171 | 200.651 | 7.63 | 188.435 | 2142.08 | 25.9 | 44.825 | 6.34 | 1.385 | 4.91 | 8644.24 | 2.046 | 97.9 | 78 | 1392 | 22.41 | 5618.8 | 3085.8 | 2933.3 | 4372 | 1200.6 | 0.68798 | 6.295
2024-12-09 | 19:00 | Data | 0 | 32.379 | 30.07 | 200.742 | 7.63 | 188.435 | 2142.08 | 25.89 | 44.554 | 6.34 | 1.384 | 4.924 | 8648.76 | 2.295 | 97.9 | 78.1 | 1392 | 22.28 | 5621.7 | 3081 | 2972.5 | 4393.3 | 1200.6 | 0.68506 | 6.308
2024-12-09 | 19:00 | Data | 0 | 32.035 | 30.124 | 200.787 | 7.63 | 188.39 | 2149.31 | 25.89 | 44.554 | 6.34 | 1.391 | 4.917 | 8626.15 | 2.127 | 97.9 | 77.9 | 1399 | 22.28 | 5607 | 3050.5 | 2966.9 | 4370.7 | 1200.6 | 0.68092 | 6.308
2024-12-09 | 19:00 | Data | 0 | 32.264 | 29.76 | 200.742 | 7.63 | 188.48 | 2159.26 | 25.89 | 44.554 | 6.34 | 1.393 | 4.908 | 8662.33 | 2.349 | 97.9 | 77.9 | 1404 | 22.32 | 5630.5 | 3051.3 | 2937.6 | 4352.3 | 1200.6 | 0.68493 | 6.301
2024-12-09 | 19:00 | Data | 0 | 32.15 | 30.111 | 200.697 | 7.63 | 188.39 | 2158.35 | 25.89 | 44.644 | 6.34 | 1.388 | 4.91 | 8594.49 | 2.302 | 97.9 | 78 | 1404 | 22.32 | 5586.4 | 3065.7 | 2958.6 | 4377.5 | 1200.6 | 0.68281 | 6.299
2024-12-09 | 19:00 | Data | 0 | 32.372 | 30.009 | 200.697 | 7.62 | 188.435 | 2158.35 | 25.89 | 44.464 | 6.34 | 1.396 | 4.92 | 8585.45 | 2.268 | 97.9 | 77.9 | 1404 | 22.23 | 5580.5 | 3063.9 | 2960.7 | 4375.4 | 1200.6 | 0.68431 | 6.316
2024-12-09 | 19:00 | Data | 0 | 32.028 | 29.733 | 200.697 | 7.63 | 188.39 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.38 | 4.931 | 8594.49 | 2.282 | 97.9 | 78.1 | 1405 | 22.28 | 5586.4 | 3063.2 | 2953.2 | 4373.8 | 1200.6 | 0.68498 | 6.311
2024-12-09 | 19:00 | Data | 0 | 32.237 | 29.78 | 200.787 | 7.63 | 188.435 | 2164.68 | 25.89 | 44.554 | 6.33 | 1.387 | 4.921 | 8599.01 | 2.295 | 97.9 | 78 | 1406 | 22.28 | 5589.4 | 3089 | 2956.9 | 4387.9 | 1200.6 | 0.68653 | 6.31
2024-12-09 | 19:00 | Data | 0 | 32.264 | 30.158 | 200.697 | 7.62 | 188.39 | 2161.06 | 25.89 | 44.644 | 6.34 | 1.393 | 4.945 | 8603.54 | 2.194 | 97.9 | 78 | 1405 | 22.32 | 5592.3 | 3068.1 | 2954.6 | 4373.3 | 1200.6 | 0.68437 | 6.338
2024-12-09 | 19:01 | Data | 0 | 32.042 | 29.955 | 200.832 | 7.63 | 188.39 | 2161.06 | 25.89 | 44.644 | 6.33 | 1.387 | 4.904 | 8599.01 | 2.073 | 97.9 | 77.9 | 1405 | 22.23 | 5589.4 | 3062.9 | 2972.5 | 4384.2 | 1200.6 | 0.68192 | 6.291
2024-12-09 | 19:01 | Data | 0 | 32.177 | 30.266 | 200.787 | 7.62 | 188.39 | 2158.35 | 25.89 | 44.554 | 6.34 | 1.389 | 4.91 | 8621.63 | 2.025 | 97.9 | 77.9 | 1403 | 22.28 | 5604.1 | 3058.4 | 2956.3 | 4368.1 | 1200.6 | 0.68279 | 6.3
2024-12-09 | 19:01 | Data | 0 | 32.028 | 29.834 | 200.742 | 7.63 | 188.254 | 2158.35 | 25.89 | 44.554 | 6.34 | 1.379 | 4.91 | 8603.54 | 2.194 | 97.9 | 78.1 | 1403 | 22.28 | 5592.3 | 3066.6 | 2971.4 | 4382 | 1200.6 | 0.68333 | 6.289
2024-12-09 | 19:01 | Data | 0 | 31.812 | 29.726 | 200.651 | 7.62 | 188.254 | 2158.35 | 25.9 | 44.644 | 6.33 | 1.38 | 4.917 | 8617.1 | 2.248 | 97.9 | 78.1 | 1402 | 22.28 | 5601.1 | 3070.4 | 2956 | 4376.3 | 1200.6 | 0.68457 | 6.297
2024-12-09 | 19:01 | Data | 0 | 32.258 | 30.124 | 200.787 | 7.63 | 188.48 | 2158.35 | 25.89 | 44.554 | 6.34 | 1.388 | 4.915 | 8621.63 | 2.194 | 97.9 | 78 | 1404 | 22.28 | 5604.1 | 3067.6 | 2937.8 | 4366.3 | 1200.6 | 0.68611 | 6.304
2024-12-09 | 19:01 | Data | 0 | 32.042 | 29.847 | 200.742 | 7.63 | 188.39 | 2155.64 | 25.89 | 44.554 | 6.33 | 1.39 | 4.935 | 8621.63 | 2.302 | 97.9 | 78 | 1401 | 22.28 | 5604.1 | 3063.2 | 2969 | 4384 | 1200.6 | 0.68236 | 6.325
2024-12-09 | 19:01 | Data | 0 | 32.028 | 30.225 | 200.606 | 7.62 | 188.345 | 2155.64 | 25.89 | 44.554 | 6.34 | 1.387 | 4.929 | 8635.19 | 2.309 | 97.9 | 78 | 1402 | 22.28 | 5612.9 | 3069.9 | 2951.6 | 4363.2 | 1200.6 | 0.68619 | 6.317
2024-12-09 | 19:01 | Data | 0 | 31.805 | 29.928 | 200.787 | 7.63 | 188.299 | 2153.83 | 25.89 | 44.915 | 6.33 | 1.393 | 4.928 | 8630.67 | 1.904 | 97.9 | 78 | 1399 | 22.46 | 5609.9 | 3055 | 2926.5 | 4345.1 | 1200.6 | 0.68531 | 6.32
2024-12-09 | 19:01 | Data | 0 | 32.028 | 29.557 | 200.561 | 7.63 | 188.254 | 2153.83 | 25.89 | 44.373 | 6.34 | 1.393 | 4.926 | 8648.76 | 2.417 | 97.9 | 78 | 1400 | 22.19 | 5621.7 | 3060.7 | 2950.1 | 4363 | 1200.6 | 0.68477 | 6.319
2024-12-09 | 19:01 | Data | 0 | 32.251 | 29.739 | 200.561 | 7.62 | 188.345 | 2153.83 | 25.89 | 44.915 | 6.34 | 1.387 | 4.903 | 8648.76 | 2.302 | 97.9 | 78 | 1400 | 22.41 | 5621.7 | 3009.1 | 2961.3 | 4331.5 | 1200.6 | 0.67931 | 6.291
2024-12-09 | 19:01 | Data | 0 | 32.318 | 29.766 | 200.697 | 7.63 | 188.435 | 2154.74 | 25.9 | 44.554 | 6.34 | 1.384 | 4.912 | 8644.24 | 2.289 | 97.9 | 78 | 1401 | 22.28 | 5618.8 | 2983.7 | 2965.6 | 4319 | 1200.6 | 0.67375 | 6.297
2024-12-09 | 19:01 | Data | 0 | 31.819 | 29.726 | 200.516 | 7.63 | 188.299 | 2155.64 | 25.89 | 44.554 | 6.33 | 1.399 | 4.938 | 8657.8 | 2.073 | 97.9 | 77.9 | 1401 | 22.28 | 5627.6 | 2986.8 | 2940.9 | 4301.9 | 1200.6 | 0.67924 | 6.338
2024-12-09 | 19:01 | Data | 0 | 32.129 | 29.726 | 200.651 | 7.63 | 188.435 | 2156.54 | 25.89 | 44.554 | 6.34 | 1.4 | 4.913 | 8662.33 | 2.316 | 97.9 | 77.8 | 1402 | 22.28 | 5630.5 | 2992.2 | 2930 | 4294.1 | 1200.6 | 0.68126 | 6.313
2024-12-09 | 19:01 | Data | 0 | 31.947 | 29.719 | 200.606 | 7.63 | 188.254 | 2151.12 | 25.89 | 44.554 | 6.34 | 1.388 | 4.926 | 8648.76 | 2.309 | 97.9 | 78 | 1399 | 22.28 | 5621.7 | 3006.7 | 2965 | 4331.7 | 1200.6 | 0.67802 | 6.315
2024-12-09 | 19:01 | Data | 0 | 32.028 | 29.726 | 200.742 | 7.62 | 188.435 | 2159.26 | 25.89 | 44.915 | 6.34 | 1.389 | 4.919 | 8662.33 | 2.214 | 97.9 | 78 | 1404 | 22.41 | 5630.5 | 3004 | 2942.6 | 4312.4 | 1200.6 | 0.68064 | 6.308
2024-12-09 | 19:01 | Data | 0 | 32.264 | 29.746 | 200.697 | 7.63 | 188.435 | 2153.83 | 25.89 | 44.915 | 6.34 | 1.393 | 4.92 | 8680.41 | 2.282 | 97.9 | 77.9 | 1400 | 22.41 | 5642.3 | 2978.3 | 2933.5 | 4289.4 | 1200.6 | 0.67836 | 6.313
2024-12-09 | 19:01 | Data | 0 | 31.832 | 29.625 | 200.651 | 7.62 | 188.39 | 2158.35 | 25.89 | 44.825 | 6.34 | 1.388 | 4.924 | 8671.37 | 2.275 | 97.9 | 78 | 1403 | 22.41 | 5636.4 | 2986.8 | 2947.3 | 4305.1 | 1200.6 | 0.67726 | 6.312
2024-12-09 | 19:02 | Data | 0 | 32.035 | 29.949 | 200.787 | 7.62 | 188.39 | 2155.64 | 25.89 | 44.825 | 6.33 | 1.387 | 4.954 | 8671.37 | 2.079 | 97.9 | 78.1 | 1401 | 22.41 | 5636.4 | 3006.9 | 2965.1 | 4329.6 | 1200.7 | 0.6797 | 6.341
2024-12-09 | 19:02 | Data | 0 | 32.055 | 29.908 | 200.651 | 7.63 | 188.435 | 2152.93 | 25.89 | 44.825 | 6.34 | 1.382 | 4.929 | 8662.33 | 2.181 | 97.9 | 78.1 | 1399 | 22.41 | 5630.5 | 3057.2 | 2970 | 4373.9 | 1200.7 | 0.68257 | 6.31
2024-12-09 | 19:02 | Data | 0 | 32.453 | 29.746 | 200.697 | 7.62 | 188.299 | 2153.83 | 25.89 | 44.373 | 6.34 | 1.391 | 4.91 | 8680.41 | 2.376 | 97.9 | 77.9 | 1399 | 22.19 | 5642.3 | 3044.6 | 2962.2 | 4363.7 | 1200.7 | 0.68089 | 6.301
2024-12-09 | 19:02 | Data | 0 | 32.028 | 29.726 | 200.516 | 7.63 | 188.254 | 2156.54 | 25.9 | 44.825 | 6.34 | 1.386 | 4.914 | 8626.15 | 2.302 | 97.9 | 78 | 1402 | 22.41 | 5607 | 3052.2 | 2966.5 | 4368.4 | 1200.7 | 0.68268 | 6.3
2024-12-09 | 19:02 | Data | 0 | 32.035 | 29.955 | 200.697 | 7.63 | 188.299 | 2153.83 | 25.89 | 44.915 | 6.34 | 1.39 | 4.92 | 8621.63 | 2.086 | 97.9 | 78 | 1400 | 22.46 | 5604.1 | 3062.3 | 2939.2 | 4354.3 | 1200.7 | 0.68751 | 6.309
2024-12-09 | 19:02 | Data | 0 | 32.028 | 29.949 | 200.651 | 7.63 | 188.299 | 2152.93 | 25.89 | 44.915 | 6.34 | 1.391 | 4.919 | 8608.06 | 2.255 | 97.9 | 77.9 | 1399 | 22.46 | 5595.2 | 3039.4 | 2939.8 | 4341.5 | 1200.7 | 0.68381 | 6.31
2024-12-09 | 19:02 | Data | 0 | 32.251 | 29.969 | 200.606 | 7.63 | 188.299 | 2151.12 | 25.89 | 44.825 | 6.34 | 1.4 | 4.93 | 8608.06 | 2.255 | 97.9 | 77.9 | 1398 | 22.41 | 5595.2 | 3022.1 | 2934.8 | 4329 | 1200.7 | 0.68144 | 6.33
2024-12-09 | 19:02 | Data | 0 | 32.082 | 29.679 | 200.606 | 7.63 | 188.299 | 2149.31 | 25.89 | 44.915 | 6.34 | 1.389 | 4.938 | 8644.24 | 2.302 | 97.9 | 78.1 | 1397 | 22.41 | 5618.8 | 3036.5 | 2947.9 | 4349.5 | 1200.7 | 0.68214 | 6.326
2024-12-09 | 19:02 | Data | 0 | 31.913 | 29.868 | 200.697 | 7.63 | 188.299 | 2146.6 | 25.89 | 44.734 | 6.33 | 1.386 | 4.929 | 8644.24 | 2.356 | 97.9 | 78 | 1395 | 22.41 | 5618.8 | 3032.3 | 2948 | 4343.2 | 1200.7 | 0.68273 | 6.316
2024-12-09 | 19:02 | Data | 0 | 31.812 | 29.746 | 200.697 | 7.62 | 188.254 | 2151.12 | 25.89 | 44.915 | 6.33 | 1.395 | 4.922 | 8648.76 | 2.019 | 97.9 | 77.9 | 1398 | 22.41 | 5621.7 | 3053.1 | 2961.5 | 4364.5 | 1200.7 | 0.68369 | 6.317
2024-12-09 | 19:02 | Data | 0 | 32.028 | 29.726 | 200.742 | 7.63 | 188.39 | 2152.02 | 25.89 | 44.825 | 6.33 | 1.397 | 4.925 | 8648.76 | 2.302 | 97.9 | 77.9 | 1399 | 22.41 | 5621.7 | 3032 | 2951.6 | 4340.1 | 1200.7 | 0.68269 | 6.321
2024-12-09 | 19:02 | Data | 0 | 32.028 | 30.171 | 200.606 | 7.63 | 188.435 | 2149.31 | 25.89 | 44.825 | 6.34 | 1.383 | 4.932 | 8608.06 | 2.086 | 97.9 | 78.1 | 1398 | 22.41 | 5595.2 | 3037.9 | 2939 | 4337.3 | 1200.7 | 0.68409 | 6.314
2024-12-09 | 19:02 | Data | 0 | 31.812 | 29.699 | 200.47 | 7.63 | 188.299 | 2155.64 | 25.89 | 44.825 | 6.34 | 1.388 | 4.935 | 8621.63 | 2.241 | 97.9 | 78 | 1401 | 22.41 | 5604.1 | 3036.4 | 2972 | 4359.9 | 1200.7 | 0.6793 | 6.323
2024-12-09 | 19:02 | Data | 0 | 32.015 | 29.942 | 200.651 | 7.63 | 188.345 | 2153.83 | 25.89 | 44.825 | 6.33 | 1.392 | 4.938 | 8621.63 | 2.1 | 97.9 | 78 | 1401 | 22.41 | 5604.1 | 3034.8 | 2937.7 | 4337.3 | 1200.7 | 0.68276 | 6.33
2024-12-09 | 19:02 | Data | 0 | 31.853 | 29.557 | 200.606 | 7.63 | 188.39 | 2153.83 | 25.89 | 44.554 | 6.33 | 1.392 | 4.918 | 8608.06 | 2.201 | 97.9 | 78 | 1400 | 22.28 | 5595.2 | 3028.8 | 2925.1 | 4323.9 | 1200.7 | 0.68345 | 6.309
2024-12-09 | 19:02 | Data | 0 | 32.204 | 29.841 | 200.742 | 7.63 | 188.299 | 2146.6 | 25.9 | 44.644 | 6.34 | 1.39 | 4.901 | 8621.63 | 2.187 | 97.9 | 77.9 | 1396 | 22.28 | 5604.1 | 3034.9 | 2918.2 | 4323.7 | 1200.7 | 0.68493 | 6.291
2024-12-09 | 19:02 | Data | 0 | 31.974 | 29.935 | 200.697 | 7.63 | 188.39 | 2153.83 | 25.89 | 44.554 | 6.34 | 1.387 | 4.902 | 8621.63 | 2.262 | 97.9 | 77.9 | 1400 | 22.32 | 5604.1 | 3035.4 | 2901.6 | 4311.9 | 1200.7 | 0.68782 | 6.29
2024-12-09 | 19:02 | Data | 0 | 32.258 | 30.07 | 200.878 | 7.63 | 188.39 | 2146.6 | 25.89 | 44.644 | 6.34 | 1.382 | 4.89 | 8639.71 | 2.309 | 97.9 | 78 | 1395 | 22.32 | 5615.8 | 3028.3 | 2918 | 4319.4 | 1200.7 | 0.68404 | 6.272
2024-12-09 | 19:03 | Data | 0 | 32.352 | 29.955 | 200.651 | 7.63 | 188.39 | 2153.83 | 25.89 | 44.554 | 6.34 | 1.386 | 4.872 | 8626.15 | 2.478 | 97.9 | 77.8 | 1400 | 22.28 | 5607 | 3045 | 2902.3 | 4315.4 | 1200.7 | 0.69077 | 6.258
2024-12-09 | 19:03 | Data | 0 | 32.204 | 29.901 | 200.606 | 7.62 | 188.345 | 2143.89 | 25.89 | 44.554 | 6.34 | 1.39 | 4.908 | 8580.93 | 2.147 | 97.9 | 77.9 | 1394 | 22.28 | 5577.6 | 3043.9 | 2918.4 | 4322.9 | 1200.7 | 0.68825 | 6.297
2024-12-09 | 19:03 | Data | 0 | 32.001 | 29.834 | 200.561 | 7.63 | 188.299 | 2147.51 | 25.9 | 44.554 | 6.34 | 1.393 | 4.908 | 8603.54 | 2.282 | 97.9 | 77.9 | 1396 | 22.32 | 5592.3 | 3051.8 | 2947.2 | 4352.1 | 1200.7 | 0.68382 | 6.301
2024-12-09 | 19:03 | Data | 0 | 32.015 | 29.672 | 200.47 | 7.63 | 188.164 | 2146.6 | 25.89 | 44.644 | 6.35 | 1.387 | 4.927 | 8599.01 | 2.214 | 97.9 | 78 | 1396 | 22.32 | 5589.4 | 3012.7 | 2952.7 | 4331.7 | 1200.7 | 0.67916 | 6.315
2024-12-09 | 19:03 | Data | 0 | 32.136 | 29.955 | 200.697 | 7.63 | 188.345 | 2147.51 | 25.89 | 44.554 | 6.34 | 1.399 | 4.939 | 8635.19 | 2.248 | 97.9 | 77.9 | 1396 | 22.28 | 5612.9 | 3028.8 | 2967.6 | 4354.2 | 1200.7 | 0.67806 | 6.339
2024-12-09 | 19:03 | Data | 0 | 31.913 | 30.057 | 200.651 | 7.63 | 188.48 | 2148.41 | 25.89 | 44.554 | 6.34 | 1.4 | 4.912 | 8684.94 | 2.073 | 97.9 | 77.8 | 1396 | 22.28 | 5645.2 | 3019.1 | 2953.3 | 4343.4 | 1200.7 | 0.67681 | 6.312
2024-12-09 | 19:03 | Data | 0 | 32.15 | 29.672 | 200.742 | 7.63 | 188.525 | 2149.31 | 25.89 | 44.644 | 6.34 | 1.397 | 4.905 | 8309.59 | 2.41 | 97.9 | 77.8 | 1397 | 22.32 | 5401.2 | 3020 | 2932.5 | 4321.1 | 1200.7 | 0.68125 | 6.301
2024-12-09 | 19:03 | Data | 0 | 31.812 | 29.638 | 200.606 | 7.63 | 188.345 | 2152.02 | 25.89 | 44.464 | 6.34 | 1.387 | 4.925 | 8621.63 | 2.16 | 97.9 | 78 | 1399 | 22.28 | 5604.1 | 3028.5 | 2930.1 | 4322.2 | 1200.7 | 0.68469 | 6.313
2024-12-09 | 19:03 | Data | 0 | 31.799 | 29.726 | 200.606 | 7.62 | 188.299 | 2155.64 | 25.89 | 44.554 | 6.34 | 1.381 | 4.938 | 8644.24 | 2.275 | 97.9 | 78.1 | 1401 | 22.23 | 5618.8 | 3038.7 | 2933.6 | 4335.3 | 1200.7 | 0.68497 | 6.319
2024-12-09 | 19:03 | Data | 0 | 32.204 | 29.949 | 200.516 | 7.63 | 188.345 | 2153.83 | 25.89 | 44.644 | 6.34 | 1.394 | 4.92 | 8653.28 | 2.187 | 97.9 | 77.9 | 1400 | 22.32 | 5624.6 | 3037 | 2905.8 | 4313.9 | 1200.7 | 0.68871 | 6.312
2024-12-09 | 19:03 | Data | 0 | 32.399 | 29.996 | 200.742 | 7.63 | 188.435 | 2153.83 | 25.89 | 44.554 | 6.34 | 1.385 | 4.909 | 8630.67 | 2.316 | 97.9 | 78 | 1399 | 22.28 | 5609.9 | 3031.2 | 2903.7 | 4308.3 | 1200.7 | 0.68657 | 6.293
2024-12-09 | 19:03 | Data | 0 | 32.001 | 29.726 | 200.516 | 7.63 | 188.209 | 2155.64 | 25.9 | 44.554 | 6.34 | 1.387 | 4.933 | 8635.19 | 2.302 | 97.9 | 78 | 1400 | 22.32 | 5612.9 | 3033 | 2937 | 4333.7 | 1200.7 | 0.68308 | 6.321
2024-12-09 | 19:03 | Data | 0 | 32.028 | 30.165 | 200.742 | 7.63 | 188.39 | 2147.51 | 25.91 | 44.644 | 6.34 | 1.391 | 4.913 | 8648.76 | 2.241 | 97.9 | 77.9 | 1396 | 22.28 | 5621.7 | 3050.7 | 2949.6 | 4356.8 | 1200.7 | 0.68471 | 6.304
2024-12-09 | 19:03 | Data | 0 | 31.65 | 29.706 | 200.561 | 7.63 | 188.435 | 2147.51 | 25.89 | 44.644 | 6.34 | 1.395 | 4.901 | 8644.24 | 1.965 | 97.9 | 77.8 | 1396 | 22.28 | 5618.8 | 3040.8 | 2925.6 | 4326.1 | 1200.7 | 0.68528 | 6.296
2024-12-09 | 19:03 | Data | 0 | 31.805 | 29.699 | 200.516 | 7.62 | 188.254 | 2153.83 | 25.91 | 44.554 | 6.34 | 1.391 | 4.913 | 8648.76 | 2.248 | 97.9 | 77.9 | 1399 | 22.28 | 5621.7 | 3039.4 | 2948.9 | 4351.9 | 1200.7 | 0.68173 | 6.303
2024-12-09 | 19:03 | Data | 0 | 32.028 | 29.726 | 200.516 | 7.63 | 188.299 | 2151.12 | 25.91 | 44.554 | 6.34 | 1.379 | 4.946 | 8639.71 | 2.302 | 97.9 | 78.2 | 1399 | 22.28 | 5615.8 | 3044 | 3001.8 | 4382.4 | 1200.7 | 0.67889 | 6.325
2024-12-09 | 19:03 | Data | 0 | 32.345 | 30.165 | 200.697 | 7.63 | 188.39 | 2151.12 | 25.91 | 44.554 | 6.34 | 1.384 | 4.929 | 8639.71 | 2.289 | 97.9 | 78.1 | 1398 | 22.28 | 5615.8 | 3045.8 | 2986.7 | 4374.5 | 1200.7 | 0.67962 | 6.311
2024-12-09 | 19:03 | Data | 0 | 31.799 | 29.719 | 200.697 | 7.63 | 188.254 | 2151.12 | 25.91 | 44.554 | 6.34 | 1.387 | 4.903 | 8635.19 | 2.194 | 97.9 | 77.9 | 1398 | 22.28 | 5612.9 | 3047.9 | 2968.3 | 4364.6 | 1200.8 | 0.68063 | 6.291
2024-12-09 | 19:04 | Data | 0 | 32.143 | 29.739 | 200.651 | 7.62 | 188.345 | 2147.51 | 25.9 | 44.644 | 6.34 | 1.389 | 4.91 | 8657.8 | 2.16 | 97.9 | 78 | 1395 | 22.28 | 5627.6 | 3029 | 2962.1 | 4347.5 | 1200.8 | 0.68108 | 6.298
2024-12-09 | 19:04 | Data | 0 | 32.021 | 29.503 | 200.335 | 7.63 | 188.254 | 2147.51 | 25.91 | 44.554 | 6.34 | 1.392 | 4.913 | 8648.76 | 2.403 | 97.9 | 77.9 | 1396 | 22.28 | 5621.7 | 3028.9 | 2955.6 | 4342.8 | 1200.8 | 0.68101 | 6.305
2024-12-09 | 19:04 | Data | 0 | 31.826 | 29.719 | 200.561 | 7.63 | 188.254 | 2153.83 | 25.89 | 44.644 | 6.34 | 1.389 | 4.92 | 8648.76 | 2.113 | 97.9 | 78 | 1400 | 22.32 | 5621.7 | 3038.1 | 2962.1 | 4349.7 | 1200.8 | 0.68293 | 6.309
2024-12-09 | 19:04 | Data | 0 | 32.285 | 29.739 | 200.606 | 7.63 | 188.435 | 2149.31 | 25.89 | 44.554 | 6.34 | 1.389 | 4.932 | 8635.19 | 2.127 | 97.9 | 78 | 1397 | 22.28 | 5612.9 | 3038.7 | 2932.1 | 4335 | 1200.8 | 0.68439 | 6.322
2024-12-09 | 19:04 | Data | 0 | 32.001 | 29.726 | 200.561 | 7.63 | 188.254 | 2152.93 | 25.89 | 44.554 | 6.34 | 1.392 | 4.922 | 8626.15 | 2.289 | 97.9 | 78 | 1400 | 22.23 | 5607 | 3040.5 | 2943.2 | 4338.7 | 1200.8 | 0.6849 | 6.314
2024-12-09 | 19:04 | Data | 0 | 32.258 | 29.739 | 200.742 | 7.63 | 188.39 | 2145.7 | 25.9 | 44.644 | 6.34 | 1.385 | 4.924 | 8621.63 | 2.275 | 97.9 | 78.1 | 1395 | 22.28 | 5604.1 | 3029.8 | 2949.5 | 4341.4 | 1200.8 | 0.68162 | 6.31
2024-12-09 | 19:04 | Data | 0 | 32.028 | 30.043 | 200.561 | 7.63 | 188.345 | 2145.7 | 25.9 | 44.554 | 6.34 | 1.388 | 4.929 | 8621.63 | 2.187 | 97.9 | 78 | 1394 | 22.32 | 5604.1 | 3023.3 | 2949.5 | 4330.5 | 1200.8 | 0.68242 | 6.319
2024-12-09 | 19:04 | Data | 0 | 32.021 | 29.618 | 200.561 | 7.63 | 188.254 | 2144.79 | 25.89 | 44.554 | 6.34 | 1.393 | 4.911 | 8617.1 | 2.282 | 97.9 | 77.9 | 1394 | 22.32 | 5601.1 | 3013.1 | 2942.5 | 4325.8 | 1200.8 | 0.67939 | 6.304
2024-12-09 | 19:04 | Data | 0 | 31.812 | 29.706 | 200.561 | 7.63 | 188.254 | 2144.79 | 25.89 | 44.554 | 6.34 | 1.389 | 4.907 | 8635.19 | 2.113 | 97.9 | 77.9 | 1394 | 22.28 | 5612.9 | 3024.1 | 2934.6 | 4327.5 | 1200.8 | 0.68195 | 6.296
2024-12-09 | 19:04 | Data | 0 | 32.305 | 29.78 | 200.697 | 7.63 | 188.39 | 2142.08 | 25.89 | 44.464 | 6.34 | 1.38 | 4.919 | 8630.67 | 2.309 | 97.9 | 78.1 | 1393 | 22.28 | 5609.9 | 3036.4 | 2919.5 | 4318.9 | 1200.8 | 0.68435 | 6.299
2024-12-09 | 19:04 | Data | 0 | 32.015 | 29.564 | 200.651 | 7.63 | 188.299 | 2142.08 | 25.9 | 44.644 | 6.34 | 1.384 | 4.919 | 8653.28 | 2.289 | 97.9 | 78.1 | 1392 | 22.32 | 5624.6 | 3023 | 2919 | 4314 | 1200.8 | 0.68497 | 6.301
2024-12-09 | 19:04 | Data | 0 | 32.231 | 29.726 | 200.606 | 7.63 | 188.299 | 2142.08 | 25.89 | 44.825 | 6.34 | 1.386 | 4.913 | 8648.76 | 2.322 | 97.9 | 78 | 1392 | 22.41 | 5621.7 | 3044.7 | 2929.3 | 4335 | 1200.8 | 0.68221 | 6.301
2024-12-09 | 19:04 | Data | 0 | 32.237 | 29.955 | 200.697 | 7.63 | 188.345 | 2143.89 | 25.89 | 44.554 | 6.34 | 1.387 | 4.926 | 8648.76 | 2.302 | 97.9 | 78 | 1394 | 22.32 | 5621.7 | 3034.1 | 2937.3 | 4332.8 | 1200.8 | 0.68414 | 6.312
2024-12-09 | 19:04 | Data | 0 | 32.055 | 29.53 | 200.606 | 7.63 | 188.299 | 2142.08 | 25.89 | 44.554 | 6.34 | 1.392 | 4.944 | 8648.76 | 2.302 | 97.9 | 78 | 1393 | 22.28 | 5621.7 | 3028.4 | 2935.8 | 4330.4 | 1200.8 | 0.68332 | 6.336
2024-12-09 | 19:04 | Data | 0 | 32.015 | 29.699 | 200.606 | 7.63 | 188.299 | 2149.31 | 25.89 | 44.554 | 6.34 | 1.386 | 4.936 | 8648.76 | 2.518 | 97.9 | 78.1 | 1397 | 22.28 | 5621.7 | 3045.4 | 2972.4 | 4361.7 | 1200.8 | 0.68228 | 6.32
2024-12-09 | 19:04 | Data | 0 | 32.204 | 29.571 | 200.651 | 7.62 | 188.39 | 2151.12 | 25.89 | 44.554 | 6.34 | 1.385 | 4.91 | 8662.33 | 2.397 | 97.9 | 78 | 1398 | 22.32 | 5630.5 | 3038.8 | 2953.9 | 4347 | 1200.8 | 0.68367 | 6.294
2024-12-09 | 19:04 | Data | 0 | 32.021 | 29.726 | 200.516 | 7.63 | 188.254 | 2151.12 | 25.89 | 44.554 | 6.34 | 1.387 | 4.93 | 8693.98 | 2.302 | 97.9 | 78.1 | 1397 | 22.28 | 5651.1 | 3032.8 | 2958.7 | 4347.8 | 1200.8 | 0.68257 | 6.317
2024-12-09 | 19:04 | Data | 0 | 31.974 | 29.726 | 200.561 | 7.63 | 188.254 | 2149.31 | 25.89 | 44.825 | 6.34 | 1.39 | 4.948 | 8689.46 | 2.295 | 97.9 | 78.1 | 1397 | 22.41 | 5648.1 | 3018.5 | 2973 | 4346.5 | 1200.8 | 0.67966 | 6.338
2024-12-09 | 19:05 | Data | 0 | 32.19 | 29.841 | 200.561 | 7.63 | 188.299 | 2147.51 | 25.89 | 44.554 | 6.34 | 1.381 | 4.894 | 8716.59 | 2.417 | 97.9 | 78 | 1396 | 22.28 | 5665.8 | 3026 | 3010.4 | 4379.8 | 1200.8 | 0.67227 | 6.275
2024-12-09 | 19:05 | Data | 0 | 32.17 | 29.618 | 200.697 | 7.63 | 188.39 | 2149.31 | 25.89 | 44.825 | 6.34 | 1.391 | 4.914 | 8703.03 | 2.309 | 97.9 | 77.9 | 1397 | 22.37 | 5657 | 3038.4 | 3001 | 4382.8 | 1200.8 | 0.6754 | 6.304
2024-12-09 | 19:05 | Data | 0 | 31.805 | 29.699 | 200.47 | 7.63 | 188.299 | 2152.93 | 25.89 | 44.825 | 6.34 | 1.393 | 4.915 | 8689.46 | 2.1 | 97.9 | 77.9 | 1399 | 22.5 | 5648.1 | 3017.7 | 2993.3 | 4363.5 | 1200.8 | 0.67546 | 6.307
2024-12-09 | 19:05 | Data | 0 | 31.812 | 29.895 | 200.697 | 7.63 | 188.299 | 2153.83 | 25.9 | 44.554 | 6.34 | 1.387 | 4.905 | 8693.98 | 2.228 | 97.9 | 78 | 1400 | 22.32 | 5651.1 | 3035.1 | 3015.9 | 4391.9 | 1200.8 | 0.6745 | 6.292
2024-12-09 | 19:05 | Data | 0 | 31.913 | 29.726 | 200.742 | 7.63 | 188.345 | 2149.31 | 25.89 | 44.915 | 6.35 | 1.387 | 4.929 | 8689.46 | 2.295 | 97.9 | 78 | 1397 | 22.46 | 5648.1 | 3056 | 2995.8 | 4387 | 1200.8 | 0.6795 | 6.317
2024-12-09 | 19:05 | Data | 0 | 32.042 | 29.523 | 200.651 | 7.63 | 188.299 | 2158.35 | 25.89 | 44.915 | 6.34 | 1.38 | 4.929 | 8689.46 | 2.241 | 97.9 | 78.1 | 1403 | 22.41 | 5648.1 | 3019.1 | 2976.3 | 4351.8 | 1200.8 | 0.67679 | 6.31
2024-12-09 | 19:05 | Data | 0 | 32.021 | 29.618 | 200.606 | 7.62 | 188.39 | 2153.83 | 25.89 | 44.825 | 6.34 | 1.383 | 4.912 | 8689.46 | 2.41 | 97.9 | 78 | 1399 | 22.41 | 5648.1 | 3031 | 2975.8 | 4360.4 | 1200.8 | 0.68028 | 6.295
2024-12-09 | 19:05 | Data | 0 | 31.913 | 29.935 | 200.606 | 7.62 | 188.345 | 2155.64 | 25.89 | 44.825 | 6.34 | 1.386 | 4.91 | 8703.03 | 2.194 | 97.9 | 78 | 1402 | 22.41 | 5657 | 3034.3 | 2962.3 | 4350 | 1200.8 | 0.6805 | 6.297
2024-12-09 | 19:05 | Data | 0 | 31.913 | 29.928 | 200.787 | 7.63 | 188.39 | 2152.02 | 25.89 | 44.734 | 6.34 | 1.386 | 4.928 | 8703.03 | 2.187 | 97.9 | 78 | 1398 | 22.41 | 5657 | 3010.2 | 2982.2 | 4352.2 | 1200.8 | 0.67527 | 6.315
2024-12-09 | 19:05 | Data | 0 | 32.028 | 29.895 | 200.606 | 7.63 | 188.345 | 2156.54 | 25.89 | 44.825 | 6.34 | 1.38 | 4.934 | 8707.55 | 2.16 | 97.9 | 78.1 | 1402 | 22.37 | 5659.9 | 3046.7 | 2997.1 | 4384 | 1200.8 | 0.67783 | 6.314
2024-12-09 | 19:05 | Data | 0 | 32.102 | 29.631 | 200.651 | 7.63 | 188.435 | 2155.64 | 25.89 | 44.734 | 6.35 | 1.387 | 4.918 | 8662.33 | 2.208 | 97.9 | 78 | 1401 | 22.41 | 5630.5 | 3035.7 | 3020.2 | 4366.6 | 1200.8 | 0.67398 | 6.304
2024-12-09 | 19:05 | Data | 0 | 31.947 | 29.517 | 200.606 | 7.63 | 188.48 | 2157.45 | 25.9 | 44.825 | 6.34 | 1.389 | 4.905 | 8635.19 | 2.302 | 97.9 | 77.9 | 1402 | 22.46 | 5612.9 | 3035.8 | 3012.8 | 4398.6 | 1200.8 | 0.6759 | 6.295
2024-12-09 | 19:05 | Data | 0 | 32.129 | 29.726 | 200.697 | 7.63 | 188.345 | 2159.26 | 25.89 | 44.734 | 6.34 | 1.39 | 4.916 | 8635.19 | 2.194 | 97.9 | 78 | 1404 | 22.41 | 5612.9 | 3035.4 | 3016.1 | 4386.2 | 1200.8 | 0.67606 | 6.305
2024-12-09 | 19:05 | Data | 0 | 31.94 | 29.733 | 200.651 | 7.63 | 188.299 | 2161.97 | 25.89 | 44.825 | 6.34 | 1.392 | 4.91 | 8621.63 | 2.079 | 97.9 | 77.9 | 1405 | 22.41 | 5604.1 | 3036.2 | 2982.6 | 4369.9 | 1200.8 | 0.6759 | 6.302
2024-12-09 | 19:05 | Data | 0 | 32.028 | 29.557 | 200.651 | 7.62 | 188.299 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.384 | 4.925 | 8644.24 | 2.417 | 97.9 | 78.1 | 1405 | 22.28 | 5618.8 | 3050.8 | 3018.5 | 4400.4 | 1200.8 | 0.6769 | 6.31
2024-12-09 | 19:05 | Data | 0 | 31.947 | 29.726 | 200.787 | 7.63 | 188.345 | 2162.87 | 25.89 | 44.554 | 6.34 | 1.387 | 4.908 | 8648.76 | 2.086 | 97.9 | 78 | 1406 | 22.32 | 5621.7 | 3036.3 | 3005.7 | 4380.4 | 1200.8 | 0.67748 | 6.296
2024-12-09 | 19:05 | Data | 0 | 32.264 | 30.158 | 200.742 | 7.63 | 188.39 | 2163.77 | 25.89 | 44.734 | 6.34 | 1.396 | 4.905 | 8666.85 | 2.14 | 97.9 | 77.8 | 1406 | 22.41 | 5633.5 | 3025.9 | 2992.6 | 4374.9 | 1200.9 | 0.67668 | 6.301
2024-12-09 | 19:06 | Data | 0 | 31.846 | 29.699 | 200.742 | 7.63 | 188.39 | 2163.77 | 25.9 | 44.825 | 6.33 | 1.397 | 4.939 | 8662.33 | 2.14 | 97.9 | 77.9 | 1406 | 22.41 | 5630.5 | 3044.4 | 2939.7 | 4338.8 | 1200.9 | 0.68623 | 6.337
2024-12-09 | 19:06 | Data | 0 | 32.001 | 30.05 | 200.606 | 7.63 | 188.299 | 2158.35 | 25.9 | 44.825 | 6.34 | 1.398 | 4.929 | 8671.37 | 2.194 | 97.9 | 77.9 | 1404 | 22.41 | 5636.4 | 3032.2 | 2926.4 | 4323.8 | 1200.9 | 0.68466 | 6.327
2024-12-09 | 19:06 | Data | 0 | 32.352 | 29.807 | 200.742 | 7.63 | 188.435 | 2161.06 | 25.9 | 44.825 | 6.34 | 1.385 | 4.907 | 8671.37 | 2.41 | 97.9 | 78 | 1405 | 22.41 | 5636.4 | 3043.2 | 2957.4 | 4353.7 | 1200.9 | 0.68283 | 6.291
2024-12-09 | 19:06 | Data | 0 | 32.231 | 29.733 | 200.697 | 7.63 | 188.345 | 2163.77 | 25.89 | 44.825 | 6.34 | 1.387 | 4.912 | 8666.85 | 2.343 | 97.9 | 78 | 1406 | 22.41 | 5633.5 | 3032.3 | 2940.6 | 4335.6 | 1200.9 | 0.68152 | 6.3
2024-12-09 | 19:06 | Data | 0 | 32.028 | 29.726 | 200.697 | 7.62 | 188.299 | 2161.97 | 25.9 | 44.825 | 6.34 | 1.396 | 4.933 | 8671.37 | 2.295 | 97.9 | 77.9 | 1405 | 22.41 | 5636.4 | 3034 | 2975.5 | 4357.7 | 1200.9 | 0.68053 | 6.329
2024-12-09 | 19:06 | Data | 0 | 31.873 | 29.51 | 200.606 | 7.63 | 188.345 | 2161.06 | 25.89 | 44.825 | 6.34 | 1.384 | 4.929 | 8653.28 | 2.268 | 97.9 | 78.1 | 1405 | 22.41 | 5624.6 | 3049.1 | 3011.9 | 4394 | 1200.9 | 0.67812 | 6.313
2024-12-09 | 19:06 | Data | 0 | 32.197 | 29.888 | 200.697 | 7.63 | 188.435 | 2056.22 | 25.89 | 44.915 | 6.34 | 1.389 | 4.929 | 8653.28 | 2.295 | 97.8 | 78 | 1336 | 22.46 | 5624.6 | 3047.7 | 2996.5 | 4382.3 | 1200.9 | 0.6781 | 6.318
2024-12-09 | 19:06 | Data | 0 | 32.001 | 29.51 | 200.47 | 7.63 | 188.254 | 2161.06 | 25.89 | 44.644 | 6.34 | 1.387 | 4.929 | 8644.24 | 2.498 | 97.9 | 78 | 1405 | 22.28 | 5618.8 | 3034.9 | 3006.7 | 4382.8 | 1200.9 | 0.67556 | 6.316
2024-12-09 | 19:06 | Data | 0 | 31.859 | 29.51 | 200.606 | 7.62 | 188.299 | 2163.77 | 25.89 | 44.734 | 6.34 | 1.381 | 4.921 | 8653.28 | 2.235 | 97.9 | 78.1 | 1406 | 22.41 | 5624.6 | 3028.7 | 3015.3 | 4382.6 | 1200.9 | 0.67233 | 6.302
2024-12-09 | 19:06 | Data | 0 | 32.042 | 29.78 | 200.606 | 7.63 | 188.299 | 2163.77 | 25.89 | 44.554 | 6.34 | 1.389 | 4.939 | 8743.73 | 2.1 | 97.9 | 78 | 1406 | 22.28 | 5683.4 | 3037.6 | 3003 | 4381.5 | 1200.9 | 0.67678 | 6.328
2024-12-09 | 19:06 | Data | 0 | 32.015 | 29.955 | 200.561 | 7.63 | 188.299 | 2163.77 | 25.89 | 44.825 | 6.34 | 1.393 | 4.947 | 8856.78 | 2.194 | 97.9 | 78 | 1406 | 22.41 | 5756.9 | 3037.5 | 2994.9 | 4375.1 | 1200.9 | 0.67776 | 6.339
2024-12-09 | 19:06 | Data | 0 | 32.001 | 29.726 | 200.606 | 7.63 | 188.345 | 2163.77 | 25.89 | 44.734 | 6.34 | 1.395 | 4.933 | 8843.21 | 2.295 | 97.9 | 78 | 1406 | 22.41 | 5748.1 | 3021.5 | 2957.3 | 4339.1 | 1200.9 | 0.678 | 6.328
2024-12-09 | 19:06 | Data | 0 | 31.832 | 29.726 | 200.606 | 7.62 | 188.299 | 2161.06 | 25.89 | 44.644 | 6.34 | 1.388 | 4.919 | 8856.78 | 2.079 | 97.9 | 78 | 1405 | 22.32 | 5756.9 | 3033.1 | 2963.2 | 4359.8 | 1200.9 | 0.6787 | 6.307
2024-12-09 | 19:06 | Data | 0 | 31.819 | 29.53 | 200.651 | 7.63 | 188.435 | 2161.97 | 25.89 | 44.734 | 6.34 | 1.387 | 4.883 | 8861.3 | 2.187 | 97.9 | 77.9 | 1405 | 22.37 | 5759.8 | 3033.2 | 2958.1 | 4349.3 | 1200.9 | 0.68046 | 6.272
2024-12-09 | 19:06 | Data | 0 | 31.913 | 29.726 | 200.606 | 7.63 | 188.345 | 2161.97 | 25.9 | 44.915 | 6.34 | 1.396 | 4.903 | 8639.71 | 2.262 | 97.9 | 77.8 | 1405 | 22.41 | 5615.8 | 3054.2 | 2937.5 | 4337.5 | 1200.9 | 0.68538 | 6.3
2024-12-09 | 19:06 | Data | 0 | 31.913 | 29.726 | 200.47 | 7.62 | 188.299 | 2161.06 | 25.89 | 44.464 | 6.34 | 1.384 | 4.92 | 8662.33 | 2.248 | 97.9 | 78.1 | 1405 | 22.23 | 5630.5 | 3065.1 | 2949.6 | 4361.6 | 1200.9 | 0.68568 | 6.304
2024-12-09 | 19:06 | Data | 0 | 32.001 | 29.881 | 200.651 | 7.62 | 188.299 | 2163.77 | 25.89 | 44.915 | 6.34 | 1.382 | 4.929 | 8648.76 | 2.329 | 97.9 | 78.1 | 1406 | 22.41 | 5621.7 | 3043.2 | 2986.3 | 4372.8 | 1200.9 | 0.68157 | 6.311
2024-12-09 | 19:06 | Data | 0 | 31.792 | 29.719 | 200.516 | 7.63 | 188.254 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.381 | 4.92 | 8644.24 | 2.295 | 97.9 | 78.1 | 1404 | 22.28 | 5618.8 | 3031.1 | 2997 | 4382.6 | 1200.9 | 0.67783 | 6.301
2024-12-09 | 19:07 | Data | 0 | 31.832 | 29.841 | 200.561 | 7.63 | 188.39 | 2163.77 | 25.89 | 44.554 | 6.34 | 1.395 | 4.94 | 8671.37 | 2.295 | 97.9 | 78 | 1406 | 22.28 | 5636.4 | 3030.8 | 3000.8 | 4372.9 | 1200.9 | 0.67587 | 6.337
2024-12-09 | 19:07 | Data | 0 | 31.974 | 29.726 | 200.516 | 7.62 | 188.345 | 2163.77 | 25.89 | 44.464 | 6.34 | 1.387 | 4.937 | 8662.33 | 2.295 | 97.9 | 78.1 | 1406 | 22.32 | 5630.5 | 3047.3 | 2992.5 | 4380.8 | 1200.9 | 0.67851 | 6.323
2024-12-09 | 19:07 | Data | 0 | 31.826 | 29.672 | 200.561 | 7.63 | 188.39 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.38 | 4.922 | 8653.28 | 2.302 | 97.9 | 78.1 | 1405 | 22.28 | 5624.6 | 3026.3 | 3008.9 | 4391.4 | 1200.9 | 0.67327 | 6.304
2024-12-09 | 19:07 | Data | 0 | 31.988 | 29.908 | 200.742 | 7.63 | 188.48 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.388 | 4.94 | 8689.46 | 2.356 | 97.9 | 78.1 | 1405 | 22.28 | 5648.1 | 3034.5 | 3002.6 | 4384.6 | 1200.9 | 0.67637 | 6.328
2024-12-09 | 19:07 | Data | 0 | 32.21 | 29.739 | 200.697 | 7.62 | 188.48 | 2161.06 | 25.91 | 44.554 | 6.34 | 1.39 | 4.919 | 8630.67 | 2.397 | 97.9 | 78 | 1405 | 22.23 | 5609.9 | 3028.5 | 2961.5 | 4347.9 | 1200.9 | 0.68087 | 6.309
2024-12-09 | 19:07 | Data | 0 | 32.163 | 29.658 | 200.787 | 7.62 | 188.435 | 2161.97 | 25.89 | 44.644 | 6.34 | 1.385 | 4.917 | 8644.24 | 2.505 | 97.9 | 78 | 1405 | 22.28 | 5618.8 | 3043.4 | 2932.6 | 4335.8 | 1200.9 | 0.68283 | 6.301
2024-12-09 | 19:07 | Data | 0 | 32.136 | 29.834 | 200.561 | 7.63 | 188.254 | 2161.06 | 25.89 | 44.644 | 6.34 | 1.385 | 4.925 | 8630.67 | 2.417 | 97.9 | 78.1 | 1405 | 22.32 | 5609.9 | 3037.7 | 2942 | 4339.7 | 1200.9 | 0.68412 | 6.31
2024-12-09 | 19:07 | Data | 0 | 32.143 | 29.955 | 200.697 | 7.63 | 188.435 | 2161.06 | 25.89 | 44.644 | 6.34 | 1.388 | 4.926 | 8626.15 | 2.302 | 97.9 | 78 | 1405 | 22.28 | 5607 | 3030.3 | 2933 | 4330.2 | 1200.9 | 0.68443 | 6.314
2024-12-09 | 19:07 | Data | 0 | 32.332 | 29.733 | 200.787 | 7.63 | 188.48 | 2163.77 | 25.89 | 44.554 | 6.34 | 1.394 | 4.919 | 8635.19 | 2.133 | 97.9 | 77.9 | 1406 | 22.28 | 5612.9 | 3026 | 2931.3 | 4324.4 | 1200.9 | 0.68295 | 6.312
2024-12-09 | 19:07 | Data | 0 | 32.237 | 30.063 | 200.606 | 7.63 | 188.345 | 2164.68 | 25.89 | 44.554 | 6.34 | 1.386 | 4.93 | 8630.67 | 2.1 | 97.9 | 78.1 | 1406 | 22.28 | 5609.9 | 3032.6 | 2957.7 | 4349.4 | 1200.9 | 0.68101 | 6.317
2024-12-09 | 19:07 | Data | 0 | 31.994 | 29.726 | 200.697 | 7.63 | 188.435 | 2161.06 | 25.89 | 44.464 | 6.34 | 1.391 | 4.914 | 8635.19 | 2.329 | 97.9 | 77.9 | 1405 | 22.32 | 5612.9 | 3044.8 | 2990.3 | 4376.9 | 1200.9 | 0.67965 | 6.304
2024-12-09 | 19:07 | Data | 0 | 32.366 | 29.53 | 200.697 | 7.63 | 188.525 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.39 | 4.897 | 8635.19 | 2.356 | 97.9 | 77.9 | 1405 | 22.28 | 5612.9 | 3055.4 | 3014.7 | 4403.5 | 1200.9 | 0.67692 | 6.287
2024-12-09 | 19:07 | Data | 0 | 32.028 | 29.928 | 200.561 | 7.63 | 188.299 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.38 | 4.901 | 8648.76 | 2.221 | 97.9 | 78 | 1405 | 22.28 | 5621.7 | 3050.2 | 3020.8 | 4401.9 | 1200.9 | 0.67678 | 6.281
2024-12-09 | 19:07 | Data | 0 | 32.021 | 29.726 | 200.561 | 7.63 | 188.345 | 2161.97 | 25.89 | 44.554 | 6.34 | 1.395 | 4.914 | 8662.33 | 2.187 | 97.9 | 77.9 | 1405 | 22.32 | 5630.5 | 3014.1 | 3000.4 | 4368.3 | 1200.9 | 0.67376 | 6.31
2024-12-09 | 19:07 | Data | 0 | 32.028 | 30.09 | 200.697 | 7.62 | 188.435 | 2161.97 | 25.9 | 44.554 | 6.34 | 1.391 | 4.895 | 8648.76 | 2.201 | 97.9 | 77.9 | 1406 | 22.28 | 5621.7 | 3055.8 | 2983.1 | 4379.2 | 1200.9 | 0.68103 | 6.286
2024-12-09 | 19:07 | Data | 0 | 32.089 | 29.753 | 200.606 | 7.63 | 188.345 | 2156.54 | 25.89 | 44.644 | 6.33 | 1.386 | 4.89 | 8662.33 | 2.268 | 97.9 | 77.9 | 1402 | 22.32 | 5630.5 | 3041.2 | 2957.7 | 4343.7 | 1200.9 | 0.67889 | 6.274
2024-12-09 | 19:07 | Data | 0 | 32.028 | 29.928 | 200.697 | 7.63 | 188.345 | 2167.39 | 25.89 | 44.554 | 6.34 | 1.391 | 4.916 | 8671.37 | 2.302 | 97.9 | 77.9 | 1409 | 22.28 | 5636.4 | 3029.8 | 2947.3 | 4341.3 | 1201 | 0.67997 | 6.307
2024-12-09 | 19:08 | Data | 0 | 32.264 | 30.063 | 200.697 | 7.63 | 188.48 | 2163.77 | 25.9 | 44.554 | 6.34 | 1.392 | 4.898 | 8698.5 | 2.14 | 97.9 | 77.9 | 1406 | 22.32 | 5654 | 3039 | 2947.4 | 4344.3 | 1201 | 0.6827 | 6.29
2024-12-09 | 19:08 | Data | 0 | 32.102 | 29.733 | 200.651 | 7.62 | 188.435 | 2163.77 | 25.9 | 44.554 | 6.34 | 1.385 | 4.927 | 8693.98 | 2.093 | 97.9 | 78.1 | 1406 | 22.32 | 5651.1 | 3025.9 | 2955 | 4341.1 | 1201 | 0.67963 | 6.311
2024-12-09 | 19:08 | Data | 0 | 32.143 | 29.773 | 200.606 | 7.62 | 188.345 | 2161.06 | 25.89 | 44.644 | 6.34 | 1.381 | 4.918 | 8680.41 | 2.127 | 97.9 | 78.1 | 1405 | 22.32 | 5642.3 | 3040.2 | 2992.2 | 4378.1 | 1201 | 0.67767 | 6.299
2024-12-09 | 19:08 | Data | 0 | 32.183 | 30.144 | 200.742 | 7.62 | 188.435 | 2158.35 | 25.89 | 44.644 | 6.34 | 1.377 | 4.899 | 8680.41 | 2.174 | 97.9 | 78.1 | 1403 | 22.32 | 5642.3 | 3052.1 | 2972.2 | 4363.7 | 1201 | 0.6831 | 6.276
2024-12-09 | 19:08 | Data | 0 | 31.805 | 29.895 | 200.651 | 7.63 | 188.345 | 2158.35 | 25.89 | 44.554 | 6.34 | 1.385 | 4.913 | 8671.37 | 2.174 | 97.9 | 78 | 1404 | 22.23 | 5636.4 | 3039.6 | 2978.4 | 4362 | 1201 | 0.67983 | 6.298
2024-12-09 | 19:08 | Data | 0 | 32.305 | 29.955 | 200.606 | 7.62 | 188.435 | 2158.35 | 25.89 | 44.554 | 6.34 | 1.395 | 4.925 | 8689.46 | 2.316 | 97.9 | 77.9 | 1404 | 22.28 | 5648.1 | 3051.1 | 2991 | 4387.9 | 1201 | 0.67827 | 6.32
2024-12-09 | 19:08 | Data | 0 | 32.028 | 29.726 | 200.651 | 7.62 | 188.345 | 2155.64 | 25.9 | 44.554 | 6.34 | 1.391 | 4.918 | 8693.98 | 2.302 | 97.9 | 78 | 1402 | 22.28 | 5651.1 | 3040.7 | 2976.4 | 4363.4 | 1201 | 0.67933 | 6.309
2024-12-09 | 19:08 | Data | 0 | 32.129 | 29.841 | 200.561 | 7.62 | 188.299 | 2158.35 | 25.89 | 44.554 | 6.34 | 1.381 | 4.91 | 8680.41 | 2.471 | 97.9 | 78 | 1404 | 22.28 | 5642.3 | 3028.5 | 2978 | 4355.7 | 1201 | 0.67893 | 6.293
2024-12-09 | 19:08 | Data | 0 | 32.042 | 29.78 | 200.697 | 7.63 | 188.39 | 2161.97 | 25.9 | 44.825 | 6.34 | 1.387 | 4.935 | 8689.46 | 2.086 | 97.9 | 78.1 | 1405 | 22.46 | 5648.1 | 3035.7 | 2971.4 | 4362.1 | 1201 | 0.67974 | 6.322
2024-12-09 | 19:08 | Data | 0 | 32.561 | 29.854 | 200.787 | 7.62 | 188.525 | 2161.97 | 25.89 | 44.554 | 6.34 | 1.383 | 4.939 | 8693.98 | 2.586 | 97.9 | 78.1 | 1405 | 22.28 | 5651.1 | 3039.9 | 2963.7 | 4358.9 | 1201 | 0.68198 | 6.323
2024-12-09 | 19:08 | Data | 0 | 31.805 | 29.726 | 200.516 | 7.62 | 188.345 | 2162.87 | 25.89 | 44.554 | 6.34 | 1.39 | 4.917 | 8693.98 | 2.079 | 97.9 | 78 | 1406 | 22.28 | 5651.1 | 3023.7 | 2961.2 | 4343.8 | 1201 | 0.67877 | 6.308
2024-12-09 | 19:08 | Data | 0 | 32.17 | 29.787 | 200.787 | 7.63 | 188.435 | 2161.97 | 25.9 | 44.554 | 6.34 | 1.395 | 4.924 | 8716.59 | 2.147 | 97.9 | 77.9 | 1405 | 22.28 | 5665.8 | 3056.9 | 2943.6 | 4352 | 1201 | 0.68657 | 6.319
2024-12-09 | 19:08 | Data | 0 | 31.799 | 29.726 | 200.606 | 7.63 | 188.345 | 2158.35 | 25.89 | 44.554 | 6.34 | 1.385 | 4.947 | 8712.07 | 2.275 | 97.9 | 78.1 | 1404 | 22.28 | 5662.8 | 3052.2 | 2944.3 | 4350.4 | 1201 | 0.68473 | 6.33
2024-12-09 | 19:08 | Data | 0 | 32.028 | 29.726 | 200.697 | 7.63 | 188.39 | 2159.26 | 25.89 | 44.644 | 6.34 | 1.393 | 4.92 | 8698.5 | 2.289 | 97.9 | 77.9 | 1403 | 22.32 | 5654 | 3053 | 2939.1 | 4347.1 | 1201 | 0.68619 | 6.312
2024-12-09 | 19:08 | Data | 0 | 32.204 | 30.158 | 200.742 | 7.62 | 188.39 | 2158.35 | 25.89 | 44.554 | 6.34 | 1.393 | 4.892 | 8716.59 | 2.295 | 97.9 | 77.9 | 1403 | 22.28 | 5665.8 | 3046.8 | 2946.7 | 4347.9 | 1201 | 0.68342 | 6.284
2024-12-09 | 19:08 | Data | 0 | 31.913 | 29.841 | 200.697 | 7.63 | 188.39 | 2159.26 | 25.91 | 44.644 | 6.34 | 1.386 | 4.92 | 8716.59 | 2.201 | 97.9 | 78 | 1404 | 22.32 | 5665.8 | 3040 | 2961.8 | 4355.4 | 1201 | 0.68003 | 6.306
2024-12-09 | 19:08 | Data | 0 | 32.487 | 29.746 | 200.832 | 7.63 | 188.435 | 2161.97 | 25.89 | 44.464 | 6.34 | 1.394 | 4.931 | 8716.59 | 2.376 | 97.9 | 78 | 1405 | 22.28 | 5665.8 | 3030.4 | 2979.5 | 4359.1 | 1201 | 0.67803 | 6.325
2024-12-09 | 19:08 | Data | 0 | 32.318 | 29.753 | 200.742 | 7.63 | 188.435 | 2158.35 | 25.89 | 44.554 | 6.34 | 1.4 | 4.887 | 8716.59 | 2.356 | 97.9 | 77.7 | 1403 | 22.28 | 5665.8 | 3036.9 | 2961.1 | 4349.7 | 1201 | 0.68115 | 6.287
2024-12-09 | 19:09 | Data | 0 | 31.913 | 29.922 | 200.651 | 7.63 | 188.299 | 2158.35 | 25.89 | 44.554 | 6.34 | 1.395 | 4.91 | 8730.16 | 2.248 | 97.9 | 77.9 | 1404 | 22.32 | 5674.6 | 3046.1 | 3005.3 | 4389.1 | 1201 | 0.67739 | 6.305
2024-12-09 | 19:09 | Data | 0 | 32.15 | 30.165 | 200.742 | 7.63 | 188.435 | 2158.35 | 25.89 | 44.644 | 6.34 | 1.389 | 4.926 | 8730.16 | 2.268 | 97.9 | 78 | 1403 | 22.28 | 5674.6 | 3046.4 | 3016.4 | 4396.3 | 1201 | 0.6764 | 6.315
2024-12-09 | 19:09 | Data | 0 | 32.035 | 29.942 | 200.697 | 7.63 | 188.435 | 2158.35 | 25.9 | 44.554 | 6.34 | 1.388 | 4.915 | 8698.5 | 2.127 | 97.9 | 78 | 1403 | 22.28 | 5654 | 3019.9 | 2979.1 | 4354 | 1201 | 0.67513 | 6.303
2024-12-09 | 19:09 | Data | 0 | 32.487 | 29.982 | 200.787 | 7.63 | 188.435 | 2159.26 | 25.9 | 44.554 | 6.34 | 1.395 | 4.92 | 8716.59 | 2.309 | 97.9 | 77.9 | 1404 | 22.28 | 5665.8 | 3041.7 | 2989.1 | 4377.8 | 1201 | 0.6778 | 6.314
2024-12-09 | 19:09 | Data | 0 | 32.352 | 30.063 | 200.742 | 7.63 | 188.39 | 2156.54 | 25.89 | 44.554 | 6.34 | 1.388 | 4.91 | 8730.16 | 2.41 | 97.9 | 78 | 1402 | 22.28 | 5674.6 | 3047.6 | 2980.9 | 4370.9 | 1201 | 0.68063 | 6.299
2024-12-09 | 19:09 | Data | 0 | 32.028 | 29.928 | 200.697 | 7.63 | 188.39 | 2159.26 | 25.9 | 44.644 | 6.34 | 1.396 | 4.912 | 8734.68 | 2.1 | 97.9 | 77.9 | 1404 | 22.28 | 5677.5 | 3048.8 | 2969 | 4368.3 | 1201 | 0.68203 | 6.309
2024-12-09 | 19:09 | Data | 0 | 32.42 | 29.868 | 200.878 | 7.63 | 188.48 | 2153.83 | 25.89 | 44.644 | 6.34 | 1.395 | 4.915 | 8707.55 | 2.309 | 97.9 | 77.9 | 1400 | 22.28 | 5659.9 | 3037.2 | 2969.1 | 4359.1 | 1201 | 0.67844 | 6.31
2024-12-09 | 19:09 | Data | 0 | 32.062 | 29.841 | 200.787 | 7.62 | 188.435 | 2159.26 | 25.9 | 44.644 | 6.34 | 1.394 | 4.911 | 8716.59 | 2.127 | 97.9 | 77.9 | 1403 | 22.32 | 5665.8 | 3039.4 | 2937.1 | 4335.6 | 1201 | 0.68367 | 6.306
2024-12-09 | 19:09 | Data | 0 | 32.028 | 29.571 | 200.787 | 7.62 | 188.435 | 2159.26 | 25.89 | 44.554 | 6.35 | 1.385 | 4.909 | 8712.07 | 2.133 | 97.9 | 78 | 1404 | 22.23 | 5662.8 | 3026.2 | 2951.6 | 4336.9 | 1201 | 0.68111 | 6.293
2024-12-09 | 19:09 | Data | 0 | 31.859 | 29.726 | 200.561 | 7.63 | 188.345 | 2160.16 | 25.9 | 44.554 | 6.34 | 1.388 | 4.935 | 8725.64 | 2.079 | 97.9 | 78 | 1404 | 22.28 | 5671.7 | 3016.3 | 2948.6 | 4328.8 | 1201 | 0.6803 | 6.323
2024-12-09 | 19:09 | Data | 0 | 32.48 | 29.895 | 200.787 | 7.63 | 188.435 | 2159.26 | 25.89 | 44.644 | 6.34 | 1.39 | 4.91 | 8707.55 | 2.248 | 97.9 | 77.9 | 1404 | 22.28 | 5659.9 | 3019.2 | 2960.2 | 4337.4 | 1201 | 0.67975 | 6.301
2024-12-09 | 19:09 | Data | 0 | 31.974 | 29.841 | 200.651 | 7.63 | 188.39 | 2157.45 | 25.89 | 44.554 | 6.34 | 1.388 | 4.907 | 8707.55 | 2.295 | 97.9 | 77.9 | 1402 | 22.28 | 5659.9 | 3019.3 | 2965.7 | 4345.1 | 1201 | 0.67745 | 6.295
2024-12-09 | 19:09 | Data | 0 | 32.204 | 29.868 | 200.742 | 7.63 | 188.48 | 2159.26 | 25.89 | 44.464 | 6.34 | 1.392 | 4.92 | 8707.55 | 2.471 | 97.9 | 78 | 1404 | 22.32 | 5659.9 | 3012.2 | 2957.4 | 4331.6 | 1201 | 0.67914 | 6.311
2024-12-09 | 19:09 | Data | 0 | 32.264 | 30.273 | 200.923 | 7.63 | 188.39 | 2158.35 | 25.9 | 44.554 | 6.35 | 1.393 | 4.905 | 8698.5 | 2.106 | 97.9 | 77.9 | 1404 | 22.28 | 5654 | 3026.9 | 2969.9 | 4345.3 | 1201 | 0.68013 | 6.298
2024-12-09 | 19:09 | Data | 0 | 31.832 | 29.726 | 200.606 | 7.63 | 188.345 | 2158.35 | 25.89 | 44.554 | 6.34 | 1.388 | 4.925 | 8743.73 | 2.086 | 97.9 | 78 | 1403 | 22.28 | 5683.4 | 3059.2 | 3002.6 | 4397.9 | 1201 | 0.67982 | 6.313
2024-12-09 | 19:09 | Data | 0 | 32.359 | 29.787 | 200.697 | 7.63 | 188.525 | 2158.35 | 25.89 | 44.915 | 6.34 | 1.384 | 4.942 | 8748.25 | 2.349 | 97.9 | 78.1 | 1403 | 22.41 | 5686.4 | 3029 | 2981.4 | 4363.4 | 1201 | 0.67896 | 6.324
2024-12-09 | 19:09 | Data | 0 | 32.244 | 30.057 | 200.697 | 7.63 | 188.39 | 2159.26 | 25.89 | 44.554 | 6.34 | 1.393 | 4.938 | 8761.81 | 2.208 | 97.9 | 78 | 1403 | 22.28 | 5695.2 | 3033.9 | 2980 | 4364.4 | 1201.1 | 0.67901 | 6.332
2024-12-09 | 19:09 | Data | 0 | 32.258 | 29.76 | 200.787 | 7.63 | 188.48 | 2158.35 | 25.89 | 44.915 | 6.34 | 1.39 | 4.93 | 8739.2 | 2.329 | 97.9 | 78 | 1404 | 22.41 | 5680.5 | 3028.9 | 2977.5 | 4358.5 | 1201.1 | 0.6777 | 6.32
2024-12-09 | 19:10 | Data | 0 | 31.988 | 29.841 | 200.832 | 7.63 | 188.345 | 2158.35 | 25.89 | 44.554 | 6.34 | 1.392 | 4.935 | 8730.16 | 2.086 | 97.9 | 78 | 1403 | 22.28 | 5674.6 | 3023.3 | 2984.6 | 4358.4 | 1201.1 | 0.67708 | 6.326
2024-12-09 | 19:10 | Data | 0 | 32.028 | 30.043 | 200.606 | 7.62 | 188.345 | 2152.93 | 25.91 | 44.554 | 6.34 | 1.388 | 4.908 | 8730.16 | 2.106 | 97.9 | 78 | 1399 | 22.28 | 5674.6 | 3048.3 | 2988.6 | 4381.1 | 1201.1 | 0.67917 | 6.295
2024-12-09 | 19:10 | Data | 0 | 32.487 | 29.766 | 200.697 | 7.63 | 188.48 | 2158.35 | 25.91 | 44.283 | 6.34 | 1.383 | 4.9 | 8743.73 | 2.424 | 97.9 | 78 | 1404 | 22.14 | 5683.4 | 3037 | 2932.9 | 4330.9 | 1201.1 | 0.68381 | 6.282
2024-12-09 | 19:10 | Data | 0 | 32.042 | 30.111 | 200.742 | 7.63 | 188.345 | 2158.35 | 25.9 | 44.644 | 6.34 | 1.387 | 4.932 | 8748.25 | 2.133 | 97.9 | 78 | 1403 | 22.28 | 5686.4 | 3034.5 | 2979.4 | 4361.6 | 1201.1 | 0.6801 | 6.32
2024-12-09 | 19:10 | Data | 0 | 32.028 | 29.928 | 200.606 | 7.62 | 188.345 | 2158.35 | 25.89 | 44.554 | 6.34 | 1.391 | 4.925 | 8707.55 | 2.127 | 97.9 | 78 | 1403 | 22.28 | 5659.9 | 3036.4 | 2969 | 4359.3 | 1201.1 | 0.67977 | 6.315
2024-12-09 | 19:10 | Data | 0 | 32.028 | 29.949 | 200.697 | 7.63 | 188.39 | 2161.06 | 25.89 | 44.644 | 6.34 | 1.395 | 4.92 | 8684.94 | 2.262 | 97.9 | 77.9 | 1405 | 22.28 | 5645.2 | 3024.1 | 2954.5 | 4339.6 | 1201.1 | 0.68008 | 6.316
2024-12-09 | 19:10 | Data | 0 | 31.974 | 29.766 | 200.561 | 7.63 | 188.299 | 2161.06 | 25.89 | 44.554 | 6.35 | 1.395 | 4.928 | 8703.03 | 2.464 | 97.9 | 77.9 | 1405 | 22.32 | 5657 | 3030.9 | 2940.4 | 4331 | 1201.1 | 0.68441 | 6.323
2024-12-09 | 19:10 | Data | 0 | 31.799 | 29.895 | 200.606 | 7.63 | 188.254 | 2165.58 | 25.89 | 44.644 | 6.34 | 1.395 | 4.947 | 8689.46 | 2.093 | 97.9 | 78 | 1408 | 22.28 | 5648.1 | 3029.6 | 2953.7 | 4344.8 | 1201.1 | 0.68073 | 6.341
2024-12-09 | 19:10 | Data | 0 | 32.089 | 29.746 | 200.787 | 7.63 | 188.48 | 2166.49 | 25.91 | 44.554 | 6.34 | 1.395 | 4.916 | 8680.41 | 2.275 | 97.9 | 77.9 | 1408 | 22.28 | 5642.3 | 3027.9 | 2972.7 | 4356.1 | 1201.1 | 0.67838 | 6.312
2024-12-09 | 19:10 | Data | 0 | 32.028 | 30.036 | 200.787 | 7.63 | 188.39 | 2165.58 | 25.9 | 44.554 | 6.34 | 1.393 | 4.91 | 8680.41 | 2.086 | 97.9 | 77.9 | 1408 | 22.28 | 5642.3 | 3032.5 | 2981.7 | 4365.3 | 1201.1 | 0.67869 | 6.302
2024-12-09 | 19:10 | Data | 0 | 32.15 | 30.144 | 200.651 | 7.63 | 188.435 | 2163.77 | 25.89 | 44.554 | 6.34 | 1.392 | 4.9 | 8662.33 | 2.187 | 97.9 | 77.9 | 1406 | 22.32 | 5630.5 | 3026.4 | 2992.4 | 4366.6 | 1201.1 | 0.67571 | 6.292
2024-12-09 | 19:10 | Data | 0 | 32.629 | 29.881 | 200.697 | 7.62 | 188.48 | 2161.97 | 25.89 | 45.005 | 6.34 | 1.381 | 4.902 | 8666.85 | 2.417 | 97.9 | 78 | 1405 | 22.5 | 5633.5 | 3050.6 | 2992 | 4385.2 | 1201.1 | 0.67754 | 6.283
2024-12-09 | 19:10 | Data | 0 | 32.318 | 30.205 | 200.651 | 7.63 | 188.48 | 2160.16 | 25.89 | 44.554 | 6.34 | 1.385 | 4.93 | 8671.37 | 2.086 | 97.9 | 78.1 | 1404 | 22.28 | 5636.4 | 3032.4 | 3003.3 | 4377.9 | 1201.1 | 0.67677 | 6.315
2024-12-09 | 19:10 | Data | 0 | 32.028 | 29.949 | 200.742 | 7.63 | 188.39 | 2161.06 | 25.89 | 44.644 | 6.34 | 1.382 | 4.929 | 8693.98 | 2.079 | 97.9 | 78.1 | 1405 | 22.28 | 5651.1 | 3028 | 2964.8 | 4342.5 | 1201.1 | 0.67838 | 6.31
2024-12-09 | 19:10 | Data | 0 | 32.224 | 29.915 | 200.697 | 7.63 | 188.435 | 2161.06 | 25.9 | 44.554 | 6.34 | 1.379 | 4.933 | 8684.94 | 2.322 | 97.9 | 78.1 | 1405 | 22.28 | 5645.2 | 3027.9 | 2970.4 | 4352.5 | 1201.1 | 0.67889 | 6.312
2024-12-09 | 19:10 | Data | 0 | 32.028 | 29.841 | 200.606 | 7.63 | 188.39 | 2161.06 | 25.89 | 44.644 | 6.34 | 1.383 | 4.934 | 8693.98 | 2.302 | 97.9 | 78.1 | 1405 | 22.28 | 5651.1 | 3022.1 | 2961.9 | 4345.2 | 1201.1 | 0.67957 | 6.317
2024-12-09 | 19:10 | Data | 0 | 32.204 | 30.205 | 200.651 | 7.63 | 188.39 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.388 | 4.908 | 8698.5 | 2.194 | 97.9 | 78 | 1405 | 22.28 | 5654 | 3047 | 2966 | 4354.1 | 1201.1 | 0.68218 | 6.296
2024-12-09 | 19:10 | Data | 0 | 32.46 | 29.793 | 200.832 | 7.63 | 188.48 | 2161.06 | 25.89 | 44.464 | 6.34 | 1.394 | 4.908 | 8707.55 | 2.356 | 97.9 | 77.9 | 1405 | 22.28 | 5659.9 | 3031.3 | 2936.5 | 4335.2 | 1201.1 | 0.68354 | 6.301
2024-12-09 | 19:11 | Data | 0 | 32.028 | 30.057 | 200.878 | 7.63 | 188.48 | 2161.97 | 25.9 | 44.734 | 6.34 | 1.392 | 4.918 | 8703.03 | 2.221 | 97.9 | 77.9 | 1405 | 22.32 | 5657 | 3035 | 2970.2 | 4354.2 | 1201.1 | 0.68139 | 6.31
2024-12-09 | 19:11 | Data | 0 | 31.805 | 29.611 | 200.742 | 7.63 | 188.345 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.388 | 4.928 | 8689.46 | 2.41 | 97.9 | 78 | 1405 | 22.32 | 5648.1 | 3038 | 2971.3 | 4360.6 | 1201.1 | 0.68026 | 6.317
2024-12-09 | 19:11 | Data | 0 | 31.819 | 29.712 | 200.651 | 7.62 | 188.435 | 2163.77 | 25.89 | 44.825 | 6.34 | 1.392 | 4.907 | 8662.33 | 2.12 | 97.9 | 77.9 | 1406 | 22.41 | 5630.5 | 3058.7 | 2979.9 | 4379.5 | 1201.1 | 0.6824 | 6.299
2024-12-09 | 19:11 | Data | 0 | 32.264 | 29.949 | 200.787 | 7.62 | 188.571 | 2163.77 | 25.9 | 44.825 | 6.34 | 1.39 | 4.888 | 8662.33 | 2.316 | 97.9 | 77.9 | 1407 | 22.41 | 5630.5 | 3024.7 | 2997.7 | 4366.5 | 1201.1 | 0.67701 | 6.278
2024-12-09 | 19:11 | Data | 0 | 32.156 | 29.625 | 200.742 | 7.63 | 188.48 | 2158.35 | 25.89 | 44.644 | 6.34 | 1.39 | 4.92 | 8648.76 | 2.167 | 97.9 | 78 | 1402 | 22.28 | 5621.7 | 3029.4 | 3000.5 | 4373.1 | 1201.1 | 0.6765 | 6.31
2024-12-09 | 19:11 | Data | 0 | 32.028 | 29.841 | 200.697 | 7.62 | 188.435 | 2162.87 | 25.89 | 44.554 | 6.34 | 1.381 | 4.897 | 8648.76 | 2.181 | 97.9 | 78 | 1406 | 22.28 | 5621.7 | 3046.7 | 3005.7 | 4386.1 | 1201.1 | 0.67853 | 6.279
2024-12-09 | 19:11 | Data | 0 | 32.177 | 29.955 | 200.832 | 7.62 | 188.525 | 2159.26 | 25.89 | 44.825 | 6.35 | 1.387 | 4.916 | 8648.76 | 2.086 | 97.9 | 78 | 1404 | 22.41 | 5621.7 | 3021.8 | 2991.8 | 4375 | 1201.1 | 0.67767 | 6.303
2024-12-09 | 19:11 | Data | 0 | 32.46 | 30.016 | 200.787 | 7.63 | 188.48 | 2166.49 | 25.89 | 44.825 | 6.34 | 1.388 | 4.907 | 8671.37 | 2.403 | 97.9 | 77.9 | 1408 | 22.41 | 5636.4 | 3038.3 | 2991 | 4374.4 | 1201.1 | 0.67823 | 6.295
2024-12-09 | 19:11 | Data | 0 | 31.934 | 30.165 | 200.742 | 7.63 | 188.48 | 2159.26 | 25.9 | 44.825 | 6.34 | 1.393 | 4.92 | 8662.33 | 2.289 | 97.9 | 77.9 | 1404 | 22.37 | 5630.5 | 3038 | 2977.5 | 4365.2 | 1201.1 | 0.67724 | 6.314
2024-12-09 | 19:11 | Data | 0 | 32.17 | 29.962 | 200.923 | 7.62 | 188.525 | 2155.64 | 25.89 | 44.825 | 6.34 | 1.388 | 4.925 | 8657.8 | 2.1 | 97.9 | 78 | 1401 | 22.37 | 5627.6 | 3029.2 | 2975.5 | 4358.2 | 1201.1 | 0.67815 | 6.312
2024-12-09 | 19:11 | Data | 0 | 32.487 | 29.854 | 200.742 | 7.63 | 188.48 | 2156.54 | 25.9 | 44.915 | 6.34 | 1.389 | 4.912 | 8657.8 | 2.363 | 97.9 | 78 | 1402 | 22.41 | 5627.6 | 3038.7 | 2961.8 | 4352.5 | 1201.1 | 0.68145 | 6.301
2024-12-09 | 19:11 | Data | 0 | 32.008 | 29.955 | 200.878 | 7.62 | 188.571 | 2155.64 | 25.89 | 44.734 | 6.34 | 1.395 | 4.895 | 8648.76 | 2.187 | 97.9 | 77.8 | 1402 | 22.37 | 5621.7 | 3023.8 | 2959.7 | 4343.1 | 1201.1 | 0.67957 | 6.29
2024-12-09 | 19:11 | Data | 0 | 32.494 | 29.969 | 200.742 | 7.63 | 188.48 | 2157.45 | 25.89 | 44.825 | 6.34 | 1.39 | 4.919 | 8635.19 | 2.133 | 97.9 | 78 | 1402 | 22.41 | 5612.9 | 3014.2 | 2951.2 | 4334.9 | 1201.1 | 0.67878 | 6.31
2024-12-09 | 19:11 | Data | 0 | 32.028 | 29.726 | 200.742 | 7.62 | 188.345 | 2160.16 | 25.89 | 44.915 | 6.34 | 1.399 | 4.902 | 8639.71 | 2.295 | 97.9 | 77.8 | 1405 | 22.37 | 5615.8 | 3046 | 2933.8 | 4338.7 | 1201.1 | 0.68467 | 6.301
2024-12-09 | 19:11 | Data | 0 | 32.082 | 29.847 | 200.787 | 7.62 | 188.39 | 2161.06 | 25.89 | 44.825 | 6.34 | 1.393 | 4.912 | 8639.71 | 2.309 | 97.9 | 77.9 | 1405 | 22.46 | 5615.8 | 3036.3 | 2946.9 | 4327 | 1201.1 | 0.68268 | 6.306
2024-12-09 | 19:11 | Data | 0 | 31.846 | 30.111 | 200.923 | 7.63 | 188.435 | 2161.06 | 25.9 | 44.825 | 6.34 | 1.395 | 4.909 | 8644.24 | 1.931 | 97.9 | 77.9 | 1405 | 22.41 | 5618.8 | 3032.1 | 2988.6 | 4365.9 | 1201.1 | 0.67744 | 6.302
2024-12-09 | 19:11 | Data | 0 | 32.069 | 29.955 | 200.742 | 7.62 | 188.525 | 2161.06 | 25.89 | 44.825 | 6.34 | 1.392 | 4.909 | 8648.76 | 2.086 | 97.9 | 77.9 | 1405 | 22.41 | 5621.7 | 3038.2 | 3002.5 | 4385.6 | 1201.2 | 0.67892 | 6.302
2024-12-09 | 19:12 | Data | 0 | 31.913 | 30.03 | 200.742 | 7.62 | 188.345 | 2160.16 | 25.9 | 44.915 | 6.34 | 1.386 | 4.917 | 8648.76 | 2.16 | 97.9 | 78 | 1403 | 22.41 | 5621.7 | 3021.4 | 3003.7 | 4369.6 | 1201.2 | 0.67303 | 6.303
2024-12-09 | 19:12 | Data | 0 | 32.264 | 30.178 | 200.742 | 7.63 | 188.435 | 2102.31 | 25.89 | 44.825 | 6.34 | 1.396 | 4.915 | 8644.24 | 2.106 | 97.9 | 77.9 | 1367 | 22.41 | 5618.8 | 3040.5 | 2991.1 | 4378.3 | 1201.2 | 0.67865 | 6.311
2024-12-09 | 19:12 | Data | 0 | 32.075 | 29.76 | 200.787 | 7.63 | 188.616 | 2103.22 | 25.89 | 44.825 | 6.34 | 1.386 | 4.931 | 8662.33 | 2.201 | 97.9 | 78.1 | 1368 | 22.41 | 5630.5 | 3024.4 | 2964.4 | 4348.1 | 1201.2 | 0.67791 | 6.318
2024-12-09 | 19:12 | Data | 0 | 32.028 | 29.739 | 200.697 | 7.63 | 188.48 | 2104.12 | 25.89 | 44.825 | 6.34 | 1.383 | 4.922 | 8657.8 | 2.275 | 97.9 | 78.1 | 1368 | 22.41 | 5627.6 | 3034.1 | 2968.5 | 4355.1 | 1201.2 | 0.6797 | 6.305
2024-12-09 | 19:12 | Data | 0 | 32.015 | 29.726 | 200.742 | 7.62 | 188.39 | 2104.12 | 25.89 | 44.825 | 6.34 | 1.384 | 4.918 | 8662.33 | 2.302 | 97.9 | 78 | 1368 | 22.41 | 5630.5 | 3047.5 | 2948 | 4348.3 | 1201.2 | 0.68449 | 6.302
2024-12-09 | 19:12 | Data | 0 | 32.264 | 29.955 | 200.832 | 7.63 | 188.435 | 2160.16 | 25.89 | 44.825 | 6.34 | 1.389 | 4.934 | 8680.41 | 2.309 | 97.9 | 78 | 1405 | 22.41 | 5642.3 | 3052.5 | 2940 | 4347.9 | 1201.2 | 0.68572 | 6.323
2024-12-09 | 19:12 | Data | 0 | 32.015 | 29.726 | 200.697 | 7.63 | 188.435 | 2161.06 | 25.89 | 44.825 | 6.34 | 1.381 | 4.908 | 8671.37 | 2.302 | 97.9 | 78 | 1405 | 22.41 | 5636.4 | 3031.8 | 2926.9 | 4317 | 1201.2 | 0.68293 | 6.29
2024-12-09 | 19:12 | Data | 0 | 31.839 | 29.753 | 200.651 | 7.63 | 188.435 | 2158.35 | 25.91 | 44.825 | 6.34 | 1.384 | 4.913 | 8671.37 | 2.052 | 97.9 | 78 | 1403 | 22.41 | 5636.4 | 3034.8 | 2958.4 | 4344.9 | 1201.2 | 0.68296 | 6.297
2024-12-09 | 19:12 | Data | 0 | 32.021 | 30.111 | 200.878 | 7.62 | 188.48 | 2161.06 | 25.89 | 44.825 | 6.34 | 1.391 | 4.921 | 8680.41 | 2.16 | 97.9 | 78 | 1405 | 22.41 | 5642.3 | 3036.6 | 2980.8 | 4358.2 | 1201.2 | 0.67936 | 6.312
2024-12-09 | 19:12 | Data | 0 | 32.028 | 30.057 | 200.651 | 7.63 | 188.39 | 2159.26 | 25.89 | 44.825 | 6.34 | 1.395 | 4.895 | 8671.37 | 2.221 | 97.9 | 77.8 | 1403 | 22.46 | 5636.4 | 3045.2 | 2993.8 | 4381.4 | 1201.2 | 0.67792 | 6.291
2024-12-09 | 19:12 | Data | 0 | 32.177 | 29.847 | 200.742 | 7.63 | 188.48 | 2158.35 | 25.89 | 44.825 | 6.35 | 1.397 | 4.908 | 8635.19 | 2.316 | 97.9 | 77.8 | 1403 | 22.46 | 5612.9 | 3049.3 | 3002.6 | 4385.6 | 1201.2 | 0.67848 | 6.305
2024-12-09 | 19:12 | Data | 0 | 32.089 | 29.949 | 200.651 | 7.63 | 188.299 | 2158.35 | 25.89 | 44.644 | 6.34 | 1.387 | 4.934 | 8639.71 | 2.235 | 97.9 | 78.1 | 1404 | 22.32 | 5615.8 | 3028 | 3029.5 | 4395.5 | 1201.2 | 0.67122 | 6.321
2024-12-09 | 19:12 | Data | 0 | 32.035 | 29.949 | 200.832 | 7.63 | 188.299 | 2161.06 | 25.89 | 44.825 | 6.34 | 1.382 | 4.924 | 8648.76 | 2.079 | 97.9 | 78.1 | 1404 | 22.41 | 5621.7 | 3044.1 | 3028.5 | 4405.2 | 1201.2 | 0.67243 | 6.306
2024-12-09 | 19:12 | Data | 0 | 32.177 | 29.753 | 200.697 | 7.62 | 188.435 | 2208.97 | 25.89 | 44.825 | 6.34 | 1.39 | 4.92 | 8639.71 | 2.275 | 98 | 78 | 1436 | 22.37 | 5615.8 | 3036.2 | 3006.6 | 4383 | 1201.2 | 0.67695 | 6.311
2024-12-09 | 19:12 | Data | 0 | 32.318 | 29.814 | 200.968 | 7.62 | 188.48 | 2212.58 | 25.89 | 44.825 | 6.34 | 1.396 | 4.903 | 8644.24 | 2.019 | 98 | 77.8 | 1438 | 22.41 | 5618.8 | 3040.7 | 2990.7 | 4378.5 | 1201.2 | 0.6777 | 6.301
2024-12-09 | 19:12 | Data | 0 | 32.028 | 29.901 | 200.742 | 7.63 | 188.48 | 2213.49 | 25.9 | 44.825 | 6.34 | 1.391 | 4.927 | 8662.33 | 2.181 | 98 | 78 | 1439 | 22.41 | 5630.5 | 3033.4 | 2960.5 | 4349.5 | 1201.2 | 0.68047 | 6.318
2024-12-09 | 19:12 | Data | 0 | 32.028 | 29.841 | 200.878 | 7.62 | 188.571 | 2215.29 | 25.91 | 44.915 | 6.34 | 1.395 | 4.928 | 8662.33 | 2.187 | 98 | 77.9 | 1439 | 22.41 | 5630.5 | 3042 | 2967.8 | 4358.5 | 1201.2 | 0.68153 | 6.322
2024-12-09 | 19:12 | Data | 0 | 32.143 | 30.158 | 200.742 | 7.63 | 188.525 | 2164.68 | 25.89 | 44.915 | 6.34 | 1.387 | 4.94 | 8662.33 | 2.086 | 97.9 | 78.1 | 1406 | 22.41 | 5630.5 | 3046 | 2977.4 | 4372.4 | 1201.2 | 0.68038 | 6.327
2024-12-09 | 19:13 | Data | 0 | 31.846 | 29.726 | 200.742 | 7.63 | 188.435 | 2159.26 | 25.89 | 44.825 | 6.34 | 1.386 | 4.961 | 8644.24 | 2.079 | 97.9 | 78.2 | 1404 | 22.41 | 5618.8 | 3042.1 | 2966.1 | 4358.7 | 1201.2 | 0.68179 | 6.348
2024-12-09 | 19:13 | Data | 0 | 32.264 | 29.955 | 200.651 | 7.62 | 188.435 | 2161.06 | 25.89 | 44.825 | 6.34 | 1.395 | 4.921 | 8644.24 | 2.187 | 97.9 | 77.9 | 1405 | 22.41 | 5618.8 | 3039.3 | 2982.4 | 4370 | 1201.2 | 0.68068 | 6.315
2024-12-09 | 19:13 | Data | 0 | 32.204 | 29.739 | 200.742 | 7.63 | 188.39 | 2158.35 | 25.89 | 44.825 | 6.34 | 1.389 | 4.901 | 8644.24 | 2.268 | 97.9 | 77.9 | 1404 | 22.41 | 5618.8 | 3041.7 | 3005.5 | 4389.9 | 1201.2 | 0.67571 | 6.291
2024-12-09 | 19:13 | Data | 0 | 32.204 | 29.773 | 200.832 | 7.62 | 188.571 | 2159.26 | 25.89 | 44.825 | 6.34 | 1.388 | 4.907 | 8635.19 | 2.255 | 97.9 | 78 | 1404 | 22.41 | 5612.9 | 3028.6 | 3008.8 | 4380 | 1201.2 | 0.67574 | 6.296
2024-12-09 | 19:13 | Data | 0 | 32.474 | 30.009 | 200.787 | 7.63 | 188.571 | 2158.35 | 25.89 | 44.644 | 6.34 | 1.389 | 4.91 | 8639.71 | 2.37 | 97.9 | 78 | 1403 | 22.32 | 5615.8 | 3019.4 | 2998.1 | 4371.8 | 1201.2 | 0.67323 | 6.299
2024-12-09 | 19:13 | Data | 0 | 32.035 | 29.733 | 200.787 | 7.63 | 188.435 | 2159.26 | 25.89 | 44.554 | 6.34 | 1.376 | 4.954 | 8689.46 | 2.275 | 97.9 | 78.3 | 1404 | 22.28 | 5648.1 | 3028.3 | 3014.6 | 4381.4 | 1201.2 | 0.67504 | 6.329
2024-12-09 | 19:13 | Data | 0 | 32.035 | 29.841 | 200.787 | 7.63 | 188.48 | 2158.35 | 25.89 | 44.554 | 6.35 | 1.389 | 4.951 | 8689.46 | 2.073 | 97.9 | 78.1 | 1403 | 22.28 | 5648.1 | 3058.9 | 3028.7 | 4414.3 | 1201.2 | 0.67592 | 6.34
2024-12-09 | 19:13 | Data | 0 | 32.001 | 29.841 | 200.742 | 7.63 | 188.48 | 2158.35 | 25.89 | 44.825 | 6.34 | 1.392 | 4.907 | 8680.41 | 2.525 | 97.9 | 77.9 | 1403 | 22.37 | 5642.3 | 3041 | 3022.1 | 4393.5 | 1201.2 | 0.67534 | 6.298
2024-12-09 | 19:13 | Data | 0 | 32.062 | 29.955 | 200.878 | 7.63 | 188.48 | 2158.35 | 25.89 | 44.825 | 6.34 | 1.398 | 4.916 | 8703.03 | 2.086 | 97.9 | 77.9 | 1403 | 22.41 | 5657 | 3046.2 | 3001.6 | 4387.5 | 1201.2 | 0.67795 | 6.314
2024-12-09 | 19:13 | Data | 0 | 32.109 | 29.847 | 200.787 | 7.62 | 188.525 | 2158.35 | 25.89 | 44.825 | 6.34 | 1.387 | 4.924 | 8693.98 | 2.1 | 97.9 | 78 | 1403 | 22.41 | 5651.1 | 3033.5 | 2997.3 | 4390.3 | 1201.2 | 0.6768 | 6.312
2024-12-09 | 19:13 | Data | 0 | 32.467 | 30.205 | 200.923 | 7.63 | 188.616 | 2158.35 | 25.89 | 44.915 | 6.34 | 1.377 | 4.911 | 8671.37 | 2.066 | 97.9 | 78.1 | 1403 | 22.41 | 5636.4 | 3040.2 | 2976.5 | 4369.3 | 1201.2 | 0.67884 | 6.289
2024-12-09 | 19:13 | Data | 0 | 32.028 | 29.901 | 200.742 | 7.63 | 188.48 | 2160.16 | 25.89 | 44.915 | 6.34 | 1.39 | 4.944 | 8684.94 | 2.275 | 97.9 | 78.1 | 1405 | 22.41 | 5645.2 | 3049.7 | 3001.4 | 4391.7 | 1201.2 | 0.67759 | 6.335
2024-12-09 | 19:13 | Data | 0 | 32.237 | 29.901 | 200.697 | 7.62 | 188.435 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.398 | 4.942 | 8693.98 | 2.518 | 97.9 | 77.9 | 1405 | 22.28 | 5651.1 | 3051.9 | 3011.5 | 4403.1 | 1201.2 | 0.67912 | 6.339
2024-12-09 | 19:13 | Data | 0 | 32.305 | 29.793 | 200.787 | 7.63 | 188.525 | 2161.06 | 25.9 | 44.554 | 6.34 | 1.39 | 4.939 | 8680.41 | 2.302 | 97.9 | 78 | 1405 | 22.28 | 5642.3 | 3070.2 | 2988 | 4393.5 | 1201.2 | 0.68215 | 6.329
2024-12-09 | 19:13 | Data | 0 | 32.15 | 30.171 | 200.742 | 7.63 | 188.48 | 2161.06 | 25.9 | 44.825 | 6.34 | 1.39 | 4.945 | 8693.98 | 2.248 | 97.9 | 78.1 | 1405 | 22.41 | 5651.1 | 3041.4 | 3027.5 | 4405.2 | 1201.2 | 0.67435 | 6.335
2024-12-09 | 19:13 | Data | 0 | 32.291 | 29.955 | 200.832 | 7.62 | 188.571 | 2161.97 | 25.89 | 44.554 | 6.34 | 1.38 | 4.928 | 8666.85 | 2.106 | 97.9 | 78.1 | 1405 | 22.28 | 5633.5 | 3029 | 3028.4 | 4392.9 | 1201.2 | 0.67181 | 6.308
2024-12-09 | 19:13 | Data | 0 | 32.264 | 29.793 | 200.832 | 7.62 | 188.571 | 2157.45 | 25.89 | 44.825 | 6.34 | 1.387 | 4.925 | 8662.33 | 2.397 | 97.9 | 78 | 1402 | 22.46 | 5630.5 | 3048.1 | 3032.7 | 4411.4 | 1201.3 | 0.67405 | 6.312
2024-12-09 | 19:13 | Data | 0 | 32.366 | 29.996 | 200.742 | 7.62 | 188.525 | 2161.06 | 25.9 | 44.554 | 6.34 | 1.384 | 4.929 | 8639.71 | 2.322 | 97.9 | 78.1 | 1405 | 22.32 | 5615.8 | 3035.7 | 3015.2 | 4394.2 | 1201.3 | 0.67425 | 6.312
2024-12-09 | 19:14 | Data | 0 | 32.352 | 29.982 | 200.787 | 7.62 | 188.48 | 2161.06 | 25.89 | 44.915 | 6.34 | 1.39 | 4.905 | 8648.76 | 2.471 | 97.9 | 77.9 | 1405 | 22.41 | 5621.7 | 3041.1 | 3009.5 | 4386.5 | 1201.3 | 0.67819 | 6.295
2024-12-09 | 19:14 | Data | 0 | 32.264 | 29.962 | 200.878 | 7.63 | 188.48 | 2161.06 | 25.89 | 44.825 | 6.34 | 1.396 | 4.933 | 8662.33 | 2.302 | 97.9 | 77.9 | 1405 | 22.41 | 5630.5 | 3047.7 | 2977.3 | 4371.2 | 1201.3 | 0.68019 | 6.329
2024-12-09 | 19:14 | Data | 0 | 32.109 | 30.259 | 200.832 | 7.63 | 188.571 | 2164.68 | 25.89 | 44.825 | 6.35 | 1.395 | 4.931 | 8648.76 | 2.019 | 97.9 | 78 | 1407 | 22.41 | 5621.7 | 3069.2 | 2983.2 | 4386.2 | 1201.3 | 0.6839 | 6.326
2024-12-09 | 19:14 | Data | 0 | 32.433 | 29.955 | 200.697 | 7.63 | 188.39 | 2166.49 | 25.89 | 44.825 | 6.34 | 1.389 | 4.913 | 8671.37 | 2.329 | 97.9 | 78 | 1408 | 22.41 | 5636.4 | 3032.4 | 2975.5 | 4359.1 | 1201.3 | 0.67834 | 6.302
2024-12-09 | 19:14 | Data | 0 | 32.703 | 30.097 | 200.742 | 7.63 | 188.571 | 2166.49 | 25.89 | 44.825 | 6.34 | 1.398 | 4.882 | 8693.98 | 2.248 | 97.9 | 77.7 | 1408 | 22.41 | 5651.1 | 3036 | 3010.9 | 4392.8 | 1201.3 | 0.676 | 6.281
2024-12-09 | 19:14 | Data | 0 | 32.264 | 29.793 | 200.832 | 7.62 | 188.616 | 2166.49 | 25.89 | 44.915 | 6.34 | 1.388 | 4.91 | 8689.46 | 2.471 | 97.9 | 78 | 1408 | 22.41 | 5648.1 | 3028.3 | 3026.1 | 4395.2 | 1201.3 | 0.67339 | 6.299
2024-12-09 | 19:14 | Data | 0 | 32.379 | 29.969 | 200.878 | 7.63 | 188.571 | 2166.49 | 25.89 | 44.825 | 6.34 | 1.392 | 4.944 | 8680.41 | 2.295 | 97.9 | 78 | 1408 | 22.37 | 5642.3 | 3034 | 3032.6 | 4404.3 | 1201.3 | 0.67228 | 6.335
2024-12-09 | 19:14 | Data | 0 | 32.791 | 29.928 | 200.878 | 7.63 | 188.616 | 2166.49 | 25.89 | 44.825 | 6.34 | 1.391 | 4.962 | 8662.33 | 2.484 | 97.9 | 78.1 | 1408 | 22.41 | 5630.5 | 3040.1 | 3037.2 | 4408.9 | 1201.3 | 0.67321 | 6.351
2024-12-09 | 19:14 | Data | 0 | 32.204 | 30.171 | 200.787 | 7.62 | 188.525 | 2166.49 | 25.89 | 44.373 | 6.34 | 1.399 | 4.942 | 8662.33 | 2.228 | 97.9 | 77.9 | 1408 | 22.23 | 5630.5 | 3047 | 3026.4 | 4404.2 | 1201.3 | 0.67488 | 6.342
2024-12-09 | 19:14 | Data | 0 | 32.237 | 29.962 | 200.878 | 7.62 | 188.571 | 2166.49 | 25.89 | 44.825 | 6.34 | 1.4 | 4.933 | 8671.37 | 2.289 | 97.9 | 77.9 | 1408 | 22.41 | 5636.4 | 3029.1 | 3014.1 | 4385.7 | 1201.3 | 0.67383 | 6.333
2024-12-09 | 19:14 | Data | 0 | 32.042 | 29.901 | 200.697 | 7.63 | 188.39 | 2163.77 | 25.91 | 44.734 | 6.34 | 1.391 | 4.896 | 8671.37 | 2.295 | 97.9 | 77.9 | 1406 | 22.41 | 5636.4 | 3056.6 | 3015.4 | 4410.4 | 1201.3 | 0.67607 | 6.288
2024-12-09 | 19:14 | Data | 0 | 32.251 | 30.057 | 200.742 | 7.63 | 188.525 | 2163.77 | 25.89 | 44.734 | 6.34 | 1.391 | 4.913 | 8671.37 | 2.349 | 97.9 | 77.9 | 1406 | 22.28 | 5636.4 | 3022.2 | 2968.1 | 4349.5 | 1201.3 | 0.67844 | 6.303
2024-12-09 | 19:14 | Data | 0 | 32.426 | 30.205 | 200.697 | 7.63 | 188.525 | 2162.87 | 25.89 | 44.825 | 6.34 | 1.391 | 4.947 | 8680.41 | 2.187 | 97.9 | 78.1 | 1405 | 22.41 | 5642.3 | 3025.8 | 2956.9 | 4342.8 | 1201.3 | 0.67971 | 6.339
2024-12-09 | 19:14 | Data | 0 | 32.183 | 29.76 | 200.923 | 7.62 | 188.571 | 2163.77 | 25.89 | 44.915 | 6.34 | 1.389 | 4.931 | 8671.37 | 2.235 | 97.9 | 78 | 1406 | 22.41 | 5636.4 | 3031.9 | 2961 | 4350.8 | 1201.3 | 0.68057 | 6.32
2024-12-09 | 19:14 | Data | 0 | 32.258 | 29.908 | 200.787 | 7.63 | 188.525 | 2167.39 | 25.89 | 44.644 | 6.34 | 1.395 | 4.929 | 8644.24 | 2.282 | 97.9 | 78 | 1408 | 22.28 | 5618.8 | 3030.1 | 2979.5 | 4371.9 | 1201.3 | 0.67723 | 6.322
2024-12-09 | 19:14 | Data | 0 | 32.089 | 29.955 | 200.832 | 7.63 | 188.48 | 2163.77 | 25.89 | 44.644 | 6.34 | 1.39 | 4.939 | 8680.41 | 2.073 | 97.9 | 78 | 1406 | 22.32 | 5642.3 | 3047.4 | 3010.9 | 4394.4 | 1201.3 | 0.67669 | 6.33
2024-12-09 | 19:14 | Data | 0 | 32.217 | 30.063 | 200.606 | 7.63 | 188.435 | 2163.77 | 25.91 | 44.825 | 6.34 | 1.396 | 4.908 | 8698.5 | 2.309 | 97.9 | 77.8 | 1406 | 22.37 | 5654 | 3042 | 3030.6 | 4402.6 | 1201.3 | 0.67497 | 6.304
2024-12-09 | 19:14 | Data | 0 | 32.062 | 29.942 | 200.878 | 7.62 | 188.571 | 2162.87 | 25.91 | 44.554 | 6.34 | 1.395 | 4.916 | 8684.94 | 2.093 | 97.9 | 77.9 | 1406 | 22.28 | 5645.2 | 3039.6 | 2990.9 | 4380.1 | 1201.3 | 0.67747 | 6.311
2024-12-09 | 19:15 | Data | 0 | 32.426 | 30.178 | 200.697 | 7.63 | 188.571 | 2164.68 | 25.89 | 44.464 | 6.34 | 1.385 | 4.915 | 8680.41 | 2.316 | 97.9 | 78 | 1407 | 22.32 | 5642.3 | 3052.6 | 2997.7 | 4390.8 | 1201.3 | 0.67897 | 6.3
2024-12-09 | 19:15 | Data | 0 | 32.264 | 29.847 | 200.787 | 7.63 | 188.525 | 2164.68 | 25.89 | 44.825 | 6.34 | 1.396 | 4.909 | 8662.33 | 2.187 | 97.9 | 77.9 | 1407 | 22.46 | 5630.5 | 3010.9 | 2989.6 | 4354.7 | 1201.3 | 0.67386 | 6.305
2024-12-09 | 19:15 | Data | 0 | 31.92 | 29.733 | 200.697 | 7.63 | 188.435 | 2159.26 | 25.89 | 44.915 | 6.34 | 1.396 | 4.926 | 8648.76 | 2.282 | 97.9 | 77.9 | 1404 | 22.41 | 5621.7 | 3038.1 | 2938 | 4344.3 | 1201.3 | 0.68185 | 6.322
2024-12-09 | 19:15 | Data | 0 | 32.258 | 29.982 | 200.832 | 7.62 | 188.571 | 2163.77 | 25.89 | 44.825 | 6.35 | 1.39 | 4.943 | 8648.76 | 2.255 | 97.9 | 78.1 | 1406 | 22.41 | 5621.7 | 3047.6 | 2954.2 | 4361.8 | 1201.3 | 0.68487 | 6.333
2024-12-09 | 19:15 | Data | 0 | 32.264 | 29.955 | 200.878 | 7.63 | 188.571 | 2163.77 | 25.9 | 44.554 | 6.34 | 1.396 | 4.917 | 8648.76 | 2.079 | 97.9 | 77.9 | 1406 | 22.28 | 5621.7 | 3037.6 | 2968.7 | 4358.7 | 1201.3 | 0.68071 | 6.314
2024-12-09 | 19:15 | Data | 0 | 32.318 | 29.787 | 200.742 | 7.63 | 188.525 | 2163.77 | 25.89 | 44.554 | 6.35 | 1.396 | 4.912 | 8621.63 | 2.221 | 97.9 | 77.9 | 1406 | 22.28 | 5604.1 | 3023.8 | 2970.1 | 4349.8 | 1201.3 | 0.67922 | 6.308
2024-12-09 | 19:15 | Data | 0 | 32.264 | 29.955 | 200.787 | 7.63 | 188.525 | 2162.87 | 25.89 | 44.734 | 6.34 | 1.386 | 4.925 | 8617.1 | 2.309 | 97.9 | 78.1 | 1406 | 22.37 | 5601.1 | 3048 | 2978.3 | 4371.5 | 1201.3 | 0.68022 | 6.31
2024-12-09 | 19:15 | Data | 0 | 31.826 | 29.976 | 200.742 | 7.62 | 188.525 | 2161.06 | 25.89 | 44.644 | 6.34 | 1.39 | 4.912 | 8648.76 | 2.079 | 97.9 | 77.9 | 1405 | 22.32 | 5621.7 | 3028.5 | 2981.2 | 4358.5 | 1201.3 | 0.67993 | 6.302
2024-12-09 | 19:15 | Data | 0 | 32.197 | 29.78 | 200.787 | 7.63 | 188.435 | 2156.54 | 25.89 | 44.825 | 6.34 | 1.397 | 4.933 | 8648.76 | 2.302 | 97.9 | 77.9 | 1402 | 22.41 | 5621.7 | 3039.1 | 2950.8 | 4346.1 | 1201.3 | 0.68304 | 6.33
2024-12-09 | 19:15 | Data | 0 | 32.325 | 30.131 | 200.878 | 7.63 | 188.571 | 2161.06 | 25.89 | 44.644 | 6.34 | 1.384 | 4.938 | 8644.24 | 2.194 | 97.9 | 78.1 | 1405 | 22.32 | 5618.8 | 3017 | 2972.4 | 4347.6 | 1201.3 | 0.67816 | 6.323
2024-12-09 | 19:15 | Data | 0 | 31.988 | 29.928 | 200.787 | 7.63 | 188.435 | 2161.06 | 25.89 | 44.734 | 6.34 | 1.377 | 4.925 | 8671.37 | 2.241 | 97.9 | 78.1 | 1405 | 22.37 | 5636.4 | 3049.4 | 2971.8 | 4373.6 | 1201.3 | 0.67938 | 6.301
2024-12-09 | 19:15 | Data | 0 | 32.264 | 29.955 | 200.742 | 7.63 | 188.525 | 2161.06 | 25.89 | 44.915 | 6.35 | 1.393 | 4.92 | 8630.67 | 2.133 | 97.9 | 77.9 | 1405 | 22.41 | 5609.9 | 3026.4 | 2958.6 | 4348.3 | 1201.3 | 0.67987 | 6.313
2024-12-09 | 19:15 | Data | 0 | 32.467 | 29.868 | 200.832 | 7.62 | 188.616 | 2161.06 | 25.89 | 44.825 | 6.34 | 1.385 | 4.92 | 8608.06 | 2.451 | 97.9 | 78 | 1405 | 22.41 | 5595.2 | 3044.2 | 2982.9 | 4376.1 | 1201.3 | 0.67999 | 6.304
2024-12-09 | 19:15 | Data | 0 | 32.676 | 29.976 | 200.923 | 7.63 | 188.616 | 2161.97 | 25.9 | 44.915 | 6.34 | 1.394 | 4.936 | 8612.58 | 2.154 | 97.9 | 78 | 1405 | 22.41 | 5598.2 | 3045.4 | 2963.8 | 4363.7 | 1201.4 | 0.6811 | 6.329
2024-12-09 | 19:15 | Data | 0 | 32.264 | 29.955 | 200.787 | 7.62 | 188.435 | 2161.06 | 25.89 | 44.915 | 6.34 | 1.395 | 4.942 | 8603.54 | 2.309 | 97.9 | 78 | 1405 | 22.41 | 5592.3 | 3037.2 | 2973.4 | 4362.8 | 1201.4 | 0.67862 | 6.337
2024-12-09 | 19:15 | Data | 0 | 32.487 | 30.185 | 201.013 | 7.63 | 188.571 | 2161.06 | 25.89 | 44.825 | 6.34 | 1.396 | 4.947 | 8580.93 | 2.133 | 97.9 | 78 | 1405 | 22.41 | 5577.6 | 3033.2 | 2969.3 | 4358.6 | 1201.4 | 0.67917 | 6.343
2024-12-09 | 19:16 | Data | 0 | 32.251 | 29.955 | 200.832 | 7.62 | 188.435 | 2163.77 | 25.91 | 44.825 | 6.34 | 1.381 | 4.942 | 8599.01 | 2.302 | 97.9 | 78.2 | 1406 | 22.41 | 5589.4 | 3045.4 | 2968.7 | 4360.3 | 1201.4 | 0.68296 | 6.323
2024-12-09 | 19:16 | Data | 0 | 32.339 | 29.962 | 200.742 | 7.63 | 188.616 | 2163.77 | 25.9 | 44.734 | 6.35 | 1.382 | 4.922 | 8621.63 | 2.106 | 97.9 | 78.1 | 1406 | 22.41 | 5604.1 | 3042.5 | 2978.3 | 4368.7 | 1201.4 | 0.68071 | 6.303
2024-12-09 | 19:16 | Data | 0 | 32.264 | 30.131 | 200.832 | 7.63 | 188.525 | 2166.49 | 25.89 | 44.825 | 6.34 | 1.384 | 4.908 | 8608.06 | 2.309 | 97.9 | 78 | 1408 | 22.41 | 5595.2 | 3043.6 | 2995.9 | 4380.5 | 1201.4 | 0.67768 | 6.291
2024-12-09 | 19:16 | Data | 0 | 32.204 | 29.955 | 200.651 | 7.62 | 188.435 | 2166.49 | 25.9 | 44.825 | 6.34 | 1.382 | 4.91 | 8255.33 | 2.289 | 97.9 | 78 | 1408 | 22.46 | 5366 | 3026.6 | 3017 | 4378.3 | 1201.4 | 0.67448 | 6.293
2024-12-09 | 19:16 | Data | 0 | 32.487 | 30.023 | 200.878 | 7.63 | 188.571 | 2170.1 | 25.89 | 44.825 | 6.34 | 1.388 | 4.938 | 8689.46 | 2.255 | 97.9 | 78.1 | 1411 | 22.41 | 5648.1 | 3034.6 | 3015.1 | 4390.6 | 1201.4 | 0.67539 | 6.325
2024-12-09 | 19:16 | Data | 0 | 32.487 | 30.185 | 200.787 | 7.63 | 188.616 | 2161.97 | 25.89 | 44.825 | 6.34 | 1.393 | 4.928 | 8671.37 | 2.309 | 97.9 | 78 | 1405 | 22.37 | 5636.4 | 3042.6 | 3008.7 | 4386.6 | 1201.4 | 0.67723 | 6.32
2024-12-09 | 19:16 | Data | 0 | 32.163 | 29.746 | 200.742 | 7.63 | 188.616 | 2163.77 | 25.9 | 44.825 | 6.34 | 1.396 | 4.915 | 8689.46 | 2.295 | 97.9 | 77.9 | 1406 | 22.46 | 5648.1 | 3038.8 | 3006.1 | 4387.1 | 1201.4 | 0.67577 | 6.311
2024-12-09 | 19:16 | Data | 0 | 32.575 | 30.239 | 200.832 | 7.63 | 188.661 | 2159.26 | 25.9 | 44.644 | 6.34 | 1.385 | 4.93 | 8703.03 | 2.309 | 97.9 | 78.1 | 1403 | 22.28 | 5657 | 3048.4 | 2996.9 | 4386.6 | 1201.4 | 0.67876 | 6.316
2024-12-09 | 19:16 | Data | 0 | 32.197 | 30.151 | 200.878 | 7.62 | 188.571 | 2163.77 | 25.89 | 44.644 | 6.34 | 1.381 | 4.924 | 8684.94 | 2.187 | 97.9 | 78.1 | 1406 | 22.32 | 5645.2 | 3036.1 | 2961.6 | 4356.7 | 1201.4 | 0.67907 | 6.306
2024-12-09 | 19:16 | Data | 0 | 32.264 | 29.955 | 200.787 | 7.63 | 188.616 | 2163.77 | 25.89 | 44.734 | 6.34 | 1.397 | 4.917 | 8657.8 | 2.309 | 97.9 | 77.9 | 1406 | 22.32 | 5627.6 | 3033 | 2942.9 | 4342.8 | 1201.4 | 0.68196 | 6.314
2024-12-09 | 19:16 | Data | 0 | 32.291 | 29.746 | 200.742 | 7.63 | 188.616 | 2165.58 | 25.89 | 44.644 | 6.34 | 1.391 | 4.915 | 8662.33 | 2.329 | 97.9 | 77.9 | 1408 | 22.32 | 5630.5 | 3049.8 | 2935.2 | 4346.2 | 1201.4 | 0.68574 | 6.308
2024-12-09 | 19:16 | Data | 0 | 32.312 | 29.955 | 200.787 | 7.63 | 188.525 | 2165.58 | 25.89 | 44.915 | 6.34 | 1.399 | 4.909 | 8662.33 | 2.201 | 97.9 | 77.8 | 1407 | 22.46 | 5630.5 | 3035 | 2937.1 | 4342.1 | 1201.4 | 0.68434 | 6.308
2024-12-09 | 19:16 | Data | 0 | 32.467 | 29.82 | 200.832 | 7.63 | 188.616 | 2164.68 | 25.89 | 44.554 | 6.34 | 1.399 | 4.918 | 8657.8 | 2.579 | 97.9 | 77.9 | 1406 | 22.28 | 5627.6 | 3032 | 2928.8 | 4330.5 | 1201.4 | 0.68358 | 6.317
2024-12-09 | 19:16 | Data | 0 | 32.48 | 29.969 | 200.878 | 7.63 | 188.571 | 2161.06 | 25.9 | 44.554 | 6.35 | 1.391 | 4.912 | 8666.85 | 2.478 | 97.9 | 77.9 | 1405 | 22.32 | 5633.5 | 3054.8 | 2923.5 | 4338 | 1201.4 | 0.68358 | 6.304
2024-12-09 | 19:16 | Data | 0 | 32.487 | 30.185 | 200.832 | 7.63 | 188.571 | 2161.06 | 25.89 | 44.464 | 6.35 | 1.387 | 4.943 | 8689.46 | 2.106 | 97.9 | 78.1 | 1405 | 22.28 | 5648.1 | 3029.7 | 2936.7 | 4332.7 | 1201.4 | 0.68232 | 6.329
2024-12-09 | 19:16 | Data | 0 | 32.264 | 30.131 | 200.832 | 7.62 | 188.525 | 2156.54 | 25.9 | 44.644 | 6.35 | 1.395 | 4.951 | 8693.98 | 2.309 | 97.9 | 78 | 1401 | 22.28 | 5651.1 | 3039.2 | 2975.2 | 4364.4 | 1201.4 | 0.67923 | 6.346
2024-12-09 | 19:17 | Data | 0 | 32.042 | 29.955 | 200.923 | 7.63 | 188.571 | 2163.77 | 25.89 | 44.644 | 6.35 | 1.386 | 4.933 | 8680.41 | 2.255 | 97.9 | 78.1 | 1407 | 22.32 | 5642.3 | 3030 | 2961 | 4352.2 | 1201.4 | 0.67894 | 6.32
2024-12-09 | 19:17 | Data | 0 | 32.069 | 30.171 | 200.878 | 7.62 | 188.571 | 2159.26 | 25.89 | 44.554 | 6.34 | 1.388 | 4.928 | 8684.94 | 1.89 | 97.9 | 78 | 1404 | 22.28 | 5645.2 | 3028.1 | 2953.1 | 4345 | 1201.4 | 0.68043 | 6.315
2024-12-09 | 19:17 | Data | 0 | 32.264 | 30.198 | 200.832 | 7.62 | 188.616 | 2163.77 | 25.9 | 44.554 | 6.35 | 1.386 | 4.913 | 8671.37 | 2.208 | 97.9 | 78 | 1407 | 22.28 | 5636.4 | 3035.6 | 2932.8 | 4334.7 | 1201.4 | 0.68226 | 6.301
2024-12-09 | 19:17 | Data | 0 | 32.258 | 29.955 | 200.832 | 7.63 | 188.48 | 2165.58 | 25.89 | 44.554 | 6.34 | 1.386 | 4.924 | 8721.11 | 2.302 | 97.9 | 78.1 | 1406 | 22.28 | 5668.7 | 3042.9 | 2939.2 | 4341.6 | 1201.4 | 0.68526 | 6.31
2024-12-09 | 19:17 | Data | 0 | 32.082 | 30.043 | 200.787 | 7.63 | 188.435 | 2161.97 | 25.9 | 44.644 | 6.35 | 1.394 | 4.91 | 8698.5 | 2.302 | 97.9 | 77.9 | 1405 | 22.28 | 5654 | 3047.4 | 2947.9 | 4352.4 | 1201.4 | 0.68432 | 6.304
2024-12-09 | 19:17 | Data | 0 | 32.69 | 29.976 | 200.968 | 7.63 | 188.661 | 2160.16 | 25.89 | 44.644 | 6.34 | 1.388 | 4.926 | 8671.37 | 2.208 | 97.9 | 78 | 1404 | 22.28 | 5636.4 | 1959.8 | 2391.7 | 3103.2 | 1201.4 | 0.62936 | 6.313
2024-12-09 | 19:17 | Data | 0 | 32.143 | 29.955 | 200.787 | 7.62 | 188.571 | 2158.35 | 25.89 | 44.554 | 6.35 | 1.396 | 4.935 | 8684.94 | 2.208 | 97.9 | 77.9 | 1402 | 22.28 | 5645.2 | 1946 | 2387.2 | 3091.4 | 1201.4 | 0.62765 | 6.332
2024-12-09 | 19:17 | Data | 0 | 32.217 | 29.746 | 200.832 | 7.63 | 188.571 | 2159.26 | 25.89 | 44.464 | 6.35 | 1.388 | 4.901 | 8689.46 | 2.12 | 97.9 | 77.9 | 1403 | 22.28 | 5648.1 | 1974.9 | 2396.6 | 3115 | 1201.4 | 0.6318 | 6.291
2024-12-09 | 19:17 | Data | 0 | 32.035 | 30.178 | 200.832 | 7.63 | 188.616 | 2158.35 | 25.89 | 44.554 | 6.34 | 1.382 | 4.907 | 8666.85 | 2.248 | 97.9 | 78 | 1403 | 22.28 | 5633.5 | 1954 | 2404.7 | 3105.8 | 1201.4 | 0.62536 | 6.289
2024-12-09 | 19:17 | Data | 0 | 32.17 | 29.962 | 200.923 | 7.63 | 188.571 | 2157.45 | 25.89 | 44.554 | 6.35 | 1.389 | 4.929 | 8680.41 | 2.194 | 97.9 | 78 | 1402 | 22.28 | 5642.3 | 1965.2 | 2417.9 | 3126.1 | 1201.4 | 0.6275 | 6.318
2024-12-09 | 19:17 | Data | 0 | 32.264 | 30.34 | 200.923 | 7.63 | 188.525 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.377 | 4.91 | 8671.37 | 2.16 | 97.9 | 78.1 | 1405 | 22.32 | 5636.4 | 1952.1 | 2381.2 | 3088.9 | 1201.4 | 0.62955 | 6.286
2024-12-09 | 19:17 | Data | 0 | 32.467 | 29.982 | 200.742 | 7.63 | 188.571 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.387 | 4.904 | 8666.85 | 2.295 | 97.9 | 77.9 | 1405 | 22.28 | 5633.5 | 1943.3 | 2398.3 | 3098.4 | 1201.4 | 0.62401 | 6.291
2024-12-09 | 19:17 | Data | 0 | 32.055 | 30.124 | 200.787 | 7.63 | 188.525 | 2161.97 | 25.89 | 44.644 | 6.34 | 1.392 | 4.921 | 8703.03 | 2.14 | 97.9 | 78 | 1405 | 22.32 | 5657 | 1955.4 | 2417.3 | 3120.6 | 1201.4 | 0.62427 | 6.313
2024-12-09 | 19:17 | Data | 0 | 32.487 | 29.766 | 201.013 | 7.63 | 188.616 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.393 | 4.935 | 8698.5 | 2.343 | 97.9 | 78 | 1405 | 22.28 | 5654 | 1947.7 | 2434.3 | 3129.6 | 1201.4 | 0.61947 | 6.328
2024-12-09 | 19:17 | Data | 0 | 32.575 | 30.212 | 200.832 | 7.63 | 188.571 | 2161.06 | 25.89 | 44.554 | 6.35 | 1.389 | 4.917 | 8703.03 | 2.302 | 97.9 | 78 | 1405 | 22.23 | 5657 | 1947.5 | 2463.7 | 3151.1 | 1201.4 | 0.61565 | 6.305
2024-12-09 | 19:17 | Data | 0 | 32.541 | 30.07 | 200.968 | 7.63 | 188.616 | 2161.06 | 25.9 | 44.554 | 6.34 | 1.384 | 4.928 | 8689.46 | 2.147 | 97.9 | 78.1 | 1405 | 22.32 | 5648.1 | 1956.9 | 2395.7 | 3105.6 | 1201.4 | 0.62809 | 6.312
2024-12-09 | 19:17 | Data | 0 | 32.035 | 29.726 | 200.878 | 7.62 | 188.435 | 2161.06 | 25.9 | 44.825 | 6.34 | 1.38 | 4.91 | 8662.33 | 2.302 | 97.9 | 78.1 | 1405 | 22.41 | 5630.5 | 1938.8 | 2403.9 | 3118.5 | 1201.4 | 0.62514 | 6.29
2024-12-09 | 19:17 | Data | 0 | 32.15 | 30.293 | 200.923 | 7.63 | 188.571 | 2163.77 | 25.89 | 44.915 | 6.34 | 1.385 | 4.898 | 8648.76 | 2.201 | 97.9 | 78 | 1406 | 22.41 | 5621.7 | 1958.7 | 2403.2 | 3112.6 | 1201.4 | 0.62615 | 6.282
2024-12-09 | 19:18 | Data | 0 | 32.204 | 29.982 | 200.968 | 7.63 | 188.525 | 2172.81 | 25.89 | 44.554 | 6.34 | 1.395 | 4.884 | 8644.24 | 2.39 | 97.9 | 77.8 | 1412 | 22.28 | 5618.8 | 1956.1 | 2402.6 | 3109.2 | 1201.4 | 0.62555 | 6.278
2024-12-09 | 19:18 | Data | 0 | 32.028 | 29.955 | 200.697 | 7.63 | 188.616 | 2167.39 | 25.89 | 44.825 | 6.34 | 1.392 | 4.899 | 8635.19 | 2.073 | 97.9 | 77.9 | 1409 | 22.41 | 5612.9 | 1956.9 | 2391.1 | 3100.9 | 1201.4 | 0.62858 | 6.291
2024-12-09 | 19:18 | Data | 0 | 32.048 | 29.928 | 200.742 | 7.62 | 188.435 | 2163.77 | 25.9 | 44.644 | 6.34 | 1.389 | 4.929 | 8635.19 | 2.221 | 97.9 | 78 | 1406 | 22.28 | 5612.9 | 1961.2 | 2374.5 | 3089.7 | 1201.5 | 0.6325 | 6.318
2024-12-09 | 19:18 | Data | 0 | 32.075 | 29.955 | 200.787 | 7.63 | 188.616 | 2161.06 | 25.9 | 44.554 | 6.35 | 1.386 | 4.912 | 8635.19 | 1.978 | 97.9 | 78 | 1405 | 22.28 | 5612.9 | 1965.6 | 2376.9 | 3095.8 | 1201.5 | 0.63249 | 6.299
2024-12-09 | 19:18 | Data | 0 | 32.028 | 29.841 | 200.742 | 7.63 | 188.435 | 2164.68 | 25.89 | 44.554 | 6.33 | 1.397 | 4.9 | 8630.67 | 2.275 | 97.9 | 77.8 | 1406 | 22.32 | 5609.9 | 1954 | 2429.8 | 3130.2 | 1201.5 | 0.62212 | 6.297
2024-12-09 | 19:18 | Data | 0 | 32.183 | 29.928 | 200.787 | 7.62 | 188.616 | 2163.77 | 25.89 | 44.554 | 6.34 | 1.387 | 4.897 | 8621.63 | 2.248 | 97.9 | 77.9 | 1406 | 22.28 | 5604.1 | 1954 | 2429.6 | 3130.2 | 1201.5 | 0.62256 | 6.284
2024-12-09 | 19:18 | Data | 0 | 32.379 | 30.07 | 200.742 | 7.63 | 188.525 | 2159.26 | 25.89 | 44.644 | 6.34 | 1.391 | 4.914 | 8580.93 | 2.302 | 97.9 | 77.9 | 1404 | 22.28 | 5577.6 | 1967.7 | 2403.5 | 3118.9 | 1201.5 | 0.62804 | 6.305
2024-12-09 | 19:18 | Data | 0 | 32.035 | 29.955 | 200.787 | 7.62 | 188.525 | 2163.77 | 25.89 | 44.644 | 6.35 | 1.393 | 4.903 | 8567.36 | 2.073 | 97.9 | 77.9 | 1406 | 22.32 | 5568.8 | 1959 | 2469 | 3161.2 | 1201.5 | 0.61816 | 6.296
2024-12-09 | 19:18 | Data | 0 | 32.278 | 30.158 | 200.923 | 7.62 | 188.39 | 2163.77 | 25.89 | 44.554 | 6.34 | 1.384 | 4.918 | 8562.84 | 2.316 | 97.9 | 78 | 1406 | 22.28 | 5565.8 | 1951.2 | 2444.6 | 3138.8 | 1201.5 | 0.61954 | 6.301
2024-12-09 | 19:18 | Data | 0 | 31.819 | 29.746 | 200.651 | 7.63 | 188.48 | 2164.68 | 25.89 | 44.554 | 6.34 | 1.379 | 4.925 | 8567.36 | 1.992 | 97.9 | 78.1 | 1406 | 22.23 | 5568.8 | 1946.5 | 2396.8 | 3100.6 | 1201.5 | 0.62525 | 6.304
2024-12-09 | 19:18 | Data | 0 | 32.143 | 29.942 | 200.697 | 7.62 | 188.525 | 2163.77 | 25.89 | 44.825 | 6.35 | 1.385 | 4.91 | 8599.01 | 2.302 | 97.9 | 78 | 1406 | 22.41 | 5589.4 | 1951.9 | 2394.1 | 3100.6 | 1201.5 | 0.62697 | 6.295
2024-12-09 | 19:18 | Data | 0 | 32.271 | 29.976 | 200.787 | 7.62 | 188.661 | 2163.77 | 25.89 | 44.825 | 6.34 | 1.388 | 4.911 | 8612.58 | 2.268 | 97.9 | 78 | 1406 | 22.46 | 5598.2 | 1943.4 | 2410.5 | 3109.5 | 1201.5 | 0.62208 | 6.301
2024-12-09 | 19:18 | Data | 0 | 32.028 | 29.787 | 200.697 | 7.63 | 188.48 | 2162.87 | 25.89 | 44.915 | 6.35 | 1.387 | 4.901 | 8603.54 | 2.241 | 97.9 | 77.9 | 1406 | 22.46 | 5592.3 | 1953.6 | 2404.7 | 3110.6 | 1201.5 | 0.6269 | 6.288
2024-12-09 | 19:18 | Data | 0 | 32.062 | 29.949 | 200.787 | 7.63 | 188.435 | 2163.77 | 25.89 | 44.734 | 6.34 | 1.384 | 4.881 | 8626.15 | 2.086 | 97.9 | 77.9 | 1407 | 22.41 | 5607 | 1961 | 2409.2 | 3109.5 | 1201.5 | 0.62469 | 6.265
2024-12-09 | 19:18 | Data | 0 | 32.474 | 30.28 | 200.742 | 7.62 | 188.571 | 2164.68 | 25.89 | 44.825 | 6.34 | 1.389 | 4.922 | 8612.58 | 2.167 | 97.9 | 78 | 1407 | 22.46 | 5598.2 | 1945.8 | 2406.4 | 3105.6 | 1201.5 | 0.62444 | 6.311
2024-12-09 | 19:18 | Data | 0 | 32.251 | 29.847 | 200.697 | 7.62 | 188.525 | 2163.77 | 25.9 | 44.825 | 6.34 | 1.394 | 4.913 | 8626.15 | 2.262 | 97.9 | 77.9 | 1406 | 22.41 | 5607 | 1953 | 2400.6 | 3108 | 1201.5 | 0.6262 | 6.308
2024-12-09 | 19:18 | Data | 0 | 31.832 | 29.901 | 200.651 | 7.63 | 188.435 | 2158.35 | 25.89 | 44.825 | 6.34 | 1.385 | 4.895 | 8617.1 | 2.275 | 97.9 | 78 | 1404 | 22.41 | 5601.1 | 1936.1 | 2416.7 | 3108.7 | 1201.5 | 0.6222 | 6.28
2024-12-09 | 19:18 | Data | 0 | 32.028 | 30.063 | 200.832 | 7.63 | 188.525 | 2159.26 | 25.9 | 44.825 | 6.34 | 1.39 | 4.92 | 8599.01 | 2.052 | 97.9 | 78 | 1403 | 22.41 | 5589.4 | 1960.1 | 2400.4 | 3110.3 | 1201.5 | 0.62774 | 6.31
2024-12-09 | 19:19 | Data | 0 | 32.015 | 29.928 | 200.651 | 7.63 | 188.48 | 2161.97 | 25.89 | 44.554 | 6.34 | 1.381 | 4.919 | 8599.01 | 2.127 | 97.9 | 78.1 | 1405 | 22.28 | 5589.4 | 1966.2 | 2414.8 | 3125.3 | 1201.5 | 0.62676 | 6.301
2024-12-09 | 19:19 | Data | 0 | 31.853 | 29.901 | 200.742 | 7.63 | 188.39 | 2161.06 | 25.89 | 44.825 | 6.34 | 1.383 | 4.953 | 8635.19 | 2.167 | 97.9 | 78.2 | 1405 | 22.41 | 5612.9 | 1947.7 | 2403 | 3104.2 | 1201.5 | 0.62433 | 6.336
2024-12-09 | 19:19 | Data | 0 | 32.237 | 29.955 | 200.832 | 7.62 | 188.48 | 2156.54 | 25.89 | 44.825 | 6.34 | 1.393 | 4.917 | 8585.45 | 2.309 | 97.9 | 77.9 | 1402 | 22.41 | 5580.5 | 1941.8 | 2376.3 | 3080.6 | 1201.5 | 0.62744 | 6.31
2024-12-09 | 19:19 | Data | 0 | 32.372 | 29.8 | 200.832 | 7.62 | 188.616 | 2151.12 | 25.89 | 44.644 | 6.35 | 1.382 | 4.886 | 8630.67 | 2.309 | 97.9 | 78 | 1398 | 22.37 | 5609.9 | 1948.1 | 2405.5 | 3106.5 | 1201.5 | 0.62656 | 6.268
2024-12-09 | 19:19 | Data | 0 | 32.204 | 29.955 | 200.697 | 7.62 | 188.48 | 2156.54 | 25.89 | 44.644 | 6.35 | 1.388 | 4.895 | 8626.15 | 2.309 | 97.9 | 77.9 | 1402 | 22.37 | 5607 | 1935.3 | 2398.2 | 3084.8 | 1201.5 | 0.62388 | 6.285
2024-12-09 | 19:19 | Data | 0 | 32.028 | 29.942 | 200.697 | 7.63 | 188.435 | 2158.35 | 25.89 | 44.825 | 6.34 | 1.389 | 4.909 | 8648.76 | 2.086 | 97.9 | 77.9 | 1403 | 22.37 | 5621.7 | 1950.8 | 2394.8 | 3099.8 | 1201.5 | 0.62732 | 6.298
2024-12-09 | 19:19 | Data | 0 | 32.143 | 29.8 | 200.606 | 7.63 | 188.525 | 2154.74 | 25.9 | 44.915 | 6.34 | 1.394 | 4.901 | 9159.77 | 2.174 | 97.9 | 77.8 | 1400 | 22.41 | 5953.9 | 1951.6 | 2399.9 | 3104.6 | 1201.5 | 0.62574 | 6.295
2024-12-09 | 19:19 | Data | 0 | 32.028 | 29.753 | 200.787 | 7.62 | 188.435 | 2152.93 | 25.9 | 44.734 | 6.35 | 1.394 | 4.897 | 8680.41 | 2.309 | 97.9 | 77.8 | 1400 | 22.41 | 5642.3 | 1950.9 | 2400.7 | 3105.1 | 1201.5 | 0.62646 | 6.291
2024-12-09 | 19:19 | Data | 0 | 32.042 | 29.78 | 200.561 | 7.63 | 188.435 | 2152.93 | 25.89 | 44.825 | 6.35 | 1.388 | 4.918 | 8277.94 | 2.194 | 97.9 | 78 | 1400 | 22.41 | 5380.7 | 1944.9 | 2381.2 | 3084.6 | 1201.5 | 0.62842 | 6.307
2024-12-09 | 19:19 | Data | 0 | 32.467 | 29.982 | 200.697 | 7.62 | 188.525 | 2151.12 | 25.89 | 44.825 | 6.34 | 1.395 | 4.92 | 8662.33 | 2.295 | 97.9 | 77.9 | 1399 | 22.41 | 5630.5 | 1972.2 | 2411.8 | 3123.5 | 1201.5 | 0.62986 | 6.314
2024-12-09 | 19:19 | Data | 0 | 32.15 | 29.733 | 200.742 | 7.63 | 188.48 | 2157.45 | 25.89 | 44.825 | 6.34 | 1.389 | 4.917 | 8680.41 | 2.12 | 97.9 | 78 | 1402 | 22.41 | 5642.3 | 1941 | 2425.8 | 3118.4 | 1201.5 | 0.62068 | 6.309
2024-12-09 | 19:19 | Data | 0 | 32.028 | 29.949 | 200.742 | 7.63 | 188.48 | 2155.64 | 25.89 | 44.825 | 6.34 | 1.385 | 4.901 | 8662.33 | 2.275 | 97.9 | 78 | 1401 | 22.41 | 5630.5 | 1952.8 | 2431 | 3128.3 | 1201.5 | 0.61917 | 6.286
2024-12-09 | 19:19 | Data | 0 | 32.015 | 29.928 | 200.742 | 7.63 | 188.39 | 2152.93 | 25.89 | 44.464 | 6.34 | 1.383 | 4.934 | 8666.85 | 2.181 | 97.9 | 78.1 | 1399 | 22.23 | 5633.5 | 1969.8 | 2424.8 | 3135.1 | 1201.5 | 0.6257 | 6.317
2024-12-09 | 19:19 | Data | 0 | 31.839 | 29.928 | 200.832 | 7.63 | 188.571 | 2058.93 | 25.9 | 44.554 | 6.34 | 1.389 | 4.933 | 8680.41 | 2.079 | 97.8 | 78 | 1338 | 22.28 | 5642.3 | 1950.2 | 2388.6 | 3094.4 | 1201.5 | 0.62787 | 6.322
2024-12-09 | 19:19 | Data | 0 | 32.406 | 29.962 | 200.923 | 7.63 | 188.525 | 2163.77 | 25.9 | 44.554 | 6.34 | 1.38 | 4.915 | 8671.37 | 2.383 | 97.9 | 78.1 | 1406 | 22.28 | 5636.4 | 1937 | 2383.2 | 3083.4 | 1201.5 | 0.62672 | 6.295
2024-12-09 | 19:19 | Data | 0 | 32.035 | 29.841 | 200.651 | 7.63 | 188.435 | 2163.77 | 25.89 | 44.644 | 6.35 | 1.388 | 4.907 | 8657.8 | 2.302 | 97.9 | 78 | 1406 | 22.37 | 5627.6 | 1939.3 | 2399.5 | 3094.2 | 1201.5 | 0.62498 | 6.294
2024-12-09 | 19:19 | Data | 0 | 32.028 | 29.726 | 200.516 | 7.63 | 188.345 | 2166.49 | 25.89 | 44.644 | 6.34 | 1.398 | 4.888 | 8671.37 | 2.093 | 97.9 | 77.8 | 1408 | 22.28 | 5636.4 | 1929.5 | 2372.4 | 3070 | 1201.5 | 0.63037 | 6.286
2024-12-09 | 19:20 | Data | 0 | 32.366 | 29.976 | 200.697 | 7.63 | 188.48 | 2166.49 | 25.89 | 44.915 | 6.34 | 1.399 | 4.901 | 8644.24 | 2.484 | 97.9 | 77.8 | 1408 | 22.46 | 5618.8 | 3253.2 | 3407.4 | 4788.1 | 1201.5 | 0.65867 | 6.299
2024-12-09 | 19:20 | Data | 0 | 31.805 | 29.942 | 200.697 | 7.63 | 188.435 | 2161.97 | 25.9 | 44.825 | 6.34 | 1.398 | 4.893 | 8653.28 | 2.201 | 97.9 | 77.8 | 1405 | 22.41 | 5624.6 | 3032.7 | 2960.4 | 4351.8 | 1201.5 | 0.68105 | 6.291
2024-12-09 | 19:20 | Data | 0 | 32.021 | 29.726 | 200.651 | 7.63 | 188.39 | 2166.49 | 25.9 | 44.825 | 6.34 | 1.394 | 4.916 | 8662.33 | 2.187 | 97.9 | 77.9 | 1408 | 22.41 | 5630.5 | 3027 | 2965.2 | 4335.8 | 1201.5 | 0.68314 | 6.31
2024-12-09 | 19:20 | Data | 0 | 32.258 | 29.739 | 200.742 | 7.63 | 188.48 | 2166.49 | 25.89 | 44.734 | 6.34 | 1.398 | 4.904 | 8648.76 | 2.302 | 97.9 | 77.8 | 1408 | 22.37 | 5621.7 | 3039.3 | 2952.5 | 4352.3 | 1201.5 | 0.67935 | 6.303
2024-12-09 | 19:20 | Data | 0 | 32.028 | 29.638 | 200.651 | 7.63 | 188.39 | 2163.77 | 25.9 | 44.825 | 6.33 | 1.397 | 4.916 | 8644.24 | 2.194 | 97.9 | 77.9 | 1407 | 22.41 | 5618.8 | 3027.3 | 2962.5 | 4352.6 | 1201.5 | 0.67824 | 6.311
2024-12-09 | 19:20 | Data | 0 | 32.258 | 30.171 | 200.832 | 7.63 | 188.571 | 2166.49 | 25.89 | 44.825 | 6.34 | 1.394 | 4.915 | 8662.33 | 2.093 | 97.9 | 77.9 | 1409 | 22.41 | 5630.5 | 3053.7 | 2972.6 | 4371.5 | 1201.5 | 0.68181 | 6.309
2024-12-09 | 19:20 | Data | 0 | 31.805 | 29.699 | 200.697 | 7.62 | 188.48 | 2165.58 | 25.89 | 44.915 | 6.34 | 1.38 | 4.918 | 8639.71 | 2.241 | 97.9 | 78.1 | 1407 | 22.41 | 5615.8 | 3047.2 | 2975.6 | 4373.3 | 1201.5 | 0.68142 | 6.299
2024-12-09 | 19:20 | Data | 0 | 31.988 | 29.739 | 200.787 | 7.63 | 188.48 | 2163.77 | 25.9 | 44.915 | 6.34 | 1.385 | 4.911 | 8644.24 | 2.39 | 97.9 | 78 | 1406 | 22.37 | 5618.8 | 3019.6 | 2976.6 | 4354.8 | 1201.5 | 0.67749 | 6.296
2024-12-09 | 19:20 | Data | 0 | 32.366 | 29.868 | 200.742 | 7.62 | 188.435 | 2163.77 | 25.89 | 44.825 | 6.34 | 1.397 | 4.904 | 8662.33 | 2.302 | 97.9 | 77.8 | 1406 | 22.41 | 5630.5 | 3048.4 | 2975.1 | 4369.6 | 1201.5 | 0.68193 | 6.301
2024-12-09 | 19:20 | Data | 0 | 31.799 | 29.739 | 200.742 | 7.63 | 188.48 | 2163.77 | 25.89 | 44.554 | 6.34 | 1.391 | 4.91 | 8644.24 | 2.39 | 97.9 | 77.9 | 1406 | 22.28 | 5618.8 | 3037.7 | 2976.3 | 4366.3 | 1201.5 | 0.68099 | 6.301
2024-12-09 | 19:20 | Data | 0 | 32.028 | 29.726 | 200.697 | 7.63 | 188.435 | 2163.77 | 25.89 | 44.554 | 6.34 | 1.387 | 4.922 | 8662.33 | 2.181 | 97.9 | 78 | 1407 | 22.28 | 5630.5 | 3048.6 | 2937 | 4344.3 | 1201.5 | 0.6846 | 6.31
2024-12-09 | 19:20 | Data | 0 | 32.258 | 30.131 | 200.878 | 7.62 | 188.48 | 2158.35 | 25.89 | 44.554 | 6.34 | 1.384 | 4.91 | 8671.37 | 2.302 | 97.9 | 78 | 1403 | 22.28 | 5636.4 | 3051.4 | 2958.2 | 4364 | 1201.5 | 0.6822 | 6.293
2024-12-09 | 19:20 | Data | 0 | 32.433 | 30.07 | 200.742 | 7.63 | 188.525 | 2163.77 | 25.89 | 44.554 | 6.35 | 1.376 | 4.904 | 8653.28 | 2.302 | 97.9 | 78.1 | 1406 | 22.28 | 5624.6 | 3032.6 | 2954 | 4353.3 | 1201.5 | 0.68003 | 6.279
2024-12-09 | 19:20 | Data | 0 | 32.042 | 29.739 | 200.787 | 7.62 | 188.525 | 2163.77 | 25.89 | 44.915 | 6.34 | 1.379 | 4.927 | 8635.19 | 2.289 | 97.9 | 78.1 | 1406 | 22.46 | 5612.9 | 3041.8 | 2969.6 | 4362.7 | 1201.5 | 0.68065 | 6.306
2024-12-09 | 19:20 | Data | 0 | 31.92 | 29.726 | 200.697 | 7.63 | 188.435 | 2163.77 | 25.89 | 44.734 | 6.35 | 1.387 | 4.943 | 8648.76 | 2.289 | 97.9 | 78.1 | 1406 | 22.41 | 5621.7 | 3044.1 | 2960.8 | 4358.7 | 1201.6 | 0.68312 | 6.33
2024-12-09 | 19:20 | Data | 0 | 32.46 | 29.766 | 200.651 | 7.62 | 188.525 | 2161.97 | 25.9 | 44.644 | 6.34 | 1.388 | 4.925 | 8626.15 | 2.295 | 97.9 | 78 | 1405 | 22.32 | 5607 | 3036.7 | 2957.6 | 4357 | 1201.6 | 0.68107 | 6.314
2024-12-09 | 19:20 | Data | 0 | 31.947 | 29.834 | 200.742 | 7.63 | 188.435 | 2158.35 | 25.89 | 44.554 | 6.35 | 1.393 | 4.932 | 8626.15 | 2.066 | 97.9 | 78 | 1403 | 22.28 | 5607 | 3014 | 2960.6 | 4340 | 1201.6 | 0.67693 | 6.325
2024-12-09 | 19:20 | Data | 0 | 32.089 | 29.76 | 200.832 | 7.63 | 188.525 | 2163.77 | 25.9 | 44.554 | 6.34 | 1.381 | 4.903 | 8621.63 | 2.336 | 97.9 | 78 | 1406 | 22.28 | 5604.1 | 3037.5 | 2930.9 | 4336.6 | 1201.6 | 0.68529 | 6.285
2024-12-09 | 19:21 | Data | 0 | 31.886 | 29.895 | 200.787 | 7.63 | 188.525 | 2163.77 | 25.89 | 45.005 | 6.34 | 1.385 | 4.91 | 8630.67 | 2.295 | 97.9 | 78 | 1407 | 22.5 | 5609.9 | 3055.5 | 2965.6 | 4368.1 | 1201.6 | 0.68316 | 6.294
2024-12-09 | 19:21 | Data | 0 | 32.001 | 29.942 | 200.697 | 7.62 | 188.345 | 2164.68 | 25.9 | 44.554 | 6.34 | 1.387 | 4.905 | 8635.19 | 2.127 | 97.9 | 78 | 1407 | 22.32 | 5612.9 | 3031.8 | 2938.6 | 4334.2 | 1201.6 | 0.68407 | 6.291
2024-12-09 | 19:21 | Data | 0 | 31.812 | 29.679 | 200.606 | 7.63 | 188.39 | 2163.77 | 25.89 | 44.554 | 6.34 | 1.387 | 4.901 | 8657.8 | 2.241 | 97.9 | 77.9 | 1407 | 22.28 | 5627.6 | 3044.6 | 2930.3 | 4338.5 | 1201.6 | 0.68557 | 6.289
2024-12-09 | 19:21 | Data | 0 | 32.082 | 29.847 | 200.697 | 7.62 | 188.435 | 2165.58 | 25.89 | 44.554 | 6.34 | 1.388 | 4.917 | 8707.55 | 2.309 | 97.9 | 78 | 1408 | 22.28 | 5659.9 | 3045.6 | 2956.9 | 4358.2 | 1201.6 | 0.68279 | 6.305
2024-12-09 | 19:21 | Data | 0 | 32.015 | 29.719 | 200.697 | 7.63 | 188.435 | 2166.49 | 25.89 | 44.464 | 6.34 | 1.394 | 4.911 | 8703.03 | 2.309 | 97.9 | 77.9 | 1408 | 22.28 | 5657 | 3039.8 | 2955.4 | 4351.8 | 1201.6 | 0.68298 | 6.303
2024-12-09 | 19:21 | Data | 0 | 31.927 | 29.949 | 200.697 | 7.63 | 188.435 | 2165.58 | 25.89 | 44.554 | 6.34 | 1.388 | 4.929 | 8703.03 | 2.093 | 97.9 | 78 | 1408 | 22.28 | 5657 | 3052.9 | 2971.6 | 4374.1 | 1201.6 | 0.68172 | 6.319
2024-12-09 | 19:21 | Data | 0 | 31.913 | 29.726 | 200.651 | 7.63 | 188.39 | 2167.39 | 25.89 | 44.554 | 6.34 | 1.389 | 4.898 | 8703.03 | 2.086 | 98 | 77.9 | 1410 | 22.23 | 5657 | 3053.5 | 2957.9 | 4365.7 | 1201.6 | 0.68244 | 6.288
2024-12-09 | 19:21 | Data | 0 | 31.9 | 29.712 | 200.651 | 7.62 | 188.48 | 2170.1 | 25.89 | 44.644 | 6.34 | 1.395 | 4.9 | 8635.19 | 2.295 | 97.9 | 77.8 | 1411 | 22.32 | 5612.9 | 3034.5 | 2974.6 | 4365.5 | 1201.6 | 0.67767 | 6.296
2024-12-09 | 19:21 | Data | 0 | 32.143 | 30.165 | 200.787 | 7.63 | 188.435 | 2170.1 | 25.89 | 44.554 | 6.34 | 1.39 | 4.934 | 8617.1 | 2.275 | 97.9 | 78 | 1411 | 22.32 | 5601.1 | 3045.2 | 2974.9 | 4370.4 | 1201.6 | 0.68012 | 6.323
2024-12-09 | 19:21 | Data | 0 | 32.069 | 29.942 | 200.561 | 7.63 | 188.39 | 2166.49 | 25.89 | 44.644 | 6.34 | 1.392 | 4.902 | 8626.15 | 2.113 | 97.9 | 77.9 | 1408 | 22.28 | 5607 | 3034.7 | 2963.4 | 4356.3 | 1201.6 | 0.68012 | 6.294
2024-12-09 | 19:21 | Data | 0 | 31.92 | 29.726 | 200.697 | 7.62 | 188.48 | 2162.87 | 25.89 | 44.554 | 6.34 | 1.393 | 4.878 | 8621.63 | 2.289 | 97.9 | 77.8 | 1406 | 22.32 | 5604.1 | 3054.5 | 2950.2 | 4359.9 | 1201.6 | 0.68439 | 6.27
2024-12-09 | 19:21 | Data | 0 | 31.913 | 29.719 | 200.697 | 7.62 | 188.435 | 2162.87 | 25.89 | 44.464 | 6.34 | 1.395 | 4.885 | 8703.03 | 2.1 | 97.9 | 77.8 | 1406 | 22.28 | 5657 | 3034.4 | 2939 | 4346.9 | 1201.6 | 0.68224 | 6.28
2024-12-09 | 19:21 | Data | 0 | 32.035 | 29.726 | 200.651 | 7.62 | 188.435 | 2163.77 | 25.89 | 44.554 | 6.34 | 1.383 | 4.917 | 8693.98 | 2.1 | 97.9 | 78 | 1406 | 22.28 | 5651.1 | 3042.1 | 2962.2 | 4358.8 | 1201.6 | 0.68138 | 6.3
2024-12-09 | 19:21 | Data | 0 | 32.204 | 29.976 | 200.742 | 7.63 | 188.435 | 2164.68 | 25.89 | 44.554 | 6.35 | 1.378 | 4.905 | 8693.98 | 2.268 | 97.9 | 78.1 | 1407 | 22.32 | 5651.1 | 3034.5 | 2937.5 | 4336.9 | 1201.6 | 0.6835 | 6.283
2024-12-09 | 19:21 | Data | 0 | 31.799 | 29.901 | 200.651 | 7.63 | 188.39 | 2164.68 | 25.89 | 44.373 | 6.34 | 1.384 | 4.915 | 8689.46 | 2.187 | 97.9 | 78 | 1406 | 22.19 | 5648.1 | 3032.3 | 2962.2 | 4355 | 1201.6 | 0.68078 | 6.299
2024-12-09 | 19:21 | Data | 0 | 32.028 | 29.726 | 200.787 | 7.62 | 188.435 | 2163.77 | 25.89 | 44.644 | 6.34 | 1.388 | 4.911 | 8689.46 | 2.302 | 97.9 | 77.9 | 1406 | 22.32 | 5648.1 | 3031.6 | 2980.3 | 4365.8 | 1201.6 | 0.67823 | 6.3
2024-12-09 | 19:21 | Data | 0 | 32.055 | 30.111 | 200.697 | 7.62 | 188.525 | 2163.77 | 25.89 | 44.554 | 6.34 | 1.395 | 4.905 | 8680.41 | 2.133 | 97.9 | 77.9 | 1406 | 22.28 | 5642.3 | 3049.6 | 2983.6 | 4383.5 | 1201.6 | 0.67932 | 6.3
2024-12-09 | 19:21 | Data | 0 | 31.805 | 29.719 | 200.697 | 7.63 | 188.435 | 2163.77 | 25.89 | 44.554 | 6.34 | 1.39 | 4.915 | 8680.41 | 2.262 | 97.9 | 78 | 1406 | 22.28 | 5642.3 | 3041 | 2953.5 | 4353.1 | 1201.6 | 0.68234 | 6.305
2024-12-09 | 19:22 | Data | 0 | 32.028 | 29.733 | 200.832 | 7.62 | 188.39 | 2158.35 | 25.89 | 44.554 | 6.34 | 1.39 | 4.92 | 9119.07 | 2.275 | 97.9 | 78 | 1403 | 22.28 | 5927.4 | 3035.1 | 2946.4 | 4353 | 1201.6 | 0.68379 | 6.31
2024-12-09 | 19:22 | Data | 0 | 32.177 | 29.726 | 200.697 | 7.62 | 188.525 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.389 | 4.896 | 8716.59 | 2.113 | 97.9 | 77.9 | 1405 | 22.32 | 5665.8 | 3044.8 | 2948.1 | 4350.5 | 1201.6 | 0.68391 | 6.285
2024-12-09 | 19:22 | Data | 0 | 32.42 | 29.814 | 201.058 | 7.63 | 188.571 | 2161.97 | 25.89 | 44.554 | 6.34 | 1.387 | 4.901 | 8716.59 | 2.41 | 97.9 | 77.9 | 1405 | 22.28 | 5665.8 | 3054.7 | 2938.3 | 4353.6 | 1201.6 | 0.68522 | 6.289
2024-12-09 | 19:22 | Data | 0 | 31.913 | 29.733 | 200.697 | 7.63 | 188.345 | 2163.77 | 25.89 | 44.644 | 6.34 | 1.389 | 4.897 | 8703.03 | 2.282 | 97.9 | 77.9 | 1407 | 22.32 | 5657 | 3024.7 | 2930.6 | 4326.4 | 1201.6 | 0.68294 | 6.286
2024-12-09 | 19:22 | Data | 0 | 32.258 | 29.969 | 200.968 | 7.63 | 188.616 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.398 | 4.924 | 8689.46 | 2.451 | 97.9 | 77.9 | 1405 | 22.23 | 5648.1 | 3031.1 | 2944 | 4336.9 | 1201.6 | 0.68269 | 6.322
2024-12-09 | 19:22 | Data | 0 | 32.028 | 29.571 | 200.742 | 7.63 | 188.48 | 2161.97 | 25.9 | 44.825 | 6.34 | 1.401 | 4.914 | 8666.85 | 2.302 | 97.9 | 77.8 | 1405 | 22.41 | 5633.5 | 3034.7 | 2940.4 | 4339.1 | 1201.6 | 0.68193 | 6.316
2024-12-09 | 19:22 | Data | 0 | 32.386 | 29.847 | 200.878 | 7.63 | 188.616 | 2158.35 | 25.89 | 44.825 | 6.34 | 1.388 | 4.916 | 8648.76 | 2.025 | 97.9 | 78 | 1403 | 22.41 | 5621.7 | 3057.2 | 2937.5 | 4349.6 | 1201.6 | 0.68705 | 6.302
2024-12-09 | 19:22 | Data | 0 | 31.913 | 29.726 | 200.787 | 7.63 | 188.435 | 2158.35 | 25.89 | 44.644 | 6.34 | 1.384 | 4.915 | 8626.15 | 2.248 | 97.9 | 78 | 1403 | 22.28 | 5607 | 3060.6 | 2959.2 | 4369.2 | 1201.6 | 0.68488 | 6.299
2024-12-09 | 19:22 | Data | 0 | 31.981 | 29.901 | 200.651 | 7.63 | 188.435 | 2158.35 | 25.9 | 44.825 | 6.34 | 1.387 | 4.912 | 8644.24 | 2.16 | 97.9 | 78 | 1403 | 22.41 | 5618.8 | 3049.1 | 2941.5 | 4342.4 | 1201.6 | 0.68664 | 6.301
2024-12-09 | 19:22 | Data | 0 | 31.913 | 29.841 | 200.651 | 7.62 | 188.345 | 2158.35 | 25.89 | 44.825 | 6.34 | 1.395 | 4.929 | 8635.19 | 2.289 | 97.9 | 78 | 1404 | 22.46 | 5612.9 | 3044.5 | 2933.5 | 4339.1 | 1201.6 | 0.68618 | 6.324
2024-12-09 | 19:22 | Data | 0 | 32.102 | 29.739 | 200.697 | 7.63 | 188.525 | 2158.35 | 25.89 | 44.825 | 6.35 | 1.395 | 4.938 | 8621.63 | 2.174 | 97.9 | 78 | 1404 | 22.41 | 5604.1 | 3045.6 | 2944.9 | 4348.3 | 1201.6 | 0.68433 | 6.334
2024-12-09 | 19:22 | Data | 0 | 32.197 | 30.063 | 200.787 | 7.63 | 188.525 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.397 | 4.919 | 8635.19 | 2.194 | 97.9 | 77.9 | 1405 | 22.28 | 5612.9 | 3015.2 | 2939.7 | 4326.4 | 1201.7 | 0.68072 | 6.317
2024-12-09 | 19:22 | Data | 0 | 31.974 | 30.05 | 200.787 | 7.63 | 188.525 | 2158.35 | 25.89 | 44.825 | 6.34 | 1.38 | 4.909 | 8635.19 | 2.248 | 97.9 | 78.1 | 1403 | 22.46 | 5612.9 | 3048.5 | 2918.1 | 4330.2 | 1201.7 | 0.68756 | 6.289
2024-12-09 | 19:22 | Data | 0 | 32.028 | 29.726 | 200.697 | 7.62 | 188.48 | 2161.06 | 25.89 | 44.825 | 6.34 | 1.377 | 4.899 | 8648.76 | 2.295 | 97.9 | 78.1 | 1405 | 22.46 | 5621.7 | 3051.8 | 2927.8 | 4342 | 1201.7 | 0.68542 | 6.276
2024-12-09 | 19:22 | Data | 0 | 32.258 | 30.124 | 200.787 | 7.63 | 188.48 | 2158.35 | 25.9 | 44.825 | 6.34 | 1.389 | 4.903 | 8635.19 | 2.194 | 97.9 | 77.9 | 1404 | 22.41 | 5612.9 | 3058.7 | 2940.1 | 4356.3 | 1201.7 | 0.68588 | 6.292
2024-12-09 | 19:22 | Data | 0 | 32.028 | 29.901 | 200.787 | 7.62 | 188.39 | 2161.97 | 25.89 | 44.825 | 6.35 | 1.385 | 4.876 | 8630.67 | 2.187 | 97.9 | 77.9 | 1405 | 22.41 | 5609.9 | 3036.6 | 2939.3 | 4338.8 | 1201.7 | 0.68437 | 6.261
2024-12-09 | 19:23 | Data | 0 | 31.805 | 29.557 | 200.787 | 7.63 | 188.435 | 2159.26 | 25.89 | 44.825 | 6.34 | 1.385 | 4.881 | 8635.19 | 2.302 | 97.9 | 77.9 | 1403 | 22.41 | 5612.9 | 3045.3 | 2965 | 4363.5 | 1201.7 | 0.68286 | 6.263
2024-12-09 | 19:23 | Data | 0 | 32.244 | 30.07 | 200.742 | 7.62 | 188.525 | 2161.06 | 25.9 | 44.825 | 6.35 | 1.391 | 4.909 | 8617.1 | 2.309 | 97.9 | 77.9 | 1404 | 22.41 | 5601.1 | 3066.7 | 2948.3 | 4372.2 | 1201.7 | 0.68409 | 6.3
2024-12-09 | 19:23 | Data | 0 | 32.366 | 29.854 | 200.878 | 7.63 | 188.571 | 2161.06 | 25.89 | 44.825 | 6.34 | 1.389 | 4.907 | 8626.15 | 2.363 | 97.9 | 77.9 | 1405 | 22.37 | 5607 | 3049.6 | 2938.2 | 4351.7 | 1201.7 | 0.68527 | 6.296
2024-12-09 | 19:23 | Data | 0 | 31.913 | 29.955 | 200.697 | 7.63 | 188.48 | 2163.77 | 25.89 | 44.825 | 6.35 | 1.386 | 4.907 | 8608.06 | 2.248 | 97.9 | 78 | 1406 | 22.41 | 5595.2 | 3045.3 | 2934.2 | 4346 | 1201.7 | 0.68382 | 6.293
2024-12-09 | 19:23 | Data | 0 | 32.102 | 29.76 | 200.787 | 7.63 | 188.571 | 2166.49 | 25.9 | 44.825 | 6.35 | 1.392 | 4.893 | 8621.63 | 2.106 | 97.9 | 77.8 | 1408 | 22.41 | 5604.1 | 3055.5 | 2947.7 | 4365.1 | 1201.7 | 0.68387 | 6.286
2024-12-09 | 19:23 | Data | 0 | 31.974 | 29.82 | 200.742 | 7.63 | 188.525 | 2164.68 | 25.89 | 44.825 | 6.35 | 1.382 | 4.931 | 8621.63 | 2.376 | 97.9 | 78.1 | 1407 | 22.41 | 5604.1 | 3073.4 | 2970.9 | 4387.1 | 1201.7 | 0.68434 | 6.313
2024-12-09 | 19:23 | Data | 0 | 32.055 | 29.834 | 200.787 | 7.63 | 188.48 | 2161.97 | 25.89 | 44.554 | 6.35 | 1.38 | 4.896 | 8635.19 | 2.093 | 97.9 | 78 | 1405 | 22.32 | 5612.9 | 3059.1 | 2942.4 | 4362 | 1201.7 | 0.68534 | 6.275
2024-12-09 | 19:23 | Data | 0 | 32.595 | 30.117 | 200.832 | 7.63 | 188.616 | 2162.87 | 25.89 | 44.644 | 6.34 | 1.376 | 4.909 | 8635.19 | 2.275 | 97.9 | 78.1 | 1406 | 22.32 | 5612.9 | 3052 | 2930.1 | 4347 | 1201.7 | 0.68573 | 6.284
2024-12-09 | 19:23 | Data | 0 | 31.799 | 29.618 | 200.651 | 7.63 | 188.39 | 2163.77 | 25.89 | 44.464 | 6.34 | 1.387 | 4.925 | 8621.63 | 2.356 | 97.9 | 78 | 1406 | 22.28 | 5604.1 | 3052.6 | 2948.6 | 4359 | 1201.7 | 0.68445 | 6.311
2024-12-09 | 19:23 | Data | 0 | 32.204 | 29.739 | 200.787 | 7.63 | 188.525 | 2166.49 | 25.9 | 44.554 | 6.35 | 1.394 | 4.891 | 8639.71 | 2.106 | 97.9 | 77.8 | 1408 | 22.28 | 5615.8 | 3092.5 | 2958.2 | 4396.2 | 1201.7 | 0.68358 | 6.286
2024-12-09 | 19:23 | Data | 0 | 32.291 | 30.178 | 200.923 | 7.63 | 188.616 | 2167.39 | 25.89 | 44.644 | 6.35 | 1.395 | 4.866 | 8635.19 | 2.1 | 97.9 | 77.7 | 1408 | 22.28 | 5612.9 | 3064.5 | 2934.1 | 4356.9 | 1201.7 | 0.68725 | 6.261
2024-12-09 | 19:23 | Data | 0 | 32.136 | 29.962 | 200.787 | 7.63 | 188.525 | 2167.39 | 25.89 | 44.644 | 6.34 | 1.382 | 4.915 | 8635.19 | 2.39 | 97.9 | 78.1 | 1408 | 22.28 | 5612.9 | 3071.2 | 2967 | 4383.8 | 1201.7 | 0.68468 | 6.298
2024-12-09 | 19:23 | Data | 0 | 32.109 | 29.733 | 200.787 | 7.63 | 188.525 | 2170.1 | 25.89 | 44.554 | 6.35 | 1.396 | 4.914 | 8639.71 | 2.106 | 97.9 | 77.9 | 1410 | 22.32 | 5615.8 | 3059.1 | 2934.6 | 4351.1 | 1201.7 | 0.68742 | 6.31
2024-12-09 | 19:23 | Data | 0 | 32.021 | 29.901 | 200.787 | 7.63 | 188.525 | 2170.1 | 25.89 | 44.554 | 6.35 | 1.4 | 4.937 | 8635.19 | 2.187 | 97.9 | 77.9 | 1410 | 22.32 | 5612.9 | 3069.7 | 2954.6 | 4378.1 | 1201.7 | 0.68452 | 6.337
2024-12-09 | 19:23 | Data | 0 | 32.251 | 29.753 | 200.742 | 7.63 | 188.435 | 2172.81 | 25.9 | 44.554 | 6.34 | 1.393 | 4.908 | 8666.85 | 2.309 | 98 | 77.9 | 1412 | 22.23 | 5633.5 | 3067.5 | 2931 | 4351.7 | 1201.7 | 0.68756 | 6.3
2024-12-09 | 19:23 | Data | 0 | 31.913 | 30.057 | 200.742 | 7.62 | 188.39 | 2166.49 | 25.89 | 44.554 | 6.34 | 1.387 | 4.939 | 8666.85 | 2.228 | 97.9 | 78.1 | 1408 | 22.28 | 5633.5 | 3062.4 | 2947 | 4371.7 | 1201.7 | 0.68448 | 6.327
2024-12-09 | 19:23 | Data | 0 | 32.028 | 29.955 | 200.742 | 7.63 | 188.48 | 2166.49 | 25.89 | 44.554 | 6.34 | 1.386 | 4.96 | 8666.85 | 2.282 | 97.9 | 78.2 | 1408 | 22.28 | 5633.5 | 3054.5 | 2957.8 | 4368.1 | 1201.7 | 0.68203 | 6.346
2024-12-09 | 19:23 | Data | 0 | 31.805 | 29.78 | 200.697 | 7.62 | 188.48 | 2167.39 | 25.89 | 44.554 | 6.35 | 1.385 | 4.939 | 8653.28 | 2.133 | 97.9 | 78.1 | 1409 | 22.28 | 5624.6 | 3053 | 2936.6 | 4351.9 | 1201.7 | 0.68197 | 6.324
2024-12-09 | 19:24 | Data | 0 | 31.988 | 29.955 | 200.787 | 7.63 | 188.525 | 2166.49 | 25.89 | 44.554 | 6.35 | 1.395 | 4.907 | 8662.33 | 2.181 | 97.9 | 77.9 | 1409 | 22.28 | 5630.5 | 3066.6 | 2954.4 | 4377.7 | 1201.7 | 0.68333 | 6.301
2024-12-09 | 19:24 | Data | 0 | 32.028 | 29.949 | 200.697 | 7.63 | 188.48 | 2169.2 | 25.89 | 44.644 | 6.34 | 1.391 | 4.934 | 8671.37 | 2.255 | 97.9 | 78 | 1411 | 22.28 | 5636.4 | 3065.4 | 2943.5 | 4367.1 | 1201.7 | 0.68612 | 6.325
2024-12-09 | 19:24 | Data | 0 | 31.751 | 29.638 | 200.697 | 7.63 | 188.345 | 2170.1 | 25.89 | 44.554 | 6.35 | 1.383 | 4.919 | 8635.19 | 2.289 | 97.9 | 78.1 | 1410 | 22.28 | 5612.9 | 3058.3 | 2949.2 | 4372.3 | 1201.7 | 0.68273 | 6.301
2024-12-09 | 19:24 | Data | 0 | 32.46 | 30.07 | 200.878 | 7.63 | 188.571 | 2170.1 | 25.89 | 44.554 | 6.35 | 1.396 | 4.915 | 8639.71 | 2.309 | 97.9 | 77.9 | 1411 | 22.23 | 5615.8 | 3063.4 | 2941.3 | 4361.2 | 1201.7 | 0.68642 | 6.311
2024-12-09 | 19:24 | Data | 0 | 32.028 | 29.726 | 200.742 | 7.62 | 188.571 | 2077.91 | 25.89 | 44.554 | 6.34 | 1.384 | 4.897 | 8635.19 | 2.464 | 97.9 | 78 | 1349 | 22.28 | 5612.9 | 3049.6 | 2976.9 | 4382.9 | 1201.7 | 0.67977 | 6.281
2024-12-09 | 19:24 | Data | 0 | 32.204 | 30.057 | 200.787 | 7.62 | 188.48 | 2143.89 | 25.9 | 44.644 | 6.34 | 1.382 | 4.911 | 8630.67 | 2.201 | 97.9 | 78 | 1396 | 22.32 | 5609.9 | 3063.6 | 2951.5 | 4371.4 | 1201.7 | 0.68473 | 6.294
2024-12-09 | 19:24 | Data | 0 | 32.075 | 29.733 | 200.697 | 7.63 | 188.435 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.39 | 4.91 | 8657.8 | 2.187 | 97.9 | 77.9 | 1405 | 22.28 | 5627.6 | 3068.4 | 2958.1 | 4380 | 1201.7 | 0.68528 | 6.301
2024-12-09 | 19:24 | Data | 0 | 31.934 | 29.679 | 200.832 | 7.63 | 188.571 | 2159.26 | 25.89 | 44.554 | 6.35 | 1.384 | 4.921 | 8662.33 | 2.181 | 97.9 | 78.1 | 1404 | 22.28 | 5630.5 | 3054.2 | 2958.2 | 4368.7 | 1201.7 | 0.68178 | 6.304
2024-12-09 | 19:24 | Data | 0 | 32.028 | 29.841 | 200.606 | 7.62 | 188.345 | 2156.54 | 25.9 | 44.554 | 6.34 | 1.383 | 4.91 | 8268.89 | 2.187 | 97.9 | 78 | 1402 | 22.28 | 5374.8 | 3071 | 2974.7 | 4392.7 | 1201.7 | 0.68268 | 6.291
2024-12-09 | 19:24 | Data | 0 | 32.399 | 29.955 | 200.742 | 7.63 | 188.48 | 2158.35 | 25.89 | 44.644 | 6.35 | 1.394 | 4.901 | 8599.01 | 2.41 | 97.9 | 77.9 | 1403 | 22.32 | 5589.4 | 2993.8 | 2958.3 | 4322.2 | 1201.7 | 0.67809 | 6.295
2024-12-09 | 19:24 | Data | 0 | 32.453 | 29.982 | 200.923 | 7.62 | 188.571 | 2159.26 | 25.89 | 44.283 | 6.34 | 1.384 | 4.898 | 8621.63 | 2.424 | 97.9 | 78 | 1404 | 22.14 | 5604.1 | 3023.5 | 2959.2 | 4338 | 1201.7 | 0.68165 | 6.282
2024-12-09 | 19:24 | Data | 0 | 31.913 | 29.841 | 200.651 | 7.63 | 188.39 | 2162.87 | 25.89 | 44.554 | 6.35 | 1.382 | 4.904 | 8580.93 | 2.289 | 97.9 | 78 | 1406 | 22.28 | 5577.6 | 2984.6 | 2942.1 | 4305.3 | 1201.7 | 0.6768 | 6.286
2024-12-09 | 19:24 | Data | 0 | 32.474 | 29.76 | 200.787 | 7.63 | 188.48 | 2164.68 | 25.9 | 44.554 | 6.34 | 1.387 | 4.884 | 8580.93 | 2.376 | 97.9 | 77.9 | 1407 | 22.28 | 5577.6 | 2968.1 | 2944.8 | 4291.9 | 1201.8 | 0.67512 | 6.272
2024-12-09 | 19:24 | Data | 0 | 31.63 | 29.719 | 200.651 | 7.63 | 188.48 | 2170.1 | 25.89 | 44.644 | 6.35 | 1.391 | 4.905 | 8585.45 | 2.1 | 97.9 | 77.9 | 1411 | 22.28 | 5580.5 | 2989.5 | 2948.7 | 4314.7 | 1201.8 | 0.67898 | 6.297
2024-12-09 | 19:24 | Data | 0 | 32.116 | 29.739 | 200.697 | 7.63 | 188.39 | 2167.39 | 25.89 | 44.554 | 6.35 | 1.394 | 4.921 | 8608.06 | 2.491 | 97.9 | 77.9 | 1409 | 22.28 | 5595.2 | 3005 | 2969.9 | 4338.9 | 1201.8 | 0.6763 | 6.315
2024-12-09 | 19:24 | Data | 0 | 31.812 | 29.949 | 200.787 | 7.62 | 188.435 | 2166.49 | 25.89 | 44.554 | 6.35 | 1.38 | 4.913 | 8639.71 | 2.046 | 97.9 | 78.1 | 1408 | 22.28 | 5615.8 | 2985.8 | 2951.9 | 4311.2 | 1201.8 | 0.67757 | 6.293
2024-12-09 | 19:24 | Data | 0 | 32.028 | 30.097 | 200.697 | 7.62 | 188.435 | 2166.49 | 25.89 | 44.554 | 6.34 | 1.382 | 4.92 | 8639.71 | 2.302 | 97.9 | 78.1 | 1408 | 22.28 | 5615.8 | 2992.2 | 2934.3 | 4302.8 | 1201.8 | 0.68005 | 6.301
2024-12-09 | 19:24 | Data | 0 | 31.873 | 29.814 | 200.606 | 7.63 | 188.435 | 2166.49 | 25.89 | 44.554 | 6.34 | 1.38 | 4.895 | 8653.28 | 2.032 | 97.9 | 78 | 1408 | 22.28 | 5624.6 | 2994.1 | 2931.5 | 4304 | 1201.8 | 0.68141 | 6.274
2024-12-09 | 19:25 | Data | 0 | 31.643 | 29.584 | 200.516 | 7.63 | 188.345 | 2166.49 | 25.89 | 44.554 | 6.35 | 1.381 | 4.882 | 8648.76 | 2.079 | 97.9 | 77.9 | 1408 | 22.28 | 5621.7 | 3049.6 | 2943.5 | 4355.7 | 1201.8 | 0.68432 | 6.265
2024-12-09 | 19:25 | Data | 0 | 31.907 | 29.726 | 200.697 | 7.62 | 188.435 | 2161.97 | 25.89 | 44.644 | 6.35 | 1.391 | 4.912 | 8648.76 | 2.262 | 97.9 | 77.9 | 1405 | 22.32 | 5621.7 | 3037.1 | 2944.6 | 4347.6 | 1201.8 | 0.68246 | 6.303
2024-12-09 | 19:25 | Data | 0 | 31.799 | 29.496 | 200.561 | 7.62 | 188.345 | 2166.49 | 25.89 | 44.554 | 6.34 | 1.392 | 4.895 | 8644.24 | 2.356 | 97.9 | 77.9 | 1409 | 22.32 | 5618.8 | 3056.2 | 2951.6 | 4361.3 | 1201.8 | 0.68455 | 6.287
2024-12-09 | 19:25 | Data | 0 | 32.258 | 29.733 | 200.787 | 7.63 | 188.435 | 2166.49 | 25.89 | 44.554 | 6.35 | 1.397 | 4.902 | 8644.24 | 2.322 | 97.9 | 77.8 | 1408 | 22.32 | 5618.8 | 3049.6 | 2953 | 4356.1 | 1201.8 | 0.68412 | 6.3
2024-12-09 | 19:25 | Data | 0 | 31.913 | 29.712 | 200.787 | 7.63 | 188.435 | 2169.2 | 25.9 | 44.644 | 6.34 | 1.39 | 4.91 | 8684.94 | 2.201 | 97.9 | 77.9 | 1410 | 22.28 | 5645.2 | 3064.2 | 2933.2 | 4357.8 | 1201.8 | 0.68496 | 6.301
2024-12-09 | 19:25 | Data | 0 | 31.812 | 29.827 | 200.742 | 7.63 | 188.48 | 2166.49 | 25.89 | 44.464 | 6.35 | 1.387 | 4.917 | 8680.41 | 2.086 | 97.9 | 78 | 1408 | 22.28 | 5642.3 | 3040.9 | 2922.4 | 4339.9 | 1201.8 | 0.68677 | 6.303
2024-12-09 | 19:25 | Data | 0 | 32.028 | 29.733 | 200.651 | 7.63 | 188.435 | 2165.58 | 25.89 | 44.554 | 6.35 | 1.388 | 4.909 | 8662.33 | 2.275 | 97.9 | 78 | 1408 | 22.32 | 5630.5 | 3026.8 | 2934.4 | 4329.5 | 1201.8 | 0.68294 | 6.296
2024-12-09 | 19:25 | Data | 0 | 31.805 | 29.55 | 200.606 | 7.63 | 188.39 | 2170.1 | 25.89 | 44.554 | 6.35 | 1.389 | 4.91 | 8662.33 | 2.302 | 97.9 | 77.9 | 1411 | 22.32 | 5630.5 | 3044.9 | 2922.8 | 4335 | 1201.8 | 0.68571 | 6.299
2024-12-09 | 19:25 | Data | 0 | 31.643 | 29.496 | 200.561 | 7.62 | 188.48 | 2163.77 | 25.89 | 44.644 | 6.35 | 1.393 | 4.904 | 8662.33 | 2.073 | 97.9 | 77.9 | 1407 | 22.32 | 5630.5 | 3056.8 | 2942.1 | 4353.3 | 1201.8 | 0.68569 | 6.298
2024-12-09 | 19:25 | Data | 0 | 31.832 | 29.827 | 200.742 | 7.62 | 188.525 | 2163.77 | 25.89 | 44.644 | 6.35 | 1.393 | 4.931 | 8644.24 | 2.127 | 97.9 | 78 | 1406 | 22.28 | 5618.8 | 3033.1 | 2950.3 | 4348.8 | 1201.8 | 0.67986 | 6.325
2024-12-09 | 19:25 | Data | 0 | 31.704 | 29.503 | 200.561 | 7.63 | 188.39 | 2166.49 | 25.89 | 44.554 | 6.35 | 1.394 | 4.922 | 8648.76 | 2.106 | 97.9 | 77.9 | 1408 | 22.28 | 5621.7 | 3041.6 | 2959.1 | 4357.5 | 1201.8 | 0.68238 | 6.316
2024-12-09 | 19:25 | Data | 0 | 31.859 | 29.503 | 200.651 | 7.63 | 188.48 | 2166.49 | 25.89 | 44.554 | 6.34 | 1.391 | 4.919 | 8648.76 | 2.187 | 97.9 | 78 | 1408 | 22.28 | 5621.7 | 3038.7 | 2970.5 | 4367.1 | 1201.8 | 0.67838 | 6.309
2024-12-09 | 19:25 | Data | 0 | 31.792 | 29.868 | 200.651 | 7.62 | 188.345 | 2166.49 | 25.89 | 44.554 | 6.35 | 1.394 | 4.91 | 8648.76 | 2.417 | 97.9 | 77.9 | 1408 | 22.32 | 5621.7 | 3051.8 | 2954.8 | 4363.9 | 1201.8 | 0.68274 | 6.302
2024-12-09 | 19:25 | Data | 0 | 31.812 | 29.503 | 200.606 | 7.63 | 188.39 | 2161.06 | 25.89 | 44.644 | 6.34 | 1.39 | 4.913 | 8653.28 | 2.289 | 97.9 | 77.9 | 1405 | 22.28 | 5624.6 | 3039.5 | 2945.2 | 4350.2 | 1201.8 | 0.68032 | 6.303
2024-12-09 | 19:25 | Data | 0 | 32.312 | 29.739 | 200.742 | 7.63 | 188.571 | 2163.77 | 25.89 | 44.644 | 6.34 | 1.395 | 4.92 | 8653.28 | 2.133 | 97.9 | 77.9 | 1406 | 22.28 | 5624.6 | 3045.9 | 2930.3 | 4343.3 | 1201.8 | 0.68347 | 6.315
2024-12-09 | 19:25 | Data | 0 | 31.826 | 29.699 | 200.697 | 7.63 | 188.39 | 2161.97 | 25.89 | 44.554 | 6.35 | 1.402 | 4.948 | 8684.94 | 2.181 | 97.9 | 77.9 | 1405 | 22.28 | 5645.2 | 3042.8 | 2930.7 | 4340.4 | 1201.8 | 0.68435 | 6.349
2024-12-09 | 19:25 | Data | 0 | 32.015 | 29.901 | 200.606 | 7.63 | 188.39 | 2161.06 | 25.89 | 44.644 | 6.34 | 1.396 | 4.92 | 8662.33 | 2.302 | 97.9 | 77.9 | 1405 | 22.28 | 5630.5 | 3045.1 | 2941.3 | 4357.9 | 1201.8 | 0.68375 | 6.317
2024-12-09 | 19:26 | Data | 0 | 31.832 | 29.307 | 200.561 | 7.63 | 188.39 | 2161.97 | 25.9 | 44.554 | 6.35 | 1.385 | 4.917 | 8662.33 | 2.295 | 97.9 | 78 | 1405 | 22.28 | 5630.5 | 3035.2 | 2940.7 | 4343.5 | 1201.8 | 0.68271 | 6.303
2024-12-09 | 19:26 | Data | 0 | 31.967 | 29.571 | 200.697 | 7.63 | 188.48 | 2161.97 | 25.88 | 44.554 | 6.35 | 1.377 | 4.919 | 8662.33 | 2.316 | 97.9 | 78.1 | 1405 | 22.28 | 5630.5 | 3030.3 | 2963.1 | 4348 | 1201.8 | 0.68085 | 6.296
2024-12-09 | 19:26 | Data | 0 | 31.886 | 29.672 | 200.651 | 7.63 | 188.39 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.378 | 4.91 | 8662.33 | 2.397 | 97.9 | 78.1 | 1405 | 22.28 | 5630.5 | 3029.4 | 2935.6 | 4331.6 | 1201.8 | 0.68168 | 6.289
2024-12-09 | 19:26 | Data | 0 | 32.028 | 29.726 | 200.697 | 7.63 | 188.48 | 2161.97 | 25.89 | 44.554 | 6.34 | 1.38 | 4.9 | 8644.24 | 2.187 | 97.9 | 78 | 1405 | 22.28 | 5618.8 | 3028.2 | 2952.1 | 4349.9 | 1201.8 | 0.67959 | 6.281
2024-12-09 | 19:26 | Data | 0 | 32.231 | 29.584 | 200.606 | 7.63 | 188.39 | 2156.54 | 25.89 | 44.554 | 6.35 | 1.388 | 4.9 | 8666.85 | 2.41 | 97.9 | 77.9 | 1402 | 22.28 | 5633.5 | 3035 | 2951 | 4347.9 | 1201.8 | 0.6825 | 6.288
2024-12-09 | 19:26 | Data | 0 | 32.231 | 29.955 | 200.787 | 7.63 | 188.435 | 2160.16 | 25.89 | 44.464 | 6.35 | 1.385 | 4.934 | 8689.46 | 2.309 | 97.9 | 78.1 | 1405 | 22.28 | 5648.1 | 3016.8 | 2919.9 | 4313.5 | 1201.8 | 0.68289 | 6.318
2024-12-09 | 19:26 | Data | 0 | 32.028 | 29.834 | 200.651 | 7.63 | 188.48 | 2163.77 | 25.89 | 44.554 | 6.35 | 1.382 | 4.919 | 8666.85 | 2.194 | 97.9 | 78.1 | 1406 | 22.23 | 5633.5 | 3029.7 | 2925.6 | 4323.5 | 1201.8 | 0.68432 | 6.301
2024-12-09 | 19:26 | Data | 0 | 31.637 | 29.625 | 200.742 | 7.62 | 188.345 | 2164.68 | 25.9 | 44.554 | 6.35 | 1.389 | 4.901 | 8680.41 | 2.37 | 97.9 | 77.9 | 1407 | 22.28 | 5642.3 | 3039.4 | 2933.5 | 4335.9 | 1201.8 | 0.68499 | 6.29
2024-12-09 | 19:26 | Data | 0 | 32.028 | 29.996 | 200.742 | 7.62 | 188.48 | 2166.49 | 25.89 | 44.554 | 6.35 | 1.393 | 4.894 | 8644.24 | 2.241 | 97.9 | 77.9 | 1408 | 22.28 | 5618.8 | 3029.5 | 2951.6 | 4340.7 | 1201.8 | 0.68232 | 6.286
2024-12-09 | 19:26 | Data | 0 | 32.015 | 29.726 | 200.561 | 7.63 | 188.39 | 2166.49 | 25.89 | 44.644 | 6.35 | 1.388 | 4.903 | 8657.8 | 2.302 | 97.9 | 77.9 | 1408 | 22.32 | 5627.6 | 3035.9 | 2943.8 | 4344.2 | 1201.8 | 0.68238 | 6.292
2024-12-09 | 19:26 | Data | 0 | 32.102 | 29.733 | 200.697 | 7.63 | 188.48 | 2166.49 | 25.89 | 44.644 | 6.35 | 1.392 | 4.899 | 8666.85 | 2.187 | 97.9 | 77.9 | 1408 | 22.28 | 5633.5 | 3020.9 | 2954.4 | 4336.6 | 1201.8 | 0.68062 | 6.29
2024-12-09 | 19:26 | Data | 0 | 32.055 | 29.618 | 200.697 | 7.63 | 188.435 | 2163.77 | 25.89 | 44.554 | 6.35 | 1.394 | 4.916 | 8662.33 | 2.241 | 97.9 | 77.9 | 1406 | 22.32 | 5630.5 | 3040.7 | 2935.8 | 4337.5 | 1201.8 | 0.6838 | 6.31
2024-12-09 | 19:26 | Data | 0 | 32.244 | 29.53 | 200.697 | 7.62 | 188.435 | 2161.97 | 25.9 | 44.554 | 6.35 | 1.394 | 4.913 | 8662.33 | 2.37 | 97.9 | 77.9 | 1405 | 22.28 | 5630.5 | 3034.1 | 2917.8 | 4320.2 | 1201.9 | 0.68624 | 6.309
2024-12-09 | 19:26 | Data | 0 | 32.028 | 30.036 | 200.742 | 7.63 | 188.39 | 2161.97 | 25.89 | 44.554 | 6.35 | 1.402 | 4.903 | 8684.94 | 2.194 | 97.9 | 77.8 | 1405 | 22.32 | 5645.2 | 3038.4 | 2932.6 | 4330.3 | 1201.9 | 0.68551 | 6.305
2024-12-09 | 19:26 | Data | 0 | 32.251 | 29.955 | 200.697 | 7.63 | 188.525 | 2163.77 | 25.89 | 44.554 | 6.35 | 1.395 | 4.901 | 8662.33 | 2.309 | 97.9 | 77.9 | 1406 | 22.28 | 5630.5 | 3039.7 | 2917.4 | 4330.6 | 1201.9 | 0.68543 | 6.294
2024-12-09 | 19:26 | Data | 0 | 31.886 | 29.726 | 200.606 | 7.63 | 188.48 | 2164.68 | 25.89 | 44.554 | 6.35 | 1.392 | 4.902 | 8671.37 | 2.248 | 97.9 | 77.9 | 1407 | 22.32 | 5636.4 | 3038.6 | 2919.9 | 4330.3 | 1201.9 | 0.68719 | 6.293
2024-12-09 | 19:26 | Data | 0 | 31.812 | 29.557 | 200.606 | 7.63 | 188.435 | 2166.49 | 25.89 | 44.644 | 6.35 | 1.401 | 4.934 | 8680.41 | 2.241 | 97.9 | 77.9 | 1408 | 22.28 | 5642.3 | 3032.9 | 2916.6 | 4319.1 | 1201.9 | 0.68675 | 6.334
2024-12-09 | 19:26 | Data | 0 | 32.082 | 29.733 | 200.561 | 7.63 | 188.435 | 2171.01 | 25.89 | 44.554 | 6.35 | 1.393 | 4.92 | 8680.41 | 2.133 | 98 | 77.9 | 1411 | 22.23 | 5642.3 | 3033.2 | 2914.2 | 4316.9 | 1201.9 | 0.68693 | 6.312
2024-12-09 | 19:27 | Data | 0 | 31.799 | 29.868 | 200.651 | 7.63 | 188.48 | 2161.06 | 25.89 | 44.644 | 6.35 | 1.379 | 4.908 | 8698.5 | 2.302 | 97.9 | 78.1 | 1405 | 22.28 | 5654 | 3031.3 | 2936 | 4333.9 | 1201.9 | 0.6834 | 6.287
2024-12-09 | 19:27 | Data | 0 | 32.244 | 29.739 | 200.651 | 7.63 | 188.435 | 2163.77 | 25.9 | 44.554 | 6.35 | 1.391 | 4.917 | 8689.46 | 2.329 | 97.9 | 78 | 1406 | 22.32 | 5648.1 | 3042.5 | 2930.7 | 4337.2 | 1201.9 | 0.68468 | 6.309
2024-12-09 | 19:27 | Data | 0 | 31.9 | 29.496 | 200.697 | 7.62 | 188.39 | 2163.77 | 25.89 | 44.554 | 6.35 | 1.398 | 4.897 | 8693.98 | 2.106 | 97.9 | 77.8 | 1406 | 22.28 | 5651.1 | 3038.6 | 2953.5 | 4349.5 | 1201.9 | 0.68242 | 6.294
2024-12-09 | 19:27 | Data | 0 | 31.981 | 29.726 | 200.606 | 7.63 | 188.39 | 2161.97 | 25.89 | 44.554 | 6.35 | 1.389 | 4.902 | 8662.33 | 2.289 | 97.9 | 77.9 | 1405 | 22.28 | 5630.5 | 3029.5 | 2966.1 | 4358.6 | 1201.9 | 0.67944 | 6.292
2024-12-09 | 19:27 | Data | 0 | 32.298 | 29.78 | 200.697 | 7.62 | 188.525 | 2158.35 | 25.89 | 44.644 | 6.34 | 1.398 | 4.89 | 8657.8 | 2.208 | 97.9 | 77.8 | 1403 | 22.28 | 5627.6 | 3033.6 | 2961.3 | 4349.1 | 1201.9 | 0.68051 | 6.287
2024-12-09 | 19:27 | Data | 0 | 31.758 | 29.719 | 200.561 | 7.63 | 188.345 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.401 | 4.917 | 8657.8 | 2.079 | 97.9 | 77.8 | 1405 | 22.37 | 5627.6 | 3045.6 | 2945.2 | 4348.3 | 1201.9 | 0.68454 | 6.318
2024-12-09 | 19:27 | Data | 0 | 32.143 | 29.739 | 200.832 | 7.63 | 188.435 | 2163.77 | 25.89 | 44.554 | 6.35 | 1.398 | 4.917 | 8671.37 | 2.302 | 97.9 | 77.9 | 1406 | 22.32 | 5636.4 | 3046.2 | 2943.5 | 4347.6 | 1201.9 | 0.68156 | 6.315
2024-12-09 | 19:27 | Data | 0 | 32.082 | 29.726 | 200.742 | 7.63 | 188.48 | 2164.68 | 25.89 | 44.554 | 6.35 | 1.393 | 4.916 | 8671.37 | 2.309 | 97.9 | 77.9 | 1407 | 22.28 | 5636.4 | 3031.3 | 2924.6 | 4323.3 | 1201.9 | 0.68536 | 6.31
2024-12-09 | 19:27 | Data | 0 | 32.19 | 29.955 | 200.651 | 7.63 | 188.48 | 2163.77 | 25.9 | 44.644 | 6.34 | 1.393 | 4.921 | 8707.55 | 2.302 | 97.9 | 77.9 | 1406 | 22.28 | 5659.9 | 3045.8 | 2953 | 4356.5 | 1201.9 | 0.6829 | 6.314
2024-12-09 | 19:27 | Data | 0 | 32.001 | 29.928 | 200.787 | 7.63 | 188.48 | 2163.77 | 25.89 | 44.554 | 6.35 | 1.392 | 4.891 | 8689.46 | 2.214 | 97.9 | 77.9 | 1406 | 22.28 | 5648.1 | 3049.9 | 2963.4 | 4365.7 | 1201.9 | 0.68324 | 6.282
2024-12-09 | 19:27 | Data | 0 | 31.805 | 29.712 | 200.742 | 7.63 | 188.48 | 2166.49 | 25.89 | 44.644 | 6.35 | 1.388 | 4.896 | 8680.41 | 2.1 | 97.9 | 77.9 | 1408 | 22.32 | 5642.3 | 3029.6 | 2933 | 4329.2 | 1201.9 | 0.68414 | 6.284
2024-12-09 | 19:27 | Data | 0 | 32.021 | 29.726 | 200.561 | 7.62 | 188.39 | 2161.97 | 25.89 | 44.554 | 6.34 | 1.383 | 4.913 | 8703.03 | 2.302 | 97.9 | 78 | 1406 | 22.28 | 5657 | 3030 | 2964.3 | 4349.6 | 1201.9 | 0.67925 | 6.296
2024-12-09 | 19:27 | Data | 0 | 32.028 | 29.841 | 200.561 | 7.63 | 188.39 | 2163.77 | 25.89 | 44.554 | 6.35 | 1.387 | 4.943 | 8703.03 | 2.302 | 97.9 | 78.1 | 1407 | 22.32 | 5657 | 3029 | 2974.1 | 4360.5 | 1201.9 | 0.67859 | 6.331
2024-12-09 | 19:27 | Data | 0 | 31.927 | 29.726 | 200.832 | 7.63 | 188.525 | 2167.39 | 25.89 | 44.644 | 6.34 | 1.388 | 4.929 | 8707.55 | 2.14 | 97.9 | 78 | 1408 | 22.28 | 5659.9 | 3036.2 | 2989.1 | 4385.3 | 1201.9 | 0.67989 | 6.317
2024-12-09 | 19:27 | Data | 0 | 31.981 | 29.854 | 200.697 | 7.63 | 188.48 | 2170.1 | 25.89 | 44.554 | 6.34 | 1.384 | 4.928 | 8716.59 | 2.127 | 97.9 | 78.1 | 1410 | 22.28 | 5665.8 | 3024.7 | 2985.8 | 4365.2 | 1201.9 | 0.67749 | 6.31
2024-12-09 | 19:27 | Data | 0 | 31.826 | 29.51 | 200.651 | 7.63 | 188.39 | 2166.49 | 25.9 | 44.554 | 6.34 | 1.389 | 4.93 | 8730.16 | 2.295 | 97.9 | 78 | 1408 | 22.28 | 5674.6 | 3032.5 | 2954.8 | 4345.2 | 1201.9 | 0.68098 | 6.32
2024-12-09 | 19:27 | Data | 0 | 32.042 | 29.726 | 200.742 | 7.63 | 188.435 | 2163.77 | 25.89 | 44.554 | 6.35 | 1.388 | 4.912 | 8730.16 | 2.295 | 97.9 | 78 | 1407 | 22.28 | 5674.6 | 3043.6 | 2979.7 | 4371.9 | 1201.9 | 0.68067 | 6.301
2024-12-09 | 19:27 | Data | 0 | 31.974 | 30.151 | 200.742 | 7.63 | 188.39 | 2166.49 | 25.89 | 44.644 | 6.35 | 1.383 | 4.901 | 8734.68 | 2.241 | 97.9 | 78 | 1408 | 22.32 | 5677.5 | 3051 | 2939.3 | 4347.5 | 1201.9 | 0.68499 | 6.283
2024-12-09 | 19:28 | Data | 0 | 32.055 | 29.753 | 200.742 | 7.63 | 188.48 | 2169.2 | 25.89 | 44.644 | 6.35 | 1.373 | 4.91 | 8716.59 | 2.201 | 97.9 | 78.1 | 1411 | 22.32 | 5665.8 | 3038.5 | 2927.9 | 4330.7 | 1201.9 | 0.6849 | 6.282
2024-12-09 | 19:28 | Data | 0 | 32.258 | 29.618 | 200.651 | 7.63 | 188.48 | 2166.49 | 25.89 | 44.644 | 6.34 | 1.383 | 4.893 | 8743.73 | 2.208 | 97.9 | 78 | 1408 | 22.28 | 5683.4 | 3041.7 | 2927.4 | 4331.4 | 1201.9 | 0.68589 | 6.275
2024-12-09 | 19:28 | Data | 0 | 32.001 | 29.726 | 200.651 | 7.62 | 188.435 | 2166.49 | 25.89 | 44.554 | 6.35 | 1.382 | 4.9 | 8743.73 | 2.295 | 97.9 | 78 | 1409 | 22.28 | 5683.4 | 3045.3 | 2955.6 | 4354.4 | 1201.9 | 0.68369 | 6.282
2024-12-09 | 19:28 | Data | 0 | 31.812 | 29.712 | 200.742 | 7.62 | 188.48 | 2161.97 | 25.89 | 44.554 | 6.35 | 1.38 | 4.891 | 8730.16 | 2.12 | 97.9 | 78 | 1405 | 22.32 | 5674.6 | 3028.2 | 2944.5 | 4340 | 1201.9 | 0.68103 | 6.272
2024-12-09 | 19:28 | Data | 0 | 31.799 | 29.726 | 200.651 | 7.63 | 188.39 | 2163.77 | 25.89 | 44.554 | 6.35 | 1.387 | 4.893 | 8730.16 | 2.073 | 97.9 | 77.9 | 1406 | 22.28 | 5674.6 | 3036.9 | 2954 | 4350 | 1201.9 | 0.68321 | 6.281
2024-12-09 | 19:28 | Data | 0 | 31.799 | 29.726 | 200.651 | 7.63 | 188.39 | 2162.87 | 25.89 | 44.554 | 6.35 | 1.39 | 4.921 | 8716.59 | 2.248 | 97.9 | 78 | 1406 | 22.23 | 5665.8 | 3051.6 | 2983.3 | 4378.3 | 1201.9 | 0.68138 | 6.31
2024-12-09 | 19:28 | Data | 0 | 32.021 | 29.611 | 200.606 | 7.62 | 188.39 | 2166.49 | 25.89 | 44.554 | 6.35 | 1.387 | 4.922 | 8721.11 | 2.302 | 97.9 | 78 | 1408 | 22.28 | 5668.7 | 3037 | 2941.7 | 4339.7 | 1201.9 | 0.68406 | 6.308
2024-12-09 | 19:28 | Data | 0 | 31.866 | 29.935 | 200.697 | 7.63 | 188.435 | 2165.58 | 25.89 | 44.644 | 6.35 | 1.385 | 4.907 | 8743.73 | 2.181 | 97.9 | 78 | 1408 | 22.32 | 5683.4 | 3044.1 | 2970.1 | 4365.7 | 1201.9 | 0.68138 | 6.291
2024-12-09 | 19:28 | Data | 0 | 32.231 | 29.746 | 200.651 | 7.63 | 188.39 | 2162.87 | 25.89 | 44.554 | 6.35 | 1.386 | 4.921 | 8689.46 | 2.451 | 97.9 | 78 | 1406 | 22.28 | 5648.1 | 3048.6 | 2937.7 | 4350.7 | 1201.9 | 0.6841 | 6.307
2024-12-09 | 19:28 | Data | 0 | 31.859 | 29.523 | 200.606 | 7.62 | 188.39 | 2160.16 | 25.89 | 44.825 | 6.35 | 1.387 | 4.904 | 8703.03 | 2.282 | 97.9 | 77.9 | 1405 | 22.41 | 5657 | 3042.7 | 2960.5 | 4358.6 | 1201.9 | 0.68328 | 6.291
2024-12-09 | 19:28 | Data | 0 | 32.123 | 29.976 | 200.787 | 7.62 | 188.571 | 2161.06 | 25.89 | 44.554 | 6.35 | 1.389 | 4.933 | 8703.03 | 2.349 | 97.9 | 78 | 1405 | 22.28 | 5657 | 3027.2 | 2951.1 | 4345.8 | 1201.9 | 0.67998 | 6.323
2024-12-09 | 19:28 | Data | 0 | 32.197 | 29.78 | 200.606 | 7.63 | 188.435 | 2161.97 | 25.89 | 44.554 | 6.35 | 1.386 | 4.915 | 8703.03 | 2.295 | 97.9 | 78 | 1405 | 22.28 | 5657 | 3043.2 | 2958.8 | 4358.4 | 1202 | 0.68068 | 6.302
2024-12-09 | 19:28 | Data | 0 | 31.832 | 29.753 | 200.651 | 7.62 | 188.435 | 2159.26 | 25.89 | 44.554 | 6.34 | 1.385 | 4.891 | 8693.98 | 2.201 | 97.9 | 77.9 | 1404 | 22.28 | 5651.1 | 3012.9 | 2974.4 | 4352.1 | 1202 | 0.67592 | 6.276
2024-12-09 | 19:28 | Data | 0 | 32.163 | 29.753 | 200.742 | 7.63 | 188.48 | 2159.26 | 25.9 | 44.554 | 6.35 | 1.384 | 4.921 | 8703.03 | 2.39 | 97.9 | 78.1 | 1403 | 22.28 | 5657 | 3045.5 | 2950.5 | 4354.6 | 1202 | 0.6828 | 6.306
2024-12-09 | 19:28 | Data | 0 | 31.704 | 29.712 | 200.651 | 7.62 | 188.39 | 2152.93 | 25.89 | 44.554 | 6.35 | 1.388 | 4.908 | 8693.98 | 2.059 | 97.9 | 78 | 1399 | 22.32 | 5651.1 | 3008.1 | 2951 | 4331.4 | 1202 | 0.67858 | 6.295
2024-12-09 | 19:28 | Data | 0 | 32.055 | 29.517 | 200.697 | 7.63 | 188.48 | 2161.06 | 25.89 | 44.554 | 6.35 | 1.387 | 4.911 | 8689.46 | 2.403 | 97.9 | 78 | 1405 | 22.28 | 5648.1 | 3028.2 | 2932.8 | 4327.2 | 1202 | 0.68329 | 6.299
2024-12-09 | 19:28 | Data | 0 | 32.264 | 29.793 | 200.832 | 7.63 | 188.525 | 2161.06 | 25.9 | 44.644 | 6.35 | 1.38 | 4.888 | 8684.94 | 2.295 | 97.9 | 78 | 1405 | 22.28 | 5645.2 | 3032.7 | 2951.6 | 4345.4 | 1202 | 0.68152 | 6.269
2024-12-09 | 19:28 | Data | 0 | 32.028 | 29.928 | 200.651 | 7.63 | 188.435 | 2163.77 | 25.9 | 44.554 | 6.34 | 1.393 | 4.882 | 8644.24 | 2.241 | 97.9 | 77.8 | 1406 | 22.32 | 5618.8 | 3046.6 | 2941.6 | 4345 | 1202 | 0.68427 | 6.275
2024-12-09 | 19:29 | Data | 0 | 32.028 | 29.739 | 200.651 | 7.63 | 188.39 | 2158.35 | 25.89 | 44.825 | 6.35 | 1.384 | 4.899 | 8621.63 | 2.235 | 97.9 | 78 | 1404 | 22.41 | 5604.1 | 3038.3 | 2969.2 | 4359.3 | 1202 | 0.68266 | 6.283
2024-12-09 | 19:29 | Data | 0 | 31.967 | 29.949 | 200.832 | 7.63 | 188.48 | 2158.35 | 25.89 | 44.825 | 6.34 | 1.381 | 4.924 | 8621.63 | 2.255 | 97.9 | 78.1 | 1403 | 22.41 | 5604.1 | 3043.6 | 2976.2 | 4368.9 | 1202 | 0.68147 | 6.305
2024-12-09 | 19:29 | Data | 0 | 32.143 | 29.753 | 200.787 | 7.62 | 188.435 | 2156.54 | 25.9 | 44.734 | 6.35 | 1.387 | 4.913 | 8621.63 | 2.16 | 97.9 | 78 | 1402 | 22.37 | 5604.1 | 3046.3 | 2956.3 | 4359.5 | 1202 | 0.68184 | 6.301
2024-12-09 | 19:29 | Data | 0 | 31.92 | 29.922 | 200.651 | 7.62 | 188.48 | 2159.26 | 25.89 | 44.734 | 6.35 | 1.381 | 4.901 | 8621.63 | 2.046 | 97.9 | 78 | 1403 | 22.37 | 5604.1 | 3028.9 | 2927.9 | 4324.2 | 1202 | 0.68375 | 6.283
2024-12-09 | 19:29 | Data | 0 | 31.772 | 29.712 | 200.606 | 7.63 | 188.299 | 2159.26 | 25.89 | 44.825 | 6.35 | 1.391 | 4.907 | 8635.19 | 2.228 | 97.9 | 77.9 | 1404 | 22.41 | 5612.9 | 3031 | 2965.9 | 4354.8 | 1202 | 0.68052 | 6.298
2024-12-09 | 19:29 | Data | 0 | 31.913 | 29.827 | 200.651 | 7.63 | 188.48 | 2158.35 | 25.89 | 44.825 | 6.35 | 1.384 | 4.898 | 8246.28 | 2.302 | 97.9 | 78 | 1404 | 22.46 | 5360.1 | 3016 | 2935.7 | 4322 | 1202 | 0.68258 | 6.282
2024-12-09 | 19:29 | Data | 0 | 31.853 | 29.611 | 200.606 | 7.63 | 188.435 | 2158.35 | 25.89 | 44.825 | 6.34 | 1.381 | 4.882 | 8232.71 | 2.079 | 97.9 | 77.9 | 1403 | 22.41 | 5351.3 | 3060.6 | 2945.3 | 4356.4 | 1202 | 0.68576 | 6.263
2024-12-09 | 19:29 | Data | 0 | 31.92 | 29.726 | 200.697 | 7.63 | 188.435 | 2158.35 | 25.89 | 44.825 | 6.35 | 1.392 | 4.901 | 8671.37 | 2.1 | 97.9 | 77.9 | 1403 | 22.41 | 5636.4 | 3037 | 2976.5 | 4361.4 | 1202 | 0.68179 | 6.293
2024-12-09 | 19:29 | Data | 0 | 31.799 | 29.672 | 200.651 | 7.63 | 188.345 | 2161.06 | 25.89 | 44.915 | 6.35 | 1.391 | 4.911 | 8662.33 | 2.127 | 97.9 | 77.9 | 1404 | 22.41 | 5630.5 | 3034.2 | 2920.8 | 4322.3 | 1202 | 0.68554 | 6.303
2024-12-09 | 19:29 | Data | 0 | 31.859 | 30.09 | 200.697 | 7.62 | 188.39 | 2161.97 | 25.89 | 44.554 | 6.35 | 1.389 | 4.932 | 8662.33 | 2.248 | 97.9 | 78 | 1405 | 22.28 | 5630.5 | 3022.3 | 2940.5 | 4334.6 | 1202 | 0.68106 | 6.321
2024-12-09 | 19:29 | Data | 0 | 31.684 | 29.787 | 200.606 | 7.63 | 188.39 | 2161.06 | 25.89 | 44.644 | 6.34 | 1.395 | 4.905 | 8657.8 | 2.39 | 97.9 | 77.9 | 1405 | 22.28 | 5627.6 | 3046.2 | 2945.5 | 4348.1 | 1202 | 0.68471 | 6.3
2024-12-09 | 19:29 | Data | 0 | 32.021 | 29.726 | 200.697 | 7.63 | 188.435 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.392 | 4.929 | 8653.28 | 2.417 | 97.9 | 78 | 1405 | 22.32 | 5624.6 | 3026.5 | 2925.1 | 4324 | 1202 | 0.68386 | 6.32
2024-12-09 | 19:29 | Data | 0 | 32.143 | 29.955 | 200.697 | 7.63 | 188.525 | 2161.06 | 25.89 | 44.825 | 6.35 | 1.389 | 4.884 | 8666.85 | 2.086 | 97.9 | 77.9 | 1405 | 22.41 | 5633.5 | 3048.9 | 2924.8 | 4335.8 | 1202 | 0.68497 | 6.273
2024-12-09 | 19:29 | Data | 0 | 32.231 | 29.955 | 200.651 | 7.62 | 188.525 | 2161.06 | 25.89 | 44.554 | 6.35 | 1.384 | 4.912 | 8680.41 | 2.309 | 97.9 | 78 | 1405 | 22.28 | 5642.3 | 3038.5 | 2923 | 4329.3 | 1202 | 0.6847 | 6.296
2024-12-09 | 19:29 | Data | 0 | 32.453 | 29.868 | 200.832 | 7.62 | 188.525 | 2159.26 | 25.89 | 44.554 | 6.35 | 1.382 | 4.914 | 8662.33 | 2.41 | 97.9 | 78.1 | 1403 | 22.32 | 5630.5 | 3041.7 | 2943.2 | 4333.5 | 1202 | 0.68436 | 6.296
2024-12-09 | 19:29 | Data | 0 | 31.832 | 29.827 | 200.651 | 7.63 | 188.435 | 2161.97 | 25.89 | 44.825 | 6.35 | 1.388 | 4.94 | 8662.33 | 2.1 | 97.9 | 78.1 | 1405 | 22.41 | 5630.5 | 3042.7 | 2953 | 4352.6 | 1202 | 0.68282 | 6.33
2024-12-09 | 19:29 | Data | 0 | 32.366 | 29.523 | 200.651 | 7.63 | 188.435 | 2161.97 | 25.89 | 44.915 | 6.35 | 1.381 | 4.927 | 8689.46 | 2.41 | 97.9 | 78.1 | 1405 | 22.41 | 5648.1 | 3039.5 | 2942.3 | 4344.7 | 1202 | 0.68387 | 6.308
2024-12-09 | 19:30 | Data | 0 | 31.907 | 29.726 | 200.651 | 7.62 | 188.39 | 2161.06 | 25.89 | 44.825 | 6.34 | 1.385 | 4.901 | 8662.33 | 2.403 | 97.9 | 78 | 1405 | 22.41 | 5630.5 | 3035 | 2940.9 | 4340.8 | 1202 | 0.68106 | 6.285
2024-12-09 | 19:30 | Data | 0 | 32.089 | 29.739 | 200.787 | 7.62 | 188.48 | 2160.16 | 25.9 | 45.186 | 6.35 | 1.387 | 4.925 | 8671.37 | 2.093 | 97.9 | 78 | 1405 | 22.5 | 5636.4 | 3051.1 | 2929.8 | 4341.1 | 1202 | 0.68568 | 6.312
2024-12-09 | 19:30 | Data | 0 | 32.008 | 29.901 | 200.742 | 7.63 | 188.525 | 2163.77 | 25.89 | 44.734 | 6.35 | 1.395 | 4.915 | 8680.41 | 2.181 | 97.9 | 77.9 | 1406 | 22.41 | 5642.3 | 3041.9 | 2936.4 | 4343.3 | 1202 | 0.68491 | 6.31
2024-12-09 | 19:30 | Data | 0 | 32.129 | 29.517 | 200.606 | 7.63 | 188.48 | 2163.77 | 25.89 | 44.734 | 6.35 | 1.394 | 4.883 | 8703.03 | 2.505 | 97.9 | 77.8 | 1406 | 22.41 | 5657 | 3054.3 | 2933.8 | 4345.7 | 1202 | 0.68702 | 6.278
2024-12-09 | 19:30 | Data | 0 | 32.258 | 29.571 | 200.697 | 7.63 | 188.48 | 2163.77 | 25.89 | 44.825 | 6.35 | 1.389 | 4.888 | 8703.03 | 2.295 | 97.9 | 77.9 | 1407 | 22.46 | 5657 | 3031 | 2939.3 | 4337.9 | 1202 | 0.68148 | 6.277
2024-12-09 | 19:30 | Data | 0 | 32.028 | 29.841 | 200.787 | 7.63 | 188.435 | 2166.49 | 25.89 | 44.915 | 6.35 | 1.389 | 4.909 | 8703.03 | 2.302 | 97.9 | 77.9 | 1408 | 22.46 | 5657 | 3008.8 | 2929.1 | 4318.8 | 1202 | 0.6806 | 6.298
2024-12-09 | 19:30 | Data | 0 | 31.94 | 29.53 | 200.697 | 7.63 | 188.48 | 2170.1 | 25.89 | 44.825 | 6.35 | 1.378 | 4.897 | 8689.46 | 2.113 | 97.9 | 78 | 1411 | 22.41 | 5648.1 | 3017.8 | 2925.1 | 4319.4 | 1202 | 0.68103 | 6.275
2024-12-09 | 19:30 | Data | 0 | 32.258 | 29.726 | 200.832 | 7.62 | 188.435 | 2170.1 | 25.9 | 44.825 | 6.34 | 1.399 | 4.9 | 8703.03 | 2.14 | 97.9 | 77.8 | 1411 | 22.37 | 5657 | 3016 | 2939.6 | 4324.4 | 1202 | 0.6828 | 6.298
2024-12-09 | 19:30 | Data | 0 | 32.028 | 29.773 | 200.697 | 7.63 | 188.435 | 2170.1 | 25.9 | 44.825 | 6.35 | 1.395 | 4.896 | 8703.03 | 2.1 | 97.9 | 77.8 | 1409 | 22.41 | 5657 | 3027.8 | 2955.3 | 4349.6 | 1202 | 0.68012 | 6.291
2024-12-09 | 19:30 | Data | 0 | 32.136 | 29.571 | 200.742 | 7.63 | 188.435 | 2170.1 | 25.9 | 44.825 | 6.35 | 1.396 | 4.898 | 8716.59 | 2.241 | 97.9 | 77.8 | 1410 | 22.46 | 5665.8 | 3033.5 | 2971.9 | 4359.4 | 1202 | 0.68052 | 6.294
2024-12-09 | 19:30 | Data | 0 | 32.028 | 29.685 | 200.697 | 7.63 | 188.39 | 2171.01 | 25.89 | 44.825 | 6.35 | 1.397 | 4.898 | 8703.03 | 2.41 | 97.9 | 77.8 | 1411 | 22.46 | 5657 | 3018.7 | 2962.2 | 4343.4 | 1202 | 0.67834 | 6.295
2024-12-09 | 19:30 | Data | 0 | 31.826 | 29.51 | 200.697 | 7.63 | 188.48 | 2164.68 | 25.89 | 44.915 | 6.35 | 1.394 | 4.926 | 8680.41 | 2.255 | 97.9 | 77.9 | 1406 | 22.46 | 5642.3 | 3055.4 | 2970.6 | 4375.5 | 1202.1 | 0.682 | 6.32
2024-12-09 | 19:30 | Data | 0 | 32.062 | 29.557 | 200.516 | 7.63 | 188.48 | 2170.1 | 25.89 | 44.825 | 6.35 | 1.389 | 4.92 | 8689.46 | 2.235 | 97.9 | 78 | 1411 | 22.41 | 5648.1 | 3034.2 | 2932.4 | 4336.8 | 1202.1 | 0.68298 | 6.309
2024-12-09 | 19:30 | Data | 0 | 32.021 | 29.726 | 200.651 | 7.62 | 188.435 | 2170.1 | 25.89 | 44.825 | 6.35 | 1.39 | 4.944 | 8689.46 | 2.1 | 97.9 | 78.1 | 1410 | 22.41 | 5648.1 | 3039.7 | 2934 | 4323.1 | 1202.1 | 0.6833 | 6.334
2024-12-09 | 19:30 | Data | 0 | 31.819 | 29.928 | 200.832 | 7.63 | 188.525 | 2170.1 | 25.89 | 44.825 | 6.35 | 1.391 | 4.92 | 8693.98 | 1.965 | 97.9 | 78 | 1411 | 22.41 | 5651.1 | 3043.5 | 2934.4 | 4341 | 1202.1 | 0.68548 | 6.31
2024-12-09 | 19:30 | Data | 0 | 31.913 | 29.949 | 200.742 | 7.62 | 188.48 | 2169.2 | 25.89 | 44.825 | 6.35 | 1.386 | 4.913 | 8693.98 | 2.248 | 97.9 | 78 | 1410 | 22.41 | 5651.1 | 3018 | 2923.4 | 4319.9 | 1202.1 | 0.68239 | 6.301
2024-12-09 | 19:30 | Data | 0 | 31.974 | 29.996 | 200.832 | 7.62 | 188.525 | 2171.01 | 25.89 | 44.825 | 6.35 | 1.387 | 4.9 | 8721.11 | 2.154 | 97.9 | 77.9 | 1411 | 22.41 | 5668.7 | 3054.5 | 2945.8 | 4355.9 | 1202.1 | 0.68505 | 6.288
2024-12-09 | 19:30 | Data | 0 | 32.015 | 29.922 | 200.651 | 7.62 | 188.435 | 2170.1 | 25.89 | 44.915 | 6.35 | 1.393 | 4.908 | 8707.55 | 2.309 | 97.9 | 77.9 | 1411 | 22.41 | 5659.9 | 3022.9 | 2942.6 | 4335.4 | 1202.1 | 0.68149 | 6.3
2024-12-09 | 19:31 | Data | 0 | 32.021 | 29.753 | 200.742 | 7.62 | 188.48 | 2170.1 | 25.89 | 44.825 | 6.35 | 1.397 | 4.897 | 8721.11 | 2.255 | 97.9 | 77.8 | 1411 | 22.46 | 5668.7 | 3029 | 2930 | 4327.9 | 1202.1 | 0.68318 | 6.294
2024-12-09 | 19:31 | Data | 0 | 31.913 | 29.712 | 200.697 | 7.63 | 188.39 | 2166.49 | 25.89 | 44.734 | 6.35 | 1.4 | 4.907 | 8739.2 | 2.316 | 97.9 | 77.8 | 1408 | 22.41 | 5680.5 | 3059.3 | 2945.6 | 4357.6 | 1202.1 | 0.68543 | 6.305
2024-12-09 | 19:31 | Data | 0 | 32.028 | 29.51 | 200.651 | 7.63 | 188.435 | 2158.35 | 25.9 | 44.825 | 6.35 | 1.374 | 4.901 | 8721.11 | 2.336 | 97.9 | 78.1 | 1403 | 22.41 | 5668.7 | 3049 | 2943.6 | 4350.5 | 1202.1 | 0.68435 | 6.275
2024-12-09 | 19:31 | Data | 0 | 31.812 | 29.672 | 200.697 | 7.63 | 188.435 | 2161.97 | 25.89 | 44.734 | 6.35 | 1.387 | 4.913 | 8716.59 | 2.302 | 97.9 | 78 | 1405 | 22.32 | 5665.8 | 3037.1 | 2963.6 | 4358.1 | 1202.1 | 0.68059 | 6.301
2024-12-09 | 19:31 | Data | 0 | 31.819 | 29.503 | 200.651 | 7.63 | 188.435 | 2165.58 | 25.89 | 44.554 | 6.35 | 1.392 | 4.894 | 8712.07 | 2.275 | 97.9 | 77.9 | 1408 | 22.28 | 5662.8 | 3021.8 | 2928.8 | 4323.4 | 1202.1 | 0.68301 | 6.286
2024-12-09 | 19:31 | Data | 0 | 32.244 | 29.753 | 200.742 | 7.63 | 188.525 | 2166.49 | 25.89 | 44.554 | 6.35 | 1.378 | 4.894 | 8707.55 | 2.302 | 97.9 | 78 | 1409 | 22.28 | 5659.9 | 3033.1 | 2924.4 | 4325.9 | 1202.1 | 0.68412 | 6.272
2024-12-09 | 19:31 | Data | 0 | 32.028 | 29.739 | 200.787 | 7.63 | 188.435 | 2167.39 | 25.89 | 44.554 | 6.34 | 1.384 | 4.901 | 8662.33 | 2.262 | 97.9 | 78 | 1409 | 22.32 | 5630.5 | 3030.4 | 2903.3 | 4310.7 | 1202.1 | 0.68745 | 6.285
2024-12-09 | 19:31 | Data | 0 | 32.035 | 29.841 | 200.742 | 7.63 | 188.435 | 2169.2 | 25.89 | 44.554 | 6.35 | 1.381 | 4.94 | 8657.8 | 2.295 | 97.9 | 78.2 | 1410 | 22.28 | 5627.6 | 3019.4 | 2911.5 | 4306.3 | 1202.1 | 0.68513 | 6.323
2024-12-09 | 19:31 | Data | 0 | 31.603 | 29.726 | 200.832 | 7.62 | 188.435 | 2161.97 | 25.89 | 44.644 | 6.34 | 1.377 | 4.899 | 8662.33 | 2.16 | 97.9 | 78.1 | 1406 | 22.28 | 5630.5 | 3027.4 | 2941.4 | 4337.1 | 1202.1 | 0.68113 | 6.275
2024-12-09 | 19:31 | Data | 0 | 32.001 | 29.827 | 200.651 | 7.62 | 188.435 | 2166.49 | 25.89 | 44.644 | 6.35 | 1.381 | 4.907 | 8657.8 | 2.086 | 97.9 | 78 | 1408 | 22.28 | 5627.6 | 3034.6 | 2959.8 | 4354.5 | 1202.1 | 0.68171 | 6.289
2024-12-09 | 19:31 | Data | 0 | 32.345 | 29.955 | 200.697 | 7.63 | 188.525 | 2167.39 | 25.9 | 44.644 | 6.35 | 1.388 | 4.878 | 8703.03 | 2.464 | 97.9 | 77.8 | 1408 | 22.28 | 5657 | 3032.5 | 2959.5 | 4352.3 | 1202.1 | 0.68115 | 6.266
2024-12-09 | 19:31 | Data | 0 | 32.028 | 29.726 | 200.878 | 7.62 | 188.571 | 2167.39 | 25.89 | 44.644 | 6.35 | 1.395 | 4.9 | 8680.41 | 2.295 | 97.9 | 77.8 | 1409 | 22.28 | 5642.3 | 3039.4 | 2959.2 | 4355 | 1202.1 | 0.68243 | 6.293
2024-12-09 | 19:31 | Data | 0 | 31.637 | 29.726 | 200.697 | 7.63 | 188.48 | 2166.49 | 25.89 | 44.644 | 6.34 | 1.4 | 4.931 | 8693.98 | 1.877 | 97.9 | 77.9 | 1408 | 22.32 | 5651.1 | 3039.5 | 2973.8 | 4368 | 1202.1 | 0.68055 | 6.331
2024-12-09 | 19:31 | Data | 0 | 31.994 | 29.726 | 200.742 | 7.63 | 188.435 | 2170.1 | 25.89 | 44.554 | 6.35 | 1.394 | 4.924 | 8689.46 | 2.295 | 97.9 | 77.9 | 1411 | 22.28 | 5648.1 | 3042.4 | 2953 | 4341.3 | 1202.1 | 0.68393 | 6.318
2024-12-09 | 19:31 | Data | 0 | 32.028 | 29.726 | 200.606 | 7.62 | 188.39 | 2169.2 | 25.89 | 44.464 | 6.35 | 1.39 | 4.919 | 8689.46 | 2.302 | 97.9 | 78 | 1410 | 22.28 | 5648.1 | 3045.1 | 2960.8 | 4359.9 | 1202.1 | 0.68313 | 6.309
2024-12-09 | 19:31 | Data | 0 | 32.204 | 30.158 | 200.878 | 7.62 | 188.616 | 2164.68 | 25.89 | 44.554 | 6.35 | 1.391 | 4.92 | 8680.41 | 2.154 | 97.9 | 78 | 1406 | 22.28 | 5642.3 | 3035.3 | 2943.3 | 4342 | 1202.1 | 0.68286 | 6.311
2024-12-09 | 19:31 | Data | 0 | 32.055 | 30.124 | 200.832 | 7.62 | 188.48 | 2169.2 | 25.89 | 44.554 | 6.34 | 1.395 | 4.95 | 8689.46 | 2.113 | 97.9 | 78 | 1410 | 22.32 | 5648.1 | 3048.7 | 2957.5 | 4361.9 | 1202.1 | 0.6831 | 6.345
2024-12-09 | 19:32 | Data | 0 | 32.237 | 30.178 | 200.832 | 7.62 | 188.525 | 2169.2 | 25.89 | 44.644 | 6.35 | 1.394 | 4.917 | 8689.46 | 2.194 | 97.9 | 77.9 | 1410 | 22.28 | 5648.1 | 3031.8 | 2967.7 | 4345.3 | 1202.1 | 0.6771 | 6.31
2024-12-09 | 19:32 | Data | 0 | 32.089 | 29.962 | 200.697 | 7.62 | 188.616 | 2170.1 | 25.89 | 44.554 | 6.35 | 1.38 | 4.903 | 8716.59 | 2.282 | 97.9 | 78 | 1410 | 22.28 | 5665.8 | 3025.2 | 2966.4 | 4352.7 | 1202.1 | 0.6786 | 6.283
2024-12-09 | 19:32 | Data | 0 | 32.244 | 29.53 | 200.742 | 7.63 | 188.525 | 2172.81 | 25.9 | 44.554 | 6.35 | 1.39 | 4.926 | 8734.68 | 2.329 | 97.9 | 78 | 1412 | 22.28 | 5677.5 | 3051.7 | 2951.7 | 4356.5 | 1202.1 | 0.68469 | 6.317
2024-12-09 | 19:32 | Data | 0 | 32.048 | 29.949 | 200.697 | 7.62 | 188.616 | 2171.01 | 25.89 | 44.554 | 6.34 | 1.387 | 4.92 | 8730.16 | 2.1 | 97.9 | 78 | 1412 | 22.28 | 5674.6 | 3034.1 | 2979.2 | 4365.7 | 1202.1 | 0.67868 | 6.308
2024-12-09 | 19:32 | Data | 0 | 31.832 | 29.726 | 201.104 | 7.62 | 188.706 | 2172.81 | 25.89 | 44.554 | 6.34 | 1.384 | 4.849 | 8716.59 | 2.194 | 97.9 | 77.8 | 1412 | 22.28 | 5665.8 | 3019.9 | 2969.6 | 4350.2 | 1202.1 | 0.67885 | 6.232
2024-12-09 | 19:32 | Data | 0 | 32.231 | 29.793 | 201.466 | 7.63 | 189.113 | 2174.62 | 25.89 | 44.644 | 6.35 | 1.386 | 4.907 | 8680.41 | 2.289 | 98 | 78 | 1414 | 22.28 | 5642.3 | 3058 | 2960.4 | 4364.5 | 1202.1 | 0.68494 | 6.293
2024-12-09 | 19:32 | Data | 0 | 31.907 | 29.685 | 201.375 | 7.63 | 189.158 | 2172.81 | 25.89 | 44.554 | 6.35 | 1.399 | 4.916 | 8648.76 | 2.437 | 97.9 | 77.8 | 1412 | 22.28 | 5621.7 | 3036.5 | 2953.5 | 4348.4 | 1202.1 | 0.68265 | 6.315
2024-12-09 | 19:32 | Data | 0 | 31.873 | 29.611 | 201.33 | 7.62 | 189.022 | 2172.81 | 25.89 | 44.554 | 6.35 | 1.397 | 4.91 | 8653.28 | 2.208 | 97.9 | 77.9 | 1412 | 22.28 | 5624.6 | 3045.7 | 2934.4 | 4342.3 | 1202.1 | 0.68569 | 6.309
2024-12-09 | 19:32 | Data | 0 | 32.028 | 29.949 | 201.42 | 7.63 | 189.113 | 2172.81 | 25.9 | 44.644 | 6.35 | 1.389 | 4.909 | 8680.41 | 2.086 | 97.9 | 77.9 | 1412 | 22.23 | 5642.3 | 3060.4 | 2935.9 | 4350.2 | 1202.1 | 0.6874 | 6.297
2024-12-09 | 19:32 | Data | 0 | 31.927 | 29.834 | 201.466 | 7.63 | 189.158 | 2172.81 | 25.89 | 44.644 | 6.35 | 1.393 | 4.926 | 8680.41 | 2.127 | 97.9 | 78 | 1412 | 22.28 | 5642.3 | 3039 | 2921.7 | 4331.2 | 1202.1 | 0.68565 | 6.319
2024-12-09 | 19:32 | Data | 0 | 31.805 | 29.672 | 201.42 | 7.63 | 189.158 | 2163.77 | 25.89 | 44.554 | 6.35 | 1.393 | 4.918 | 8662.33 | 2.181 | 97.9 | 77.9 | 1406 | 22.28 | 5630.5 | 3053.8 | 2924 | 4337.4 | 1202.1 | 0.68796 | 6.31
2024-12-09 | 19:32 | Data | 0 | 32.264 | 29.739 | 201.511 | 7.62 | 189.158 | 2166.49 | 25.9 | 44.554 | 6.34 | 1.402 | 4.926 | 8666.85 | 2.221 | 97.9 | 77.8 | 1408 | 22.28 | 5633.5 | 3063.4 | 2974.6 | 4380.5 | 1202.2 | 0.68379 | 6.328
2024-12-09 | 19:32 | Data | 0 | 31.799 | 29.895 | 201.511 | 7.63 | 189.203 | 2166.49 | 25.89 | 44.644 | 6.35 | 1.397 | 4.912 | 8657.8 | 2.295 | 97.9 | 77.9 | 1409 | 22.32 | 5627.6 | 3046.5 | 2944.7 | 4351.1 | 1202.2 | 0.68368 | 6.31
2024-12-09 | 19:32 | Data | 0 | 31.805 | 29.719 | 201.33 | 7.63 | 189.068 | 2163.77 | 25.89 | 44.644 | 6.35 | 1.386 | 4.948 | 8716.59 | 2.086 | 97.9 | 78.1 | 1406 | 22.28 | 5665.8 | 3028.5 | 2953 | 4338.7 | 1202.2 | 0.68097 | 6.334
2024-12-09 | 19:32 | Data | 0 | 32.15 | 29.982 | 201.601 | 7.63 | 189.294 | 2164.68 | 25.89 | 44.554 | 6.35 | 1.385 | 4.951 | 8680.41 | 2.356 | 97.9 | 78.1 | 1406 | 22.28 | 5642.3 | 3046.2 | 2946.4 | 4348.7 | 1202.2 | 0.68425 | 6.337
2024-12-09 | 19:32 | Data | 0 | 32.143 | 29.733 | 201.601 | 7.62 | 189.203 | 2167.39 | 25.89 | 44.554 | 6.35 | 1.388 | 4.903 | 8693.98 | 2.302 | 97.9 | 77.9 | 1408 | 22.28 | 5651.1 | 3047.5 | 2964.9 | 4363.9 | 1202.2 | 0.68236 | 6.291
2024-12-09 | 19:32 | Data | 0 | 32.42 | 29.76 | 201.466 | 7.63 | 189.248 | 2166.49 | 25.89 | 44.554 | 6.35 | 1.376 | 4.92 | 8689.46 | 2.302 | 97.9 | 78.2 | 1409 | 22.28 | 5648.1 | 3060.2 | 2944 | 4356.9 | 1202.2 | 0.68673 | 6.296
2024-12-09 | 19:32 | Data | 0 | 32.433 | 29.8 | 201.511 | 7.62 | 189.203 | 2161.97 | 25.89 | 44.554 | 6.35 | 1.385 | 4.911 | 8689.46 | 2.295 | 97.9 | 78 | 1405 | 22.28 | 5648.1 | 3042.9 | 2950.4 | 4352.9 | 1202.2 | 0.68259 | 6.295
2024-12-09 | 19:33 | Data | 0 | 31.92 | 30.117 | 201.601 | 7.63 | 189.294 | 2161.97 | 25.89 | 44.554 | 6.35 | 1.396 | 4.897 | 8689.46 | 2.343 | 97.9 | 77.8 | 1405 | 22.28 | 5648.1 | 3039.9 | 2955.7 | 4352.8 | 1202.2 | 0.68213 | 6.294
2024-12-09 | 19:33 | Data | 0 | 32.028 | 29.726 | 201.33 | 7.63 | 189.113 | 2158.35 | 25.89 | 44.554 | 6.35 | 1.386 | 4.893 | 8689.46 | 2.302 | 97.9 | 77.9 | 1403 | 22.28 | 5648.1 | 3041.1 | 2957.9 | 4354.7 | 1202.2 | 0.68281 | 6.279
2024-12-09 | 19:33 | Data | 0 | 32.15 | 29.564 | 201.42 | 7.62 | 189.158 | 2159.26 | 25.89 | 44.554 | 6.35 | 1.393 | 4.902 | 8662.33 | 2.329 | 97.9 | 77.9 | 1403 | 22.28 | 5630.5 | 3044.3 | 2953.1 | 4351.9 | 1202.2 | 0.68289 | 6.296
2024-12-09 | 19:33 | Data | 0 | 31.927 | 29.638 | 201.42 | 7.63 | 189.158 | 2158.35 | 25.89 | 44.644 | 6.34 | 1.384 | 4.879 | 8671.37 | 2.174 | 97.9 | 77.9 | 1403 | 22.28 | 5636.4 | 3038.1 | 2946.1 | 4346.3 | 1202.2 | 0.68337 | 6.263
2024-12-09 | 19:33 | Data | 0 | 31.596 | 29.672 | 201.511 | 7.63 | 189.113 | 2159.26 | 25.89 | 44.554 | 6.35 | 1.398 | 4.873 | 8680.41 | 2.079 | 97.9 | 77.7 | 1404 | 22.28 | 5642.3 | 3035.8 | 2947.7 | 4345 | 1202.2 | 0.68277 | 6.272
2024-12-09 | 19:33 | Data | 0 | 32.028 | 30.111 | 201.375 | 7.63 | 189.203 | 2158.35 | 25.89 | 44.644 | 6.35 | 1.395 | 4.912 | 8662.33 | 2.093 | 97.9 | 77.9 | 1403 | 22.28 | 5630.5 | 3035.3 | 2923.9 | 4329.5 | 1202.2 | 0.68642 | 6.307
2024-12-09 | 19:33 | Data | 0 | 32.028 | 29.618 | 201.466 | 7.62 | 189.113 | 2159.26 | 25.89 | 44.554 | 6.35 | 1.394 | 4.916 | 8653.28 | 2.208 | 97.9 | 77.9 | 1404 | 22.28 | 5624.6 | 3038.6 | 2968 | 4361.9 | 1202.2 | 0.68115 | 6.31
2024-12-09 | 19:33 | Data | 0 | 32.136 | 29.942 | 201.511 | 7.63 | 189.158 | 2151.12 | 25.9 | 44.644 | 6.35 | 1.382 | 4.903 | 8662.33 | 2.302 | 97.9 | 78 | 1398 | 22.28 | 5630.5 | 3038.2 | 2940.9 | 4343.2 | 1202.2 | 0.68267 | 6.286
2024-12-09 | 19:33 | Data | 0 | 31.805 | 29.814 | 201.42 | 7.63 | 189.113 | 2155.64 | 25.89 | 44.554 | 6.35 | 1.389 | 4.939 | 8662.33 | 2.356 | 97.9 | 78 | 1401 | 22.28 | 5630.5 | 3034.9 | 2938.7 | 4337.3 | 1202.2 | 0.68402 | 6.329
2024-12-09 | 19:33 | Data | 0 | 31.913 | 29.746 | 201.466 | 7.63 | 189.113 | 2155.64 | 25.89 | 44.554 | 6.35 | 1.383 | 4.956 | 8671.37 | 2.268 | 97.9 | 78.2 | 1402 | 22.28 | 5636.4 | 3049.7 | 2950.2 | 4352.8 | 1202.2 | 0.68434 | 6.339
2024-12-09 | 19:33 | Data | 0 | 31.832 | 29.699 | 201.42 | 7.63 | 189.113 | 2156.54 | 25.89 | 44.193 | 6.34 | 1.383 | 4.92 | 8662.33 | 2.106 | 98 | 78.1 | 1402 | 22.1 | 5630.5 | 3025.6 | 2922.4 | 4321.5 | 1202.2 | 0.68477 | 6.303
2024-12-09 | 19:33 | Data | 0 | 31.934 | 30.09 | 201.556 | 7.62 | 189.203 | 2161.06 | 25.89 | 44.644 | 6.35 | 1.383 | 4.926 | 8662.33 | 2.187 | 97.9 | 78.1 | 1405 | 22.32 | 5630.5 | 3041 | 2922 | 4334.1 | 1202.2 | 0.68409 | 6.309
2024-12-09 | 19:33 | Data | 0 | 31.799 | 29.888 | 201.601 | 7.62 | 189.203 | 2161.06 | 25.89 | 44.554 | 6.35 | 1.385 | 4.919 | 8644.24 | 2.228 | 97.9 | 78 | 1405 | 22.28 | 5618.8 | 3027.6 | 2951 | 4342.5 | 1202.2 | 0.68397 | 6.303
2024-12-09 | 19:33 | Data | 0 | 32.251 | 29.996 | 201.601 | 7.62 | 189.248 | 2163.77 | 25.89 | 44.644 | 6.35 | 1.382 | 4.926 | 8639.71 | 2.214 | 97.9 | 78.1 | 1406 | 22.28 | 5615.8 | 3037.9 | 2953.4 | 4349 | 1202.2 | 0.68229 | 6.308
2024-12-09 | 19:33 | Data | 0 | 32.197 | 29.901 | 201.556 | 7.63 | 189.158 | 2164.68 | 25.9 | 44.554 | 6.35 | 1.393 | 4.928 | 8635.19 | 2.086 | 97.9 | 78 | 1408 | 22.28 | 5612.9 | 3037 | 2945.8 | 4344.3 | 1202.2 | 0.68134 | 6.32
2024-12-09 | 19:33 | Data | 0 | 31.832 | 29.733 | 201.601 | 7.62 | 189.113 | 2163.77 | 25.89 | 44.554 | 6.35 | 1.399 | 4.925 | 8621.63 | 2.073 | 97.9 | 77.9 | 1406 | 22.28 | 5604.1 | 3030.2 | 2964.2 | 4352.4 | 1202.2 | 0.68016 | 6.325
2024-12-09 | 19:33 | Data | 0 | 32.231 | 29.955 | 201.511 | 7.63 | 189.203 | 2163.77 | 25.89 | 44.644 | 6.35 | 1.404 | 4.928 | 8689.46 | 2.309 | 97.9 | 77.8 | 1406 | 22.32 | 5648.1 | 3043.9 | 2942.9 | 4346.6 | 1202.2 | 0.68433 | 6.331
2024-12-09 | 19:33 | Data | 0 | 32.028 | 29.841 | 201.42 | 7.63 | 189.158 | 2161.06 | 25.89 | 44.554 | 6.34 | 1.402 | 4.944 | 8703.03 | 2.302 | 97.9 | 77.9 | 1405 | 22.28 | 5657 | 3042.3 | 2945.5 | 4350.7 | 1202.2 | 0.68389 | 6.346
2024-12-09 | 19:34 | Data | 0 | 32.015 | 29.895 | 201.511 | 7.62 | 189.113 | 2161.97 | 25.89 | 44.554 | 6.35 | 1.395 | 4.92 | 8721.11 | 2.309 | 97.9 | 77.9 | 1405 | 22.28 | 5668.7 | 3054.1 | 2949 | 4357 | 1202.2 | 0.68475 | 6.315
2024-12-09 | 19:34 | Data | 0 | 31.859 | 29.726 | 201.375 | 7.62 | 189.158 | 2166.49 | 25.89 | 44.373 | 6.35 | 1.399 | 4.926 | 8703.03 | 2.106 | 97.9 | 77.9 | 1409 | 22.23 | 5657 | 3018.3 | 2963.9 | 4346.3 | 1202.2 | 0.6776 | 6.327
2024-12-09 | 19:34 | Data | 0 | 32.028 | 29.935 | 201.42 | 7.63 | 189.022 | 2166.49 | 25.89 | 44.554 | 6.34 | 1.392 | 4.933 | 8703.03 | 2.221 | 97.9 | 78 | 1408 | 22.28 | 5657 | 3041.1 | 2944.8 | 4344.6 | 1202.2 | 0.68407 | 6.325
2024-12-09 | 19:34 | Data | 0 | 32.028 | 30.036 | 201.466 | 7.62 | 189.203 | 2170.1 | 25.89 | 44.554 | 6.35 | 1.394 | 4.93 | 8703.03 | 2.1 | 97.9 | 78 | 1411 | 22.28 | 5657 | 3052.6 | 2954.2 | 4360.6 | 1202.2 | 0.68426 | 6.324
2024-12-09 | 19:34 | Data | 0 | 32.244 | 29.78 | 201.511 | 7.63 | 189.158 | 2170.1 | 25.89 | 44.554 | 6.35 | 1.392 | 4.924 | 8716.59 | 2.302 | 97.9 | 78 | 1411 | 22.32 | 5665.8 | 3040.5 | 2961 | 4356.8 | 1202.2 | 0.68163 | 6.316
2024-12-09 | 19:34 | Data | 0 | 31.832 | 29.827 | 201.511 | 7.63 | 189.113 | 2171.01 | 25.89 | 44.644 | 6.35 | 1.392 | 4.938 | 8716.59 | 2.093 | 97.9 | 78 | 1411 | 22.28 | 5665.8 | 3054.6 | 2968.1 | 4363.9 | 1202.2 | 0.68155 | 6.329
2024-12-09 | 19:34 | Data | 0 | 32.062 | 29.928 | 201.511 | 7.63 | 189.203 | 2172.81 | 25.9 | 44.554 | 6.35 | 1.38 | 4.934 | 8703.03 | 2.133 | 97.9 | 78.1 | 1412 | 22.28 | 5657 | 3051.2 | 2967.6 | 4373.7 | 1202.2 | 0.68292 | 6.316
2024-12-09 | 19:34 | Data | 0 | 32.048 | 30.057 | 201.692 | 7.63 | 189.294 | 2171.91 | 25.89 | 44.554 | 6.35 | 1.387 | 4.935 | 8712.07 | 2.133 | 97.9 | 78.1 | 1412 | 22.28 | 5662.8 | 3050.1 | 2967.2 | 4368.1 | 1202.2 | 0.68086 | 6.323
2024-12-09 | 19:34 | Data | 0 | 32.46 | 29.76 | 201.556 | 7.63 | 189.203 | 2171.91 | 25.89 | 44.644 | 6.35 | 1.385 | 4.935 | 8698.5 | 2.349 | 97.9 | 78.1 | 1412 | 22.28 | 5654 | 3040.9 | 2955.7 | 4352.3 | 1202.2 | 0.68259 | 6.319
2024-12-09 | 19:34 | Data | 0 | 32.204 | 29.807 | 201.556 | 7.63 | 189.158 | 2172.81 | 25.89 | 44.464 | 6.35 | 1.395 | 4.952 | 8693.98 | 2.376 | 98 | 78 | 1412 | 22.28 | 5651.1 | 3054.7 | 2967.2 | 4378.8 | 1202.2 | 0.68173 | 6.346
2024-12-09 | 19:34 | Data | 0 | 32.251 | 29.753 | 201.511 | 7.63 | 189.248 | 2171.91 | 25.89 | 44.554 | 6.34 | 1.388 | 4.921 | 8684.94 | 2.302 | 97.9 | 78 | 1412 | 22.32 | 5645.2 | 3049.2 | 2972.3 | 4366.4 | 1202.3 | 0.6808 | 6.309
2024-12-09 | 19:34 | Data | 0 | 31.913 | 29.719 | 201.375 | 7.63 | 189.113 | 2172.81 | 25.89 | 44.554 | 6.35 | 1.387 | 4.929 | 8689.46 | 2.289 | 97.9 | 78 | 1412 | 22.28 | 5648.1 | 3037.5 | 2958.1 | 4350.2 | 1202.3 | 0.68153 | 6.315
2024-12-09 | 19:34 | Data | 0 | 32.318 | 29.746 | 201.375 | 7.63 | 189.294 | 2171.01 | 25.89 | 44.644 | 6.35 | 1.392 | 4.913 | 8693.98 | 2.302 | 97.9 | 77.9 | 1411 | 22.32 | 5651.1 | 3045 | 2967.3 | 4360.2 | 1202.3 | 0.68252 | 6.306
2024-12-09 | 19:34 | Data | 0 | 32.366 | 29.895 | 201.511 | 7.62 | 189.248 | 2171.91 | 25.89 | 44.554 | 6.34 | 1.395 | 4.904 | 8693.98 | 2.302 | 97.9 | 77.9 | 1411 | 22.28 | 5651.1 | 3052.1 | 2965.4 | 4365.7 | 1202.3 | 0.68334 | 6.299
2024-12-09 | 19:34 | Data | 0 | 32.345 | 29.982 | 201.601 | 7.63 | 189.248 | 2170.1 | 25.89 | 44.554 | 6.35 | 1.39 | 4.94 | 8703.03 | 2.221 | 97.9 | 78.1 | 1411 | 22.28 | 5657 | 3021.6 | 2961.9 | 4347 | 1202.3 | 0.67796 | 6.329
2024-12-09 | 19:34 | Data | 0 | 32.015 | 29.888 | 201.466 | 7.63 | 189.113 | 2169.2 | 25.9 | 44.554 | 6.34 | 1.394 | 4.942 | 8730.16 | 2.343 | 97.9 | 78 | 1411 | 22.28 | 5674.6 | 3034.5 | 2987.1 | 4375.6 | 1202.3 | 0.67662 | 6.338
2024-12-09 | 19:34 | Data | 0 | 32.089 | 29.901 | 201.511 | 7.62 | 189.248 | 2163.77 | 25.89 | 44.554 | 6.35 | 1.391 | 4.924 | 8730.16 | 2.302 | 97.9 | 78 | 1406 | 22.23 | 5674.6 | 3047.5 | 3006.2 | 4391.3 | 1202.3 | 0.67803 | 6.317
2024-12-09 | 19:34 | Data | 0 | 31.826 | 29.827 | 201.511 | 7.62 | 189.203 | 2170.1 | 25.89 | 44.644 | 6.35 | 1.393 | 4.894 | 8716.59 | 2.187 | 97.9 | 77.8 | 1411 | 22.28 | 5665.8 | 3062.3 | 3001 | 4397.3 | 1202.3 | 0.68081 | 6.287
2024-12-09 | 19:35 | Data | 0 | 32.258 | 29.955 | 201.601 | 7.63 | 189.248 | 2170.1 | 25.9 | 44.464 | 6.35 | 1.395 | 4.92 | 8721.11 | 2.309 | 97.9 | 77.9 | 1411 | 22.28 | 5668.7 | 3047.9 | 2982 | 4371.3 | 1202.3 | 0.67986 | 6.315
2024-12-09 | 19:35 | Data | 0 | 32.352 | 30.009 | 201.737 | 7.62 | 189.294 | 2170.1 | 25.89 | 44.554 | 6.35 | 1.396 | 4.951 | 8689.46 | 2.289 | 97.9 | 78 | 1411 | 22.28 | 5648.1 | 3042.9 | 3009.7 | 4393.1 | 1202.3 | 0.67732 | 6.348
2024-12-09 | 19:35 | Data | 0 | 31.805 | 29.895 | 201.42 | 7.62 | 189.022 | 2170.1 | 25.89 | 44.554 | 6.35 | 1.389 | 4.928 | 8693.98 | 2.16 | 97.9 | 78 | 1411 | 22.28 | 5651.1 | 3044.6 | 2955.7 | 4354.1 | 1202.3 | 0.6823 | 6.317
2024-12-09 | 19:35 | Data | 0 | 32.278 | 29.895 | 201.556 | 7.63 | 189.339 | 2170.1 | 25.89 | 44.554 | 6.35 | 1.395 | 4.926 | 8693.98 | 2.201 | 97.9 | 77.9 | 1411 | 22.28 | 5651.1 | 3044.3 | 2962.5 | 4361.5 | 1202.3 | 0.68099 | 6.32
2024-12-09 | 19:35 | Data | 0 | 32.156 | 29.733 | 201.511 | 7.63 | 189.248 | 2170.1 | 25.89 | 44.554 | 6.35 | 1.394 | 4.925 | 8680.41 | 2.14 | 97.9 | 77.9 | 1410 | 22.28 | 5642.3 | 3054.4 | 2957.9 | 4356.7 | 1202.3 | 0.68306 | 6.32
2024-12-09 | 19:35 | Data | 0 | 32.028 | 29.841 | 201.511 | 7.63 | 189.203 | 2170.1 | 25.89 | 44.554 | 6.34 | 1.388 | 4.932 | 8671.37 | 2.275 | 98 | 78 | 1411 | 22.23 | 5636.4 | 3046.9 | 2975.3 | 4368.8 | 1202.3 | 0.68408 | 6.32
2024-12-09 | 19:35 | Data | 0 | 32.028 | 29.726 | 201.511 | 7.63 | 189.248 | 2170.1 | 25.89 | 44.644 | 6.34 | 1.394 | 4.931 | 8693.98 | 2.302 | 97.9 | 78 | 1411 | 22.32 | 5651.1 | 3021.7 | 2961 | 4343.6 | 1202.3 | 0.67971 | 6.326
2024-12-09 | 19:35 | Data | 0 | 31.805 | 29.699 | 201.42 | 7.62 | 189.158 | 2170.1 | 25.89 | 44.644 | 6.35 | 1.397 | 4.904 | 8693.98 | 2.127 | 97.9 | 77.8 | 1411 | 22.32 | 5651.1 | 3053.6 | 2951 | 4360.5 | 1202.3 | 0.68433 | 6.301
2024-12-09 | 19:35 | Data | 0 | 32.028 | 29.942 | 201.556 | 7.63 | 189.158 | 2170.1 | 25.89 | 44.554 | 6.34 | 1.391 | 4.913 | 8689.46 | 2.214 | 97.9 | 77.9 | 1411 | 22.32 | 5648.1 | 3037.2 | 2968 | 4362.6 | 1202.3 | 0.6778 | 6.305
2024-12-09 | 19:35 | Data | 0 | 32.318 | 29.739 | 201.466 | 7.63 | 189.248 | 2166.49 | 25.9 | 44.554 | 6.35 | 1.392 | 4.93 | 8689.46 | 2.147 | 97.9 | 78 | 1408 | 22.28 | 5648.1 | 3055.6 | 2963 | 4368.9 | 1202.3 | 0.68196 | 6.322
2024-12-09 | 19:35 | Data | 0 | 32.001 | 29.726 | 201.42 | 7.62 | 189.203 | 2170.1 | 25.9 | 44.464 | 6.35 | 1.398 | 4.938 | 8703.03 | 2.289 | 98 | 77.9 | 1411 | 22.23 | 5657 | 3027.1 | 2983.1 | 4366.3 | 1202.3 | 0.6773 | 6.336
2024-12-09 | 19:35 | Data | 0 | 32.264 | 29.969 | 201.511 | 7.63 | 189.248 | 2169.2 | 25.89 | 44.554 | 6.35 | 1.396 | 4.926 | 8703.03 | 2.295 | 97.9 | 77.9 | 1411 | 22.23 | 5657 | 3042.5 | 2991.8 | 4380 | 1202.3 | 0.67889 | 6.322
2024-12-09 | 19:35 | Data | 0 | 31.859 | 29.719 | 201.42 | 7.63 | 189.113 | 2172.81 | 25.89 | 44.554 | 6.35 | 1.394 | 4.931 | 8693.98 | 2.1 | 97.9 | 78 | 1412 | 22.28 | 5651.1 | 3033.9 | 2981.7 | 4368 | 1202.3 | 0.67758 | 6.326
2024-12-09 | 19:35 | Data | 0 | 31.805 | 29.928 | 201.511 | 7.63 | 189.158 | 2172.81 | 25.89 | 44.554 | 6.35 | 1.4 | 4.92 | 8707.55 | 2.16 | 97.9 | 77.8 | 1412 | 22.28 | 5659.9 | 3059.6 | 2979.4 | 4382 | 1202.3 | 0.68207 | 6.32
2024-12-09 | 19:35 | Data | 0 | 32.474 | 30.212 | 201.646 | 7.62 | 189.339 | 2174.62 | 25.89 | 44.554 | 6.34 | 1.4 | 4.924 | 8703.03 | 2.14 | 98 | 77.9 | 1414 | 22.28 | 5657 | 3054.4 | 2979.6 | 4375.7 | 1202.3 | 0.68303 | 6.324
2024-12-09 | 19:35 | Data | 0 | 32.028 | 29.78 | 201.466 | 7.63 | 189.158 | 2171.91 | 25.9 | 44.554 | 6.35 | 1.387 | 4.936 | 8707.55 | 2.181 | 97.9 | 78 | 1412 | 22.28 | 5659.9 | 3034.1 | 2951.1 | 4350.9 | 1202.3 | 0.6805 | 6.323
2024-12-09 | 19:35 | Data | 0 | 31.913 | 29.895 | 201.42 | 7.63 | 189.068 | 2171.91 | 25.89 | 44.554 | 6.35 | 1.382 | 4.943 | 8707.55 | 2.241 | 97.9 | 78.2 | 1412 | 22.32 | 5659.9 | 3041.2 | 2950.7 | 4356 | 1202.3 | 0.68109 | 6.325
2024-12-09 | 19:36 | Data | 0 | 32.264 | 29.76 | 201.375 | 7.62 | 189.248 | 2170.1 | 25.89 | 44.464 | 6.34 | 1.39 | 4.907 | 8671.37 | 2.295 | 97.9 | 77.9 | 1411 | 22.28 | 5636.4 | 3045.1 | 2978.5 | 4371.2 | 1202.3 | 0.68138 | 6.297
2024-12-09 | 19:36 | Data | 0 | 31.758 | 29.712 | 201.466 | 7.63 | 189.068 | 2171.01 | 25.89 | 44.554 | 6.35 | 1.398 | 4.929 | 8662.33 | 2.268 | 97.9 | 77.9 | 1411 | 22.28 | 5630.5 | 3040.8 | 2952.7 | 4352.2 | 1202.3 | 0.68299 | 6.329
2024-12-09 | 19:36 | Data | 0 | 32.339 | 30.016 | 201.646 | 7.63 | 189.248 | 2171.01 | 25.89 | 44.644 | 6.35 | 1.395 | 4.949 | 8671.37 | 2.484 | 97.9 | 78 | 1411 | 22.28 | 5636.4 | 3051.9 | 2931.5 | 4347.4 | 1202.3 | 0.68632 | 6.345
2024-12-09 | 19:36 | Data | 0 | 32.028 | 30.09 | 201.556 | 7.63 | 189.203 | 2172.81 | 25.89 | 44.644 | 6.35 | 1.391 | 4.942 | 8680.41 | 2.14 | 97.9 | 78 | 1412 | 22.32 | 5642.3 | 3047.5 | 2953.1 | 4366.3 | 1202.3 | 0.68396 | 6.333
2024-12-09 | 19:36 | Data | 0 | 32.264 | 30.117 | 201.692 | 7.63 | 189.248 | 2172.81 | 25.89 | 44.554 | 6.35 | 1.398 | 4.901 | 8703.03 | 2.329 | 97.9 | 77.8 | 1412 | 22.28 | 5657 | 3061.1 | 2959.7 | 4369.1 | 1202.3 | 0.68381 | 6.3
2024-12-09 | 19:36 | Data | 0 | 32.143 | 29.841 | 199.701 | 7.63 | 187.576 | 2172.81 | 25.9 | 44.464 | 6.35 | 1.4 | 4.891 | 8703.03 | 2.201 | 98 | 77.7 | 1412 | 22.28 | 5657 | 3043.4 | 2921.2 | 4334.8 | 1202.3 | 0.68529 | 6.291
2024-12-09 | 19:36 | Data | 0 | 32.649 | 30.617 | 194.047 | 7.63 | 182.515 | 2166.49 | 25.89 | 44.554 | 6.35 | 1.376 | 4.852 | 8707.55 | 2.16 | 97.9 | 77.9 | 1408 | 22.32 | 5659.9 | 2982.7 | 2895.6 | 4272.2 | 1202.3 | 0.68172 | 6.228
2024-12-09 | 19:36 | Data | 0 | 32.501 | 30.529 | 189.208 | 7.63 | 177.95 | 2163.77 | 25.89 | 44.554 | 6.35 | 1.37 | 4.75 | 8693.98 | 1.843 | 97.9 | 77.6 | 1406 | 22.28 | 5651.1 | 2944.9 | 2850.9 | 4214.9 | 1202.3 | 0.68265 | 6.12
2024-12-09 | 19:36 | Data | 0 | 32.946 | 30.766 | 185.182 | 7.62 | 174.289 | 2163.77 | 25.89 | 44.554 | 6.35 | 1.348 | 4.672 | 8671.37 | 1.897 | 97.9 | 77.6 | 1406 | 22.28 | 5636.4 | 2886.2 | 2786.7 | 4129.9 | 1202.3 | 0.68168 | 6.019
2024-12-09 | 19:36 | Data | 0 | 32.953 | 31.312 | 182.106 | 7.63 | 171.578 | 2163.77 | 25.9 | 44.554 | 6.35 | 1.343 | 4.58 | 8689.46 | 1.728 | 97.9 | 77.3 | 1407 | 22.28 | 5648.1 | 2835.2 | 2786.6 | 4099.9 | 1202.3 | 0.67469 | 5.924
2024-12-09 | 19:36 | Data | 0 | 33.129 | 31.454 | 179.483 | 7.63 | 169.092 | 2163.77 | 25.89 | 44.825 | 6.35 | 1.334 | 4.493 | 8684.94 | 1.85 | 97.9 | 77.1 | 1406 | 22.41 | 5645.2 | 2836.9 | 2771.3 | 4087.1 | 1202.4 | 0.67718 | 5.827
2024-12-09 | 19:36 | Data | 0 | 33.412 | 31.738 | 177.899 | 7.63 | 167.646 | 2163.77 | 25.89 | 44.915 | 6.35 | 1.326 | 4.421 | 8662.33 | 1.789 | 97.9 | 76.9 | 1406 | 22.41 | 5630.5 | 2789.8 | 2748.3 | 4037.6 | 1202.4 | 0.67331 | 5.747
2024-12-09 | 19:36 | Data | 0 | 33.183 | 31.285 | 176.226 | 7.63 | 166.2 | 2161.06 | 25.89 | 45.547 | 6.36 | 1.32 | 4.408 | 8653.28 | 1.776 | 97.9 | 77 | 1405 | 22.77 | 5624.6 | 2791.2 | 2735.8 | 4031.1 | 1202.4 | 0.67558 | 5.728
2024-12-09 | 19:36 | Data | 0 | 33.257 | 31.184 | 175.231 | 7.62 | 165.296 | 2158.35 | 25.89 | 46.089 | 6.36 | 1.312 | 4.381 | 8635.19 | 1.809 | 97.9 | 77 | 1403 | 23.04 | 5612.9 | 2788.6 | 2734.9 | 4028.7 | 1202.4 | 0.67472 | 5.693
2024-12-09 | 19:36 | Data | 0 | 33.432 | 31.414 | 174.145 | 7.62 | 164.211 | 2159.26 | 25.9 | 46.45 | 6.37 | 1.307 | 4.35 | 8617.1 | 1.681 | 97.8 | 76.9 | 1404 | 23.22 | 5601.1 | 2776.3 | 2714.9 | 4003.7 | 1202.4 | 0.67714 | 5.657
2024-12-09 | 19:36 | Data | 0 | 33.189 | 31.515 | 174.1 | 7.63 | 164.076 | 2164.68 | 25.9 | 46.721 | 6.38 | 1.317 | 4.317 | 8594.49 | 1.843 | 97.8 | 76.6 | 1407 | 23.41 | 5586.4 | 2776.9 | 2713.5 | 4005.6 | 1202.4 | 0.67646 | 5.634
2024-12-09 | 19:36 | Data | 0 | 33.284 | 31.366 | 174.055 | 7.63 | 164.121 | 2161.06 | 25.9 | 47.172 | 6.37 | 1.31 | 4.334 | 8594.49 | 1.89 | 97.8 | 76.8 | 1405 | 23.59 | 5586.4 | 2761.9 | 2701.5 | 3987.8 | 1202.4 | 0.67665 | 5.643
2024-12-09 | 19:36 | Data | 0 | 33.237 | 31.461 | 174.236 | 7.63 | 164.166 | 2161.06 | 25.91 | 47.353 | 6.37 | 1.302 | 4.331 | 8576.4 | 1.85 | 97.8 | 76.9 | 1405 | 23.68 | 5574.7 | 2763.2 | 2689.8 | 3979.1 | 1202.4 | 0.67896 | 5.633
2024-12-09 | 19:37 | Data | 0 | 33.412 | 31.346 | 174.236 | 7.63 | 164.166 | 2161.06 | 25.91 | 47.894 | 6.38 | 1.303 | 4.336 | 8540.22 | 1.843 | 97.8 | 76.9 | 1405 | 23.95 | 5551.1 | 2769 | 2697.6 | 3989.8 | 1202.4 | 0.67717 | 5.639
2024-12-09 | 19:37 | Data | 0 | 33.183 | 31.339 | 173.828 | 7.63 | 163.85 | 2161.97 | 25.93 | 47.804 | 6.38 | 1.31 | 4.364 | 8522.14 | 1.843 | 97.8 | 76.9 | 1405 | 23.95 | 5539.4 | 2766.8 | 2683.8 | 3985 | 1202.4 | 0.67798 | 5.674
2024-12-09 | 19:37 | Data | 0 | 33.243 | 31.542 | 173.105 | 7.62 | 163.172 | 2164.68 | 25.91 | 47.894 | 6.38 | 1.305 | 4.343 | 8291.5 | 1.553 | 97.8 | 76.9 | 1406 | 23.95 | 5389.5 | 2760.1 | 2674.8 | 3971.1 | 1202.4 | 0.67786 | 5.649
2024-12-09 | 19:37 | Data | 0 | 33.027 | 31.515 | 173.15 | 7.62 | 163.217 | 2166.49 | 25.91 | 48.165 | 6.39 | 1.3 | 4.318 | 8277.94 | 1.512 | 97.8 | 76.9 | 1408 | 24.04 | 5380.7 | 2759 | 2687.5 | 3976.2 | 1202.4 | 0.67718 | 5.617
2024-12-09 | 19:37 | Data | 0 | 33.156 | 31.542 | 173.105 | 7.63 | 163.081 | 2167.39 | 25.92 | 48.165 | 6.38 | 1.293 | 4.302 | 8250.8 | 1.931 | 97.8 | 76.9 | 1408 | 24.08 | 5363 | 2754.6 | 2696.4 | 3975.1 | 1202.4 | 0.6777 | 5.595
2024-12-09 | 19:37 | Data | 0 | 33.183 | 31.4 | 173.15 | 7.62 | 163.307 | 2162.87 | 25.91 | 48.165 | 6.38 | 1.297 | 4.315 | 8255.33 | 1.728 | 97.8 | 76.9 | 1406 | 24.08 | 5366 | 2747 | 2681 | 3968.2 | 1202.4 | 0.67587 | 5.611
2024-12-09 | 19:37 | Data | 0 | 33.385 | 31.454 | 173.195 | 7.63 | 163.172 | 2166.49 | 25.92 | 48.165 | 6.39 | 1.309 | 4.295 | 8431.69 | 1.87 | 97.8 | 76.6 | 1408 | 24.08 | 5480.6 | 2751.4 | 2687.3 | 3972.2 | 1202.4 | 0.67586 | 5.604
2024-12-09 | 19:37 | Data | 0 | 33.608 | 31.697 | 173.15 | 7.63 | 163.172 | 2163.77 | 25.92 | 48.436 | 6.39 | 1.304 | 4.308 | 8440.74 | 1.823 | 97.8 | 76.8 | 1406 | 24.22 | 5486.5 | 2765.2 | 2695.8 | 3981.9 | 1202.4 | 0.67684 | 5.612
2024-12-09 | 19:37 | Data | 0 | 33.183 | 31.785 | 173.195 | 7.63 | 163.262 | 2162.87 | 25.92 | 48.436 | 6.39 | 1.301 | 4.29 | 8431.69 | 1.674 | 97.8 | 76.7 | 1406 | 24.22 | 5480.6 | 2757.3 | 2684.7 | 3973.9 | 1202.4 | 0.67721 | 5.591
2024-12-09 | 19:37 | Data | 0 | 33.412 | 31.799 | 173.195 | 7.63 | 163.172 | 2170.1 | 25.93 | 48.346 | 6.39 | 1.305 | 4.291 | 8409.08 | 1.789 | 97.8 | 76.7 | 1411 | 24.17 | 5465.9 | 2744.6 | 2676.1 | 3962.3 | 1202.4 | 0.67634 | 5.596
2024-12-09 | 19:37 | Data | 0 | 33.183 | 31.562 | 173.06 | 7.63 | 163.081 | 2169.2 | 25.93 | 48.436 | 6.39 | 1.302 | 4.291 | 8418.13 | 1.641 | 97.8 | 76.7 | 1410 | 24.22 | 5471.8 | 2791.7 | 2683.5 | 3993 | 1202.4 | 0.68337 | 5.592
2024-12-09 | 19:37 | Data | 0 | 33.196 | 31.339 | 173.014 | 7.63 | 163.081 | 2170.1 | 25.93 | 48.436 | 6.39 | 1.291 | 4.321 | 8418.13 | 1.755 | 97.8 | 77 | 1411 | 24.22 | 5471.8 | 2760.1 | 2687.5 | 3975.3 | 1202.4 | 0.67889 | 5.611
2024-12-09 | 19:37 | Data | 0 | 33.52 | 31.596 | 173.195 | 7.63 | 163.217 | 2166.49 | 25.92 | 48.346 | 6.39 | 1.3 | 4.323 | 8404.56 | 1.816 | 97.8 | 76.9 | 1409 | 24.22 | 5463 | 2751.9 | 2675.9 | 3958.1 | 1202.4 | 0.67781 | 5.622
2024-12-09 | 19:37 | Data | 0 | 33.804 | 31.65 | 173.331 | 7.62 | 163.217 | 2170.1 | 25.92 | 48.346 | 6.39 | 1.294 | 4.308 | 8400.04 | 1.715 | 97.8 | 76.9 | 1411 | 24.22 | 5460 | 2766.7 | 2680.6 | 3973.6 | 1202.4 | 0.67906 | 5.602
2024-12-09 | 19:37 | Data | 0 | 33.311 | 31.528 | 173.105 | 7.63 | 163.172 | 2171.01 | 25.92 | 48.436 | 6.39 | 1.302 | 4.318 | 8381.95 | 1.6 | 97.8 | 76.8 | 1412 | 24.17 | 5448.3 | 2744.9 | 2683.1 | 3977.9 | 1202.4 | 0.6765 | 5.62
2024-12-09 | 19:37 | Data | 0 | 33.412 | 31.616 | 173.331 | 7.62 | 163.262 | 2175.52 | 25.93 | 48.526 | 6.39 | 1.31 | 4.313 | 8377.43 | 1.749 | 97.8 | 76.7 | 1414 | 24.22 | 5445.3 | 2738.4 | 2672.4 | 3954.8 | 1202.4 | 0.67498 | 5.623
2024-12-09 | 19:37 | Data | 0 | 33.689 | 31.63 | 173.331 | 7.63 | 163.262 | 2170.1 | 25.91 | 48.075 | 6.39 | 1.304 | 4.313 | 8400.04 | 1.728 | 97.8 | 76.8 | 1411 | 24.08 | 5460 | 2776 | 2689.5 | 3992.4 | 1202.4 | 0.67829 | 5.617
2024-12-09 | 19:37 | Data | 0 | 33.574 | 31.63 | 173.24 | 7.63 | 163.172 | 2170.1 | 25.91 | 47.894 | 6.38 | 1.293 | 4.31 | 8377.43 | 1.823 | 97.8 | 76.9 | 1411 | 23.95 | 5445.3 | 2742.2 | 2669.7 | 3956 | 1202.4 | 0.67658 | 5.602
2024-12-09 | 19:38 | Data | 0 | 33.466 | 31.414 | 173.105 | 7.63 | 163.172 | 2167.39 | 25.92 | 48.075 | 6.39 | 1.301 | 4.307 | 8345.77 | 1.769 | 97.8 | 76.8 | 1409 | 24.08 | 5424.8 | 2739.6 | 2669.8 | 3952.9 | 1202.4 | 0.67715 | 5.609
2024-12-09 | 19:38 | Data | 0 | 33.385 | 31.738 | 173.195 | 7.63 | 163.126 | 2177.33 | 25.91 | 48.075 | 6.39 | 1.315 | 4.308 | 8323.16 | 1.857 | 97.8 | 76.6 | 1415 | 24.08 | 5410.1 | 2751.2 | 2669.8 | 3959.5 | 1202.4 | 0.67735 | 5.626
2024-12-09 | 19:38 | Data | 0 | 33.189 | 31.569 | 173.15 | 7.63 | 163.172 | 2171.91 | 25.93 | 48.165 | 6.39 | 1.304 | 4.313 | 8332.2 | 1.614 | 97.8 | 76.8 | 1412 | 24.08 | 5415.9 | 2738.3 | 2679.8 | 3954.5 | 1202.4 | 0.67604 | 5.616
2024-12-09 | 19:38 | Data | 0 | 33.203 | 31.569 | 173.15 | 7.62 | 163.217 | 2172.81 | 25.93 | 48.165 | 6.39 | 1.296 | 4.331 | 8332.2 | 1.506 | 97.8 | 77 | 1412 | 24.08 | 5415.9 | 2772.9 | 2664.6 | 3963.7 | 1202.4 | 0.68311 | 5.626
2024-12-09 | 19:38 | Data | 0 | 33.635 | 31.576 | 173.195 | 7.62 | 163.262 | 2170.1 | 25.92 | 48.075 | 6.39 | 1.308 | 4.307 | 8336.72 | 1.742 | 97.8 | 76.7 | 1410 | 24.08 | 5418.9 | 2774.3 | 2662.1 | 3969.2 | 1202.4 | 0.67961 | 5.616
2024-12-09 | 19:38 | Data | 0 | 33.405 | 31.569 | 173.014 | 7.63 | 163.126 | 2170.1 | 25.92 | 48.165 | 6.39 | 1.301 | 4.295 | 8332.2 | 1.836 | 97.8 | 76.8 | 1411 | 24.08 | 5415.9 | 2742.5 | 2653.1 | 3940.9 | 1202.4 | 0.6793 | 5.597
2024-12-09 | 19:38 | Data | 0 | 33.588 | 31.637 | 173.15 | 7.63 | 163.262 | 2171.01 | 25.93 | 48.255 | 6.39 | 1.294 | 4.285 | 8336.72 | 1.809 | 97.8 | 76.8 | 1411 | 24.08 | 5418.9 | 2748.5 | 2660.5 | 3952.1 | 1202.4 | 0.6802 | 5.578
2024-12-09 | 19:38 | Data | 0 | 33.567 | 31.637 | 173.06 | 7.63 | 163.172 | 2170.1 | 25.92 | 48.255 | 6.39 | 1.291 | 4.302 | 8318.64 | 1.776 | 97.8 | 76.9 | 1411 | 24.04 | 5407.1 | 2757.2 | 2666.3 | 3959.4 | 1202.4 | 0.67837 | 5.592
2024-12-09 | 19:38 | Data | 0 | 33.385 | 31.785 | 173.195 | 7.63 | 163.126 | 2170.1 | 25.93 | 48.165 | 6.38 | 1.299 | 4.324 | 8345.77 | 1.668 | 97.8 | 76.9 | 1411 | 24.08 | 5424.8 | 2737.2 | 2662.9 | 3946.2 | 1202.4 | 0.67775 | 5.623
2024-12-09 | 19:38 | Data | 0 | 33.581 | 31.63 | 173.195 | 7.63 | 163.172 | 2176.43 | 25.93 | 48.165 | 6.39 | 1.294 | 4.31 | 8318.64 | 1.789 | 97.8 | 76.9 | 1415 | 24.08 | 5407.1 | 2740.2 | 2661.5 | 3939.7 | 1202.4 | 0.67922 | 5.603
2024-12-09 | 19:38 | Data | 0 | 33.52 | 31.799 | 173.06 | 7.63 | 163.126 | 2177.33 | 25.92 | 48.075 | 6.39 | 1.302 | 4.297 | 8323.16 | 1.661 | 97.8 | 76.7 | 1415 | 24.04 | 5410.1 | 2756.5 | 2667 | 3955.3 | 1202.4 | 0.68333 | 5.6
2024-12-09 | 19:38 | Data | 0 | 33.257 | 31.569 | 173.15 | 7.62 | 163.217 | 2176.43 | 25.92 | 48.165 | 6.39 | 1.302 | 4.314 | 8332.2 | 1.634 | 97.8 | 76.8 | 1414 | 24.13 | 5415.9 | 2753 | 2662.2 | 3956.7 | 1202.4 | 0.6778 | 5.616
2024-12-09 | 19:38 | Data | 0 | 33.257 | 31.569 | 173.15 | 7.62 | 163.217 | 2177.33 | 25.93 | 48.165 | 6.38 | 1.306 | 4.319 | 8332.2 | 1.62 | 97.8 | 76.8 | 1415 | 24.08 | 5415.9 | 2753.1 | 2704.2 | 3985.3 | 1202.4 | 0.67285 | 5.626
2024-12-09 | 19:38 | Data | 0 | 33.311 | 31.515 | 173.06 | 7.62 | 163.172 | 2174.62 | 25.92 | 48.165 | 6.39 | 1.295 | 4.283 | 8318.64 | 1.742 | 97.8 | 76.8 | 1414 | 24.08 | 5407.1 | 2764.7 | 2727 | 3992.6 | 1202.5 | 0.67094 | 5.578
2024-12-09 | 19:38 | Data | 0 | 33.189 | 31.576 | 173.24 | 7.63 | 163.307 | 2172.81 | 25.93 | 48.165 | 6.39 | 1.302 | 4.305 | 8332.2 | 1.782 | 97.8 | 76.8 | 1412 | 24.08 | 5415.9 | 2783.1 | 2712.4 | 4014.7 | 1202.5 | 0.67624 | 5.608
2024-12-09 | 19:38 | Data | 0 | 33.851 | 31.643 | 173.195 | 7.63 | 163.352 | 2173.72 | 25.93 | 48.075 | 6.39 | 1.303 | 4.303 | 8323.16 | 1.843 | 97.8 | 76.8 | 1412 | 24.04 | 5410.1 | 2764.1 | 2703.8 | 3990 | 1202.5 | 0.67567 | 5.606
2024-12-09 | 19:38 | Data | 0 | 33.297 | 31.569 | 173.15 | 7.63 | 163.172 | 2172.81 | 25.93 | 48.165 | 6.39 | 1.297 | 4.324 | 8323.16 | 1.62 | 97.8 | 76.9 | 1412 | 24.08 | 5410.1 | 2765.1 | 2728 | 4009.6 | 1202.5 | 0.67265 | 5.621
2024-12-09 | 19:38 | Data | 0 | 33.021 | 31.724 | 173.24 | 7.63 | 163.217 | 2172.81 | 25.92 | 48.075 | 6.39 | 1.293 | 4.329 | 8305.07 | 1.506 | 97.8 | 77 | 1412 | 24.08 | 5398.3 | 2766.8 | 2637.2 | 3945.8 | 1202.5 | 0.68519 | 5.623
2024-12-09 | 19:39 | Data | 0 | 33.21 | 31.67 | 173.15 | 7.63 | 163.172 | 2172.81 | 25.92 | 48.165 | 6.39 | 1.302 | 4.283 | 8323.16 | 1.593 | 97.8 | 76.7 | 1412 | 24.08 | 5410.1 | 2743.4 | 2655 | 3944 | 1202.5 | 0.67931 | 5.587
2024-12-09 | 19:39 | Data | 0 | 33.351 | 31.481 | 173.06 | 7.62 | 163.172 | 2172.81 | 25.92 | 48.165 | 6.39 | 1.303 | 4.305 | 8332.2 | 2.005 | 97.8 | 76.8 | 1412 | 24.08 | 5415.9 | 2755 | 2646.1 | 3942.8 | 1202.5 | 0.6812 | 5.609
2024-12-09 | 19:39 | Data | 0 | 33.412 | 31.569 | 173.105 | 7.62 | 163.172 | 2169.2 | 25.92 | 48.165 | 6.38 | 1.311 | 4.321 | 8332.2 | 1.843 | 97.8 | 76.7 | 1410 | 24.08 | 5415.9 | 2752.2 | 2664.3 | 3955.2 | 1202.5 | 0.67821 | 5.632
2024-12-09 | 19:39 | Data | 0 | 33.419 | 31.569 | 173.15 | 7.63 | 163.217 | 2170.1 | 25.93 | 48.165 | 6.39 | 1.303 | 4.301 | 8332.2 | 1.722 | 97.8 | 76.7 | 1411 | 24.08 | 5415.9 | 2778.1 | 2689.2 | 3986.6 | 1202.5 | 0.6798 | 5.604
2024-12-09 | 19:39 | Data | 0 | 33.574 | 31.677 | 173.15 | 7.63 | 163.262 | 2170.1 | 25.94 | 48.075 | 6.39 | 1.297 | 4.314 | 8336.72 | 1.823 | 97.8 | 76.9 | 1411 | 24.08 | 5418.9 | 2759.2 | 2668.9 | 3956.2 | 1202.5 | 0.68056 | 5.61
2024-12-09 | 19:39 | Data | 0 | 33.183 | 31.569 | 173.105 | 7.62 | 163.172 | 2170.1 | 25.91 | 48.075 | 6.39 | 1.301 | 4.347 | 8332.2 | 1.641 | 97.8 | 77 | 1410 | 24.08 | 5415.9 | 2765 | 2670.4 | 3964.3 | 1202.5 | 0.68165 | 5.647
2024-12-09 | 19:39 | Data | 0 | 33.297 | 31.569 | 173.06 | 7.63 | 163.126 | 2170.1 | 25.93 | 48.165 | 6.39 | 1.294 | 4.321 | 8323.16 | 1.627 | 97.8 | 77 | 1410 | 24.08 | 5410.1 | 2752.7 | 2651.4 | 3945.8 | 1202.5 | 0.68101 | 5.614
2024-12-09 | 19:39 | Data | 0 | 33.392 | 31.67 | 173.105 | 7.63 | 163.172 | 2171.91 | 25.91 | 48.165 | 6.39 | 1.303 | 4.313 | 8336.72 | 1.715 | 97.8 | 76.8 | 1412 | 24.08 | 5418.9 | 2761.3 | 2674.9 | 3969 | 1202.5 | 0.67833 | 5.618
2024-12-09 | 19:39 | Data | 0 | 33.196 | 31.542 | 173.06 | 7.63 | 163.172 | 2177.33 | 25.92 | 48.165 | 6.38 | 1.306 | 4.324 | 8332.2 | 1.722 | 97.8 | 76.8 | 1415 | 24.13 | 5415.9 | 2770.9 | 2679.2 | 3976.3 | 1202.5 | 0.68124 | 5.631
2024-12-09 | 19:39 | Data | 0 | 33.412 | 31.623 | 173.15 | 7.63 | 163.172 | 2172.81 | 25.93 | 48.165 | 6.38 | 1.297 | 4.325 | 8332.2 | 1.728 | 97.8 | 76.9 | 1412 | 24.08 | 5415.9 | 2748.7 | 2659.7 | 3946.1 | 1202.5 | 0.67977 | 5.624
2024-12-09 | 19:39 | Data | 0 | 33.237 | 31.569 | 173.105 | 7.63 | 163.126 | 2172.81 | 25.93 | 48.165 | 6.39 | 1.302 | 4.313 | 8323.16 | 1.62 | 97.8 | 76.8 | 1413 | 24.08 | 5410.1 | 2762.2 | 2662 | 3958.1 | 1202.5 | 0.68096 | 5.616
2024-12-09 | 19:39 | Data | 0 | 33.837 | 31.637 | 173.24 | 7.63 | 163.352 | 2175.52 | 25.93 | 48.165 | 6.39 | 1.303 | 4.285 | 8318.64 | 1.89 | 97.8 | 76.7 | 1414 | 24.08 | 5407.1 | 2759.2 | 2664.9 | 3958.5 | 1202.5 | 0.68038 | 5.589
2024-12-09 | 19:39 | Data | 0 | 33.412 | 31.569 | 173.105 | 7.62 | 163.126 | 2172.81 | 25.92 | 48.165 | 6.38 | 1.302 | 4.285 | 8309.59 | 1.634 | 97.8 | 76.7 | 1412 | 24.08 | 5401.2 | 2762.4 | 2672.4 | 3964.5 | 1202.5 | 0.68277 | 5.588
2024-12-09 | 19:39 | Data | 0 | 33.412 | 31.745 | 173.15 | 7.63 | 163.172 | 2172.81 | 25.93 | 48.075 | 6.39 | 1.31 | 4.308 | 8318.64 | 1.668 | 97.8 | 76.7 | 1412 | 24.08 | 5407.1 | 2736 | 2676.3 | 3949.7 | 1202.5 | 0.67659 | 5.619
2024-12-09 | 19:39 | Data | 0 | 33.297 | 31.792 | 173.331 | 7.63 | 163.172 | 2172.81 | 25.91 | 48.165 | 6.39 | 1.301 | 4.305 | 8336.72 | 1.593 | 97.8 | 76.8 | 1412 | 24.08 | 5418.9 | 2763.5 | 2683.8 | 3972.6 | 1202.5 | 0.67916 | 5.607
2024-12-09 | 19:39 | Data | 0 | 33.453 | 31.569 | 173.376 | 7.63 | 163.262 | 2172.81 | 25.92 | 48.255 | 6.39 | 1.291 | 4.302 | 8332.2 | 1.627 | 97.8 | 76.9 | 1412 | 24.08 | 5415.9 | 2760.5 | 2674.5 | 3961.9 | 1202.5 | 0.68018 | 5.593
2024-12-09 | 19:39 | Data | 0 | 33.324 | 31.36 | 173.195 | 7.63 | 163.262 | 2172.81 | 25.91 | 48.075 | 6.38 | 1.3 | 4.309 | 8341.25 | 1.843 | 97.8 | 76.8 | 1412 | 24.08 | 5421.8 | 2748.4 | 2700.9 | 3977 | 1202.5 | 0.67349 | 5.61
2024-12-09 | 19:40 | Data | 0 | 33.581 | 31.792 | 173.195 | 7.63 | 163.217 | 2172.81 | 25.92 | 48.165 | 6.38 | 1.302 | 4.323 | 8350.29 | 1.823 | 97.8 | 76.9 | 1412 | 24.08 | 5427.7 | 2752.5 | 2653.1 | 3948.2 | 1202.5 | 0.68043 | 5.626
2024-12-09 | 19:40 | Data | 0 | 33.203 | 31.954 | 173.014 | 7.63 | 163.172 | 2066.16 | 25.93 | 48.075 | 6.39 | 1.301 | 4.342 | 8336.72 | 1.62 | 97.7 | 76.9 | 1343 | 24.08 | 5418.9 | 2754.8 | 2674.9 | 3966.4 | 1202.5 | 0.6778 | 5.642
2024-12-09 | 19:40 | Data | 0 | 33.399 | 31.684 | 173.195 | 7.63 | 163.217 | 2164.68 | 25.92 | 48.165 | 6.38 | 1.304 | 4.338 | 8300.55 | 1.728 | 97.8 | 76.9 | 1407 | 24.08 | 5395.4 | 2741.1 | 2648.8 | 3933.5 | 1202.5 | 0.68086 | 5.642
2024-12-09 | 19:40 | Data | 0 | 33.243 | 31.555 | 173.06 | 7.62 | 163.217 | 2166.49 | 25.93 | 48.165 | 6.38 | 1.301 | 4.334 | 8332.2 | 1.674 | 97.8 | 76.9 | 1408 | 24.08 | 5415.9 | 2749.9 | 2659.2 | 3949.2 | 1202.5 | 0.68032 | 5.636
2024-12-09 | 19:40 | Data | 0 | 33.291 | 31.569 | 173.195 | 7.63 | 163.172 | 2167.39 | 25.93 | 48.165 | 6.39 | 1.292 | 4.318 | 8332.2 | 1.803 | 97.8 | 77 | 1408 | 24.08 | 5415.9 | 2756 | 2657.4 | 3953 | 1202.5 | 0.6796 | 5.61
2024-12-09 | 19:40 | Data | 0 | 33.405 | 31.569 | 173.105 | 7.63 | 163.126 | 2166.49 | 25.93 | 48.165 | 6.39 | 1.3 | 4.321 | 8314.11 | 1.843 | 97.8 | 76.9 | 1408 | 24.08 | 5404.2 | 2745.1 | 2641.5 | 3928.8 | 1202.5 | 0.68167 | 5.621
2024-12-09 | 19:40 | Data | 0 | 33.385 | 31.569 | 173.15 | 7.63 | 163.172 | 2165.58 | 25.93 | 48.075 | 6.39 | 1.295 | 4.338 | 8305.07 | 1.836 | 97.8 | 77 | 1408 | 24.08 | 5398.3 | 2750.3 | 2668.8 | 3956.5 | 1202.5 | 0.67753 | 5.632
2024-12-09 | 19:40 | Data | 0 | 33.669 | 31.657 | 173.15 | 7.62 | 163.262 | 2166.49 | 25.93 | 48.075 | 6.38 | 1.296 | 4.318 | 8305.07 | 1.674 | 97.8 | 76.9 | 1409 | 24.08 | 5398.3 | 2766.7 | 2667 | 3958.2 | 1202.5 | 0.68118 | 5.614
2024-12-09 | 19:40 | Data | 0 | 33.642 | 31.637 | 173.195 | 7.62 | 163.217 | 2165.58 | 25.92 | 48.075 | 6.38 | 1.297 | 4.314 | 8305.07 | 1.823 | 97.8 | 76.9 | 1408 | 24.08 | 5398.3 | 2742.6 | 2659.8 | 3943.8 | 1202.5 | 0.67844 | 5.61
2024-12-09 | 19:40 | Data | 0 | 33.385 | 31.792 | 173.014 | 7.63 | 163.262 | 2169.2 | 25.93 | 48.075 | 6.39 | 1.306 | 4.295 | 8332.2 | 1.742 | 97.8 | 76.7 | 1410 | 24.08 | 5415.9 | 2754.7 | 2678.2 | 3962.1 | 1202.5 | 0.67784 | 5.601
2024-12-09 | 19:40 | Data | 0 | 33.412 | 31.569 | 173.15 | 7.63 | 163.172 | 2171.01 | 25.9 | 48.165 | 6.39 | 1.31 | 4.312 | 8350.29 | 1.83 | 97.8 | 76.7 | 1411 | 24.13 | 5427.7 | 2754 | 2655.8 | 3951.7 | 1202.5 | 0.67902 | 5.622
2024-12-09 | 19:40 | Data | 0 | 33.527 | 31.954 | 173.15 | 7.63 | 163.217 | 2170.1 | 25.91 | 48.165 | 6.38 | 1.307 | 4.32 | 8336.72 | 1.728 | 97.8 | 76.8 | 1411 | 24.08 | 5418.9 | 2777.6 | 2665.5 | 3968.7 | 1202.5 | 0.68298 | 5.627
2024-12-09 | 19:40 | Data | 0 | 33.183 | 31.765 | 173.105 | 7.63 | 163.172 | 2170.1 | 25.91 | 48.165 | 6.38 | 1.311 | 4.308 | 8341.25 | 1.593 | 97.8 | 76.7 | 1411 | 24.04 | 5421.8 | 2752.6 | 2669.3 | 3960.6 | 1202.5 | 0.6789 | 5.619
2024-12-09 | 19:40 | Data | 0 | 33.311 | 31.684 | 173.195 | 7.63 | 163.217 | 2161.97 | 25.92 | 48.075 | 6.39 | 1.302 | 4.29 | 8332.2 | 1.83 | 97.8 | 76.7 | 1405 | 24.08 | 5415.9 | 2745.7 | 2684.1 | 3968 | 1202.5 | 0.6759 | 5.593
2024-12-09 | 19:40 | Data | 0 | 33.412 | 31.691 | 173.15 | 7.63 | 163.262 | 2169.2 | 25.93 | 48.165 | 6.39 | 1.295 | 4.315 | 8332.2 | 1.722 | 97.8 | 76.9 | 1411 | 24.08 | 5415.9 | 2754.6 | 2665.9 | 3960.9 | 1202.5 | 0.67791 | 5.61
2024-12-09 | 19:40 | Data | 0 | 33.628 | 31.846 | 173.24 | 7.63 | 163.262 | 2165.58 | 25.9 | 48.165 | 6.4 | 1.305 | 4.317 | 8332.2 | 1.796 | 97.8 | 76.8 | 1408 | 24.13 | 5415.9 | 1835.5 | 2339.3 | 2991.8 | 1202.5 | 0.62284 | 5.622
2024-12-09 | 19:40 | Data | 0 | 33.412 | 31.691 | 173.195 | 7.63 | 163.262 | 2166.49 | 25.92 | 48.075 | 6.38 | 1.301 | 4.297 | 8332.2 | 1.776 | 97.8 | 76.7 | 1408 | 24.08 | 5415.9 | 1682.4 | 2067 | 2677.8 | 1202.5 | 0.62635 | 5.6
2024-12-09 | 19:40 | Data | 0 | 33.419 | 31.907 | 173.24 | 7.63 | 163.217 | 2167.39 | 25.93 | 48.075 | 6.38 | 1.296 | 4.332 | 8332.2 | 1.742 | 97.8 | 77 | 1408 | 24.04 | 5415.9 | 1662.8 | 2095.5 | 2688.7 | 1202.6 | 0.619 | 5.628
2024-12-09 | 19:41 | Data | 0 | 33.405 | 31.684 | 173.195 | 7.62 | 163.307 | 2171.91 | 25.93 | 48.165 | 6.38 | 1.301 | 4.329 | 8350.29 | 1.728 | 97.8 | 76.9 | 1412 | 24.13 | 5427.7 | 1668.5 | 2084.6 | 2681.6 | 1202.6 | 0.62009 | 5.631
2024-12-09 | 19:41 | Data | 0 | 33.412 | 31.569 | 173.195 | 7.62 | 163.172 | 2170.1 | 25.92 | 48.165 | 6.39 | 1.301 | 4.31 | 8332.2 | 1.803 | 97.8 | 76.8 | 1411 | 24.08 | 5415.9 | 1673.1 | 2067.5 | 2674.6 | 1202.6 | 0.61855 | 5.61
2024-12-09 | 19:41 | Data | 0 | 33.189 | 31.569 | 173.195 | 7.63 | 163.172 | 2170.1 | 25.92 | 48.165 | 6.38 | 1.309 | 4.312 | 8336.72 | 1.735 | 97.8 | 76.7 | 1410 | 24.08 | 5418.9 | 1662.3 | 2082.5 | 2676.8 | 1202.6 | 0.61914 | 5.62
2024-12-09 | 19:41 | Data | 0 | 33.419 | 31.576 | 173.331 | 7.63 | 163.307 | 2170.1 | 25.91 | 48.075 | 6.38 | 1.299 | 4.317 | 8332.2 | 1.668 | 97.8 | 76.9 | 1411 | 24.08 | 5415.9 | 1676.7 | 2075.1 | 2679.9 | 1202.6 | 0.62317 | 5.616
2024-12-09 | 19:41 | Data | 0 | 33.196 | 31.4 | 173.15 | 7.62 | 163.217 | 2170.1 | 25.91 | 48.165 | 6.39 | 1.303 | 4.297 | 8350.29 | 1.83 | 97.8 | 76.7 | 1411 | 24.13 | 5427.7 | 1681.2 | 2064.9 | 2674.8 | 1202.6 | 0.62619 | 5.601
2024-12-09 | 19:41 | Data | 0 | 33.412 | 31.684 | 173.15 | 7.62 | 163.262 | 2170.1 | 25.91 | 48.165 | 6.39 | 1.308 | 4.3 | 8345.77 | 1.843 | 97.8 | 76.7 | 1411 | 24.13 | 5424.8 | 1681.4 | 2086.7 | 2693.6 | 1202.6 | 0.62196 | 5.606
2024-12-09 | 19:41 | Data | 0 | 33.608 | 32.008 | 173.331 | 7.62 | 163.307 | 2164.68 | 25.89 | 48.165 | 6.38 | 1.301 | 4.319 | 8345.77 | 1.681 | 97.8 | 76.9 | 1407 | 24.04 | 5424.8 | 1670.7 | 2092.1 | 2691.9 | 1202.6 | 0.61842 | 5.619
2024-12-09 | 19:41 | Data | 0 | 33.628 | 31.569 | 173.195 | 7.63 | 163.172 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.297 | 4.334 | 8336.72 | 1.668 | 97.8 | 77 | 1411 | 24.04 | 5418.9 | 1678.3 | 2088.5 | 2692.4 | 1202.6 | 0.62098 | 5.631
2024-12-09 | 19:41 | Data | 0 | 33.237 | 31.846 | 173.105 | 7.63 | 163.172 | 2169.2 | 25.89 | 48.165 | 6.38 | 1.301 | 4.332 | 8137.75 | 1.674 | 97.8 | 76.9 | 1411 | 24.08 | 5289.5 | 1664 | 2079.7 | 2677.7 | 1202.6 | 0.61888 | 5.634
2024-12-09 | 19:41 | Data | 0 | 33.581 | 31.994 | 173.376 | 7.63 | 163.262 | 2171.91 | 25.89 | 47.984 | 6.39 | 1.299 | 4.322 | 8155.84 | 1.722 | 97.8 | 76.9 | 1412 | 24.08 | 5301.3 | 1677.7 | 2093.4 | 2694.4 | 1202.6 | 0.62048 | 5.621
2024-12-09 | 19:41 | Data | 0 | 33.534 | 31.562 | 173.195 | 7.63 | 163.262 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.303 | 4.331 | 8296.02 | 1.674 | 97.8 | 76.9 | 1407 | 24.08 | 5392.4 | 1649.7 | 2086.9 | 2672.3 | 1202.6 | 0.61477 | 5.634
2024-12-09 | 19:41 | Data | 0 | 33.689 | 31.603 | 173.421 | 7.63 | 163.352 | 2167.39 | 25.89 | 48.165 | 6.38 | 1.304 | 4.321 | 8368.38 | 1.728 | 97.8 | 76.8 | 1408 | 24.13 | 5439.4 | 1681.2 | 2079.6 | 2686.6 | 1202.6 | 0.62049 | 5.625
2024-12-09 | 19:41 | Data | 0 | 33.372 | 31.623 | 173.376 | 7.63 | 163.262 | 2167.39 | 25.89 | 48.075 | 6.38 | 1.304 | 4.299 | 8363.86 | 1.627 | 97.8 | 76.7 | 1408 | 24.08 | 5436.5 | 1647.6 | 2089.3 | 2673.3 | 1202.6 | 0.61592 | 5.604
2024-12-09 | 19:41 | Data | 0 | 33.25 | 31.724 | 173.195 | 7.63 | 163.217 | 2163.77 | 25.9 | 47.894 | 6.38 | 1.301 | 4.304 | 8359.34 | 1.587 | 97.8 | 76.8 | 1406 | 23.95 | 5433.6 | 1677.1 | 2084.7 | 2686 | 1202.6 | 0.62189 | 5.604
2024-12-09 | 19:41 | Data | 0 | 32.967 | 31.555 | 173.06 | 7.63 | 163.126 | 2170.1 | 25.89 | 47.804 | 6.39 | 1.292 | 4.325 | 8372.9 | 1.728 | 97.8 | 77 | 1411 | 23.9 | 5442.4 | 1650.3 | 2106.1 | 2692.7 | 1202.6 | 0.61058 | 5.617
2024-12-09 | 19:41 | Data | 0 | 33.426 | 31.36 | 173.105 | 7.63 | 163.172 | 2170.1 | 25.89 | 47.894 | 6.39 | 1.301 | 4.295 | 8386.47 | 1.83 | 97.8 | 76.8 | 1411 | 23.95 | 5451.2 | 1679.9 | 2099.7 | 2700.6 | 1202.6 | 0.61998 | 5.595
2024-12-09 | 19:42 | Data | 0 | 33.297 | 31.684 | 173.15 | 7.63 | 163.172 | 2172.81 | 25.89 | 50.693 | 6.38 | 1.305 | 4.31 | 8386.47 | 1.789 | 97.7 | 76.8 | 1412 | 25.35 | 5451.2 | 1679.2 | 2106.1 | 2707.2 | 1202.6 | 0.61833 | 5.614
2024-12-09 | 19:42 | Data | 0 | 33.426 | 31.569 | 173.331 | 7.62 | 163.262 | 2172.81 | 25.89 | 48.165 | 6.39 | 1.302 | 4.314 | 8386.47 | 1.627 | 97.8 | 76.8 | 1412 | 24.08 | 5451.2 | 1666.5 | 2094.7 | 2689.2 | 1202.6 | 0.61736 | 5.618
2024-12-09 | 19:42 | Data | 0 | 33.345 | 31.616 | 173.105 | 7.62 | 163.217 | 2172.81 | 25.89 | 48.165 | 6.38 | 1.294 | 4.33 | 8386.47 | 1.735 | 97.8 | 77 | 1412 | 24.13 | 5451.2 | 1662.6 | 2084.9 | 2678.3 | 1202.6 | 0.61867 | 5.624
2024-12-09 | 19:42 | Data | 0 | 33.297 | 31.569 | 173.195 | 7.63 | 163.262 | 2171.91 | 25.89 | 48.165 | 6.39 | 1.292 | 4.315 | 8386.47 | 1.816 | 97.8 | 77 | 1412 | 24.08 | 5451.2 | 1673.2 | 2089.1 | 2689.4 | 1202.6 | 0.61943 | 5.609
2024-12-09 | 19:42 | Data | 0 | 33.385 | 31.569 | 173.06 | 7.63 | 163.172 | 2171.91 | 25.9 | 48.165 | 6.39 | 1.305 | 4.309 | 8381.95 | 1.836 | 97.8 | 76.7 | 1412 | 24.08 | 5448.3 | 1674.3 | 2076 | 2679.3 | 1202.6 | 0.62259 | 5.613
2024-12-09 | 19:42 | Data | 0 | 33.405 | 31.569 | 173.195 | 7.63 | 163.217 | 2169.2 | 25.89 | 48.165 | 6.39 | 1.306 | 4.3 | 8381.95 | 1.843 | 97.8 | 76.7 | 1411 | 24.08 | 5448.3 | 1686.6 | 2073.8 | 2684.7 | 1202.6 | 0.62213 | 5.606
2024-12-09 | 19:42 | Data | 0 | 33.189 | 31.447 | 173.014 | 7.63 | 163.172 | 2170.1 | 25.89 | 48.165 | 6.39 | 1.301 | 4.296 | 8386.47 | 1.627 | 97.8 | 76.8 | 1411 | 24.08 | 5451.2 | 1695.7 | 2101.3 | 2705.7 | 1202.6 | 0.62551 | 5.597
2024-12-09 | 19:42 | Data | 0 | 33.243 | 31.569 | 173.105 | 7.63 | 163.217 | 2167.39 | 25.89 | 48.165 | 6.38 | 1.294 | 4.316 | 8390.99 | 1.62 | 97.8 | 76.9 | 1408 | 24.08 | 5454.1 | 1706.6 | 2087.1 | 2697.1 | 1202.6 | 0.62138 | 5.61
2024-12-09 | 19:42 | Data | 0 | 33.412 | 31.373 | 173.15 | 7.63 | 163.262 | 2164.68 | 25.9 | 48.165 | 6.38 | 1.301 | 4.31 | 8390.99 | 1.789 | 97.8 | 76.8 | 1407 | 24.08 | 5454.1 | 1674.4 | 2090.9 | 2693.2 | 1202.6 | 0.61839 | 5.611
2024-12-09 | 19:42 | Data | 0 | 33.466 | 31.583 | 173.331 | 7.62 | 163.262 | 2162.87 | 25.89 | 48.165 | 6.38 | 1.296 | 4.314 | 8400.04 | 1.62 | 97.8 | 76.9 | 1406 | 24.08 | 5460 | 1667.3 | 2086.7 | 2683.3 | 1202.6 | 0.61872 | 5.61
2024-12-09 | 19:42 | Data | 0 | 33.156 | 31.616 | 173.06 | 7.63 | 163.126 | 2163.77 | 25.89 | 48.075 | 6.38 | 1.297 | 4.316 | 8390.99 | 1.715 | 97.8 | 76.9 | 1407 | 24.04 | 5454.1 | 1674.6 | 2081.3 | 2683.2 | 1202.6 | 0.62258 | 5.612
2024-12-09 | 19:42 | Data | 0 | 33.183 | 31.569 | 173.06 | 7.63 | 163.126 | 2166.49 | 25.89 | 47.894 | 6.39 | 1.296 | 4.315 | 8350.29 | 1.782 | 97.8 | 76.9 | 1408 | 23.95 | 5427.7 | 1681.5 | 2093.4 | 2697.2 | 1202.6 | 0.62075 | 5.61
2024-12-09 | 19:42 | Data | 0 | 33.621 | 31.623 | 173.15 | 7.63 | 163.217 | 2167.39 | 25.9 | 47.804 | 6.38 | 1.307 | 4.278 | 8350.29 | 1.816 | 97.8 | 76.6 | 1408 | 23.95 | 5427.7 | 1678.5 | 2108.7 | 2709.1 | 1202.6 | 0.61682 | 5.585
2024-12-09 | 19:42 | Data | 0 | 33.183 | 31.515 | 172.969 | 7.62 | 163.081 | 2166.49 | 25.89 | 47.894 | 6.39 | 1.3 | 4.308 | 8359.34 | 1.668 | 97.8 | 76.8 | 1408 | 23.95 | 5433.6 | 1679.9 | 2127.9 | 2715.3 | 1202.6 | 0.61878 | 5.608
2024-12-09 | 19:42 | Data | 0 | 33.412 | 31.366 | 173.014 | 7.63 | 163.172 | 2161.06 | 25.9 | 47.894 | 6.38 | 1.295 | 4.285 | 8368.38 | 1.728 | 97.8 | 76.8 | 1405 | 23.95 | 5439.4 | 1671.9 | 2127.2 | 2718.7 | 1202.6 | 0.61221 | 5.579
2024-12-09 | 19:42 | Data | 0 | 33.581 | 31.846 | 173.195 | 7.63 | 163.262 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.292 | 4.304 | 8359.34 | 1.627 | 97.8 | 76.9 | 1411 | 23.95 | 5433.6 | 1668.1 | 2104.1 | 2697.5 | 1202.6 | 0.61601 | 5.597
2024-12-09 | 19:42 | Data | 0 | 33.183 | 31.542 | 173.15 | 7.63 | 163.081 | 2169.2 | 25.89 | 47.894 | 6.38 | 1.306 | 4.288 | 8359.34 | 1.816 | 97.8 | 76.7 | 1408 | 23.99 | 5433.6 | 1686.4 | 2097.2 | 2703.4 | 1202.6 | 0.62104 | 5.594
2024-12-09 | 19:42 | Data | 0 | 33.365 | 31.623 | 173.24 | 7.63 | 163.262 | 2170.1 | 25.9 | 47.804 | 6.38 | 1.31 | 4.304 | 8350.29 | 1.803 | 97.8 | 76.7 | 1411 | 23.95 | 5427.7 | 1663.9 | 2100.6 | 2693.2 | 1202.6 | 0.61501 | 5.614
2024-12-09 | 19:43 | Data | 0 | 33.412 | 31.569 | 173.331 | 7.63 | 163.217 | 2170.1 | 25.89 | 47.984 | 6.38 | 1.307 | 4.329 | 8359.34 | 1.836 | 97.8 | 76.8 | 1411 | 23.95 | 5433.6 | 1680.4 | 2100.1 | 2702.7 | 1202.6 | 0.61965 | 5.637
2024-12-09 | 19:43 | Data | 0 | 33.291 | 31.569 | 173.15 | 7.63 | 163.126 | 2163.77 | 25.89 | 47.894 | 6.39 | 1.301 | 4.297 | 8350.29 | 1.681 | 97.8 | 76.8 | 1406 | 23.95 | 5427.7 | 1678.5 | 2104.5 | 2704.5 | 1202.6 | 0.61895 | 5.598
2024-12-09 | 19:43 | Data | 0 | 33.466 | 31.353 | 173.24 | 7.63 | 163.262 | 2163.77 | 25.89 | 47.894 | 6.39 | 1.301 | 4.321 | 8359.34 | 1.641 | 97.8 | 76.9 | 1406 | 23.95 | 5433.6 | 1664.2 | 2106.2 | 2697.5 | 1202.6 | 0.6204 | 5.62
2024-12-09 | 19:43 | Data | 0 | 33.52 | 31.576 | 173.06 | 7.62 | 163.307 | 2163.77 | 25.9 | 47.894 | 6.38 | 1.304 | 4.322 | 8345.77 | 1.87 | 97.8 | 76.8 | 1406 | 23.95 | 5424.8 | 1658.8 | 2119.6 | 2705.8 | 1202.6 | 0.6108 | 5.626
2024-12-09 | 19:43 | Data | 0 | 33.21 | 31.366 | 173.06 | 7.63 | 163.217 | 2163.77 | 25.89 | 47.894 | 6.38 | 1.303 | 4.296 | 8345.77 | 1.789 | 97.8 | 76.7 | 1406 | 23.99 | 5424.8 | 1682.2 | 2126.7 | 2722.8 | 1202.6 | 0.61594 | 5.6
2024-12-09 | 19:43 | Data | 0 | 33.358 | 31.576 | 173.24 | 7.62 | 163.172 | 2163.77 | 25.89 | 47.894 | 6.38 | 1.304 | 4.301 | 8336.72 | 1.924 | 97.8 | 76.7 | 1406 | 23.95 | 5418.9 | 1683 | 2132.5 | 2729.3 | 1202.6 | 0.61354 | 5.604
2024-12-09 | 19:43 | Data | 0 | 33.196 | 31.339 | 173.15 | 7.63 | 163.081 | 2163.77 | 25.89 | 47.894 | 6.38 | 1.305 | 4.322 | 8332.2 | 1.836 | 97.8 | 76.8 | 1406 | 23.95 | 5415.9 | 1688.7 | 2110 | 2718 | 1202.6 | 0.62173 | 5.628
2024-12-09 | 19:43 | Data | 0 | 33.075 | 31.339 | 172.969 | 7.63 | 163.126 | 2161.97 | 25.89 | 47.804 | 6.38 | 1.302 | 4.331 | 8332.2 | 1.803 | 97.8 | 76.9 | 1405 | 23.95 | 5415.9 | 1672.7 | 2130.8 | 2702.7 | 1202.6 | 0.61061 | 5.633
2024-12-09 | 19:43 | Data | 0 | 33.27 | 31.447 | 173.15 | 7.63 | 163.217 | 2160.16 | 25.89 | 47.894 | 6.38 | 1.305 | 4.297 | 8332.2 | 1.83 | 97.8 | 76.7 | 1404 | 23.95 | 5415.9 | 1679.4 | 2113.5 | 2711.1 | 1202.6 | 0.61738 | 5.603
2024-12-09 | 19:43 | Data | 0 | 33.297 | 31.677 | 173.195 | 7.62 | 163.081 | 2161.06 | 25.89 | 47.894 | 6.39 | 1.305 | 4.312 | 8350.29 | 1.83 | 97.8 | 76.8 | 1405 | 23.95 | 5427.7 | 1668.1 | 2110.1 | 2703.6 | 1202.6 | 0.61455 | 5.618
2024-12-09 | 19:43 | Data | 0 | 33.439 | 31.468 | 173.195 | 7.63 | 163.217 | 2159.26 | 25.89 | 47.984 | 6.39 | 1.296 | 4.288 | 8350.29 | 1.789 | 97.8 | 76.8 | 1404 | 23.99 | 5427.7 | 1670.6 | 2093.3 | 2691.1 | 1202.6 | 0.61741 | 5.584
2024-12-09 | 19:43 | Data | 0 | 33.183 | 31.353 | 172.969 | 7.63 | 163.036 | 2163.77 | 25.89 | 47.894 | 6.38 | 1.301 | 4.309 | 8359.34 | 1.816 | 97.8 | 76.8 | 1406 | 23.99 | 5433.6 | 1658 | 2100.7 | 2690.6 | 1202.6 | 0.61341 | 5.61
2024-12-09 | 19:43 | Data | 0 | 33.156 | 31.454 | 173.195 | 7.62 | 163.172 | 2163.77 | 25.89 | 47.984 | 6.38 | 1.308 | 4.324 | 8345.77 | 1.951 | 97.8 | 76.8 | 1406 | 23.95 | 5424.8 | 1678.3 | 2096.1 | 2698.8 | 1202.6 | 0.61958 | 5.631
2024-12-09 | 19:43 | Data | 0 | 32.96 | 31.42 | 173.014 | 7.63 | 162.991 | 2163.77 | 25.89 | 47.894 | 6.38 | 1.31 | 4.309 | 8368.38 | 1.512 | 97.8 | 76.7 | 1406 | 23.95 | 5439.4 | 1677.8 | 2100.5 | 2700.8 | 1202.6 | 0.61868 | 5.619
2024-12-09 | 19:43 | Data | 0 | 33.223 | 31.454 | 173.195 | 7.63 | 163.172 | 2158.35 | 25.89 | 48.075 | 6.38 | 1.313 | 4.291 | 8377.43 | 1.627 | 97.8 | 76.6 | 1403 | 24.08 | 5445.3 | 1680.5 | 2097.8 | 2684.6 | 1202.6 | 0.62191 | 5.605
2024-12-09 | 19:43 | Data | 0 | 33.567 | 31.886 | 173.105 | 7.63 | 163.172 | 2161.97 | 25.9 | 48.165 | 6.38 | 1.304 | 4.326 | 8386.47 | 1.917 | 97.8 | 76.8 | 1405 | 24.08 | 5451.2 | 1698.7 | 2076.7 | 2694.9 | 1202.6 | 0.62809 | 5.63
2024-12-09 | 19:43 | Data | 0 | 33.412 | 31.36 | 173.06 | 7.63 | 163.126 | 2161.97 | 25.89 | 48.165 | 6.38 | 1.297 | 4.299 | 8372.9 | 1.796 | 97.8 | 76.8 | 1405 | 24.08 | 5442.4 | 1786.9 | 2495.8 | 3101.3 | 1202.6 | 0.59333 | 5.596
2024-12-09 | 19:44 | Data | 0 | 33.189 | 31.339 | 173.06 | 7.63 | 163.081 | 2161.06 | 25.89 | 48.255 | 6.38 | 1.283 | 4.284 | 8372.9 | 1.661 | 97.8 | 76.9 | 1405 | 24.08 | 5442.4 | 2773.1 | 2678.4 | 3984.9 | 1202.6 | 0.67898 | 5.566
2024-12-09 | 19:44 | Data | 0 | 33.156 | 31.454 | 173.06 | 7.63 | 163.081 | 2161.06 | 25.89 | 48.165 | 6.39 | 1.293 | 4.316 | 8377.43 | 1.843 | 97.8 | 77 | 1405 | 24.08 | 5445.3 | 2747.8 | 2685.4 | 3972.6 | 1202.6 | 0.67413 | 5.609
2024-12-09 | 19:44 | Data | 0 | 33.284 | 31.832 | 173.06 | 7.63 | 163.081 | 2161.06 | 25.91 | 48.075 | 6.38 | 1.301 | 4.306 | 8368.38 | 1.728 | 97.8 | 76.8 | 1405 | 24.08 | 5439.4 | 2739.1 | 2673.3 | 3955.2 | 1202.6 | 0.6749 | 5.608
2024-12-09 | 19:44 | Data | 0 | 33.183 | 31.569 | 173.105 | 7.63 | 163.172 | 2161.06 | 25.89 | 48.165 | 6.38 | 1.308 | 4.306 | 8359.34 | 1.728 | 97.8 | 76.7 | 1405 | 24.08 | 5433.6 | 2768.4 | 2683.9 | 3978.2 | 1202.6 | 0.67969 | 5.613
2024-12-09 | 19:44 | Data | 0 | 33.183 | 31.555 | 172.969 | 7.63 | 163.036 | 2161.06 | 25.89 | 48.075 | 6.39 | 1.296 | 4.304 | 8332.2 | 1.627 | 97.8 | 76.9 | 1405 | 24.04 | 5415.9 | 2771.2 | 2678.3 | 3973.8 | 1202.6 | 0.68367 | 5.6
2024-12-09 | 19:44 | Data | 0 | 33.176 | 31.346 | 173.06 | 7.62 | 163.126 | 2161.97 | 25.89 | 48.255 | 6.39 | 1.305 | 4.287 | 8350.29 | 1.83 | 97.8 | 76.7 | 1405 | 24.08 | 5427.7 | 2736.3 | 2674.9 | 3950.1 | 1202.6 | 0.67751 | 5.591
2024-12-09 | 19:44 | Data | 0 | 33.567 | 31.65 | 173.15 | 7.62 | 163.262 | 2161.06 | 25.89 | 48.165 | 6.38 | 1.301 | 4.289 | 8757.29 | 1.627 | 97.8 | 76.7 | 1405 | 24.08 | 5692.2 | 2732.5 | 2663.4 | 3948.1 | 1202.7 | 0.67555 | 5.59
2024-12-09 | 19:44 | Data | 0 | 33.129 | 31.724 | 173.105 | 7.63 | 163.081 | 2161.06 | 25.89 | 48.165 | 6.38 | 1.31 | 4.321 | 8345.77 | 1.769 | 97.8 | 76.7 | 1405 | 24.04 | 5424.8 | 2768.2 | 2674.4 | 3971 | 1202.7 | 0.68012 | 5.631
2024-12-09 | 19:44 | Data | 0 | 33.183 | 31.515 | 173.014 | 7.62 | 162.991 | 2161.06 | 25.9 | 48.165 | 6.38 | 1.305 | 4.313 | 8336.72 | 1.843 | 97.8 | 76.8 | 1405 | 24.13 | 5418.9 | 2737.4 | 2669 | 3946 | 1202.7 | 0.67878 | 5.618
2024-12-09 | 19:44 | Data | 0 | 33.453 | 31.488 | 173.105 | 7.62 | 163.217 | 2161.06 | 25.9 | 48.075 | 6.39 | 1.304 | 4.285 | 8336.72 | 1.836 | 97.8 | 76.7 | 1405 | 24.04 | 5418.9 | 2758.2 | 2675.3 | 3964 | 1202.7 | 0.67796 | 5.591
2024-12-09 | 19:44 | Data | 0 | 33.054 | 31.346 | 172.969 | 7.63 | 163.172 | 2161.06 | 25.89 | 48.165 | 6.39 | 1.299 | 4.292 | 8336.72 | 1.533 | 97.8 | 76.8 | 1405 | 24.08 | 5418.9 | 2767.3 | 2678.8 | 3974.5 | 1202.7 | 0.67983 | 5.591
2024-12-09 | 19:44 | Data | 0 | 33.385 | 31.42 | 172.969 | 7.63 | 163.081 | 2161.06 | 25.89 | 48.165 | 6.38 | 1.303 | 4.276 | 8332.2 | 1.904 | 97.8 | 76.6 | 1405 | 24.13 | 5415.9 | 2749.8 | 2694.2 | 3979.8 | 1202.7 | 0.67295 | 5.58
2024-12-09 | 19:44 | Data | 0 | 33.189 | 31.339 | 173.06 | 7.63 | 163.081 | 2161.97 | 25.89 | 48.165 | 6.38 | 1.3 | 4.302 | 8359.34 | 1.843 | 97.8 | 76.8 | 1405 | 24.08 | 5433.6 | 2758.4 | 2670.7 | 3963.1 | 1202.7 | 0.67948 | 5.6
2024-12-09 | 19:44 | Data | 0 | 33.27 | 31.562 | 173.014 | 7.63 | 163.126 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.301 | 4.305 | 8341.25 | 1.836 | 97.8 | 76.8 | 1406 | 24.08 | 5421.8 | 2756.6 | 2694.8 | 3978.9 | 1202.7 | 0.6772 | 5.605
2024-12-09 | 19:44 | Data | 0 | 32.96 | 31.555 | 173.06 | 7.63 | 163.126 | 2162.87 | 25.89 | 48.075 | 6.39 | 1.301 | 4.282 | 8363.86 | 1.614 | 97.8 | 76.7 | 1406 | 24.04 | 5436.5 | 2751.6 | 2682.2 | 3965.2 | 1202.7 | 0.67763 | 5.585
2024-12-09 | 19:44 | Data | 0 | 33.297 | 31.339 | 173.15 | 7.63 | 163.172 | 2163.77 | 25.9 | 48.075 | 6.39 | 1.296 | 4.296 | 8350.29 | 1.728 | 97.8 | 76.8 | 1406 | 24.04 | 5427.7 | 2741.8 | 2693.6 | 3982.4 | 1202.7 | 0.67353 | 5.592
2024-12-09 | 19:44 | Data | 0 | 33.169 | 31.468 | 172.969 | 7.62 | 163.081 | 2163.77 | 25.9 | 48.075 | 6.39 | 1.31 | 4.336 | 8350.29 | 1.89 | 97.8 | 76.8 | 1406 | 24.04 | 5427.7 | 2734.2 | 2686.6 | 3962.5 | 1202.7 | 0.67292 | 5.645
2024-12-09 | 19:44 | Data | 0 | 33.189 | 31.569 | 173.06 | 7.62 | 163.172 | 2166.49 | 25.89 | 48.165 | 6.38 | 1.291 | 4.313 | 8350.29 | 1.62 | 97.8 | 77 | 1408 | 24.08 | 5427.7 | 2734 | 2677.4 | 3956.4 | 1202.7 | 0.67706 | 5.603
2024-12-09 | 19:45 | Data | 0 | 33.189 | 31.792 | 173.195 | 7.63 | 163.217 | 2171.01 | 25.89 | 48.165 | 6.38 | 1.295 | 4.297 | 8345.77 | 1.614 | 97.8 | 76.9 | 1411 | 24.13 | 5424.8 | 2763.4 | 2687.6 | 3979.6 | 1202.7 | 0.67705 | 5.591
2024-12-09 | 19:45 | Data | 0 | 33.547 | 31.799 | 173.15 | 7.62 | 163.262 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.308 | 4.308 | 8350.29 | 1.661 | 97.8 | 76.7 | 1411 | 24.04 | 5427.7 | 2757.5 | 2678.5 | 3965 | 1202.7 | 0.67924 | 5.616
2024-12-09 | 19:45 | Data | 0 | 33.567 | 31.697 | 173.15 | 7.63 | 163.217 | 2170.1 | 25.89 | 48.165 | 6.39 | 1.304 | 4.304 | 8323.16 | 1.843 | 97.8 | 76.7 | 1411 | 24.08 | 5410.1 | 2770.1 | 2680.2 | 3979.5 | 1202.7 | 0.67876 | 5.609
2024-12-09 | 19:45 | Data | 0 | 33.183 | 31.387 | 173.105 | 7.63 | 163.172 | 2170.1 | 25.89 | 48.075 | 6.39 | 1.301 | 4.332 | 8341.25 | 1.742 | 97.8 | 76.9 | 1411 | 24.08 | 5421.8 | 2745.4 | 2670.6 | 3956.4 | 1202.7 | 0.67731 | 5.634
2024-12-09 | 19:45 | Data | 0 | 33.27 | 31.393 | 173.06 | 7.63 | 163.172 | 2174.62 | 25.9 | 48.165 | 6.38 | 1.296 | 4.314 | 8318.64 | 1.668 | 97.8 | 76.9 | 1414 | 24.08 | 5407.1 | 2758.7 | 2679 | 3975.5 | 1202.7 | 0.67986 | 5.61
2024-12-09 | 19:45 | Data | 0 | 33.297 | 31.569 | 173.105 | 7.62 | 163.172 | 2170.1 | 25.9 | 48.075 | 6.38 | 1.302 | 4.284 | 8314.11 | 1.803 | 97.8 | 76.7 | 1411 | 24.08 | 5404.2 | 2770.3 | 2666.1 | 3964.3 | 1202.7 | 0.68153 | 5.587
2024-12-09 | 19:45 | Data | 0 | 33.027 | 31.339 | 173.06 | 7.63 | 163.126 | 2170.1 | 25.89 | 48.075 | 6.38 | 1.305 | 4.331 | 8336.72 | 1.789 | 97.8 | 76.8 | 1411 | 24.04 | 5418.9 | 2746.6 | 2687.7 | 3965.6 | 1202.7 | 0.67658 | 5.636
2024-12-09 | 19:45 | Data | 0 | 33.5 | 31.623 | 173.06 | 7.62 | 163.172 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.299 | 4.332 | 8332.2 | 1.809 | 97.8 | 76.9 | 1411 | 24.08 | 5415.9 | 2745.6 | 2659.6 | 3947.8 | 1202.7 | 0.67875 | 5.63
2024-12-09 | 19:45 | Data | 0 | 33.189 | 31.569 | 173.15 | 7.63 | 163.081 | 2169.2 | 25.89 | 48.165 | 6.38 | 1.296 | 4.31 | 8332.2 | 1.614 | 97.8 | 76.9 | 1411 | 24.08 | 5415.9 | 2767.8 | 2673.6 | 3976.1 | 1202.7 | 0.67959 | 5.606
2024-12-09 | 19:45 | Data | 0 | 33.129 | 31.738 | 173.15 | 7.62 | 163.217 | 2169.2 | 25.89 | 48.165 | 6.38 | 1.306 | 4.291 | 8332.2 | 1.789 | 97.8 | 76.7 | 1410 | 24.08 | 5415.9 | 2728.4 | 2682.9 | 3952.6 | 1202.7 | 0.67408 | 5.598
2024-12-09 | 19:45 | Data | 0 | 33.129 | 31.664 | 173.06 | 7.63 | 163.126 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.305 | 4.27 | 8363.86 | 1.83 | 97.8 | 76.6 | 1411 | 24.08 | 5436.5 | 2760.4 | 2686.3 | 3966.6 | 1202.7 | 0.67826 | 5.575
2024-12-09 | 19:45 | Data | 0 | 33.399 | 31.569 | 173.06 | 7.63 | 163.126 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.302 | 4.306 | 8372.9 | 1.641 | 97.8 | 76.8 | 1411 | 24.04 | 5442.4 | 2762.3 | 2681.1 | 3973.3 | 1202.7 | 0.67926 | 5.609
2024-12-09 | 19:45 | Data | 0 | 33.189 | 31.569 | 173.105 | 7.62 | 163.172 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.297 | 4.31 | 8381.95 | 1.614 | 97.8 | 76.9 | 1411 | 23.95 | 5448.3 | 2759.3 | 2685.5 | 3977 | 1202.7 | 0.67583 | 5.607
2024-12-09 | 19:45 | Data | 0 | 33.385 | 31.765 | 173.06 | 7.63 | 163.126 | 2163.77 | 25.9 | 48.165 | 6.38 | 1.294 | 4.317 | 8386.47 | 1.789 | 97.8 | 76.9 | 1407 | 24.08 | 5451.2 | 2743.1 | 2689.8 | 3971.4 | 1202.7 | 0.67358 | 5.61
2024-12-09 | 19:45 | Data | 0 | 33.405 | 31.576 | 173.105 | 7.63 | 163.172 | 2162.87 | 25.89 | 48.165 | 6.38 | 1.307 | 4.307 | 8363.86 | 1.715 | 97.8 | 76.7 | 1406 | 24.08 | 5436.5 | 2762.5 | 2697.6 | 3973.4 | 1202.7 | 0.67326 | 5.612
2024-12-09 | 19:45 | Data | 0 | 33.27 | 31.778 | 173.15 | 7.63 | 163.172 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.308 | 4.322 | 8359.34 | 1.627 | 97.8 | 76.8 | 1406 | 24.08 | 5433.6 | 2771.6 | 2700.1 | 3989.4 | 1202.7 | 0.67859 | 5.629
2024-12-09 | 19:45 | Data | 0 | 33.183 | 31.589 | 173.06 | 7.63 | 163.172 | 2163.77 | 25.89 | 47.894 | 6.38 | 1.307 | 4.314 | 8359.34 | 1.776 | 97.8 | 76.7 | 1406 | 23.95 | 5433.6 | 2738.2 | 2665.3 | 3954.4 | 1202.7 | 0.67444 | 5.623
2024-12-09 | 19:45 | Data | 0 | 33.176 | 31.339 | 173.06 | 7.63 | 163.081 | 2166.49 | 25.9 | 48.165 | 6.38 | 1.3 | 4.302 | 8359.34 | 1.843 | 97.8 | 76.8 | 1408 | 24.08 | 5433.6 | 2760.7 | 2679.4 | 3973.5 | 1202.7 | 0.67943 | 5.601
2024-12-09 | 19:46 | Data | 0 | 33.196 | 31.657 | 173.105 | 7.63 | 163.172 | 2166.49 | 25.89 | 48.165 | 6.38 | 1.301 | 4.307 | 8377.43 | 1.674 | 97.8 | 76.8 | 1408 | 24.08 | 5445.3 | 2749.2 | 2685.5 | 3971.6 | 1202.7 | 0.6764 | 5.607
2024-12-09 | 19:46 | Data | 0 | 33.297 | 31.454 | 173.06 | 7.63 | 163.126 | 2166.49 | 25.89 | 48.165 | 6.39 | 1.295 | 4.315 | 8377.43 | 1.701 | 97.8 | 76.9 | 1408 | 24.08 | 5445.3 | 2773.9 | 2682.2 | 3986 | 1202.7 | 0.67849 | 5.61
2024-12-09 | 19:46 | Data | 0 | 33.399 | 31.583 | 173.15 | 7.63 | 163.172 | 2163.77 | 25.89 | 48.075 | 6.38 | 1.3 | 4.329 | 8381.95 | 1.823 | 97.8 | 76.9 | 1406 | 24.04 | 5448.3 | 2805.5 | 2672.2 | 3994.9 | 1202.7 | 0.68256 | 5.628
2024-12-09 | 19:46 | Data | 0 | 33.554 | 31.583 | 173.15 | 7.63 | 163.217 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.295 | 4.323 | 8381.95 | 1.863 | 97.8 | 76.9 | 1406 | 24.08 | 5448.3 | 2779.4 | 2661.4 | 3987.7 | 1202.7 | 0.68064 | 5.619
2024-12-09 | 19:46 | Data | 0 | 33.304 | 32.008 | 173.15 | 7.63 | 163.217 | 2161.06 | 25.89 | 47.714 | 6.38 | 1.301 | 4.309 | 8363.86 | 1.728 | 97.8 | 76.8 | 1405 | 23.86 | 5436.5 | 2771.8 | 2679.4 | 3978.5 | 1202.7 | 0.68132 | 5.61
2024-12-09 | 19:46 | Data | 0 | 32.96 | 31.366 | 173.06 | 7.63 | 163.126 | 2161.06 | 25.89 | 47.894 | 6.38 | 1.302 | 4.308 | 8372.9 | 1.998 | 97.8 | 76.8 | 1405 | 23.95 | 5442.4 | 2765 | 2685.8 | 3987.3 | 1202.7 | 0.67637 | 5.611
2024-12-09 | 19:46 | Data | 0 | 33.297 | 31.339 | 173.06 | 7.63 | 163.172 | 2161.06 | 25.89 | 47.984 | 6.39 | 1.302 | 4.303 | 8386.47 | 1.924 | 97.8 | 76.8 | 1405 | 23.95 | 5451.2 | 2795.9 | 2693.7 | 4008.8 | 1202.7 | 0.67989 | 5.606
2024-12-09 | 19:46 | Data | 0 | 33.183 | 31.515 | 173.105 | 7.63 | 163.081 | 2166.49 | 25.9 | 47.984 | 6.38 | 1.299 | 4.299 | 8386.47 | 1.728 | 97.8 | 76.8 | 1408 | 24.04 | 5451.2 | 2778.1 | 2686.4 | 3992.7 | 1202.7 | 0.68073 | 5.598
2024-12-09 | 19:46 | Data | 0 | 33.405 | 31.745 | 172.969 | 7.63 | 163.217 | 2163.77 | 25.89 | 48.075 | 6.38 | 1.301 | 4.305 | 8368.38 | 1.836 | 97.8 | 76.8 | 1406 | 24.04 | 5439.4 | 2774.8 | 2691.3 | 4000.8 | 1202.8 | 0.67961 | 5.606
2024-12-09 | 19:46 | Data | 0 | 33.27 | 31.765 | 173.15 | 7.62 | 163.172 | 2163.77 | 25.89 | 47.984 | 6.38 | 1.301 | 4.309 | 8377.43 | 1.796 | 97.8 | 76.8 | 1406 | 23.95 | 5445.3 | 2831.2 | 2706.8 | 4045.7 | 1202.8 | 0.68257 | 5.611
2024-12-09 | 19:46 | Data | 0 | 33.189 | 31.569 | 173.06 | 7.63 | 163.172 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.306 | 4.287 | 8372.9 | 1.614 | 97.8 | 76.7 | 1406 | 24.13 | 5442.4 | 2779.1 | 2674.2 | 3981.8 | 1202.8 | 0.68254 | 5.593
2024-12-09 | 19:46 | Data | 0 | 33.615 | 31.704 | 173.15 | 7.62 | 163.217 | 2163.77 | 25.89 | 47.984 | 6.38 | 1.297 | 4.301 | 8368.38 | 1.803 | 97.8 | 76.8 | 1406 | 23.95 | 5439.4 | 2781.3 | 2694.5 | 4001.5 | 1202.8 | 0.67867 | 5.598
2024-12-09 | 19:46 | Data | 0 | 33.385 | 31.616 | 173.15 | 7.63 | 163.262 | 2164.68 | 25.89 | 47.894 | 6.38 | 1.3 | 4.301 | 8350.29 | 1.776 | 97.8 | 76.8 | 1406 | 23.95 | 5427.7 | 2781 | 2698 | 4006.6 | 1202.8 | 0.67741 | 5.6
2024-12-09 | 19:46 | Data | 0 | 33.338 | 31.562 | 173.06 | 7.62 | 163.081 | 2162.87 | 25.89 | 47.894 | 6.38 | 1.292 | 4.318 | 8332.2 | 1.735 | 97.8 | 77 | 1406 | 23.95 | 5415.9 | 2789.1 | 2703.7 | 4009.2 | 1202.8 | 0.67971 | 5.611
2024-12-09 | 19:46 | Data | 0 | 33.183 | 31.718 | 173.24 | 7.63 | 163.217 | 2163.77 | 25.89 | 47.804 | 6.38 | 1.295 | 4.303 | 8345.77 | 1.641 | 97.8 | 76.9 | 1406 | 23.95 | 5424.8 | 2773.5 | 2686.7 | 3988.3 | 1202.8 | 0.67468 | 5.598
2024-12-09 | 19:46 | Data | 0 | 33.183 | 31.596 | 173.014 | 7.62 | 163.081 | 2164.68 | 25.89 | 48.165 | 6.39 | 1.301 | 4.3 | 8350.29 | 1.668 | 97.8 | 76.8 | 1406 | 24.04 | 5427.7 | 2786.6 | 2685.3 | 3998.9 | 1202.8 | 0.67886 | 5.6
2024-12-09 | 19:46 | Data | 0 | 33.203 | 31.745 | 173.105 | 7.63 | 163.217 | 2164.68 | 25.89 | 48.165 | 6.38 | 1.304 | 4.315 | 8345.77 | 1.627 | 97.8 | 76.8 | 1406 | 24.08 | 5424.8 | 2768.3 | 2681.8 | 3987.5 | 1202.8 | 0.67818 | 5.619
2024-12-09 | 19:46 | Data | 0 | 33.493 | 31.373 | 173.014 | 7.63 | 163.172 | 2163.77 | 25.89 | 47.894 | 6.38 | 1.319 | 4.301 | 8336.72 | 1.836 | 97.8 | 76.5 | 1406 | 23.95 | 5418.9 | 2779.8 | 2687.3 | 3998.4 | 1202.8 | 0.67724 | 5.619
2024-12-09 | 19:47 | Data | 0 | 33.351 | 31.36 | 173.195 | 7.63 | 163.217 | 2171.91 | 25.89 | 47.894 | 6.38 | 1.31 | 4.304 | 8350.29 | 1.857 | 97.8 | 76.7 | 1412 | 23.95 | 5427.7 | 2797.3 | 2708.2 | 4017.9 | 1202.8 | 0.67907 | 5.614
2024-12-09 | 19:47 | Data | 0 | 33.412 | 31.407 | 173.15 | 7.63 | 163.217 | 2166.49 | 25.89 | 47.894 | 6.38 | 1.301 | 4.289 | 8345.77 | 1.796 | 97.8 | 76.7 | 1408 | 23.9 | 5424.8 | 2776.6 | 2710.8 | 4010.6 | 1202.8 | 0.67931 | 5.591
2024-12-09 | 19:47 | Data | 0 | 33.21 | 31.785 | 173.105 | 7.63 | 163.217 | 2166.49 | 25.89 | 47.804 | 6.38 | 1.3 | 4.292 | 8345.77 | 1.715 | 97.8 | 76.8 | 1408 | 23.95 | 5424.8 | 2794.7 | 2707.4 | 4014.8 | 1202.8 | 0.67941 | 5.591
2024-12-09 | 19:47 | Data | 0 | 33.176 | 31.555 | 173.06 | 7.63 | 163.172 | 2166.49 | 25.9 | 47.984 | 6.38 | 1.292 | 4.292 | 8359.34 | 1.796 | 97.8 | 76.9 | 1408 | 23.95 | 5433.6 | 2802.5 | 2689.3 | 4007.1 | 1202.8 | 0.68221 | 5.583
2024-12-09 | 19:47 | Data | 0 | 33.237 | 31.461 | 173.105 | 7.62 | 163.172 | 2166.49 | 25.89 | 47.984 | 6.38 | 1.303 | 4.285 | 8359.34 | 1.843 | 97.8 | 76.7 | 1408 | 23.95 | 5433.6 | 2781.8 | 2700.3 | 4007.9 | 1202.8 | 0.67522 | 5.589
2024-12-09 | 19:47 | Data | 0 | 33.088 | 31.555 | 173.195 | 7.62 | 163.262 | 2166.49 | 25.89 | 47.894 | 6.39 | 1.303 | 4.272 | 8350.29 | 1.654 | 97.8 | 76.6 | 1408 | 23.95 | 5427.7 | 2790.6 | 2713 | 4014.4 | 1202.8 | 0.67817 | 5.575
2024-12-09 | 19:47 | Data | 0 | 33.176 | 31.562 | 173.105 | 7.63 | 163.126 | 2170.1 | 25.89 | 47.804 | 6.38 | 1.296 | 4.299 | 8354.81 | 1.742 | 97.8 | 76.8 | 1411 | 23.9 | 5430.6 | 2780.3 | 2687.5 | 3994.2 | 1202.8 | 0.67903 | 5.595
2024-12-09 | 19:47 | Data | 0 | 33.203 | 31.339 | 173.15 | 7.63 | 163.262 | 2169.2 | 25.9 | 47.894 | 6.38 | 1.299 | 4.308 | 8345.77 | 1.755 | 97.8 | 76.8 | 1410 | 23.9 | 5424.8 | 2789.3 | 2696.1 | 4002.7 | 1202.8 | 0.67957 | 5.608
2024-12-09 | 19:47 | Data | 0 | 33.466 | 31.596 | 173.331 | 7.62 | 163.262 | 2169.2 | 25.89 | 48.165 | 6.38 | 1.31 | 4.297 | 8314.11 | 1.762 | 97.8 | 76.6 | 1411 | 24.08 | 5404.2 | 2767.8 | 2703.7 | 3997.9 | 1202.8 | 0.67482 | 5.607
2024-12-09 | 19:47 | Data | 0 | 33.237 | 31.684 | 173.014 | 7.63 | 163.126 | 2169.2 | 25.89 | 47.894 | 6.38 | 1.297 | 4.304 | 8345.77 | 1.735 | 97.8 | 76.8 | 1410 | 23.95 | 5424.8 | 2730 | 2659 | 3928.6 | 1202.8 | 0.67886 | 5.601
2024-12-09 | 19:47 | Data | 0 | 33.405 | 31.569 | 173.06 | 7.63 | 163.126 | 2166.49 | 25.89 | 48.255 | 6.38 | 1.294 | 4.301 | 8314.11 | 1.668 | 97.8 | 76.9 | 1408 | 24.08 | 5404.2 | 2721.7 | 2660 | 3926.8 | 1202.8 | 0.67388 | 5.595
2024-12-09 | 19:47 | Data | 0 | 33.459 | 31.799 | 173.195 | 7.63 | 163.172 | 2167.39 | 25.89 | 48.075 | 6.39 | 1.301 | 4.288 | 8318.64 | 1.627 | 97.8 | 76.7 | 1408 | 24.08 | 5407.1 | 2709.6 | 2690 | 3941.9 | 1202.8 | 0.6716 | 5.59
2024-12-09 | 19:47 | Data | 0 | 33.243 | 31.555 | 173.15 | 7.63 | 163.217 | 2167.39 | 25.89 | 48.165 | 6.39 | 1.301 | 4.274 | 8332.2 | 1.479 | 97.8 | 76.7 | 1409 | 24.08 | 5415.9 | 2698.1 | 2668.8 | 3919.1 | 1202.8 | 0.67153 | 5.575
2024-12-09 | 19:47 | Data | 0 | 33.385 | 31.738 | 173.195 | 7.63 | 163.172 | 2167.39 | 25.89 | 48.075 | 6.39 | 1.306 | 4.304 | 8363.86 | 1.87 | 97.8 | 76.7 | 1409 | 24.04 | 5436.5 | 2707 | 2664.7 | 3916.6 | 1202.8 | 0.67447 | 5.61
2024-12-09 | 19:47 | Data | 0 | 33.183 | 31.231 | 172.924 | 7.63 | 163.081 | 2166.49 | 25.89 | 48.165 | 6.38 | 1.31 | 4.316 | 8318.64 | 1.83 | 97.8 | 76.7 | 1408 | 24.04 | 5407.1 | 2712 | 2668 | 3926.3 | 1202.8 | 0.67472 | 5.627
2024-12-09 | 19:47 | Data | 0 | 33.243 | 31.393 | 173.014 | 7.63 | 163.081 | 2166.49 | 25.89 | 48.165 | 6.38 | 1.304 | 4.312 | 8314.11 | 1.83 | 97.8 | 76.8 | 1408 | 24.08 | 5404.2 | 2716.6 | 2672 | 3931.4 | 1202.8 | 0.67626 | 5.616
2024-12-09 | 19:47 | Data | 0 | 33.237 | 31.569 | 173.105 | 7.63 | 163.262 | 2166.49 | 25.89 | 48.165 | 6.38 | 1.295 | 4.32 | 8305.07 | 1.641 | 97.8 | 76.9 | 1408 | 24.13 | 5398.3 | 2707.1 | 2668.5 | 3925.3 | 1202.8 | 0.67338 | 5.615
2024-12-09 | 19:48 | Data | 0 | 33.264 | 31.299 | 173.15 | 7.63 | 163.172 | 2166.49 | 25.89 | 48.436 | 6.38 | 1.295 | 4.295 | 8309.59 | 1.843 | 97.8 | 76.8 | 1408 | 24.22 | 5401.2 | 2707.6 | 2659.7 | 3911.8 | 1202.8 | 0.6757 | 5.59
2024-12-09 | 19:48 | Data | 0 | 33.601 | 31.583 | 173.195 | 7.63 | 163.172 | 2167.39 | 25.89 | 48.075 | 6.38 | 1.301 | 4.291 | 8350.29 | 1.668 | 97.8 | 76.7 | 1408 | 24.08 | 5427.7 | 2759.2 | 2674.7 | 3967.7 | 1202.8 | 0.6779 | 5.592
2024-12-09 | 19:48 | Data | 0 | 33.237 | 31.346 | 173.15 | 7.63 | 163.262 | 2166.49 | 25.89 | 48.075 | 6.38 | 1.291 | 4.317 | 8345.77 | 1.836 | 97.8 | 77 | 1408 | 24.08 | 5424.8 | 2757.2 | 2655.7 | 3954 | 1202.8 | 0.67944 | 5.608
2024-12-09 | 19:48 | Data | 0 | 33.196 | 31.346 | 173.105 | 7.62 | 163.126 | 2166.49 | 25.89 | 48.165 | 6.39 | 1.297 | 4.299 | 8350.29 | 1.823 | 97.8 | 76.8 | 1408 | 24.13 | 5427.7 | 2797.2 | 2674.1 | 3980.2 | 1202.8 | 0.68022 | 5.599
2024-12-09 | 19:48 | Data | 0 | 33.243 | 31.238 | 173.06 | 7.63 | 163.172 | 2166.49 | 25.89 | 48.165 | 6.39 | 1.309 | 4.307 | 8363.86 | 1.816 | 97.8 | 76.7 | 1408 | 24.08 | 5436.5 | 2773.2 | 2686.9 | 3993 | 1202.8 | 0.67803 | 5.616
2024-12-09 | 19:48 | Data | 0 | 33.183 | 31.562 | 173.105 | 7.63 | 163.172 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.309 | 4.314 | 8345.77 | 1.62 | 97.8 | 76.7 | 1406 | 24.08 | 5424.8 | 2749 | 2667.3 | 3956.8 | 1202.8 | 0.6776 | 5.624
2024-12-09 | 19:48 | Data | 0 | 33.176 | 31.515 | 173.06 | 7.63 | 163.126 | 2159.26 | 25.89 | 48.075 | 6.38 | 1.3 | 4.306 | 8359.34 | 1.722 | 97.8 | 76.8 | 1404 | 24.04 | 5433.6 | 2759.4 | 2682.3 | 3976.1 | 1202.8 | 0.67601 | 5.606
2024-12-09 | 19:48 | Data | 0 | 33.351 | 31.765 | 173.105 | 7.62 | 163.126 | 2166.49 | 25.89 | 48.165 | 6.39 | 1.31 | 4.313 | 8345.77 | 1.708 | 97.8 | 76.7 | 1408 | 24.08 | 5424.8 | 2779.4 | 2680.9 | 3982.3 | 1202.8 | 0.68141 | 5.624
2024-12-09 | 19:48 | Data | 0 | 33.162 | 31.569 | 173.15 | 7.62 | 163.217 | 2165.58 | 25.9 | 48.075 | 6.38 | 1.309 | 4.314 | 8350.29 | 1.722 | 97.8 | 76.7 | 1408 | 24.08 | 5427.7 | 2769.9 | 2671.7 | 3967.9 | 1202.8 | 0.68074 | 5.623
2024-12-09 | 19:48 | Data | 0 | 33.183 | 31.562 | 173.06 | 7.63 | 163.081 | 2165.58 | 25.89 | 48.165 | 6.38 | 1.305 | 4.317 | 8332.2 | 1.641 | 97.8 | 76.8 | 1408 | 24.08 | 5415.9 | 2764.3 | 2692.5 | 3981.6 | 1202.8 | 0.67907 | 5.622
2024-12-09 | 19:48 | Data | 0 | 33.196 | 31.346 | 173.15 | 7.63 | 163.081 | 2161.06 | 25.89 | 48.075 | 6.38 | 1.303 | 4.291 | 8332.2 | 1.627 | 97.8 | 76.7 | 1404 | 24.08 | 5415.9 | 2755.4 | 2694.1 | 3982.3 | 1202.8 | 0.6753 | 5.594
2024-12-09 | 19:48 | Data | 0 | 33.183 | 31.339 | 173.06 | 7.63 | 163.081 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.291 | 4.285 | 8345.77 | 1.843 | 97.8 | 76.9 | 1406 | 24.08 | 5424.8 | 2758.6 | 2678.1 | 3972.2 | 1202.8 | 0.67782 | 5.575
2024-12-09 | 19:48 | Data | 0 | 32.96 | 31.515 | 173.195 | 7.63 | 163.081 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.303 | 4.305 | 8332.2 | 1.735 | 97.8 | 76.8 | 1407 | 24.08 | 5415.9 | 2769.1 | 2667.5 | 3967.8 | 1202.9 | 0.68067 | 5.609
2024-12-09 | 19:48 | Data | 0 | 33.385 | 31.346 | 173.06 | 7.63 | 163.081 | 2161.06 | 25.89 | 48.165 | 6.38 | 1.305 | 4.308 | 8350.29 | 1.728 | 97.8 | 76.7 | 1405 | 24.13 | 5427.7 | 2749.2 | 2667.6 | 3959.9 | 1202.9 | 0.67662 | 5.612
2024-12-09 | 19:48 | Data | 0 | 33.183 | 31.441 | 173.105 | 7.62 | 163.036 | 2163.77 | 25.89 | 48.165 | 6.39 | 1.302 | 4.323 | 8350.29 | 1.668 | 97.8 | 76.8 | 1406 | 24.08 | 5427.7 | 2767.9 | 2684.2 | 3982 | 1202.9 | 0.6793 | 5.625
2024-12-09 | 19:48 | Data | 0 | 33.007 | 31.339 | 172.969 | 7.63 | 163.081 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.295 | 4.291 | 8345.77 | 1.62 | 97.8 | 76.8 | 1406 | 24.04 | 5424.8 | 2754.6 | 2688.4 | 3977.1 | 1202.9 | 0.67476 | 5.585
2024-12-09 | 19:48 | Data | 0 | 32.953 | 31.447 | 173.06 | 7.62 | 163.036 | 2163.77 | 25.9 | 48.075 | 6.38 | 1.306 | 4.297 | 8345.77 | 1.708 | 97.8 | 76.7 | 1407 | 24.04 | 5424.8 | 2743 | 2695 | 3971.1 | 1202.9 | 0.67709 | 5.602
2024-12-09 | 19:48 | Data | 0 | 33.183 | 31.339 | 173.014 | 7.63 | 162.991 | 2163.77 | 25.89 | 48.436 | 6.39 | 1.305 | 4.312 | 8345.77 | 1.843 | 97.8 | 76.8 | 1406 | 24.22 | 5424.8 | 2770.8 | 2686.2 | 3981.1 | 1202.9 | 0.68036 | 5.617
2024-12-09 | 19:49 | Data | 0 | 33.129 | 31.346 | 172.969 | 7.63 | 163.036 | 2166.49 | 25.89 | 48.075 | 6.38 | 1.305 | 4.295 | 8345.77 | 1.816 | 97.8 | 76.7 | 1408 | 24.08 | 5424.8 | 2772.5 | 2679.7 | 3975.9 | 1202.9 | 0.68103 | 5.6
2024-12-09 | 19:49 | Data | 0 | 33.068 | 31.393 | 173.06 | 7.63 | 163.036 | 2166.49 | 25.89 | 47.894 | 6.38 | 1.299 | 4.303 | 8350.29 | 1.816 | 97.8 | 76.8 | 1408 | 23.99 | 5427.7 | 2765.8 | 2666.2 | 3963.8 | 1202.9 | 0.68125 | 5.601
2024-12-09 | 19:49 | Data | 0 | 33.129 | 31.542 | 173.014 | 7.62 | 163.126 | 2164.68 | 25.89 | 47.894 | 6.38 | 1.3 | 4.297 | 8350.29 | 1.654 | 97.8 | 76.8 | 1407 | 23.95 | 5427.7 | 2735.1 | 2663.9 | 3946.6 | 1202.9 | 0.6768 | 5.596
2024-12-09 | 19:49 | Data | 0 | 33.176 | 31.339 | 173.105 | 7.63 | 163.081 | 2163.77 | 25.89 | 48.075 | 6.39 | 1.305 | 4.327 | 8332.2 | 1.836 | 97.8 | 76.8 | 1406 | 24.08 | 5415.9 | 2767.7 | 2676.9 | 3974.1 | 1202.9 | 0.6794 | 5.633
2024-12-09 | 19:49 | Data | 0 | 33.284 | 31.481 | 173.06 | 7.62 | 163.217 | 2165.58 | 25.89 | 48.075 | 6.38 | 1.297 | 4.315 | 8318.64 | 1.904 | 97.8 | 76.9 | 1408 | 24.08 | 5407.1 | 2755.3 | 2660.1 | 3951.6 | 1202.9 | 0.68035 | 5.612
2024-12-09 | 19:49 | Data | 0 | 33.095 | 31.346 | 172.969 | 7.62 | 163.036 | 2166.49 | 25.89 | 48.255 | 6.38 | 1.302 | 4.333 | 8332.2 | 1.641 | 97.8 | 76.9 | 1409 | 24.13 | 5415.9 | 2786.8 | 2701.2 | 4003.9 | 1202.9 | 0.67999 | 5.635
2024-12-09 | 19:49 | Data | 0 | 33.095 | 31.299 | 173.15 | 7.63 | 163.126 | 2166.49 | 25.89 | 47.984 | 6.38 | 1.304 | 4.32 | 8332.2 | 1.674 | 97.8 | 76.8 | 1408 | 23.99 | 5415.9 | 2742.5 | 2629.8 | 3922.7 | 1202.9 | 0.68524 | 5.624
2024-12-09 | 19:49 | Data | 0 | 33.027 | 31.339 | 172.969 | 7.62 | 163.081 | 2166.49 | 25.89 | 48.075 | 6.38 | 1.311 | 4.314 | 8318.64 | 1.728 | 97.8 | 76.7 | 1409 | 23.99 | 5407.1 | 2740.4 | 2634.5 | 3936.1 | 1202.9 | 0.68001 | 5.625
2024-12-09 | 19:49 | Data | 0 | 33.068 | 31.339 | 172.969 | 7.63 | 163.081 | 2167.39 | 25.89 | 48.255 | 6.38 | 1.289 | 4.309 | 8309.59 | 1.83 | 97.8 | 77 | 1411 | 24.13 | 5401.2 | 2760.7 | 2687.1 | 3975.3 | 1202.9 | 0.6766 | 5.597
2024-12-09 | 19:49 | Data | 0 | 33.345 | 31.366 | 173.06 | 7.62 | 163.081 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.287 | 4.334 | 8323.16 | 1.83 | 97.8 | 77.1 | 1410 | 24.04 | 5410.1 | 2758.7 | 2669.6 | 3964.7 | 1202.9 | 0.67564 | 5.622
2024-12-09 | 19:49 | Data | 0 | 33.21 | 31.238 | 173.014 | 7.63 | 163.081 | 2174.62 | 25.9 | 48.075 | 6.38 | 1.306 | 4.331 | 8314.11 | 1.809 | 97.8 | 76.8 | 1413 | 24.04 | 5404.2 | 2757.4 | 2673.4 | 3965 | 1202.9 | 0.67951 | 5.637
2024-12-09 | 19:49 | Data | 0 | 32.953 | 31.542 | 173.014 | 7.62 | 163.081 | 2171.91 | 25.9 | 48.165 | 6.38 | 1.309 | 4.31 | 8332.2 | 1.884 | 97.8 | 76.7 | 1411 | 24.08 | 5415.9 | 2757.7 | 2675.7 | 3965.3 | 1202.9 | 0.67728 | 5.619
2024-12-09 | 19:49 | Data | 0 | 33.081 | 31.117 | 172.924 | 7.63 | 163.036 | 2166.49 | 25.89 | 47.984 | 6.39 | 1.302 | 4.303 | 8332.2 | 1.83 | 97.8 | 76.8 | 1408 | 23.95 | 5415.9 | 2763.3 | 2671 | 3964.6 | 1202.9 | 0.68011 | 5.605
2024-12-09 | 19:49 | Data | 0 | 32.967 | 31.454 | 173.06 | 7.62 | 163.036 | 2170.1 | 25.89 | 47.984 | 6.38 | 1.309 | 4.306 | 8336.72 | 1.62 | 97.8 | 76.7 | 1411 | 23.95 | 5418.9 | 2762.4 | 2660.9 | 3959.4 | 1202.9 | 0.68098 | 5.615
2024-12-09 | 19:49 | Data | 0 | 33.399 | 31.583 | 173.06 | 7.63 | 163.172 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.303 | 4.315 | 8336.72 | 1.647 | 97.8 | 76.8 | 1411 | 23.95 | 5418.9 | 2757 | 2656.1 | 3954.1 | 1202.9 | 0.68105 | 5.619
2024-12-09 | 19:49 | Data | 0 | 33.399 | 31.353 | 173.105 | 7.63 | 163.126 | 2163.77 | 25.89 | 47.804 | 6.38 | 1.295 | 4.306 | 8332.2 | 1.904 | 97.8 | 76.9 | 1407 | 23.95 | 5415.9 | 2732.4 | 2666.8 | 3943.6 | 1202.9 | 0.67601 | 5.602
2024-12-09 | 19:49 | Data | 0 | 32.953 | 31.508 | 172.969 | 7.62 | 162.991 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.304 | 4.291 | 8318.64 | 1.647 | 97.8 | 76.7 | 1411 | 24.08 | 5407.1 | 2753.9 | 2670.2 | 3958.6 | 1202.9 | 0.68049 | 5.595
2024-12-09 | 19:49 | Data | 0 | 32.96 | 31.339 | 173.014 | 7.62 | 163.081 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.305 | 4.274 | 8259.85 | 1.728 | 97.8 | 76.6 | 1411 | 24.04 | 5368.9 | 2767.9 | 2671.1 | 3969.4 | 1202.9 | 0.68009 | 5.579
2024-12-09 | 19:50 | Data | 0 | 32.98 | 31.339 | 172.924 | 7.63 | 163.081 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.295 | 4.3 | 7983.99 | 1.62 | 97.8 | 76.9 | 1410 | 24.08 | 5189.6 | 2752.2 | 2673.5 | 3959.6 | 1202.9 | 0.67694 | 5.595
2024-12-09 | 19:50 | Data | 0 | 32.967 | 31.339 | 173.014 | 7.63 | 163.081 | 2170.1 | 25.89 | 48.075 | 6.38 | 1.295 | 4.315 | 8549.27 | 1.647 | 97.8 | 76.9 | 1411 | 24.08 | 5557 | 2748.4 | 2675.4 | 3957.7 | 1202.9 | 0.67649 | 5.61
2024-12-09 | 19:50 | Data | 0 | 33.196 | 31.353 | 173.105 | 7.63 | 163.172 | 2049.89 | 25.89 | 47.984 | 6.38 | 1.3 | 4.299 | 8526.66 | 1.816 | 97.7 | 76.8 | 1332 | 23.95 | 5542.3 | 2730.6 | 2693.9 | 3961.8 | 1202.9 | 0.67177 | 5.6
2024-12-09 | 19:50 | Data | 0 | 33.149 | 31.562 | 173.014 | 7.63 | 163.036 | 2050.8 | 25.89 | 47.984 | 6.38 | 1.292 | 4.291 | 8526.66 | 1.776 | 97.7 | 76.8 | 1333 | 23.95 | 5542.3 | 2761.2 | 2693.1 | 3979.9 | 1202.9 | 0.67624 | 5.582
2024-12-09 | 19:50 | Data | 0 | 32.953 | 31.515 | 172.969 | 7.63 | 163.036 | 2153.83 | 25.89 | 47.804 | 6.38 | 1.295 | 4.296 | 8526.66 | 1.614 | 97.8 | 76.8 | 1400 | 23.86 | 5542.3 | 2752.1 | 2686.1 | 3971.5 | 1202.9 | 0.6754 | 5.591
2024-12-09 | 19:50 | Data | 0 | 33.129 | 31.758 | 173.105 | 7.63 | 163.172 | 2152.93 | 25.89 | 47.984 | 6.39 | 1.301 | 4.312 | 8513.09 | 1.769 | 97.8 | 76.8 | 1399 | 23.95 | 5533.5 | 2752.7 | 2679.2 | 3963.2 | 1202.9 | 0.67751 | 5.613
2024-12-09 | 19:50 | Data | 0 | 33.129 | 31.353 | 173.014 | 7.62 | 163.081 | 2166.49 | 25.9 | 47.984 | 6.38 | 1.292 | 4.275 | 8495 | 1.816 | 97.8 | 76.8 | 1408 | 23.95 | 5521.8 | 2738.6 | 2688.2 | 3963.2 | 1202.9 | 0.67295 | 5.567
2024-12-09 | 19:50 | Data | 0 | 33.075 | 31.515 | 173.06 | 7.63 | 163.081 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.303 | 4.298 | 8499.53 | 1.769 | 97.8 | 76.7 | 1411 | 23.95 | 5524.7 | 2755.2 | 2688.6 | 3973.2 | 1202.9 | 0.67498 | 5.602
2024-12-09 | 19:50 | Data | 0 | 33.156 | 31.238 | 172.924 | 7.63 | 163.036 | 2170.1 | 25.89 | 47.984 | 6.38 | 1.304 | 4.295 | 8481.44 | 1.809 | 97.8 | 76.7 | 1411 | 23.95 | 5512.9 | 2764.7 | 2703.2 | 3985.4 | 1202.9 | 0.67725 | 5.6
2024-12-09 | 19:50 | Data | 0 | 33.405 | 31.569 | 173.06 | 7.62 | 163.126 | 2166.49 | 25.89 | 47.804 | 6.38 | 1.305 | 4.308 | 8472.39 | 1.836 | 97.8 | 76.7 | 1408 | 23.95 | 5507.1 | 2755.9 | 2661.7 | 3954.9 | 1202.9 | 0.67862 | 5.614
2024-12-09 | 19:50 | Data | 0 | 33.412 | 31.38 | 173.06 | 7.63 | 163.217 | 2171.01 | 25.89 | 47.894 | 6.39 | 1.305 | 4.306 | 8458.83 | 1.87 | 97.8 | 76.7 | 1412 | 23.99 | 5498.2 | 2762.1 | 2689.5 | 3979.5 | 1202.9 | 0.67607 | 5.61
2024-12-09 | 19:50 | Data | 0 | 33.075 | 31.542 | 173.15 | 7.63 | 163.172 | 2171.91 | 25.89 | 47.894 | 6.38 | 1.301 | 4.309 | 8454.3 | 1.769 | 97.8 | 76.8 | 1412 | 23.9 | 5495.3 | 2760.1 | 2655.4 | 3953.2 | 1202.9 | 0.6821 | 5.61
2024-12-09 | 19:50 | Data | 0 | 33.169 | 31.63 | 173.105 | 7.63 | 163.126 | 2166.49 | 25.89 | 47.894 | 6.38 | 1.289 | 4.303 | 8454.3 | 1.951 | 97.8 | 77 | 1408 | 23.95 | 5495.3 | 2768.9 | 2668.9 | 3966.5 | 1202.9 | 0.68189 | 5.591
2024-12-09 | 19:50 | Data | 0 | 33.297 | 31.785 | 173.15 | 7.63 | 163.217 | 2166.49 | 25.89 | 47.894 | 6.38 | 1.299 | 4.297 | 8418.13 | 1.62 | 97.8 | 76.8 | 1408 | 23.95 | 5471.8 | 2752 | 2682.8 | 3968.2 | 1202.9 | 0.67814 | 5.597
2024-12-09 | 19:50 | Data | 0 | 33.183 | 31.346 | 172.969 | 7.63 | 163.081 | 2164.68 | 25.89 | 47.804 | 6.39 | 1.297 | 4.318 | 8431.69 | 1.654 | 97.8 | 76.9 | 1406 | 23.95 | 5480.6 | 2749.5 | 2693.8 | 3976.8 | 1203 | 0.67484 | 5.614
2024-12-09 | 19:50 | Data | 0 | 33.297 | 31.792 | 173.15 | 7.63 | 163.172 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.308 | 4.297 | 8409.08 | 1.735 | 97.8 | 76.7 | 1406 | 24.08 | 5465.9 | 2762.2 | 2701.6 | 3982.5 | 1203 | 0.67678 | 5.606
2024-12-09 | 19:50 | Data | 0 | 33.176 | 31.339 | 172.969 | 7.63 | 163.036 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.308 | 4.279 | 8400.04 | 1.843 | 97.8 | 76.6 | 1406 | 24.08 | 5460 | 2757.4 | 2677.9 | 3963.2 | 1203 | 0.67801 | 5.587
2024-12-09 | 19:50 | Data | 0 | 32.967 | 31.225 | 172.969 | 7.63 | 163.081 | 2161.06 | 25.89 | 48.165 | 6.38 | 1.304 | 4.304 | 8386.47 | 1.62 | 97.8 | 76.8 | 1405 | 24.08 | 5451.2 | 2743.5 | 2670.4 | 3953.6 | 1203 | 0.6764 | 5.607
2024-12-09 | 19:51 | Data | 0 | 33.027 | 31.117 | 173.014 | 7.62 | 163.172 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.303 | 4.312 | 8386.47 | 1.674 | 97.8 | 76.8 | 1406 | 24.08 | 5451.2 | 2756.9 | 2676.1 | 3967.5 | 1203 | 0.67821 | 5.615
2024-12-09 | 19:51 | Data | 0 | 32.96 | 31.366 | 172.969 | 7.63 | 163.036 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.302 | 4.284 | 8390.99 | 1.769 | 97.8 | 76.7 | 1406 | 24.08 | 5454.1 | 2749.6 | 2668.1 | 3956.2 | 1203 | 0.67931 | 5.586
2024-12-09 | 19:51 | Data | 0 | 33.385 | 31.366 | 173.06 | 7.63 | 163.126 | 2162.87 | 25.89 | 48.165 | 6.38 | 1.308 | 4.295 | 8377.43 | 1.816 | 97.8 | 76.7 | 1406 | 24.08 | 5445.3 | 2744.8 | 2666.6 | 3949.3 | 1203 | 0.67774 | 5.603
2024-12-09 | 19:51 | Data | 0 | 33.412 | 31.589 | 173.06 | 7.62 | 163.217 | 2166.49 | 25.89 | 48.075 | 6.38 | 1.3 | 4.302 | 8381.95 | 1.708 | 97.8 | 76.8 | 1408 | 24.04 | 5448.3 | 2758.4 | 2664.9 | 3952.5 | 1203 | 0.6791 | 5.6
2024-12-09 | 19:51 | Data | 0 | 33.486 | 31.407 | 173.105 | 7.63 | 163.172 | 2161.97 | 25.89 | 48.165 | 6.39 | 1.295 | 4.296 | 8368.38 | 1.809 | 97.8 | 76.8 | 1405 | 24.08 | 5439.4 | 2762.2 | 2672.4 | 3966.4 | 1203 | 0.68034 | 5.591
2024-12-09 | 19:51 | Data | 0 | 33.183 | 31.339 | 173.014 | 7.62 | 163.081 | 2169.2 | 25.89 | 48.255 | 6.39 | 1.302 | 4.3 | 8363.86 | 1.83 | 97.8 | 76.7 | 1411 | 24.08 | 5436.5 | 2744.9 | 2657 | 3939.3 | 1203 | 0.68037 | 5.601
2024-12-09 | 19:51 | Data | 0 | 33.189 | 31.353 | 173.105 | 7.63 | 163.126 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.311 | 4.284 | 8350.29 | 1.816 | 97.8 | 76.5 | 1411 | 24.08 | 5427.7 | 2760.6 | 2676.2 | 3970.4 | 1203 | 0.68054 | 5.596
2024-12-09 | 19:51 | Data | 0 | 33.291 | 31.346 | 173.06 | 7.63 | 163.172 | 2170.1 | 25.89 | 48.255 | 6.38 | 1.301 | 4.285 | 8350.29 | 1.857 | 97.8 | 76.7 | 1411 | 24.08 | 5427.7 | 2758.9 | 2678.8 | 3970.8 | 1203 | 0.67483 | 5.586
2024-12-09 | 19:51 | Data | 0 | 33.412 | 31.711 | 173.105 | 7.63 | 163.126 | 2170.1 | 25.89 | 48.165 | 6.39 | 1.3 | 4.332 | 8345.77 | 1.789 | 97.8 | 76.9 | 1411 | 24.08 | 5424.8 | 2761.6 | 2689.9 | 3978.5 | 1203 | 0.67718 | 5.632
2024-12-09 | 19:51 | Data | 0 | 33.183 | 31.589 | 173.014 | 7.63 | 163.126 | 2169.2 | 25.89 | 48.165 | 6.38 | 1.307 | 4.306 | 8336.72 | 1.776 | 97.8 | 76.7 | 1411 | 24.04 | 5418.9 | 2731.9 | 2686.7 | 3957 | 1203 | 0.67289 | 5.613
2024-12-09 | 19:51 | Data | 0 | 33.183 | 31.393 | 173.105 | 7.62 | 163.126 | 2170.1 | 25.89 | 48.075 | 6.38 | 1.308 | 4.308 | 8386.47 | 1.735 | 97.8 | 76.7 | 1411 | 24.08 | 5451.2 | 2751.6 | 2659.8 | 3952.5 | 1203 | 0.67994 | 5.616
2024-12-09 | 19:51 | Data | 0 | 33.027 | 31.339 | 173.014 | 7.63 | 163.126 | 2170.1 | 25.89 | 48.255 | 6.38 | 1.301 | 4.298 | 8372.9 | 1.627 | 97.8 | 76.8 | 1411 | 24.13 | 5442.4 | 2726.4 | 2653.7 | 3933.3 | 1203 | 0.67702 | 5.6
2024-12-09 | 19:51 | Data | 0 | 33.183 | 31.346 | 172.969 | 7.63 | 163.081 | 2170.1 | 25.89 | 48.075 | 6.39 | 1.306 | 4.306 | 8359.34 | 1.83 | 97.8 | 76.7 | 1411 | 24.08 | 5433.6 | 2748.6 | 2668.9 | 3955.4 | 1203 | 0.67859 | 5.613
2024-12-09 | 19:51 | Data | 0 | 33.183 | 31.38 | 172.969 | 7.63 | 163.172 | 2170.1 | 25.89 | 48.165 | 6.39 | 1.306 | 4.324 | 8354.81 | 1.755 | 97.8 | 76.8 | 1411 | 24.08 | 5430.6 | 2749.7 | 2670.1 | 3952.9 | 1203 | 0.67898 | 5.631
2024-12-09 | 19:51 | Data | 0 | 33.068 | 31.515 | 172.924 | 7.63 | 163.126 | 2170.1 | 25.9 | 48.075 | 6.39 | 1.306 | 4.331 | 8350.29 | 1.526 | 97.8 | 76.8 | 1411 | 24.04 | 5427.7 | 2763.9 | 2677.4 | 3968.3 | 1203 | 0.67966 | 5.637
2024-12-09 | 19:51 | Data | 0 | 33.297 | 31.366 | 173.06 | 7.63 | 163.217 | 2171.91 | 25.89 | 48.165 | 6.38 | 1.3 | 4.288 | 8350.29 | 1.83 | 97.8 | 76.7 | 1412 | 24.08 | 5427.7 | 2759.8 | 2683.2 | 3971.1 | 1203 | 0.67886 | 5.588
2024-12-09 | 19:51 | Data | 0 | 33.412 | 31.36 | 173.105 | 7.63 | 163.172 | 2172.81 | 25.89 | 47.804 | 6.38 | 1.306 | 4.31 | 8345.77 | 1.83 | 97.8 | 76.8 | 1412 | 23.95 | 5424.8 | 2737.9 | 2678.8 | 3962.6 | 1203 | 0.67667 | 5.615
2024-12-09 | 19:52 | Data | 0 | 32.98 | 31.515 | 172.969 | 7.63 | 163.081 | 2175.52 | 25.9 | 47.984 | 6.38 | 1.304 | 4.271 | 8350.29 | 1.735 | 97.8 | 76.6 | 1414 | 23.95 | 5427.7 | 2753.2 | 2678.7 | 3962.8 | 1203 | 0.67622 | 5.574
2024-12-09 | 19:52 | Data | 0 | 33.21 | 31.461 | 173.105 | 7.62 | 163.172 | 2178.24 | 25.89 | 47.984 | 6.38 | 1.297 | 4.27 | 8354.81 | 1.674 | 97.8 | 76.7 | 1416 | 23.95 | 5430.6 | 2755.1 | 2691.4 | 3978.3 | 1203 | 0.6759 | 5.565
2024-12-09 | 19:52 | Data | 0 | 33.378 | 31.792 | 173.195 | 7.63 | 163.126 | 2177.33 | 25.89 | 47.894 | 6.38 | 1.296 | 4.287 | 8345.77 | 1.809 | 97.8 | 76.8 | 1416 | 23.99 | 5424.8 | 2749.6 | 2694.9 | 3970.1 | 1203 | 0.6762 | 5.583
2024-12-09 | 19:52 | Data | 0 | 33.156 | 31.562 | 172.969 | 7.63 | 163.081 | 2178.24 | 25.89 | 47.894 | 6.38 | 1.301 | 4.299 | 8341.25 | 1.614 | 97.8 | 76.8 | 1415 | 23.9 | 5421.8 | 2745.7 | 2696.9 | 3969.4 | 1203 | 0.6759 | 5.6
2024-12-09 | 19:52 | Data | 0 | 33.183 | 31.339 | 173.105 | 7.63 | 163.126 | 2180.95 | 25.89 | 47.894 | 6.38 | 1.299 | 4.297 | 8345.77 | 1.843 | 97.8 | 76.8 | 1417 | 23.99 | 5424.8 | 2755.2 | 2680.5 | 3970.1 | 1203 | 0.67858 | 5.595
2024-12-09 | 19:52 | Data | 0 | 33.183 | 31.826 | 173.105 | 7.63 | 163.172 | 2182.75 | 25.89 | 47.894 | 6.38 | 1.295 | 4.296 | 8350.29 | 1.668 | 97.8 | 76.8 | 1419 | 23.95 | 5427.7 | 2744.9 | 2670 | 3947 | 1203 | 0.67833 | 5.591
2024-12-09 | 19:52 | Data | 0 | 33.135 | 31.562 | 173.014 | 7.63 | 163.126 | 2180.04 | 25.89 | 47.894 | 6.38 | 1.301 | 4.275 | 8332.2 | 1.796 | 97.8 | 76.7 | 1418 | 23.9 | 5415.9 | 2742.5 | 2673.5 | 3957.3 | 1203 | 0.67514 | 5.576
2024-12-09 | 19:52 | Data | 0 | 33.608 | 31.704 | 173.195 | 7.62 | 163.217 | 2180.04 | 25.89 | 47.894 | 6.39 | 1.3 | 4.295 | 8305.07 | 1.931 | 97.8 | 76.8 | 1417 | 23.95 | 5398.3 | 2734.7 | 2684.7 | 3957.1 | 1203 | 0.67402 | 5.595
2024-12-09 | 19:52 | Data | 0 | 33.196 | 31.468 | 173.105 | 7.62 | 163.172 | 2180.04 | 25.89 | 47.894 | 6.38 | 1.3 | 4.316 | 8323.16 | 1.809 | 97.8 | 76.9 | 1417 | 23.95 | 5410.1 | 2765.3 | 2664 | 3964 | 1203 | 0.68165 | 5.617
2024-12-09 | 19:52 | Data | 0 | 33.27 | 31.61 | 173.15 | 7.63 | 163.172 | 2177.33 | 25.89 | 47.894 | 6.38 | 1.302 | 4.304 | 8314.11 | 1.614 | 97.8 | 76.8 | 1415 | 23.99 | 5404.2 | 2742 | 2687.2 | 3965.9 | 1203 | 0.67379 | 5.608
2024-12-09 | 19:52 | Data | 0 | 33.385 | 31.65 | 173.06 | 7.62 | 163.172 | 2178.24 | 25.89 | 47.894 | 6.38 | 1.299 | 4.305 | 8314.11 | 1.728 | 97.8 | 76.8 | 1416 | 23.95 | 5404.2 | 2746.5 | 2677.1 | 3958.9 | 1203 | 0.67757 | 5.604
2024-12-09 | 19:52 | Data | 0 | 32.96 | 31.535 | 173.15 | 7.63 | 163.081 | 2177.33 | 25.89 | 47.984 | 6.38 | 1.287 | 4.285 | 8318.64 | 1.641 | 97.8 | 76.9 | 1415 | 23.99 | 5407.1 | 2745.5 | 2691.1 | 3967.7 | 1203 | 0.67581 | 5.572
2024-12-09 | 19:52 | Data | 0 | 32.967 | 31.454 | 173.014 | 7.63 | 163.126 | 2176.43 | 25.9 | 48.436 | 6.38 | 1.29 | 4.318 | 8318.64 | 1.789 | 97.8 | 77 | 1415 | 24.17 | 5407.1 | 2778.8 | 2668 | 3975.8 | 1203 | 0.68205 | 5.609
2024-12-09 | 19:52 | Data | 0 | 33.426 | 31.454 | 173.24 | 7.62 | 163.172 | 2178.24 | 25.89 | 47.894 | 6.38 | 1.302 | 4.321 | 8314.11 | 1.668 | 97.8 | 76.8 | 1415 | 23.95 | 5404.2 | 2769 | 2646.4 | 3949.3 | 1203 | 0.6841 | 5.625
2024-12-09 | 19:52 | Data | 0 | 33.068 | 31.515 | 173.014 | 7.63 | 163.126 | 2179.14 | 25.89 | 47.894 | 6.38 | 1.304 | 4.309 | 8332.2 | 1.641 | 97.8 | 76.8 | 1416 | 23.95 | 5415.9 | 2755.7 | 2661.7 | 3956.9 | 1203 | 0.67914 | 5.613
2024-12-09 | 19:52 | Data | 0 | 33.183 | 31.555 | 173.014 | 7.63 | 163.172 | 2178.24 | 25.89 | 47.804 | 6.38 | 1.293 | 4.321 | 8300.55 | 1.641 | 97.8 | 77 | 1416 | 23.95 | 5395.4 | 2768 | 2692.1 | 3982.1 | 1203 | 0.67892 | 5.615
2024-12-09 | 19:52 | Data | 0 | 33.237 | 31.346 | 173.105 | 7.63 | 163.217 | 2175.52 | 25.89 | 48.165 | 6.38 | 1.295 | 4.295 | 8305.07 | 1.674 | 97.8 | 76.8 | 1414 | 24.04 | 5398.3 | 2765.7 | 2682.7 | 3969.8 | 1203 | 0.68128 | 5.59
2024-12-09 | 19:52 | Data | 0 | 33.513 | 31.677 | 173.105 | 7.63 | 163.172 | 2174.62 | 25.89 | 48.165 | 6.38 | 1.292 | 4.287 | 8318.64 | 1.809 | 97.8 | 76.8 | 1414 | 24.08 | 5407.1 | 2778.7 | 2658.9 | 3970.3 | 1203 | 0.6812 | 5.58
2024-12-09 | 19:53 | Data | 0 | 33.129 | 31.657 | 173.105 | 7.63 | 163.081 | 2172.81 | 25.89 | 48.075 | 6.38 | 1.299 | 4.309 | 8318.64 | 1.722 | 97.8 | 76.8 | 1412 | 24.04 | 5407.1 | 2755 | 2672.1 | 3963.6 | 1203.1 | 0.67681 | 5.608
2024-12-09 | 19:53 | Data | 0 | 33.183 | 31.38 | 173.06 | 7.63 | 163.126 | 2174.62 | 25.9 | 48.165 | 6.38 | 1.305 | 4.3 | 8318.64 | 1.668 | 97.8 | 76.7 | 1414 | 24.08 | 5407.1 | 2730.2 | 2677.4 | 3952.5 | 1203.1 | 0.67334 | 5.605
2024-12-09 | 19:53 | Data | 0 | 33.574 | 31.373 | 173.15 | 7.63 | 163.217 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.308 | 4.295 | 8345.77 | 2.019 | 97.8 | 76.7 | 1411 | 24.13 | 5424.8 | 2765.7 | 2668.6 | 3964.3 | 1203.1 | 0.68048 | 5.603
2024-12-09 | 19:53 | Data | 0 | 33.183 | 31.562 | 173.105 | 7.62 | 163.172 | 2161.06 | 25.89 | 48.255 | 6.38 | 1.314 | 4.291 | 8332.2 | 1.627 | 97.8 | 76.6 | 1405 | 24.13 | 5415.9 | 2737.6 | 2668.6 | 3949.5 | 1203.1 | 0.67505 | 5.604
2024-12-09 | 19:53 | Data | 0 | 33.021 | 31.339 | 173.105 | 7.63 | 163.081 | 2166.49 | 25.89 | 48.075 | 6.38 | 1.31 | 4.302 | 8332.2 | 1.641 | 97.8 | 76.6 | 1408 | 24.08 | 5415.9 | 2760.2 | 2710.6 | 3989.7 | 1203.1 | 0.67356 | 5.611
2024-12-09 | 19:53 | Data | 0 | 33.183 | 31.366 | 172.969 | 7.63 | 162.991 | 2166.49 | 25.9 | 48.165 | 6.38 | 1.301 | 4.32 | 8359.34 | 1.843 | 97.8 | 76.9 | 1408 | 24.08 | 5433.6 | 2745.7 | 2686.3 | 3964.5 | 1203.1 | 0.67634 | 5.619
2024-12-09 | 19:53 | Data | 0 | 32.73 | 31.339 | 173.014 | 7.63 | 163.126 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.309 | 4.333 | 8363.86 | 1.917 | 97.8 | 76.8 | 1410 | 24.08 | 5436.5 | 2745.4 | 2677 | 3952.6 | 1203.1 | 0.6772 | 5.641
2024-12-09 | 19:53 | Data | 0 | 33.351 | 31.569 | 173.06 | 7.63 | 163.172 | 2166.49 | 25.89 | 47.984 | 6.38 | 1.299 | 4.309 | 8372.9 | 1.843 | 97.8 | 76.8 | 1408 | 23.99 | 5442.4 | 2769.3 | 2689.4 | 3985.1 | 1203.1 | 0.67758 | 5.607
2024-12-09 | 19:53 | Data | 0 | 33.162 | 31.569 | 173.06 | 7.63 | 163.126 | 2165.58 | 25.89 | 48.075 | 6.38 | 1.303 | 4.309 | 8372.9 | 1.782 | 97.8 | 76.8 | 1408 | 24.08 | 5442.4 | 2751.3 | 2671.3 | 3958.6 | 1203.1 | 0.67889 | 5.612
2024-12-09 | 19:53 | Data | 0 | 33.189 | 31.353 | 173.06 | 7.63 | 163.081 | 2166.49 | 25.89 | 48.165 | 6.38 | 1.308 | 4.324 | 8345.77 | 1.789 | 97.8 | 76.8 | 1409 | 24.08 | 5424.8 | 2750.5 | 2654 | 3946.8 | 1203.1 | 0.67892 | 5.631
2024-12-09 | 19:53 | Data | 0 | 33.189 | 31.339 | 173.06 | 7.63 | 163.081 | 2167.39 | 25.89 | 48.436 | 6.38 | 1.303 | 4.313 | 8363.86 | 1.843 | 97.8 | 76.8 | 1409 | 24.22 | 5436.5 | 2746.8 | 2655.5 | 3942.6 | 1203.1 | 0.68041 | 5.617
2024-12-09 | 19:53 | Data | 0 | 32.96 | 31.339 | 173.15 | 7.63 | 163.081 | 2162.87 | 25.89 | 48.165 | 6.37 | 1.306 | 4.322 | 8363.86 | 1.62 | 97.8 | 76.8 | 1406 | 24.08 | 5436.5 | 2761 | 2671.3 | 3962.9 | 1203.1 | 0.68044 | 5.628
2024-12-09 | 19:53 | Data | 0 | 33.608 | 31.583 | 173.105 | 7.63 | 163.217 | 2163.77 | 25.9 | 48.165 | 6.38 | 1.304 | 4.31 | 8350.29 | 1.843 | 97.8 | 76.8 | 1406 | 24.08 | 5427.7 | 2741.9 | 2655.2 | 3944.5 | 1203.1 | 0.6839 | 5.614
2024-12-09 | 19:53 | Data | 0 | 33.189 | 31.731 | 173.15 | 7.63 | 163.081 | 2163.77 | 25.9 | 48.075 | 6.38 | 1.305 | 4.321 | 8372.9 | 1.641 | 97.8 | 76.8 | 1406 | 24.08 | 5442.4 | 2743.7 | 2646.4 | 3934.3 | 1203.1 | 0.68154 | 5.626
2024-12-09 | 19:53 | Data | 0 | 33.075 | 31.366 | 173.06 | 7.63 | 163.217 | 2161.97 | 25.89 | 48.165 | 6.38 | 1.304 | 4.313 | 8386.47 | 1.89 | 97.8 | 76.8 | 1405 | 24.04 | 5451.2 | 2753.2 | 2664.8 | 3954.1 | 1203.1 | 0.68047 | 5.618
2024-12-09 | 19:53 | Data | 0 | 33.27 | 31.36 | 173.15 | 7.62 | 163.172 | 2161.97 | 25.89 | 48.255 | 6.38 | 1.295 | 4.314 | 8359.34 | 1.803 | 97.8 | 76.9 | 1405 | 24.08 | 5433.6 | 2748.5 | 2677.6 | 3959.4 | 1203.1 | 0.67614 | 5.61
2024-12-09 | 19:53 | Data | 0 | 33.399 | 31.353 | 173.014 | 7.63 | 163.172 | 2161.06 | 25.89 | 48.165 | 6.38 | 1.292 | 4.309 | 8377.43 | 1.897 | 97.8 | 76.9 | 1405 | 24.08 | 5445.3 | 2769.2 | 2702.9 | 3987.7 | 1203.1 | 0.67691 | 5.601
2024-12-09 | 19:53 | Data | 0 | 33.189 | 31.461 | 173.06 | 7.63 | 163.172 | 2159.26 | 25.89 | 48.165 | 6.38 | 1.309 | 4.304 | 8386.47 | 1.816 | 97.8 | 76.7 | 1403 | 24.08 | 5451.2 | 2735.2 | 2695.7 | 3965 | 1203.1 | 0.67361 | 5.612
2024-12-09 | 19:54 | Data | 0 | 33.297 | 31.569 | 173.06 | 7.63 | 163.172 | 2161.06 | 25.9 | 48.165 | 6.38 | 1.301 | 4.313 | 8390.99 | 1.668 | 97.8 | 76.8 | 1405 | 24.08 | 5454.1 | 2760.1 | 2688 | 3967.2 | 1203.1 | 0.67707 | 5.617
2024-12-09 | 19:54 | Data | 0 | 33.156 | 31.353 | 173.06 | 7.62 | 163.126 | 2163.77 | 25.89 | 48.075 | 6.38 | 1.295 | 4.33 | 8381.95 | 1.809 | 97.8 | 77 | 1406 | 24.08 | 5448.3 | 2756.2 | 2700.8 | 3985.1 | 1203.1 | 0.67563 | 5.626
2024-12-09 | 19:54 | Data | 0 | 33.412 | 31.569 | 173.195 | 7.63 | 163.217 | 2164.68 | 25.89 | 47.714 | 6.38 | 1.308 | 4.303 | 8372.9 | 1.843 | 97.8 | 76.7 | 1406 | 23.86 | 5442.4 | 2744.7 | 2648.4 | 3940.4 | 1203.1 | 0.67858 | 5.61
2024-12-09 | 19:54 | Data | 0 | 33.183 | 31.569 | 173.105 | 7.63 | 163.126 | 2161.97 | 25.89 | 48.165 | 6.38 | 1.308 | 4.286 | 8381.95 | 1.62 | 97.8 | 76.6 | 1405 | 24.13 | 5448.3 | 2752.2 | 2669 | 3959.2 | 1203.1 | 0.67824 | 5.594
2024-12-09 | 19:54 | Data | 0 | 33.196 | 31.373 | 173.15 | 7.63 | 163.172 | 2166.49 | 25.89 | 48.165 | 6.38 | 1.303 | 4.297 | 8368.38 | 1.985 | 97.8 | 76.7 | 1409 | 24.08 | 5439.4 | 2743.3 | 2675.1 | 3953.8 | 1203.1 | 0.67766 | 5.6
2024-12-09 | 19:54 | Data | 0 | 33.621 | 31.481 | 173.15 | 7.62 | 163.172 | 2169.2 | 25.89 | 48.075 | 6.39 | 1.303 | 4.303 | 8386.47 | 1.728 | 97.8 | 76.8 | 1411 | 23.99 | 5451.2 | 2738.7 | 2673.1 | 3953 | 1203.1 | 0.67679 | 5.605
2024-12-09 | 19:54 | Data | 0 | 33.297 | 31.393 | 173.014 | 7.63 | 163.172 | 2169.2 | 25.89 | 48.075 | 6.39 | 1.306 | 4.304 | 8390.99 | 1.836 | 97.8 | 76.7 | 1410 | 24.08 | 5454.1 | 2767.6 | 2665.5 | 3964.6 | 1203.1 | 0.68076 | 5.61
2024-12-09 | 19:54 | Data | 0 | 33.297 | 31.569 | 173.15 | 7.63 | 163.126 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.304 | 4.299 | 8372.9 | 1.789 | 97.8 | 76.7 | 1411 | 24.08 | 5442.4 | 2745.9 | 2697.2 | 3971.6 | 1203.1 | 0.67442 | 5.603
2024-12-09 | 19:54 | Data | 0 | 33.021 | 31.258 | 173.105 | 7.63 | 163.217 | 2167.39 | 25.89 | 48.075 | 6.38 | 1.297 | 4.308 | 8372.9 | 1.796 | 97.8 | 76.9 | 1408 | 24.08 | 5442.4 | 2745.6 | 2702.6 | 3979.3 | 1203.1 | 0.67364 | 5.605
2024-12-09 | 19:54 | Data | 0 | 33.297 | 31.528 | 173.195 | 7.62 | 163.172 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.297 | 4.338 | 8345.77 | 1.965 | 97.8 | 77 | 1407 | 24.08 | 5424.8 | 2732 | 2694.4 | 3964.3 | 1203.1 | 0.6704 | 5.634
2024-12-09 | 19:54 | Data | 0 | 33.405 | 31.738 | 173.105 | 7.62 | 163.126 | 2162.87 | 25.89 | 48.255 | 6.38 | 1.312 | 4.32 | 8341.25 | 1.728 | 97.8 | 76.7 | 1406 | 24.08 | 5421.8 | 2751.3 | 2713.5 | 3986.3 | 1203.1 | 0.67515 | 5.633
2024-12-09 | 19:54 | Data | 0 | 33.183 | 31.772 | 173.195 | 7.63 | 163.217 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.301 | 4.301 | 8363.86 | 1.647 | 97.8 | 76.8 | 1407 | 24.08 | 5436.5 | 2760 | 2671.9 | 3967.2 | 1203.1 | 0.67855 | 5.601
2024-12-09 | 19:54 | Data | 0 | 33.223 | 31.549 | 173.195 | 7.63 | 163.217 | 2163.77 | 25.9 | 48.165 | 6.38 | 1.295 | 4.281 | 8377.43 | 1.641 | 97.8 | 76.8 | 1406 | 24.08 | 5445.3 | 2751.7 | 2673.7 | 3959.1 | 1203.1 | 0.67812 | 5.576
2024-12-09 | 19:54 | Data | 0 | 33.5 | 31.697 | 173.24 | 7.62 | 163.307 | 2164.68 | 25.89 | 48.075 | 6.39 | 1.296 | 4.302 | 8372.9 | 1.924 | 97.8 | 76.8 | 1407 | 24.08 | 5442.4 | 2753.9 | 2664.7 | 3957.3 | 1203.1 | 0.679 | 5.598
2024-12-09 | 19:54 | Data | 0 | 33.129 | 31.562 | 173.06 | 7.63 | 163.172 | 2166.49 | 25.9 | 48.165 | 6.38 | 1.307 | 4.278 | 8359.34 | 1.728 | 97.8 | 76.6 | 1408 | 24.08 | 5433.6 | 2746.7 | 2680.8 | 3961.5 | 1203.1 | 0.67735 | 5.585
2024-12-09 | 19:54 | Data | 0 | 33.183 | 31.339 | 173.014 | 7.63 | 163.172 | 2167.39 | 25.89 | 48.436 | 6.39 | 1.305 | 4.283 | 8350.29 | 1.83 | 97.8 | 76.6 | 1409 | 24.22 | 5427.7 | 2753.7 | 2646.9 | 3945.6 | 1203.1 | 0.67978 | 5.588
2024-12-09 | 19:54 | Data | 0 | 33.021 | 31.657 | 173.105 | 7.63 | 163.172 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.301 | 4.306 | 8341.25 | 1.506 | 97.8 | 76.8 | 1411 | 24.08 | 5421.8 | 2746.4 | 2668.7 | 3956 | 1203.1 | 0.67799 | 5.607
2024-12-09 | 19:54 | Data | 0 | 33.378 | 31.569 | 173.06 | 7.63 | 163.172 | 2163.77 | 25.89 | 48.165 | 6.39 | 1.3 | 4.289 | 8363.86 | 1.823 | 97.8 | 76.7 | 1406 | 24.08 | 5436.5 | 2760.7 | 2674.2 | 3962.2 | 1203.1 | 0.68041 | 5.589
2024-12-09 | 19:55 | Data | 0 | 33.412 | 31.454 | 173.15 | 7.63 | 163.217 | 2170.1 | 25.89 | 48.075 | 6.38 | 1.3 | 4.285 | 8359.34 | 1.843 | 97.8 | 76.7 | 1411 | 24.04 | 5433.6 | 2750 | 2676.2 | 3960.9 | 1203.1 | 0.67728 | 5.584
2024-12-09 | 19:55 | Data | 0 | 33.183 | 31.569 | 173.06 | 7.63 | 163.172 | 2169.2 | 25.89 | 48.075 | 6.38 | 1.299 | 4.292 | 8359.34 | 1.728 | 97.8 | 76.8 | 1411 | 24.08 | 5433.6 | 2755 | 2681.3 | 3967.9 | 1203.1 | 0.67602 | 5.59
2024-12-09 | 19:55 | Data | 0 | 33.567 | 31.799 | 173.24 | 7.63 | 163.217 | 2166.49 | 25.89 | 48.165 | 6.38 | 1.302 | 4.301 | 8359.34 | 1.836 | 97.8 | 76.8 | 1408 | 24.08 | 5433.6 | 2754.4 | 2684.6 | 3969.4 | 1203.1 | 0.67815 | 5.605
2024-12-09 | 19:55 | Data | 0 | 32.96 | 31.562 | 173.105 | 7.63 | 163.217 | 2172.81 | 25.89 | 48.075 | 6.38 | 1.307 | 4.304 | 8359.34 | 1.762 | 97.8 | 76.7 | 1412 | 24.04 | 5433.6 | 2763.2 | 2668.2 | 3963.5 | 1203.2 | 0.67988 | 5.61
2024-12-09 | 19:55 | Data | 0 | 33.297 | 31.677 | 173.24 | 7.63 | 163.262 | 2171.91 | 25.89 | 47.894 | 6.38 | 1.307 | 4.297 | 8363.86 | 1.776 | 97.8 | 76.7 | 1412 | 23.95 | 5436.5 | 2750.6 | 2665 | 3951.2 | 1203.2 | 0.68006 | 5.605
2024-12-09 | 19:55 | Data | 0 | 33.189 | 31.555 | 173.15 | 7.63 | 163.172 | 2172.81 | 25.89 | 48.075 | 6.38 | 1.304 | 4.313 | 8305.07 | 1.836 | 97.8 | 76.8 | 1412 | 24.08 | 5398.3 | 2760.5 | 2655.9 | 3959.2 | 1203.2 | 0.67912 | 5.617
2024-12-09 | 19:55 | Data | 0 | 33.183 | 31.657 | 173.105 | 7.62 | 163.172 | 2171.91 | 25.89 | 48.075 | 6.38 | 1.304 | 4.304 | 8291.5 | 1.816 | 97.8 | 76.7 | 1412 | 24.08 | 5389.5 | 2757 | 2663.9 | 3960.1 | 1203.2 | 0.67938 | 5.609
2024-12-09 | 19:55 | Data | 0 | 33.513 | 31.799 | 173.195 | 7.63 | 163.217 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.31 | 4.295 | 8300.55 | 1.782 | 97.8 | 76.6 | 1411 | 24.04 | 5395.4 | 2759.8 | 2657.4 | 3955.8 | 1203.2 | 0.68126 | 5.606
2024-12-09 | 19:55 | Data | 0 | 33.189 | 31.346 | 173.195 | 7.62 | 163.126 | 2170.1 | 25.89 | 48.075 | 6.38 | 1.304 | 4.295 | 8296.02 | 1.816 | 97.8 | 76.7 | 1411 | 24.08 | 5392.4 | 2740.7 | 2673.5 | 3952.7 | 1203.2 | 0.67782 | 5.599
2024-12-09 | 19:55 | Data | 0 | 33.412 | 31.481 | 173.331 | 7.63 | 163.352 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.304 | 4.298 | 8323.16 | 1.742 | 97.8 | 76.7 | 1411 | 24.08 | 5410.1 | 2782.5 | 2688.4 | 3990.9 | 1203.2 | 0.67653 | 5.601
2024-12-09 | 19:55 | Data | 0 | 33.466 | 31.576 | 173.24 | 7.63 | 163.262 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.302 | 4.297 | 8350.29 | 1.674 | 97.8 | 76.7 | 1411 | 24.08 | 5427.7 | 2753.6 | 2683.1 | 3965.3 | 1203.2 | 0.67746 | 5.6
2024-12-09 | 19:55 | Data | 0 | 33.021 | 31.366 | 173.15 | 7.63 | 163.217 | 2169.2 | 25.89 | 48.255 | 6.38 | 1.303 | 4.324 | 8354.81 | 1.512 | 97.8 | 76.8 | 1410 | 24.08 | 5430.6 | 2765.1 | 2689.5 | 3976.9 | 1203.2 | 0.67811 | 5.628
2024-12-09 | 19:55 | Data | 0 | 33.189 | 31.339 | 173.105 | 7.63 | 163.126 | 2173.72 | 25.89 | 47.804 | 6.38 | 1.299 | 4.319 | 8350.29 | 1.836 | 97.8 | 76.9 | 1412 | 23.95 | 5427.7 | 2749.1 | 2680 | 3979.3 | 1203.2 | 0.67817 | 5.618
2024-12-09 | 19:55 | Data | 0 | 33.297 | 31.792 | 173.24 | 7.63 | 163.262 | 2171.91 | 25.89 | 47.984 | 6.38 | 1.302 | 4.315 | 8332.2 | 1.634 | 97.8 | 76.8 | 1412 | 23.95 | 5415.9 | 2748.7 | 2673.4 | 3958.9 | 1203.2 | 0.67784 | 5.617
2024-12-09 | 19:55 | Data | 0 | 32.96 | 31.839 | 173.15 | 7.62 | 163.262 | 2171.91 | 25.89 | 47.984 | 6.38 | 1.305 | 4.301 | 8323.16 | 1.836 | 97.8 | 76.7 | 1412 | 23.95 | 5410.1 | 2757.9 | 2679.7 | 3968.8 | 1203.2 | 0.67792 | 5.606
2024-12-09 | 19:55 | Data | 0 | 33.102 | 31.522 | 173.331 | 7.63 | 163.217 | 2172.81 | 25.89 | 47.894 | 6.38 | 1.305 | 4.301 | 8336.72 | 1.701 | 97.8 | 76.7 | 1412 | 23.95 | 5418.9 | 2748.5 | 2671.1 | 3958 | 1203.2 | 0.67778 | 5.606
2024-12-09 | 19:55 | Data | 0 | 33.311 | 31.36 | 173.15 | 7.63 | 163.262 | 2172.81 | 25.89 | 47.804 | 6.38 | 1.303 | 4.282 | 8332.2 | 1.83 | 97.8 | 76.7 | 1412 | 23.95 | 5415.9 | 2737.9 | 2687.3 | 3972.1 | 1203.2 | 0.6752 | 5.585
2024-12-09 | 19:56 | Data | 0 | 33.405 | 31.454 | 173.15 | 7.63 | 163.217 | 2170.1 | 25.89 | 47.804 | 6.38 | 1.301 | 4.285 | 8341.25 | 1.843 | 97.8 | 76.7 | 1411 | 23.86 | 5421.8 | 2738.5 | 2667.9 | 3962 | 1203.2 | 0.67874 | 5.585
2024-12-09 | 19:56 | Data | 0 | 33.628 | 31.596 | 173.24 | 7.62 | 163.262 | 2165.58 | 25.89 | 47.984 | 6.38 | 1.301 | 4.31 | 8350.29 | 1.944 | 97.8 | 76.8 | 1408 | 23.95 | 5427.7 | 2740.5 | 2663.3 | 3942.5 | 1203.2 | 0.67742 | 5.612
2024-12-09 | 19:56 | Data | 0 | 33.527 | 31.994 | 173.195 | 7.63 | 163.262 | 2166.49 | 25.89 | 47.984 | 6.38 | 1.301 | 4.313 | 8345.77 | 1.654 | 97.8 | 76.8 | 1408 | 23.99 | 5424.8 | 2730.7 | 2707.3 | 3976.6 | 1203.2 | 0.67073 | 5.615
2024-12-09 | 19:56 | Data | 0 | 33.405 | 31.583 | 173.195 | 7.63 | 163.172 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.296 | 4.295 | 8350.29 | 1.715 | 97.8 | 76.8 | 1411 | 24.08 | 5427.7 | 2754.8 | 2710.5 | 3990.2 | 1203.2 | 0.67335 | 5.591
2024-12-09 | 19:56 | Data | 0 | 33.216 | 31.569 | 173.195 | 7.63 | 163.307 | 2171.91 | 25.89 | 48.165 | 6.38 | 1.308 | 4.295 | 8363.86 | 1.627 | 97.8 | 76.6 | 1412 | 24.08 | 5436.5 | 2746.6 | 2696.1 | 3973.7 | 1203.2 | 0.67344 | 5.603
2024-12-09 | 19:56 | Data | 0 | 32.967 | 31.555 | 173.15 | 7.63 | 163.217 | 2172.81 | 25.9 | 48.346 | 6.38 | 1.309 | 4.295 | 8372.9 | 1.533 | 97.8 | 76.6 | 1412 | 24.13 | 5442.4 | 2770.5 | 2721.3 | 4006.6 | 1203.2 | 0.67352 | 5.604
2024-12-09 | 19:56 | Data | 0 | 33.358 | 31.366 | 173.24 | 7.63 | 163.262 | 2171.91 | 25.89 | 48.255 | 6.38 | 1.299 | 4.288 | 8359.34 | 1.924 | 97.8 | 76.7 | 1412 | 24.08 | 5433.6 | 2752 | 2713.4 | 3989.2 | 1203.2 | 0.67259 | 5.588
2024-12-09 | 19:56 | Data | 0 | 33.574 | 31.961 | 173.24 | 7.63 | 163.217 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.296 | 4.271 | 8359.34 | 1.836 | 97.8 | 76.7 | 1411 | 24.04 | 5433.6 | 2764.4 | 2702.6 | 3986.2 | 1203.2 | 0.67639 | 5.567
2024-12-09 | 19:56 | Data | 0 | 33.311 | 31.772 | 173.331 | 7.63 | 163.352 | 2169.2 | 25.89 | 48.165 | 6.38 | 1.305 | 4.303 | 8377.43 | 1.425 | 97.8 | 76.7 | 1410 | 24.13 | 5445.3 | 2767.7 | 2702.8 | 3994 | 1203.2 | 0.67568 | 5.608
2024-12-09 | 19:56 | Data | 0 | 33.642 | 31.583 | 173.195 | 7.63 | 163.262 | 2172.81 | 25.89 | 48.165 | 6.38 | 1.31 | 4.333 | 8350.29 | 1.755 | 97.8 | 76.8 | 1412 | 24.08 | 5427.7 | 2766.7 | 2698.6 | 3970.4 | 1203.2 | 0.67479 | 5.644
2024-12-09 | 19:56 | Data | 0 | 33.567 | 31.799 | 173.331 | 7.63 | 163.262 | 2172.81 | 25.89 | 48.165 | 6.38 | 1.3 | 4.32 | 8350.29 | 1.836 | 97.8 | 76.9 | 1412 | 24.08 | 5427.7 | 2770.2 | 2703 | 3995.6 | 1203.2 | 0.67576 | 5.619
2024-12-09 | 19:56 | Data | 0 | 33.183 | 31.353 | 173.06 | 7.63 | 163.217 | 2172.81 | 25.9 | 48.165 | 6.38 | 1.311 | 4.312 | 8354.81 | 1.816 | 97.8 | 76.7 | 1412 | 24.04 | 5430.6 | 2734.9 | 2698.2 | 3966.2 | 1203.2 | 0.67123 | 5.623
2024-12-09 | 19:56 | Data | 0 | 33.297 | 31.515 | 173.195 | 7.63 | 163.262 | 2175.52 | 25.89 | 48.165 | 6.38 | 1.311 | 4.304 | 8359.34 | 2.032 | 97.8 | 76.6 | 1414 | 24.04 | 5433.6 | 2779.9 | 2698.8 | 3996.1 | 1203.2 | 0.67799 | 5.616
2024-12-09 | 19:56 | Data | 0 | 33.797 | 31.812 | 173.467 | 7.62 | 163.307 | 2175.52 | 25.89 | 48.165 | 6.39 | 1.3 | 4.316 | 8354.81 | 1.843 | 97.8 | 76.9 | 1414 | 24.04 | 5430.6 | 2744.2 | 2713.5 | 3983.3 | 1203.2 | 0.67053 | 5.616
2024-12-09 | 19:56 | Data | 0 | 33.412 | 31.468 | 173.195 | 7.62 | 163.262 | 2172.81 | 25.89 | 48.165 | 6.38 | 1.295 | 4.331 | 8359.34 | 1.816 | 97.8 | 77 | 1412 | 24.08 | 5433.6 | 2756 | 2705.1 | 3979 | 1203.2 | 0.67677 | 5.626
2024-12-09 | 19:56 | Data | 0 | 33.297 | 31.562 | 173.06 | 7.63 | 163.217 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.303 | 4.289 | 8359.34 | 1.803 | 97.8 | 76.7 | 1411 | 24.04 | 5433.6 | 2745.4 | 2720.7 | 3985.6 | 1203.2 | 0.67183 | 5.592
2024-12-09 | 19:56 | Data | 0 | 33.405 | 31.569 | 173.15 | 7.63 | 163.217 | 2166.49 | 25.89 | 48.165 | 6.38 | 1.312 | 4.323 | 8377.43 | 1.728 | 97.8 | 76.7 | 1408 | 24.08 | 5445.3 | 2757.7 | 2695.3 | 3977.3 | 1203.2 | 0.67509 | 5.635
2024-12-09 | 19:56 | Data | 0 | 33.412 | 31.731 | 173.105 | 7.63 | 163.172 | 2166.49 | 25.89 | 48.075 | 6.37 | 1.301 | 4.317 | 8386.47 | 1.681 | 97.8 | 76.8 | 1408 | 24.08 | 5451.2 | 2756.2 | 2702.3 | 3980.3 | 1203.2 | 0.67446 | 5.618
2024-12-09 | 19:57 | Data | 0 | 33.608 | 31.893 | 173.331 | 7.63 | 163.307 | 2166.49 | 25.9 | 48.075 | 6.38 | 1.296 | 4.299 | 8368.38 | 1.742 | 97.8 | 76.8 | 1408 | 24.08 | 5439.4 | 2766.2 | 2692.2 | 3971.8 | 1203.2 | 0.67826 | 5.596
2024-12-09 | 19:57 | Data | 0 | 33.196 | 31.569 | 173.24 | 7.63 | 163.262 | 2169.2 | 25.9 | 48.165 | 6.38 | 1.295 | 4.304 | 8372.9 | 1.62 | 97.8 | 76.9 | 1410 | 24.08 | 5442.4 | 2743.1 | 2705.5 | 3976.8 | 1203.2 | 0.67242 | 5.599
2024-12-09 | 19:57 | Data | 0 | 33.466 | 31.468 | 173.376 | 7.63 | 163.307 | 2169.2 | 25.89 | 48.165 | 6.38 | 1.301 | 4.32 | 8372.9 | 1.722 | 97.8 | 76.9 | 1411 | 24.13 | 5442.4 | 2737.8 | 2695.9 | 3964.8 | 1203.2 | 0.67287 | 5.62
2024-12-09 | 19:57 | Data | 0 | 33.412 | 31.684 | 173.24 | 7.63 | 163.307 | 2172.81 | 25.89 | 48.165 | 6.38 | 1.3 | 4.325 | 8363.86 | 1.62 | 97.8 | 76.9 | 1412 | 24.08 | 5436.5 | 2729.7 | 2707.7 | 3971.4 | 1203.2 | 0.67057 | 5.624
2024-12-09 | 19:57 | Data | 0 | 32.994 | 31.515 | 173.195 | 7.63 | 163.307 | 2171.01 | 25.89 | 47.984 | 6.38 | 1.295 | 4.325 | 8354.81 | 1.614 | 97.8 | 76.9 | 1411 | 23.86 | 5430.6 | 2748.4 | 2665.9 | 3957.6 | 1203.2 | 0.67371 | 5.621
2024-12-09 | 19:57 | Data | 0 | 33.527 | 31.576 | 173.195 | 7.63 | 163.262 | 2171.91 | 25.89 | 45.727 | 6.38 | 1.301 | 4.318 | 8363.86 | 1.627 | 97.9 | 76.9 | 1412 | 22.86 | 5436.5 | 2749.1 | 2680.9 | 3966.5 | 1203.2 | 0.67508 | 5.619
2024-12-09 | 19:57 | Data | 0 | 33.52 | 31.576 | 173.24 | 7.62 | 163.262 | 2172.81 | 25.89 | 48.075 | 6.38 | 1.3 | 4.301 | 8359.34 | 1.668 | 97.8 | 76.8 | 1412 | 24.08 | 5433.6 | 2757.6 | 2707.5 | 3988.4 | 1203.3 | 0.67486 | 5.6
2024-12-09 | 19:57 | Data | 0 | 33.405 | 31.67 | 173.195 | 7.63 | 163.307 | 2167.39 | 25.89 | 48.165 | 6.38 | 1.293 | 4.305 | 8372.9 | 1.762 | 97.8 | 76.9 | 1410 | 24.08 | 5442.4 | 2750 | 2687.5 | 3972.9 | 1203.3 | 0.67463 | 5.599
2024-12-09 | 19:57 | Data | 0 | 33.291 | 31.542 | 173.195 | 7.63 | 163.126 | 2171.01 | 25.89 | 48.075 | 6.38 | 1.294 | 4.308 | 8359.34 | 1.681 | 97.8 | 76.9 | 1411 | 24.04 | 5433.6 | 2757.9 | 2709.1 | 3994.7 | 1203.3 | 0.67355 | 5.602
2024-12-09 | 19:57 | Data | 0 | 33.405 | 31.684 | 173.195 | 7.63 | 163.126 | 2169.2 | 25.89 | 48.165 | 6.38 | 1.296 | 4.302 | 8359.34 | 1.668 | 97.8 | 76.9 | 1409 | 24.08 | 5433.6 | 2775.8 | 2701.9 | 3996.8 | 1203.3 | 0.67913 | 5.599
2024-12-09 | 19:57 | Data | 0 | 33.311 | 31.792 | 173.24 | 7.63 | 163.172 | 2165.58 | 25.89 | 48.165 | 6.38 | 1.301 | 4.315 | 8363.86 | 1.593 | 97.8 | 76.8 | 1408 | 24.08 | 5436.5 | 2748.6 | 2685.2 | 3967.5 | 1203.3 | 0.67532 | 5.617
2024-12-09 | 19:57 | Data | 0 | 33.412 | 31.346 | 173.105 | 7.63 | 163.172 | 2157.45 | 25.89 | 48.165 | 6.38 | 1.311 | 4.309 | 8345.77 | 1.789 | 97.8 | 76.7 | 1404 | 24.08 | 5424.8 | 2753 | 2675.6 | 3962.1 | 1203.3 | 0.67671 | 5.621
2024-12-09 | 19:57 | Data | 0 | 33.412 | 31.569 | 173.195 | 7.63 | 163.172 | 2161.06 | 25.89 | 48.436 | 6.38 | 1.294 | 4.314 | 8332.2 | 1.843 | 97.8 | 76.9 | 1405 | 24.22 | 5415.9 | 2744.7 | 2701.9 | 3979 | 1203.3 | 0.67444 | 5.609
2024-12-09 | 19:57 | Data | 0 | 33.642 | 31.589 | 173.195 | 7.63 | 163.307 | 2158.35 | 25.9 | 48.165 | 6.38 | 1.292 | 4.323 | 8336.72 | 1.904 | 97.8 | 77 | 1403 | 24.08 | 5418.9 | 2773.4 | 2708.6 | 3994 | 1203.3 | 0.67751 | 5.614
2024-12-09 | 19:57 | Data | 0 | 33.412 | 31.454 | 173.24 | 7.63 | 163.262 | 2158.35 | 25.9 | 48.165 | 6.38 | 1.31 | 4.313 | 8332.2 | 1.83 | 97.8 | 76.7 | 1403 | 24.08 | 5415.9 | 2751.5 | 2692.8 | 3971.4 | 1203.3 | 0.67511 | 5.623
2024-12-09 | 19:57 | Data | 0 | 33.027 | 31.515 | 173.06 | 7.63 | 163.172 | 2155.64 | 25.89 | 48.165 | 6.38 | 1.295 | 4.3 | 8336.72 | 1.789 | 97.8 | 76.9 | 1401 | 24.08 | 5418.9 | 2758.2 | 2708.1 | 3988.8 | 1203.3 | 0.674 | 5.595
2024-12-09 | 19:57 | Data | 0 | 33.412 | 31.569 | 173.06 | 7.62 | 163.217 | 2156.54 | 25.89 | 48.165 | 6.38 | 1.294 | 4.275 | 8318.64 | 1.843 | 97.8 | 76.8 | 1402 | 24.04 | 5407.1 | 2755.4 | 2700.1 | 3977.5 | 1203.3 | 0.67501 | 5.569
2024-12-09 | 19:57 | Data | 0 | 33.412 | 31.576 | 173.15 | 7.63 | 163.262 | 2158.35 | 25.89 | 48.165 | 6.38 | 1.311 | 4.275 | 8332.2 | 1.816 | 97.8 | 76.5 | 1404 | 24.08 | 5415.9 | 2756.3 | 2707.3 | 3985 | 1203.3 | 0.6747 | 5.586
2024-12-09 | 19:58 | Data | 0 | 33.405 | 31.596 | 173.195 | 7.63 | 163.262 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.302 | 4.314 | 8314.11 | 1.614 | 97.8 | 76.8 | 1406 | 24.08 | 5404.2 | 2778.5 | 2707.4 | 4000.5 | 1203.3 | 0.679 | 5.617
2024-12-09 | 19:58 | Data | 0 | 33.358 | 31.562 | 173.15 | 7.63 | 163.172 | 2163.77 | 25.89 | 47.984 | 6.38 | 1.297 | 4.33 | 8318.64 | 1.843 | 97.8 | 76.9 | 1406 | 23.99 | 5407.1 | 2771.4 | 2692.7 | 3982.9 | 1203.3 | 0.67983 | 5.626
2024-12-09 | 19:58 | Data | 0 | 33.581 | 31.994 | 173.24 | 7.62 | 163.217 | 2163.77 | 25.89 | 48.075 | 6.38 | 1.295 | 4.322 | 8332.2 | 1.668 | 97.8 | 76.9 | 1406 | 24.04 | 5415.9 | 2788.6 | 2708.2 | 4006.2 | 1203.3 | 0.68009 | 5.618
2024-12-09 | 19:58 | Data | 0 | 33.392 | 31.569 | 173.24 | 7.63 | 163.172 | 2163.77 | 25.89 | 47.984 | 6.38 | 1.296 | 4.304 | 8332.2 | 1.843 | 97.8 | 76.9 | 1406 | 23.99 | 5415.9 | 2764.8 | 2699.6 | 3986.4 | 1203.3 | 0.67707 | 5.6
2024-12-09 | 19:58 | Data | 0 | 33.358 | 31.677 | 173.421 | 7.63 | 163.307 | 2159.26 | 25.89 | 48.075 | 6.38 | 1.297 | 4.292 | 8336.72 | 1.627 | 97.8 | 76.8 | 1404 | 24.08 | 5418.9 | 2752.2 | 2679.9 | 3961.9 | 1203.3 | 0.67692 | 5.589
2024-12-09 | 19:58 | Data | 0 | 33.473 | 31.596 | 173.195 | 7.62 | 163.352 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.304 | 4.299 | 8345.77 | 1.627 | 97.8 | 76.7 | 1407 | 24.08 | 5424.8 | 2758.6 | 2684.8 | 3977.6 | 1203.3 | 0.67616 | 5.603
2024-12-09 | 19:58 | Data | 0 | 33.642 | 31.603 | 173.376 | 7.63 | 163.352 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.308 | 4.313 | 8332.2 | 1.735 | 97.8 | 76.7 | 1406 | 24.08 | 5415.9 | 2766.7 | 2682.9 | 3976.4 | 1203.3 | 0.67896 | 5.621
2024-12-09 | 19:58 | Data | 0 | 33.183 | 31.569 | 173.195 | 7.62 | 163.262 | 2166.49 | 25.89 | 48.255 | 6.38 | 1.304 | 4.315 | 8332.2 | 1.614 | 97.8 | 76.8 | 1408 | 24.08 | 5415.9 | 2763.9 | 2689.9 | 3986 | 1203.3 | 0.67648 | 5.619
2024-12-09 | 19:58 | Data | 0 | 33.203 | 31.393 | 173.24 | 7.63 | 163.217 | 2166.49 | 25.9 | 48.075 | 6.38 | 1.301 | 4.291 | 8341.25 | 1.614 | 97.8 | 76.7 | 1408 | 24.04 | 5421.8 | 2775 | 2666.8 | 3973 | 1203.3 | 0.68124 | 5.592
2024-12-09 | 19:58 | Data | 0 | 33.696 | 31.657 | 173.331 | 7.63 | 163.352 | 2165.58 | 25.9 | 48.165 | 6.38 | 1.305 | 4.301 | 8336.72 | 1.755 | 97.8 | 76.7 | 1408 | 24.08 | 5418.9 | 2743.2 | 2704.8 | 3972.7 | 1203.3 | 0.67018 | 5.606
2024-12-09 | 19:58 | Data | 0 | 33.696 | 31.603 | 173.331 | 7.63 | 163.307 | 2166.49 | 25.89 | 48.075 | 6.38 | 1.304 | 4.301 | 8341.25 | 1.654 | 97.8 | 76.7 | 1408 | 24.08 | 5421.8 | 2766.5 | 2707.7 | 3993.8 | 1203.3 | 0.67602 | 5.605
2024-12-09 | 19:58 | Data | 0 | 33.216 | 31.569 | 173.467 | 7.63 | 163.262 | 2167.39 | 25.89 | 48.165 | 6.38 | 1.303 | 4.284 | 8350.29 | 1.62 | 97.8 | 76.7 | 1409 | 24.08 | 5427.7 | 2736.7 | 2717.5 | 3978.9 | 1203.3 | 0.67071 | 5.587
2024-12-09 | 19:58 | Data | 0 | 33.608 | 31.61 | 173.24 | 7.63 | 163.443 | 2159.26 | 25.89 | 48.165 | 6.38 | 1.305 | 4.307 | 8341.25 | 1.911 | 97.8 | 76.7 | 1404 | 24.08 | 5421.8 | 2756.7 | 2662.2 | 3957.9 | 1203.3 | 0.67833 | 5.612
2024-12-09 | 19:58 | Data | 0 | 33.088 | 31.731 | 173.24 | 7.63 | 163.217 | 2171.01 | 25.89 | 48.075 | 6.38 | 1.3 | 4.32 | 8345.77 | 1.728 | 97.8 | 76.9 | 1411 | 24.04 | 5424.8 | 2772.4 | 2666.9 | 3972.5 | 1203.3 | 0.6818 | 5.619
2024-12-09 | 19:58 | Data | 0 | 33.196 | 31.657 | 173.24 | 7.63 | 163.217 | 2171.91 | 25.89 | 48.165 | 6.38 | 1.305 | 4.3 | 8359.34 | 1.782 | 97.8 | 76.7 | 1412 | 24.08 | 5433.6 | 2767.4 | 2669 | 3970.2 | 1203.3 | 0.68003 | 5.606
2024-12-09 | 19:58 | Data | 0 | 33.837 | 31.826 | 173.376 | 7.63 | 163.307 | 2177.33 | 25.89 | 48.075 | 6.38 | 1.301 | 4.316 | 8359.34 | 1.701 | 97.8 | 76.8 | 1415 | 24.08 | 5433.6 | 2773.4 | 2679.7 | 3971.7 | 1203.3 | 0.68287 | 5.617
2024-12-09 | 19:58 | Data | 0 | 33.48 | 31.583 | 173.331 | 7.63 | 163.262 | 2177.33 | 25.89 | 48.165 | 6.38 | 1.302 | 4.323 | 8359.34 | 1.701 | 97.8 | 76.8 | 1415 | 24.08 | 5433.6 | 2759.6 | 2676.6 | 3966.2 | 1203.3 | 0.68007 | 5.626
2024-12-09 | 19:58 | Data | 0 | 33.324 | 31.373 | 173.15 | 7.62 | 163.307 | 2180.95 | 25.89 | 48.075 | 6.38 | 1.302 | 4.298 | 8341.25 | 1.776 | 97.8 | 76.7 | 1418 | 24.04 | 5421.8 | 2784.9 | 2671.3 | 3976.2 | 1203.3 | 0.67698 | 5.6
2024-12-09 | 19:59 | Data | 0 | 33.412 | 31.61 | 173.24 | 7.63 | 163.217 | 2182.75 | 25.89 | 48.075 | 6.38 | 1.304 | 4.295 | 8345.77 | 1.803 | 97.8 | 76.7 | 1419 | 24.04 | 5424.8 | 2750 | 2673.4 | 3958.5 | 1203.3 | 0.67923 | 5.599
2024-12-09 | 19:59 | Data | 0 | 33.257 | 31.576 | 173.331 | 7.63 | 163.307 | 2182.75 | 25.89 | 48.255 | 6.38 | 1.305 | 4.306 | 8345.77 | 1.62 | 97.8 | 76.7 | 1419 | 24.08 | 5424.8 | 2765.2 | 2691.7 | 3980.6 | 1203.3 | 0.67905 | 5.612
2024-12-09 | 19:59 | Data | 0 | 33.635 | 31.805 | 173.24 | 7.63 | 163.262 | 2183.66 | 25.89 | 48.075 | 6.38 | 1.301 | 4.317 | 8350.29 | 1.816 | 97.8 | 76.8 | 1419 | 24.04 | 5427.7 | 2756.6 | 2679.5 | 3967.4 | 1203.3 | 0.67824 | 5.618
2024-12-09 | 19:59 | Data | 0 | 33.642 | 31.907 | 173.421 | 7.62 | 163.307 | 2182.75 | 25.89 | 47.894 | 6.38 | 1.301 | 4.313 | 8372.9 | 1.641 | 97.8 | 76.8 | 1419 | 23.95 | 5442.4 | 2728.2 | 2701.2 | 3974.3 | 1203.3 | 0.67385 | 5.615
2024-12-09 | 19:59 | Data | 0 | 33.27 | 31.36 | 173.376 | 7.63 | 163.352 | 2182.75 | 25.89 | 48.165 | 6.38 | 1.31 | 4.307 | 8363.86 | 1.661 | 97.8 | 76.7 | 1419 | 24.08 | 5436.5 | 1664.3 | 2088.8 | 2682.6 | 1203.3 | 0.6179 | 5.618
2024-12-09 | 19:59 | Data | 0 | 33.615 | 31.799 | 173.421 | 7.63 | 163.443 | 2182.75 | 25.89 | 48.165 | 6.38 | 1.309 | 4.324 | 8359.34 | 1.884 | 97.8 | 76.8 | 1419 | 24.08 | 5433.6 | 1670.3 | 2094.4 | 2690.1 | 1203.3 | 0.61879 | 5.633
2024-12-09 | 19:59 | Data | 0 | 33.385 | 31.474 | 173.331 | 7.63 | 163.352 | 2184.56 | 25.89 | 48.075 | 6.38 | 1.306 | 4.33 | 8359.34 | 1.674 | 97.8 | 76.8 | 1420 | 24.08 | 5433.6 | 1688.4 | 2096.7 | 2705.3 | 1203.3 | 0.62168 | 5.637
2024-12-09 | 19:59 | Data | 0 | 33.412 | 31.596 | 173.195 | 7.63 | 163.262 | 2186.37 | 25.89 | 48.075 | 6.38 | 1.299 | 4.312 | 8359.34 | 1.796 | 97.8 | 76.9 | 1420 | 24.04 | 5433.6 | 1659.8 | 2096.7 | 2687.3 | 1203.3 | 0.62102 | 5.61
2024-12-09 | 19:59 | Data | 0 | 33.358 | 31.569 | 173.15 | 7.63 | 163.262 | 2179.14 | 25.89 | 48.255 | 6.38 | 1.311 | 4.304 | 8359.34 | 1.83 | 97.8 | 76.6 | 1416 | 24.08 | 5433.6 | 1674.7 | 2098.8 | 2697.3 | 1203.3 | 0.619 | 5.615
2024-12-09 | 19:59 | Data | 0 | 33.412 | 31.576 | 173.331 | 7.63 | 163.307 | 2175.52 | 25.89 | 48.075 | 6.38 | 1.31 | 4.291 | 8363.86 | 1.836 | 97.8 | 76.6 | 1414 | 24.08 | 5436.5 | 1679.1 | 2114.5 | 2712.3 | 1203.3 | 0.61656 | 5.6
2024-12-09 | 19:59 | Data | 0 | 33.304 | 31.461 | 173.195 | 7.63 | 163.262 | 2180.95 | 25.89 | 48.165 | 6.38 | 1.3 | 4.305 | 8332.2 | 1.647 | 97.8 | 76.8 | 1418 | 24.08 | 5415.9 | 1665 | 2106.6 | 2700.6 | 1203.3 | 0.61383 | 5.605
2024-12-09 | 19:59 | Data | 0 | 33.358 | 31.792 | 173.376 | 7.63 | 163.352 | 2180.95 | 25.89 | 48.165 | 6.38 | 1.299 | 4.324 | 8318.64 | 1.715 | 97.8 | 76.9 | 1418 | 24.08 | 5407.1 | 1673.2 | 2115 | 2709.7 | 1203.3 | 0.61464 | 5.623
2024-12-09 | 19:59 | Data | 0 | 33.216 | 31.684 | 173.376 | 7.63 | 163.352 | 2180.04 | 25.89 | 48.075 | 6.38 | 1.299 | 4.313 | 8318.64 | 1.634 | 97.8 | 76.9 | 1418 | 24.04 | 5407.1 | 1673.5 | 2119.4 | 2713.1 | 1203.4 | 0.61388 | 5.611
2024-12-09 | 19:59 | Data | 0 | 33.311 | 31.772 | 173.376 | 7.62 | 163.352 | 2180.04 | 25.89 | 47.894 | 6.38 | 1.301 | 4.317 | 8314.11 | 1.742 | 97.8 | 76.8 | 1417 | 23.99 | 5404.2 | 1663.5 | 2090.8 | 2678.1 | 1203.4 | 0.61492 | 5.619
2024-12-09 | 19:59 | Data | 0 | 33.628 | 31.799 | 173.376 | 7.62 | 163.352 | 2180.95 | 25.89 | 47.894 | 6.38 | 1.301 | 4.298 | 8305.07 | 1.83 | 97.8 | 76.8 | 1417 | 23.95 | 5398.3 | 1685.3 | 2078.4 | 2690.4 | 1203.4 | 0.62276 | 5.598
2024-12-09 | 19:59 | Data | 0 | 33.358 | 31.569 | 173.195 | 7.62 | 163.217 | 2182.75 | 25.89 | 47.894 | 6.38 | 1.301 | 4.312 | 8332.2 | 1.836 | 97.8 | 76.8 | 1419 | 23.9 | 5415.9 | 1667.8 | 2113.7 | 2705.4 | 1203.4 | 0.61389 | 5.613
2024-12-09 | 19:59 | Data | 0 | 33.412 | 31.576 | 173.331 | 7.62 | 163.262 | 2186.37 | 25.9 | 47.894 | 6.38 | 1.309 | 4.314 | 8318.64 | 1.816 | 97.8 | 76.7 | 1421 | 23.9 | 5407.1 | 1672.3 | 2110.4 | 2702.1 | 1203.4 | 0.61627 | 5.623
2024-12-09 | 20:00 | Data | 0 | 33.183 | 31.569 | 173.24 | 7.63 | 163.307 | 2180.04 | 25.89 | 47.894 | 6.38 | 1.31 | 4.289 | 8332.2 | 1.728 | 97.8 | 76.6 | 1418 | 23.9 | 5415.9 | 1671 | 2089.7 | 2688 | 1203.4 | 0.61912 | 5.598
2024-12-09 | 20:00 | Data | 0 | 33.297 | 31.569 | 173.24 | 7.63 | 163.262 | 2177.33 | 25.89 | 47.984 | 6.38 | 1.31 | 4.295 | 8332.2 | 1.668 | 97.8 | 76.6 | 1415 | 23.99 | 5415.9 | 1673.5 | 2121.2 | 2717.6 | 1203.4 | 0.61582 | 5.604
2024-12-09 | 20:00 | Data | 0 | 33.412 | 31.745 | 173.24 | 7.63 | 163.307 | 2175.52 | 25.89 | 47.804 | 6.38 | 1.307 | 4.292 | 8300.55 | 1.728 | 97.8 | 76.7 | 1414 | 23.9 | 5395.4 | 1669 | 2137.2 | 2723.6 | 1203.4 | 0.61042 | 5.6
2024-12-09 | 20:00 | Data | 0 | 33.243 | 31.549 | 173.331 | 7.63 | 163.262 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.311 | 4.312 | 8318.64 | 1.708 | 97.8 | 76.7 | 1414 | 23.9 | 5407.1 | 1663.2 | 2123.4 | 2710.6 | 1203.4 | 0.61592 | 5.624
2024-12-09 | 20:00 | Data | 0 | 33.297 | 31.454 | 173.15 | 7.63 | 163.307 | 2172.81 | 25.89 | 47.804 | 6.38 | 1.301 | 4.337 | 8318.64 | 1.742 | 97.8 | 76.9 | 1412 | 23.95 | 5407.1 | 1664.7 | 2117.6 | 2705.8 | 1203.4 | 0.60943 | 5.638
2024-12-09 | 20:00 | Data | 0 | 33.48 | 31.583 | 173.331 | 7.63 | 163.262 | 2172.81 | 25.89 | 47.894 | 6.38 | 1.308 | 4.317 | 8318.64 | 1.688 | 97.8 | 76.8 | 1412 | 23.95 | 5407.1 | 1685 | 2117.9 | 2721.4 | 1203.4 | 0.61683 | 5.625
2024-12-09 | 20:00 | Data | 0 | 33.196 | 31.684 | 173.15 | 7.63 | 163.217 | 2172.81 | 25.89 | 47.894 | 6.38 | 1.294 | 4.276 | 8318.64 | 1.62 | 97.8 | 76.8 | 1412 | 23.95 | 5407.1 | 1670.2 | 2108.2 | 2710.4 | 1203.4 | 0.6142 | 5.571
2024-12-09 | 20:00 | Data | 0 | 33.5 | 31.967 | 173.331 | 7.63 | 163.352 | 2170.1 | 25.89 | 47.804 | 6.38 | 1.291 | 4.282 | 8314.11 | 1.884 | 97.8 | 76.8 | 1411 | 23.95 | 5404.2 | 1640.2 | 2067.9 | 2654 | 1203.4 | 0.61476 | 5.572
2024-12-09 | 20:00 | Data | 0 | 33.21 | 31.542 | 173.15 | 7.63 | 163.262 | 2171.91 | 25.89 | 47.894 | 6.38 | 1.301 | 4.304 | 8314.11 | 1.722 | 97.8 | 76.8 | 1412 | 23.95 | 5404.2 | 1684.8 | 2075.9 | 2684.9 | 1203.4 | 0.62516 | 5.604
2024-12-09 | 20:00 | Data | 0 | 33.196 | 31.569 | 173.15 | 7.62 | 163.307 | 2171.91 | 25.89 | 47.894 | 6.38 | 1.309 | 4.289 | 8323.16 | 1.735 | 97.8 | 76.6 | 1412 | 23.95 | 5410.1 | 1667.6 | 2081.7 | 2679.2 | 1203.4 | 0.62135 | 5.599
2024-12-09 | 20:00 | Data | 0 | 33.405 | 31.569 | 173.24 | 7.63 | 163.217 | 2167.39 | 25.89 | 47.894 | 6.38 | 1.304 | 4.285 | 8318.64 | 1.668 | 97.8 | 76.7 | 1408 | 23.95 | 5407.1 | 1676.5 | 2083.7 | 2688.3 | 1203.4 | 0.62034 | 5.588
2024-12-09 | 20:00 | Data | 0 | 33.196 | 31.569 | 173.105 | 7.63 | 163.217 | 2163.77 | 25.89 | 47.894 | 6.38 | 1.295 | 4.314 | 8332.2 | 1.62 | 97.8 | 76.9 | 1407 | 23.95 | 5415.9 | 1670.9 | 2073.1 | 2674.2 | 1203.4 | 0.62254 | 5.61
2024-12-09 | 20:00 | Data | 0 | 33.183 | 31.583 | 173.15 | 7.62 | 163.172 | 2166.49 | 25.89 | 47.894 | 6.38 | 1.302 | 4.305 | 8341.25 | 1.789 | 97.8 | 76.8 | 1408 | 23.95 | 5421.8 | 1644.4 | 2079.4 | 2669.1 | 1203.4 | 0.61647 | 5.608
2024-12-09 | 20:00 | Data | 0 | 33.399 | 31.583 | 173.331 | 7.63 | 163.307 | 2166.49 | 25.89 | 47.894 | 6.38 | 1.304 | 4.297 | 8336.72 | 1.816 | 97.8 | 76.7 | 1408 | 23.95 | 5418.9 | 1662 | 2086.9 | 2679.9 | 1203.4 | 0.61848 | 5.601
2024-12-09 | 20:00 | Data | 0 | 33.412 | 31.569 | 173.376 | 7.62 | 163.262 | 2165.58 | 25.89 | 47.894 | 6.38 | 1.307 | 4.313 | 8332.2 | 1.641 | 97.8 | 76.8 | 1408 | 23.95 | 5415.9 | 1670.7 | 2069.7 | 2673.4 | 1203.4 | 0.62265 | 5.619
2024-12-09 | 20:00 | Data | 0 | 33.196 | 31.542 | 173.24 | 7.63 | 163.262 | 2156.54 | 25.89 | 47.984 | 6.38 | 1.301 | 4.326 | 8336.72 | 1.674 | 97.8 | 76.9 | 1402 | 23.95 | 5418.9 | 1668.9 | 2084.9 | 2685.7 | 1203.4 | 0.61901 | 5.625
2024-12-09 | 20:00 | Data | 0 | 33.439 | 31.569 | 173.195 | 7.63 | 163.307 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.301 | 4.312 | 8332.2 | 1.641 | 97.8 | 76.8 | 1411 | 24.08 | 5415.9 | 1661.6 | 2092.1 | 2684.8 | 1203.4 | 0.6189 | 5.612
2024-12-09 | 20:00 | Data | 0 | 33.588 | 31.583 | 173.195 | 7.63 | 163.262 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.3 | 4.295 | 8363.86 | 1.89 | 97.8 | 76.8 | 1411 | 24.08 | 5436.5 | 1673.7 | 2080.9 | 2682.8 | 1203.4 | 0.62135 | 5.594
2024-12-09 | 20:01 | Data | 0 | 33.297 | 31.569 | 173.195 | 7.63 | 163.307 | 2169.2 | 25.89 | 47.984 | 6.38 | 1.303 | 4.295 | 8354.81 | 1.641 | 97.8 | 76.7 | 1410 | 23.99 | 5430.6 | 1660.5 | 2098.4 | 2685.7 | 1203.4 | 0.61674 | 5.599
2024-12-09 | 20:01 | Data | 0 | 33.142 | 31.528 | 173.24 | 7.62 | 163.217 | 2167.39 | 25.89 | 48.165 | 6.38 | 1.297 | 4.299 | 8359.34 | 1.782 | 97.8 | 76.8 | 1409 | 24.04 | 5433.6 | 1678.9 | 2102.8 | 2702.6 | 1203.4 | 0.61919 | 5.595
2024-12-09 | 20:01 | Data | 0 | 33.419 | 31.799 | 173.331 | 7.63 | 163.307 | 2171.91 | 25.89 | 48.075 | 6.39 | 1.297 | 4.292 | 8345.77 | 1.627 | 97.8 | 76.8 | 1412 | 24.08 | 5424.8 | 1672.3 | 2089.8 | 2688.7 | 1203.4 | 0.62054 | 5.589
2024-12-09 | 20:01 | Data | 0 | 33.358 | 31.616 | 173.24 | 7.63 | 163.217 | 2173.72 | 25.89 | 47.804 | 6.38 | 1.301 | 4.303 | 8345.77 | 1.789 | 97.8 | 76.8 | 1412 | 23.95 | 5424.8 | 1667.6 | 2102.3 | 2696.1 | 1203.4 | 0.62114 | 5.604
2024-12-09 | 20:01 | Data | 0 | 33.439 | 31.576 | 173.195 | 7.62 | 163.352 | 2175.52 | 25.89 | 48.255 | 6.38 | 1.301 | 4.302 | 8359.34 | 1.668 | 97.8 | 76.8 | 1414 | 24.13 | 5433.6 | 1692.2 | 2099 | 2689.4 | 1203.4 | 0.62214 | 5.601
2024-12-09 | 20:01 | Data | 0 | 33.068 | 31.555 | 173.06 | 7.62 | 163.172 | 2173.72 | 25.89 | 48.165 | 6.38 | 1.301 | 4.318 | 8341.25 | 1.782 | 97.8 | 76.9 | 1414 | 24.08 | 5421.8 | 1689.5 | 2072 | 2685.1 | 1203.4 | 0.6278 | 5.619
2024-12-09 | 20:01 | Data | 0 | 33.183 | 31.562 | 173.06 | 7.63 | 163.172 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.311 | 4.32 | 8354.81 | 1.641 | 97.8 | 76.7 | 1414 | 23.95 | 5430.6 | 1667.5 | 2082.8 | 2680.4 | 1203.4 | 0.62223 | 5.63
2024-12-09 | 20:01 | Data | 0 | 33.581 | 31.799 | 173.331 | 7.63 | 163.307 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.303 | 4.319 | 8363.86 | 1.816 | 97.8 | 76.8 | 1414 | 23.9 | 5436.5 | 1663.3 | 2102.2 | 2693.1 | 1203.4 | 0.61563 | 5.621
2024-12-09 | 20:01 | Data | 0 | 33.183 | 31.569 | 173.15 | 7.63 | 163.217 | 2173.72 | 25.9 | 48.165 | 6.38 | 1.307 | 4.323 | 8350.29 | 1.614 | 97.8 | 76.8 | 1413 | 24.08 | 5427.7 | 1666.7 | 2101.9 | 2693.4 | 1203.4 | 0.61659 | 5.628
2024-12-09 | 20:01 | Data | 0 | 33.513 | 31.623 | 173.24 | 7.63 | 163.262 | 2173.72 | 25.89 | 47.804 | 6.39 | 1.301 | 4.305 | 8372.9 | 1.742 | 97.8 | 76.8 | 1413 | 23.95 | 5442.4 | 1689.1 | 2095.8 | 2701.7 | 1203.4 | 0.62325 | 5.607
2024-12-09 | 20:01 | Data | 0 | 33.297 | 31.569 | 173.195 | 7.63 | 163.217 | 2174.62 | 25.89 | 47.894 | 6.38 | 1.3 | 4.3 | 8359.34 | 1.614 | 97.8 | 76.8 | 1413 | 23.95 | 5433.6 | 1671.5 | 2097.5 | 2695.6 | 1203.4 | 0.61721 | 5.6
2024-12-09 | 20:01 | Data | 0 | 33.183 | 31.562 | 173.105 | 7.62 | 163.172 | 2173.72 | 25.89 | 47.894 | 6.38 | 1.295 | 4.297 | 8363.86 | 1.62 | 97.8 | 76.8 | 1413 | 23.95 | 5436.5 | 1693.3 | 2103.6 | 2712.2 | 1203.4 | 0.62193 | 5.592
2024-12-09 | 20:01 | Data | 0 | 33.183 | 31.454 | 173.06 | 7.63 | 163.217 | 2172.81 | 25.89 | 47.894 | 6.38 | 1.301 | 4.298 | 8386.47 | 1.62 | 97.8 | 76.8 | 1412 | 23.95 | 5451.2 | 1692.4 | 2091.8 | 2702.2 | 1203.4 | 0.62213 | 5.6
2024-12-09 | 20:01 | Data | 0 | 33.412 | 31.684 | 173.195 | 7.62 | 163.307 | 2176.43 | 25.89 | 47.894 | 6.38 | 1.31 | 4.309 | 8359.34 | 1.728 | 97.8 | 76.7 | 1414 | 23.9 | 5433.6 | 1681 | 2095.2 | 2699.2 | 1203.4 | 0.62008 | 5.619
2024-12-09 | 20:01 | Data | 0 | 33.304 | 31.353 | 173.15 | 7.62 | 163.217 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.304 | 4.296 | 8377.43 | 1.796 | 97.8 | 76.7 | 1414 | 23.95 | 5445.3 | 1683.4 | 2108.3 | 2712.2 | 1203.4 | 0.6177 | 5.6
2024-12-09 | 20:01 | Data | 0 | 33.075 | 31.542 | 173.195 | 7.63 | 163.081 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.301 | 4.324 | 8372.9 | 1.641 | 97.8 | 76.9 | 1414 | 23.95 | 5442.4 | 1675.2 | 2085.4 | 2688.6 | 1203.4 | 0.62026 | 5.625
2024-12-09 | 20:01 | Data | 0 | 33.291 | 31.346 | 173.15 | 7.62 | 163.172 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.304 | 4.332 | 8359.34 | 1.85 | 97.8 | 76.9 | 1414 | 23.95 | 5433.6 | 1670.6 | 2093.1 | 2691.7 | 1203.4 | 0.61861 | 5.638
2024-12-09 | 20:02 | Data | 0 | 33.351 | 31.731 | 173.376 | 7.63 | 163.217 | 2178.24 | 25.89 | 48.075 | 6.38 | 1.308 | 4.304 | 8372.9 | 1.863 | 97.8 | 76.7 | 1415 | 24.13 | 5442.4 | 1669.1 | 2069.6 | 2670.8 | 1203.4 | 0.62311 | 5.612
2024-12-09 | 20:02 | Data | 0 | 32.994 | 31.555 | 173.06 | 7.63 | 163.172 | 2178.24 | 25.89 | 47.984 | 6.38 | 1.305 | 4.309 | 8363.86 | 1.56 | 97.8 | 76.8 | 1416 | 23.95 | 5436.5 | 1679.6 | 2083.2 | 2689 | 1203.4 | 0.62278 | 5.614
2024-12-09 | 20:02 | Data | 0 | 33.027 | 31.454 | 173.06 | 7.63 | 163.307 | 2174.62 | 25.89 | 47.894 | 6.38 | 1.302 | 4.309 | 8345.77 | 1.62 | 97.8 | 76.8 | 1414 | 23.95 | 5424.8 | 1656.1 | 2080.8 | 2679.6 | 1203.4 | 0.61988 | 5.611
2024-12-09 | 20:02 | Data | 0 | 33.183 | 31.515 | 173.105 | 7.63 | 163.217 | 2175.52 | 25.89 | 47.984 | 6.38 | 1.301 | 4.325 | 8345.77 | 1.668 | 97.8 | 76.9 | 1414 | 23.95 | 5424.8 | 1658.2 | 2073.4 | 2668.1 | 1203.4 | 0.61913 | 5.626
2024-12-09 | 20:02 | Data | 0 | 33.237 | 31.346 | 173.105 | 7.63 | 163.172 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.293 | 4.323 | 8359.34 | 1.843 | 97.8 | 77 | 1411 | 23.9 | 5433.6 | 1646.3 | 2071.9 | 2660.4 | 1203.4 | 0.61652 | 5.617
2024-12-09 | 20:02 | Data | 0 | 32.967 | 31.542 | 173.06 | 7.62 | 163.172 | 2170.1 | 25.9 | 47.894 | 6.38 | 1.307 | 4.301 | 8350.29 | 1.701 | 97.8 | 76.7 | 1411 | 23.95 | 5427.7 | 1669.7 | 2080.4 | 2678.9 | 1203.4 | 0.62113 | 5.608
2024-12-09 | 20:02 | Data | 0 | 33.183 | 31.562 | 173.15 | 7.63 | 163.081 | 2169.2 | 25.89 | 47.894 | 6.38 | 1.307 | 4.317 | 8363.86 | 1.627 | 97.8 | 76.8 | 1411 | 23.95 | 5436.5 | 1668.2 | 2091 | 2686.4 | 1203.4 | 0.61901 | 5.624
2024-12-09 | 20:02 | Data | 0 | 33.405 | 31.569 | 173.195 | 7.62 | 163.217 | 2170.1 | 25.89 | 47.714 | 6.38 | 1.291 | 4.322 | 8359.34 | 1.843 | 97.8 | 77 | 1411 | 23.81 | 5433.6 | 2034.3 | 2920.3 | 3590.5 | 1203.4 | 0.59701 | 5.612
2024-12-09 | 20:02 | Data | 0 | 33.547 | 31.677 | 173.195 | 7.62 | 163.262 | 2166.49 | 25.89 | 47.804 | 6.38 | 1.301 | 4.316 | 8359.34 | 1.816 | 97.8 | 76.8 | 1408 | 23.95 | 5433.6 | 2772.2 | 2687.7 | 3984.8 | 1203.4 | 0.67878 | 5.617
2024-12-09 | 20:02 | Data | 0 | 33.297 | 31.366 | 173.105 | 7.63 | 163.217 | 2167.39 | 25.89 | 47.894 | 6.38 | 1.308 | 4.309 | 8359.34 | 1.782 | 97.8 | 76.7 | 1408 | 23.99 | 5433.6 | 2757.5 | 2682.1 | 3969.9 | 1203.4 | 0.67672 | 5.616
2024-12-09 | 20:02 | Data | 0 | 33.385 | 31.454 | 173.15 | 7.63 | 163.172 | 2166.49 | 25.89 | 48.165 | 6.38 | 1.299 | 4.323 | 8350.29 | 1.836 | 97.8 | 76.9 | 1408 | 24.08 | 5427.7 | 2740.9 | 2673 | 3961.7 | 1203.4 | 0.67365 | 5.622
2024-12-09 | 20:02 | Data | 0 | 33.304 | 31.785 | 173.24 | 7.63 | 163.217 | 2165.58 | 25.89 | 47.804 | 6.38 | 1.31 | 4.306 | 8345.77 | 1.62 | 97.8 | 76.7 | 1408 | 23.95 | 5424.8 | 2747.3 | 2698.1 | 3978.4 | 1203.4 | 0.6723 | 5.616
2024-12-09 | 20:02 | Data | 0 | 33.102 | 31.339 | 173.06 | 7.62 | 163.172 | 2169.2 | 25.89 | 47.894 | 6.38 | 1.31 | 4.315 | 8341.25 | 1.823 | 97.8 | 76.7 | 1411 | 23.9 | 5421.8 | 2762.2 | 2669.7 | 3966.8 | 1203.4 | 0.67923 | 5.624
2024-12-09 | 20:02 | Data | 0 | 33.196 | 31.555 | 173.105 | 7.63 | 163.217 | 2170.1 | 25.9 | 47.894 | 6.38 | 1.306 | 4.295 | 8341.25 | 1.641 | 97.8 | 76.7 | 1411 | 23.95 | 5421.8 | 2750.5 | 2691.7 | 3975.2 | 1203.4 | 0.67489 | 5.6
2024-12-09 | 20:02 | Data | 0 | 33.081 | 31.515 | 173.06 | 7.62 | 163.172 | 2169.2 | 25.89 | 47.984 | 6.38 | 1.301 | 4.27 | 8354.81 | 1.641 | 97.8 | 76.6 | 1411 | 23.99 | 5430.6 | 2762.7 | 2693.9 | 3982.6 | 1203.4 | 0.6773 | 5.572
2024-12-09 | 20:02 | Data | 0 | 33.183 | 31.454 | 173.15 | 7.63 | 163.217 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.291 | 4.286 | 8341.25 | 1.958 | 97.8 | 76.8 | 1415 | 23.95 | 5421.8 | 2736.4 | 2668.8 | 3955.4 | 1203.4 | 0.6751 | 5.578
2024-12-09 | 20:02 | Data | 0 | 33.142 | 31.427 | 173.24 | 7.62 | 163.172 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.296 | 4.319 | 8332.2 | 1.512 | 97.8 | 76.9 | 1411 | 23.95 | 5415.9 | 2767 | 2680.5 | 3979.4 | 1203.4 | 0.67821 | 5.614
2024-12-09 | 20:02 | Data | 0 | 33.52 | 31.785 | 173.15 | 7.63 | 163.172 | 2166.49 | 25.9 | 47.894 | 6.38 | 1.303 | 4.31 | 8336.72 | 1.843 | 97.8 | 76.8 | 1408 | 23.95 | 5418.9 | 2750.6 | 2678.7 | 3968.3 | 1203.5 | 0.67573 | 5.613
2024-12-09 | 20:03 | Data | 0 | 33.358 | 31.846 | 173.331 | 7.63 | 163.217 | 2165.58 | 25.89 | 47.804 | 6.38 | 1.311 | 4.303 | 8336.72 | 1.708 | 97.8 | 76.6 | 1408 | 23.9 | 5418.9 | 2759.3 | 2676.9 | 3968.1 | 1203.5 | 0.67824 | 5.615
2024-12-09 | 20:03 | Data | 0 | 33.183 | 31.542 | 173.014 | 7.63 | 163.126 | 2166.49 | 25.89 | 47.894 | 6.38 | 1.303 | 4.285 | 8318.64 | 1.668 | 97.8 | 76.7 | 1408 | 23.95 | 5407.1 | 2750.5 | 2681.3 | 3966.1 | 1203.5 | 0.67645 | 5.588
2024-12-09 | 20:03 | Data | 0 | 33.264 | 31.346 | 173.105 | 7.63 | 163.262 | 2164.68 | 25.89 | 47.894 | 6.38 | 1.293 | 4.313 | 8314.11 | 1.668 | 97.8 | 76.9 | 1407 | 23.95 | 5404.2 | 2751.6 | 2686.9 | 3972.4 | 1203.5 | 0.67542 | 5.606
2024-12-09 | 20:03 | Data | 0 | 33.075 | 31.562 | 173.06 | 7.62 | 163.126 | 2164.68 | 25.89 | 47.804 | 6.38 | 1.301 | 4.303 | 8318.64 | 1.789 | 97.8 | 76.8 | 1406 | 23.95 | 5407.1 | 2763.3 | 2679.2 | 3971.8 | 1203.5 | 0.67843 | 5.602
2024-12-09 | 20:03 | Data | 0 | 33.297 | 31.778 | 173.06 | 7.63 | 163.217 | 2163.77 | 25.88 | 47.894 | 6.38 | 1.299 | 4.324 | 8336.72 | 1.62 | 97.8 | 76.9 | 1406 | 23.95 | 5418.9 | 2741.2 | 2710.2 | 3983.6 | 1203.5 | 0.67042 | 5.622
2024-12-09 | 20:03 | Data | 0 | 33.621 | 31.596 | 173.331 | 7.62 | 163.217 | 2163.77 | 25.89 | 47.804 | 6.38 | 1.307 | 4.296 | 8318.64 | 1.762 | 97.8 | 76.7 | 1407 | 23.9 | 5407.1 | 2756.4 | 2716.1 | 3991.5 | 1203.5 | 0.67304 | 5.603
2024-12-09 | 20:03 | Data | 0 | 32.967 | 31.339 | 173.105 | 7.63 | 163.126 | 2165.58 | 25.89 | 47.894 | 6.38 | 1.299 | 4.304 | 8323.16 | 1.789 | 97.8 | 76.8 | 1408 | 23.95 | 5410.1 | 2770.7 | 2707.5 | 4000.3 | 1203.5 | 0.6746 | 5.602
2024-12-09 | 20:03 | Data | 0 | 33.351 | 31.353 | 173.15 | 7.63 | 163.262 | 2170.1 | 25.89 | 47.804 | 6.38 | 1.301 | 4.302 | 8305.07 | 1.641 | 97.8 | 76.8 | 1411 | 23.95 | 5398.3 | 2748.5 | 2701.2 | 3978.9 | 1203.5 | 0.67236 | 5.603
2024-12-09 | 20:03 | Data | 0 | 33.459 | 31.576 | 173.331 | 7.62 | 163.217 | 2170.1 | 25.89 | 47.984 | 6.38 | 1.303 | 4.304 | 8309.59 | 1.641 | 97.8 | 76.8 | 1411 | 23.95 | 5401.2 | 2764.9 | 2691.8 | 3981.5 | 1203.5 | 0.67663 | 5.606
2024-12-09 | 20:03 | Data | 0 | 33.183 | 31.542 | 173.195 | 7.62 | 163.172 | 2166.49 | 25.89 | 47.894 | 6.38 | 1.304 | 4.304 | 8305.07 | 1.668 | 97.8 | 76.8 | 1409 | 23.95 | 5398.3 | 2770.5 | 2693.9 | 3984.9 | 1203.5 | 0.67872 | 5.607
2024-12-09 | 20:03 | Data | 0 | 33.439 | 31.4 | 173.195 | 7.63 | 163.217 | 2166.49 | 25.89 | 47.894 | 6.38 | 1.299 | 4.288 | 8314.11 | 1.762 | 97.8 | 76.8 | 1408 | 23.95 | 5404.2 | 2762.1 | 2680.9 | 3970.6 | 1203.5 | 0.67836 | 5.587
2024-12-09 | 20:03 | Data | 0 | 33.075 | 31.339 | 173.014 | 7.62 | 163.081 | 2163.77 | 25.89 | 47.894 | 6.38 | 1.302 | 4.298 | 8314.11 | 1.634 | 97.8 | 76.8 | 1406 | 23.95 | 5404.2 | 2739.6 | 2703.3 | 3978.9 | 1203.5 | 0.67219 | 5.6
2024-12-09 | 20:03 | Data | 0 | 33.169 | 31.447 | 173.15 | 7.62 | 163.172 | 2163.77 | 25.9 | 47.894 | 6.38 | 1.3 | 4.321 | 8318.64 | 1.904 | 97.8 | 76.9 | 1406 | 23.95 | 5407.1 | 2747 | 2736.1 | 3993.1 | 1203.5 | 0.67157 | 5.621
2024-12-09 | 20:03 | Data | 0 | 32.96 | 31.339 | 172.969 | 7.63 | 163.126 | 2163.77 | 25.89 | 47.894 | 6.37 | 1.309 | 4.305 | 8305.07 | 1.789 | 97.8 | 76.7 | 1406 | 23.95 | 5398.3 | 2754.3 | 2715.3 | 3991.5 | 1203.5 | 0.67311 | 5.614
2024-12-09 | 20:03 | Data | 0 | 33.432 | 31.373 | 173.15 | 7.63 | 163.262 | 2163.77 | 25.89 | 47.894 | 6.38 | 1.308 | 4.308 | 8332.2 | 1.803 | 97.8 | 76.7 | 1407 | 23.95 | 5415.9 | 2749.2 | 2711.8 | 3987.4 | 1203.5 | 0.67117 | 5.615
2024-12-09 | 20:03 | Data | 0 | 33.081 | 31.515 | 173.105 | 7.63 | 163.172 | 2163.77 | 25.89 | 48.075 | 6.38 | 1.309 | 4.3 | 8336.72 | 1.533 | 97.8 | 76.7 | 1407 | 24.04 | 5418.9 | 2773.3 | 2721.1 | 4006.6 | 1203.5 | 0.67563 | 5.61
2024-12-09 | 20:03 | Data | 0 | 33.075 | 31.441 | 173.06 | 7.63 | 163.172 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.301 | 4.295 | 8314.11 | 1.843 | 97.8 | 76.8 | 1406 | 24.08 | 5404.2 | 2774.3 | 2717.3 | 4008.1 | 1203.5 | 0.67453 | 5.596
2024-12-09 | 20:03 | Data | 0 | 33.014 | 31.562 | 173.195 | 7.63 | 163.217 | 2164.68 | 25.89 | 48.165 | 6.38 | 1.293 | 4.298 | 8345.77 | 1.607 | 97.8 | 76.9 | 1406 | 24.08 | 5424.8 | 2758.8 | 2705.8 | 3988 | 1203.5 | 0.67537 | 5.592
2024-12-09 | 20:04 | Data | 0 | 33.304 | 31.677 | 173.195 | 7.62 | 163.307 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.301 | 4.299 | 8350.29 | 1.607 | 97.8 | 76.8 | 1406 | 24.08 | 5427.7 | 2783.5 | 2687.4 | 3988.4 | 1203.5 | 0.68039 | 5.599
2024-12-09 | 20:04 | Data | 0 | 33.183 | 31.589 | 173.195 | 7.63 | 163.172 | 2166.49 | 25.9 | 47.894 | 6.38 | 1.296 | 4.321 | 8341.25 | 1.668 | 97.8 | 76.9 | 1409 | 23.95 | 5421.8 | 2736.9 | 2698.8 | 3971.2 | 1203.5 | 0.6728 | 5.617
2024-12-09 | 20:04 | Data | 0 | 33.412 | 31.583 | 173.24 | 7.63 | 163.262 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.299 | 4.301 | 8359.34 | 1.83 | 97.8 | 76.8 | 1411 | 24.08 | 5433.6 | 2751.5 | 2677.9 | 3963.2 | 1203.5 | 0.67768 | 5.6
2024-12-09 | 20:04 | Data | 0 | 33.385 | 31.407 | 173.15 | 7.62 | 163.217 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.297 | 4.281 | 8359.34 | 1.958 | 97.8 | 76.7 | 1411 | 24.08 | 5433.6 | 2740.2 | 2677.4 | 3953.8 | 1203.5 | 0.67571 | 5.578
2024-12-09 | 20:04 | Data | 0 | 33.399 | 31.65 | 173.15 | 7.63 | 163.217 | 2170.1 | 25.89 | 48.255 | 6.38 | 1.307 | 4.301 | 8363.86 | 1.762 | 97.8 | 76.7 | 1411 | 24.08 | 5436.5 | 2774.7 | 2674.8 | 3971.4 | 1203.5 | 0.67539 | 5.609
2024-12-09 | 20:04 | Data | 0 | 33.095 | 31.319 | 173.15 | 7.63 | 163.217 | 2169.2 | 25.89 | 48.165 | 6.38 | 1.308 | 4.297 | 8345.77 | 1.688 | 97.8 | 76.7 | 1411 | 24.08 | 5424.8 | 2765.7 | 2668.4 | 3965.7 | 1203.5 | 0.6799 | 5.605
2024-12-09 | 20:04 | Data | 0 | 33.412 | 31.623 | 173.331 | 7.62 | 163.262 | 2171.01 | 25.89 | 48.075 | 6.38 | 1.293 | 4.283 | 8359.34 | 1.789 | 97.8 | 76.8 | 1411 | 24.04 | 5433.6 | 2757 | 2689.8 | 3974.2 | 1203.5 | 0.67938 | 5.576
2024-12-09 | 20:04 | Data | 0 | 33.284 | 31.562 | 173.105 | 7.62 | 163.172 | 2170.1 | 25.9 | 48.165 | 6.38 | 1.293 | 4.305 | 8350.29 | 1.836 | 97.8 | 76.9 | 1411 | 24.08 | 5427.7 | 2755.6 | 2690.6 | 3975.2 | 1203.5 | 0.67708 | 5.6
2024-12-09 | 20:04 | Data | 0 | 32.96 | 31.866 | 173.105 | 7.63 | 163.262 | 2170.1 | 25.89 | 48.165 | 6.37 | 1.295 | 4.303 | 8359.34 | 1.776 | 97.8 | 76.9 | 1411 | 24.08 | 5433.6 | 2754.4 | 2711.1 | 3991.8 | 1203.5 | 0.67441 | 5.598
2024-12-09 | 20:04 | Data | 0 | 32.987 | 31.454 | 173.105 | 7.63 | 163.217 | 2165.58 | 25.89 | 48.165 | 6.38 | 1.301 | 4.315 | 8359.34 | 1.614 | 97.8 | 76.8 | 1408 | 24.04 | 5433.6 | 2757.4 | 2721.9 | 4001.2 | 1203.5 | 0.67651 | 5.615
2024-12-09 | 20:04 | Data | 0 | 33.324 | 31.4 | 173.195 | 7.62 | 163.262 | 2167.39 | 25.89 | 48.165 | 6.38 | 1.303 | 4.29 | 8359.34 | 1.627 | 97.8 | 76.7 | 1408 | 24.08 | 5433.6 | 2749.2 | 2680.1 | 3966.6 | 1203.5 | 0.67634 | 5.593
2024-12-09 | 20:04 | Data | 0 | 33.142 | 31.569 | 173.06 | 7.63 | 163.172 | 2166.49 | 25.9 | 48.165 | 6.38 | 1.304 | 4.271 | 8363.86 | 1.803 | 97.8 | 76.6 | 1408 | 24.08 | 5436.5 | 2756.6 | 2698.6 | 3995.7 | 1203.5 | 0.67618 | 5.576
2024-12-09 | 20:04 | Data | 0 | 33.183 | 31.596 | 173.331 | 7.63 | 163.262 | 2169.2 | 25.89 | 48.165 | 6.38 | 1.31 | 4.268 | 8359.34 | 1.681 | 97.8 | 76.5 | 1411 | 24.08 | 5433.6 | 2721.5 | 2709.7 | 3968.4 | 1203.5 | 0.66947 | 5.578
2024-12-09 | 20:04 | Data | 0 | 33.183 | 31.562 | 173.15 | 7.63 | 163.172 | 2170.1 | 25.89 | 48.075 | 6.38 | 1.313 | 4.317 | 8359.34 | 1.742 | 97.8 | 76.7 | 1410 | 24.08 | 5433.6 | 2761.7 | 2707.3 | 3996.1 | 1203.5 | 0.67438 | 5.63
2024-12-09 | 20:04 | Data | 0 | 33.412 | 31.366 | 173.105 | 7.63 | 163.172 | 2170.1 | 25.89 | 47.804 | 6.38 | 1.297 | 4.295 | 8345.77 | 1.728 | 97.8 | 76.8 | 1411 | 23.95 | 5424.8 | 2765.3 | 2688.8 | 3984.1 | 1203.5 | 0.67584 | 5.593
2024-12-09 | 20:04 | Data | 0 | 33.608 | 31.623 | 173.421 | 7.62 | 163.262 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.291 | 4.299 | 8350.29 | 1.701 | 97.8 | 76.9 | 1411 | 23.95 | 5427.7 | 2760.1 | 2694.5 | 3984.4 | 1203.5 | 0.67603 | 5.591
2024-12-09 | 20:04 | Data | 0 | 32.987 | 31.454 | 173.15 | 7.62 | 163.217 | 2165.58 | 25.89 | 47.894 | 6.38 | 1.306 | 4.275 | 8332.2 | 1.506 | 97.8 | 76.6 | 1407 | 23.99 | 5415.9 | 2751.4 | 2698.3 | 3979.1 | 1203.5 | 0.67451 | 5.581
2024-12-09 | 20:04 | Data | 0 | 33.615 | 31.373 | 173.15 | 7.62 | 163.262 | 2165.58 | 25.89 | 47.894 | 6.38 | 1.3 | 4.296 | 8336.72 | 1.917 | 97.8 | 76.8 | 1408 | 23.99 | 5418.9 | 2754.2 | 2696.1 | 3974.2 | 1203.5 | 0.67553 | 5.597
2024-12-09 | 20:05 | Data | 0 | 33.196 | 31.528 | 173.15 | 7.62 | 163.262 | 2163.77 | 25.9 | 47.894 | 6.38 | 1.293 | 4.313 | 8332.2 | 1.654 | 97.8 | 76.9 | 1406 | 23.95 | 5415.9 | 2749.6 | 2717.2 | 3990.3 | 1203.5 | 0.67307 | 5.606
2024-12-09 | 20:05 | Data | 0 | 33.189 | 31.542 | 173.105 | 7.62 | 163.217 | 2164.68 | 25.89 | 47.894 | 6.38 | 1.299 | 4.313 | 8332.2 | 1.661 | 97.8 | 76.8 | 1406 | 23.95 | 5415.9 | 2740.5 | 2700.1 | 3974.9 | 1203.5 | 0.67172 | 5.612
2024-12-09 | 20:05 | Data | 0 | 33.216 | 31.745 | 173.105 | 7.63 | 163.262 | 2164.68 | 25.9 | 47.894 | 6.38 | 1.3 | 4.32 | 8300.55 | 1.614 | 97.8 | 76.9 | 1407 | 23.95 | 5395.4 | 2750.6 | 2703.2 | 3981.6 | 1203.6 | 0.67547 | 5.619
2024-12-09 | 20:05 | Data | 0 | 33.237 | 31.346 | 173.15 | 7.63 | 163.262 | 2163.77 | 25.89 | 47.894 | 6.38 | 1.304 | 4.323 | 8300.55 | 1.843 | 97.8 | 76.8 | 1406 | 23.95 | 5395.4 | 2749.4 | 2693.7 | 3977.2 | 1203.6 | 0.67332 | 5.626
2024-12-09 | 20:05 | Data | 0 | 33.183 | 31.515 | 173.06 | 7.62 | 163.172 | 2155.64 | 25.89 | 47.894 | 6.38 | 1.312 | 4.346 | 8300.55 | 1.728 | 97.8 | 76.8 | 1401 | 23.95 | 5395.4 | 2749.2 | 2679.2 | 3968.1 | 1203.6 | 0.67825 | 5.658
2024-12-09 | 20:05 | Data | 0 | 32.96 | 31.339 | 173.014 | 7.63 | 163.172 | 2167.39 | 25.9 | 47.894 | 6.38 | 1.309 | 4.321 | 8318.64 | 1.614 | 97.8 | 76.7 | 1408 | 23.9 | 5407.1 | 2765.1 | 2695.8 | 3982.1 | 1203.6 | 0.67752 | 5.628
2024-12-09 | 20:05 | Data | 0 | 33.628 | 31.603 | 173.421 | 7.62 | 163.307 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.297 | 4.31 | 8336.72 | 1.924 | 97.8 | 76.9 | 1411 | 23.95 | 5418.9 | 2758.3 | 2702 | 3992.1 | 1203.6 | 0.67558 | 5.607
2024-12-09 | 20:05 | Data | 0 | 33.243 | 31.569 | 173.331 | 7.63 | 163.262 | 2166.49 | 25.89 | 47.984 | 6.38 | 1.294 | 4.32 | 8314.11 | 1.452 | 97.8 | 76.9 | 1408 | 23.95 | 5404.2 | 2774.5 | 2715.4 | 4006 | 1203.6 | 0.67501 | 5.614
2024-12-09 | 20:05 | Data | 0 | 33.183 | 31.454 | 173.24 | 7.63 | 163.262 | 2166.49 | 25.89 | 47.804 | 6.38 | 1.306 | 4.305 | 8314.11 | 1.796 | 97.8 | 76.7 | 1408 | 23.95 | 5404.2 | 2772.4 | 2706.7 | 3999.5 | 1203.6 | 0.67638 | 5.611
2024-12-09 | 20:05 | Data | 0 | 33.628 | 31.42 | 173.421 | 7.62 | 163.262 | 2166.49 | 25.89 | 47.894 | 6.38 | 1.3 | 4.298 | 8332.2 | 1.769 | 97.8 | 76.8 | 1408 | 23.95 | 5415.9 | 2766.7 | 2711.1 | 3991.6 | 1203.6 | 0.67505 | 5.598
2024-12-09 | 20:05 | Data | 0 | 33.21 | 31.569 | 173.195 | 7.62 | 163.262 | 2166.49 | 25.9 | 47.804 | 6.38 | 1.301 | 4.312 | 8345.77 | 1.62 | 97.8 | 76.8 | 1408 | 23.9 | 5424.8 | 2758.6 | 2711.2 | 3992.3 | 1203.6 | 0.67451 | 5.611
2024-12-09 | 20:05 | Data | 0 | 33.399 | 31.576 | 173.331 | 7.63 | 163.307 | 2163.77 | 25.89 | 47.894 | 6.38 | 1.31 | 4.329 | 8345.77 | 1.809 | 97.8 | 76.8 | 1406 | 23.95 | 5424.8 | 2776.2 | 2704.8 | 3997.3 | 1203.6 | 0.67795 | 5.639
2024-12-09 | 20:05 | Data | 0 | 33.169 | 31.616 | 173.376 | 7.63 | 163.307 | 2170.1 | 25.89 | 47.984 | 6.37 | 1.312 | 4.329 | 8345.77 | 1.749 | 97.8 | 76.7 | 1411 | 23.99 | 5424.8 | 2782.5 | 2689.3 | 3988.6 | 1203.6 | 0.68065 | 5.641
2024-12-09 | 20:05 | Data | 0 | 33.736 | 31.495 | 173.331 | 7.63 | 163.352 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.306 | 4.321 | 8345.77 | 1.884 | 97.8 | 76.8 | 1411 | 23.99 | 5424.8 | 2762.6 | 2689.7 | 3976 | 1203.6 | 0.67607 | 5.626
2024-12-09 | 20:05 | Data | 0 | 33.183 | 31.562 | 173.105 | 7.62 | 163.172 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.3 | 4.313 | 8363.86 | 1.735 | 97.8 | 76.8 | 1411 | 23.95 | 5436.5 | 2753.7 | 2689.6 | 3971.3 | 1203.6 | 0.67691 | 5.613
2024-12-09 | 20:05 | Data | 0 | 33.351 | 31.684 | 173.014 | 7.62 | 163.172 | 2169.2 | 25.89 | 47.804 | 6.38 | 1.31 | 4.295 | 8332.2 | 1.836 | 97.8 | 76.6 | 1410 | 23.9 | 5415.9 | 2770.4 | 2672.5 | 3975.1 | 1203.6 | 0.678 | 5.603
2024-12-09 | 20:05 | Data | 0 | 33.412 | 31.583 | 173.195 | 7.63 | 163.262 | 2165.58 | 25.9 | 48.165 | 6.38 | 1.305 | 4.295 | 8345.77 | 1.816 | 97.8 | 76.7 | 1408 | 24.08 | 5424.8 | 2748.6 | 2693.3 | 3977.6 | 1203.6 | 0.67589 | 5.599
2024-12-09 | 20:06 | Data | 0 | 33.628 | 31.684 | 173.331 | 7.63 | 163.262 | 2166.49 | 25.89 | 47.894 | 6.37 | 1.296 | 4.317 | 8345.77 | 1.668 | 97.8 | 76.9 | 1408 | 23.95 | 5424.8 | 2763.4 | 2662.2 | 3962.6 | 1203.6 | 0.67959 | 5.612
2024-12-09 | 20:06 | Data | 0 | 33.385 | 31.589 | 173.376 | 7.62 | 163.262 | 2166.49 | 25.89 | 48.075 | 6.38 | 1.299 | 4.329 | 8309.59 | 1.884 | 97.8 | 76.9 | 1408 | 24.04 | 5401.2 | 2770.8 | 2719.2 | 4006.2 | 1203.6 | 0.67533 | 5.628
2024-12-09 | 20:06 | Data | 0 | 33.27 | 31.562 | 173.331 | 7.63 | 163.307 | 2175.52 | 25.89 | 48.165 | 6.38 | 1.289 | 4.334 | 8305.07 | 1.83 | 97.8 | 77.1 | 1415 | 24.08 | 5398.3 | 2766.4 | 2710.1 | 3996.5 | 1203.6 | 0.67598 | 5.623
2024-12-09 | 20:06 | Data | 0 | 33.405 | 31.569 | 173.195 | 7.63 | 163.217 | 2170.1 | 25.89 | 47.984 | 6.38 | 1.3 | 4.307 | 8314.11 | 1.728 | 97.8 | 76.8 | 1411 | 23.95 | 5404.2 | 2743.2 | 2701.9 | 3975 | 1203.6 | 0.67629 | 5.608
2024-12-09 | 20:06 | Data | 0 | 33.183 | 31.886 | 173.331 | 7.63 | 163.307 | 2172.81 | 25.89 | 47.894 | 6.38 | 1.309 | 4.31 | 8314.11 | 1.701 | 97.8 | 76.7 | 1412 | 23.95 | 5404.2 | 2770.7 | 2723.9 | 4010 | 1203.6 | 0.6746 | 5.619
2024-12-09 | 20:06 | Data | 0 | 33.216 | 31.461 | 173.15 | 7.63 | 163.307 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.305 | 4.317 | 8336.72 | 1.668 | 97.8 | 76.8 | 1411 | 23.9 | 5418.9 | 2757.8 | 2694.9 | 3982.7 | 1203.6 | 0.67388 | 5.621
2024-12-09 | 20:06 | Data | 0 | 33.183 | 31.468 | 173.105 | 7.62 | 163.172 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.309 | 4.288 | 8336.72 | 1.816 | 97.8 | 76.6 | 1411 | 23.95 | 5418.9 | 2752.9 | 2686.8 | 3968.4 | 1203.6 | 0.67592 | 5.597
2024-12-09 | 20:06 | Data | 0 | 33.581 | 31.846 | 173.24 | 7.63 | 163.262 | 2170.1 | 25.89 | 48.075 | 6.37 | 1.3 | 4.305 | 8345.77 | 1.614 | 97.8 | 76.8 | 1410 | 24.04 | 5424.8 | 2756.3 | 2717.3 | 3996.3 | 1203.6 | 0.67449 | 5.606
2024-12-09 | 20:06 | Data | 0 | 33.453 | 31.576 | 173.24 | 7.63 | 163.307 | 2161.06 | 25.89 | 48.165 | 6.38 | 1.301 | 4.333 | 8345.77 | 1.843 | 97.8 | 76.9 | 1405 | 24.08 | 5424.8 | 2768.6 | 2717.6 | 3997.9 | 1203.6 | 0.67674 | 5.635
2024-12-09 | 20:06 | Data | 0 | 33.297 | 31.454 | 173.195 | 7.63 | 163.262 | 2166.49 | 25.89 | 47.894 | 6.38 | 1.292 | 4.307 | 8332.2 | 1.816 | 97.8 | 76.9 | 1408 | 23.95 | 5415.9 | 2731.6 | 2726.9 | 3991.3 | 1203.6 | 0.6684 | 5.6
2024-12-09 | 20:06 | Data | 0 | 33.183 | 31.576 | 173.195 | 7.62 | 163.217 | 2163.77 | 25.89 | 48.165 | 6.38 | 1.296 | 4.302 | 8332.2 | 1.742 | 97.8 | 76.8 | 1407 | 24.08 | 5415.9 | 2762.5 | 2724.4 | 4004.4 | 1203.6 | 0.6725 | 5.598
2024-12-09 | 20:06 | Data | 0 | 33.21 | 31.549 | 173.376 | 7.63 | 163.217 | 2162.87 | 25.9 | 48.075 | 6.38 | 1.308 | 4.317 | 8336.72 | 1.708 | 97.8 | 76.8 | 1406 | 24.04 | 5418.9 | 2776.5 | 2681.6 | 3976.7 | 1203.6 | 0.6826 | 5.625
2024-12-09 | 20:06 | Data | 0 | 33.52 | 31.596 | 173.331 | 7.62 | 163.307 | 2166.49 | 25.89 | 48.075 | 6.37 | 1.303 | 4.317 | 8332.2 | 1.627 | 97.8 | 76.8 | 1408 | 24.04 | 5415.9 | 2757.4 | 2705.2 | 3990 | 1203.6 | 0.67461 | 5.621
2024-12-09 | 20:06 | Data | 0 | 33.567 | 31.799 | 173.376 | 7.63 | 163.307 | 2166.49 | 25.89 | 47.894 | 6.38 | 1.31 | 4.318 | 8318.64 | 1.836 | 97.8 | 76.7 | 1408 | 23.95 | 5407.1 | 2742.7 | 2693.2 | 3979.2 | 1203.6 | 0.67345 | 5.628
2024-12-09 | 20:06 | Data | 0 | 33.183 | 31.555 | 173.195 | 7.63 | 163.262 | 2167.39 | 25.89 | 48.075 | 6.38 | 1.305 | 4.302 | 8323.16 | 1.654 | 97.8 | 76.7 | 1408 | 24.08 | 5410.1 | 2759.6 | 2709.1 | 3992.3 | 1203.6 | 0.67482 | 5.607
2024-12-09 | 20:06 | Data | 0 | 33.021 | 31.515 | 173.24 | 7.63 | 163.262 | 2166.49 | 25.89 | 48.075 | 6.38 | 1.305 | 4.308 | 8314.11 | 1.681 | 97.8 | 76.7 | 1408 | 24.08 | 5404.2 | 2762.4 | 2698.6 | 3995.9 | 1203.6 | 0.67409 | 5.613
2024-12-09 | 20:06 | Data | 0 | 33.405 | 31.684 | 173.331 | 7.63 | 163.262 | 2162.87 | 25.89 | 47.894 | 6.38 | 1.304 | 4.289 | 8314.11 | 1.728 | 97.8 | 76.7 | 1406 | 23.95 | 5404.2 | 2739 | 2707.2 | 3981.5 | 1203.6 | 0.67164 | 5.593
2024-12-09 | 20:06 | Data | 0 | 33.297 | 31.542 | 173.331 | 7.63 | 163.262 | 2166.49 | 25.9 | 48.165 | 6.38 | 1.302 | 4.302 | 8332.2 | 1.85 | 97.8 | 76.8 | 1408 | 24.08 | 5415.9 | 2757.6 | 2688.6 | 3975.2 | 1203.6 | 0.67666 | 5.604
2024-12-09 | 20:07 | Data | 0 | 33.196 | 31.765 | 173.24 | 7.63 | 163.352 | 2166.49 | 25.89 | 48.165 | 6.38 | 1.304 | 4.305 | 8336.72 | 1.56 | 97.8 | 76.8 | 1408 | 24.08 | 5418.9 | 2755.5 | 2708.9 | 3988.9 | 1203.6 | 0.67479 | 5.61
2024-12-09 | 20:07 | Data | 0 | 33.21 | 31.569 | 173.331 | 7.63 | 163.307 | 2169.2 | 25.89 | 47.894 | 6.38 | 1.294 | 4.285 | 8341.25 | 1.627 | 97.8 | 76.8 | 1411 | 23.95 | 5421.8 | 2753.8 | 2728.4 | 4001.5 | 1203.6 | 0.67148 | 5.579
2024-12-09 | 20:07 | Data | 0 | 33.324 | 31.569 | 173.195 | 7.63 | 163.262 | 2171.01 | 25.89 | 47.804 | 6.38 | 1.302 | 4.276 | 8350.29 | 1.627 | 97.8 | 76.7 | 1411 | 23.95 | 5427.7 | 2787.5 | 2730.7 | 4019.4 | 1203.6 | 0.67031 | 5.579
2024-12-09 | 20:07 | Data | 0 | 33.183 | 31.724 | 173.24 | 7.63 | 163.262 | 2171.01 | 25.89 | 47.984 | 6.38 | 1.31 | 4.312 | 8323.16 | 1.668 | 97.8 | 76.7 | 1411 | 23.95 | 5410.1 | 2772.5 | 2724.1 | 4006.2 | 1203.6 | 0.67448 | 5.62
2024-12-09 | 20:07 | Data | 0 | 33.297 | 31.765 | 173.331 | 7.62 | 163.217 | 2170.1 | 25.89 | 48.075 | 6.38 | 1.31 | 4.315 | 8354.81 | 1.708 | 97.8 | 76.7 | 1411 | 24.08 | 5430.6 | 2749.7 | 2748.3 | 4011.7 | 1203.6 | 0.66851 | 5.624
2024-12-09 | 20:07 | Data | 0 | 33.27 | 31.583 | 173.24 | 7.63 | 163.307 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.318 | 4.313 | 8323.16 | 1.992 | 97.8 | 76.6 | 1411 | 24.08 | 5410.1 | 2772.7 | 2723 | 4012.6 | 1203.7 | 0.67342 | 5.63
2024-12-09 | 20:07 | Data | 0 | 33.189 | 31.569 | 173.331 | 7.63 | 163.307 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.305 | 4.272 | 8341.25 | 1.614 | 97.8 | 76.6 | 1411 | 24.08 | 5421.8 | 2743.8 | 2742.5 | 4006.2 | 1203.7 | 0.66915 | 5.576
2024-12-09 | 20:07 | Data | 0 | 33.358 | 31.569 | 173.195 | 7.62 | 163.262 | 2171.91 | 25.89 | 48.075 | 6.38 | 1.299 | 4.285 | 8363.86 | 1.83 | 97.8 | 76.7 | 1412 | 24.04 | 5436.5 | 2748.2 | 2716.3 | 3990.5 | 1203.7 | 0.66853 | 5.584
2024-12-09 | 20:07 | Data | 0 | 32.98 | 31.562 | 173.24 | 7.62 | 163.307 | 2171.91 | 25.89 | 48.165 | 6.38 | 1.3 | 4.286 | 8359.34 | 1.404 | 97.8 | 76.7 | 1412 | 24.08 | 5433.6 | 2742.8 | 2734.7 | 4001.9 | 1203.7 | 0.668 | 5.586
2024-12-09 | 20:07 | Data | 0 | 33.412 | 31.569 | 173.15 | 7.62 | 163.307 | 2175.52 | 25.9 | 48.165 | 6.38 | 1.302 | 4.295 | 8354.81 | 1.728 | 97.8 | 76.7 | 1414 | 24.04 | 5430.6 | 2759.7 | 2728.5 | 4002.5 | 1203.7 | 0.67193 | 5.597
2024-12-09 | 20:07 | Data | 0 | 33.297 | 31.88 | 173.24 | 7.63 | 163.262 | 2175.52 | 25.89 | 48.255 | 6.38 | 1.305 | 4.275 | 8341.25 | 1.836 | 97.8 | 76.6 | 1414 | 24.08 | 5421.8 | 2748.1 | 2724 | 3992.1 | 1203.7 | 0.67327 | 5.581
2024-12-09 | 20:07 | Data | 0 | 33.297 | 31.468 | 173.331 | 7.63 | 163.262 | 2179.14 | 25.89 | 47.894 | 6.38 | 1.302 | 4.298 | 8336.72 | 1.614 | 97.8 | 76.7 | 1416 | 23.95 | 5418.9 | 2768.7 | 2713.5 | 4004 | 1203.7 | 0.67257 | 5.6
2024-12-09 | 20:07 | Data | 0 | 33.615 | 31.596 | 173.376 | 7.63 | 163.307 | 2177.33 | 25.89 | 47.894 | 6.38 | 1.293 | 4.318 | 8323.16 | 1.843 | 97.8 | 76.9 | 1415 | 23.95 | 5410.1 | 2771.5 | 2711.3 | 4001.9 | 1203.7 | 0.67416 | 5.612
2024-12-09 | 20:07 | Data | 0 | 33.716 | 31.799 | 173.24 | 7.62 | 163.307 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.292 | 4.316 | 8336.72 | 1.998 | 97.8 | 77 | 1414 | 23.95 | 5418.9 | 2753.7 | 2725.4 | 4001.1 | 1203.7 | 0.67099 | 5.609
2024-12-09 | 20:07 | Data | 0 | 33.257 | 31.346 | 173.331 | 7.62 | 163.352 | 2174.62 | 25.89 | 47.804 | 6.37 | 1.3 | 4.29 | 8336.72 | 1.661 | 97.8 | 76.8 | 1414 | 23.95 | 5418.9 | 2753.9 | 2719.5 | 4002.1 | 1203.7 | 0.67083 | 5.591
2024-12-09 | 20:07 | Data | 0 | 33.615 | 31.596 | 173.331 | 7.62 | 163.352 | 2173.72 | 25.89 | 47.894 | 6.38 | 1.3 | 4.309 | 8757.29 | 1.836 | 97.8 | 76.8 | 1413 | 23.95 | 5692.2 | 2752.5 | 2719.4 | 3996.7 | 1203.7 | 0.67024 | 5.609
2024-12-09 | 20:07 | Data | 0 | 33.412 | 31.799 | 173.331 | 7.62 | 163.262 | 2167.39 | 25.89 | 47.894 | 6.38 | 1.301 | 4.304 | 8341.25 | 1.614 | 97.8 | 76.8 | 1410 | 23.95 | 5421.8 | 2785.8 | 2712.5 | 4009.6 | 1203.7 | 0.67611 | 5.607
2024-12-09 | 20:07 | Data | 0 | 33.243 | 31.4 | 173.195 | 7.63 | 163.262 | 2172.81 | 25.89 | 47.894 | 6.38 | 1.303 | 4.274 | 8345.77 | 1.796 | 97.8 | 76.6 | 1412 | 23.95 | 5424.8 | 2760.5 | 2709.8 | 3989.3 | 1203.7 | 0.67501 | 5.577
2024-12-09 | 20:08 | Data | 0 | 33.183 | 31.569 | 173.195 | 7.63 | 163.307 | 2172.81 | 25.89 | 48.165 | 6.38 | 1.302 | 4.318 | 8345.77 | 1.816 | 97.8 | 76.8 | 1413 | 24.08 | 5424.8 | 2735.1 | 2711 | 3975 | 1203.7 | 0.67039 | 5.621
2024-12-09 | 20:08 | Data | 0 | 33.412 | 31.583 | 173.331 | 7.62 | 163.307 | 2173.72 | 25.89 | 47.894 | 6.38 | 1.308 | 4.306 | 8345.77 | 1.735 | 97.8 | 76.7 | 1413 | 23.95 | 5424.8 | 2758 | 2695.3 | 3978.6 | 1203.7 | 0.67645 | 5.614
2024-12-09 | 20:08 | Data | 0 | 33.385 | 31.569 | 173.195 | 7.63 | 163.262 | 2171.91 | 25.89 | 47.894 | 6.38 | 1.307 | 4.294 | 8345.77 | 1.83 | 97.8 | 76.7 | 1412 | 23.95 | 5424.8 | 2759.8 | 2716.8 | 3997.3 | 1203.7 | 0.67337 | 5.6
2024-12-09 | 20:08 | Data | 0 | 33.189 | 31.461 | 173.195 | 7.63 | 163.262 | 2172.81 | 25.89 | 47.894 | 6.38 | 1.301 | 4.322 | 8336.72 | 1.83 | 97.8 | 76.9 | 1412 | 23.95 | 5418.9 | 2770.3 | 2748.8 | 4031.4 | 1203.7 | 0.67371 | 5.622
2024-12-09 | 20:08 | Data | 0 | 33.574 | 31.583 | 173.195 | 7.62 | 163.307 | 2172.81 | 25.89 | 47.894 | 6.38 | 1.302 | 4.327 | 8332.2 | 1.85 | 97.8 | 76.9 | 1412 | 23.99 | 5415.9 | 2758.4 | 2731.8 | 4003.7 | 1203.7 | 0.67208 | 5.629
2024-12-09 | 20:08 | Data | 0 | 33.628 | 31.684 | 173.24 | 7.62 | 163.443 | 2173.72 | 25.89 | 47.984 | 6.38 | 1.304 | 4.313 | 8372.9 | 1.668 | 97.8 | 76.8 | 1412 | 23.95 | 5442.4 | 2757.3 | 2735.9 | 4007.9 | 1203.7 | 0.66974 | 5.618
2024-12-09 | 20:08 | Data | 0 | 33.412 | 31.684 | 173.331 | 7.63 | 163.262 | 2172.81 | 25.89 | 47.894 | 6.38 | 1.307 | 4.31 | 8372.9 | 1.843 | 97.8 | 76.7 | 1412 | 23.95 | 5442.4 | 2743.2 | 2739.3 | 4001.8 | 1203.7 | 0.66794 | 5.617
2024-12-09 | 20:08 | Data | 0 | 33.412 | 31.569 | 173.195 | 7.63 | 163.352 | 2171.91 | 25.89 | 47.894 | 6.38 | 1.305 | 4.3 | 8377.43 | 1.728 | 97.8 | 76.7 | 1412 | 23.9 | 5445.3 | 2763.3 | 2743.4 | 4017.2 | 1203.7 | 0.67013 | 5.605
2024-12-09 | 20:08 | Data | 0 | 33.189 | 31.738 | 173.195 | 7.62 | 163.262 | 2174.62 | 25.89 | 47.804 | 6.38 | 1.304 | 4.292 | 8372.9 | 1.728 | 97.8 | 76.7 | 1414 | 23.95 | 5442.4 | 2750.4 | 2739.7 | 4003.9 | 1203.7 | 0.6683 | 5.597
2024-12-09 | 20:08 | Data | 0 | 33.216 | 31.792 | 173.376 | 7.63 | 163.443 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.305 | 4.313 | 8363.86 | 1.539 | 97.8 | 76.8 | 1414 | 23.95 | 5436.5 | 2795 | 2729.3 | 4029.3 | 1203.7 | 0.67624 | 5.616
2024-12-09 | 20:08 | Data | 0 | 33.21 | 31.366 | 173.06 | 7.63 | 163.262 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.304 | 4.31 | 8359.34 | 1.735 | 97.8 | 76.8 | 1414 | 23.95 | 5433.6 | 2756.1 | 2702.5 | 3982.7 | 1203.7 | 0.67496 | 5.614
2024-12-09 | 20:08 | Data | 0 | 33.237 | 31.555 | 173.195 | 7.62 | 163.307 | 2175.52 | 25.89 | 47.714 | 6.38 | 1.303 | 4.303 | 8372.9 | 1.634 | 97.8 | 76.7 | 1414 | 23.86 | 5442.4 | 2748.9 | 2718.6 | 3993.1 | 1203.7 | 0.6713 | 5.607
2024-12-09 | 20:08 | Data | 0 | 33.581 | 31.583 | 173.195 | 7.63 | 163.307 | 2172.81 | 25.89 | 47.894 | 6.38 | 1.302 | 4.313 | 8363.86 | 1.897 | 97.8 | 76.8 | 1412 | 23.99 | 5436.5 | 2762.1 | 2730 | 4008.2 | 1203.7 | 0.6746 | 5.616
2024-12-09 | 20:08 | Data | 0 | 33.385 | 31.596 | 173.376 | 7.62 | 163.217 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.296 | 4.323 | 8359.34 | 1.809 | 97.8 | 76.9 | 1414 | 23.9 | 5433.6 | 2760.1 | 2720.2 | 3997.7 | 1203.7 | 0.67157 | 5.619
2024-12-09 | 20:08 | Data | 0 | 33.426 | 31.373 | 173.24 | 7.62 | 163.307 | 2172.81 | 25.89 | 47.623 | 6.38 | 1.297 | 4.304 | 8363.86 | 1.836 | 97.8 | 76.9 | 1412 | 23.81 | 5436.5 | 2767.7 | 2711.1 | 3996.7 | 1203.7 | 0.67495 | 5.6
2024-12-09 | 20:08 | Data | 0 | 33.129 | 31.522 | 173.15 | 7.63 | 163.217 | 2170.1 | 25.9 | 47.804 | 6.38 | 1.301 | 4.317 | 8359.34 | 1.944 | 97.8 | 76.8 | 1410 | 23.95 | 5433.6 | 2732.8 | 2734.8 | 3995.1 | 1203.7 | 0.66632 | 5.619
2024-12-09 | 20:08 | Data | 0 | 33.358 | 31.569 | 173.24 | 7.62 | 163.217 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.303 | 4.322 | 8377.43 | 1.836 | 97.8 | 76.8 | 1410 | 23.95 | 5445.3 | 2754.6 | 2715.1 | 3992 | 1203.7 | 0.673 | 5.626
2024-12-09 | 20:08 | Data | 0 | 33.635 | 31.623 | 173.376 | 7.62 | 163.352 | 2166.49 | 25.89 | 48.165 | 6.38 | 1.295 | 4.34 | 8386.47 | 1.641 | 97.8 | 77 | 1408 | 24.08 | 5451.2 | 2727.3 | 2738.3 | 3995.8 | 1203.7 | 0.66379 | 5.635
2024-12-09 | 20:09 | Data | 0 | 33.527 | 31.819 | 173.331 | 7.63 | 163.352 | 2171.01 | 25.89 | 48.165 | 6.38 | 1.306 | 4.313 | 8390.99 | 1.789 | 97.8 | 76.7 | 1411 | 24.08 | 5454.1 | 2795.7 | 2731 | 4028.8 | 1203.7 | 0.67647 | 5.62
2024-12-09 | 20:09 | Data | 0 | 33.466 | 31.373 | 173.24 | 7.62 | 163.352 | 2163.77 | 25.89 | 47.894 | 6.37 | 1.304 | 4.313 | 8381.95 | 1.809 | 97.8 | 76.8 | 1407 | 23.95 | 5448.3 | 2761.6 | 2720.5 | 4009.2 | 1203.7 | 0.67136 | 5.617
2024-12-09 | 20:09 | Data | 0 | 33.304 | 31.596 | 173.331 | 7.63 | 163.352 | 2171.01 | 25.89 | 48.075 | 6.38 | 1.297 | 4.313 | 8390.99 | 1.6 | 97.8 | 76.9 | 1411 | 24.08 | 5454.1 | 2781.6 | 2699.7 | 4003.1 | 1203.7 | 0.6776 | 5.61
2024-12-09 | 20:09 | Data | 0 | 33.628 | 31.799 | 173.376 | 7.63 | 163.307 | 2175.52 | 25.89 | 47.984 | 6.38 | 1.291 | 4.326 | 8386.47 | 1.843 | 97.8 | 77 | 1414 | 23.99 | 5451.2 | 2772.2 | 2699.1 | 3999.2 | 1203.7 | 0.67479 | 5.618
2024-12-09 | 20:09 | Data | 0 | 33.5 | 31.603 | 173.331 | 7.63 | 163.443 | 2170.1 | 25.89 | 48.075 | 6.38 | 1.297 | 4.317 | 8381.95 | 1.836 | 97.8 | 76.9 | 1411 | 24.08 | 5448.3 | 2772.9 | 2721.2 | 4011.8 | 1203.7 | 0.67408 | 5.615
2024-12-09 | 20:09 | Data | 0 | 33.642 | 31.907 | 173.512 | 7.63 | 163.578 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.308 | 4.309 | 8386.47 | 1.627 | 97.8 | 76.7 | 1411 | 23.95 | 5451.2 | 2780 | 2718.9 | 4011.5 | 1203.7 | 0.67675 | 5.615
2024-12-09 | 20:09 | Data | 0 | 33.358 | 31.954 | 173.376 | 7.63 | 163.352 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.301 | 4.307 | 8400.04 | 1.769 | 97.8 | 76.8 | 1410 | 24.13 | 5460 | 2782.2 | 2707.5 | 4007.1 | 1203.7 | 0.67669 | 5.608
2024-12-09 | 20:09 | Data | 0 | 33.405 | 31.623 | 173.331 | 7.63 | 163.352 | 2171.91 | 25.89 | 48.075 | 6.37 | 1.303 | 4.278 | 8350.29 | 1.843 | 97.8 | 76.7 | 1412 | 24.04 | 5427.7 | 2775.3 | 2706.1 | 4003.5 | 1203.7 | 0.67528 | 5.581
2024-12-09 | 20:09 | Data | 0 | 33.378 | 31.684 | 173.24 | 7.63 | 163.262 | 2171.91 | 25.89 | 48.165 | 6.38 | 1.301 | 4.276 | 8359.34 | 1.722 | 97.8 | 76.7 | 1412 | 24.08 | 5433.6 | 2780.8 | 2741.5 | 4033.2 | 1203.8 | 0.67234 | 5.579
2024-12-09 | 20:09 | Data | 0 | 33.412 | 31.569 | 173.331 | 7.63 | 163.262 | 2172.81 | 25.9 | 47.894 | 6.38 | 1.301 | 4.299 | 8345.77 | 1.843 | 97.8 | 76.8 | 1412 | 23.95 | 5424.8 | 2765.2 | 2718.5 | 4009.6 | 1203.8 | 0.67102 | 5.599
2024-12-09 | 20:09 | Data | 0 | 33.527 | 31.583 | 173.24 | 7.63 | 163.352 | 2172.81 | 25.89 | 47.894 | 6.38 | 1.3 | 4.309 | 8350.29 | 1.715 | 97.8 | 76.8 | 1412 | 23.95 | 5427.7 | 2785.5 | 2715.7 | 4019.9 | 1203.8 | 0.67777 | 5.609
2024-12-09 | 20:09 | Data | 0 | 33.142 | 31.67 | 173.331 | 7.62 | 163.262 | 2174.62 | 25.89 | 48.165 | 6.38 | 1.305 | 4.306 | 8341.25 | 1.749 | 97.8 | 76.7 | 1414 | 24.08 | 5421.8 | 2796.6 | 2723.9 | 4032 | 1203.8 | 0.67658 | 5.611
2024-12-09 | 20:09 | Data | 0 | 33.297 | 31.461 | 173.195 | 7.63 | 163.352 | 2174.62 | 25.89 | 48.165 | 6.38 | 1.302 | 4.307 | 8336.72 | 1.863 | 97.8 | 76.8 | 1414 | 24.04 | 5418.9 | 2781.7 | 2728.2 | 4025.4 | 1203.8 | 0.67315 | 5.61
2024-12-09 | 20:09 | Data | 0 | 33.412 | 31.576 | 173.331 | 7.62 | 163.307 | 2175.52 | 25.9 | 48.165 | 6.38 | 1.299 | 4.327 | 8336.72 | 1.715 | 97.8 | 76.9 | 1414 | 24.08 | 5418.9 | 2798.6 | 2707.2 | 4019.9 | 1203.8 | 0.68056 | 5.625
2024-12-09 | 20:09 | Data | 0 | 33.189 | 31.583 | 173.24 | 7.62 | 163.307 | 2175.52 | 25.89 | 48.075 | 6.38 | 1.305 | 4.327 | 8345.77 | 1.762 | 97.8 | 76.8 | 1414 | 24.04 | 5424.8 | 2760.1 | 2721.7 | 4009.8 | 1203.8 | 0.67106 | 5.631
2024-12-09 | 20:09 | Data | 0 | 33.581 | 31.677 | 173.467 | 7.62 | 163.488 | 2173.72 | 25.89 | 48.165 | 6.37 | 1.3 | 4.313 | 8332.2 | 1.836 | 97.8 | 76.8 | 1413 | 24.08 | 5415.9 | 2784.6 | 2703.2 | 4011.4 | 1203.8 | 0.67702 | 5.613
2024-12-09 | 20:09 | Data | 0 | 33.75 | 31.61 | 173.512 | 7.63 | 163.488 | 2172.81 | 25.89 | 48.165 | 6.38 | 1.3 | 4.299 | 8323.16 | 1.823 | 97.8 | 76.8 | 1412 | 24.08 | 5410.1 | 2776.4 | 2713.2 | 4019.5 | 1203.8 | 0.67679 | 5.598
2024-12-09 | 20:10 | Data | 0 | 33.264 | 31.569 | 173.376 | 7.63 | 163.443 | 2172.81 | 25.89 | 48.075 | 6.37 | 1.302 | 4.299 | 8336.72 | 1.62 | 97.8 | 76.8 | 1412 | 24.04 | 5418.9 | 2794.9 | 2694.6 | 4008.7 | 1203.8 | 0.68106 | 5.6
2024-12-09 | 20:10 | Data | 0 | 33.588 | 31.853 | 173.421 | 7.63 | 163.443 | 2174.62 | 25.89 | 48.165 | 6.38 | 1.292 | 4.326 | 8332.2 | 1.931 | 97.8 | 77 | 1414 | 24.04 | 5415.9 | 2783.3 | 2734 | 4032.8 | 1203.8 | 0.6719 | 5.619
2024-12-09 | 20:10 | Data | 0 | 33.527 | 31.819 | 173.24 | 7.62 | 163.307 | 2178.24 | 25.89 | 48.165 | 6.38 | 1.302 | 4.313 | 8318.64 | 1.796 | 97.8 | 76.8 | 1416 | 24.08 | 5407.1 | 2775.9 | 2734.6 | 4026.7 | 1203.8 | 0.67146 | 5.615
2024-12-09 | 20:10 | Data | 0 | 33.567 | 31.799 | 173.512 | 7.63 | 163.488 | 2180.04 | 25.89 | 48.255 | 6.38 | 1.301 | 4.312 | 8309.59 | 1.809 | 97.8 | 76.8 | 1418 | 24.08 | 5401.2 | 2783.8 | 2696.5 | 4007.9 | 1203.8 | 0.67763 | 5.614
2024-12-09 | 20:10 | Data | 0 | 33.021 | 31.461 | 173.195 | 7.63 | 163.307 | 2180.04 | 25.89 | 48.165 | 6.38 | 1.304 | 4.283 | 8318.64 | 1.735 | 97.8 | 76.7 | 1418 | 24.08 | 5407.1 | 2792.2 | 2731.2 | 4030.2 | 1203.8 | 0.67521 | 5.588
2024-12-09 | 20:10 | Data | 0 | 33.183 | 31.758 | 173.331 | 7.63 | 163.262 | 2180.04 | 25.89 | 48.165 | 6.38 | 1.303 | 4.288 | 8314.11 | 1.647 | 97.8 | 76.7 | 1417 | 24.04 | 5404.2 | 2796.9 | 2701.4 | 4015 | 1203.8 | 0.67841 | 5.591
2024-12-09 | 20:10 | Data | 0 | 33.291 | 31.569 | 173.15 | 7.63 | 163.262 | 2180.04 | 25.89 | 48.165 | 6.38 | 1.299 | 4.288 | 8323.16 | 1.627 | 97.8 | 76.8 | 1417 | 24.08 | 5410.1 | 2788.1 | 2696.9 | 4002.4 | 1203.8 | 0.67962 | 5.585
2024-12-09 | 20:10 | Data | 0 | 33.412 | 31.596 | 173.24 | 7.62 | 163.307 | 2180.95 | 25.89 | 48.075 | 6.38 | 1.31 | 4.299 | 8323.16 | 1.641 | 97.8 | 76.6 | 1417 | 24.04 | 5410.1 | 2807 | 2724.6 | 4035.5 | 1203.8 | 0.6782 | 5.608
2024-12-09 | 20:10 | Data | 0 | 33.129 | 31.569 | 173.24 | 7.62 | 163.262 | 2180.04 | 25.89 | 48.255 | 6.38 | 1.306 | 4.315 | 8323.16 | 1.776 | 97.8 | 76.8 | 1417 | 24.08 | 5410.1 | 2806.8 | 2718.2 | 4033.6 | 1203.8 | 0.68007 | 5.622
2024-12-09 | 20:10 | Data | 0 | 33.297 | 31.954 | 173.331 | 7.63 | 163.352 | 2180.95 | 25.89 | 48.165 | 6.38 | 1.308 | 4.323 | 8336.72 | 1.728 | 97.8 | 76.8 | 1417 | 24.08 | 5418.9 | 2790.7 | 2701.6 | 4011.6 | 1203.8 | 0.67942 | 5.63
2024-12-09 | 20:10 | Data | 0 | 33.183 | 31.555 | 173.195 | 7.63 | 163.262 | 2180.04 | 25.89 | 48.165 | 6.38 | 1.303 | 4.316 | 8350.29 | 1.641 | 97.8 | 76.8 | 1418 | 24.08 | 5427.7 | 2704.6 | 2707.6 | 3954.4 | 1203.8 | 0.66917 | 5.619
2024-12-09 | 20:10 | Data | 0 | 33.426 | 31.67 | 173.331 | 7.63 | 163.307 | 2178.24 | 25.89 | 48.165 | 6.38 | 1.308 | 4.302 | 8350.29 | 1.668 | 97.8 | 76.7 | 1416 | 24.04 | 5427.7 | 2707.7 | 2709.4 | 3956.2 | 1203.8 | 0.67058 | 5.61
2024-12-09 | 20:10 | Data | 0 | 33.358 | 31.738 | 173.331 | 7.63 | 163.307 | 2177.33 | 25.89 | 48.165 | 6.38 | 1.304 | 4.295 | 8350.29 | 1.715 | 97.8 | 76.7 | 1415 | 24.08 | 5427.7 | 2731.4 | 2684.2 | 3951.5 | 1203.8 | 0.67325 | 5.6
2024-12-09 | 20:10 | Data | 0 | 33.412 | 31.393 | 173.15 | 7.63 | 163.262 | 2177.33 | 25.89 | 48.165 | 6.38 | 1.302 | 4.288 | 8368.38 | 1.742 | 97.8 | 76.7 | 1415 | 24.04 | 5439.4 | 2736.1 | 2690.5 | 3959 | 1203.8 | 0.67447 | 5.591
2024-12-09 | 20:10 | Data | 0 | 33.608 | 31.569 | 173.331 | 7.63 | 163.262 | 2177.33 | 25.9 | 48.075 | 6.38 | 1.299 | 4.286 | 8359.34 | 1.857 | 97.8 | 76.7 | 1416 | 24.04 | 5433.6 | 2717.1 | 2694.2 | 3944.6 | 1203.8 | 0.67307 | 5.585
2024-12-09 | 20:10 | Data | 0 | 33.284 | 31.569 | 173.331 | 7.63 | 163.307 | 2174.62 | 25.89 | 48.075 | 6.38 | 1.303 | 4.305 | 8359.34 | 1.83 | 97.8 | 76.8 | 1414 | 24.08 | 5433.6 | 2720.3 | 2696 | 3937.8 | 1203.8 | 0.6708 | 5.609
2024-12-09 | 20:10 | Data | 0 | 33.257 | 31.4 | 173.195 | 7.62 | 163.307 | 2175.52 | 25.89 | 47.984 | 6.38 | 1.297 | 4.315 | 8359.34 | 1.742 | 97.8 | 76.9 | 1414 | 23.99 | 5433.6 | 2689.7 | 2690.1 | 3928.6 | 1203.8 | 0.66973 | 5.613
2024-12-09 | 20:10 | Data | 0 | 33.412 | 31.61 | 173.24 | 7.63 | 163.443 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.306 | 4.308 | 8359.34 | 1.755 | 97.8 | 76.7 | 1414 | 23.99 | 5433.6 | 2704.3 | 2717.2 | 3953.9 | 1203.8 | 0.6673 | 5.614
2024-12-09 | 20:11 | Data | 0 | 33.385 | 31.745 | 173.331 | 7.63 | 163.352 | 2175.52 | 25.89 | 48.165 | 6.38 | 1.312 | 4.331 | 8354.81 | 1.83 | 97.8 | 76.7 | 1414 | 24.08 | 5430.6 | 2729.8 | 2683.2 | 3957.6 | 1203.8 | 0.67104 | 5.642
2024-12-09 | 20:11 | Data | 0 | 32.994 | 31.454 | 173.331 | 7.63 | 163.307 | 2177.33 | 25.9 | 47.894 | 6.38 | 1.306 | 4.319 | 8314.11 | 1.627 | 97.8 | 76.8 | 1416 | 23.95 | 5404.2 | 2725.1 | 2707.4 | 3970.9 | 1203.8 | 0.66702 | 5.625
2024-12-09 | 20:11 | Data | 0 | 33.189 | 31.515 | 173.24 | 7.63 | 163.307 | 2177.33 | 25.89 | 48.165 | 6.38 | 1.31 | 4.319 | 8314.11 | 1.816 | 97.8 | 76.7 | 1415 | 24.04 | 5404.2 | 2763.1 | 2731.2 | 4011.9 | 1203.8 | 0.67226 | 5.629
2024-12-09 | 20:11 | Data | 0 | 33.412 | 31.596 | 173.24 | 7.63 | 163.307 | 2177.33 | 25.89 | 48.165 | 6.38 | 1.305 | 4.303 | 8318.64 | 1.782 | 97.8 | 76.7 | 1415 | 24.08 | 5407.1 | 2753.6 | 2709.5 | 3991.4 | 1203.8 | 0.6725 | 5.609
2024-12-09 | 20:11 | Data | 0 | 33.412 | 31.569 | 173.331 | 7.63 | 163.262 | 2176.43 | 25.89 | 48.165 | 6.38 | 1.303 | 4.323 | 8305.07 | 1.836 | 97.8 | 76.8 | 1414 | 24.04 | 5398.3 | 2776 | 2710.9 | 4007.2 | 1203.8 | 0.67547 | 5.626
2024-12-09 | 20:11 | Data | 0 | 33.412 | 31.488 | 173.195 | 7.63 | 163.262 | 2175.52 | 25.89 | 47.984 | 6.38 | 1.303 | 4.314 | 8336.72 | 1.809 | 97.8 | 76.8 | 1414 | 23.99 | 5418.9 | 2787.5 | 2707.9 | 4008.4 | 1203.8 | 0.67898 | 5.619
2024-12-09 | 20:11 | Data | 0 | 33.324 | 31.907 | 173.376 | 7.63 | 163.352 | 2175.52 | 25.89 | 47.894 | 6.37 | 1.301 | 4.316 | 8336.72 | 1.823 | 97.8 | 76.8 | 1414 | 23.9 | 5418.9 | 2783.4 | 2700.7 | 4002.3 | 1203.8 | 0.67673 | 5.618
2024-12-09 | 20:11 | Data | 0 | 33.635 | 31.576 | 173.331 | 7.63 | 163.307 | 2174.62 | 25.9 | 47.894 | 6.38 | 1.303 | 4.302 | 8336.72 | 1.742 | 97.8 | 76.7 | 1414 | 23.95 | 5418.9 | 2778.9 | 2683 | 3988.3 | 1203.8 | 0.67983 | 5.604
2024-12-09 | 20:11 | Data | 0 | 33.203 | 31.569 | 173.24 | 7.62 | 163.307 | 2175.52 | 25.89 | 48.075 | 6.38 | 1.302 | 4.318 | 8336.72 | 1.614 | 97.8 | 76.8 | 1414 | 24.04 | 5418.9 | 2781.4 | 2691.5 | 3996.5 | 1203.8 | 0.67813 | 5.62
2024-12-09 | 20:11 | Data | 0 | 33.183 | 31.569 | 173.15 | 7.63 | 163.217 | 2174.62 | 25.89 | 47.894 | 6.37 | 1.297 | 4.295 | 8372.9 | 1.62 | 97.8 | 76.8 | 1414 | 23.95 | 5442.4 | 2766.2 | 2715.3 | 4000.1 | 1203.8 | 0.67318 | 5.591
2024-12-09 | 20:11 | Data | 0 | 33.297 | 31.772 | 173.195 | 7.62 | 163.217 | 2174.62 | 25.89 | 47.984 | 6.38 | 1.296 | 4.273 | 8386.47 | 1.742 | 97.8 | 76.7 | 1414 | 23.95 | 5451.2 | 2760.6 | 2695.5 | 3983.9 | 1203.8 | 0.6754 | 5.569
2024-12-09 | 20:11 | Data | 0 | 33.21 | 31.339 | 173.195 | 7.62 | 163.217 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.301 | 4.294 | 8390.99 | 1.843 | 97.8 | 76.7 | 1414 | 23.99 | 5454.1 | 2784.3 | 2701.4 | 4003.3 | 1203.9 | 0.67857 | 5.595
2024-12-09 | 20:11 | Data | 0 | 33.196 | 31.569 | 173.24 | 7.62 | 163.352 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.318 | 4.316 | 8372.9 | 1.789 | 97.8 | 76.6 | 1414 | 23.95 | 5442.4 | 2759.2 | 2725.9 | 4003.1 | 1203.9 | 0.67088 | 5.634
2024-12-09 | 20:11 | Data | 0 | 33.527 | 31.576 | 173.24 | 7.63 | 163.443 | 2174.62 | 25.89 | 47.894 | 6.38 | 1.318 | 4.323 | 8354.81 | 1.681 | 97.8 | 76.6 | 1413 | 23.9 | 5430.6 | 2780.7 | 2719.8 | 4015.9 | 1203.9 | 0.67567 | 5.64
2024-12-09 | 20:11 | Data | 0 | 33.183 | 31.542 | 173.15 | 7.63 | 163.262 | 2172.81 | 25.89 | 48.165 | 6.38 | 1.301 | 4.289 | 8359.34 | 1.668 | 97.8 | 76.7 | 1412 | 24.08 | 5433.6 | 2780.4 | 2716.4 | 4006.3 | 1203.9 | 0.67739 | 5.59
2024-12-09 | 20:11 | Data | 0 | 33.183 | 31.569 | 173.24 | 7.63 | 163.262 | 2177.33 | 25.89 | 47.894 | 6.38 | 1.299 | 4.314 | 8359.34 | 1.789 | 97.8 | 76.9 | 1415 | 23.95 | 5433.6 | 2765.6 | 2703.3 | 3993.2 | 1203.9 | 0.67568 | 5.611
2024-12-09 | 20:11 | Data | 0 | 33.183 | 31.555 | 173.105 | 7.62 | 163.262 | 2172.81 | 25.89 | 47.894 | 6.38 | 1.294 | 4.332 | 8386.47 | 1.782 | 97.8 | 77 | 1412 | 23.99 | 5451.2 | 2762.1 | 2714.3 | 3999.8 | 1203.9 | 0.67176 | 5.625
2024-12-09 | 20:11 | Data | 0 | 33.088 | 31.562 | 173.195 | 7.63 | 163.217 | 2173.72 | 25.89 | 47.894 | 6.38 | 1.294 | 4.29 | 8350.29 | 1.796 | 97.8 | 76.8 | 1413 | 23.95 | 5427.7 | 2756.4 | 2737.7 | 4014.2 | 1203.9 | 0.67014 | 5.585
2024-12-09 | 20:12 | Data | 0 | 33.513 | 31.596 | 173.195 | 7.62 | 163.443 | 2171.01 | 25.89 | 47.894 | 6.38 | 1.289 | 4.271 | 8359.34 | 1.776 | 97.8 | 76.8 | 1411 | 23.95 | 5433.6 | 2772.9 | 2680.1 | 3981.2 | 1203.9 | 0.67655 | 5.561
2024-12-09 | 20:12 | Data | 0 | 33.345 | 31.366 | 173.105 | 7.62 | 163.307 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.296 | 4.281 | 8345.77 | 1.863 | 97.8 | 76.8 | 1411 | 23.95 | 5424.8 | 2763 | 2692.3 | 3979.2 | 1203.9 | 0.67781 | 5.577
2024-12-09 | 20:12 | Data | 0 | 33.183 | 31.522 | 173.06 | 7.63 | 163.172 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.302 | 4.304 | 8345.77 | 1.816 | 97.8 | 76.8 | 1411 | 23.95 | 5424.8 | 2770.8 | 2713.4 | 4001.4 | 1203.9 | 0.67597 | 5.605
2024-12-09 | 20:12 | Data | 0 | 33.581 | 31.387 | 173.195 | 7.63 | 163.352 | 2166.49 | 25.89 | 47.894 | 6.38 | 1.297 | 4.302 | 8345.77 | 1.998 | 97.8 | 76.8 | 1408 | 23.95 | 5424.8 | 2772.7 | 2716.2 | 3998.9 | 1203.9 | 0.67837 | 5.599
2024-12-09 | 20:12 | Data | 0 | 33.183 | 31.569 | 173.195 | 7.62 | 163.262 | 2166.49 | 25.89 | 47.894 | 6.38 | 1.297 | 4.296 | 8332.2 | 1.816 | 97.8 | 76.8 | 1408 | 23.95 | 5415.9 | 2759.4 | 2717.6 | 3997.3 | 1203.9 | 0.67297 | 5.594
2024-12-09 | 20:12 | Data | 0 | 33.189 | 31.4 | 173.15 | 7.63 | 163.262 | 2166.49 | 25.89 | 47.804 | 6.38 | 1.309 | 4.313 | 8345.77 | 1.722 | 97.8 | 76.7 | 1408 | 23.95 | 5424.8 | 2772 | 2715.4 | 4002.1 | 1203.9 | 0.67558 | 5.621
2024-12-09 | 20:12 | Data | 0 | 33.102 | 31.569 | 173.105 | 7.63 | 163.262 | 2166.49 | 25.89 | 47.894 | 6.38 | 1.305 | 4.312 | 8345.77 | 1.715 | 97.8 | 76.8 | 1408 | 23.99 | 5424.8 | 2771.9 | 2736.8 | 4013.7 | 1203.9 | 0.67521 | 5.616
2024-12-09 | 20:12 | Data | 0 | 33.183 | 31.461 | 173.195 | 7.63 | 163.262 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.3 | 4.295 | 8359.34 | 1.83 | 97.8 | 76.8 | 1411 | 23.99 | 5433.6 | 2768.2 | 2735.7 | 4017 | 1203.9 | 0.67159 | 5.593
2024-12-09 | 20:12 | Data | 0 | 33.534 | 31.346 | 173.195 | 7.63 | 163.262 | 2170.1 | 25.89 | 47.984 | 6.38 | 1.295 | 4.28 | 8368.38 | 1.681 | 97.8 | 76.8 | 1411 | 23.99 | 5439.4 | 2764.6 | 2721.1 | 3998 | 1203.9 | 0.67422 | 5.573
2024-12-09 | 20:12 | Data | 0 | 33.297 | 31.785 | 173.195 | 7.63 | 163.217 | 2166.49 | 25.9 | 47.894 | 6.39 | 1.302 | 4.269 | 8359.34 | 1.728 | 97.8 | 76.6 | 1408 | 23.9 | 5433.6 | 2748 | 2719.1 | 3990.2 | 1203.9 | 0.6721 | 5.572
2024-12-09 | 20:12 | Data | 0 | 32.973 | 31.461 | 173.15 | 7.62 | 163.307 | 2170.1 | 25.89 | 47.804 | 6.38 | 1.303 | 4.285 | 8368.38 | 1.688 | 97.8 | 76.7 | 1411 | 23.9 | 5439.4 | 2761.6 | 2722.7 | 4004.3 | 1203.9 | 0.67197 | 5.588
2024-12-09 | 20:12 | Data | 0 | 33.311 | 31.785 | 173.24 | 7.63 | 163.262 | 2169.2 | 25.89 | 47.894 | 6.38 | 1.301 | 4.304 | 8345.77 | 1.742 | 97.8 | 76.8 | 1411 | 23.95 | 5424.8 | 2764.4 | 2708.4 | 3999.9 | 1203.9 | 0.67338 | 5.604
2024-12-09 | 20:12 | Data | 0 | 33.52 | 31.515 | 173.331 | 7.62 | 163.352 | 2166.49 | 25.9 | 47.894 | 6.38 | 1.306 | 4.326 | 8332.2 | 1.816 | 97.8 | 76.8 | 1408 | 23.95 | 5415.9 | 2765.9 | 2686.9 | 3979.4 | 1203.9 | 0.67787 | 5.632
2024-12-09 | 20:12 | Data | 0 | 33.183 | 31.542 | 173.195 | 7.62 | 163.217 | 2161.97 | 25.89 | 47.894 | 6.38 | 1.305 | 4.295 | 8323.16 | 1.641 | 97.8 | 76.7 | 1405 | 23.99 | 5410.1 | 2745.3 | 2704.3 | 3982.3 | 1203.9 | 0.67208 | 5.6
2024-12-09 | 20:12 | Data | 0 | 33.169 | 31.562 | 173.15 | 7.63 | 163.217 | 2161.06 | 25.9 | 47.894 | 6.38 | 1.303 | 4.267 | 8314.11 | 1.823 | 97.8 | 76.6 | 1405 | 23.95 | 5404.2 | 2764.6 | 2717.2 | 3997 | 1203.9 | 0.67449 | 5.571
2024-12-09 | 20:12 | Data | 0 | 33.183 | 31.542 | 173.105 | 7.62 | 163.172 | 2166.49 | 25.89 | 47.804 | 6.38 | 1.303 | 4.285 | 8354.81 | 1.755 | 97.8 | 76.7 | 1408 | 23.95 | 5430.6 | 2761.6 | 2703.9 | 3986.8 | 1203.9 | 0.6766 | 5.588
2024-12-09 | 20:12 | Data | 0 | 33.183 | 31.785 | 173.195 | 7.63 | 163.307 | 2165.58 | 25.89 | 47.894 | 6.38 | 1.301 | 4.302 | 8345.77 | 1.755 | 97.8 | 76.8 | 1408 | 23.99 | 5424.8 | 2766.8 | 2707.3 | 3995 | 1203.9 | 0.67531 | 5.601
2024-12-09 | 20:12 | Data | 0 | 33.412 | 31.461 | 173.195 | 7.63 | 163.307 | 2167.39 | 25.89 | 47.894 | 6.38 | 1.302 | 4.309 | 8354.81 | 1.836 | 97.8 | 76.8 | 1408 | 23.95 | 5430.6 | 2775 | 2718 | 4006.8 | 1203.9 | 0.67621 | 5.611
2024-12-09 | 20:13 | Data | 0 | 33.196 | 31.515 | 173.24 | 7.63 | 163.307 | 2179.14 | 25.89 | 47.894 | 6.38 | 1.303 | 4.302 | 8350.29 | 1.836 | 97.8 | 76.7 | 1417 | 23.95 | 5427.7 | 2739.9 | 2717 | 3983.6 | 1203.9 | 0.671 | 5.605
2024-12-09 | 20:13 | Data | 0 | 33.473 | 31.528 | 173.331 | 7.63 | 163.352 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.303 | 4.307 | 8332.2 | 1.762 | 97.8 | 76.8 | 1411 | 23.95 | 5415.9 | 2767.1 | 2727.9 | 4009.1 | 1203.9 | 0.67345 | 5.61
2024-12-09 | 20:13 | Data | 0 | 33.183 | 31.731 | 173.15 | 7.63 | 163.262 | 2163.77 | 25.89 | 48.075 | 6.38 | 1.301 | 4.286 | 8323.16 | 1.782 | 97.8 | 76.7 | 1406 | 24.04 | 5410.1 | 2740.2 | 2711.2 | 3978.2 | 1203.9 | 0.67193 | 5.588
2024-12-09 | 20:13 | Data | 0 | 33.196 | 31.738 | 173.195 | 7.63 | 163.307 | 2171.91 | 25.89 | 48.165 | 6.38 | 1.299 | 4.321 | 8332.2 | 1.62 | 97.8 | 76.9 | 1412 | 24.08 | 5415.9 | 2758.9 | 2728.1 | 3999.9 | 1203.9 | 0.67219 | 5.62
2024-12-09 | 20:13 | Data | 0 | 33.493 | 31.792 | 173.195 | 7.63 | 163.262 | 2159.26 | 25.9 | 48.165 | 6.38 | 1.306 | 4.304 | 8341.25 | 1.89 | 97.8 | 76.7 | 1403 | 24.08 | 5421.8 | 2765.1 | 2727.4 | 4007.7 | 1203.9 | 0.67274 | 5.61
2024-12-09 | 20:13 | Data | 0 | 33.183 | 31.447 | 173.195 | 7.62 | 163.262 | 2170.1 | 25.89 | 48.165 | 6.38 | 1.306 | 4.31 | 8345.77 | 1.641 | 97.8 | 76.7 | 1411 | 24.08 | 5424.8 | 2751.4 | 2733.6 | 4004.6 | 1203.9 | 0.67158 | 5.616
2024-12-09 | 20:13 | Data | 0 | 33.183 | 31.468 | 173.105 | 7.63 | 163.217 | 2169.2 | 25.89 | 47.894 | 6.38 | 1.302 | 4.309 | 8345.77 | 1.789 | 97.8 | 76.8 | 1411 | 23.95 | 5424.8 | 2768.2 | 2753.3 | 4026 | 1203.9 | 0.66853 | 5.612
2024-12-09 | 20:13 | Data | 0 | 33.183 | 31.562 | 173.24 | 7.62 | 163.172 | 2171.01 | 25.89 | 47.894 | 6.38 | 1.292 | 4.313 | 8345.77 | 1.742 | 97.8 | 76.9 | 1411 | 23.95 | 5424.8 | 2766.8 | 2726 | 4006.6 | 1203.9 | 0.67359 | 5.605
2024-12-09 | 20:13 | Data | 0 | 33.513 | 31.799 | 173.421 | 7.63 | 163.262 | 2170.1 | 25.89 | 48.075 | 6.38 | 1.292 | 4.309 | 8345.77 | 1.722 | 97.8 | 76.9 | 1411 | 24.08 | 5424.8 | 2751.6 | 2757.5 | 4018.4 | 1203.9 | 0.66673 | 5.602
2024-12-09 | 20:13 | Data | 0 | 33.297 | 31.569 | 173.421 | 7.63 | 163.217 | 2089.66 | 25.89 | 47.894 | 6.38 | 1.3 | 4.305 | 8350.29 | 1.627 | 97.7 | 76.8 | 1357 | 23.95 | 5427.7 | 2768.9 | 2747.3 | 4021.2 | 1203.9 | 0.67033 | 5.605
2024-12-09 | 20:13 | Data | 0 | 33.399 | 31.94 | 173.24 | 7.63 | 163.307 | 2132.14 | 25.89 | 47.894 | 6.38 | 1.302 | 4.295 | 8363.86 | 1.951 | 97.8 | 76.7 | 1391 | 23.95 | 5436.5 | 2776.2 | 2704.3 | 3997.6 | 1203.9 | 0.67671 | 5.598
2024-12-09 | 20:13 | Data | 0 | 33.405 | 31.569 | 173.15 | 7.62 | 163.307 | 2158.35 | 25.89 | 47.894 | 6.38 | 1.293 | 4.317 | 8354.81 | 1.843 | 97.8 | 76.9 | 1403 | 23.95 | 5430.6 | 2760.3 | 2701.6 | 3982.1 | 1203.9 | 0.67569 | 5.61
2024-12-09 | 20:13 | Data | 0 | 33.358 | 31.785 | 173.331 | 7.63 | 163.262 | 2155.64 | 25.89 | 47.894 | 6.38 | 1.301 | 4.304 | 8345.77 | 1.789 | 97.8 | 76.8 | 1401 | 23.95 | 5424.8 | 2764.7 | 2711.9 | 3994.3 | 1203.9 | 0.67469 | 5.605
2024-12-09 | 20:13 | Data | 0 | 32.967 | 31.339 | 173.376 | 7.63 | 163.172 | 2158.35 | 25.89 | 47.894 | 6.38 | 1.302 | 4.331 | 8345.77 | 1.789 | 97.8 | 76.9 | 1404 | 23.95 | 5424.8 | 2752.5 | 2717.2 | 3994.2 | 1203.9 | 0.67429 | 5.634
2024-12-09 | 20:13 | Data | 0 | 33.581 | 31.603 | 173.24 | 7.63 | 163.352 | 2178.24 | 25.89 | 47.894 | 6.38 | 1.303 | 4.317 | 8350.29 | 1.89 | 97.8 | 76.8 | 1416 | 23.95 | 5427.7 | 2752.7 | 2703.9 | 3981 | 1204 | 0.67493 | 5.619
2024-12-09 | 20:13 | Data | 0 | 33.25 | 31.522 | 173.24 | 7.63 | 163.262 | 2169.2 | 25.89 | 47.894 | 6.38 | 1.306 | 4.332 | 8345.77 | 1.728 | 97.8 | 76.8 | 1412 | 23.95 | 5424.8 | 2752.8 | 2728.5 | 4002.8 | 1204 | 0.67016 | 5.638
2024-12-09 | 20:13 | Data | 0 | 33.297 | 31.738 | 173.15 | 7.62 | 163.262 | 2172.81 | 25.89 | 47.894 | 6.38 | 1.307 | 4.298 | 8345.77 | 1.728 | 97.8 | 76.7 | 1412 | 23.95 | 5424.8 | 2748.1 | 2752.1 | 4013.5 | 1204 | 0.66626 | 5.604
2024-12-09 | 20:14 | Data | 0 | 33.432 | 31.4 | 173.06 | 7.63 | 163.262 | 2175.52 | 25.89 | 47.984 | 6.38 | 1.303 | 4.288 | 8363.86 | 1.735 | 97.8 | 76.7 | 1414 | 23.95 | 5436.5 | 2760.4 | 2727.4 | 4004.9 | 1204 | 0.67089 | 5.591
2024-12-09 | 20:14 | Data | 0 | 33.196 | 31.792 | 173.24 | 7.63 | 163.262 | 2175.52 | 25.89 | 48.075 | 6.38 | 1.306 | 4.305 | 8363.86 | 1.553 | 97.8 | 76.7 | 1414 | 24.04 | 5436.5 | 2769.2 | 2732.4 | 4016.3 | 1204 | 0.67148 | 5.61
2024-12-09 | 20:14 | Data | 0 | 33.486 | 31.36 | 173.195 | 7.63 | 163.262 | 2174.62 | 25.89 | 48.075 | 6.38 | 1.305 | 4.297 | 8372.9 | 1.87 | 97.8 | 76.7 | 1414 | 24.04 | 5442.4 | 2761.7 | 2725.6 | 4007.6 | 1204 | 0.67032 | 5.603
2024-12-09 | 20:14 | Data | 0 | 33.385 | 31.562 | 173.24 | 7.63 | 163.217 | 2166.49 | 25.89 | 48.165 | 6.38 | 1.302 | 4.283 | 8350.29 | 1.843 | 97.8 | 76.7 | 1408 | 24.08 | 5427.7 | 2745.3 | 2717.2 | 3987.2 | 1204 | 0.67048 | 5.586
2024-12-09 | 20:14 | Data | 0 | 33.21 | 31.569 | 173.24 | 7.62 | 163.172 | 2178.24 | 25.89 | 48.075 | 6.38 | 1.295 | 4.285 | 8368.38 | 1.62 | 97.8 | 76.8 | 1416 | 24.08 | 5439.4 | 2738.3 | 2688.7 | 3967.2 | 1204 | 0.67247 | 5.581
2024-12-09 | 20:14 | Data | 0 | 33.075 | 31.171 | 173.105 | 7.63 | 163.262 | 2174.62 | 25.9 | 47.894 | 6.38 | 1.299 | 4.298 | 8372.9 | 1.911 | 97.8 | 76.8 | 1414 | 23.95 | 5442.4 | 2750.6 | 2698.6 | 3978.1 | 1204 | 0.67328 | 5.597
2024-12-09 | 20:14 | Data | 0 | 33.183 | 31.461 | 173.24 | 7.63 | 163.352 | 2177.33 | 25.89 | 47.984 | 6.38 | 1.311 | 4.306 | 8377.43 | 1.83 | 97.8 | 76.7 | 1416 | 23.99 | 5445.3 | 2750 | 2693.1 | 3973.1 | 1204 | 0.67617 | 5.618
2024-12-09 | 20:14 | Data | 0 | 33.196 | 31.562 | 173.15 | 7.63 | 163.262 | 2178.24 | 25.89 | 47.984 | 6.38 | 1.304 | 4.313 | 8381.95 | 1.742 | 97.8 | 76.8 | 1415 | 23.95 | 5448.3 | 2767.8 | 2696.2 | 3983.6 | 1204 | 0.67802 | 5.617
2024-12-09 | 20:14 | Data | 0 | 33.378 | 31.61 | 173.331 | 7.62 | 163.307 | 2178.24 | 25.89 | 48.165 | 6.38 | 1.306 | 4.305 | 8359.34 | 1.83 | 97.8 | 76.7 | 1416 | 24.08 | 5433.6 | 2731.3 | 2630.5 | 3920.7 | 1204 | 0.68165 | 5.611
2024-12-09 | 20:14 | Data | 0 | 33.635 | 31.819 | 173.331 | 7.62 | 163.443 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.306 | 4.3 | 8363.86 | 1.755 | 97.8 | 76.7 | 1414 | 23.95 | 5436.5 | 2748.8 | 2701.3 | 3977.3 | 1204 | 0.67412 | 5.604
2024-12-09 | 20:14 | Data | 0 | 33.21 | 31.515 | 173.195 | 7.62 | 163.307 | 2171.91 | 25.9 | 47.984 | 6.38 | 1.301 | 4.294 | 8359.34 | 1.843 | 97.8 | 76.8 | 1412 | 23.99 | 5433.6 | 2753.7 | 2704.6 | 3986.6 | 1204 | 0.67327 | 5.594
2024-12-09 | 20:14 | Data | 0 | 33.196 | 31.515 | 173.105 | 7.62 | 163.262 | 2167.39 | 25.89 | 47.804 | 6.38 | 1.294 | 4.287 | 8381.95 | 1.668 | 97.8 | 76.8 | 1409 | 23.9 | 5448.3 | 2739.2 | 2703.3 | 3979.1 | 1204 | 0.67082 | 5.581
2024-12-09 | 20:14 | Data | 0 | 33.243 | 31.596 | 173.24 | 7.63 | 163.352 | 2169.2 | 25.89 | 47.894 | 6.38 | 1.302 | 4.301 | 8350.29 | 1.688 | 97.8 | 76.8 | 1411 | 23.95 | 5427.7 | 2751.3 | 2700.7 | 3981.1 | 1204 | 0.67317 | 5.603
2024-12-09 | 20:14 | Data | 0 | 33.399 | 31.569 | 173.331 | 7.62 | 163.262 | 2170.1 | 25.9 | 47.894 | 6.38 | 1.305 | 4.277 | 8323.16 | 1.843 | 97.8 | 76.6 | 1411 | 23.95 | 5410.1 | 2739.7 | 2695.5 | 3966.3 | 1204 | 0.66935 | 5.582
2024-12-09 | 20:14 | Data | 0 | 33.5 | 31.961 | 173.421 | 7.63 | 163.262 | 2164.68 | 25.89 | 47.894 | 6.38 | 1.3 | 4.271 | 8345.77 | 1.708 | 97.8 | 76.7 | 1407 | 23.95 | 5424.8 | 2734.5 | 2696 | 3966.6 | 1204 | 0.67283 | 5.572
2024-12-09 | 20:14 | Data | 0 | 33.183 | 31.366 | 173.331 | 7.63 | 163.307 | 2171.91 | 25.89 | 47.894 | 6.38 | 1.301 | 4.297 | 8332.2 | 1.965 | 97.8 | 76.8 | 1412 | 23.95 | 5415.9 | 2724 | 2689 | 3954.1 | 1204 | 0.67114 | 5.598
2024-12-09 | 20:14 | Data | 0 | 33.189 | 31.569 | 173.331 | 7.63 | 163.307 | 2166.49 | 25.89 | 47.804 | 6.38 | 1.301 | 4.301 | 8345.77 | 1.789 | 97.8 | 76.8 | 1408 | 23.9 | 5424.8 | 2762.3 | 2702.8 | 3989 | 1204 | 0.67616 | 5.603
2024-12-09 | 20:14 | Data | 0 | 33.081 | 31.454 | 173.24 | 7.63 | 163.307 | 2162.87 | 25.89 | 47.894 | 6.38 | 1.3 | 4.283 | 8345.77 | 1.641 | 97.8 | 76.7 | 1406 | 23.95 | 5424.8 | 2774.3 | 2705.8 | 3994.2 | 1204 | 0.67718 | 5.583
2024-12-09 | 20:15 | Data | 0 | 33.21 | 31.569 | 173.331 | 7.63 | 163.307 | 2171.91 | 25.89 | 47.984 | 6.38 | 1.304 | 4.303 | 8345.77 | 1.62 | 97.8 | 76.7 | 1412 | 23.95 | 5424.8 | 2759.2 | 2699.8 | 3981.1 | 1204 | 0.6739 | 5.608
2024-12-09 | 20:15 | Data | 0 | 33.21 | 31.522 | 173.195 | 7.63 | 163.217 | 2172.81 | 25.89 | 47.894 | 6.38 | 1.31 | 4.304 | 8359.34 | 1.89 | 97.8 | 76.6 | 1412 | 23.9 | 5433.6 | 2756.6 | 2715 | 3995.5 | 1204 | 0.67265 | 5.616
2024-12-09 | 20:15 | Data | 0 | 33.297 | 31.738 | 173.195 | 7.63 | 163.262 | 2172.81 | 25.89 | 47.894 | 6.38 | 1.296 | 4.299 | 8363.86 | 1.708 | 97.8 | 76.8 | 1412 | 23.95 | 5436.5 | 2735.9 | 2718.3 | 3988.9 | 1204 | 0.66773 | 5.595
2024-12-09 | 20:15 | Data | 0 | 33.358 | 31.461 | 173.195 | 7.63 | 163.307 | 2172.81 | 25.89 | 47.894 | 6.37 | 1.309 | 4.309 | 8350.29 | 1.938 | 97.8 | 76.7 | 1412 | 23.95 | 5427.7 | 2755.1 | 2699.1 | 3980.2 | 1204 | 0.67617 | 5.617
2024-12-09 | 20:15 | Data | 0 | 33.412 | 31.967 | 173.24 | 7.62 | 163.307 | 2171.91 | 25.89 | 47.804 | 6.38 | 1.302 | 4.314 | 8363.86 | 1.647 | 97.8 | 76.8 | 1412 | 23.95 | 5436.5 | 2758.8 | 2696.2 | 3982.2 | 1204 | 0.67575 | 5.617
2024-12-09 | 20:15 | Data | 0 | 33.358 | 31.785 | 173.331 | 7.63 | 163.307 | 2166.49 | 25.89 | 47.804 | 6.37 | 1.291 | 4.315 | 8359.34 | 1.634 | 97.8 | 77 | 1408 | 23.95 | 5433.6 | 2742.7 | 2691.2 | 3948.5 | 1204 | 0.67358 | 5.607
2024-12-09 | 20:15 | Data | 0 | 33.412 | 31.623 | 173.331 | 7.63 | 163.307 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.302 | 4.313 | 8359.34 | 1.789 | 97.8 | 76.8 | 1411 | 23.95 | 5433.6 | 2761.6 | 2705.9 | 3986.8 | 1204 | 0.67512 | 5.615
2024-12-09 | 20:15 | Data | 0 | 33.297 | 31.562 | 173.195 | 7.63 | 163.307 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.296 | 4.292 | 8359.34 | 1.863 | 97.8 | 76.8 | 1411 | 23.95 | 5433.6 | 2745.8 | 2705.5 | 3976.8 | 1204 | 0.67296 | 5.587
2024-12-09 | 20:15 | Data | 0 | 33.297 | 31.569 | 173.24 | 7.63 | 163.352 | 2163.77 | 25.89 | 47.623 | 6.38 | 1.292 | 4.305 | 8363.86 | 1.62 | 97.8 | 76.9 | 1407 | 23.86 | 5436.5 | 2755.2 | 2701.3 | 3983 | 1204 | 0.67504 | 5.599
2024-12-09 | 20:15 | Data | 0 | 33.257 | 31.515 | 173.195 | 7.63 | 163.307 | 2169.2 | 25.9 | 47.804 | 6.38 | 1.303 | 4.314 | 8354.81 | 1.647 | 97.8 | 76.8 | 1410 | 23.95 | 5430.6 | 2748.1 | 2711.9 | 3983.1 | 1204 | 0.67306 | 5.617
2024-12-09 | 20:15 | Data | 0 | 33.189 | 31.353 | 173.376 | 7.63 | 163.352 | 2171.91 | 25.9 | 47.804 | 6.38 | 1.302 | 4.317 | 8332.2 | 1.782 | 97.8 | 76.8 | 1412 | 23.95 | 5415.9 | 2748.5 | 2717.4 | 3986.3 | 1204 | 0.67352 | 5.619
2024-12-09 | 20:15 | Data | 0 | 33.237 | 31.569 | 173.24 | 7.63 | 163.262 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.296 | 4.319 | 8336.72 | 1.627 | 97.8 | 76.9 | 1414 | 23.95 | 5418.9 | 2772 | 2696.8 | 3989.3 | 1204 | 0.67716 | 5.615
2024-12-09 | 20:15 | Data | 0 | 33.52 | 31.623 | 173.24 | 7.63 | 163.307 | 2178.24 | 25.89 | 47.894 | 6.38 | 1.301 | 4.308 | 8350.29 | 1.843 | 97.8 | 76.8 | 1415 | 23.95 | 5427.7 | 2766 | 2687.2 | 3980.2 | 1204 | 0.67765 | 5.61
2024-12-09 | 20:15 | Data | 0 | 33.297 | 31.461 | 173.15 | 7.62 | 163.307 | 2179.14 | 25.89 | 47.894 | 6.38 | 1.307 | 4.292 | 8350.29 | 1.843 | 97.8 | 76.7 | 1416 | 23.95 | 5427.7 | 2758.2 | 2704.4 | 3983.5 | 1204 | 0.67419 | 5.599
2024-12-09 | 20:15 | Data | 0 | 33.297 | 31.772 | 173.195 | 7.63 | 163.262 | 2180.04 | 25.89 | 47.894 | 6.38 | 1.295 | 4.3 | 8363.86 | 1.627 | 97.8 | 76.9 | 1417 | 23.95 | 5436.5 | 2757.2 | 2708.2 | 3987.1 | 1204 | 0.6738 | 5.595
2024-12-09 | 20:15 | Data | 0 | 33.412 | 31.738 | 173.195 | 7.62 | 163.307 | 2178.24 | 25.9 | 48.075 | 6.37 | 1.288 | 4.314 | 8372.9 | 1.728 | 97.8 | 77 | 1416 | 24.04 | 5442.4 | 2744.9 | 2704.3 | 3979.9 | 1204 | 0.67198 | 5.601
2024-12-09 | 20:15 | Data | 0 | 33.196 | 31.461 | 173.195 | 7.63 | 163.307 | 2175.52 | 25.89 | 48.165 | 6.38 | 1.293 | 4.304 | 8368.38 | 1.722 | 97.8 | 76.9 | 1414 | 24.04 | 5439.4 | 2776.8 | 2709.4 | 4002.1 | 1204 | 0.677 | 5.597
2024-12-09 | 20:16 | Data | 0 | 33.385 | 31.772 | 173.24 | 7.63 | 163.307 | 2180.04 | 25.89 | 48.165 | 6.38 | 1.301 | 4.279 | 8368.38 | 1.857 | 97.8 | 76.7 | 1416 | 24.08 | 5439.4 | 2751 | 2705.3 | 3978.2 | 1204.1 | 0.67266 | 5.581
2024-12-09 | 20:16 | Data | 0 | 33.21 | 31.461 | 173.376 | 7.62 | 163.443 | 2178.24 | 25.89 | 48.255 | 6.38 | 1.295 | 4.321 | 8368.38 | 1.83 | 97.8 | 76.9 | 1415 | 24.08 | 5439.4 | 2753 | 2740.3 | 3997.6 | 1204.1 | 0.67127 | 5.616
2024-12-09 | 20:16 | Data | 0 | 32.987 | 31.562 | 173.105 | 7.63 | 163.217 | 2176.43 | 25.89 | 47.984 | 6.38 | 1.31 | 4.316 | 8377.43 | 1.519 | 97.8 | 76.7 | 1415 | 23.99 | 5445.3 | 2744.5 | 2735 | 3996 | 1204.1 | 0.66962 | 5.627
2024-12-09 | 20:16 | Data | 0 | 33.243 | 31.711 | 173.15 | 7.62 | 163.307 | 2180.95 | 25.89 | 47.894 | 6.38 | 1.302 | 4.285 | 8377.43 | 1.728 | 97.8 | 76.7 | 1418 | 23.9 | 5445.3 | 2752.8 | 2724.8 | 3998.3 | 1204.1 | 0.67104 | 5.588
2024-12-09 | 20:16 | Data | 0 | 33.189 | 31.569 | 173.195 | 7.62 | 163.262 | 2174.62 | 25.89 | 48.255 | 6.38 | 1.305 | 4.307 | 8372.9 | 1.614 | 97.8 | 76.7 | 1414 | 24.08 | 5442.4 | 2758.3 | 2717.8 | 3994.3 | 1204.1 | 0.67271 | 5.612
2024-12-09 | 20:16 | Data | 0 | 33.297 | 31.569 | 173.331 | 7.62 | 163.262 | 2177.33 | 25.89 | 48.075 | 6.38 | 1.286 | 4.287 | 8363.86 | 1.83 | 97.8 | 76.9 | 1415 | 24.04 | 5436.5 | 2773.7 | 2717.2 | 4002.7 | 1204.1 | 0.67604 | 5.573
2024-12-09 | 20:16 | Data | 0 | 33.189 | 31.562 | 173.331 | 7.63 | 163.307 | 2177.33 | 25.89 | 48.165 | 6.38 | 1.297 | 4.286 | 8354.81 | 1.62 | 97.8 | 76.8 | 1415 | 24.08 | 5430.6 | 2737.1 | 2709.7 | 3977.2 | 1204.1 | 0.66926 | 5.582
2024-12-09 | 20:16 | Data | 0 | 33.574 | 31.623 | 173.331 | 7.63 | 163.352 | 2175.52 | 25.89 | 48.165 | 6.38 | 1.292 | 4.268 | 8359.34 | 1.816 | 97.8 | 76.8 | 1414 | 24.04 | 5433.6 | 2751.2 | 2716.7 | 3993.4 | 1204.1 | 0.67002 | 5.561
2024-12-09 | 20:16 | Data | 0 | 33.25 | 31.569 | 173.24 | 7.63 | 163.307 | 2175.52 | 25.89 | 48.165 | 6.37 | 1.299 | 4.294 | 8368.38 | 1.627 | 97.8 | 76.8 | 1414 | 24.08 | 5439.4 | 2757.6 | 2703.6 | 3986.2 | 1204.1 | 0.6741 | 5.593
2024-12-09 | 20:16 | Data | 0 | 33.304 | 31.785 | 173.331 | 7.62 | 163.307 | 2178.24 | 25.9 | 48.255 | 6.37 | 1.305 | 4.323 | 8400.04 | 1.674 | 97.8 | 76.8 | 1415 | 24.08 | 5460 | 2756 | 2693.2 | 3978.8 | 1204.1 | 0.67475 | 5.628
2024-12-09 | 20:16 | Data | 0 | 33.196 | 31.677 | 173.376 | 7.63 | 163.443 | 2178.24 | 25.89 | 48.075 | 6.38 | 1.302 | 4.302 | 8440.74 | 1.627 | 97.8 | 76.8 | 1415 | 24.04 | 5486.5 | 2747 | 2712.5 | 3980.3 | 1204.1 | 0.67147 | 5.604
2024-12-09 | 20:16 | Data | 0 | 33.621 | 31.596 | 173.376 | 7.63 | 163.443 | 2180.04 | 25.89 | 48.255 | 6.38 | 1.301 | 4.304 | 8400.04 | 1.836 | 97.8 | 76.8 | 1417 | 24.08 | 5460 | 2760.4 | 2713.1 | 3984.5 | 1204.1 | 0.67673 | 5.602
2024-12-09 | 20:16 | Data | 0 | 33.399 | 31.569 | 173.331 | 7.63 | 163.352 | 2174.62 | 25.89 | 48.075 | 6.37 | 1.299 | 4.297 | 8400.04 | 1.843 | 97.8 | 76.8 | 1414 | 24.04 | 5460 | 2764.1 | 2718.4 | 4002.3 | 1204.1 | 0.67215 | 5.596
2024-12-09 | 20:16 | Data | 0 | 33.189 | 31.772 | 173.15 | 7.63 | 163.262 | 2175.52 | 25.89 | 48.165 | 6.38 | 1.301 | 4.299 | 8400.04 | 1.755 | 97.8 | 76.8 | 1414 | 24.08 | 5460 | 2740.9 | 2742.3 | 3985.6 | 1204.1 | 0.66884 | 5.6
2024-12-09 | 20:16 | Data | 0 | 33.405 | 31.576 | 173.376 | 7.63 | 163.307 | 2174.62 | 25.89 | 47.894 | 6.37 | 1.31 | 4.316 | 8386.47 | 1.816 | 97.8 | 76.7 | 1414 | 23.99 | 5451.2 | 2777.9 | 2701.2 | 3995.4 | 1204.1 | 0.67752 | 5.627
2024-12-09 | 20:16 | Data | 0 | 33.412 | 31.684 | 173.331 | 7.62 | 163.443 | 2165.58 | 25.89 | 48.165 | 6.38 | 1.306 | 4.322 | 8386.47 | 1.83 | 97.8 | 76.8 | 1407 | 24.08 | 5451.2 | 2729.8 | 2701.3 | 3970.4 | 1204.1 | 0.66965 | 5.629
2024-12-09 | 20:16 | Data | 0 | 33.588 | 31.805 | 173.512 | 7.63 | 163.488 | 2176.43 | 25.89 | 48.165 | 6.38 | 1.304 | 4.295 | 8377.43 | 1.816 | 97.8 | 76.7 | 1415 | 24.08 | 5445.3 | 2729.8 | 2718.6 | 3980.1 | 1204.1 | 0.66775 | 5.598
2024-12-09 | 20:16 | Data | 0 | 33.412 | 31.596 | 173.331 | 7.63 | 163.307 | 2174.62 | 25.89 | 48.165 | 6.37 | 1.301 | 4.283 | 8372.9 | 1.782 | 97.8 | 76.7 | 1414 | 24.08 | 5442.4 | 2755.5 | 2717.5 | 3993 | 1204.1 | 0.67303 | 5.583
2024-12-09 | 20:16 | Data | 0 | 33.189 | 31.454 | 173.24 | 7.62 | 163.443 | 2180.04 | 25.89 | 47.623 | 6.38 | 1.297 | 4.313 | 8381.95 | 1.728 | 97.8 | 76.9 | 1418 | 23.81 | 5448.3 | 2749.4 | 2727.8 | 3999.7 | 1204.1 | 0.67067 | 5.609
2024-12-09 | 20:17 | Data | 0 | 33.203 | 31.745 | 173.376 | 7.62 | 163.443 | 2177.33 | 25.9 | 47.894 | 6.38 | 1.289 | 4.325 | 8390.99 | 1.62 | 97.8 | 77 | 1415 | 23.95 | 5454.1 | 2761 | 2711.8 | 3992.5 | 1204.1 | 0.67505 | 5.614
2024-12-09 | 20:17 | Data | 0 | 33.196 | 31.346 | 173.195 | 7.62 | 163.352 | 2178.24 | 25.89 | 48.165 | 6.38 | 1.301 | 4.297 | 8372.9 | 1.836 | 97.8 | 76.8 | 1415 | 24.04 | 5442.4 | 2752 | 2707.4 | 3986 | 1204.1 | 0.67134 | 5.599
2024-12-09 | 20:17 | Data | 0 | 33.189 | 31.616 | 173.376 | 7.63 | 163.352 | 2178.24 | 25.89 | 48.075 | 6.38 | 1.297 | 4.28 | 8368.38 | 1.742 | 97.8 | 76.7 | 1416 | 24.08 | 5439.4 | 2759.4 | 2733.8 | 3999.6 | 1204.1 | 0.67267 | 5.577
2024-12-09 | 20:17 | Data | 0 | 33.52 | 31.596 | 173.376 | 7.63 | 163.262 | 2178.24 | 25.89 | 47.984 | 6.38 | 1.301 | 4.33 | 8345.77 | 1.998 | 97.8 | 76.9 | 1416 | 23.95 | 5424.8 | 2745.1 | 2717.9 | 3988.7 | 1204.1 | 0.67114 | 5.629
2024-12-09 | 20:17 | Data | 0 | 33.243 | 31.562 | 173.467 | 7.63 | 163.352 | 2177.33 | 25.89 | 47.894 | 6.38 | 1.308 | 4.336 | 8336.72 | 1.884 | 97.8 | 76.8 | 1416 | 23.99 | 5418.9 | 2764.5 | 2702.7 | 3990.1 | 1204.1 | 0.67567 | 5.644
2024-12-09 | 20:17 | Data | 0 | 33.635 | 31.691 | 173.376 | 7.63 | 163.307 | 2171.91 | 25.89 | 48.165 | 6.38 | 1.3 | 4.316 | 8336.72 | 1.735 | 97.8 | 76.9 | 1412 | 24.13 | 5418.9 | 2749.9 | 2691.3 | 3979.4 | 1204.1 | 0.67707 | 5.615
2024-12-09 | 20:17 | Data | 0 | 33.183 | 31.88 | 173.376 | 7.63 | 163.443 | 2178.24 | 25.89 | 47.984 | 6.38 | 1.296 | 4.273 | 8336.72 | 1.627 | 97.8 | 76.7 | 1415 | 23.99 | 5418.9 | 2751.7 | 2689.2 | 3964.4 | 1204.1 | 0.67437 | 5.57
2024-12-09 | 20:17 | Data | 0 | 33.466 | 31.63 | 173.512 | 7.62 | 163.488 | 2177.33 | 25.89 | 47.804 | 6.37 | 1.296 | 4.284 | 8336.72 | 1.735 | 97.8 | 76.8 | 1416 | 23.9 | 5418.9 | 2746.1 | 2693.4 | 3968 | 1204.1 | 0.67481 | 5.579
2024-12-09 | 20:17 | Data | 0 | 33.723 | 31.616 | 173.421 | 7.63 | 163.533 | 2178.24 | 25.89 | 47.894 | 6.37 | 1.291 | 4.3 | 8332.2 | 1.89 | 97.8 | 76.9 | 1415 | 23.95 | 5415.9 | 2754.9 | 2712.7 | 3992.3 | 1204.1 | 0.67188 | 5.591
2024-12-09 | 20:17 | Data | 0 | 33.635 | 31.704 | 173.467 | 7.63 | 163.352 | 2166.49 | 25.89 | 47.984 | 6.37 | 1.299 | 4.295 | 8336.72 | 1.89 | 97.8 | 76.8 | 1408 | 23.95 | 5418.9 | 2748.5 | 2723.2 | 3988.3 | 1204.1 | 0.67025 | 5.593
2024-12-09 | 20:17 | Data | 0 | 33.331 | 31.596 | 173.376 | 7.63 | 163.352 | 2178.24 | 25.89 | 47.894 | 6.38 | 1.308 | 4.292 | 8341.25 | 1.533 | 97.8 | 76.6 | 1415 | 23.95 | 5421.8 | 2745.8 | 2702.3 | 3977.9 | 1204.1 | 0.67472 | 5.6
2024-12-09 | 20:17 | Data | 0 | 33.419 | 32.001 | 173.421 | 7.63 | 163.443 | 2177.33 | 25.89 | 47.804 | 6.38 | 1.301 | 4.304 | 8336.72 | 1.62 | 97.8 | 76.8 | 1415 | 23.95 | 5418.9 | 2741.2 | 2700.8 | 3972.6 | 1204.1 | 0.6729 | 5.606
2024-12-09 | 20:17 | Data | 0 | 33.183 | 31.562 | 173.24 | 7.63 | 163.307 | 2177.33 | 25.89 | 47.984 | 6.38 | 1.303 | 4.294 | 8345.77 | 1.627 | 97.8 | 76.7 | 1415 | 23.95 | 5424.8 | 1675.2 | 2147.7 | 2737.8 | 1204.1 | 0.60955 | 5.597
2024-12-09 | 20:17 | Data | 0 | 33.696 | 31.583 | 173.602 | 7.63 | 163.488 | 2180.04 | 25.89 | 47.894 | 6.37 | 1.303 | 4.304 | 8332.2 | 1.634 | 97.8 | 76.8 | 1418 | 23.95 | 5415.9 | 1666.9 | 2125.1 | 2711.1 | 1204.1 | 0.61626 | 5.608
2024-12-09 | 20:17 | Data | 0 | 33.412 | 31.569 | 173.376 | 7.62 | 163.443 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.301 | 4.3 | 8300.55 | 1.843 | 97.8 | 76.8 | 1414 | 23.95 | 5395.4 | 1687.6 | 2128.2 | 2728.7 | 1204.1 | 0.61393 | 5.601
2024-12-09 | 20:17 | Data | 0 | 33.81 | 31.657 | 173.376 | 7.63 | 163.443 | 2174.62 | 25.89 | 47.894 | 6.38 | 1.306 | 4.284 | 8300.55 | 1.944 | 97.8 | 76.6 | 1413 | 23.95 | 5395.4 | 1678.4 | 2116.4 | 2698.3 | 1204.1 | 0.61016 | 5.59
2024-12-09 | 20:17 | Data | 0 | 33.21 | 31.569 | 173.24 | 7.63 | 163.352 | 2166.49 | 25.89 | 47.894 | 6.38 | 1.304 | 4.295 | 8291.5 | 1.614 | 97.8 | 76.7 | 1408 | 23.95 | 5389.5 | 1664.6 | 2144.5 | 2725.7 | 1204.1 | 0.60828 | 5.598
2024-12-09 | 20:18 | Data | 0 | 33.628 | 31.799 | 173.331 | 7.63 | 163.443 | 2174.62 | 25.89 | 47.894 | 6.37 | 1.305 | 4.303 | 8291.5 | 1.728 | 97.8 | 76.7 | 1414 | 23.95 | 5389.5 | 1657.4 | 2136.3 | 2718.4 | 1204.1 | 0.6069 | 5.607
2024-12-09 | 20:18 | Data | 0 | 33.25 | 31.569 | 173.421 | 7.63 | 163.443 | 2177.33 | 25.89 | 47.894 | 6.38 | 1.306 | 4.285 | 8286.98 | 1.627 | 97.8 | 76.6 | 1415 | 23.9 | 5386.5 | 1671.4 | 2124.5 | 2716.6 | 1204.1 | 0.61175 | 5.591
2024-12-09 | 20:18 | Data | 0 | 33.412 | 31.569 | 173.331 | 7.62 | 163.307 | 2176.43 | 25.89 | 47.804 | 6.38 | 1.3 | 4.309 | 8314.11 | 1.843 | 97.8 | 76.8 | 1415 | 23.95 | 5404.2 | 1680 | 2148.8 | 2739.9 | 1204.1 | 0.61098 | 5.609
2024-12-09 | 20:18 | Data | 0 | 33.628 | 31.805 | 173.421 | 7.63 | 163.352 | 2173.72 | 25.89 | 47.804 | 6.38 | 1.31 | 4.306 | 8323.16 | 1.816 | 97.8 | 76.7 | 1414 | 23.95 | 5410.1 | 1669.7 | 2144.5 | 2729.2 | 1204.1 | 0.60594 | 5.617
2024-12-09 | 20:18 | Data | 0 | 33.399 | 31.684 | 173.331 | 7.63 | 163.307 | 2180.04 | 25.89 | 47.894 | 6.38 | 1.3 | 4.287 | 8318.64 | 1.944 | 97.8 | 76.7 | 1417 | 23.99 | 5407.1 | 1653.6 | 2112.3 | 2697 | 1204.1 | 0.6099 | 5.588
2024-12-09 | 20:18 | Data | 0 | 33.311 | 31.569 | 173.195 | 7.63 | 163.352 | 2176.43 | 25.89 | 47.984 | 6.37 | 1.296 | 4.29 | 8318.64 | 1.627 | 97.8 | 76.8 | 1414 | 23.95 | 5407.1 | 1673.7 | 2136.6 | 2728.7 | 1204.1 | 0.61024 | 5.584
2024-12-09 | 20:18 | Data | 0 | 33.412 | 31.684 | 173.24 | 7.63 | 163.307 | 2178.24 | 25.89 | 47.894 | 6.37 | 1.293 | 4.284 | 8318.64 | 1.728 | 97.8 | 76.8 | 1416 | 23.9 | 5407.1 | 1680.8 | 2146.6 | 2734.6 | 1204.1 | 0.60876 | 5.577
2024-12-09 | 20:18 | Data | 0 | 33.183 | 31.569 | 173.331 | 7.63 | 163.352 | 2171.91 | 25.89 | 47.984 | 6.37 | 1.302 | 4.281 | 8332.2 | 1.789 | 97.8 | 76.7 | 1412 | 23.95 | 5415.9 | 1677.9 | 2126.2 | 2722.2 | 1204.1 | 0.61319 | 5.581
2024-12-09 | 20:18 | Data | 0 | 33.203 | 31.569 | 173.467 | 7.63 | 163.352 | 2178.24 | 25.9 | 47.894 | 6.38 | 1.301 | 4.285 | 8332.2 | 1.614 | 97.8 | 76.7 | 1416 | 23.95 | 5415.9 | 1688.1 | 2124.4 | 2727 | 1204.1 | 0.61588 | 5.586
2024-12-09 | 20:18 | Data | 0 | 33.034 | 31.542 | 173.331 | 7.63 | 163.443 | 2178.24 | 25.89 | 47.894 | 6.38 | 1.3 | 4.295 | 8332.2 | 1.62 | 97.8 | 76.8 | 1416 | 23.95 | 5415.9 | 1669.9 | 2121.2 | 2711.5 | 1204.2 | 0.61155 | 5.594
2024-12-09 | 20:18 | Data | 0 | 33.358 | 31.576 | 173.331 | 7.63 | 163.443 | 2177.33 | 25.89 | 47.894 | 6.38 | 1.306 | 4.294 | 8359.34 | 1.499 | 97.8 | 76.7 | 1415 | 23.95 | 5433.6 | 1668.3 | 2119.8 | 2709.5 | 1204.2 | 0.61299 | 5.6
2024-12-09 | 20:18 | Data | 0 | 33.297 | 31.569 | 173.331 | 7.62 | 163.443 | 2176.43 | 25.89 | 47.894 | 6.37 | 1.296 | 4.298 | 8359.34 | 1.789 | 97.8 | 76.8 | 1414 | 23.99 | 5433.6 | 1698.4 | 2130.5 | 2736.8 | 1204.2 | 0.61827 | 5.593
2024-12-09 | 20:18 | Data | 0 | 33.493 | 31.583 | 173.376 | 7.63 | 163.488 | 2172.81 | 25.9 | 47.894 | 6.38 | 1.301 | 4.313 | 8359.34 | 2.025 | 97.8 | 76.8 | 1412 | 23.95 | 5433.6 | 1672.1 | 2123 | 2715.4 | 1204.2 | 0.61245 | 5.613
2024-12-09 | 20:18 | Data | 0 | 33.574 | 31.846 | 173.331 | 7.63 | 163.443 | 2177.33 | 25.89 | 45.727 | 6.38 | 1.306 | 4.303 | 8359.34 | 1.695 | 97.9 | 76.7 | 1416 | 22.86 | 5433.6 | 1683.1 | 2108.9 | 2710.7 | 1204.2 | 0.61804 | 5.608
2024-12-09 | 20:18 | Data | 0 | 33.243 | 31.569 | 173.376 | 7.63 | 163.352 | 2180.95 | 25.89 | 48.165 | 6.38 | 1.306 | 4.29 | 8345.77 | 1.62 | 97.8 | 76.7 | 1417 | 24.04 | 5424.8 | 1672.5 | 2136.5 | 2725.5 | 1204.2 | 0.60625 | 5.596
2024-12-09 | 20:18 | Data | 0 | 33.385 | 31.826 | 173.331 | 7.63 | 163.307 | 2178.24 | 25.89 | 48.255 | 6.38 | 1.296 | 4.313 | 8359.34 | 1.836 | 97.8 | 76.9 | 1416 | 24.08 | 5433.6 | 1667.4 | 2129.4 | 2716.9 | 1204.2 | 0.61098 | 5.609
2024-12-09 | 20:18 | Data | 0 | 33.297 | 31.954 | 173.331 | 7.63 | 163.307 | 2183.66 | 25.89 | 47.894 | 6.38 | 1.304 | 4.313 | 8359.34 | 1.776 | 97.8 | 76.8 | 1419 | 23.95 | 5433.6 | 1675.3 | 2150.7 | 2737.9 | 1204.2 | 0.60944 | 5.616
2024-12-09 | 20:18 | Data | 0 | 33.405 | 31.691 | 173.376 | 7.63 | 163.352 | 2183.66 | 25.89 | 48.165 | 6.38 | 1.312 | 4.298 | 8345.77 | 1.816 | 97.8 | 76.6 | 1419 | 24.08 | 5424.8 | 1670.6 | 2146.2 | 2732.7 | 1204.2 | 0.60798 | 5.61
2024-12-09 | 20:19 | Data | 0 | 33.358 | 31.569 | 173.195 | 7.63 | 163.262 | 2182.75 | 25.89 | 48.075 | 6.38 | 1.31 | 4.286 | 8377.43 | 1.83 | 97.8 | 76.6 | 1419 | 24.08 | 5445.3 | 1649 | 2138.6 | 2714.1 | 1204.2 | 0.6043 | 5.597
2024-12-09 | 20:19 | Data | 0 | 33.243 | 31.569 | 173.376 | 7.63 | 163.352 | 2182.75 | 25.89 | 48.165 | 6.38 | 1.303 | 4.306 | 8368.38 | 1.803 | 97.8 | 76.8 | 1418 | 24.08 | 5439.4 | 1665.7 | 2112.4 | 2702.8 | 1204.2 | 0.61212 | 5.61
2024-12-09 | 20:19 | Data | 0 | 33.196 | 31.569 | 173.105 | 7.62 | 163.307 | 2182.75 | 25.89 | 48.075 | 6.38 | 1.296 | 4.288 | 8372.9 | 1.62 | 97.8 | 76.8 | 1419 | 24.08 | 5442.4 | 1650.4 | 2132.8 | 2709.6 | 1204.2 | 0.60675 | 5.585
2024-12-09 | 20:19 | Data | 0 | 33.405 | 31.9 | 173.421 | 7.63 | 163.262 | 2183.66 | 25.89 | 47.894 | 6.38 | 1.293 | 4.307 | 8368.38 | 1.782 | 97.8 | 76.9 | 1419 | 23.95 | 5439.4 | 1660.8 | 2124.6 | 2709.4 | 1204.2 | 0.6128 | 5.6
2024-12-09 | 20:19 | Data | 0 | 33.405 | 31.555 | 173.105 | 7.63 | 163.217 | 2180.95 | 25.9 | 47.894 | 6.38 | 1.311 | 4.313 | 8363.86 | 1.877 | 97.8 | 76.7 | 1418 | 23.95 | 5436.5 | 1668.3 | 2147.8 | 2732 | 1204.2 | 0.6082 | 5.623
2024-12-09 | 20:19 | Data | 0 | 33.277 | 31.994 | 173.376 | 7.63 | 163.352 | 2182.75 | 25.89 | 47.894 | 6.38 | 1.317 | 4.314 | 8345.77 | 1.87 | 97.8 | 76.6 | 1419 | 23.95 | 5424.8 | 1675.7 | 2156.4 | 2744 | 1204.2 | 0.60754 | 5.633
2024-12-09 | 20:19 | Data | 0 | 33.412 | 31.583 | 173.24 | 7.62 | 163.307 | 2177.33 | 25.9 | 47.894 | 6.38 | 1.306 | 4.318 | 8345.77 | 1.816 | 97.8 | 76.8 | 1416 | 23.99 | 5424.8 | 1686.2 | 2148.5 | 2743.9 | 1204.2 | 0.60932 | 5.623
2024-12-09 | 20:19 | Data | 0 | 33.358 | 31.596 | 173.467 | 7.63 | 163.443 | 2186.37 | 25.89 | 47.804 | 6.37 | 1.291 | 4.312 | 8345.77 | 1.728 | 97.8 | 77 | 1422 | 23.95 | 5424.8 | 1641.3 | 2138.1 | 2709.4 | 1204.2 | 0.60148 | 5.603
2024-12-09 | 20:19 | Data | 0 | 33.081 | 31.569 | 173.421 | 7.62 | 163.352 | 2186.37 | 25.9 | 47.894 | 6.37 | 1.297 | 4.302 | 8336.72 | 1.566 | 97.8 | 76.8 | 1421 | 23.9 | 5418.9 | 1666.9 | 2183.8 | 2759.3 | 1204.2 | 0.60117 | 5.6
2024-12-09 | 20:19 | Data | 0 | 33.527 | 31.596 | 173.512 | 7.63 | 163.443 | 2187.27 | 25.89 | 47.804 | 6.38 | 1.308 | 4.288 | 8332.2 | 1.782 | 97.8 | 76.6 | 1421 | 23.95 | 5415.9 | 1676.1 | 2181.2 | 2762.3 | 1204.2 | 0.6041 | 5.596
2024-12-09 | 20:19 | Data | 0 | 33.129 | 31.934 | 173.195 | 7.63 | 163.352 | 2187.27 | 25.89 | 47.894 | 6.38 | 1.301 | 4.295 | 8350.29 | 1.614 | 97.8 | 76.8 | 1421 | 23.9 | 5427.7 | 1656.7 | 2191.2 | 2759.9 | 1204.2 | 0.59725 | 5.595
2024-12-09 | 20:19 | Data | 0 | 33.412 | 31.461 | 173.24 | 7.62 | 163.352 | 2191.79 | 25.89 | 47.894 | 6.38 | 1.301 | 4.296 | 8350.29 | 1.749 | 97.8 | 76.8 | 1425 | 23.9 | 5427.7 | 1670.8 | 2208.6 | 2782.2 | 1204.2 | 0.59705 | 5.597
2024-12-09 | 20:19 | Data | 0 | 33.183 | 31.569 | 173.421 | 7.63 | 163.352 | 2186.37 | 25.89 | 47.894 | 6.38 | 1.297 | 4.312 | 8345.77 | 1.728 | 97.8 | 76.9 | 1421 | 23.9 | 5424.8 | 1679.6 | 2183.4 | 2765.5 | 1204.2 | 0.60488 | 5.609
2024-12-09 | 20:19 | Data | 0 | 33.52 | 31.799 | 173.421 | 7.62 | 163.352 | 2180.95 | 25.89 | 47.894 | 6.38 | 1.297 | 4.304 | 8350.29 | 1.668 | 97.8 | 76.8 | 1417 | 23.95 | 5427.7 | 1674 | 2190.1 | 2767.9 | 1204.2 | 0.60298 | 5.602
2024-12-09 | 20:19 | Data | 0 | 33.412 | 31.745 | 173.24 | 7.63 | 163.352 | 2178.24 | 25.89 | 47.894 | 6.37 | 1.297 | 4.295 | 8345.77 | 1.668 | 97.8 | 76.8 | 1415 | 23.95 | 5424.8 | 1687.6 | 2166.5 | 2760.2 | 1204.2 | 0.60862 | 5.592
2024-12-09 | 20:19 | Data | 0 | 33.412 | 31.623 | 173.421 | 7.62 | 163.307 | 2177.33 | 25.89 | 47.894 | 6.38 | 1.3 | 4.286 | 8345.77 | 1.708 | 97.8 | 76.7 | 1415 | 23.95 | 5424.8 | 1654 | 2172 | 2744.1 | 1204.2 | 0.59778 | 5.586
2024-12-09 | 20:19 | Data | 0 | 33.183 | 31.542 | 173.24 | 7.63 | 163.262 | 2177.33 | 25.9 | 47.894 | 6.37 | 1.302 | 4.291 | 8345.77 | 1.668 | 97.8 | 76.7 | 1416 | 23.95 | 5424.8 | 1680.9 | 2161.4 | 2739.5 | 1204.2 | 0.60906 | 5.593
2024-12-09 | 20:20 | Data | 0 | 33.189 | 31.596 | 173.24 | 7.63 | 163.262 | 2179.14 | 25.9 | 47.894 | 6.38 | 1.306 | 4.299 | 8359.34 | 1.674 | 97.8 | 76.7 | 1416 | 23.95 | 5433.6 | 1652.5 | 2183.2 | 2750.7 | 1204.2 | 0.59753 | 5.604
2024-12-09 | 20:20 | Data | 0 | 33.183 | 31.569 | 173.24 | 7.62 | 163.217 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.3 | 4.304 | 8363.86 | 1.614 | 97.8 | 76.8 | 1411 | 23.95 | 5436.5 | 1670.8 | 2182.7 | 2760.6 | 1204.2 | 0.59711 | 5.603
2024-12-09 | 20:20 | Data | 0 | 33.351 | 31.562 | 173.24 | 7.63 | 163.217 | 2171.91 | 25.89 | 47.894 | 6.38 | 1.307 | 4.296 | 8359.34 | 1.843 | 97.8 | 76.7 | 1412 | 23.9 | 5433.6 | 1676 | 2197.8 | 2776.4 | 1204.2 | 0.60132 | 5.603
2024-12-09 | 20:20 | Data | 0 | 33.297 | 31.569 | 173.376 | 7.63 | 163.352 | 2172.81 | 25.89 | 47.984 | 6.38 | 1.307 | 4.285 | 8359.34 | 1.641 | 97.8 | 76.6 | 1413 | 23.95 | 5433.6 | 1685.4 | 2192.1 | 2775.9 | 1204.2 | 0.60491 | 5.591
2024-12-09 | 20:20 | Data | 0 | 33.102 | 31.778 | 173.195 | 7.63 | 163.307 | 2174.62 | 25.9 | 47.894 | 6.38 | 1.304 | 4.302 | 8359.34 | 1.654 | 97.8 | 76.7 | 1414 | 23.95 | 5433.6 | 1658.4 | 2156.4 | 2733.7 | 1204.2 | 0.60418 | 5.605
2024-12-09 | 20:20 | Data | 0 | 33.358 | 31.569 | 173.195 | 7.63 | 163.262 | 2171.01 | 25.89 | 47.894 | 6.37 | 1.301 | 4.313 | 8359.34 | 1.83 | 97.8 | 76.8 | 1411 | 23.95 | 5433.6 | 1664.9 | 2146.4 | 2745.6 | 1204.2 | 0.60797 | 5.614
2024-12-09 | 20:20 | Data | 0 | 33.189 | 31.555 | 173.105 | 7.62 | 163.262 | 2167.39 | 25.89 | 47.894 | 6.37 | 1.304 | 4.297 | 8363.86 | 1.641 | 97.8 | 76.7 | 1410 | 23.9 | 5436.5 | 1658.5 | 2145.9 | 2726 | 1204.2 | 0.60572 | 5.602
2024-12-09 | 20:20 | Data | 0 | 33.297 | 31.684 | 173.331 | 7.63 | 163.307 | 2172.81 | 25.89 | 48.165 | 6.37 | 1.3 | 4.282 | 8350.29 | 1.944 | 97.8 | 76.7 | 1412 | 24.08 | 5427.7 | 1667 | 2156.7 | 2739.2 | 1204.2 | 0.60673 | 5.582
2024-12-09 | 20:20 | Data | 0 | 33.399 | 31.569 | 173.376 | 7.62 | 163.307 | 2172.81 | 25.89 | 48.165 | 6.37 | 1.291 | 4.274 | 8332.2 | 1.823 | 97.8 | 76.8 | 1412 | 24.08 | 5415.9 | 1672.8 | 2152.7 | 2726 | 1204.2 | 0.60511 | 5.565
2024-12-09 | 20:20 | Data | 0 | 33.196 | 31.562 | 173.15 | 7.63 | 163.262 | 2175.52 | 25.89 | 48.165 | 6.37 | 1.296 | 4.28 | 8332.2 | 1.62 | 97.8 | 76.8 | 1415 | 24.08 | 5415.9 | 1695.1 | 2161.1 | 2758.1 | 1204.2 | 0.61179 | 5.576
2024-12-09 | 20:20 | Data | 0 | 33.284 | 31.67 | 173.195 | 7.63 | 163.307 | 2175.52 | 25.89 | 48.165 | 6.38 | 1.299 | 4.262 | 8332.2 | 1.863 | 97.8 | 76.7 | 1413 | 24.08 | 5415.9 | 1657.6 | 2154.7 | 2731.8 | 1204.2 | 0.60634 | 5.56
2024-12-09 | 20:20 | Data | 0 | 33.358 | 31.583 | 173.421 | 7.62 | 163.352 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.294 | 4.285 | 8354.81 | 1.809 | 97.8 | 76.8 | 1411 | 23.95 | 5430.6 | 1661.2 | 2185.5 | 2756.2 | 1204.2 | 0.60391 | 5.581
2024-12-09 | 20:20 | Data | 0 | 33.156 | 31.339 | 173.15 | 7.63 | 163.172 | 2170.1 | 25.89 | 47.804 | 6.38 | 1.302 | 4.302 | 8341.25 | 1.836 | 97.8 | 76.8 | 1411 | 23.95 | 5421.8 | 1669.3 | 2181 | 2755.6 | 1204.2 | 0.60345 | 5.604
2024-12-09 | 20:20 | Data | 0 | 33.102 | 31.623 | 173.195 | 7.63 | 163.307 | 2169.2 | 25.89 | 47.984 | 6.38 | 1.304 | 4.318 | 8345.77 | 1.492 | 97.8 | 76.8 | 1411 | 23.95 | 5424.8 | 1662.1 | 2183.4 | 2754.5 | 1204.2 | 0.60193 | 5.622
2024-12-09 | 20:20 | Data | 0 | 33.399 | 31.454 | 173.195 | 7.62 | 163.262 | 2169.2 | 25.89 | 47.894 | 6.38 | 1.301 | 4.318 | 8345.77 | 1.782 | 97.8 | 76.9 | 1411 | 23.95 | 5424.8 | 1696.6 | 2189.3 | 2782.6 | 1204.2 | 0.60289 | 5.619
2024-12-09 | 20:20 | Data | 0 | 33.021 | 31.366 | 173.376 | 7.62 | 163.443 | 2164.68 | 25.89 | 47.894 | 6.38 | 1.291 | 4.287 | 8363.86 | 1.681 | 97.8 | 76.9 | 1407 | 23.95 | 5436.5 | 2966.2 | 3695.1 | 4795.4 | 1204.2 | 0.61604 | 5.578
2024-12-09 | 20:20 | Data | 0 | 33.075 | 31.515 | 173.15 | 7.63 | 163.262 | 2170.1 | 25.9 | 47.894 | 6.37 | 1.286 | 4.273 | 8368.38 | 1.83 | 97.8 | 76.9 | 1411 | 23.95 | 5439.4 | 2757.6 | 2748.5 | 4016.6 | 1204.2 | 0.66968 | 5.558
2024-12-09 | 20:20 | Data | 0 | 33.304 | 31.36 | 173.331 | 7.63 | 163.443 | 2172.81 | 25.89 | 47.894 | 6.38 | 1.296 | 4.283 | 8359.34 | 1.83 | 97.8 | 76.8 | 1412 | 23.95 | 5433.6 | 2753.6 | 2728 | 4004.1 | 1204.2 | 0.6695 | 5.578
2024-12-09 | 20:21 | Data | 0 | 33.412 | 31.583 | 173.195 | 7.62 | 163.307 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.299 | 4.28 | 8359.34 | 1.654 | 97.8 | 76.7 | 1414 | 23.99 | 5433.6 | 2765.8 | 2698.4 | 3987.6 | 1204.2 | 0.67568 | 5.577
2024-12-09 | 20:21 | Data | 0 | 33.574 | 31.623 | 173.331 | 7.63 | 163.352 | 2172.81 | 25.89 | 47.894 | 6.37 | 1.3 | 4.285 | 8350.29 | 1.782 | 97.8 | 76.7 | 1412 | 23.9 | 5427.7 | 2740.6 | 2728 | 3990.7 | 1204.2 | 0.66947 | 5.585
2024-12-09 | 20:21 | Data | 0 | 33.169 | 31.67 | 173.195 | 7.62 | 163.262 | 2172.81 | 25.89 | 47.894 | 6.38 | 1.299 | 4.321 | 8332.2 | 1.715 | 97.8 | 76.9 | 1412 | 23.95 | 5415.9 | 2755.1 | 2720.9 | 3999.7 | 1204.2 | 0.67196 | 5.62
2024-12-09 | 20:21 | Data | 0 | 32.953 | 31.555 | 173.195 | 7.63 | 163.262 | 2175.52 | 25.9 | 47.894 | 6.37 | 1.295 | 4.316 | 8345.77 | 1.62 | 97.8 | 76.9 | 1414 | 23.95 | 5424.8 | 2766.5 | 2719.7 | 4000.4 | 1204.2 | 0.67479 | 5.611
2024-12-09 | 20:21 | Data | 0 | 33.385 | 31.792 | 173.331 | 7.63 | 163.262 | 2171.01 | 25.89 | 47.984 | 6.38 | 1.305 | 4.279 | 8336.72 | 1.789 | 97.8 | 76.6 | 1411 | 23.99 | 5418.9 | 2752.3 | 2751.4 | 4018.1 | 1204.2 | 0.66588 | 5.585
2024-12-09 | 20:21 | Data | 0 | 33.405 | 31.616 | 173.24 | 7.63 | 163.307 | 2171.91 | 25.89 | 47.894 | 6.37 | 1.293 | 4.303 | 8332.2 | 1.742 | 97.8 | 76.9 | 1412 | 23.95 | 5415.9 | 2760.8 | 2754 | 4020.1 | 1204.2 | 0.66803 | 5.597
2024-12-09 | 20:21 | Data | 0 | 33.21 | 31.819 | 173.331 | 7.62 | 163.352 | 2172.81 | 25.89 | 47.894 | 6.37 | 1.295 | 4.309 | 8336.72 | 1.485 | 97.8 | 76.9 | 1412 | 23.95 | 5418.9 | 2731.1 | 2739.2 | 3994.7 | 1204.2 | 0.66508 | 5.605
2024-12-09 | 20:21 | Data | 0 | 33.405 | 31.657 | 173.195 | 7.63 | 163.262 | 2170.1 | 25.9 | 47.894 | 6.38 | 1.301 | 4.305 | 8345.77 | 1.755 | 97.8 | 76.8 | 1410 | 23.95 | 5424.8 | 2740.3 | 2742.2 | 4000.8 | 1204.2 | 0.66685 | 5.606
2024-12-09 | 20:21 | Data | 0 | 32.973 | 31.555 | 173.376 | 7.62 | 163.262 | 2171.91 | 25.88 | 47.894 | 6.37 | 1.306 | 4.291 | 8345.77 | 1.587 | 97.8 | 76.7 | 1412 | 23.99 | 5424.8 | 2762.1 | 2723.9 | 4000.5 | 1204.2 | 0.67302 | 5.598
2024-12-09 | 20:21 | Data | 0 | 33.183 | 31.454 | 173.15 | 7.62 | 163.262 | 2174.62 | 25.88 | 47.894 | 6.38 | 1.301 | 4.28 | 8363.86 | 1.843 | 97.8 | 76.7 | 1414 | 23.95 | 5436.5 | 2756.6 | 2723.1 | 3998.6 | 1204.2 | 0.67323 | 5.581
2024-12-09 | 20:21 | Data | 0 | 33.183 | 31.468 | 173.195 | 7.62 | 163.307 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.295 | 4.273 | 8345.77 | 1.728 | 97.8 | 76.7 | 1415 | 23.95 | 5424.8 | 2733.4 | 2719.8 | 3985.7 | 1204.2 | 0.66782 | 5.568
2024-12-09 | 20:21 | Data | 0 | 33.385 | 31.873 | 173.331 | 7.62 | 163.352 | 2175.52 | 25.88 | 47.804 | 6.37 | 1.304 | 4.287 | 8359.34 | 1.695 | 97.8 | 76.7 | 1414 | 23.86 | 5433.6 | 2754.4 | 2713.4 | 3996 | 1204.3 | 0.67159 | 5.591
2024-12-09 | 20:21 | Data | 0 | 33.513 | 31.67 | 173.331 | 7.62 | 163.262 | 2174.62 | 25.88 | 47.894 | 6.38 | 1.303 | 4.258 | 8359.34 | 1.843 | 97.8 | 76.6 | 1414 | 23.95 | 5433.6 | 2751.8 | 2705.2 | 3983.5 | 1204.3 | 0.67478 | 5.562
2024-12-09 | 20:21 | Data | 0 | 33.183 | 31.528 | 173.24 | 7.63 | 163.262 | 2174.62 | 25.89 | 47.894 | 6.37 | 1.293 | 4.284 | 8341.25 | 1.823 | 97.8 | 76.8 | 1414 | 23.95 | 5421.8 | 2759.9 | 2712.4 | 3993.7 | 1204.3 | 0.67367 | 5.577
2024-12-09 | 20:21 | Data | 0 | 33.183 | 31.346 | 173.24 | 7.63 | 163.307 | 2180.04 | 25.88 | 47.894 | 6.37 | 1.296 | 4.305 | 8345.77 | 1.816 | 97.8 | 76.9 | 1417 | 23.95 | 5424.8 | 2764.8 | 2722.3 | 3999.6 | 1204.3 | 0.67097 | 5.601
2024-12-09 | 20:21 | Data | 0 | 33.358 | 31.792 | 173.376 | 7.63 | 163.307 | 2180.04 | 25.88 | 47.894 | 6.38 | 1.3 | 4.29 | 8345.77 | 1.782 | 97.8 | 76.7 | 1417 | 23.95 | 5424.8 | 2757.5 | 2752.4 | 4021.2 | 1204.3 | 0.66703 | 5.59
2024-12-09 | 20:21 | Data | 0 | 33.237 | 31.366 | 173.195 | 7.63 | 163.217 | 2172.81 | 25.88 | 47.623 | 6.37 | 1.301 | 4.276 | 8345.77 | 1.796 | 97.8 | 76.7 | 1412 | 23.86 | 5424.8 | 2751.9 | 2737.9 | 4001 | 1204.3 | 0.6716 | 5.575
2024-12-09 | 20:21 | Data | 0 | 33.297 | 31.447 | 173.24 | 7.63 | 163.307 | 2172.81 | 25.89 | 48.255 | 6.38 | 1.297 | 4.3 | 8345.77 | 1.722 | 97.8 | 76.8 | 1412 | 24.08 | 5424.8 | 2748.3 | 2742.2 | 4004.8 | 1204.3 | 0.66798 | 5.597
2024-12-09 | 20:22 | Data | 0 | 33.372 | 31.474 | 173.24 | 7.63 | 163.352 | 2171.91 | 25.89 | 47.894 | 6.38 | 1.302 | 4.305 | 8341.25 | 1.931 | 97.8 | 76.8 | 1412 | 23.95 | 5421.8 | 2718.3 | 2739 | 3983.4 | 1204.3 | 0.66482 | 5.608
2024-12-09 | 20:22 | Data | 0 | 33.297 | 31.738 | 173.376 | 7.63 | 163.307 | 2172.81 | 25.89 | 48.165 | 6.37 | 1.302 | 4.304 | 8350.29 | 1.782 | 97.8 | 76.8 | 1412 | 24.08 | 5427.7 | 2736.6 | 2733.3 | 3993.5 | 1204.3 | 0.66697 | 5.606
2024-12-09 | 20:22 | Data | 0 | 33.203 | 31.569 | 173.331 | 7.63 | 163.307 | 2172.81 | 25.88 | 48.436 | 6.37 | 1.3 | 4.325 | 8350.29 | 1.62 | 97.8 | 76.9 | 1412 | 24.22 | 5427.7 | 2750.2 | 2738.5 | 4006.9 | 1204.3 | 0.66904 | 5.625
2024-12-09 | 20:22 | Data | 0 | 33.169 | 31.664 | 173.24 | 7.62 | 163.217 | 2170.1 | 25.88 | 47.894 | 6.37 | 1.302 | 4.308 | 8363.86 | 1.674 | 97.8 | 76.8 | 1411 | 23.95 | 5436.5 | 2749.8 | 2738.8 | 4003.7 | 1204.3 | 0.66782 | 5.611
2024-12-09 | 20:22 | Data | 0 | 33.183 | 31.772 | 173.331 | 7.63 | 163.307 | 2176.43 | 25.89 | 47.894 | 6.37 | 1.308 | 4.286 | 8372.9 | 1.614 | 97.8 | 76.6 | 1414 | 23.95 | 5442.4 | 2751.7 | 2738.4 | 4008.6 | 1204.3 | 0.66954 | 5.595
2024-12-09 | 20:22 | Data | 0 | 33.183 | 31.569 | 173.421 | 7.62 | 163.262 | 2174.62 | 25.88 | 48.075 | 6.37 | 1.304 | 4.263 | 8377.43 | 1.735 | 97.8 | 76.6 | 1414 | 24.08 | 5445.3 | 2739.3 | 2787.1 | 4037 | 1204.3 | 0.66085 | 5.568
2024-12-09 | 20:22 | Data | 0 | 33.399 | 31.61 | 173.195 | 7.62 | 163.443 | 2173.72 | 25.88 | 47.984 | 6.37 | 1.299 | 4.325 | 8386.47 | 1.749 | 97.8 | 76.9 | 1414 | 23.95 | 5451.2 | 2749.4 | 2759.4 | 4021.8 | 1204.3 | 0.66449 | 5.624
2024-12-09 | 20:22 | Data | 0 | 32.96 | 31.38 | 173.195 | 7.63 | 163.443 | 2176.43 | 25.89 | 47.894 | 6.38 | 1.296 | 4.312 | 8377.43 | 1.749 | 97.8 | 76.9 | 1414 | 23.9 | 5445.3 | 2759.7 | 2738.1 | 4013.5 | 1204.3 | 0.66688 | 5.608
2024-12-09 | 20:22 | Data | 0 | 33.162 | 31.555 | 173.195 | 7.62 | 163.307 | 2177.33 | 25.89 | 47.894 | 6.37 | 1.302 | 4.303 | 8363.86 | 1.661 | 97.8 | 76.8 | 1415 | 23.95 | 5436.5 | 2736.2 | 2752.9 | 4005.1 | 1204.3 | 0.66563 | 5.605
2024-12-09 | 20:22 | Data | 0 | 33.399 | 31.569 | 173.195 | 7.63 | 163.443 | 2172.81 | 25.89 | 47.894 | 6.37 | 1.32 | 4.299 | 8377.43 | 1.722 | 97.8 | 76.5 | 1412 | 23.95 | 5445.3 | 2757.7 | 2754.9 | 4021.3 | 1204.3 | 0.6685 | 5.618
2024-12-09 | 20:22 | Data | 0 | 33.297 | 31.569 | 173.331 | 7.63 | 163.352 | 2178.24 | 25.89 | 47.804 | 6.38 | 1.309 | 4.295 | 8359.34 | 1.816 | 97.8 | 76.6 | 1416 | 23.9 | 5433.6 | 2759.3 | 2763.4 | 4029.2 | 1204.3 | 0.66625 | 5.602
2024-12-09 | 20:22 | Data | 0 | 33.189 | 31.346 | 173.376 | 7.62 | 163.443 | 2180.04 | 25.89 | 47.894 | 6.37 | 1.291 | 4.302 | 8345.77 | 1.836 | 97.8 | 76.9 | 1417 | 23.99 | 5424.8 | 2769.3 | 2757.8 | 4030.2 | 1204.3 | 0.66922 | 5.592
2024-12-09 | 20:22 | Data | 0 | 33.77 | 31.583 | 173.376 | 7.63 | 163.443 | 2180.95 | 25.89 | 47.894 | 6.37 | 1.296 | 4.326 | 8336.72 | 1.978 | 97.8 | 76.9 | 1418 | 23.95 | 5418.9 | 2756.2 | 2736.4 | 4004.4 | 1204.3 | 0.67176 | 5.622
2024-12-09 | 20:22 | Data | 0 | 33.21 | 31.346 | 173.195 | 7.63 | 163.262 | 2180.04 | 25.89 | 47.894 | 6.38 | 1.309 | 4.298 | 8336.72 | 1.836 | 97.8 | 76.7 | 1418 | 23.95 | 5418.9 | 2765.6 | 2729.2 | 4008.1 | 1204.3 | 0.6722 | 5.606
2024-12-09 | 20:22 | Data | 0 | 33.129 | 31.684 | 173.195 | 7.62 | 163.262 | 2180.95 | 25.89 | 47.894 | 6.37 | 1.299 | 4.286 | 8336.72 | 1.816 | 97.8 | 76.7 | 1418 | 23.95 | 5418.9 | 2747.5 | 2734.9 | 3999.7 | 1204.3 | 0.67101 | 5.585
2024-12-09 | 20:22 | Data | 0 | 33.297 | 31.454 | 173.15 | 7.63 | 163.307 | 2180.95 | 25.89 | 47.804 | 6.37 | 1.302 | 4.3 | 8345.77 | 1.668 | 97.8 | 76.8 | 1417 | 23.95 | 5424.8 | 2748.6 | 2735 | 4003 | 1204.3 | 0.66803 | 5.602
2024-12-09 | 20:22 | Data | 0 | 33.223 | 31.542 | 173.24 | 7.62 | 163.262 | 2186.37 | 25.89 | 47.894 | 6.37 | 1.304 | 4.301 | 8359.34 | 1.647 | 97.8 | 76.7 | 1421 | 23.95 | 5433.6 | 2743.9 | 2747.3 | 4009.8 | 1204.3 | 0.66656 | 5.605
2024-12-09 | 20:22 | Data | 0 | 33.378 | 31.461 | 173.24 | 7.63 | 163.217 | 2177.33 | 25.89 | 47.804 | 6.37 | 1.302 | 4.313 | 8354.81 | 1.857 | 97.8 | 76.8 | 1416 | 23.9 | 5430.6 | 2780.9 | 2723.3 | 4011.2 | 1204.3 | 0.67528 | 5.616
2024-12-09 | 20:23 | Data | 0 | 33.412 | 31.67 | 173.331 | 7.63 | 163.352 | 2178.24 | 25.89 | 47.894 | 6.38 | 1.309 | 4.309 | 8372.9 | 1.884 | 97.8 | 76.7 | 1415 | 23.95 | 5442.4 | 2753.2 | 2732.7 | 4004.1 | 1204.3 | 0.67074 | 5.618
2024-12-09 | 20:23 | Data | 0 | 33.574 | 31.481 | 173.24 | 7.63 | 163.307 | 2183.66 | 25.89 | 47.804 | 6.37 | 1.299 | 4.295 | 8359.34 | 1.89 | 97.8 | 76.8 | 1419 | 23.95 | 5433.6 | 2757.9 | 2723.6 | 4002.2 | 1204.3 | 0.67212 | 5.592
2024-12-09 | 20:23 | Data | 0 | 33.183 | 31.65 | 173.195 | 7.63 | 163.352 | 2183.66 | 25.89 | 47.894 | 6.38 | 1.295 | 4.297 | 8363.86 | 1.735 | 97.8 | 76.8 | 1419 | 23.95 | 5436.5 | 2764.2 | 2715.5 | 4001.9 | 1204.3 | 0.67287 | 5.592
2024-12-09 | 20:23 | Data | 0 | 33.183 | 31.393 | 173.24 | 7.63 | 163.352 | 2182.75 | 25.9 | 47.894 | 6.37 | 1.306 | 4.304 | 8359.34 | 1.728 | 97.8 | 76.7 | 1419 | 23.95 | 5433.6 | 2750.4 | 2746.4 | 4009.2 | 1204.3 | 0.66824 | 5.61
2024-12-09 | 20:23 | Data | 0 | 33.196 | 31.346 | 173.331 | 7.63 | 163.307 | 2180.95 | 25.89 | 47.894 | 6.37 | 1.301 | 4.299 | 8359.34 | 1.668 | 97.8 | 76.8 | 1418 | 23.95 | 5433.6 | 2760.6 | 2734 | 4010.9 | 1204.3 | 0.67177 | 5.6
2024-12-09 | 20:23 | Data | 0 | 33.223 | 31.393 | 173.195 | 7.62 | 163.307 | 2182.75 | 25.9 | 47.894 | 6.37 | 1.308 | 4.301 | 8377.43 | 1.634 | 97.8 | 76.7 | 1418 | 23.95 | 5445.3 | 2753.6 | 2751.6 | 4017.5 | 1204.3 | 0.66651 | 5.61
2024-12-09 | 20:23 | Data | 0 | 33.297 | 31.569 | 173.195 | 7.63 | 163.307 | 2183.66 | 25.9 | 47.894 | 6.37 | 1.31 | 4.312 | 8372.9 | 1.62 | 97.8 | 76.7 | 1419 | 23.95 | 5442.4 | 2758.6 | 2734.6 | 4006.7 | 1204.3 | 0.67119 | 5.622
2024-12-09 | 20:23 | Data | 0 | 33.21 | 31.569 | 173.24 | 7.63 | 163.307 | 2182.75 | 25.89 | 47.894 | 6.38 | 1.309 | 4.323 | 8372.9 | 1.627 | 97.8 | 76.8 | 1419 | 23.95 | 5442.4 | 2739.6 | 2758.5 | 4010 | 1204.3 | 0.66648 | 5.632
2024-12-09 | 20:23 | Data | 0 | 33.027 | 31.346 | 173.195 | 7.63 | 163.307 | 2183.66 | 25.89 | 47.894 | 6.38 | 1.311 | 4.315 | 8377.43 | 1.627 | 97.8 | 76.7 | 1419 | 23.95 | 5445.3 | 2752.6 | 2754.4 | 4020.2 | 1204.3 | 0.66596 | 5.627
2024-12-09 | 20:23 | Data | 0 | 33.169 | 31.339 | 173.105 | 7.62 | 163.262 | 2183.66 | 25.89 | 47.804 | 6.37 | 1.313 | 4.334 | 8345.77 | 1.843 | 97.8 | 76.7 | 1419 | 23.95 | 5424.8 | 2746.2 | 2714.4 | 3988.5 | 1204.3 | 0.67059 | 5.647
2024-12-09 | 20:23 | Data | 0 | 33.378 | 31.569 | 173.195 | 7.62 | 163.307 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.311 | 4.333 | 8345.77 | 1.836 | 97.8 | 76.8 | 1411 | 23.95 | 5424.8 | 2752.8 | 2706.4 | 3993 | 1204.3 | 0.67156 | 5.646
2024-12-09 | 20:23 | Data | 0 | 33.284 | 31.583 | 173.331 | 7.63 | 163.307 | 2180.04 | 25.9 | 47.894 | 6.37 | 1.313 | 4.3 | 8332.2 | 1.789 | 97.8 | 76.6 | 1417 | 23.95 | 5415.9 | 2781.5 | 2701 | 3999.5 | 1204.3 | 0.67959 | 5.613
2024-12-09 | 20:23 | Data | 0 | 32.987 | 31.711 | 173.195 | 7.63 | 163.217 | 2180.04 | 25.89 | 47.894 | 6.37 | 1.312 | 4.303 | 8332.2 | 1.614 | 97.8 | 76.6 | 1417 | 23.95 | 5415.9 | 2741.5 | 2711.2 | 3982.5 | 1204.3 | 0.67058 | 5.614
2024-12-09 | 20:23 | Data | 0 | 33.189 | 31.684 | 173.195 | 7.62 | 163.307 | 2178.24 | 25.89 | 47.894 | 6.38 | 1.302 | 4.287 | 8359.34 | 1.614 | 97.8 | 76.7 | 1416 | 23.95 | 5433.6 | 2764.1 | 2697.1 | 3979.5 | 1204.4 | 0.67668 | 5.591
2024-12-09 | 20:23 | Data | 0 | 33.183 | 31.596 | 173.195 | 7.62 | 163.352 | 2178.24 | 25.89 | 47.894 | 6.37 | 1.3 | 4.271 | 8359.34 | 1.83 | 97.8 | 76.7 | 1416 | 23.95 | 5433.6 | 2727.3 | 2716.3 | 3979.5 | 1204.4 | 0.66998 | 5.571
2024-12-09 | 20:23 | Data | 0 | 33.635 | 31.522 | 173.376 | 7.63 | 163.488 | 2178.24 | 25.89 | 47.894 | 6.37 | 1.301 | 4.264 | 8359.34 | 1.769 | 97.8 | 76.6 | 1415 | 23.95 | 5433.6 | 2755.5 | 2724.1 | 3996.6 | 1204.4 | 0.66908 | 5.564
2024-12-09 | 20:23 | Data | 0 | 33.129 | 31.454 | 173.24 | 7.63 | 163.307 | 2172.81 | 25.89 | 47.804 | 6.37 | 1.3 | 4.294 | 8350.29 | 1.803 | 97.8 | 76.8 | 1413 | 23.9 | 5427.7 | 2764.5 | 2732.8 | 4006.5 | 1204.4 | 0.66954 | 5.594
2024-12-09 | 20:24 | Data | 0 | 33.183 | 31.555 | 173.24 | 7.62 | 163.307 | 2177.33 | 25.89 | 47.894 | 6.38 | 1.307 | 4.307 | 8368.38 | 1.668 | 97.8 | 76.7 | 1415 | 23.95 | 5439.4 | 2740.4 | 2737.9 | 3998.7 | 1204.4 | 0.6698 | 5.614
2024-12-09 | 20:24 | Data | 0 | 33.405 | 31.481 | 173.421 | 7.62 | 163.307 | 2178.24 | 25.89 | 47.894 | 6.37 | 1.301 | 4.297 | 8359.34 | 1.735 | 97.8 | 76.7 | 1415 | 23.9 | 5433.6 | 2747.8 | 2713.2 | 3985 | 1204.4 | 0.67024 | 5.6
2024-12-09 | 20:24 | Data | 0 | 33.405 | 31.61 | 173.195 | 7.62 | 163.352 | 2177.33 | 25.89 | 47.804 | 6.38 | 1.31 | 4.278 | 8372.9 | 1.661 | 97.8 | 76.6 | 1416 | 23.9 | 5442.4 | 2732.1 | 2727.3 | 3989.6 | 1204.4 | 0.66658 | 5.588
2024-12-09 | 20:24 | Data | 0 | 33.405 | 31.4 | 173.24 | 7.63 | 163.262 | 2177.33 | 25.89 | 47.894 | 6.37 | 1.306 | 4.295 | 8377.43 | 1.836 | 97.8 | 76.7 | 1415 | 23.95 | 5445.3 | 2773.2 | 2729.7 | 4007.6 | 1204.4 | 0.67489 | 5.6
2024-12-09 | 20:24 | Data | 0 | 33.709 | 31.846 | 173.331 | 7.63 | 163.488 | 2176.43 | 25.89 | 47.894 | 6.38 | 1.294 | 4.279 | 8359.34 | 1.782 | 97.8 | 76.8 | 1415 | 23.95 | 5433.6 | 2761.2 | 2705.4 | 3988.9 | 1204.4 | 0.67525 | 5.574
2024-12-09 | 20:24 | Data | 0 | 33.547 | 31.677 | 173.376 | 7.63 | 163.352 | 2177.33 | 25.89 | 47.894 | 6.37 | 1.309 | 4.262 | 8345.77 | 1.924 | 97.8 | 76.5 | 1415 | 23.95 | 5424.8 | 2740 | 2720.9 | 3990.3 | 1204.4 | 0.66869 | 5.571
2024-12-09 | 20:24 | Data | 0 | 33.183 | 31.569 | 173.376 | 7.62 | 163.307 | 2177.33 | 25.9 | 47.894 | 6.37 | 1.311 | 4.286 | 8350.29 | 1.614 | 97.8 | 76.6 | 1416 | 23.95 | 5427.7 | 2751.3 | 2730.9 | 4003.4 | 1204.4 | 0.66923 | 5.596
2024-12-09 | 20:24 | Data | 0 | 33.196 | 31.569 | 173.195 | 7.63 | 163.307 | 2178.24 | 25.9 | 47.984 | 6.37 | 1.31 | 4.295 | 8345.77 | 1.735 | 97.8 | 76.6 | 1415 | 23.95 | 5424.8 | 2743.2 | 2750 | 4008.6 | 1204.4 | 0.66578 | 5.605
2024-12-09 | 20:24 | Data | 0 | 33.412 | 31.596 | 173.376 | 7.63 | 163.443 | 2172.81 | 25.89 | 47.894 | 6.37 | 1.309 | 4.313 | 8350.29 | 1.816 | 97.8 | 76.7 | 1413 | 23.95 | 5427.7 | 2755.3 | 2734.2 | 4007.7 | 1204.4 | 0.66983 | 5.621
2024-12-09 | 20:24 | Data | 0 | 33.351 | 31.961 | 173.421 | 7.63 | 163.352 | 2177.33 | 25.89 | 47.894 | 6.38 | 1.313 | 4.32 | 8359.34 | 1.83 | 97.8 | 76.7 | 1416 | 23.95 | 5433.6 | 2769.5 | 2759.6 | 4033 | 1204.4 | 0.66955 | 5.633
2024-12-09 | 20:24 | Data | 0 | 33.48 | 31.569 | 173.421 | 7.63 | 163.443 | 2171.91 | 25.89 | 47.804 | 6.37 | 1.31 | 4.292 | 8363.86 | 1.519 | 97.8 | 76.6 | 1412 | 23.95 | 5436.5 | 2752.4 | 2755.1 | 4018.6 | 1204.4 | 0.6676 | 5.601
2024-12-09 | 20:24 | Data | 0 | 33.635 | 31.576 | 173.467 | 7.62 | 163.533 | 2172.81 | 25.89 | 47.804 | 6.37 | 1.305 | 4.313 | 8350.29 | 1.681 | 97.8 | 76.8 | 1412 | 23.95 | 5427.7 | 2766.3 | 2749.9 | 4021.6 | 1204.4 | 0.66768 | 5.618
2024-12-09 | 20:24 | Data | 0 | 33.52 | 31.481 | 173.331 | 7.63 | 163.488 | 2177.33 | 25.89 | 47.894 | 6.38 | 1.304 | 4.284 | 8345.77 | 1.782 | 97.8 | 76.6 | 1416 | 23.95 | 5424.8 | 2752.9 | 2742.4 | 4006 | 1204.4 | 0.66834 | 5.589
2024-12-09 | 20:24 | Data | 0 | 33.351 | 31.9 | 173.331 | 7.62 | 163.443 | 2180.95 | 25.89 | 47.894 | 6.37 | 1.301 | 4.277 | 8345.77 | 1.803 | 97.8 | 76.7 | 1417 | 23.99 | 5424.8 | 2751.8 | 2744.9 | 4008 | 1204.4 | 0.6664 | 5.579
2024-12-09 | 20:24 | Data | 0 | 33.412 | 31.454 | 173.331 | 7.62 | 163.352 | 2180.04 | 25.89 | 47.804 | 6.37 | 1.308 | 4.306 | 8345.77 | 1.634 | 97.8 | 76.7 | 1417 | 23.9 | 5424.8 | 2756.8 | 2755.7 | 4017.1 | 1204.4 | 0.66793 | 5.613
2024-12-09 | 20:24 | Data | 0 | 33.412 | 31.67 | 173.331 | 7.63 | 163.307 | 2177.33 | 25.89 | 47.894 | 6.37 | 1.297 | 4.301 | 8345.77 | 1.627 | 97.8 | 76.8 | 1415 | 23.95 | 5424.8 | 2772.9 | 2739.3 | 4017.6 | 1204.4 | 0.67108 | 5.598
2024-12-09 | 20:24 | Data | 0 | 33.635 | 31.623 | 173.195 | 7.62 | 163.443 | 2183.66 | 25.89 | 47.894 | 6.37 | 1.299 | 4.307 | 8368.38 | 1.843 | 97.8 | 76.9 | 1419 | 23.95 | 5439.4 | 2744.9 | 2719.4 | 3994.1 | 1204.4 | 0.67021 | 5.604
2024-12-09 | 20:24 | Data | 0 | 33.189 | 31.542 | 173.331 | 7.62 | 163.352 | 2177.33 | 25.89 | 47.894 | 6.38 | 1.302 | 4.297 | 8350.29 | 1.722 | 97.8 | 76.7 | 1416 | 23.95 | 5427.7 | 2731.1 | 2733.2 | 3990.9 | 1204.4 | 0.66545 | 5.6
2024-12-09 | 20:25 | Data | 0 | 33.412 | 31.36 | 173.195 | 7.63 | 163.307 | 2178.24 | 25.89 | 47.894 | 6.37 | 1.3 | 4.315 | 8350.29 | 1.884 | 97.8 | 76.8 | 1416 | 23.9 | 5427.7 | 2744.4 | 2730.8 | 3997.4 | 1204.4 | 0.66994 | 5.616
2024-12-09 | 20:25 | Data | 0 | 33.183 | 31.569 | 173.195 | 7.63 | 163.307 | 2177.33 | 25.89 | 47.894 | 6.37 | 1.306 | 4.321 | 8341.25 | 1.789 | 97.8 | 76.8 | 1416 | 23.95 | 5421.8 | 2738.8 | 2717.6 | 3985.3 | 1204.4 | 0.66992 | 5.628
2024-12-09 | 20:25 | Data | 0 | 33.21 | 31.664 | 173.24 | 7.62 | 163.307 | 2178.24 | 25.89 | 47.894 | 6.38 | 1.3 | 4.323 | 8354.81 | 1.587 | 97.8 | 76.9 | 1416 | 23.95 | 5430.6 | 2735.7 | 2733 | 3992.3 | 1204.4 | 0.66701 | 5.622
2024-12-09 | 20:25 | Data | 0 | 33.237 | 31.569 | 173.24 | 7.63 | 163.307 | 2177.33 | 25.9 | 47.804 | 6.37 | 1.301 | 4.292 | 8372.9 | 1.83 | 97.8 | 76.7 | 1415 | 23.95 | 5442.4 | 2747.7 | 2733 | 4000.6 | 1204.4 | 0.66897 | 5.593
2024-12-09 | 20:25 | Data | 0 | 33.365 | 31.569 | 173.376 | 7.62 | 163.488 | 2177.33 | 25.89 | 47.894 | 6.37 | 1.3 | 4.284 | 8363.86 | 1.438 | 97.8 | 76.7 | 1415 | 23.95 | 5436.5 | 2780.2 | 2724.2 | 4010.5 | 1204.4 | 0.67577 | 5.584
2024-12-09 | 20:25 | Data | 0 | 33.183 | 31.785 | 173.331 | 7.63 | 163.352 | 2178.24 | 25.89 | 47.894 | 6.38 | 1.301 | 4.294 | 8359.34 | 1.735 | 97.8 | 76.7 | 1416 | 23.99 | 5433.6 | 2742.2 | 2731.6 | 3999.2 | 1204.4 | 0.66796 | 5.596
2024-12-09 | 20:25 | Data | 0 | 33.608 | 31.427 | 173.24 | 7.62 | 163.352 | 2178.24 | 25.89 | 47.894 | 6.37 | 1.306 | 4.275 | 8345.77 | 1.897 | 97.8 | 76.6 | 1416 | 23.95 | 5424.8 | 2737.5 | 2730.4 | 3994.5 | 1204.4 | 0.66701 | 5.58
2024-12-09 | 20:25 | Data | 0 | 33.365 | 31.569 | 173.376 | 7.63 | 163.488 | 2178.24 | 25.89 | 47.894 | 6.37 | 1.299 | 4.301 | 8336.72 | 1.519 | 97.8 | 76.8 | 1416 | 23.95 | 5418.9 | 2752 | 2741.5 | 4007 | 1204.4 | 0.66818 | 5.6
2024-12-09 | 20:25 | Data | 0 | 33.365 | 31.772 | 173.421 | 7.63 | 163.443 | 2175.52 | 25.89 | 47.894 | 6.37 | 1.295 | 4.313 | 8345.77 | 1.654 | 97.8 | 76.9 | 1414 | 23.9 | 5424.8 | 2762.9 | 2750.1 | 4015.7 | 1204.4 | 0.6699 | 5.609
2024-12-09 | 20:25 | Data | 0 | 33.223 | 31.569 | 173.24 | 7.62 | 163.352 | 2174.62 | 25.89 | 47.894 | 6.37 | 1.295 | 4.313 | 8345.77 | 1.418 | 97.8 | 76.9 | 1414 | 23.95 | 5424.8 | 2769 | 2757.8 | 4028 | 1204.4 | 0.66852 | 5.609
2024-12-09 | 20:25 | Data | 0 | 33.297 | 31.623 | 173.24 | 7.62 | 163.352 | 2175.52 | 25.89 | 47.804 | 6.37 | 1.308 | 4.323 | 8345.77 | 1.647 | 97.8 | 76.8 | 1414 | 23.95 | 5424.8 | 2750 | 2734.9 | 4006 | 1204.4 | 0.66893 | 5.629
2024-12-09 | 20:25 | Data | 0 | 33.257 | 31.569 | 173.331 | 7.63 | 163.443 | 2161.97 | 25.89 | 47.894 | 6.37 | 1.305 | 4.321 | 8332.2 | 1.62 | 97.8 | 76.8 | 1405 | 23.95 | 5415.9 | 2758.6 | 2757.2 | 4021.3 | 1204.4 | 0.66799 | 5.627
2024-12-09 | 20:25 | Data | 0 | 33.358 | 31.569 | 173.195 | 7.62 | 163.488 | 2172.81 | 25.89 | 47.984 | 6.37 | 1.301 | 4.295 | 8332.2 | 1.836 | 97.8 | 76.7 | 1412 | 23.99 | 5415.9 | 2753 | 2759.3 | 4020.9 | 1204.4 | 0.66724 | 5.596
2024-12-09 | 20:25 | Data | 0 | 33.405 | 31.792 | 173.331 | 7.63 | 163.443 | 2175.52 | 25.89 | 47.894 | 6.37 | 1.299 | 4.295 | 8336.72 | 1.83 | 97.8 | 76.8 | 1414 | 23.95 | 5418.9 | 2745.4 | 2756.7 | 4011.7 | 1204.4 | 0.66638 | 5.593
2024-12-09 | 20:25 | Data | 0 | 33.189 | 31.765 | 173.195 | 7.63 | 163.352 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.31 | 4.276 | 8336.72 | 1.634 | 97.8 | 76.5 | 1414 | 23.95 | 5418.9 | 2749.8 | 2722.9 | 3992.4 | 1204.4 | 0.67123 | 5.587
2024-12-09 | 20:25 | Data | 0 | 33.635 | 31.414 | 173.331 | 7.62 | 163.443 | 2172.81 | 25.9 | 47.804 | 6.38 | 1.3 | 4.287 | 8372.9 | 1.843 | 97.8 | 76.7 | 1412 | 23.95 | 5442.4 | 2751.1 | 2749.5 | 4015 | 1204.4 | 0.667 | 5.586
2024-12-09 | 20:25 | Data | 0 | 33.21 | 31.569 | 173.195 | 7.63 | 163.307 | 2172.81 | 25.89 | 47.894 | 6.37 | 1.301 | 4.272 | 8359.34 | 1.634 | 97.8 | 76.6 | 1412 | 23.95 | 5433.6 | 2748.3 | 2727.7 | 3997.6 | 1204.4 | 0.67019 | 5.573
2024-12-09 | 20:25 | Data | 0 | 33.412 | 31.623 | 173.421 | 7.62 | 163.443 | 2175.52 | 25.89 | 47.894 | 6.38 | 1.309 | 4.312 | 8359.34 | 1.742 | 97.8 | 76.7 | 1414 | 23.9 | 5433.6 | 2753.5 | 2750.8 | 4019.4 | 1204.5 | 0.66836 | 5.62
2024-12-09 | 20:26 | Data | 0 | 33.21 | 31.569 | 173.421 | 7.63 | 163.443 | 2176.43 | 25.9 | 47.894 | 6.37 | 1.305 | 4.292 | 8359.34 | 1.627 | 97.8 | 76.7 | 1415 | 23.95 | 5433.6 | 2763.8 | 2769.8 | 4034.4 | 1204.5 | 0.66589 | 5.597
2024-12-09 | 20:26 | Data | 0 | 33.196 | 31.346 | 173.24 | 7.63 | 163.352 | 2176.43 | 25.89 | 47.894 | 6.37 | 1.294 | 4.306 | 8359.34 | 1.641 | 97.8 | 76.9 | 1415 | 23.95 | 5433.6 | 2767.5 | 2759.7 | 4029.9 | 1204.5 | 0.66807 | 5.6
2024-12-09 | 20:26 | Data | 0 | 33.176 | 31.4 | 173.195 | 7.63 | 163.307 | 2175.52 | 25.89 | 47.804 | 6.37 | 1.288 | 4.29 | 8363.86 | 1.728 | 97.8 | 76.9 | 1415 | 23.9 | 5436.5 | 2760.2 | 2748.6 | 4016.4 | 1204.5 | 0.66799 | 5.578
2024-12-09 | 20:26 | Data | 0 | 33.466 | 31.785 | 173.376 | 7.63 | 163.352 | 2174.62 | 25.89 | 48.346 | 6.37 | 1.305 | 4.282 | 8359.34 | 1.634 | 97.8 | 76.6 | 1414 | 24.22 | 5433.6 | 2747.7 | 2739.7 | 4009.3 | 1204.5 | 0.66741 | 5.588
2024-12-09 | 20:26 | Data | 0 | 33.662 | 31.596 | 173.421 | 7.63 | 163.488 | 2177.33 | 25.89 | 47.894 | 6.38 | 1.299 | 4.296 | 8372.9 | 1.782 | 97.8 | 76.8 | 1416 | 23.95 | 5442.4 | 2751 | 2744.7 | 4006.1 | 1204.5 | 0.66796 | 5.596
2024-12-09 | 20:26 | Data | 0 | 33.189 | 31.63 | 173.421 | 7.63 | 163.352 | 2177.33 | 25.89 | 47.894 | 6.37 | 1.296 | 4.291 | 8350.29 | 1.614 | 97.8 | 76.8 | 1415 | 23.95 | 5427.7 | 2746.3 | 2707.2 | 3987.5 | 1204.5 | 0.67169 | 5.587
2024-12-09 | 20:26 | Data | 0 | 33.183 | 31.731 | 173.376 | 7.63 | 163.443 | 2178.24 | 25.89 | 46.811 | 6.37 | 1.302 | 4.295 | 8345.77 | 1.641 | 97.9 | 76.7 | 1416 | 23.41 | 5424.8 | 2749.2 | 2729.7 | 3996.4 | 1204.5 | 0.67044 | 5.597
2024-12-09 | 20:26 | Data | 0 | 33.331 | 31.569 | 173.376 | 7.63 | 163.488 | 2178.24 | 25.89 | 46.721 | 6.37 | 1.303 | 4.304 | 8359.34 | 1.641 | 97.9 | 76.8 | 1416 | 23.36 | 5433.6 | 2761.6 | 2693.8 | 3980.5 | 1204.5 | 0.67765 | 5.608
2024-12-09 | 20:26 | Data | 0 | 33.237 | 31.461 | 173.331 | 7.63 | 163.352 | 2177.33 | 25.89 | 46.63 | 6.37 | 1.303 | 4.324 | 8341.25 | 1.843 | 97.9 | 76.9 | 1415 | 23.36 | 5421.8 | 2762.4 | 2701.1 | 3989.4 | 1204.5 | 0.67392 | 5.627
2024-12-09 | 20:26 | Data | 0 | 33.189 | 31.623 | 173.467 | 7.62 | 163.443 | 2167.39 | 25.89 | 46.811 | 6.37 | 1.31 | 4.306 | 8336.72 | 1.587 | 97.8 | 76.7 | 1408 | 23.36 | 5418.9 | 2741.8 | 2744 | 4007.2 | 1204.5 | 0.67095 | 5.617
2024-12-09 | 20:26 | Data | 0 | 33.736 | 31.414 | 173.421 | 7.63 | 163.488 | 2180.04 | 25.89 | 47.804 | 6.37 | 1.312 | 4.27 | 8341.25 | 1.857 | 97.8 | 76.5 | 1418 | 23.95 | 5421.8 | 2756.1 | 2735.4 | 4008.6 | 1204.5 | 0.67116 | 5.582
2024-12-09 | 20:26 | Data | 0 | 33.439 | 31.569 | 173.512 | 7.63 | 163.533 | 2180.04 | 25.89 | 47.984 | 6.37 | 1.304 | 4.277 | 8336.72 | 1.627 | 97.8 | 76.7 | 1418 | 23.95 | 5418.9 | 2759.7 | 2777.7 | 4039.6 | 1204.5 | 0.66475 | 5.58
2024-12-09 | 20:26 | Data | 0 | 33.399 | 31.772 | 173.421 | 7.63 | 163.443 | 2180.04 | 25.89 | 47.894 | 6.38 | 1.294 | 4.298 | 8332.2 | 1.823 | 97.8 | 76.9 | 1417 | 23.99 | 5415.9 | 2758.2 | 2763.8 | 4026.9 | 1204.5 | 0.66642 | 5.592
2024-12-09 | 20:26 | Data | 0 | 33.358 | 31.596 | 173.376 | 7.63 | 163.352 | 2180.95 | 25.89 | 48.165 | 6.37 | 1.301 | 4.298 | 8359.34 | 1.924 | 97.8 | 76.8 | 1418 | 24.08 | 5433.6 | 2741.9 | 2777.4 | 4028.5 | 1204.5 | 0.66312 | 5.6
2024-12-09 | 20:26 | Data | 0 | 33.405 | 31.569 | 173.376 | 7.62 | 163.443 | 2186.37 | 25.89 | 48.165 | 6.37 | 1.301 | 4.301 | 8359.34 | 1.728 | 97.8 | 76.8 | 1421 | 24.08 | 5433.6 | 2746.3 | 2755.3 | 4021.7 | 1204.5 | 0.66629 | 5.602
2024-12-09 | 20:26 | Data | 0 | 33.797 | 31.718 | 173.467 | 7.63 | 163.533 | 2180.04 | 25.89 | 48.165 | 6.38 | 1.305 | 4.304 | 8368.38 | 1.971 | 97.8 | 76.7 | 1418 | 24.08 | 5439.4 | 2776.1 | 2767.2 | 4043.9 | 1204.5 | 0.67045 | 5.61
2024-12-09 | 20:26 | Data | 0 | 33.21 | 31.569 | 173.331 | 7.63 | 163.443 | 2183.66 | 25.89 | 48.165 | 6.37 | 1.295 | 4.315 | 8377.43 | 1.62 | 97.8 | 76.9 | 1419 | 24.04 | 5445.3 | 2763.3 | 2695.2 | 3987.1 | 1204.5 | 0.67244 | 5.611
2024-12-09 | 20:26 | Data | 0 | 33.412 | 31.569 | 173.376 | 7.62 | 163.443 | 2182.75 | 25.89 | 48.165 | 6.37 | 1.296 | 4.304 | 8359.34 | 1.836 | 97.8 | 76.9 | 1419 | 24.08 | 5433.6 | 2751.3 | 2706.6 | 3983 | 1204.5 | 0.67259 | 5.6
2024-12-09 | 20:27 | Data | 0 | 33.358 | 32.008 | 173.467 | 7.62 | 163.488 | 2180.95 | 25.89 | 48.165 | 6.37 | 1.3 | 4.28 | 8359.34 | 1.634 | 97.8 | 76.7 | 1418 | 24.04 | 5433.6 | 2767.1 | 2708.8 | 3994.9 | 1204.5 | 0.67671 | 5.579
2024-12-09 | 20:27 | Data | 0 | 33.473 | 31.583 | 173.421 | 7.63 | 163.533 | 2180.95 | 25.89 | 48.075 | 6.37 | 1.287 | 4.285 | 8363.86 | 1.634 | 97.8 | 76.9 | 1418 | 24.04 | 5436.5 | 2750.9 | 2705.8 | 3983.4 | 1204.5 | 0.67263 | 5.572
2024-12-09 | 20:27 | Data | 0 | 33.412 | 31.799 | 173.421 | 7.62 | 163.488 | 2178.24 | 25.89 | 48.165 | 6.38 | 1.296 | 4.316 | 8363.86 | 1.614 | 97.8 | 76.9 | 1416 | 24.08 | 5436.5 | 2760.8 | 2738.5 | 4011.8 | 1204.5 | 0.67081 | 5.611
2024-12-09 | 20:27 | Data | 0 | 32.994 | 31.677 | 173.421 | 7.62 | 163.443 | 2177.33 | 25.9 | 48.165 | 6.38 | 1.304 | 4.326 | 8332.2 | 1.479 | 97.8 | 76.8 | 1415 | 24.08 | 5415.9 | 2740.5 | 2773 | 4023.2 | 1204.5 | 0.66235 | 5.629
2024-12-09 | 20:27 | Data | 0 | 33.216 | 31.555 | 173.376 | 7.63 | 163.578 | 2177.33 | 25.89 | 48.075 | 6.37 | 1.295 | 4.31 | 8314.11 | 1.573 | 97.8 | 76.9 | 1416 | 24.08 | 5404.2 | 2769.5 | 2775.2 | 4048.6 | 1204.5 | 0.66544 | 5.605
2024-12-09 | 20:27 | Data | 0 | 33.324 | 31.528 | 173.376 | 7.63 | 163.488 | 2175.52 | 25.9 | 48.075 | 6.37 | 1.302 | 4.314 | 8341.25 | 1.6 | 97.8 | 76.8 | 1414 | 24.08 | 5421.8 | 2767.3 | 2774.4 | 4043.4 | 1204.5 | 0.66558 | 5.617
2024-12-09 | 20:27 | Data | 0 | 33.223 | 31.569 | 173.24 | 7.63 | 163.352 | 2174.62 | 25.89 | 48.165 | 6.37 | 1.301 | 4.304 | 8336.72 | 1.62 | 97.8 | 76.8 | 1414 | 24.08 | 5418.9 | 2779.3 | 2747.3 | 4034.1 | 1204.5 | 0.67122 | 5.604
2024-12-09 | 20:27 | Data | 0 | 33.527 | 32.096 | 173.421 | 7.63 | 163.443 | 2175.52 | 25.89 | 48.165 | 6.37 | 1.301 | 4.278 | 8345.77 | 1.647 | 97.8 | 76.7 | 1414 | 24.08 | 5424.8 | 2745.5 | 2743.4 | 4007.9 | 1204.5 | 0.66809 | 5.58
2024-12-09 | 20:27 | Data | 0 | 33.372 | 31.623 | 173.331 | 7.62 | 163.352 | 2173.72 | 25.89 | 48.075 | 6.37 | 1.291 | 4.289 | 8345.77 | 1.627 | 97.8 | 76.9 | 1413 | 24.08 | 5424.8 | 2732.5 | 2743.1 | 4001.7 | 1204.5 | 0.6654 | 5.581
2024-12-09 | 20:27 | Data | 0 | 33.21 | 31.616 | 173.376 | 7.62 | 163.352 | 2170.1 | 25.89 | 48.165 | 6.37 | 1.295 | 4.299 | 8336.72 | 1.526 | 97.8 | 76.9 | 1411 | 24.08 | 5418.9 | 2760.7 | 2744.2 | 4019.2 | 1204.5 | 0.66821 | 5.593
2024-12-09 | 20:27 | Data | 0 | 33.399 | 31.826 | 173.467 | 7.62 | 163.352 | 2171.01 | 25.9 | 47.894 | 6.37 | 1.302 | 4.299 | 8350.29 | 1.89 | 97.8 | 76.8 | 1411 | 23.99 | 5427.7 | 2751.4 | 2730.2 | 4002.2 | 1204.5 | 0.67042 | 5.602
2024-12-09 | 20:27 | Data | 0 | 33.5 | 31.474 | 173.195 | 7.63 | 163.352 | 2163.77 | 25.89 | 47.894 | 6.37 | 1.303 | 4.326 | 8350.29 | 2.046 | 97.8 | 76.8 | 1406 | 23.9 | 5427.7 | 2746.9 | 2733 | 4000.6 | 1204.5 | 0.66945 | 5.629
2024-12-09 | 20:27 | Data | 0 | 33.243 | 31.569 | 173.331 | 7.63 | 163.488 | 2170.1 | 25.89 | 48.165 | 6.37 | 1.309 | 4.306 | 8350.29 | 1.62 | 97.8 | 76.7 | 1411 | 24.13 | 5427.7 | 2742.4 | 2728 | 3994.7 | 1204.5 | 0.6686 | 5.614
2024-12-09 | 20:27 | Data | 0 | 33.635 | 31.799 | 173.467 | 7.63 | 163.488 | 2170.1 | 25.89 | 48.075 | 6.37 | 1.313 | 4.309 | 8341.25 | 1.722 | 97.8 | 76.6 | 1411 | 24.04 | 5421.8 | 2751.3 | 2721.7 | 3998.8 | 1204.5 | 0.66814 | 5.623
2024-12-09 | 20:27 | Data | 0 | 33.243 | 31.576 | 173.331 | 7.63 | 163.443 | 2170.1 | 25.89 | 47.804 | 6.37 | 1.303 | 4.297 | 8332.2 | 1.62 | 97.8 | 76.7 | 1411 | 23.95 | 5415.9 | 2773.7 | 2724.7 | 4012.1 | 1204.5 | 0.67495 | 5.6
2024-12-09 | 20:27 | Data | 0 | 33.581 | 31.569 | 173.376 | 7.63 | 163.443 | 2166.49 | 25.89 | 48.165 | 6.38 | 1.297 | 4.301 | 8363.86 | 1.749 | 97.8 | 76.8 | 1408 | 24.13 | 5436.5 | 2766.9 | 2732.7 | 4013.7 | 1204.5 | 0.67092 | 5.598
2024-12-09 | 20:27 | Data | 0 | 33.412 | 31.745 | 173.376 | 7.63 | 163.443 | 2166.49 | 25.89 | 47.894 | 6.37 | 1.31 | 4.322 | 8368.38 | 1.836 | 97.8 | 76.7 | 1408 | 23.95 | 5439.4 | 2764.9 | 2759 | 4028.3 | 1204.5 | 0.66917 | 5.631
2024-12-09 | 20:28 | Data | 0 | 33.446 | 31.569 | 173.376 | 7.62 | 163.488 | 2164.68 | 25.9 | 48.165 | 6.37 | 1.305 | 4.3 | 8363.86 | 1.668 | 97.8 | 76.7 | 1406 | 24.08 | 5436.5 | 2767 | 2726.8 | 4008.1 | 1204.5 | 0.67335 | 5.605
2024-12-09 | 20:28 | Data | 0 | 33.412 | 31.583 | 173.376 | 7.63 | 163.443 | 2163.77 | 25.9 | 47.894 | 6.37 | 1.291 | 4.3 | 8368.38 | 1.789 | 97.8 | 76.9 | 1406 | 23.95 | 5439.4 | 2741.6 | 2712.9 | 3982.8 | 1204.5 | 0.67075 | 5.592
2024-12-09 | 20:28 | Data | 0 | 33.581 | 31.772 | 173.467 | 7.62 | 163.443 | 2162.87 | 25.89 | 47.894 | 6.37 | 1.296 | 4.305 | 8372.9 | 1.884 | 97.8 | 76.9 | 1406 | 23.95 | 5442.4 | 2768.3 | 2736 | 4017.9 | 1204.6 | 0.6707 | 5.601
2024-12-09 | 20:28 | Data | 0 | 33.642 | 31.603 | 173.421 | 7.63 | 163.533 | 2164.68 | 25.89 | 47.894 | 6.37 | 1.297 | 4.313 | 8381.95 | 1.695 | 97.8 | 76.9 | 1408 | 23.95 | 5448.3 | 2752.8 | 2706.5 | 3981.7 | 1204.6 | 0.67325 | 5.61
2024-12-09 | 20:28 | Data | 0 | 33.25 | 31.515 | 173.24 | 7.62 | 163.488 | 2170.1 | 25.89 | 47.894 | 6.37 | 1.303 | 4.316 | 8377.43 | 1.857 | 97.8 | 76.8 | 1411 | 23.99 | 5445.3 | 1696.1 | 2130.2 | 2733.8 | 1204.6 | 0.61815 | 5.619
2024-12-09 | 20:28 | Data | 0 | 33.358 | 31.785 | 173.467 | 7.62 | 163.443 | 2171.01 | 25.9 | 47.894 | 6.37 | 1.304 | 4.312 | 8386.47 | 1.627 | 97.8 | 76.8 | 1411 | 23.95 | 5451.2 | 1664.5 | 2131.8 | 2716.3 | 1204.6 | 0.61082 | 5.616
2024-12-09 | 20:28 | Data | 0 | 33.419 | 31.758 | 173.467 | 7.62 | 163.533 | 2170.1 | 25.89 | 47.894 | 6.37 | 1.301 | 4.292 | 8381.95 | 1.789 | 97.8 | 76.7 | 1411 | 23.95 | 5448.3 | 1682.2 | 2134.4 | 2729.9 | 1204.6 | 0.6138 | 5.592
2024-12-09 | 20:28 | Data | 0 | 33.52 | 31.583 | 173.512 | 7.63 | 163.533 | 2165.58 | 25.89 | 47.894 | 6.37 | 1.303 | 4.27 | 8390.99 | 1.715 | 97.8 | 76.6 | 1408 | 23.95 | 5454.1 | 1686.7 | 2154.5 | 2749.2 | 1204.6 | 0.61131 | 5.573
2024-12-09 | 20:28 | Data | 0 | 33.25 | 31.9 | 173.421 | 7.63 | 163.488 | 2166.49 | 25.89 | 47.894 | 6.37 | 1.306 | 4.281 | 8381.95 | 1.593 | 97.8 | 76.6 | 1409 | 23.95 | 5448.3 | 1681.1 | 2157.9 | 2746.9 | 1204.6 | 0.60957 | 5.587
2024-12-09 | 20:28 | Data | 0 | 33.297 | 31.799 | 173.467 | 7.63 | 163.443 | 2166.49 | 25.89 | 47.894 | 6.37 | 1.306 | 4.299 | 8377.43 | 1.816 | 97.8 | 76.7 | 1408 | 23.95 | 5445.3 | 1647.2 | 2151.2 | 2722.3 | 1204.6 | 0.60174 | 5.605
2024-12-09 | 20:28 | Data | 0 | 33.297 | 31.67 | 173.421 | 7.63 | 163.352 | 2167.39 | 25.89 | 47.984 | 6.38 | 1.304 | 4.31 | 8372.9 | 1.607 | 97.8 | 76.8 | 1408 | 23.99 | 5442.4 | 1674.6 | 2163.3 | 2749.5 | 1204.6 | 0.60619 | 5.614
2024-12-09 | 20:28 | Data | 0 | 33.399 | 31.94 | 173.376 | 7.63 | 163.488 | 2159.26 | 25.9 | 47.804 | 6.37 | 1.303 | 4.305 | 8386.47 | 1.857 | 97.8 | 76.8 | 1404 | 23.95 | 5451.2 | 1662.9 | 2153 | 2734.3 | 1204.6 | 0.60574 | 5.61
2024-12-09 | 20:28 | Data | 0 | 33.297 | 31.677 | 173.421 | 7.62 | 163.488 | 2169.2 | 25.89 | 47.894 | 6.37 | 1.312 | 4.316 | 8400.04 | 1.722 | 97.8 | 76.7 | 1410 | 23.95 | 5460 | 1686.2 | 2153.7 | 2748 | 1204.6 | 0.61147 | 5.628
2024-12-09 | 20:28 | Data | 0 | 33.358 | 31.596 | 173.512 | 7.63 | 163.443 | 2171.91 | 25.89 | 47.804 | 6.38 | 1.302 | 4.305 | 8390.99 | 1.674 | 97.8 | 76.8 | 1412 | 23.95 | 5454.1 | 1661.5 | 2164.5 | 2729.9 | 1204.6 | 0.60838 | 5.607
2024-12-09 | 20:28 | Data | 0 | 33.412 | 31.711 | 173.376 | 7.63 | 163.443 | 2161.97 | 25.89 | 47.894 | 6.37 | 1.305 | 4.287 | 8372.9 | 1.62 | 97.8 | 76.7 | 1405 | 23.95 | 5442.4 | 1676.5 | 2143.7 | 2734.9 | 1204.6 | 0.61006 | 5.592
2024-12-09 | 20:28 | Data | 0 | 33.574 | 31.474 | 173.376 | 7.63 | 163.488 | 2172.81 | 25.9 | 47.894 | 6.38 | 1.31 | 4.331 | 8372.9 | 1.958 | 97.8 | 76.8 | 1412 | 23.95 | 5442.4 | 1682.4 | 2166.5 | 2754 | 1204.6 | 0.60862 | 5.639
2024-12-09 | 20:28 | Data | 0 | 33.183 | 31.569 | 173.105 | 7.63 | 163.352 | 2171.01 | 25.89 | 47.894 | 6.37 | 1.304 | 4.335 | 8386.47 | 1.789 | 97.8 | 76.9 | 1412 | 23.95 | 5451.2 | 1682.8 | 2157 | 2745 | 1204.6 | 0.61123 | 5.638
2024-12-09 | 20:28 | Data | 0 | 33.412 | 31.785 | 173.376 | 7.62 | 163.352 | 2172.81 | 25.9 | 47.894 | 6.37 | 1.303 | 4.326 | 8372.9 | 1.728 | 97.8 | 76.9 | 1412 | 23.95 | 5442.4 | 1674.3 | 2118.4 | 2712.8 | 1204.6 | 0.61345 | 5.629
2024-12-09 | 20:29 | Data | 0 | 33.426 | 31.772 | 173.467 | 7.63 | 163.533 | 2158.35 | 25.89 | 47.804 | 6.37 | 1.299 | 4.298 | 8400.04 | 1.668 | 97.8 | 76.8 | 1402 | 23.9 | 5460 | 1672.9 | 2139.7 | 2726.8 | 1204.6 | 0.6116 | 5.598
2024-12-09 | 20:29 | Data | 0 | 33.412 | 31.684 | 173.421 | 7.63 | 163.443 | 2174.62 | 25.89 | 47.894 | 6.37 | 1.303 | 4.302 | 8386.47 | 1.843 | 97.8 | 76.7 | 1414 | 23.95 | 5451.2 | 1671.3 | 2148.5 | 2733 | 1204.6 | 0.60915 | 5.604
2024-12-09 | 20:29 | Data | 0 | 33.412 | 31.549 | 173.376 | 7.63 | 163.352 | 2175.52 | 25.89 | 47.894 | 6.37 | 1.308 | 4.305 | 8400.04 | 1.884 | 97.8 | 76.7 | 1414 | 23.9 | 5460 | 1679.7 | 2112.5 | 2711 | 1204.6 | 0.61689 | 5.612
2024-12-09 | 20:29 | Data | 0 | 33.399 | 31.596 | 173.421 | 7.63 | 163.352 | 2175.52 | 25.89 | 47.894 | 6.37 | 1.304 | 4.283 | 8386.47 | 1.62 | 97.8 | 76.6 | 1414 | 23.99 | 5451.2 | 1681 | 2103.1 | 2706 | 1204.6 | 0.61786 | 5.589
2024-12-09 | 20:29 | Data | 0 | 33.439 | 31.468 | 173.331 | 7.62 | 163.488 | 2171.01 | 25.89 | 47.894 | 6.37 | 1.293 | 4.275 | 8363.86 | 1.681 | 97.8 | 76.8 | 1411 | 23.95 | 5436.5 | 1672.7 | 2116.6 | 2710.4 | 1204.6 | 0.61433 | 5.568
2024-12-09 | 20:29 | Data | 0 | 33.412 | 31.508 | 173.24 | 7.62 | 163.352 | 2175.52 | 25.9 | 47.714 | 6.37 | 1.305 | 4.272 | 8345.77 | 1.904 | 97.8 | 76.6 | 1414 | 23.81 | 5424.8 | 1695.2 | 2124.5 | 2728.9 | 1204.6 | 0.61882 | 5.577
2024-12-09 | 20:29 | Data | 0 | 33.196 | 31.745 | 173.421 | 7.63 | 163.488 | 2174.62 | 25.9 | 47.984 | 6.37 | 1.294 | 4.304 | 8341.25 | 1.641 | 97.8 | 76.9 | 1414 | 23.95 | 5421.8 | 1682.3 | 2132.1 | 2722.8 | 1204.6 | 0.61354 | 5.6
2024-12-09 | 20:29 | Data | 0 | 33.162 | 31.569 | 173.376 | 7.63 | 163.352 | 2161.97 | 25.89 | 47.804 | 6.37 | 1.304 | 4.285 | 8350.29 | 1.728 | 97.8 | 76.7 | 1405 | 23.9 | 5427.7 | 1674.3 | 2110.6 | 2707.6 | 1204.6 | 0.6152 | 5.589
2024-12-09 | 20:29 | Data | 0 | 33.419 | 31.711 | 173.331 | 7.62 | 163.352 | 2175.52 | 25.89 | 47.894 | 6.37 | 1.308 | 4.308 | 8363.86 | 1.789 | 97.8 | 76.7 | 1414 | 23.95 | 5436.5 | 1673.2 | 2168.3 | 2752 | 1204.6 | 0.60512 | 5.616
2024-12-09 | 20:29 | Data | 0 | 33.466 | 31.36 | 173.376 | 7.62 | 163.488 | 2174.62 | 25.9 | 48.436 | 6.37 | 1.306 | 4.326 | 8359.34 | 1.843 | 97.8 | 76.8 | 1414 | 24.22 | 5433.6 | 1671.6 | 2148.8 | 2733.6 | 1204.6 | 0.60906 | 5.631
2024-12-09 | 20:29 | Data | 0 | 33.412 | 31.569 | 173.376 | 7.62 | 163.443 | 2177.33 | 25.9 | 47.894 | 6.37 | 1.302 | 4.319 | 8372.9 | 1.728 | 97.8 | 76.8 | 1415 | 23.9 | 5442.4 | 1664 | 2131.6 | 2717.5 | 1204.6 | 0.60963 | 5.621
2024-12-09 | 20:29 | Data | 0 | 33.399 | 31.569 | 173.421 | 7.62 | 163.307 | 2182.75 | 25.89 | 47.894 | 6.37 | 1.297 | 4.317 | 8359.34 | 1.836 | 97.8 | 76.9 | 1419 | 23.9 | 5433.6 | 1668.2 | 2133.5 | 2731.3 | 1204.6 | 0.61605 | 5.615
2024-12-09 | 20:29 | Data | 0 | 33.412 | 31.569 | 173.24 | 7.62 | 163.352 | 2166.49 | 25.89 | 47.894 | 6.38 | 1.295 | 4.295 | 8359.34 | 1.843 | 97.8 | 76.8 | 1409 | 23.9 | 5433.6 | 1675.5 | 2113.9 | 2710.3 | 1204.6 | 0.61606 | 5.591
2024-12-09 | 20:29 | Data | 0 | 33.797 | 31.826 | 173.421 | 7.63 | 163.533 | 2178.24 | 25.89 | 47.894 | 6.38 | 1.299 | 4.289 | 8368.38 | 1.836 | 97.8 | 76.8 | 1416 | 23.95 | 5439.4 | 1678.1 | 2108.1 | 2707.2 | 1204.6 | 0.61719 | 5.589
2024-12-09 | 20:29 | Data | 0 | 33.466 | 31.481 | 173.331 | 7.63 | 163.307 | 2180.95 | 25.89 | 47.894 | 6.37 | 1.306 | 4.308 | 8359.34 | 1.681 | 97.8 | 76.7 | 1418 | 23.99 | 5433.6 | 1661 | 2113.2 | 2699.6 | 1204.6 | 0.61224 | 5.614
2024-12-09 | 20:29 | Data | 0 | 33.405 | 31.873 | 173.24 | 7.63 | 163.352 | 2180.04 | 25.89 | 47.894 | 6.38 | 1.308 | 4.312 | 8372.9 | 1.654 | 97.8 | 76.7 | 1416 | 23.95 | 5442.4 | 1666.5 | 2129.1 | 2717.8 | 1204.6 | 0.61015 | 5.619
2024-12-09 | 20:29 | Data | 0 | 33.189 | 31.569 | 173.195 | 7.62 | 163.307 | 2176.43 | 25.89 | 47.984 | 6.37 | 1.301 | 4.304 | 8372.9 | 1.614 | 97.8 | 76.8 | 1415 | 23.95 | 5442.4 | 1674.3 | 2121.6 | 2717 | 1204.6 | 0.61222 | 5.605
2024-12-09 | 20:30 | Data | 0 | 33.385 | 31.596 | 173.331 | 7.63 | 163.262 | 2176.43 | 25.89 | 47.894 | 6.38 | 1.306 | 4.274 | 8354.81 | 1.722 | 97.8 | 76.6 | 1415 | 23.9 | 5430.6 | 1698.4 | 2148.1 | 2749.7 | 1204.6 | 0.61472 | 5.581
2024-12-09 | 20:30 | Data | 0 | 33.297 | 31.772 | 173.331 | 7.63 | 163.352 | 2177.33 | 25.88 | 47.984 | 6.38 | 1.305 | 4.275 | 8359.34 | 1.755 | 97.8 | 76.6 | 1415 | 23.95 | 5433.6 | 1687.1 | 2152.2 | 2739.7 | 1204.6 | 0.61289 | 5.581
2024-12-09 | 20:30 | Data | 0 | 33.304 | 31.454 | 173.467 | 7.63 | 163.488 | 2182.75 | 25.89 | 47.894 | 6.38 | 1.308 | 4.289 | 8332.2 | 1.735 | 97.8 | 76.6 | 1419 | 23.95 | 5415.9 | 1678.4 | 2166.2 | 2752.7 | 1204.6 | 0.60745 | 5.597
2024-12-09 | 20:30 | Data | 0 | 33.183 | 31.515 | 173.376 | 7.62 | 163.352 | 2182.75 | 25.9 | 47.894 | 6.37 | 1.306 | 4.295 | 8336.72 | 1.728 | 97.8 | 76.7 | 1419 | 23.95 | 5418.9 | 1657.3 | 2145.5 | 2723.7 | 1204.6 | 0.6131 | 5.601
2024-12-09 | 20:30 | Data | 0 | 33.54 | 31.576 | 173.512 | 7.62 | 163.443 | 2182.75 | 25.89 | 47.894 | 6.37 | 1.313 | 4.285 | 8332.2 | 1.728 | 97.8 | 76.5 | 1419 | 23.99 | 5415.9 | 1665.3 | 2120.1 | 2707.6 | 1204.6 | 0.6126 | 5.599
2024-12-09 | 20:30 | Data | 0 | 33.385 | 31.623 | 173.421 | 7.62 | 163.533 | 2187.27 | 25.89 | 47.984 | 6.38 | 1.306 | 4.323 | 8336.72 | 1.836 | 97.8 | 76.8 | 1421 | 23.95 | 5418.9 | 1693.1 | 2132 | 2734.6 | 1204.6 | 0.6161 | 5.629
2024-12-09 | 20:30 | Data | 0 | 33.358 | 31.468 | 173.15 | 7.63 | 163.443 | 2180.95 | 25.89 | 47.804 | 6.37 | 1.301 | 4.287 | 8341.25 | 1.809 | 97.8 | 76.7 | 1417 | 23.9 | 5421.8 | 1678.7 | 2121.5 | 2717.7 | 1204.6 | 0.6154 | 5.587
2024-12-09 | 20:30 | Data | 0 | 33.162 | 31.366 | 173.24 | 7.63 | 163.307 | 2184.56 | 25.89 | 47.894 | 6.37 | 1.297 | 4.304 | 8345.77 | 1.782 | 97.8 | 76.9 | 1420 | 23.9 | 5424.8 | 1682.8 | 2131.2 | 2728.8 | 1204.6 | 0.6117 | 5.602
2024-12-09 | 20:30 | Data | 0 | 33.183 | 31.765 | 173.24 | 7.63 | 163.443 | 2175.52 | 25.89 | 47.894 | 6.37 | 1.295 | 4.267 | 8359.34 | 1.728 | 97.8 | 76.7 | 1414 | 23.95 | 5433.6 | 1678.9 | 2139.5 | 2719.5 | 1204.6 | 0.60669 | 5.563
2024-12-09 | 20:30 | Data | 0 | 33.196 | 31.528 | 173.195 | 7.62 | 163.352 | 2194.5 | 25.89 | 47.894 | 6.38 | 1.296 | 4.295 | 8318.64 | 1.857 | 97.8 | 76.8 | 1426 | 23.95 | 5407.1 | 1683.9 | 2156.4 | 2748.3 | 1204.6 | 0.60975 | 5.592
2024-12-09 | 20:30 | Data | 0 | 33.297 | 31.407 | 173.24 | 7.62 | 163.352 | 2175.52 | 25.89 | 47.894 | 6.37 | 1.294 | 4.315 | 8345.77 | 1.789 | 97.8 | 76.9 | 1414 | 23.95 | 5424.8 | 1689 | 2165.7 | 2760 | 1204.6 | 0.60881 | 5.61
2024-12-09 | 20:30 | Data | 0 | 33.419 | 31.569 | 173.467 | 7.62 | 163.307 | 2180.95 | 25.89 | 47.804 | 6.38 | 1.307 | 4.313 | 8345.77 | 1.512 | 97.8 | 76.7 | 1418 | 23.95 | 5424.8 | 1686.5 | 2192.1 | 2778.8 | 1204.6 | 0.60324 | 5.622
2024-12-09 | 20:30 | Data | 0 | 33.358 | 31.373 | 173.331 | 7.62 | 163.352 | 2181.85 | 25.89 | 47.894 | 6.38 | 1.295 | 4.309 | 8345.77 | 1.884 | 97.8 | 76.9 | 1419 | 23.9 | 5424.8 | 1679.9 | 2143.1 | 2736.4 | 1204.6 | 0.6115 | 5.605
2024-12-09 | 20:30 | Data | 0 | 33.129 | 31.569 | 173.331 | 7.63 | 163.352 | 2180.95 | 25.89 | 47.984 | 6.37 | 1.297 | 4.297 | 8341.25 | 1.769 | 97.8 | 76.8 | 1418 | 23.9 | 5421.8 | 1664.9 | 2121.9 | 2707.8 | 1204.6 | 0.60591 | 5.594
2024-12-09 | 20:30 | Data | 0 | 33.183 | 31.339 | 173.24 | 7.62 | 163.488 | 2180.04 | 25.89 | 47.984 | 6.37 | 1.301 | 4.297 | 8363.86 | 1.836 | 97.8 | 76.8 | 1417 | 23.95 | 5436.5 | 1678 | 2153.1 | 2741.3 | 1204.6 | 0.60955 | 5.597
2024-12-09 | 20:30 | Data | 0 | 33.399 | 31.569 | 173.24 | 7.62 | 163.307 | 2179.14 | 25.89 | 47.894 | 6.38 | 1.304 | 4.32 | 8372.9 | 1.836 | 97.8 | 76.8 | 1417 | 23.95 | 5442.4 | 1663.1 | 2108 | 2699 | 1204.6 | 0.61373 | 5.624
2024-12-09 | 20:30 | Data | 0 | 32.987 | 31.4 | 173.24 | 7.62 | 163.262 | 2180.95 | 25.89 | 47.894 | 6.38 | 1.31 | 4.34 | 8372.9 | 1.728 | 97.8 | 76.8 | 1418 | 23.95 | 5442.4 | 1691.7 | 2124.2 | 2728.2 | 1204.6 | 0.61779 | 5.649
2024-12-09 | 20:31 | Data | 0 | 33.183 | 31.569 | 173.24 | 7.63 | 163.352 | 2177.33 | 25.89 | 47.894 | 6.37 | 1.306 | 4.285 | 8359.34 | 1.789 | 97.8 | 76.7 | 1415 | 23.95 | 5433.6 | 1692.2 | 2127.3 | 2730.4 | 1204.6 | 0.61723 | 5.591
2024-12-09 | 20:31 | Data | 0 | 33.412 | 31.61 | 173.195 | 7.62 | 163.307 | 2178.24 | 25.89 | 47.804 | 6.37 | 1.308 | 4.278 | 8368.38 | 1.674 | 97.8 | 76.6 | 1415 | 23.95 | 5439.4 | 1677.6 | 2109.3 | 2709.8 | 1204.6 | 0.61576 | 5.585
2024-12-09 | 20:31 | Data | 0 | 33.297 | 31.366 | 173.331 | 7.62 | 163.352 | 2176.43 | 25.89 | 47.894 | 6.37 | 1.303 | 4.26 | 8381.95 | 1.816 | 97.8 | 76.6 | 1415 | 23.95 | 5448.3 | 1662.8 | 2112.9 | 2701.6 | 1204.6 | 0.6108 | 5.563
2024-12-09 | 20:31 | Data | 0 | 33.183 | 31.731 | 173.421 | 7.62 | 163.307 | 2172.81 | 25.89 | 47.894 | 6.37 | 1.3 | 4.29 | 8372.9 | 1.654 | 97.8 | 76.7 | 1413 | 23.95 | 5442.4 | 1680 | 2130.6 | 2725 | 1204.6 | 0.61406 | 5.59
2024-12-09 | 20:31 | Data | 0 | 33.034 | 31.346 | 173.195 | 7.63 | 163.352 | 2178.24 | 25.89 | 47.894 | 6.37 | 1.296 | 4.307 | 8377.43 | 1.641 | 97.8 | 76.9 | 1416 | 23.95 | 5445.3 | 1685 | 2141.5 | 2736.5 | 1204.6 | 0.6136 | 5.603
2024-12-09 | 20:31 | Data | 0 | 33.183 | 31.515 | 173.105 | 7.62 | 163.217 | 2173.72 | 25.89 | 47.894 | 6.37 | 1.291 | 4.294 | 8571.88 | 1.708 | 97.8 | 76.9 | 1414 | 23.95 | 5571.7 | 1678.6 | 2123.7 | 2718.8 | 1204.6 | 0.6149 | 5.585
2024-12-09 | 20:31 | Data | 0 | 33.493 | 31.407 | 173.24 | 7.63 | 163.352 | 2178.24 | 25.89 | 47.804 | 6.38 | 1.301 | 4.304 | 8580.93 | 1.681 | 97.8 | 76.8 | 1416 | 23.9 | 5577.6 | 2742.3 | 2740 | 4004.8 | 1204.6 | 0.66679 | 5.604
2024-12-09 | 20:31 | Data | 0 | 33.183 | 31.447 | 173.331 | 7.63 | 163.352 | 2177.33 | 25.9 | 47.894 | 6.37 | 1.301 | 4.304 | 8576.4 | 1.803 | 97.8 | 76.8 | 1415 | 23.95 | 5574.7 | 2763.3 | 2703.3 | 3988.2 | 1204.6 | 0.67336 | 5.604
2024-12-09 | 20:31 | Data | 0 | 33.088 | 31.339 | 173.376 | 7.63 | 163.443 | 2180.95 | 25.89 | 47.894 | 6.37 | 1.303 | 4.301 | 8567.36 | 1.701 | 97.8 | 76.7 | 1418 | 23.99 | 5568.8 | 2764.3 | 2711.9 | 3998.5 | 1204.6 | 0.67369 | 5.604
2024-12-09 | 20:31 | Data | 0 | 33.068 | 31.454 | 173.376 | 7.63 | 163.307 | 2187.27 | 25.89 | 47.894 | 6.37 | 1.306 | 4.282 | 8377.43 | 1.83 | 97.8 | 76.6 | 1422 | 23.95 | 5445.3 | 2761.9 | 2710 | 3997 | 1204.7 | 0.67424 | 5.589
2024-12-09 | 20:31 | Data | 0 | 33.399 | 31.468 | 173.376 | 7.63 | 163.307 | 2180.04 | 25.89 | 45.727 | 6.37 | 1.304 | 4.269 | 8372.9 | 2.012 | 97.9 | 76.6 | 1418 | 22.86 | 5442.4 | 2762.2 | 2718.2 | 4001.4 | 1204.7 | 0.67381 | 5.573
2024-12-09 | 20:31 | Data | 0 | 33.324 | 31.454 | 173.331 | 7.63 | 163.488 | 2180.95 | 25.89 | 47.894 | 6.37 | 1.303 | 4.296 | 8368.38 | 1.641 | 97.8 | 76.7 | 1417 | 23.99 | 5439.4 | 2738.8 | 2728.1 | 3993.2 | 1204.7 | 0.66808 | 5.6
2024-12-09 | 20:31 | Data | 0 | 32.96 | 31.285 | 173.331 | 7.62 | 163.262 | 2177.33 | 25.89 | 47.894 | 6.37 | 1.31 | 4.294 | 8363.86 | 1.836 | 97.8 | 76.6 | 1415 | 23.95 | 5436.5 | 2758.9 | 2730.9 | 4010.4 | 1204.7 | 0.67056 | 5.604
2024-12-09 | 20:31 | Data | 0 | 33.351 | 31.569 | 173.24 | 7.62 | 163.352 | 2177.33 | 25.89 | 47.894 | 6.37 | 1.305 | 4.277 | 8359.34 | 1.83 | 97.8 | 76.6 | 1416 | 23.95 | 5433.6 | 2766.1 | 2728.8 | 4004.1 | 1204.7 | 0.67263 | 5.582
2024-12-09 | 20:31 | Data | 0 | 33.405 | 31.772 | 173.376 | 7.63 | 163.352 | 2177.33 | 25.88 | 47.894 | 6.37 | 1.309 | 4.267 | 8359.34 | 1.728 | 97.8 | 76.5 | 1415 | 23.9 | 5433.6 | 2761.9 | 2738.2 | 4017 | 1204.7 | 0.67126 | 5.577
2024-12-09 | 20:31 | Data | 0 | 33.183 | 31.569 | 173.24 | 7.62 | 163.307 | 2177.33 | 25.88 | 47.984 | 6.37 | 1.31 | 4.295 | 8359.34 | 1.755 | 97.8 | 76.6 | 1415 | 23.95 | 5433.6 | 2741.6 | 2752 | 3999.1 | 1204.7 | 0.66712 | 5.605
2024-12-09 | 20:31 | Data | 0 | 33.081 | 31.292 | 173.24 | 7.63 | 163.262 | 2180.95 | 25.88 | 47.804 | 6.37 | 1.297 | 4.299 | 8350.29 | 1.722 | 97.8 | 76.8 | 1418 | 23.95 | 5427.7 | 2756.6 | 2765.5 | 4019.1 | 1204.7 | 0.66897 | 5.596
2024-12-09 | 20:32 | Data | 0 | 33.189 | 31.569 | 173.376 | 7.63 | 163.443 | 2183.66 | 25.88 | 47.894 | 6.37 | 1.308 | 4.269 | 8350.29 | 1.62 | 97.8 | 76.6 | 1419 | 23.95 | 5427.7 | 2757.1 | 2747 | 4027.1 | 1204.7 | 0.67088 | 5.577
2024-12-09 | 20:32 | Data | 0 | 33.176 | 31.346 | 173.15 | 7.62 | 163.307 | 2183.66 | 25.89 | 47.804 | 6.37 | 1.312 | 4.304 | 8332.2 | 1.83 | 97.8 | 76.6 | 1419 | 23.9 | 5415.9 | 2773 | 2721.8 | 4013.2 | 1204.7 | 0.67402 | 5.618
2024-12-09 | 20:32 | Data | 0 | 33.405 | 31.454 | 173.376 | 7.63 | 163.443 | 2184.56 | 25.88 | 47.894 | 6.38 | 1.294 | 4.312 | 8341.25 | 1.755 | 97.8 | 76.9 | 1420 | 23.95 | 5421.8 | 2774.5 | 2735.4 | 4023 | 1204.7 | 0.67161 | 5.606
2024-12-09 | 20:32 | Data | 0 | 33.183 | 31.353 | 173.195 | 7.62 | 163.307 | 2186.37 | 25.89 | 47.894 | 6.37 | 1.289 | 4.316 | 8336.72 | 1.83 | 97.8 | 77 | 1421 | 23.9 | 5418.9 | 2772.1 | 2714 | 4005.9 | 1204.7 | 0.6748 | 5.605
2024-12-09 | 20:32 | Data | 0 | 33.466 | 31.785 | 173.467 | 7.63 | 163.443 | 2186.37 | 25.88 | 47.894 | 6.38 | 1.303 | 4.308 | 8341.25 | 1.695 | 97.8 | 76.8 | 1421 | 23.95 | 5421.8 | 2756.7 | 2722.5 | 4001.5 | 1204.7 | 0.67109 | 5.611
2024-12-09 | 20:32 | Data | 0 | 33.358 | 31.393 | 173.24 | 7.62 | 163.307 | 2189.08 | 25.88 | 47.894 | 6.37 | 1.301 | 4.352 | 8336.72 | 1.776 | 97.8 | 77 | 1423 | 23.95 | 5418.9 | 2778 | 2710.3 | 4007.3 | 1204.7 | 0.67378 | 5.653
2024-12-09 | 20:32 | Data | 0 | 33.21 | 31.515 | 172.833 | 7.62 | 162.901 | 2189.08 | 25.88 | 47.894 | 6.37 | 1.288 | 4.314 | 8341.25 | 1.83 | 97.8 | 77 | 1423 | 23.99 | 5421.8 | 2803.8 | 2706.1 | 4018.7 | 1204.7 | 0.68039 | 5.601
2024-12-09 | 20:32 | Data | 0 | 33.297 | 31.4 | 172.879 | 7.63 | 163.036 | 2189.08 | 25.88 | 47.894 | 6.37 | 1.307 | 4.294 | 8336.72 | 1.755 | 97.8 | 76.7 | 1423 | 23.95 | 5418.9 | 2787.3 | 2724.9 | 4022.7 | 1204.7 | 0.6768 | 5.6
2024-12-09 | 20:32 | Data | 0 | 33.324 | 31.353 | 173.06 | 7.62 | 163.126 | 2186.37 | 25.88 | 47.804 | 6.37 | 1.299 | 4.303 | 8332.2 | 1.674 | 97.8 | 76.8 | 1421 | 23.95 | 5415.9 | 2778.8 | 2714.4 | 4015.7 | 1204.7 | 0.67432 | 5.601
2024-12-09 | 20:32 | Data | 0 | 33.183 | 31.461 | 172.833 | 7.63 | 162.991 | 2182.75 | 25.89 | 47.804 | 6.37 | 1.3 | 4.273 | 8350.29 | 1.722 | 97.8 | 76.7 | 1419 | 23.95 | 5427.7 | 2767.5 | 2721.8 | 4008.9 | 1204.7 | 0.67206 | 5.573
2024-12-09 | 20:32 | Data | 0 | 33.304 | 31.346 | 172.879 | 7.63 | 163.081 | 2187.27 | 25.89 | 47.894 | 6.37 | 1.306 | 4.28 | 8345.77 | 1.681 | 97.8 | 76.6 | 1421 | 23.95 | 5424.8 | 2779.1 | 2740.3 | 4033.7 | 1204.7 | 0.66977 | 5.586
2024-12-09 | 20:32 | Data | 0 | 32.987 | 31.562 | 172.879 | 7.63 | 162.946 | 2190.89 | 25.88 | 47.894 | 6.37 | 1.303 | 4.268 | 7947.81 | 1.58 | 97.8 | 76.6 | 1425 | 23.99 | 5166.1 | 2770.3 | 2717.7 | 4009.5 | 1204.7 | 0.67321 | 5.572
2024-12-09 | 20:32 | Data | 0 | 33.324 | 31.373 | 172.879 | 7.63 | 163.081 | 2184.56 | 25.88 | 47.984 | 6.37 | 1.297 | 4.285 | 8345.77 | 1.749 | 97.8 | 76.8 | 1421 | 23.99 | 5424.8 | 2775 | 2726.2 | 4015.9 | 1204.7 | 0.67172 | 5.582
2024-12-09 | 20:32 | Data | 0 | 33.189 | 31.454 | 172.969 | 7.63 | 163.036 | 2187.27 | 25.89 | 48.075 | 6.37 | 1.301 | 4.291 | 8350.29 | 1.836 | 97.8 | 76.7 | 1422 | 24.04 | 5427.7 | 2786.6 | 2720 | 4021.6 | 1204.7 | 0.67549 | 5.592
2024-12-09 | 20:32 | Data | 0 | 33.176 | 31.542 | 172.833 | 7.62 | 162.991 | 2186.37 | 25.89 | 47.894 | 6.38 | 1.296 | 4.304 | 8359.34 | 1.728 | 97.8 | 76.8 | 1421 | 23.95 | 5433.6 | 2782.7 | 2704.9 | 4010 | 1204.7 | 0.67635 | 5.6
2024-12-09 | 20:32 | Data | 0 | 33.297 | 31.569 | 172.924 | 7.63 | 163.036 | 2176.43 | 25.89 | 47.894 | 6.37 | 1.304 | 4.289 | 8363.86 | 1.83 | 97.8 | 76.7 | 1415 | 23.95 | 5436.5 | 2782.3 | 2733 | 4029.5 | 1204.7 | 0.67343 | 5.593
2024-12-09 | 20:32 | Data | 0 | 32.994 | 31.542 | 173.014 | 7.62 | 163.126 | 2183.66 | 25.88 | 47.894 | 6.37 | 1.303 | 4.302 | 8359.34 | 1.56 | 97.8 | 76.7 | 1419 | 23.95 | 5433.6 | 2763.7 | 2685.4 | 3985.6 | 1204.7 | 0.67608 | 5.604
2024-12-09 | 20:32 | Data | 0 | 33.453 | 31.697 | 173.014 | 7.63 | 163.081 | 2178.24 | 25.89 | 47.894 | 6.37 | 1.295 | 4.27 | 8363.86 | 1.607 | 97.8 | 76.7 | 1416 | 23.95 | 5436.5 | 2765.3 | 2705.5 | 3999.6 | 1204.7 | 0.67478 | 5.565
2024-12-09 | 20:32 | Data | 0 | 33.297 | 31.549 | 173.06 | 7.62 | 163.081 | 2182.75 | 25.88 | 47.804 | 6.37 | 1.294 | 4.287 | 8345.77 | 1.661 | 97.8 | 76.8 | 1419 | 23.9 | 5424.8 | 2763.1 | 2701.2 | 3998.6 | 1204.7 | 0.67247 | 5.581
2024-12-09 | 20:33 | Data | 0 | 33.183 | 31.569 | 172.833 | 7.62 | 162.901 | 2182.75 | 25.89 | 47.984 | 6.37 | 1.304 | 4.292 | 8359.34 | 1.647 | 97.8 | 76.7 | 1419 | 23.99 | 5433.6 | 2783.2 | 2726.3 | 4022.6 | 1204.7 | 0.67414 | 5.595
2024-12-09 | 20:33 | Data | 0 | 33.284 | 31.366 | 172.879 | 7.63 | 162.946 | 2181.85 | 25.88 | 47.894 | 6.37 | 1.295 | 4.304 | 8332.2 | 2.005 | 97.8 | 76.9 | 1418 | 23.95 | 5415.9 | 2795.9 | 2738.7 | 4038 | 1204.7 | 0.67503 | 5.599
2024-12-09 | 20:33 | Data | 0 | 32.973 | 31.724 | 172.879 | 7.63 | 163.036 | 2180.95 | 25.88 | 47.894 | 6.37 | 1.292 | 4.276 | 8332.2 | 1.479 | 97.8 | 76.8 | 1418 | 23.95 | 5415.9 | 2763.9 | 2762.5 | 4041.8 | 1204.7 | 0.66572 | 5.568
2024-12-09 | 20:33 | Data | 0 | 32.973 | 31.515 | 172.969 | 7.63 | 163.036 | 2183.66 | 25.89 | 47.894 | 6.38 | 1.305 | 4.288 | 8336.72 | 1.614 | 97.8 | 76.7 | 1419 | 23.95 | 5418.9 | 2775.6 | 2739.1 | 4025.2 | 1204.7 | 0.67024 | 5.594
2024-12-09 | 20:33 | Data | 0 | 33.108 | 31.346 | 172.879 | 7.63 | 163.081 | 2182.75 | 25.88 | 47.894 | 6.37 | 1.31 | 4.3 | 8318.64 | 1.641 | 97.8 | 76.6 | 1419 | 23.95 | 5407.1 | 2789 | 2731.7 | 4035.1 | 1204.7 | 0.67224 | 5.611
2024-12-09 | 20:33 | Data | 0 | 33.183 | 31.454 | 172.833 | 7.62 | 163.036 | 2182.75 | 25.88 | 47.894 | 6.38 | 1.305 | 4.304 | 8372.9 | 1.836 | 97.8 | 76.7 | 1419 | 23.9 | 5442.4 | 2796.4 | 2716.9 | 4025.3 | 1204.7 | 0.67935 | 5.61
2024-12-09 | 20:33 | Data | 0 | 33.189 | 31.346 | 172.879 | 7.63 | 163.036 | 2178.24 | 25.89 | 47.894 | 6.37 | 1.311 | 4.295 | 8372.9 | 1.742 | 97.8 | 76.6 | 1416 | 23.95 | 5442.4 | 2785 | 2719.4 | 4017.3 | 1204.7 | 0.67598 | 5.607
2024-12-09 | 20:33 | Data | 0 | 33.358 | 31.569 | 172.833 | 7.62 | 162.991 | 2180.95 | 25.88 | 47.894 | 6.37 | 1.305 | 4.264 | 8372.9 | 1.728 | 97.8 | 76.6 | 1418 | 23.9 | 5442.4 | 2775.8 | 2729.5 | 4021.5 | 1204.7 | 0.67415 | 5.567
2024-12-09 | 20:33 | Data | 0 | 33.189 | 31.569 | 173.06 | 7.62 | 163.036 | 2175.52 | 25.88 | 47.894 | 6.37 | 1.301 | 4.274 | 8386.47 | 1.614 | 97.8 | 76.7 | 1414 | 23.95 | 5451.2 | 2792.4 | 2718.1 | 4027.3 | 1204.7 | 0.67346 | 5.573
2024-12-09 | 20:33 | Data | 0 | 33.081 | 31.366 | 172.833 | 7.63 | 162.991 | 2180.95 | 25.89 | 47.894 | 6.37 | 1.302 | 4.276 | 8187.49 | 1.566 | 97.8 | 76.6 | 1418 | 23.95 | 5321.9 | 2694.7 | 2714.7 | 3950.9 | 1204.7 | 0.66538 | 5.58
2024-12-09 | 20:33 | Data | 0 | 33.324 | 31.339 | 172.924 | 7.62 | 162.901 | 2170.1 | 25.89 | 47.894 | 6.37 | 1.301 | 4.295 | 8160.36 | 1.512 | 97.8 | 76.7 | 1410 | 23.95 | 5304.2 | 2697.8 | 2714.7 | 3950.7 | 1204.7 | 0.66614 | 5.596
2024-12-09 | 20:33 | Data | 0 | 33.068 | 31.65 | 172.879 | 7.63 | 162.855 | 2176.43 | 25.88 | 47.533 | 6.37 | 1.3 | 4.304 | 8164.88 | 1.587 | 97.8 | 76.8 | 1415 | 23.77 | 5307.2 | 2714.9 | 2713.6 | 3958.8 | 1204.8 | 0.66831 | 5.603
2024-12-09 | 20:33 | Data | 0 | 33.183 | 31.576 | 172.788 | 7.63 | 162.946 | 2180.04 | 25.89 | 47.894 | 6.37 | 1.293 | 4.292 | 8155.84 | 1.701 | 97.8 | 76.8 | 1417 | 23.95 | 5301.3 | 2735.6 | 2689 | 3957.3 | 1204.8 | 0.67592 | 5.585
2024-12-09 | 20:33 | Data | 0 | 33.21 | 31.366 | 172.833 | 7.63 | 162.946 | 2182.75 | 25.89 | 47.894 | 6.38 | 1.292 | 4.285 | 8336.72 | 1.789 | 97.8 | 76.8 | 1419 | 23.95 | 5418.9 | 2722.6 | 2682.4 | 3944.2 | 1204.8 | 0.67332 | 5.576
2024-12-09 | 20:33 | Data | 0 | 33.095 | 31.339 | 172.833 | 7.62 | 162.946 | 2182.75 | 25.88 | 47.894 | 6.37 | 1.297 | 4.282 | 8359.34 | 1.803 | 97.8 | 76.8 | 1419 | 23.95 | 5433.6 | 2685.1 | 2695.9 | 3932.1 | 1204.8 | 0.66602 | 5.579
2024-12-09 | 20:33 | Data | 0 | 33.392 | 31.569 | 172.924 | 7.62 | 163.036 | 2174.62 | 25.88 | 47.894 | 6.38 | 1.302 | 4.283 | 8350.29 | 1.843 | 97.8 | 76.7 | 1414 | 23.95 | 5427.7 | 2716.2 | 2708.5 | 3961.6 | 1204.8 | 0.67181 | 5.584
2024-12-09 | 20:33 | Data | 0 | 33.129 | 31.677 | 172.924 | 7.63 | 162.901 | 2177.33 | 25.89 | 47.894 | 6.37 | 1.294 | 4.295 | 8359.34 | 1.701 | 97.8 | 76.9 | 1416 | 23.95 | 5433.6 | 2707.4 | 2680.5 | 3934.9 | 1204.8 | 0.67015 | 5.59
2024-12-09 | 20:34 | Data | 0 | 33.351 | 31.569 | 173.014 | 7.62 | 163.036 | 2180.04 | 25.89 | 47.894 | 6.38 | 1.293 | 4.305 | 8345.77 | 1.83 | 97.8 | 76.9 | 1417 | 23.95 | 5424.8 | 2721.3 | 2692.1 | 3961.5 | 1204.8 | 0.6682 | 5.599
2024-12-09 | 20:34 | Data | 0 | 33.183 | 31.542 | 172.788 | 7.63 | 162.901 | 2186.37 | 25.88 | 47.894 | 6.37 | 1.309 | 4.305 | 8345.77 | 1.668 | 97.8 | 76.7 | 1422 | 23.95 | 5424.8 | 2764.5 | 2696.7 | 3987.6 | 1204.8 | 0.67568 | 5.613
2024-12-09 | 20:34 | Data | 0 | 33.183 | 31.515 | 172.833 | 7.63 | 162.901 | 2183.66 | 25.88 | 47.984 | 6.38 | 1.315 | 4.281 | 8350.29 | 1.83 | 97.8 | 76.5 | 1419 | 23.95 | 5427.7 | 2742.5 | 2701 | 3976.8 | 1204.8 | 0.6718 | 5.594
2024-12-09 | 20:34 | Data | 0 | 33.156 | 31.562 | 172.743 | 7.63 | 162.901 | 2183.66 | 25.88 | 47.894 | 6.37 | 1.305 | 4.29 | 8363.86 | 1.614 | 97.8 | 76.7 | 1419 | 23.99 | 5436.5 | 2759.5 | 2710.7 | 3994 | 1204.8 | 0.67378 | 5.596
2024-12-09 | 20:34 | Data | 0 | 33.183 | 31.339 | 172.788 | 7.62 | 162.901 | 2180.95 | 25.88 | 47.714 | 6.37 | 1.296 | 4.288 | 8368.38 | 1.843 | 97.8 | 76.8 | 1418 | 23.86 | 5439.4 | 2761.8 | 2738.6 | 4020.2 | 1204.8 | 0.66825 | 5.584
2024-12-09 | 20:34 | Data | 0 | 33.284 | 31.805 | 172.879 | 7.63 | 163.036 | 2180.95 | 25.89 | 47.894 | 6.37 | 1.301 | 4.298 | 8363.86 | 1.803 | 97.8 | 76.8 | 1417 | 23.95 | 5436.5 | 2756.4 | 2733.4 | 4004.7 | 1204.8 | 0.67109 | 5.6
2024-12-09 | 20:34 | Data | 0 | 32.946 | 31.434 | 173.014 | 7.63 | 163.126 | 2180.04 | 25.89 | 47.894 | 6.37 | 1.302 | 4.283 | 8354.81 | 1.418 | 97.8 | 76.7 | 1418 | 23.95 | 5430.6 | 2762.4 | 2739 | 4013.5 | 1204.8 | 0.66973 | 5.585
2024-12-09 | 20:34 | Data | 0 | 33.081 | 31.353 | 172.698 | 7.63 | 162.901 | 2180.04 | 25.88 | 47.894 | 6.37 | 1.307 | 4.27 | 8350.29 | 1.62 | 97.8 | 76.6 | 1417 | 23.95 | 5427.7 | 2760 | 2721.8 | 4004.5 | 1204.8 | 0.67117 | 5.576
2024-12-09 | 20:34 | Data | 0 | 32.96 | 31.339 | 172.788 | 7.62 | 162.855 | 2178.24 | 25.88 | 47.894 | 6.37 | 1.305 | 4.27 | 8318.64 | 1.62 | 97.8 | 76.6 | 1416 | 23.95 | 5407.1 | 2763 | 2759.6 | 4034.8 | 1204.8 | 0.6664 | 5.576
2024-12-09 | 20:34 | Data | 0 | 33.169 | 31.339 | 172.833 | 7.63 | 162.81 | 2177.33 | 25.88 | 47.894 | 6.38 | 1.302 | 4.284 | 8305.07 | 1.843 | 97.8 | 76.7 | 1415 | 23.95 | 5398.3 | 2770.6 | 2741.9 | 4026.5 | 1204.8 | 0.67398 | 5.587
2024-12-09 | 20:34 | Data | 0 | 33.338 | 31.562 | 172.924 | 7.63 | 162.991 | 2170.1 | 25.88 | 47.894 | 6.37 | 1.302 | 4.307 | 8300.55 | 1.897 | 97.8 | 76.8 | 1411 | 23.95 | 5395.4 | 2764.1 | 2720.9 | 4002.4 | 1204.8 | 0.67118 | 5.61
2024-12-09 | 20:34 | Data | 0 | 33.014 | 31.13 | 172.743 | 7.63 | 162.946 | 2171.01 | 25.88 | 47.894 | 6.38 | 1.295 | 4.299 | 8314.11 | 1.803 | 97.8 | 76.9 | 1411 | 23.9 | 5404.2 | 2770.3 | 2732.6 | 4017.5 | 1204.8 | 0.67148 | 5.595
2024-12-09 | 20:34 | Data | 0 | 33.338 | 31.569 | 172.833 | 7.63 | 162.946 | 2170.1 | 25.88 | 47.984 | 6.37 | 1.304 | 4.268 | 8305.07 | 1.816 | 97.8 | 76.6 | 1411 | 23.99 | 5398.3 | 2786.3 | 2717 | 4016.5 | 1204.8 | 0.67759 | 5.572
2024-12-09 | 20:34 | Data | 0 | 33.27 | 31.562 | 172.833 | 7.63 | 162.946 | 2174.62 | 25.89 | 47.623 | 6.37 | 1.313 | 4.287 | 8318.64 | 1.83 | 97.8 | 76.5 | 1414 | 23.81 | 5407.1 | 2777.7 | 2716.6 | 4006.4 | 1204.8 | 0.67494 | 5.6
2024-12-09 | 20:34 | Data | 0 | 33.169 | 31.366 | 172.698 | 7.63 | 162.855 | 2175.52 | 25.86 | 47.894 | 6.37 | 1.294 | 4.279 | 8318.64 | 1.782 | 97.8 | 76.8 | 1414 | 23.95 | 5407.1 | 2788.3 | 2713.3 | 4013.1 | 1204.8 | 0.67796 | 5.573
2024-12-09 | 20:34 | Data | 0 | 33.068 | 31.339 | 172.788 | 7.62 | 162.991 | 2174.62 | 25.88 | 47.894 | 6.38 | 1.304 | 4.284 | 8323.16 | 1.627 | 97.8 | 76.7 | 1414 | 23.95 | 5410.1 | 2765.5 | 2703.3 | 3995.5 | 1204.8 | 0.67331 | 5.588
2024-12-09 | 20:34 | Data | 0 | 33.27 | 31.346 | 172.924 | 7.63 | 163.036 | 2174.62 | 25.88 | 48.165 | 6.38 | 1.303 | 4.287 | 8305.07 | 1.836 | 97.8 | 76.7 | 1414 | 24.04 | 5398.3 | 2760.2 | 2731.2 | 4007.6 | 1204.8 | 0.67111 | 5.591
2024-12-09 | 20:34 | Data | 0 | 33.068 | 31.346 | 172.833 | 7.63 | 162.946 | 2178.24 | 25.88 | 48.075 | 6.37 | 1.296 | 4.277 | 8305.07 | 1.614 | 97.8 | 76.7 | 1415 | 24.08 | 5398.3 | 2769.4 | 2708.6 | 3999.6 | 1204.8 | 0.67446 | 5.573
2024-12-09 | 20:35 | Data | 0 | 33.183 | 31.569 | 172.833 | 7.63 | 162.946 | 2178.24 | 25.88 | 47.894 | 6.37 | 1.306 | 4.268 | 8314.11 | 1.627 | 97.8 | 76.6 | 1415 | 23.99 | 5404.2 | 2776.1 | 2707.2 | 4001.1 | 1204.8 | 0.67677 | 5.574
2024-12-09 | 20:35 | Data | 0 | 33.176 | 31.515 | 172.833 | 7.63 | 162.901 | 2178.24 | 25.86 | 47.894 | 6.38 | 1.3 | 4.301 | 8318.64 | 1.843 | 97.8 | 76.8 | 1416 | 23.95 | 5407.1 | 2768 | 2722.5 | 4003.2 | 1204.8 | 0.67518 | 5.6
2024-12-09 | 20:35 | Data | 0 | 33.176 | 31.562 | 172.743 | 7.62 | 162.901 | 2177.33 | 25.89 | 47.894 | 6.38 | 1.296 | 4.288 | 8318.64 | 1.641 | 97.8 | 76.8 | 1415 | 23.9 | 5407.1 | 2749.5 | 2709.2 | 3988 | 1204.8 | 0.67128 | 5.584
2024-12-09 | 20:35 | Data | 0 | 33.196 | 31.569 | 172.833 | 7.62 | 162.946 | 2175.52 | 25.89 | 47.714 | 6.37 | 1.301 | 4.295 | 8336.72 | 1.614 | 97.8 | 76.8 | 1414 | 23.9 | 5418.9 | 2754.1 | 2727.4 | 4000.2 | 1204.8 | 0.67241 | 5.596
2024-12-09 | 20:35 | Data | 0 | 33.358 | 31.569 | 172.833 | 7.63 | 162.946 | 2174.62 | 25.89 | 47.984 | 6.37 | 1.309 | 4.29 | 8332.2 | 2.005 | 97.8 | 76.6 | 1414 | 23.95 | 5415.9 | 2772.7 | 2717.7 | 4008.7 | 1204.8 | 0.67366 | 5.599
2024-12-09 | 20:35 | Data | 0 | 33.574 | 31.596 | 172.788 | 7.63 | 162.991 | 2178.24 | 25.88 | 47.894 | 6.38 | 1.299 | 4.288 | 8318.64 | 1.668 | 97.8 | 76.7 | 1415 | 23.9 | 5407.1 | 2757.8 | 2725.6 | 3997.7 | 1204.8 | 0.6734 | 5.588
2024-12-09 | 20:35 | Data | 0 | 32.96 | 31.515 | 172.879 | 7.63 | 162.901 | 2170.1 | 25.88 | 47.984 | 6.38 | 1.291 | 4.281 | 8314.11 | 1.614 | 97.8 | 76.8 | 1411 | 23.95 | 5404.2 | 2757.3 | 2729.8 | 4003.9 | 1204.8 | 0.67158 | 5.573
2024-12-09 | 20:35 | Data | 0 | 33.453 | 31.245 | 172.788 | 7.62 | 162.946 | 2174.62 | 25.89 | 47.894 | 6.38 | 1.294 | 4.31 | 8291.5 | 1.816 | 97.8 | 76.9 | 1414 | 23.95 | 5389.5 | 2758.8 | 2693.1 | 3981.7 | 1204.8 | 0.67699 | 5.602
2024-12-09 | 20:35 | Data | 0 | 33.156 | 31.218 | 172.698 | 7.63 | 162.765 | 2172.81 | 25.88 | 47.804 | 6.38 | 1.303 | 4.304 | 8291.5 | 1.843 | 97.8 | 76.8 | 1412 | 23.95 | 5389.5 | 2752.7 | 2683.8 | 3966.5 | 1204.8 | 0.67651 | 5.608
2024-12-09 | 20:35 | Data | 0 | 33.385 | 31.569 | 172.743 | 7.63 | 162.991 | 2174.62 | 25.89 | 47.894 | 6.37 | 1.291 | 4.291 | 8305.07 | 1.83 | 97.8 | 76.9 | 1414 | 23.95 | 5398.3 | 2741.5 | 2708.2 | 3978 | 1204.8 | 0.67153 | 5.582
2024-12-09 | 20:35 | Data | 0 | 33.48 | 31.36 | 172.879 | 7.62 | 162.946 | 2174.62 | 25.89 | 47.894 | 6.37 | 1.303 | 4.274 | 8305.07 | 1.728 | 97.8 | 76.6 | 1414 | 23.95 | 5398.3 | 2751.3 | 2719.7 | 3991.1 | 1204.8 | 0.67302 | 5.577
2024-12-09 | 20:35 | Data | 0 | 32.899 | 31.542 | 172.833 | 7.62 | 162.991 | 2227.95 | 25.89 | 47.894 | 6.37 | 1.32 | 4.269 | 8359.34 | 1.701 | 97.9 | 76.4 | 1449 | 23.95 | 5433.6 | 2759.4 | 2700.7 | 3984.6 | 1204.8 | 0.67449 | 5.589
2024-12-09 | 20:35 | Data | 0 | 33.183 | 31.339 | 172.743 | 7.62 | 162.901 | 2227.95 | 25.89 | 47.894 | 6.37 | 1.303 | 4.295 | 8359.34 | 1.843 | 97.9 | 76.7 | 1448 | 23.95 | 5433.6 | 2759.5 | 2734 | 4008.7 | 1204.8 | 0.67181 | 5.599
2024-12-09 | 20:35 | Data | 0 | 33.183 | 31.339 | 172.833 | 7.63 | 162.946 | 2232.47 | 25.89 | 47.894 | 6.37 | 1.289 | 4.296 | 8363.86 | 1.715 | 97.9 | 76.9 | 1451 | 23.95 | 5436.5 | 2768.3 | 2703.9 | 3989.2 | 1204.8 | 0.676 | 5.585
2024-12-09 | 20:35 | Data | 0 | 33.183 | 31.447 | 172.788 | 7.62 | 162.901 | 2233.37 | 25.89 | 47.894 | 6.37 | 1.304 | 4.277 | 8350.29 | 1.627 | 97.9 | 76.6 | 1451 | 23.95 | 5427.7 | 2750.5 | 2730.3 | 3998.7 | 1204.8 | 0.67021 | 5.582
2024-12-09 | 20:35 | Data | 0 | 33.351 | 31.569 | 172.833 | 7.62 | 162.946 | 2174.62 | 25.89 | 47.804 | 6.37 | 1.3 | 4.284 | 8341.25 | 1.836 | 97.8 | 76.7 | 1414 | 23.9 | 5421.8 | 2753.8 | 2717.2 | 3995.6 | 1204.9 | 0.67122 | 5.584
2024-12-09 | 20:35 | Data | 0 | 32.798 | 31.339 | 172.924 | 7.62 | 162.946 | 2173.72 | 25.9 | 47.804 | 6.37 | 1.301 | 4.303 | 8359.34 | 1.573 | 97.8 | 76.8 | 1413 | 23.95 | 5433.6 | 2753.6 | 2712.2 | 3993.8 | 1204.9 | 0.672 | 5.604
2024-12-09 | 20:36 | Data | 0 | 33.567 | 31.346 | 172.924 | 7.62 | 163.036 | 2171.01 | 25.89 | 47.984 | 6.37 | 1.294 | 4.286 | 8359.34 | 1.944 | 97.8 | 76.8 | 1411 | 24.04 | 5433.6 | 2722.4 | 2705.7 | 3964.3 | 1204.9 | 0.67213 | 5.581
2024-12-09 | 20:36 | Data | 0 | 33.095 | 31.346 | 172.879 | 7.62 | 162.991 | 2172.81 | 25.89 | 47.984 | 6.38 | 1.295 | 4.304 | 8368.38 | 1.627 | 97.8 | 76.9 | 1412 | 23.99 | 5439.4 | 2753.8 | 2722.3 | 3993.4 | 1204.9 | 0.67326 | 5.6
2024-12-09 | 20:36 | Data | 0 | 33.5 | 31.569 | 172.969 | 7.62 | 163.081 | 2175.52 | 25.89 | 47.894 | 6.37 | 1.3 | 4.306 | 8363.86 | 1.857 | 97.8 | 76.8 | 1414 | 23.95 | 5436.5 | 2743.4 | 2708.1 | 3977.4 | 1204.9 | 0.67339 | 5.604
2024-12-09 | 20:36 | Data | 0 | 33.183 | 31.569 | 172.969 | 7.62 | 162.946 | 2170.1 | 25.89 | 47.894 | 6.38 | 1.304 | 4.282 | 8345.77 | 1.789 | 97.8 | 76.7 | 1411 | 23.95 | 5424.8 | 2734.6 | 2682.8 | 3960.2 | 1204.9 | 0.67176 | 5.587
2024-12-09 | 20:36 | Data | 0 | 32.987 | 31.515 | 172.833 | 7.63 | 162.991 | 2175.52 | 25.9 | 47.894 | 6.37 | 1.305 | 4.265 | 8336.72 | 1.634 | 97.8 | 76.6 | 1414 | 23.95 | 5418.9 | 2748.6 | 2720.6 | 3995.6 | 1204.9 | 0.67157 | 5.57
2024-12-09 | 20:36 | Data | 0 | 33.135 | 31.569 | 172.879 | 7.62 | 163.036 | 2175.52 | 25.89 | 47.894 | 6.37 | 1.301 | 4.285 | 8336.72 | 1.782 | 97.8 | 76.7 | 1414 | 23.95 | 5418.9 | 2739.5 | 2725.9 | 3991.9 | 1204.9 | 0.67025 | 5.587
2024-12-09 | 20:36 | Data | 0 | 33.176 | 31.495 | 176.678 | 7.63 | 166.426 | 2172.81 | 25.89 | 47.894 | 6.37 | 1.308 | 4.289 | 8354.81 | 2.012 | 97.8 | 76.6 | 1412 | 23.95 | 5430.6 | 2768.9 | 2727 | 4024.1 | 1204.9 | 0.66825 | 5.597
2024-12-09 | 20:36 | Data | 0 | 32.339 | 30.536 | 185.227 | 7.63 | 174.199 | 2178.24 | 25.89 | 47.894 | 6.37 | 1.319 | 4.402 | 8368.38 | 1.863 | 97.8 | 76.9 | 1416 | 23.95 | 5439.4 | 2864.4 | 2812.9 | 4132.3 | 1204.9 | 0.67554 | 5.72
2024-12-09 | 20:36 | Data | 0 | 32.048 | 30.084 | 192.781 | 7.63 | 181.159 | 2175.52 | 25.89 | 48.075 | 6.38 | 1.34 | 4.604 | 8363.86 | 2.221 | 97.8 | 77.4 | 1415 | 24.08 | 5436.5 | 2949.5 | 2897.3 | 4230.3 | 1204.9 | 0.67866 | 5.943
2024-12-09 | 20:36 | Data | 0 | 32.082 | 29.807 | 198.797 | 7.62 | 186.627 | 2175.52 | 25.89 | 48.165 | 6.37 | 1.376 | 4.753 | 8359.34 | 2.147 | 97.8 | 77.5 | 1414 | 24.08 | 5433.6 | 3024.2 | 2956.8 | 4338.6 | 1204.9 | 0.68106 | 6.13
2024-12-09 | 20:36 | Data | 0 | 31.569 | 29.483 | 203.456 | 7.62 | 190.83 | 2175.52 | 25.89 | 47.984 | 6.37 | 1.384 | 4.883 | 8341.25 | 2.12 | 97.8 | 77.9 | 1414 | 23.95 | 5421.8 | 3057.3 | 3002.1 | 4396.1 | 1204.9 | 0.67903 | 6.267
2024-12-09 | 20:36 | Data | 0 | 31.576 | 29.098 | 207.255 | 7.63 | 194.491 | 2177.33 | 25.88 | 47.262 | 6.37 | 1.395 | 4.953 | 8372.9 | 2.1 | 97.8 | 78 | 1416 | 23.68 | 5442.4 | 3103.9 | 3055 | 4461.9 | 1204.9 | 0.68012 | 6.348
2024-12-09 | 20:36 | Data | 0 | 31.346 | 29.152 | 210.557 | 7.63 | 197.564 | 2176.43 | 25.89 | 46.45 | 6.36 | 1.402 | 5.039 | 8386.47 | 2.302 | 97.9 | 78.2 | 1414 | 23.22 | 5451.2 | 3133.9 | 3060.2 | 4486.8 | 1204.9 | 0.68216 | 6.44
2024-12-09 | 20:36 | Data | 0 | 31.204 | 28.868 | 213.045 | 7.62 | 199.869 | 2175.52 | 25.88 | 45.727 | 6.35 | 1.412 | 5.118 | 8431.69 | 2.248 | 97.9 | 78.4 | 1414 | 22.86 | 5480.6 | 3161.2 | 3108.8 | 4543.7 | 1204.9 | 0.67864 | 6.529
2024-12-09 | 20:36 | Data | 0 | 31.319 | 29.125 | 215.081 | 7.63 | 201.496 | 2174.62 | 25.88 | 45.276 | 6.34 | 1.417 | 5.156 | 8440.74 | 2.464 | 97.9 | 78.4 | 1414 | 22.64 | 5486.5 | 3188.7 | 3123.6 | 4567.3 | 1204.9 | 0.6819 | 6.574
2024-12-09 | 20:36 | Data | 0 | 31.508 | 28.646 | 216.528 | 7.62 | 202.807 | 2177.33 | 25.88 | 44.554 | 6.34 | 1.424 | 5.208 | 8481.44 | 2.674 | 98 | 78.5 | 1416 | 22.28 | 5512.9 | 3213.4 | 3154.6 | 4605.4 | 1204.9 | 0.68237 | 6.632
2024-12-09 | 20:36 | Data | 0 | 31.312 | 28.922 | 217.659 | 7.62 | 203.936 | 2177.33 | 25.88 | 44.102 | 6.33 | 1.431 | 5.231 | 8535.7 | 2.647 | 98 | 78.5 | 1415 | 22.05 | 5548.2 | 3212.6 | 3141 | 4604.6 | 1204.9 | 0.68434 | 6.66
2024-12-09 | 20:36 | Data | 0 | 31.231 | 28.862 | 218.247 | 7.63 | 204.569 | 2177.33 | 25.89 | 43.47 | 6.33 | 1.433 | 5.261 | 8571.88 | 2.687 | 98 | 78.6 | 1416 | 21.78 | 5571.7 | 3239.2 | 3135.8 | 4609.7 | 1204.9 | 0.68695 | 6.695
2024-12-09 | 20:37 | Data | 0 | 31.333 | 28.977 | 218.292 | 7.62 | 204.388 | 2178.24 | 25.89 | 43.2 | 6.32 | 1.434 | 5.241 | 8599.01 | 2.478 | 98 | 78.5 | 1416 | 21.6 | 5589.4 | 3237 | 3153.9 | 4621.1 | 1204.9 | 0.68426 | 6.676
2024-12-09 | 20:37 | Data | 0 | 31.11 | 28.619 | 218.382 | 7.62 | 204.705 | 2180.95 | 25.88 | 42.929 | 6.32 | 1.443 | 5.234 | 8608.06 | 2.451 | 98 | 78.4 | 1418 | 21.46 | 5595.2 | 3236.8 | 3164.7 | 4632.5 | 1204.9 | 0.68201 | 6.676
2024-12-09 | 20:37 | Data | 0 | 31.326 | 28.625 | 218.473 | 7.62 | 204.75 | 2180.95 | 25.89 | 42.658 | 6.32 | 1.441 | 5.267 | 8648.76 | 2.653 | 98 | 78.5 | 1418 | 21.33 | 5621.7 | 3211.9 | 3180.6 | 4628.3 | 1204.9 | 0.68037 | 6.708
2024-12-09 | 20:37 | Data | 0 | 31.083 | 28.571 | 218.473 | 7.63 | 204.705 | 2180.95 | 25.88 | 42.568 | 6.31 | 1.446 | 5.286 | 8684.94 | 2.538 | 98 | 78.5 | 1418 | 21.33 | 5645.2 | 3213.7 | 3169.2 | 4618 | 1204.9 | 0.67972 | 6.732
2024-12-09 | 20:37 | Data | 0 | 31.252 | 28.578 | 218.609 | 7.62 | 204.84 | 2180.04 | 25.88 | 42.658 | 6.32 | 1.441 | 5.269 | 8721.11 | 2.565 | 98 | 78.5 | 1418 | 21.28 | 5668.7 | 3215.9 | 3174.1 | 4621.1 | 1204.9 | 0.68145 | 6.709
2024-12-09 | 20:37 | Data | 0 | 31.252 | 28.571 | 218.518 | 7.62 | 204.885 | 2232.47 | 25.86 | 42.387 | 6.31 | 1.434 | 5.276 | 8721.11 | 2.437 | 98.1 | 78.6 | 1452 | 21.19 | 5668.7 | 3223.6 | 3154 | 4603.7 | 1204.9 | 0.68138 | 6.71
2024-12-09 | 20:37 | Data | 0 | 31.11 | 28.693 | 218.518 | 7.62 | 204.885 | 2233.37 | 25.88 | 42.658 | 6.31 | 1.433 | 5.243 | 8739.2 | 2.538 | 98.1 | 78.5 | 1452 | 21.33 | 5680.5 | 3228.7 | 3156.4 | 4617.4 | 1204.9 | 0.68316 | 6.677
2024-12-09 | 20:37 | Data | 0 | 31.117 | 28.639 | 218.609 | 7.63 | 204.931 | 2236.08 | 25.88 | 42.297 | 6.31 | 1.437 | 5.253 | 8770.86 | 2.734 | 98.1 | 78.5 | 1453 | 21.19 | 5701.1 | 3234.4 | 3160 | 4623.7 | 1204.9 | 0.68297 | 6.69
2024-12-09 | 20:37 | Data | 0 | 31.11 | 28.585 | 219.016 | 7.62 | 205.111 | 2238.79 | 25.88 | 42.658 | 6.31 | 1.44 | 5.233 | 8797.99 | 2.505 | 98.1 | 78.4 | 1455 | 21.33 | 5718.7 | 3236.7 | 3166.3 | 4631.3 | 1204.9 | 0.68265 | 6.673
2024-12-09 | 20:37 | Data | 0 | 31.11 | 28.679 | 219.016 | 7.63 | 205.247 | 2180.95 | 25.86 | 42.568 | 6.31 | 1.442 | 5.275 | 8811.56 | 2.592 | 98 | 78.5 | 1417 | 21.28 | 5727.5 | 3223.5 | 3152.5 | 4614.2 | 1204.9 | 0.68264 | 6.717
2024-12-09 | 20:37 | Data | 0 | 31.11 | 28.646 | 219.061 | 7.62 | 205.247 | 2182.75 | 25.86 | 42.658 | 6.31 | 1.441 | 5.273 | 8829.65 | 2.39 | 98 | 78.5 | 1419 | 21.37 | 5739.3 | 3248.2 | 3144.5 | 4625.7 | 1204.9 | 0.68528 | 6.714
2024-12-09 | 20:37 | Data | 0 | 31.38 | 29.031 | 219.106 | 7.62 | 205.428 | 2189.99 | 25.88 | 42.658 | 6.31 | 1.454 | 5.252 | 8829.65 | 2.714 | 98.1 | 78.3 | 1423 | 21.33 | 5739.3 | 3233.9 | 3177 | 4639.5 | 1204.9 | 0.68029 | 6.708
2024-12-09 | 20:37 | Data | 0 | 31.164 | 28.747 | 219.106 | 7.62 | 205.292 | 2191.79 | 25.86 | 42.658 | 6.31 | 1.444 | 5.278 | 8802.51 | 2.538 | 98.1 | 78.5 | 1425 | 21.33 | 5721.6 | 3221.8 | 3181.7 | 4631 | 1204.9 | 0.67974 | 6.722
2024-12-09 | 20:37 | Data | 0 | 31.434 | 28.754 | 219.197 | 7.62 | 205.247 | 2060.74 | 25.89 | 42.658 | 6.31 | 1.444 | 5.273 | 8811.56 | 2.728 | 97.9 | 78.5 | 1339 | 21.33 | 5727.5 | 3224.5 | 3170.3 | 4624.4 | 1204.9 | 0.68122 | 6.717
2024-12-09 | 20:37 | Data | 0 | 31.103 | 28.571 | 218.925 | 7.62 | 205.157 | 2161.97 | 25.86 | 42.658 | 6.31 | 1.444 | 5.287 | 8797.99 | 2.538 | 98 | 78.5 | 1405 | 21.28 | 5718.7 | 3235 | 3171.2 | 4632.7 | 1204.9 | 0.6816 | 6.731
2024-12-09 | 20:37 | Data | 0 | 31.13 | 28.808 | 219.061 | 7.62 | 205.337 | 2167.39 | 25.88 | 42.658 | 6.31 | 1.448 | 5.248 | 8811.56 | 2.424 | 98 | 78.4 | 1408 | 21.28 | 5727.5 | 3236.8 | 3143.4 | 4615.8 | 1205 | 0.68504 | 6.696
2024-12-09 | 20:37 | Data | 0 | 31.326 | 28.578 | 219.151 | 7.62 | 205.428 | 2164.68 | 25.86 | 42.568 | 6.31 | 1.448 | 5.259 | 8856.78 | 2.552 | 98 | 78.4 | 1408 | 21.33 | 5756.9 | 3246 | 3173.7 | 4640 | 1205 | 0.68391 | 6.706
2024-12-09 | 20:37 | Data | 0 | 31.13 | 29.213 | 219.287 | 7.62 | 205.563 | 2178.24 | 25.89 | 42.658 | 6.31 | 1.448 | 5.249 | 8856.78 | 2.228 | 98 | 78.4 | 1416 | 21.33 | 5756.9 | 3235.7 | 3181.3 | 4636.5 | 1205 | 0.68262 | 6.697
2024-12-09 | 20:38 | Data | 0 | 31.117 | 28.781 | 219.151 | 7.62 | 205.337 | 2182.75 | 25.88 | 42.658 | 6.31 | 1.446 | 5.278 | 8856.78 | 2.424 | 98 | 78.5 | 1419 | 21.33 | 5756.9 | 3230.3 | 3171.2 | 4630.3 | 1205 | 0.68191 | 6.724
2024-12-09 | 20:38 | Data | 0 | 31.549 | 29.031 | 219.151 | 7.62 | 205.428 | 2183.66 | 25.88 | 42.568 | 6.31 | 1.435 | 5.267 | 8883.91 | 2.545 | 98 | 78.6 | 1419 | 21.33 | 5774.5 | 3243.6 | 3153.7 | 4618.6 | 1205 | 0.68465 | 6.701
2024-12-09 | 20:38 | Data | 0 | 31.137 | 28.578 | 219.061 | 7.63 | 205.292 | 2183.66 | 25.88 | 42.658 | 6.31 | 1.443 | 5.296 | 8892.96 | 2.538 | 98 | 78.6 | 1419 | 21.33 | 5780.4 | 3230.9 | 3169.5 | 4622.3 | 1205 | 0.68093 | 6.739
2024-12-09 | 20:38 | Data | 0 | 31.333 | 28.571 | 219.016 | 7.62 | 205.292 | 2182.75 | 25.88 | 42.658 | 6.31 | 1.439 | 5.282 | 8879.39 | 2.647 | 98 | 78.6 | 1419 | 21.33 | 5771.6 | 3241.6 | 3166.5 | 4634.9 | 1205 | 0.68279 | 6.721
2024-12-09 | 20:38 | Data | 0 | 31.697 | 28.862 | 219.242 | 7.62 | 205.563 | 2186.37 | 25.88 | 42.658 | 6.31 | 1.444 | 5.289 | 8865.83 | 2.809 | 98 | 78.5 | 1421 | 21.37 | 5762.8 | 3235.8 | 3178.9 | 4637.3 | 1205 | 0.68207 | 6.733
2024-12-09 | 20:38 | Data | 0 | 31.225 | 28.693 | 219.197 | 7.62 | 205.337 | 2180.04 | 25.86 | 42.658 | 6.31 | 1.439 | 5.307 | 8879.39 | 2.545 | 98 | 78.7 | 1418 | 21.33 | 5771.6 | 3238.4 | 3161.4 | 4630.1 | 1205 | 0.68236 | 6.746
2024-12-09 | 20:38 | Data | 0 | 31.11 | 28.571 | 219.061 | 7.62 | 205.292 | 2180.95 | 25.88 | 42.658 | 6.31 | 1.443 | 5.29 | 8883.91 | 2.538 | 98 | 78.6 | 1417 | 21.28 | 5774.5 | 3209.5 | 3163.8 | 4612 | 1205 | 0.68062 | 6.734
2024-12-09 | 20:38 | Data | 0 | 31.427 | 29.024 | 219.287 | 7.63 | 205.563 | 2183.66 | 25.89 | 42.748 | 6.31 | 1.45 | 5.298 | 8897.48 | 2.525 | 98 | 78.5 | 1419 | 21.37 | 5783.4 | 3228.1 | 3147.6 | 4611.7 | 1205 | 0.68388 | 6.747
2024-12-09 | 20:38 | Data | 0 | 31.137 | 28.578 | 219.061 | 7.62 | 205.428 | 2183.66 | 25.89 | 42.568 | 6.31 | 1.433 | 5.317 | 8892.96 | 2.538 | 98 | 78.8 | 1419 | 21.28 | 5780.4 | 3231.9 | 3139 | 4608 | 1205 | 0.68588 | 6.751
2024-12-09 | 20:38 | Data | 0 | 31.515 | 28.862 | 219.151 | 7.63 | 205.428 | 2182.75 | 25.88 | 42.658 | 6.31 | 1.435 | 5.289 | 8911.05 | 2.701 | 98 | 78.7 | 1419 | 21.33 | 5792.2 | 3231.7 | 3139.7 | 4596.8 | 1205 | 0.6839 | 6.725
2024-12-09 | 20:38 | Data | 0 | 31.447 | 28.605 | 219.242 | 7.62 | 205.428 | 2182.75 | 25.89 | 42.658 | 6.31 | 1.437 | 5.275 | 8897.48 | 2.532 | 98 | 78.6 | 1419 | 21.33 | 5783.4 | 3235.3 | 3159.5 | 4625 | 1205 | 0.6839 | 6.71
2024-12-09 | 20:38 | Data | 0 | 31.144 | 28.632 | 219.106 | 7.62 | 205.563 | 2183.66 | 25.86 | 42.658 | 6.31 | 1.447 | 5.316 | 8911.05 | 2.592 | 98.1 | 78.6 | 1419 | 21.33 | 5792.2 | 3236.9 | 3128.6 | 4604.4 | 1205 | 0.68516 | 6.764
2024-12-09 | 20:38 | Data | 0 | 31.225 | 28.801 | 219.151 | 7.62 | 205.473 | 2183.66 | 25.89 | 42.658 | 6.31 | 1.443 | 5.312 | 8924.61 | 2.491 | 98 | 78.6 | 1419 | 21.33 | 5801 | 3237.8 | 3146.7 | 4622.2 | 1205 | 0.68413 | 6.755
2024-12-09 | 20:38 | Data | 0 | 31.231 | 28.916 | 219.106 | 7.62 | 205.428 | 2182.75 | 25.89 | 42.658 | 6.31 | 1.441 | 5.289 | 8906.53 | 2.417 | 98 | 78.6 | 1419 | 21.28 | 5789.2 | 3235.7 | 3141.5 | 4614.9 | 1205 | 0.68538 | 6.73
2024-12-09 | 20:38 | Data | 0 | 31.765 | 28.646 | 219.242 | 7.63 | 205.518 | 2182.75 | 25.88 | 42.658 | 6.31 | 1.44 | 5.265 | 8911.05 | 2.626 | 98 | 78.5 | 1419 | 21.28 | 5792.2 | 3238 | 3131.6 | 4607.7 | 1205 | 0.68765 | 6.705
2024-12-09 | 20:38 | Data | 0 | 31.137 | 28.571 | 219.151 | 7.62 | 205.337 | 2181.85 | 25.88 | 42.658 | 6.31 | 1.445 | 5.269 | 8911.05 | 2.545 | 98 | 78.5 | 1418 | 21.33 | 5792.2 | 3237.1 | 3152 | 4619.8 | 1205 | 0.68488 | 6.714
2024-12-09 | 20:38 | Data | 0 | 31.339 | 28.686 | 219.061 | 7.62 | 205.428 | 2181.85 | 25.88 | 42.658 | 6.31 | 1.443 | 5.265 | 8892.96 | 2.532 | 98 | 78.5 | 1419 | 21.28 | 5780.4 | 3233.7 | 3162.5 | 4627.2 | 1205 | 0.68301 | 6.708
2024-12-09 | 20:38 | Data | 0 | 31.225 | 28.578 | 219.061 | 7.62 | 205.337 | 2180.95 | 25.88 | 42.748 | 6.31 | 1.445 | 5.279 | 8906.53 | 2.545 | 98 | 78.5 | 1417 | 21.33 | 5789.2 | 3229.1 | 3146.7 | 4613.7 | 1205 | 0.68473 | 6.724
2024-12-09 | 20:39 | Data | 0 | 31.501 | 29.105 | 219.106 | 7.62 | 205.518 | 2180.95 | 25.88 | 42.658 | 6.3 | 1.452 | 5.296 | 8897.48 | 2.552 | 98 | 78.5 | 1418 | 21.33 | 5783.4 | 3226 | 3154.4 | 4616.8 | 1205 | 0.68313 | 6.747
2024-12-09 | 20:39 | Data | 0 | 31.11 | 28.774 | 219.106 | 7.62 | 205.337 | 2183.66 | 25.88 | 42.658 | 6.31 | 1.451 | 5.255 | 8870.35 | 2.478 | 98 | 78.4 | 1419 | 21.37 | 5765.7 | 3237.5 | 3174.5 | 4636.6 | 1205 | 0.68324 | 6.706
2024-12-09 | 20:39 | Data | 0 | 31.225 | 28.97 | 219.197 | 7.62 | 205.337 | 2182.75 | 25.89 | 42.658 | 6.31 | 1.452 | 5.279 | 8870.35 | 2.674 | 98 | 78.4 | 1419 | 21.28 | 5765.7 | 3227.5 | 3148.1 | 4612.2 | 1205 | 0.68338 | 6.731
2024-12-09 | 20:39 | Data | 0 | 31.117 | 28.362 | 219.016 | 7.62 | 205.337 | 2182.75 | 25.89 | 42.748 | 6.31 | 1.454 | 5.26 | 8874.87 | 2.518 | 98 | 78.3 | 1419 | 21.33 | 5768.7 | 3239.4 | 3165.1 | 4631.8 | 1205 | 0.68392 | 6.716
2024-12-09 | 20:39 | Data | 0 | 31.231 | 28.578 | 219.242 | 7.62 | 205.473 | 2187.27 | 25.89 | 42.658 | 6.32 | 1.441 | 5.275 | 8870.35 | 2.761 | 98 | 78.6 | 1421 | 21.33 | 5765.7 | 3214.3 | 3172.9 | 4620.5 | 1205 | 0.67964 | 6.715
2024-12-09 | 20:39 | Data | 0 | 31.333 | 28.808 | 219.061 | 7.62 | 205.518 | 2192.7 | 25.88 | 42.568 | 6.31 | 1.447 | 5.295 | 8870.35 | 2.532 | 98.1 | 78.5 | 1425 | 21.28 | 5765.7 | 3224.5 | 3199.8 | 4645.5 | 1205 | 0.67849 | 6.742
2024-12-09 | 20:39 | Data | 0 | 31.495 | 29.112 | 219.287 | 7.62 | 205.518 | 2183.66 | 25.88 | 42.658 | 6.31 | 1.451 | 5.278 | 8879.39 | 2.532 | 98 | 78.4 | 1419 | 21.33 | 5771.6 | 3247 | 3183.8 | 4648.8 | 1205 | 0.68236 | 6.728
2024-12-09 | 20:39 | Data | 0 | 31.123 | 28.693 | 219.016 | 7.62 | 205.473 | 2183.66 | 25.89 | 42.658 | 6.32 | 1.443 | 5.246 | 8874.87 | 2.538 | 98.1 | 78.4 | 1419 | 21.28 | 5768.7 | 3234 | 3208.4 | 4660.5 | 1205 | 0.67818 | 6.689
2024-12-09 | 20:39 | Data | 0 | 31.076 | 28.693 | 219.061 | 7.62 | 205.518 | 2186.37 | 25.88 | 42.658 | 6.31 | 1.443 | 5.257 | 8865.83 | 2.329 | 98 | 78.5 | 1421 | 21.33 | 5762.8 | 3234.5 | 3218.2 | 4663.6 | 1205 | 0.67797 | 6.7
2024-12-09 | 20:39 | Data | 0 | 31.279 | 29.031 | 219.016 | 7.62 | 205.337 | 2191.79 | 25.88 | 42.658 | 6.31 | 1.445 | 5.281 | 8892.96 | 2.511 | 98.1 | 78.5 | 1425 | 21.33 | 5780.4 | 3239.2 | 3184 | 4637.9 | 1205 | 0.68193 | 6.727
2024-12-09 | 20:39 | Data | 0 | 31.15 | 29.017 | 219.197 | 7.62 | 205.518 | 2186.37 | 25.88 | 42.568 | 6.31 | 1.444 | 5.27 | 8897.48 | 2.505 | 98 | 78.5 | 1421 | 21.33 | 5783.4 | 3233.8 | 3162.9 | 4631.7 | 1205 | 0.68576 | 6.714
2024-12-09 | 20:39 | Data | 0 | 30.948 | 28.551 | 219.106 | 7.62 | 205.473 | 2186.37 | 25.88 | 42.658 | 6.31 | 1.443 | 5.258 | 8911.05 | 2.43 | 98 | 78.5 | 1421 | 21.33 | 5792.2 | 3235.4 | 3182.1 | 4639.7 | 1205 | 0.68255 | 6.701
2024-12-09 | 20:39 | Data | 0 | 31.495 | 28.868 | 219.106 | 7.62 | 205.428 | 2182.75 | 25.89 | 42.658 | 6.31 | 1.442 | 5.247 | 8883.91 | 2.606 | 98 | 78.4 | 1419 | 21.33 | 5774.5 | 3237.5 | 3151 | 4623.3 | 1205.1 | 0.6847 | 6.689
2024-12-09 | 20:39 | Data | 0 | 31.306 | 28.686 | 219.061 | 7.62 | 205.428 | 2181.85 | 25.88 | 42.658 | 6.31 | 1.44 | 5.255 | 8879.39 | 2.532 | 98 | 78.5 | 1419 | 21.33 | 5771.6 | 3238.3 | 3163.6 | 4629.3 | 1205.1 | 0.68367 | 6.694
2024-12-09 | 20:39 | Data | 0 | 31.333 | 28.598 | 219.242 | 7.62 | 205.518 | 2182.75 | 25.88 | 42.658 | 6.32 | 1.443 | 5.248 | 8879.39 | 2.647 | 98 | 78.4 | 1419 | 21.33 | 5771.6 | 3235.7 | 3161.6 | 4626.2 | 1205.1 | 0.68362 | 6.69
2024-12-09 | 20:39 | Data | 0 | 31.225 | 29.118 | 219.197 | 7.63 | 205.473 | 2183.66 | 25.89 | 42.568 | 6.32 | 1.443 | 5.285 | 8892.96 | 2.478 | 98 | 78.5 | 1419 | 21.33 | 5780.4 | 3251.6 | 3195.7 | 4658.9 | 1205.1 | 0.68188 | 6.729
2024-12-09 | 20:39 | Data | 0 | 31.353 | 28.808 | 219.287 | 7.62 | 205.518 | 2182.75 | 25.89 | 42.748 | 6.32 | 1.449 | 5.298 | 8883.91 | 2.532 | 98 | 78.5 | 1419 | 21.33 | 5774.5 | 3245 | 3186.5 | 4651.8 | 1205.1 | 0.6809 | 6.746
2024-12-09 | 20:40 | Data | 0 | 31.211 | 29.064 | 219.287 | 7.62 | 205.337 | 2183.66 | 25.88 | 42.568 | 6.31 | 1.44 | 5.273 | 8906.53 | 2.728 | 98 | 78.6 | 1419 | 21.33 | 5789.2 | 3233.2 | 3209.9 | 4658.7 | 1205.1 | 0.67791 | 6.713
2024-12-09 | 20:40 | Data | 0 | 31.42 | 28.578 | 219.151 | 7.62 | 205.473 | 2179.14 | 25.88 | 42.477 | 6.31 | 1.447 | 5.294 | 8920.09 | 2.586 | 98.1 | 78.5 | 1416 | 21.19 | 5798.1 | 3243.4 | 3216.3 | 4668.9 | 1205.1 | 0.67847 | 6.741
2024-12-09 | 20:40 | Data | 0 | 31.285 | 28.679 | 219.197 | 7.62 | 205.473 | 2183.66 | 25.88 | 42.658 | 6.31 | 1.451 | 5.288 | 8911.05 | 2.484 | 98 | 78.5 | 1420 | 21.33 | 5792.2 | 3250.1 | 3215.2 | 4671.2 | 1205.1 | 0.67978 | 6.737
2024-12-09 | 20:40 | Data | 0 | 31.252 | 28.578 | 219.197 | 7.62 | 205.563 | 2076.1 | 25.88 | 42.658 | 6.31 | 1.452 | 5.301 | 8929.14 | 2.478 | 97.9 | 78.5 | 1349 | 21.33 | 5803.9 | 3241.1 | 3183.8 | 4648.4 | 1205.1 | 0.68137 | 6.754
2024-12-09 | 20:40 | Data | 0 | 31.312 | 29.004 | 219.061 | 7.62 | 205.337 | 2182.75 | 25.89 | 42.568 | 6.32 | 1.437 | 5.313 | 8924.61 | 2.532 | 98 | 78.7 | 1419 | 21.33 | 5801 | 3226.8 | 3186.2 | 4641.4 | 1205.1 | 0.67893 | 6.749
2024-12-09 | 20:40 | Data | 0 | 31.522 | 28.835 | 219.242 | 7.62 | 205.337 | 2183.66 | 25.89 | 42.658 | 6.31 | 1.448 | 5.285 | 8920.09 | 2.647 | 98 | 78.5 | 1419 | 21.33 | 5798.1 | 3236.1 | 3170.2 | 4629.3 | 1205.1 | 0.68366 | 6.733
2024-12-09 | 20:40 | Data | 0 | 31.508 | 28.977 | 219.151 | 7.63 | 205.518 | 2177.33 | 25.89 | 42.658 | 6.31 | 1.444 | 5.283 | 8933.66 | 2.586 | 98 | 78.5 | 1415 | 21.28 | 5806.9 | 3226.4 | 3190.5 | 4642.5 | 1205.1 | 0.6816 | 6.727
2024-12-09 | 20:40 | Data | 0 | 31.333 | 28.484 | 219.106 | 7.62 | 205.428 | 2182.75 | 25.88 | 42.297 | 6.32 | 1.442 | 5.269 | 8933.66 | 2.586 | 98.1 | 78.5 | 1419 | 21.15 | 5806.9 | 3222.2 | 3174.3 | 4629.7 | 1205.1 | 0.68047 | 6.709
2024-12-09 | 20:40 | Data | 0 | 31.772 | 28.612 | 219.197 | 7.62 | 205.518 | 2182.75 | 25.88 | 42.206 | 6.32 | 1.448 | 5.247 | 8924.61 | 2.606 | 98.1 | 78.4 | 1419 | 21.06 | 5801 | 3231.8 | 3168.4 | 4629.2 | 1205.1 | 0.68241 | 6.695
2024-12-09 | 20:40 | Data | 0 | 31.555 | 28.922 | 219.151 | 7.62 | 205.337 | 2182.75 | 25.88 | 42.748 | 6.32 | 1.441 | 5.266 | 8933.66 | 2.336 | 98 | 78.5 | 1419 | 21.33 | 5806.9 | 3238.3 | 3174.4 | 4625.6 | 1205.1 | 0.6797 | 6.708
2024-12-09 | 20:40 | Data | 0 | 31.036 | 28.571 | 219.106 | 7.62 | 205.428 | 2183.66 | 25.88 | 42.748 | 6.31 | 1.448 | 5.277 | 8920.09 | 2.383 | 98 | 78.5 | 1419 | 21.33 | 5798.1 | 3240.8 | 3212 | 4664.3 | 1205.1 | 0.67874 | 6.725
2024-12-09 | 20:40 | Data | 0 | 31.285 | 29.024 | 219.151 | 7.62 | 205.473 | 2182.75 | 25.89 | 42.748 | 6.31 | 1.441 | 5.284 | 8924.61 | 2.403 | 98 | 78.6 | 1419 | 21.33 | 5801 | 3260.4 | 3184.2 | 4658.9 | 1205.1 | 0.68361 | 6.725
2024-12-09 | 20:40 | Data | 0 | 31.11 | 28.571 | 219.016 | 7.62 | 205.337 | 2182.75 | 25.89 | 42.568 | 6.32 | 1.449 | 5.276 | 8924.61 | 2.424 | 98 | 78.4 | 1419 | 21.28 | 5801 | 3236.2 | 3203.8 | 4660.6 | 1205.1 | 0.67818 | 6.726
2024-12-09 | 20:40 | Data | 0 | 31.002 | 28.686 | 219.197 | 7.62 | 205.428 | 2182.75 | 25.89 | 42.116 | 6.32 | 1.452 | 5.244 | 8879.39 | 2.619 | 98.1 | 78.3 | 1418 | 21.06 | 5771.6 | 3238.8 | 3201.6 | 4657.8 | 1205.1 | 0.68055 | 6.695
2024-12-09 | 20:40 | Data | 0 | 31.366 | 29.125 | 219.378 | 7.63 | 205.699 | 2183.66 | 25.89 | 42.658 | 6.31 | 1.446 | 5.275 | 8888.44 | 2.363 | 98 | 78.5 | 1419 | 21.33 | 5777.5 | 3244.7 | 3182.6 | 4650 | 1205.1 | 0.68048 | 6.722
2024-12-09 | 20:40 | Data | 0 | 31.231 | 28.578 | 219.332 | 7.62 | 205.699 | 2184.56 | 25.86 | 42.658 | 6.32 | 1.447 | 5.298 | 8874.87 | 2.545 | 98 | 78.6 | 1419 | 21.33 | 5768.7 | 3246.8 | 3201.8 | 4663.4 | 1205.1 | 0.68101 | 6.744
2024-12-09 | 20:40 | Data | 0 | 31.285 | 28.781 | 219.332 | 7.62 | 205.609 | 2183.66 | 25.89 | 42.658 | 6.31 | 1.453 | 5.281 | 8883.91 | 2.619 | 98 | 78.4 | 1419 | 21.33 | 5774.5 | 3232.6 | 3190.1 | 4646.8 | 1205.1 | 0.68021 | 6.735
2024-12-09 | 20:40 | Data | 0 | 31.137 | 28.747 | 219.332 | 7.62 | 205.518 | 2179.14 | 25.89 | 42.568 | 6.32 | 1.449 | 5.249 | 8870.35 | 2.538 | 98 | 78.4 | 1416 | 21.28 | 5765.7 | 3237.9 | 3184.2 | 4643.7 | 1205.1 | 0.68175 | 6.697
2024-12-09 | 20:41 | Data | 0 | 31.225 | 28.747 | 219.468 | 7.63 | 205.654 | 2176.43 | 25.89 | 42.658 | 6.31 | 1.435 | 5.292 | 8870.35 | 2.714 | 98 | 78.7 | 1415 | 21.33 | 5765.7 | 3250.8 | 3174.2 | 4645 | 1205.1 | 0.68353 | 6.726
2024-12-09 | 20:41 | Data | 0 | 31.265 | 28.821 | 219.242 | 7.62 | 205.654 | 2180.04 | 25.88 | 42.658 | 6.32 | 1.43 | 5.276 | 8838.69 | 2.586 | 98 | 78.7 | 1417 | 21.33 | 5745.1 | 3242.9 | 3180.2 | 4644.4 | 1205.1 | 0.68239 | 6.707
2024-12-09 | 20:41 | Data | 0 | 31.285 | 28.835 | 219.604 | 7.62 | 205.789 | 2180.04 | 25.89 | 42.568 | 6.31 | 1.449 | 5.279 | 8847.74 | 2.836 | 98 | 78.5 | 1418 | 21.28 | 5751 | 3234 | 3188.6 | 4642.1 | 1205.1 | 0.6806 | 6.727
2024-12-09 | 20:41 | Data | 0 | 31.083 | 28.963 | 219.378 | 7.62 | 205.699 | 2180.04 | 25.89 | 42.658 | 6.31 | 1.455 | 5.289 | 8924.61 | 2.316 | 98 | 78.4 | 1418 | 21.37 | 5801 | 3236.5 | 3184.1 | 4643.4 | 1205.1 | 0.68026 | 6.744
2024-12-09 | 20:41 | Data | 0 | 30.887 | 28.565 | 219.242 | 7.62 | 205.563 | 2180.95 | 25.88 | 42.658 | 6.32 | 1.453 | 5.261 | 8915.57 | 2.498 | 98 | 78.4 | 1417 | 21.33 | 5795.1 | 3241.8 | 3199.3 | 4654.2 | 1205.1 | 0.68133 | 6.714
2024-12-09 | 20:41 | Data | 0 | 30.894 | 28.524 | 219.197 | 7.62 | 205.563 | 2180.04 | 25.88 | 42.568 | 6.31 | 1.446 | 5.247 | 8929.14 | 2.471 | 98 | 78.4 | 1418 | 21.33 | 5803.9 | 3236.4 | 3204.2 | 4659.2 | 1205.1 | 0.67905 | 6.693
2024-12-09 | 20:41 | Data | 0 | 31.238 | 28.578 | 219.378 | 7.62 | 205.699 | 2180.04 | 25.89 | 42.568 | 6.32 | 1.454 | 5.287 | 8911.05 | 2.43 | 98 | 78.4 | 1418 | 21.24 | 5792.2 | 3217 | 3171.4 | 4619.3 | 1205.1 | 0.68085 | 6.741
2024-12-09 | 20:41 | Data | 0 | 31.11 | 28.349 | 219.242 | 7.62 | 205.563 | 2180.04 | 25.89 | 42.748 | 6.31 | 1.455 | 5.267 | 8892.96 | 2.748 | 98 | 78.4 | 1418 | 21.28 | 5780.4 | 3252 | 3165.7 | 4640.3 | 1205.1 | 0.68504 | 6.722
2024-12-09 | 20:41 | Data | 0 | 31.339 | 28.598 | 219.332 | 7.62 | 205.654 | 2178.24 | 25.88 | 42.658 | 6.32 | 1.445 | 5.282 | 8883.91 | 2.653 | 98 | 78.5 | 1415 | 21.33 | 5774.5 | 3234.7 | 3174.4 | 4632.4 | 1205.1 | 0.68259 | 6.727
2024-12-09 | 20:41 | Data | 0 | 31.225 | 28.801 | 219.332 | 7.62 | 205.609 | 2178.24 | 25.88 | 42.568 | 6.32 | 1.444 | 5.296 | 8883.91 | 2.532 | 98 | 78.6 | 1416 | 21.37 | 5774.5 | 3239.9 | 3173.3 | 4639.6 | 1205.2 | 0.68194 | 6.74
2024-12-09 | 20:41 | Data | 0 | 31.339 | 29.085 | 219.378 | 7.62 | 205.789 | 2175.52 | 25.88 | 42.658 | 6.32 | 1.443 | 5.268 | 8883.91 | 2.363 | 98 | 78.5 | 1414 | 21.33 | 5774.5 | 3222.5 | 3159.8 | 4620.2 | 1205.2 | 0.6814 | 6.71
2024-12-09 | 20:41 | Data | 0 | 31.177 | 28.531 | 219.378 | 7.62 | 205.609 | 2174.62 | 25.89 | 42.658 | 6.31 | 1.434 | 5.273 | 8874.87 | 2.43 | 98 | 78.6 | 1414 | 21.37 | 5768.7 | 3239.2 | 3205.4 | 4660.2 | 1205.2 | 0.6792 | 6.708
2024-12-09 | 20:41 | Data | 0 | 31.164 | 28.571 | 219.378 | 7.62 | 205.699 | 2175.52 | 25.88 | 42.658 | 6.31 | 1.448 | 5.261 | 8856.78 | 2.565 | 98 | 78.4 | 1414 | 21.33 | 5756.9 | 3235.2 | 3168.1 | 4633.3 | 1205.2 | 0.68208 | 6.71
2024-12-09 | 20:41 | Data | 0 | 31.326 | 28.693 | 219.513 | 7.62 | 205.789 | 2172.81 | 25.89 | 42.658 | 6.32 | 1.451 | 5.235 | 8856.78 | 2.592 | 98 | 78.3 | 1412 | 21.33 | 5756.9 | 3243.8 | 3197.8 | 4658.6 | 1205.2 | 0.6802 | 6.686
2024-12-09 | 20:41 | Data | 0 | 31.285 | 28.862 | 220.056 | 7.62 | 206.196 | 2175.52 | 25.88 | 42.658 | 6.32 | 1.454 | 5.289 | 8897.48 | 2.687 | 98 | 78.4 | 1414 | 21.33 | 5783.4 | 3240.7 | 3201.5 | 4659.4 | 1205.2 | 0.67947 | 6.743
2024-12-09 | 20:41 | Data | 0 | 31.697 | 28.639 | 219.966 | 7.62 | 206.106 | 2178.24 | 25.88 | 42.658 | 6.31 | 1.46 | 5.279 | 9073.85 | 2.802 | 98 | 78.3 | 1416 | 21.28 | 5898 | 3264.6 | 3195.1 | 4672.5 | 1205.2 | 0.68385 | 6.738
2024-12-09 | 20:41 | Data | 0 | 31.38 | 28.578 | 219.875 | 7.62 | 206.196 | 2175.52 | 25.88 | 42.658 | 6.32 | 1.444 | 5.284 | 9119.07 | 2.579 | 98 | 78.5 | 1414 | 21.33 | 5927.4 | 3241.5 | 3170.1 | 4637.5 | 1205.2 | 0.68257 | 6.728
2024-12-09 | 20:41 | Data | 0 | 31.495 | 28.835 | 219.92 | 7.62 | 206.151 | 2175.52 | 25.88 | 42.658 | 6.32 | 1.443 | 5.298 | 9100.98 | 2.707 | 98 | 78.6 | 1415 | 21.33 | 5915.6 | 3248 | 3196.5 | 4660.2 | 1205.2 | 0.68197 | 6.74
2024-12-09 | 20:42 | Data | 0 | 31.009 | 28.403 | 219.92 | 7.62 | 206.151 | 2172.81 | 25.88 | 42.568 | 6.31 | 1.445 | 5.292 | 9087.41 | 2.437 | 98 | 78.5 | 1413 | 21.33 | 5906.8 | 3248.7 | 3185.9 | 4649.3 | 1205.2 | 0.68486 | 6.737
2024-12-09 | 20:42 | Data | 0 | 31.285 | 28.902 | 220.011 | 7.62 | 206.06 | 2177.33 | 25.88 | 42.658 | 6.31 | 1.446 | 5.297 | 8924.61 | 2.363 | 98 | 78.6 | 1415 | 21.33 | 5801 | 3242.8 | 3166.1 | 4633.9 | 1205.2 | 0.68482 | 6.743
2024-12-09 | 20:42 | Data | 0 | 31.326 | 28.693 | 219.92 | 7.62 | 206.151 | 2180.95 | 25.88 | 42.658 | 6.31 | 1.45 | 5.311 | 8897.48 | 2.748 | 98 | 78.6 | 1418 | 21.37 | 5783.4 | 3254.8 | 3166.6 | 4641.8 | 1205.2 | 0.68589 | 6.76
2024-12-09 | 20:42 | Data | 0 | 30.887 | 28.747 | 219.875 | 7.62 | 206.151 | 2180.95 | 25.88 | 42.658 | 6.32 | 1.452 | 5.284 | 8892.96 | 2.687 | 98 | 78.4 | 1417 | 21.33 | 5780.4 | 3247.5 | 3166.8 | 4644.9 | 1205.2 | 0.68291 | 6.736
2024-12-09 | 20:42 | Data | 0 | 31.67 | 28.747 | 219.966 | 7.62 | 206.151 | 2180.04 | 25.88 | 42.658 | 6.31 | 1.443 | 5.277 | 8897.48 | 2.572 | 98 | 78.5 | 1417 | 21.33 | 5783.4 | 3239.5 | 3186.8 | 4647.8 | 1205.2 | 0.68055 | 6.72
2024-12-09 | 20:42 | Data | 0 | 31.326 | 28.416 | 219.785 | 7.62 | 206.015 | 2172.81 | 25.88 | 42.658 | 6.31 | 1.441 | 5.278 | 8883.91 | 2.707 | 98 | 78.6 | 1412 | 21.28 | 5774.5 | 3250.4 | 3213.5 | 4672.9 | 1205.2 | 0.68012 | 6.717
2024-12-09 | 20:42 | Data | 0 | 31.65 | 28.821 | 220.011 | 7.62 | 206.196 | 2178.24 | 25.89 | 42.568 | 6.31 | 1.444 | 5.298 | 8892.96 | 2.565 | 98 | 78.6 | 1415 | 21.28 | 5780.4 | 3240.4 | 3200.6 | 4659.3 | 1205.2 | 0.68024 | 6.743
2024-12-09 | 20:42 | Data | 0 | 30.948 | 28.571 | 220.056 | 7.62 | 206.151 | 2173.72 | 25.88 | 42.658 | 6.31 | 1.452 | 5.293 | 8897.48 | 2.518 | 98 | 78.5 | 1413 | 21.33 | 5783.4 | 3256.7 | 3212.8 | 4676.1 | 1205.2 | 0.68119 | 6.746
2024-12-09 | 20:42 | Data | 0 | 31.225 | 28.754 | 219.83 | 7.62 | 206.151 | 2178.24 | 25.88 | 42.658 | 6.31 | 1.449 | 5.283 | 8870.35 | 2.707 | 98 | 78.5 | 1415 | 21.33 | 5765.7 | 3239.2 | 3211.2 | 4663 | 1205.2 | 0.67841 | 6.732
2024-12-09 | 20:42 | Data | 0 | 31.542 | 28.7 | 220.101 | 7.62 | 206.196 | 2178.24 | 25.88 | 42.658 | 6.31 | 1.446 | 5.311 | 8888.44 | 2.748 | 98 | 78.6 | 1415 | 21.28 | 5777.5 | 3259.4 | 3177.2 | 4654.3 | 1205.2 | 0.68472 | 6.758
2024-12-09 | 20:42 | Data | 0 | 30.995 | 28.679 | 219.875 | 7.62 | 206.015 | 2182.75 | 25.88 | 42.658 | 6.32 | 1.444 | 5.298 | 8902 | 2.417 | 98 | 78.6 | 1419 | 21.33 | 5786.3 | 3240.4 | 3198.3 | 4653.3 | 1205.2 | 0.67983 | 6.741
2024-12-09 | 20:42 | Data | 0 | 31.009 | 28.693 | 220.011 | 7.62 | 206.196 | 2182.75 | 25.89 | 42.748 | 6.33 | 1.449 | 5.276 | 8892.96 | 2.694 | 98 | 78.5 | 1419 | 21.37 | 5780.4 | 3247.2 | 3181.4 | 4646.8 | 1205.2 | 0.68299 | 6.725
2024-12-09 | 20:42 | Data | 0 | 31.225 | 29.118 | 219.92 | 7.62 | 206.151 | 2186.37 | 25.88 | 42.658 | 6.31 | 1.45 | 5.289 | 8897.48 | 2.545 | 98 | 78.5 | 1422 | 21.33 | 5783.4 | 3228.9 | 3189.9 | 4644.3 | 1205.2 | 0.67925 | 6.737
2024-12-09 | 20:42 | Data | 0 | 31.508 | 28.936 | 219.875 | 7.62 | 206.106 | 2186.37 | 25.89 | 42.568 | 6.31 | 1.453 | 5.276 | 8897.48 | 2.491 | 98 | 78.4 | 1422 | 21.33 | 5783.4 | 3223.5 | 3190.4 | 4639.9 | 1205.2 | 0.67896 | 6.728
2024-12-09 | 20:42 | Data | 0 | 31.326 | 28.801 | 219.83 | 7.62 | 206.106 | 2187.27 | 25.89 | 42.568 | 6.31 | 1.446 | 5.292 | 8924.61 | 2.545 | 98 | 78.5 | 1422 | 21.33 | 5801 | 3236.8 | 3189.2 | 4647.3 | 1205.2 | 0.68018 | 6.738
2024-12-09 | 20:42 | Data | 0 | 31.002 | 28.949 | 220.011 | 7.62 | 206.151 | 2187.27 | 25.89 | 42.658 | 6.31 | 1.452 | 5.293 | 8933.66 | 2.64 | 98 | 78.5 | 1422 | 21.33 | 5806.9 | 3253.9 | 3186 | 4654.3 | 1205.2 | 0.68354 | 6.746
2024-12-09 | 20:42 | Data | 0 | 31.501 | 29.247 | 219.966 | 7.62 | 206.106 | 2184.56 | 25.88 | 42.658 | 6.31 | 1.451 | 5.279 | 8920.09 | 2.545 | 98 | 78.4 | 1421 | 21.33 | 5798.1 | 3258.6 | 3190.4 | 4664.7 | 1205.2 | 0.68394 | 6.729
2024-12-09 | 20:42 | Data | 0 | 31.117 | 29.105 | 219.92 | 7.62 | 206.196 | 2184.56 | 25.89 | 42.658 | 6.31 | 1.445 | 5.264 | 8911.05 | 2.343 | 98.1 | 78.5 | 1419 | 21.28 | 5792.2 | 3242.3 | 3173.7 | 4640.5 | 1205.2 | 0.68243 | 6.708
2024-12-09 | 20:43 | Data | 0 | 31.285 | 28.632 | 219.966 | 7.62 | 206.151 | 2183.66 | 25.88 | 42.568 | 6.31 | 1.446 | 5.309 | 8870.35 | 2.633 | 98 | 78.6 | 1420 | 21.33 | 5765.7 | 3253.5 | 3183.6 | 4652.2 | 1205.2 | 0.6837 | 6.755
2024-12-09 | 20:43 | Data | 0 | 31.09 | 28.355 | 219.785 | 7.62 | 206.106 | 2184.56 | 25.89 | 42.748 | 6.32 | 1.452 | 5.32 | 8870.35 | 2.701 | 98 | 78.6 | 1421 | 21.33 | 5765.7 | 3239 | 3172.2 | 4637.3 | 1205.2 | 0.68252 | 6.773
2024-12-09 | 20:43 | Data | 0 | 31.758 | 28.7 | 220.011 | 7.62 | 206.151 | 2186.37 | 25.89 | 42.658 | 6.32 | 1.447 | 5.273 | 8870.35 | 2.647 | 98 | 78.5 | 1422 | 21.33 | 5765.7 | 3239.2 | 3172.3 | 4639.7 | 1205.2 | 0.68226 | 6.721
2024-12-09 | 20:43 | Data | 0 | 31.326 | 28.598 | 219.875 | 7.62 | 206.241 | 2186.37 | 25.88 | 42.658 | 6.32 | 1.446 | 5.261 | 8902 | 2.707 | 98 | 78.4 | 1421 | 21.33 | 5786.3 | 3265.3 | 3187.2 | 4665.4 | 1205.2 | 0.68441 | 6.708
2024-12-09 | 20:43 | Data | 0 | 31.4 | 28.787 | 219.966 | 7.62 | 206.196 | 2187.27 | 25.88 | 42.477 | 6.32 | 1.442 | 5.276 | 8924.61 | 2.579 | 98.1 | 78.5 | 1422 | 21.28 | 5801 | 3250.9 | 3196.7 | 4661.6 | 1205.2 | 0.68104 | 6.717
2024-12-09 | 20:43 | Data | 0 | 31.225 | 28.578 | 219.83 | 7.62 | 206.151 | 2189.99 | 25.88 | 42.658 | 6.32 | 1.457 | 5.268 | 8920.09 | 2.505 | 98.1 | 78.3 | 1423 | 21.33 | 5798.1 | 3246.8 | 3219.6 | 4671.8 | 1205.2 | 0.67853 | 6.726
2024-12-09 | 20:43 | Data | 0 | 30.921 | 28.747 | 219.966 | 7.62 | 206.106 | 2186.37 | 25.88 | 42.658 | 6.32 | 1.451 | 5.293 | 8915.57 | 2.484 | 98 | 78.5 | 1421 | 21.33 | 5795.1 | 3237 | 3204.9 | 4660.9 | 1205.3 | 0.67864 | 6.745
2024-12-09 | 20:43 | Data | 0 | 30.914 | 28.666 | 219.875 | 7.62 | 206.06 | 2187.27 | 25.88 | 42.748 | 6.31 | 1.447 | 5.295 | 8924.61 | 2.505 | 98 | 78.5 | 1421 | 21.37 | 5801 | 3263.5 | 3205.3 | 4670.6 | 1205.3 | 0.6811 | 6.741
2024-12-09 | 20:43 | Data | 0 | 31.637 | 28.821 | 220.011 | 7.62 | 206.151 | 2189.08 | 25.88 | 42.748 | 6.31 | 1.437 | 5.298 | 8888.44 | 2.667 | 98.1 | 78.7 | 1423 | 21.33 | 5777.5 | 3233.9 | 3185.9 | 4644.6 | 1205.3 | 0.68056 | 6.735
2024-12-09 | 20:43 | Data | 0 | 31.117 | 28.598 | 219.875 | 7.62 | 206.196 | 2186.37 | 25.89 | 42.568 | 6.31 | 1.449 | 5.293 | 8883.91 | 2.532 | 98.1 | 78.5 | 1421 | 21.33 | 5774.5 | 3235.8 | 3176.8 | 4636.8 | 1205.3 | 0.68272 | 6.741
2024-12-09 | 20:43 | Data | 0 | 31.346 | 28.808 | 219.966 | 7.62 | 206.196 | 2187.27 | 25.88 | 42.658 | 6.32 | 1.45 | 5.269 | 8883.91 | 2.647 | 98.1 | 78.4 | 1421 | 21.33 | 5774.5 | 3243.5 | 3157.4 | 4629 | 1205.3 | 0.68441 | 6.718
2024-12-09 | 20:43 | Data | 0 | 31.069 | 28.571 | 219.83 | 7.62 | 206.106 | 2187.27 | 25.89 | 42.658 | 6.31 | 1.445 | 5.271 | 8897.48 | 2.532 | 98 | 78.5 | 1421 | 21.37 | 5783.4 | 3234.4 | 3162.9 | 4624.6 | 1205.3 | 0.68397 | 6.717
2024-12-09 | 20:43 | Data | 0 | 31.11 | 28.693 | 219.966 | 7.62 | 206.015 | 2187.27 | 25.88 | 42.568 | 6.31 | 1.441 | 5.286 | 8956.27 | 2.653 | 98 | 78.6 | 1422 | 21.33 | 5821.6 | 3262.8 | 3166 | 4647.7 | 1205.3 | 0.68616 | 6.727
2024-12-09 | 20:43 | Data | 0 | 31.11 | 28.571 | 219.875 | 7.62 | 205.97 | 2182.75 | 25.88 | 42.658 | 6.31 | 1.455 | 5.269 | 8978.88 | 2.538 | 98 | 78.4 | 1419 | 21.33 | 5836.3 | 3259.7 | 3161.2 | 4645 | 1205.3 | 0.68624 | 6.724
2024-12-09 | 20:43 | Data | 0 | 30.995 | 28.794 | 219.785 | 7.62 | 206.06 | 2183.66 | 25.88 | 42.658 | 6.32 | 1.45 | 5.282 | 8978.88 | 2.295 | 98.1 | 78.4 | 1419 | 21.28 | 5836.3 | 3246.5 | 3169.9 | 4640.5 | 1205.3 | 0.6836 | 6.735
2024-12-09 | 20:43 | Data | 0 | 31.252 | 28.794 | 219.966 | 7.62 | 206.196 | 2182.75 | 25.88 | 42.658 | 6.32 | 1.444 | 5.285 | 8974.36 | 2.424 | 98 | 78.5 | 1418 | 21.33 | 5833.3 | 3252.8 | 3184 | 4654.5 | 1205.3 | 0.68288 | 6.729
2024-12-09 | 20:43 | Data | 0 | 31.144 | 28.693 | 219.83 | 7.62 | 206.06 | 2183.66 | 25.89 | 42.658 | 6.31 | 1.441 | 5.3 | 8938.18 | 2.424 | 98 | 78.6 | 1419 | 21.37 | 5809.8 | 3215.4 | 3183.6 | 4629.2 | 1205.3 | 0.67881 | 6.741
2024-12-09 | 20:44 | Data | 0 | 31.333 | 28.632 | 219.92 | 7.62 | 206.196 | 2186.37 | 25.89 | 42.658 | 6.32 | 1.435 | 5.297 | 8933.66 | 2.653 | 98.1 | 78.7 | 1421 | 21.33 | 5806.9 | 3249 | 3204.2 | 4649.1 | 1205.3 | 0.68015 | 6.732
2024-12-09 | 20:44 | Data | 0 | 31.333 | 28.585 | 219.966 | 7.62 | 206.106 | 2187.27 | 25.88 | 42.658 | 6.32 | 1.443 | 5.285 | 8947.23 | 2.653 | 98 | 78.5 | 1421 | 21.33 | 5815.7 | 3229.9 | 3178.9 | 4631.2 | 1205.3 | 0.68226 | 6.729
2024-12-09 | 20:44 | Data | 0 | 31.677 | 28.841 | 220.101 | 7.62 | 206.377 | 2180.95 | 25.88 | 42.658 | 6.31 | 1.446 | 5.295 | 8951.75 | 2.674 | 98 | 78.5 | 1418 | 21.33 | 5818.6 | 3244.5 | 3184.6 | 4649.1 | 1205.3 | 0.68284 | 6.741
2024-12-09 | 20:44 | Data | 0 | 31.731 | 29.145 | 219.966 | 7.62 | 206.332 | 2182.75 | 25.88 | 42.658 | 6.31 | 1.446 | 5.284 | 9119.07 | 2.538 | 98 | 78.5 | 1419 | 21.33 | 5927.4 | 3242.7 | 3174.4 | 4639.8 | 1205.3 | 0.68273 | 6.73
2024-12-09 | 20:44 | Data | 0 | 31.164 | 28.571 | 219.92 | 7.62 | 206.06 | 2186.37 | 25.88 | 42.658 | 6.31 | 1.445 | 5.306 | 9168.81 | 2.545 | 98 | 78.6 | 1422 | 21.33 | 5959.7 | 3249.2 | 3170 | 4644.4 | 1205.3 | 0.68326 | 6.752
2024-12-09 | 20:44 | Data | 0 | 31.333 | 28.598 | 219.83 | 7.62 | 206.106 | 2183.66 | 25.88 | 42.658 | 6.32 | 1.45 | 5.32 | 9168.81 | 2.599 | 98 | 78.6 | 1419 | 21.33 | 5959.7 | 3243.6 | 3163.9 | 4633.9 | 1205.3 | 0.68357 | 6.769
2024-12-09 | 20:44 | Data | 0 | 31.11 | 28.571 | 219.83 | 7.62 | 206.106 | 2183.66 | 25.89 | 42.658 | 6.32 | 1.446 | 5.294 | 9159.77 | 2.532 | 98 | 78.5 | 1419 | 21.37 | 5953.9 | 3235.1 | 3168.2 | 4631.3 | 1205.3 | 0.67925 | 6.741
2024-12-09 | 20:44 | Data | 0 | 30.921 | 29.004 | 220.056 | 7.62 | 206.151 | 2186.37 | 25.89 | 42.658 | 6.31 | 1.46 | 5.284 | 9132.64 | 2.221 | 98 | 78.4 | 1421 | 21.33 | 5936.2 | 3245.2 | 3195.8 | 4654.1 | 1205.3 | 0.68141 | 6.745
2024-12-09 | 20:44 | Data | 0 | 31.015 | 28.997 | 219.92 | 7.62 | 206.196 | 2182.75 | 25.88 | 42.658 | 6.32 | 1.453 | 5.297 | 8969.84 | 2.505 | 98 | 78.5 | 1419 | 21.33 | 5830.4 | 3233.8 | 3179.3 | 4637.9 | 1205.3 | 0.68203 | 6.749
2024-12-09 | 20:44 | Data | 0 | 31.117 | 28.578 | 219.875 | 7.62 | 206.151 | 2187.27 | 25.88 | 42.568 | 6.32 | 1.443 | 5.289 | 8978.88 | 2.525 | 98.1 | 78.6 | 1421 | 21.28 | 5836.3 | 3243.3 | 3186.6 | 4649.2 | 1205.3 | 0.68148 | 6.733
2024-12-09 | 20:44 | Data | 0 | 31.333 | 29.037 | 219.92 | 7.62 | 206.241 | 2187.27 | 25.88 | 42.658 | 6.31 | 1.434 | 5.293 | 8992.45 | 2.532 | 98 | 78.7 | 1422 | 21.37 | 5845.1 | 3220.3 | 3184 | 4630.9 | 1205.3 | 0.68314 | 6.728
2024-12-09 | 20:44 | Data | 0 | 31.056 | 28.571 | 219.739 | 7.62 | 206.106 | 2186.37 | 25.89 | 42.568 | 6.31 | 1.443 | 5.304 | 8992.45 | 2.511 | 98 | 78.6 | 1422 | 21.28 | 5845.1 | 3252.7 | 3180 | 4653.7 | 1205.3 | 0.68299 | 6.748
2024-12-09 | 20:44 | Data | 0 | 31.555 | 28.943 | 219.966 | 7.62 | 206.196 | 2189.08 | 25.86 | 42.658 | 6.31 | 1.443 | 5.315 | 8938.18 | 2.491 | 98.1 | 78.7 | 1423 | 21.33 | 5809.8 | 3232.6 | 3181.7 | 4649.8 | 1205.3 | 0.68073 | 6.757
2024-12-09 | 20:44 | Data | 0 | 31.312 | 28.808 | 219.966 | 7.62 | 206.151 | 2189.99 | 25.88 | 42.658 | 6.31 | 1.445 | 5.303 | 8938.18 | 2.525 | 98.1 | 78.6 | 1423 | 21.33 | 5809.8 | 3231.5 | 3184.5 | 4640.6 | 1205.3 | 0.67969 | 6.748
2024-12-09 | 20:44 | Data | 0 | 31.549 | 28.585 | 219.875 | 7.62 | 206.196 | 2189.08 | 25.88 | 42.568 | 6.31 | 1.444 | 5.287 | 8920.09 | 2.565 | 98.1 | 78.6 | 1423 | 21.28 | 5798.1 | 3224.3 | 3193.7 | 4642.5 | 1205.3 | 0.67876 | 6.73
2024-12-09 | 20:44 | Data | 0 | 31.056 | 28.902 | 219.92 | 7.62 | 206.151 | 2187.27 | 25.88 | 42.658 | 6.32 | 1.447 | 5.326 | 8472.39 | 2.518 | 98 | 78.6 | 1422 | 21.33 | 5507.1 | 3240.6 | 3173.7 | 4642 | 1205.3 | 0.68163 | 6.772
2024-12-09 | 20:44 | Data | 0 | 31.198 | 28.916 | 219.966 | 7.63 | 206.106 | 2190.89 | 25.89 | 42.658 | 6.31 | 1.441 | 5.315 | 8865.83 | 2.586 | 98.1 | 78.7 | 1424 | 21.28 | 5762.8 | 3233.5 | 3182.1 | 4645.7 | 1205.3 | 0.68336 | 6.755
2024-12-09 | 20:44 | Data | 0 | 31.339 | 29.024 | 220.056 | 7.62 | 206.196 | 2191.79 | 25.88 | 42.387 | 6.31 | 1.443 | 5.289 | 8883.91 | 2.363 | 98.1 | 78.6 | 1425 | 21.24 | 5774.5 | 3253.7 | 3185.9 | 4649.2 | 1205.3 | 0.68334 | 6.732
2024-12-09 | 20:45 | Data | 0 | 31.495 | 29.031 | 219.966 | 7.62 | 206.196 | 2192.7 | 25.89 | 42.658 | 6.31 | 1.453 | 5.287 | 8879.39 | 2.707 | 98.1 | 78.4 | 1425 | 21.33 | 5771.6 | 3241.5 | 3176.7 | 4641.2 | 1205.3 | 0.68204 | 6.741
2024-12-09 | 20:45 | Data | 0 | 31.231 | 28.963 | 220.101 | 7.62 | 206.196 | 2194.5 | 25.89 | 42.387 | 6.31 | 1.46 | 5.314 | 8870.35 | 2.349 | 98.1 | 78.4 | 1426 | 21.19 | 5765.7 | 3244.2 | 3158.8 | 4628.6 | 1205.3 | 0.68268 | 6.774
2024-12-09 | 20:45 | Data | 0 | 31.11 | 28.801 | 220.011 | 7.62 | 206.106 | 2191.79 | 25.88 | 42.658 | 6.31 | 1.45 | 5.303 | 8920.09 | 2.484 | 98.1 | 78.5 | 1424 | 21.37 | 5798.1 | 3237.3 | 3148.6 | 4618 | 1205.3 | 0.68441 | 6.753
2024-12-09 | 20:45 | Data | 0 | 31.117 | 28.578 | 219.83 | 7.62 | 206.106 | 2194.5 | 25.89 | 42.568 | 6.31 | 1.445 | 5.294 | 8924.61 | 2.525 | 98.1 | 78.6 | 1426 | 21.33 | 5801 | 3242.5 | 3166 | 4633.5 | 1205.3 | 0.68415 | 6.738
2024-12-09 | 20:45 | Data | 0 | 31.164 | 28.571 | 219.875 | 7.62 | 206.106 | 2187.27 | 25.88 | 42.477 | 6.32 | 1.443 | 5.293 | 8924.61 | 2.552 | 98.1 | 78.6 | 1422 | 21.24 | 5801 | 3242.9 | 3174.9 | 4639 | 1205.4 | 0.68305 | 6.736
2024-12-09 | 20:45 | Data | 0 | 31.339 | 28.977 | 219.966 | 7.62 | 206.106 | 2186.37 | 25.88 | 42.477 | 6.32 | 1.452 | 5.273 | 8915.57 | 2.619 | 98.1 | 78.4 | 1422 | 21.24 | 5795.1 | 3235.4 | 3170.3 | 4630.8 | 1205.4 | 0.68317 | 6.726
2024-12-09 | 20:45 | Data | 0 | 31.542 | 28.916 | 220.011 | 7.62 | 206.151 | 2189.99 | 25.89 | 42.568 | 6.32 | 1.439 | 5.28 | 8924.61 | 2.552 | 98.1 | 78.6 | 1423 | 21.24 | 5801 | 3225.8 | 3175.8 | 4628.7 | 1205.4 | 0.68044 | 6.72
2024-12-09 | 20:45 | Data | 0 | 30.914 | 28.571 | 219.92 | 7.62 | 206.151 | 2191.79 | 25.88 | 42.658 | 6.31 | 1.446 | 5.299 | 8929.14 | 2.511 | 98.1 | 78.6 | 1425 | 21.33 | 5803.9 | 3220.9 | 3145.7 | 4605.5 | 1205.4 | 0.68358 | 6.745
2024-12-09 | 20:45 | Data | 0 | 31.225 | 28.835 | 220.101 | 7.62 | 206.196 | 2191.79 | 25.89 | 42.658 | 6.31 | 1.44 | 5.295 | 8933.66 | 2.795 | 98.1 | 78.6 | 1425 | 21.28 | 5806.9 | 3246.5 | 3169.4 | 4636.9 | 1205.4 | 0.68467 | 6.736
2024-12-09 | 20:45 | Data | 0 | 31.137 | 28.585 | 219.92 | 7.62 | 206.151 | 2190.89 | 25.88 | 42.568 | 6.31 | 1.452 | 5.303 | 8956.27 | 2.532 | 98.1 | 78.5 | 1425 | 21.28 | 5821.6 | 3242.5 | 3161.3 | 4633 | 1205.4 | 0.6856 | 6.755
2024-12-09 | 20:45 | Data | 0 | 31.366 | 28.578 | 219.875 | 7.62 | 206.06 | 2189.08 | 25.88 | 42.748 | 6.32 | 1.451 | 5.295 | 8924.61 | 2.741 | 98.1 | 78.5 | 1423 | 21.28 | 5801 | 3234.1 | 3152 | 4620.7 | 1205.4 | 0.68478 | 6.746
2024-12-09 | 20:45 | Data | 0 | 31.42 | 28.578 | 220.011 | 7.62 | 206.196 | 2191.79 | 25.88 | 42.748 | 6.32 | 1.447 | 5.309 | 8924.61 | 2.383 | 98 | 78.6 | 1425 | 21.33 | 5801 | 3228.4 | 3165.3 | 4624.6 | 1205.4 | 0.68235 | 6.755
2024-12-09 | 20:45 | Data | 0 | 31.326 | 28.808 | 220.101 | 7.62 | 206.151 | 2189.99 | 25.88 | 42.477 | 6.32 | 1.443 | 5.312 | 8924.61 | 2.734 | 98.1 | 78.6 | 1423 | 21.24 | 5801 | 3233 | 3160.5 | 4624.3 | 1205.4 | 0.68325 | 6.755
2024-12-09 | 20:45 | Data | 0 | 31.11 | 28.571 | 219.92 | 7.62 | 206.106 | 2189.99 | 25.88 | 42.477 | 6.32 | 1.434 | 5.313 | 8924.61 | 2.532 | 98.1 | 78.7 | 1423 | 21.19 | 5801 | 3249.3 | 3176 | 4644.3 | 1205.4 | 0.6837 | 6.747
2024-12-09 | 20:45 | Data | 0 | 31.225 | 28.747 | 219.92 | 7.63 | 206.151 | 2189.08 | 25.89 | 42.658 | 6.32 | 1.446 | 5.301 | 8978.88 | 2.633 | 98.1 | 78.6 | 1423 | 21.28 | 5836.3 | 3226.2 | 3188.8 | 4637.6 | 1205.4 | 0.67952 | 6.747
2024-12-09 | 20:45 | Data | 0 | 31.184 | 28.808 | 219.92 | 7.62 | 206.196 | 2189.08 | 25.88 | 42.297 | 6.31 | 1.458 | 5.283 | 8983.4 | 2.309 | 98.1 | 78.4 | 1423 | 21.19 | 5839.2 | 3227.5 | 3181.2 | 4635.1 | 1205.4 | 0.6799 | 6.741
2024-12-09 | 20:45 | Data | 0 | 31.252 | 28.909 | 219.966 | 7.62 | 206.241 | 2189.08 | 25.89 | 42.387 | 6.32 | 1.452 | 5.276 | 8969.84 | 2.538 | 98.1 | 78.4 | 1423 | 21.24 | 5830.4 | 3237.9 | 3153.3 | 4636.4 | 1205.4 | 0.68305 | 6.729
2024-12-09 | 20:45 | Data | 0 | 31.198 | 28.787 | 220.237 | 7.62 | 206.151 | 2189.99 | 25.88 | 42.387 | 6.31 | 1.449 | 5.271 | 8978.88 | 2.403 | 98.1 | 78.4 | 1424 | 21.19 | 5836.3 | 3227.5 | 3133.3 | 4598.1 | 1205.4 | 0.68618 | 6.72
2024-12-09 | 20:46 | Data | 0 | 31.339 | 28.808 | 219.92 | 7.62 | 206.151 | 2189.99 | 25.88 | 42.387 | 6.31 | 1.44 | 5.27 | 8960.79 | 2.532 | 98.1 | 78.5 | 1424 | 21.19 | 5824.5 | 3249.1 | 3158.8 | 4632.7 | 1205.4 | 0.68609 | 6.711
2024-12-09 | 20:46 | Data | 0 | 31.366 | 29.037 | 220.056 | 7.62 | 206.332 | 2182.75 | 25.88 | 42.387 | 6.32 | 1.446 | 5.298 | 8933.66 | 2.478 | 98.1 | 78.6 | 1419 | 21.19 | 5806.9 | 3231.4 | 3164.8 | 4628 | 1205.4 | 0.68165 | 6.745
2024-12-09 | 20:46 | Data | 0 | 31.562 | 29.125 | 220.011 | 7.62 | 206.332 | 2183.66 | 25.88 | 42.387 | 6.31 | 1.443 | 5.289 | 8933.66 | 2.748 | 98.1 | 78.6 | 1419 | 21.19 | 5806.9 | 3241.5 | 3162.7 | 4629.9 | 1205.4 | 0.68425 | 6.73
2024-12-09 | 20:46 | Data | 0 | 31.501 | 28.943 | 219.966 | 7.62 | 206.151 | 2186.37 | 25.89 | 42.387 | 6.31 | 1.443 | 5.292 | 8933.66 | 2.579 | 98.1 | 78.6 | 1419 | 21.19 | 5806.9 | 3234.9 | 3165 | 4644.9 | 1205.4 | 0.68266 | 6.733
2024-12-09 | 20:46 | Data | 0 | 31.339 | 29.078 | 220.101 | 7.62 | 206.196 | 2183.66 | 25.88 | 42.387 | 6.32 | 1.441 | 5.299 | 8951.75 | 2.538 | 98.1 | 78.6 | 1419 | 21.19 | 5818.6 | 3220.5 | 3183.7 | 4621.7 | 1205.4 | 0.67876 | 6.74
2024-12-09 | 20:46 | Data | 0 | 31.285 | 28.646 | 219.92 | 7.62 | 206.106 | 2183.66 | 25.88 | 42.387 | 6.31 | 1.447 | 5.298 | 8978.88 | 2.667 | 98.1 | 78.6 | 1419 | 21.19 | 5836.3 | 3234.5 | 3194 | 4650.3 | 1205.4 | 0.67916 | 6.744
2024-12-09 | 20:46 | Data | 0 | 31.353 | 28.713 | 219.92 | 7.62 | 206.151 | 2182.75 | 25.88 | 42.387 | 6.32 | 1.444 | 5.288 | 8992.45 | 2.478 | 98.1 | 78.5 | 1419 | 21.19 | 5845.1 | 3229.8 | 3196.2 | 4642.7 | 1205.4 | 0.68038 | 6.733
2024-12-09 | 20:46 | Data | 0 | 31.407 | 28.605 | 219.966 | 7.62 | 206.241 | 2182.75 | 25.88 | 42.387 | 6.31 | 1.45 | 5.279 | 8983.4 | 2.552 | 98.1 | 78.5 | 1419 | 21.19 | 5839.2 | 3265.3 | 3185.4 | 4664.7 | 1205.4 | 0.68374 | 6.729
2024-12-09 | 20:46 | Data | 0 | 31.312 | 28.808 | 220.056 | 7.62 | 206.151 | 2182.75 | 25.88 | 42.387 | 6.32 | 1.451 | 5.296 | 8965.31 | 2.613 | 98.1 | 78.5 | 1419 | 21.19 | 5827.5 | 3233.9 | 3184.9 | 4640.1 | 1205.4 | 0.68112 | 6.747
2024-12-09 | 20:46 | Data | 0 | 31.285 | 29.139 | 220.101 | 7.63 | 206.106 | 2182.75 | 25.89 | 42.477 | 6.31 | 1.45 | 5.295 | 8965.31 | 2.43 | 98.1 | 78.5 | 1419 | 21.24 | 5827.5 | 3246.9 | 3197.3 | 4653.1 | 1205.4 | 0.68062 | 6.746
2024-12-09 | 20:46 | Data | 0 | 31.252 | 28.578 | 220.011 | 7.62 | 206.332 | 2182.75 | 25.89 | 42.387 | 6.31 | 1.446 | 5.281 | 8951.75 | 2.552 | 98.1 | 78.5 | 1419 | 21.19 | 5818.6 | 3244.6 | 3166.4 | 4638.6 | 1205.4 | 0.6833 | 6.727
2024-12-09 | 20:46 | Data | 0 | 31.454 | 28.585 | 220.011 | 7.62 | 206.151 | 2182.75 | 25.88 | 42.387 | 6.31 | 1.441 | 5.247 | 8951.75 | 2.633 | 98.1 | 78.5 | 1419 | 21.19 | 5818.6 | 3253.2 | 3195.1 | 4664.3 | 1205.4 | 0.68188 | 6.689
2024-12-09 | 20:46 | Data | 0 | 31.339 | 28.835 | 220.056 | 7.62 | 206.196 | 2182.75 | 25.88 | 42.387 | 6.31 | 1.441 | 5.268 | 8965.31 | 2.417 | 98.1 | 78.5 | 1419 | 21.19 | 5827.5 | 3232.2 | 3191.7 | 4647.4 | 1205.4 | 0.68082 | 6.709
2024-12-09 | 20:46 | Data | 0 | 31.333 | 28.808 | 219.966 | 7.62 | 206.106 | 2186.37 | 25.88 | 42.387 | 6.32 | 1.454 | 5.265 | 8911.05 | 2.532 | 98.1 | 78.4 | 1421 | 21.19 | 5792.2 | 3242 | 3187.4 | 4647.9 | 1205.4 | 0.68205 | 6.719
2024-12-09 | 20:46 | Data | 0 | 31.333 | 29.031 | 220.056 | 7.63 | 206.196 | 2186.37 | 25.88 | 42.297 | 6.32 | 1.457 | 5.277 | 8906.53 | 2.329 | 98.1 | 78.4 | 1421 | 21.19 | 5789.2 | 3232.8 | 3192.6 | 4644.7 | 1205.4 | 0.68014 | 6.732
2024-12-09 | 20:46 | Data | 0 | 31.718 | 29.064 | 220.056 | 7.62 | 206.377 | 2187.27 | 25.88 | 42.658 | 6.32 | 1.46 | 5.281 | 8924.61 | 2.707 | 98.1 | 78.4 | 1422 | 21.33 | 5801 | 3245.4 | 3184.2 | 4649.9 | 1205.4 | 0.68252 | 6.74
2024-12-09 | 20:46 | Data | 0 | 31.225 | 28.632 | 219.875 | 7.62 | 206.196 | 2186.37 | 25.88 | 42.658 | 6.32 | 1.451 | 5.287 | 8911.05 | 2.478 | 98 | 78.5 | 1421 | 21.33 | 5792.2 | 3252.1 | 3191.4 | 4658.1 | 1205.4 | 0.6826 | 6.737
2024-12-09 | 20:46 | Data | 0 | 31.252 | 28.578 | 220.056 | 7.62 | 206.241 | 2186.37 | 25.88 | 42.387 | 6.32 | 1.439 | 5.289 | 8938.18 | 2.552 | 98.1 | 78.6 | 1421 | 21.15 | 5809.8 | 3229.2 | 3181.7 | 4636.7 | 1205.4 | 0.68017 | 6.728
2024-12-09 | 20:47 | Data | 0 | 31.495 | 28.713 | 219.875 | 7.62 | 206.106 | 2186.37 | 25.88 | 42.658 | 6.31 | 1.436 | 5.272 | 8951.75 | 2.647 | 98 | 78.6 | 1421 | 21.33 | 5818.6 | 3240.6 | 3179.2 | 4642.5 | 1205.4 | 0.68149 | 6.709
2024-12-09 | 20:47 | Data | 0 | 31.117 | 28.585 | 219.92 | 7.62 | 206.241 | 2186.37 | 25.89 | 42.658 | 6.32 | 1.447 | 5.295 | 8938.18 | 2.437 | 98 | 78.5 | 1422 | 21.33 | 5809.8 | 3244 | 3189.7 | 4654.6 | 1205.5 | 0.68098 | 6.742
2024-12-09 | 20:47 | Data | 0 | 31.333 | 28.794 | 219.83 | 7.62 | 206.06 | 2184.56 | 25.88 | 42.748 | 6.32 | 1.45 | 5.284 | 8933.66 | 2.552 | 98 | 78.5 | 1421 | 21.37 | 5806.9 | 3229.3 | 3164 | 4621.9 | 1205.5 | 0.68181 | 6.735
2024-12-09 | 20:47 | Data | 0 | 31.704 | 28.808 | 220.011 | 7.62 | 206.196 | 2183.66 | 25.89 | 42.568 | 6.32 | 1.445 | 5.297 | 8883.91 | 2.592 | 98.1 | 78.6 | 1419 | 21.33 | 5774.5 | 3235.9 | 3173.7 | 4630.8 | 1205.5 | 0.68284 | 6.741
2024-12-09 | 20:47 | Data | 0 | 31.312 | 29.125 | 220.011 | 7.62 | 206.241 | 2186.37 | 25.88 | 42.297 | 6.32 | 1.44 | 5.279 | 8883.91 | 2.613 | 98.1 | 78.6 | 1421 | 21.19 | 5774.5 | 3239.1 | 3186.7 | 4644.4 | 1205.5 | 0.68154 | 6.718
2024-12-09 | 20:47 | Data | 0 | 31.258 | 29.004 | 220.011 | 7.62 | 206.332 | 2182.75 | 25.89 | 42.387 | 6.32 | 1.452 | 5.284 | 8883.91 | 2.403 | 98.1 | 78.4 | 1419 | 21.19 | 5774.5 | 3232.7 | 3178.4 | 4638.9 | 1205.5 | 0.68023 | 6.736
2024-12-09 | 20:47 | Data | 0 | 31.117 | 28.693 | 219.92 | 7.62 | 206.196 | 2182.75 | 25.88 | 42.387 | 6.32 | 1.446 | 5.301 | 8892.96 | 2.532 | 98.1 | 78.6 | 1419 | 21.19 | 5780.4 | 3233.5 | 3206.8 | 4658.4 | 1205.5 | 0.68103 | 6.747
2024-12-09 | 20:47 | Data | 0 | 31.137 | 28.794 | 219.966 | 7.62 | 206.106 | 2182.75 | 25.88 | 42.387 | 6.32 | 1.452 | 5.307 | 8870.35 | 2.336 | 98.1 | 78.5 | 1419 | 21.19 | 5765.7 | 3240.6 | 3200.4 | 4655.4 | 1205.5 | 0.68051 | 6.758
2024-12-09 | 20:47 | Data | 0 | 31.164 | 28.754 | 219.966 | 7.62 | 206.196 | 2180.95 | 25.88 | 42.387 | 6.32 | 1.448 | 5.296 | 8861.3 | 2.363 | 98.1 | 78.5 | 1417 | 21.19 | 5759.8 | 3245 | 3176.7 | 4644.6 | 1205.5 | 0.68261 | 6.745
2024-12-09 | 20:47 | Data | 0 | 31.339 | 28.693 | 219.966 | 7.62 | 206.106 | 2180.04 | 25.88 | 42.477 | 6.32 | 1.446 | 5.293 | 8838.69 | 2.559 | 98.1 | 78.6 | 1418 | 21.19 | 5745.1 | 3244.5 | 3191.5 | 4652.2 | 1205.5 | 0.68175 | 6.739
2024-12-09 | 20:47 | Data | 0 | 31.65 | 29.132 | 219.966 | 7.62 | 206.106 | 2180.04 | 25.88 | 42.387 | 6.32 | 1.439 | 5.295 | 8847.74 | 2.532 | 98.1 | 78.6 | 1417 | 21.19 | 5751 | 3238.3 | 3163.9 | 4625.2 | 1205.5 | 0.68449 | 6.734
2024-12-09 | 20:47 | Data | 0 | 31.184 | 28.585 | 219.92 | 7.62 | 206.196 | 2180.04 | 25.89 | 42.387 | 6.31 | 1.439 | 5.3 | 8906.53 | 2.511 | 98.1 | 78.6 | 1417 | 21.24 | 5789.2 | 3255.2 | 3164 | 4637.8 | 1205.5 | 0.68446 | 6.739
2024-12-09 | 20:47 | Data | 0 | 31.11 | 28.571 | 219.83 | 7.62 | 206.106 | 2182.75 | 25.88 | 42.116 | 6.32 | 1.449 | 5.283 | 8924.61 | 2.714 | 98.1 | 78.5 | 1419 | 21.06 | 5801 | 3240.4 | 3202.3 | 4657.4 | 1205.5 | 0.68058 | 6.733
2024-12-09 | 20:47 | Data | 0 | 31.198 | 28.605 | 219.875 | 7.62 | 206.151 | 2182.75 | 25.88 | 42.297 | 6.32 | 1.452 | 5.276 | 8920.09 | 2.498 | 98.1 | 78.4 | 1419 | 21.19 | 5798.1 | 3247.1 | 3207.9 | 4670.9 | 1205.5 | 0.6785 | 6.728
2024-12-09 | 20:47 | Data | 0 | 31.11 | 28.693 | 219.785 | 7.62 | 206.196 | 2186.37 | 25.88 | 42.387 | 6.31 | 1.442 | 5.282 | 8924.61 | 2.538 | 98.1 | 78.6 | 1421 | 21.19 | 5801 | 3255 | 3168 | 4643.5 | 1205.5 | 0.6847 | 6.724
2024-12-09 | 20:47 | Data | 0 | 31.171 | 28.781 | 219.966 | 7.62 | 206.196 | 2186.37 | 25.88 | 42.477 | 6.32 | 1.441 | 5.275 | 8902 | 2.505 | 98.1 | 78.5 | 1422 | 21.24 | 5786.3 | 3239.7 | 3175.7 | 4638.2 | 1205.5 | 0.68226 | 6.716
2024-12-09 | 20:47 | Data | 0 | 31.339 | 28.909 | 220.011 | 7.62 | 206.196 | 2184.56 | 25.88 | 42.568 | 6.33 | 1.443 | 5.266 | 8888.44 | 2.633 | 98.1 | 78.5 | 1421 | 21.33 | 5777.5 | 3246.1 | 3176.9 | 4642.2 | 1205.5 | 0.68354 | 6.709
2024-12-09 | 20:48 | Data | 0 | 31.333 | 28.808 | 219.966 | 7.62 | 206.151 | 2186.37 | 25.88 | 42.658 | 6.32 | 1.444 | 5.289 | 8897.48 | 2.532 | 98 | 78.6 | 1421 | 21.33 | 5783.4 | 3231.9 | 3184.4 | 4638.6 | 1205.5 | 0.68059 | 6.734
2024-12-09 | 20:48 | Data | 0 | 30.914 | 28.794 | 219.92 | 7.62 | 206.106 | 2186.37 | 25.89 | 42.568 | 6.32 | 1.45 | 5.285 | 8911.05 | 2.282 | 98 | 78.5 | 1421 | 21.28 | 5792.2 | 3244.3 | 3186.5 | 4650.2 | 1205.5 | 0.6821 | 6.736
2024-12-09 | 20:48 | Data | 0 | 31.839 | 28.97 | 220.147 | 7.62 | 206.377 | 2186.37 | 25.88 | 42.297 | 6.32 | 1.446 | 5.269 | 8915.57 | 2.721 | 98.1 | 78.5 | 1421 | 21.15 | 5795.1 | 3246.5 | 3187.5 | 4652.7 | 1205.5 | 0.6823 | 6.714
2024-12-09 | 20:48 | Data | 0 | 31.569 | 29.01 | 220.101 | 7.62 | 206.332 | 2187.27 | 25.89 | 42.477 | 6.32 | 1.443 | 5.281 | 8915.57 | 2.478 | 98.1 | 78.5 | 1422 | 21.24 | 5795.1 | 3223 | 3200.6 | 4643.1 | 1205.5 | 0.67818 | 6.726
2024-12-09 | 20:48 | Data | 0 | 31.508 | 28.592 | 220.101 | 7.62 | 206.196 | 2187.27 | 25.89 | 42.658 | 6.32 | 1.443 | 5.3 | 8911.05 | 2.647 | 98.1 | 78.6 | 1421 | 21.28 | 5792.2 | 3253.3 | 3186.7 | 4655.3 | 1205.5 | 0.68276 | 6.742
2024-12-09 | 20:48 | Data | 0 | 31.454 | 28.977 | 219.966 | 7.62 | 206.241 | 2186.37 | 25.88 | 42.477 | 6.32 | 1.442 | 5.304 | 8897.48 | 2.633 | 98.1 | 78.6 | 1421 | 21.19 | 5783.4 | 3250.9 | 3185.7 | 4653.4 | 1205.5 | 0.68319 | 6.746
2024-12-09 | 20:48 | Data | 0 | 31.11 | 28.544 | 219.875 | 7.62 | 206.151 | 2189.08 | 25.89 | 42.658 | 6.32 | 1.442 | 5.297 | 8897.48 | 2.728 | 98.1 | 78.6 | 1423 | 21.33 | 5783.4 | 3251.3 | 3192.7 | 4655.6 | 1205.5 | 0.68206 | 6.739
2024-12-09 | 20:48 | Data | 0 | 31.393 | 28.781 | 220.011 | 7.62 | 206.332 | 2182.75 | 25.89 | 42.026 | 6.32 | 1.44 | 5.311 | 8938.18 | 2.579 | 98.1 | 78.7 | 1419 | 21.06 | 5809.8 | 3226.9 | 3162.4 | 4619.1 | 1205.5 | 0.68376 | 6.752
2024-12-09 | 20:48 | Data | 0 | 31.569 | 28.862 | 220.147 | 7.62 | 206.196 | 2186.37 | 25.89 | 42.568 | 6.32 | 1.447 | 5.298 | 8933.66 | 2.538 | 98.1 | 78.5 | 1421 | 21.33 | 5806.9 | 3246.4 | 3175 | 4644.3 | 1205.5 | 0.68308 | 6.746
2024-12-09 | 20:48 | Data | 0 | 31.508 | 28.868 | 220.011 | 7.63 | 206.241 | 2186.37 | 25.88 | 42.658 | 6.31 | 1.447 | 5.271 | 8933.66 | 2.478 | 98 | 78.5 | 1422 | 21.33 | 5806.9 | 3233.3 | 3185.7 | 4640.8 | 1205.5 | 0.67991 | 6.719
2024-12-09 | 20:48 | Data | 0 | 31.339 | 28.585 | 219.92 | 7.62 | 206.196 | 2184.56 | 25.88 | 42.658 | 6.32 | 1.445 | 5.286 | 8929.14 | 2.572 | 98 | 78.5 | 1421 | 21.33 | 5803.9 | 3244.9 | 3180.6 | 4645.1 | 1205.5 | 0.68264 | 6.73
2024-12-09 | 20:48 | Data | 0 | 31.292 | 28.889 | 220.056 | 7.62 | 206.241 | 2189.08 | 25.88 | 42.568 | 6.31 | 1.45 | 5.305 | 8897.48 | 2.43 | 98.1 | 78.5 | 1423 | 21.33 | 5783.4 | 3227.9 | 3180 | 4634.8 | 1205.5 | 0.68158 | 6.755
2024-12-09 | 20:48 | Data | 0 | 31.312 | 28.835 | 220.056 | 7.62 | 206.151 | 2189.08 | 25.88 | 42.658 | 6.31 | 1.446 | 5.288 | 8897.48 | 2.674 | 98.1 | 78.5 | 1423 | 21.33 | 5783.4 | 3217.5 | 3182.9 | 4634.6 | 1205.5 | 0.67812 | 6.735
2024-12-09 | 20:48 | Data | 0 | 31.441 | 28.632 | 220.056 | 7.62 | 206.196 | 2189.08 | 25.88 | 42.658 | 6.31 | 1.441 | 5.287 | 8897.48 | 2.606 | 98.1 | 78.6 | 1423 | 21.28 | 5783.4 | 3226.3 | 3201.4 | 4648.4 | 1205.5 | 0.67769 | 6.727
2024-12-09 | 20:48 | Data | 0 | 31.13 | 28.571 | 219.92 | 7.62 | 206.106 | 2189.08 | 25.89 | 42.658 | 6.32 | 1.439 | 5.297 | 8883.91 | 2.43 | 98 | 78.6 | 1423 | 21.33 | 5774.5 | 3236.1 | 3210.7 | 4667.8 | 1205.5 | 0.67821 | 6.735
2024-12-09 | 20:48 | Data | 0 | 31.258 | 28.808 | 219.966 | 7.62 | 206.332 | 2188.18 | 25.89 | 42.658 | 6.32 | 1.441 | 5.288 | 8472.39 | 2.322 | 98.1 | 78.6 | 1423 | 21.33 | 5507.1 | 3248.3 | 3199.9 | 4658.4 | 1205.5 | 0.67848 | 6.728
2024-12-09 | 20:48 | Data | 0 | 31.61 | 28.949 | 220.192 | 7.62 | 206.332 | 2189.08 | 25.88 | 42.658 | 6.32 | 1.447 | 5.307 | 8897.48 | 2.89 | 98.1 | 78.6 | 1423 | 21.33 | 5783.4 | 3256.7 | 3198 | 4665.3 | 1205.5 | 0.6819 | 6.754
2024-12-09 | 20:48 | Data | 0 | 31.333 | 28.808 | 219.966 | 7.62 | 206.196 | 2188.18 | 25.88 | 42.658 | 6.32 | 1.448 | 5.302 | 8892.96 | 2.532 | 98 | 78.6 | 1422 | 21.33 | 5780.4 | 3230.1 | 3176.9 | 4632.5 | 1205.6 | 0.68099 | 6.749
2024-12-09 | 20:49 | Data | 0 | 31.164 | 28.578 | 219.875 | 7.62 | 206.106 | 2186.37 | 25.88 | 42.477 | 6.32 | 1.441 | 5.29 | 8911.05 | 2.538 | 98.1 | 78.6 | 1421 | 21.28 | 5792.2 | 3246.2 | 3172 | 4640.1 | 1205.6 | 0.68336 | 6.731
2024-12-09 | 20:49 | Data | 0 | 31.866 | 29.159 | 220.056 | 7.62 | 206.241 | 2186.37 | 25.88 | 42.206 | 6.32 | 1.44 | 5.276 | 8856.78 | 2.64 | 98.1 | 78.6 | 1421 | 21.1 | 5756.9 | 3245.4 | 3154.3 | 4626.9 | 1205.6 | 0.68451 | 6.717
2024-12-09 | 20:49 | Data | 0 | 31.353 | 28.808 | 220.056 | 7.62 | 206.332 | 2184.56 | 25.88 | 42.477 | 6.32 | 1.452 | 5.279 | 8870.35 | 2.363 | 98.1 | 78.4 | 1419 | 21.19 | 5765.7 | 3234.2 | 3189.2 | 4642.1 | 1205.6 | 0.68047 | 6.731
2024-12-09 | 20:49 | Data | 0 | 31.339 | 28.808 | 219.875 | 7.62 | 206.106 | 2186.37 | 25.88 | 42.297 | 6.32 | 1.445 | 5.3 | 8870.35 | 2.532 | 98.1 | 78.6 | 1421 | 21.19 | 5765.7 | 3232.4 | 3204.8 | 4658 | 1205.6 | 0.67834 | 6.746
2024-12-09 | 20:49 | Data | 0 | 31.393 | 28.578 | 220.011 | 7.62 | 206.241 | 2178.24 | 25.88 | 42.297 | 6.32 | 1.452 | 5.283 | 8865.83 | 2.592 | 98.1 | 78.4 | 1416 | 21.19 | 5762.8 | 3227.6 | 3201.2 | 4650.6 | 1205.6 | 0.67908 | 6.736
2024-12-09 | 20:49 | Data | 0 | 31.562 | 28.72 | 219.966 | 7.62 | 206.196 | 2187.27 | 25.88 | 42.387 | 6.32 | 1.445 | 5.264 | 8960.79 | 2.363 | 98.1 | 78.5 | 1422 | 21.19 | 5824.5 | 3254.2 | 3251 | 4702.4 | 1205.6 | 0.67627 | 6.708
2024-12-09 | 20:49 | Data | 0 | 31.285 | 29.078 | 220.101 | 7.62 | 206.332 | 2186.37 | 25.88 | 42.477 | 6.31 | 1.446 | 5.287 | 8951.75 | 2.538 | 98.1 | 78.5 | 1421 | 21.19 | 5818.6 | 3240.2 | 3225 | 4673.7 | 1205.6 | 0.67708 | 6.733
2024-12-09 | 20:49 | Data | 0 | 31.279 | 28.693 | 219.875 | 7.62 | 206.196 | 2187.27 | 25.88 | 42.387 | 6.32 | 1.444 | 5.281 | 8956.27 | 2.734 | 98.1 | 78.5 | 1422 | 21.24 | 5821.6 | 3258 | 3204.8 | 4664.2 | 1205.6 | 0.68029 | 6.726
2024-12-09 | 20:49 | Data | 0 | 31.292 | 28.97 | 220.101 | 7.62 | 206.241 | 2180.04 | 25.88 | 42.477 | 6.31 | 1.454 | 5.282 | 8956.27 | 2.376 | 98.1 | 78.4 | 1418 | 21.19 | 5821.6 | 3242.2 | 3160.1 | 4631.3 | 1205.6 | 0.68422 | 6.737
2024-12-09 | 20:49 | Data | 0 | 31.481 | 29.01 | 220.011 | 7.62 | 206.241 | 2186.37 | 25.89 | 42.387 | 6.31 | 1.45 | 5.299 | 8920.09 | 2.41 | 98.1 | 78.5 | 1421 | 21.24 | 5798.1 | 3235.5 | 3149.1 | 4614.8 | 1205.6 | 0.68557 | 6.748
2024-12-09 | 20:49 | Data | 0 | 31.211 | 28.794 | 219.966 | 7.62 | 206.151 | 2186.37 | 25.89 | 42.387 | 6.31 | 1.448 | 5.336 | 8933.66 | 2.525 | 98.1 | 78.7 | 1421 | 21.24 | 5806.9 | 3219.7 | 3176.6 | 4627.3 | 1205.6 | 0.68155 | 6.782
2024-12-09 | 20:49 | Data | 0 | 31.562 | 29.037 | 219.966 | 7.62 | 206.241 | 2186.37 | 25.88 | 42.387 | 6.31 | 1.449 | 5.323 | 8911.05 | 2.532 | 98.1 | 78.6 | 1421 | 21.24 | 5792.2 | 3223 | 3176.2 | 4624.4 | 1205.6 | 0.68014 | 6.772
2024-12-09 | 20:49 | Data | 0 | 31.508 | 28.835 | 220.056 | 7.62 | 206.241 | 2187.27 | 25.88 | 42.387 | 6.31 | 1.457 | 5.318 | 8924.61 | 2.451 | 98.1 | 78.5 | 1422 | 21.19 | 5801 | 3231.6 | 3159.6 | 4621.8 | 1205.6 | 0.68317 | 6.774
2024-12-09 | 20:49 | Data | 0 | 31.387 | 29.004 | 219.966 | 7.62 | 206.196 | 2182.75 | 25.88 | 42.387 | 6.31 | 1.454 | 5.306 | 8883.91 | 2.552 | 98.1 | 78.5 | 1419 | 21.19 | 5774.5 | 3224.6 | 3187.9 | 4634.7 | 1205.6 | 0.67976 | 6.759
2024-12-09 | 20:49 | Data | 0 | 31.204 | 28.693 | 219.92 | 7.62 | 206.241 | 2182.75 | 25.88 | 42.387 | 6.32 | 1.439 | 5.313 | 8888.44 | 2.343 | 98.1 | 78.7 | 1419 | 21.19 | 5777.5 | 3224.7 | 3238 | 4673 | 1205.6 | 0.67367 | 6.752
2024-12-09 | 20:49 | Data | 0 | 31.711 | 28.592 | 220.101 | 7.62 | 206.422 | 2186.37 | 25.89 | 42.297 | 6.32 | 1.447 | 5.306 | 8897.48 | 2.674 | 98.1 | 78.6 | 1421 | 21.19 | 5783.4 | 3236.5 | 3221.6 | 4668.9 | 1205.6 | 0.68008 | 6.752
2024-12-09 | 20:49 | Data | 0 | 31.177 | 28.808 | 220.056 | 7.63 | 206.241 | 2186.37 | 25.89 | 42.838 | 6.32 | 1.453 | 5.263 | 8883.91 | 2.43 | 98 | 78.4 | 1421 | 21.42 | 5774.5 | 3250.9 | 3227.4 | 4681.1 | 1205.6 | 0.67891 | 6.717
2024-12-09 | 20:49 | Data | 0 | 31.272 | 29.172 | 220.056 | 7.62 | 206.241 | 2186.37 | 25.88 | 42.297 | 6.32 | 1.462 | 5.271 | 8920.09 | 2.532 | 98.1 | 78.3 | 1421 | 21.15 | 5798.1 | 3249.9 | 3222.2 | 4672.6 | 1205.6 | 0.67983 | 6.732
2024-12-09 | 20:50 | Data | 0 | 31.157 | 28.585 | 219.92 | 7.62 | 206.332 | 2183.66 | 25.88 | 42.477 | 6.31 | 1.457 | 5.28 | 8920.09 | 2.403 | 98.1 | 78.4 | 1419 | 21.19 | 5798.1 | 3252.6 | 3209.7 | 4668.1 | 1205.6 | 0.6818 | 6.736
2024-12-09 | 20:50 | Data | 0 | 31.339 | 29.125 | 220.011 | 7.62 | 206.196 | 2184.56 | 25.89 | 42.387 | 6.32 | 1.446 | 5.264 | 8911.05 | 2.532 | 98.1 | 78.4 | 1419 | 21.19 | 5792.2 | 3251.7 | 3202.6 | 4667.6 | 1205.6 | 0.67967 | 6.71
2024-12-09 | 20:50 | Data | 0 | 31.11 | 28.571 | 219.785 | 7.62 | 206.241 | 2187.27 | 25.88 | 42.568 | 6.32 | 1.45 | 5.278 | 8924.61 | 2.538 | 98 | 78.5 | 1422 | 21.33 | 5801 | 3232.1 | 3172.8 | 4632.3 | 1205.6 | 0.68207 | 6.727
2024-12-09 | 20:50 | Data | 0 | 31.515 | 28.808 | 220.101 | 7.62 | 206.241 | 2186.37 | 25.88 | 42.658 | 6.32 | 1.449 | 5.302 | 8933.66 | 2.619 | 98 | 78.5 | 1421 | 21.33 | 5806.9 | 3233.5 | 3175.9 | 4638.4 | 1205.6 | 0.68168 | 6.751
2024-12-09 | 20:50 | Data | 0 | 31.15 | 28.686 | 219.875 | 7.62 | 206.151 | 2187.27 | 25.89 | 42.658 | 6.32 | 1.452 | 5.276 | 8906.53 | 2.316 | 98.1 | 78.4 | 1422 | 21.28 | 5789.2 | 3219.7 | 3187.5 | 4636.6 | 1205.6 | 0.67937 | 6.728
2024-12-09 | 20:50 | Data | 0 | 31.684 | 28.814 | 220.011 | 7.62 | 206.422 | 2186.37 | 25.89 | 42.658 | 6.32 | 1.471 | 5.292 | 8920.09 | 2.653 | 98.1 | 78.3 | 1420 | 21.28 | 5798.1 | 3210.3 | 3182.3 | 4630.2 | 1205.6 | 0.67973 | 6.763
2024-12-09 | 20:50 | Data | 0 | 31.393 | 28.808 | 219.966 | 7.62 | 206.196 | 2186.37 | 25.88 | 42.658 | 6.32 | 1.457 | 5.301 | 8920.09 | 2.424 | 98 | 78.4 | 1421 | 21.33 | 5798.1 | 3235.2 | 3176.8 | 4634.8 | 1205.6 | 0.68282 | 6.758
2024-12-09 | 20:50 | Data | 0 | 31.339 | 28.781 | 219.785 | 7.62 | 206.196 | 2187.27 | 25.88 | 42.658 | 6.32 | 1.453 | 5.286 | 8911.05 | 2.586 | 98 | 78.4 | 1421 | 21.33 | 5792.2 | 3220 | 3178.6 | 4625.6 | 1205.6 | 0.67924 | 6.737
2024-12-09 | 20:50 | Data | 0 | 31.137 | 28.794 | 220.011 | 7.62 | 206.196 | 2187.27 | 25.88 | 42.658 | 6.32 | 1.447 | 5.305 | 8874.87 | 2.444 | 98 | 78.6 | 1422 | 21.37 | 5768.7 | 3238.7 | 3203.4 | 4656.1 | 1205.6 | 0.6814 | 6.752
2024-12-09 | 20:50 | Data | 0 | 31.366 | 28.754 | 220.056 | 7.62 | 206.196 | 2186.37 | 25.89 | 42.568 | 6.31 | 1.449 | 5.286 | 8874.87 | 2.552 | 98 | 78.5 | 1421 | 21.33 | 5768.7 | 3233.8 | 3197.4 | 4649.8 | 1205.6 | 0.68007 | 6.735
2024-12-09 | 20:50 | Data | 0 | 31.184 | 28.808 | 220.056 | 7.62 | 206.332 | 2189.08 | 25.89 | 42.658 | 6.32 | 1.454 | 5.288 | 8883.91 | 2.322 | 98.1 | 78.4 | 1423 | 21.33 | 5774.5 | 3245.5 | 3198.1 | 4656.6 | 1205.6 | 0.68267 | 6.742
2024-12-09 | 20:50 | Data | 0 | 31.366 | 28.808 | 219.83 | 7.62 | 206.151 | 2189.08 | 25.88 | 42.568 | 6.32 | 1.439 | 5.279 | 8870.35 | 2.538 | 98.1 | 78.6 | 1423 | 21.33 | 5765.7 | 3230 | 3184.8 | 4644.2 | 1205.6 | 0.67903 | 6.717
2024-12-09 | 20:50 | Data | 0 | 31.799 | 28.828 | 220.282 | 7.62 | 206.377 | 2189.08 | 25.88 | 42.658 | 6.32 | 1.439 | 5.279 | 8933.66 | 2.701 | 98.1 | 78.6 | 1423 | 21.28 | 5806.9 | 3246.6 | 3192.8 | 4657 | 1205.6 | 0.68098 | 6.718
2024-12-09 | 20:50 | Data | 0 | 31.562 | 28.612 | 219.92 | 7.62 | 206.332 | 2187.27 | 25.88 | 42.658 | 6.32 | 1.459 | 5.27 | 8920.09 | 2.586 | 98 | 78.3 | 1422 | 21.28 | 5798.1 | 3235.9 | 3200.9 | 4651 | 1205.6 | 0.67825 | 6.728
2024-12-09 | 20:50 | Data | 0 | 31.117 | 28.571 | 220.011 | 7.62 | 206.377 | 2186.37 | 25.89 | 42.658 | 6.32 | 1.455 | 5.307 | 8924.61 | 2.538 | 98 | 78.5 | 1422 | 21.33 | 5801 | 3243.3 | 3184.6 | 4637.2 | 1205.7 | 0.67947 | 6.763
2024-12-09 | 20:50 | Data | 0 | 31.724 | 28.936 | 220.011 | 7.62 | 206.241 | 2188.18 | 25.88 | 42.748 | 6.32 | 1.446 | 5.292 | 8920.09 | 2.545 | 98 | 78.5 | 1422 | 21.33 | 5798.1 | 3232 | 3191 | 4646.2 | 1205.7 | 0.67993 | 6.737
2024-12-09 | 20:50 | Data | 0 | 31.312 | 29.004 | 220.056 | 7.62 | 206.196 | 2189.08 | 25.89 | 42.658 | 6.32 | 1.45 | 5.285 | 8924.61 | 2.532 | 98.1 | 78.5 | 1423 | 21.28 | 5801 | 3245.6 | 3220.5 | 4672.2 | 1205.7 | 0.67924 | 6.735
2024-12-09 | 20:50 | Data | 0 | 31.67 | 28.612 | 219.92 | 7.62 | 206.241 | 2188.18 | 25.88 | 42.387 | 6.31 | 1.461 | 5.307 | 8929.14 | 2.809 | 98.1 | 78.4 | 1422 | 21.19 | 5803.9 | 3238.4 | 3204.7 | 4656.1 | 1205.7 | 0.67995 | 6.766
2024-12-09 | 20:51 | Data | 0 | 31.515 | 28.605 | 220.101 | 7.62 | 206.377 | 2186.37 | 25.89 | 42.387 | 6.32 | 1.457 | 5.307 | 8924.61 | 2.545 | 98.1 | 78.5 | 1420 | 21.24 | 5801 | 3244.6 | 3209.1 | 4663.2 | 1205.7 | 0.67972 | 6.764
2024-12-09 | 20:51 | Data | 0 | 31.393 | 28.97 | 220.101 | 7.62 | 206.332 | 2186.37 | 25.86 | 42.387 | 6.32 | 1.451 | 5.292 | 8902 | 2.451 | 98.1 | 78.5 | 1421 | 21.19 | 5786.3 | 3239.1 | 3185 | 4670.3 | 1205.7 | 0.67899 | 6.743
2024-12-09 | 20:51 | Data | 0 | 31.117 | 28.801 | 219.92 | 7.62 | 206.106 | 2187.27 | 25.89 | 42.387 | 6.32 | 1.45 | 5.28 | 8906.53 | 2.484 | 98.1 | 78.5 | 1422 | 21.19 | 5789.2 | 3254.6 | 3214.3 | 4675.6 | 1205.7 | 0.67964 | 6.73
2024-12-09 | 20:51 | Data | 0 | 31.11 | 28.578 | 219.966 | 7.62 | 206.196 | 2186.37 | 25.88 | 42.387 | 6.32 | 1.44 | 5.285 | 8897.48 | 2.728 | 98.1 | 78.6 | 1422 | 21.15 | 5783.4 | 3244.3 | 3206.5 | 4660.9 | 1205.7 | 0.68204 | 6.725
2024-12-09 | 20:51 | Data | 0 | 31.339 | 29.098 | 219.966 | 7.62 | 206.332 | 2186.37 | 25.89 | 42.387 | 6.33 | 1.434 | 5.27 | 8892.96 | 2.647 | 98.1 | 78.6 | 1420 | 21.19 | 5780.4 | 3225.3 | 3192.9 | 4654.3 | 1205.7 | 0.68077 | 6.705
2024-12-09 | 20:51 | Data | 0 | 31.258 | 28.598 | 219.875 | 7.62 | 206.332 | 2190.89 | 25.88 | 42.387 | 6.33 | 1.437 | 5.266 | 8892.96 | 2.349 | 98.1 | 78.6 | 1425 | 21.28 | 5780.4 | 3225.8 | 3215.4 | 4659.9 | 1205.7 | 0.67626 | 6.703
2024-12-09 | 20:51 | Data | 0 | 31.339 | 28.808 | 219.92 | 7.62 | 206.151 | 2186.37 | 25.88 | 42.297 | 6.32 | 1.43 | 5.297 | 8911.05 | 2.532 | 98.1 | 78.7 | 1421 | 21.19 | 5792.2 | 3247.1 | 3168.6 | 4639.8 | 1205.7 | 0.68346 | 6.727
2024-12-09 | 20:51 | Data | 0 | 31.346 | 29.193 | 220.101 | 7.62 | 206.332 | 2182.75 | 25.88 | 42.477 | 6.33 | 1.452 | 5.295 | 8911.05 | 2.471 | 98.1 | 78.5 | 1419 | 21.19 | 5792.2 | 3233.3 | 3169.6 | 4631.8 | 1205.7 | 0.68156 | 6.746
2024-12-09 | 20:51 | Data | 0 | 31.576 | 28.646 | 220.192 | 7.63 | 206.241 | 2180.95 | 25.88 | 42.477 | 6.32 | 1.447 | 5.312 | 8911.05 | 2.599 | 98.1 | 78.6 | 1418 | 21.24 | 5792.2 | 3234.7 | 3138.6 | 4612.9 | 1205.7 | 0.68615 | 6.758
2024-12-09 | 20:51 | Data | 0 | 31.508 | 29.226 | 220.056 | 7.62 | 206.332 | 2178.24 | 25.89 | 42.477 | 6.32 | 1.443 | 5.307 | 8915.57 | 2.538 | 98.1 | 78.6 | 1416 | 21.24 | 5795.1 | 3243 | 3171.5 | 4639.7 | 1205.7 | 0.6832 | 6.752
2024-12-09 | 20:51 | Data | 0 | 31.117 | 28.578 | 220.011 | 7.62 | 206.151 | 2172.81 | 25.88 | 42.387 | 6.32 | 1.449 | 5.312 | 8933.66 | 2.525 | 98 | 78.6 | 1412 | 21.19 | 5806.9 | 3250.8 | 3163.7 | 4637.1 | 1205.7 | 0.68457 | 6.761
2024-12-09 | 20:51 | Data | 0 | 31.117 | 28.693 | 219.875 | 7.62 | 206.106 | 2181.85 | 25.89 | 42.387 | 6.32 | 1.448 | 5.295 | 8938.18 | 2.545 | 98.1 | 78.5 | 1418 | 21.19 | 5809.8 | 3239.3 | 3179.3 | 4643.9 | 1205.7 | 0.6814 | 6.744
2024-12-09 | 20:51 | Data | 0 | 31.447 | 28.632 | 219.92 | 7.62 | 206.241 | 2180.04 | 25.89 | 42.387 | 6.33 | 1.453 | 5.266 | 8924.61 | 2.491 | 98.1 | 78.4 | 1418 | 21.19 | 5801 | 3235.2 | 3186.6 | 4643.4 | 1205.7 | 0.68094 | 6.719
2024-12-09 | 20:51 | Data | 0 | 31.123 | 28.693 | 220.011 | 7.63 | 206.151 | 2176.43 | 25.88 | 42.297 | 6.32 | 1.447 | 5.267 | 8933.66 | 2.417 | 98.1 | 78.4 | 1415 | 21.15 | 5806.9 | 3239.1 | 3179 | 4642.5 | 1205.7 | 0.68157 | 6.714
2024-12-09 | 20:51 | Data | 0 | 31.285 | 28.389 | 219.92 | 7.62 | 206.241 | 2177.33 | 25.88 | 42.387 | 6.32 | 1.457 | 5.277 | 8911.05 | 2.836 | 98.1 | 78.4 | 1415 | 21.24 | 5792.2 | 3236.4 | 3186.1 | 4644.2 | 1205.7 | 0.68124 | 6.735
2024-12-09 | 20:51 | Data | 0 | 31.137 | 28.949 | 219.875 | 7.62 | 206.196 | 2179.14 | 25.89 | 42.297 | 6.33 | 1.452 | 5.284 | 8902 | 2.653 | 98.1 | 78.4 | 1416 | 21.19 | 5786.3 | 3237.7 | 3169.5 | 4630.8 | 1205.7 | 0.68294 | 6.736
2024-12-09 | 20:51 | Data | 0 | 31.042 | 28.571 | 220.101 | 7.62 | 206.332 | 2180.04 | 25.88 | 42.477 | 6.32 | 1.455 | 5.277 | 8906.53 | 2.376 | 98.1 | 78.4 | 1417 | 21.19 | 5789.2 | 3243.7 | 3181.4 | 4646 | 1205.7 | 0.68172 | 6.732
2024-12-09 | 20:52 | Data | 0 | 31.697 | 28.828 | 220.011 | 7.62 | 206.332 | 2180.04 | 25.89 | 42.297 | 6.32 | 1.452 | 5.28 | 8924.61 | 2.444 | 98.1 | 78.4 | 1417 | 21.15 | 5801 | 3224.9 | 3184.4 | 4633.4 | 1205.7 | 0.68026 | 6.732
2024-12-09 | 20:52 | Data | 0 | 31.11 | 29.01 | 220.011 | 7.62 | 206.196 | 2180.95 | 25.88 | 42.387 | 6.32 | 1.435 | 5.279 | 8906.53 | 2.295 | 98.1 | 78.6 | 1418 | 21.24 | 5789.2 | 3237.9 | 3183.1 | 4642.4 | 1205.7 | 0.68216 | 6.713
2024-12-09 | 20:52 | Data | 0 | 31.461 | 29.28 | 220.327 | 7.62 | 206.377 | 2180.95 | 25.88 | 42.387 | 6.32 | 1.443 | 5.284 | 8911.05 | 2.444 | 98.1 | 78.5 | 1417 | 21.19 | 5792.2 | 3225.2 | 3173 | 4625.1 | 1205.7 | 0.68267 | 6.728
2024-12-09 | 20:52 | Data | 0 | 31.225 | 28.781 | 220.418 | 7.62 | 206.648 | 2180.04 | 25.88 | 42.387 | 6.31 | 1.449 | 5.231 | 8897.48 | 2.545 | 98.1 | 78.3 | 1418 | 21.15 | 5783.4 | 3238.4 | 3183.6 | 4641.6 | 1205.7 | 0.68365 | 6.68
2024-12-09 | 20:52 | Data | 0 | 31.792 | 28.868 | 220.689 | 7.62 | 206.874 | 2180.95 | 25.89 | 42.387 | 6.32 | 1.45 | 5.275 | 8897.48 | 2.545 | 98.1 | 78.4 | 1418 | 21.19 | 5783.4 | 3244.3 | 3172.3 | 4639.2 | 1205.7 | 0.68309 | 6.726
2024-12-09 | 20:52 | Data | 0 | 31.11 | 28.949 | 220.508 | 7.62 | 206.693 | 2180.04 | 25.89 | 42.477 | 6.32 | 1.448 | 5.288 | 8924.61 | 2.734 | 98.1 | 78.5 | 1417 | 21.24 | 5801 | 3245 | 3156.2 | 4627.5 | 1205.7 | 0.68454 | 6.736
2024-12-09 | 20:52 | Data | 0 | 31.306 | 28.693 | 220.599 | 7.62 | 206.784 | 2180.95 | 25.89 | 42.387 | 6.32 | 1.448 | 5.268 | 8978.88 | 2.39 | 98.1 | 78.4 | 1418 | 21.19 | 5836.3 | 3245.4 | 3153.4 | 4623.7 | 1205.7 | 0.68603 | 6.717
2024-12-09 | 20:52 | Data | 0 | 31.758 | 29.091 | 220.689 | 7.62 | 206.919 | 2180.95 | 25.88 | 42.387 | 6.32 | 1.448 | 5.282 | 8965.31 | 2.647 | 98.1 | 78.5 | 1418 | 21.19 | 5827.5 | 3235.7 | 3199.1 | 4653.3 | 1205.7 | 0.67999 | 6.729
2024-12-09 | 20:52 | Data | 0 | 31.549 | 28.821 | 220.599 | 7.62 | 206.738 | 2180.95 | 25.89 | 42.297 | 6.32 | 1.443 | 5.309 | 8965.31 | 2.545 | 98.1 | 78.6 | 1418 | 21.15 | 5827.5 | 3260.3 | 3226.6 | 4688.8 | 1205.7 | 0.67931 | 6.752
2024-12-09 | 20:52 | Data | 0 | 31.454 | 28.605 | 220.463 | 7.62 | 206.693 | 2187.27 | 25.88 | 42.387 | 6.31 | 1.448 | 5.311 | 8965.31 | 2.491 | 98.1 | 78.6 | 1420 | 21.24 | 5827.5 | 3252 | 3224.8 | 4679.2 | 1205.7 | 0.67906 | 6.76
2024-12-09 | 20:52 | Data | 0 | 31.117 | 28.693 | 220.418 | 7.62 | 206.648 | 2180.04 | 25.89 | 42.387 | 6.32 | 1.45 | 5.303 | 8938.18 | 2.532 | 98.1 | 78.5 | 1417 | 21.19 | 5809.8 | 3258.1 | 3182.8 | 4651.8 | 1205.7 | 0.68331 | 6.752
2024-12-09 | 20:52 | Data | 0 | 31.292 | 28.592 | 220.689 | 7.62 | 206.738 | 2181.85 | 25.88 | 42.387 | 6.32 | 1.453 | 5.285 | 8933.66 | 2.545 | 98.1 | 78.4 | 1418 | 21.19 | 5806.9 | 3257.7 | 3191.8 | 4663.8 | 1205.8 | 0.68296 | 6.739
2024-12-09 | 20:52 | Data | 0 | 31.765 | 28.862 | 220.599 | 7.62 | 206.829 | 2181.85 | 25.89 | 42.387 | 6.31 | 1.462 | 5.287 | 8938.18 | 2.674 | 98.1 | 78.4 | 1418 | 21.19 | 5809.8 | 3248.3 | 3181.5 | 4650.3 | 1205.8 | 0.68236 | 6.748
2024-12-09 | 20:52 | Data | 0 | 31.312 | 28.598 | 220.735 | 7.62 | 206.919 | 2183.66 | 25.88 | 42.387 | 6.32 | 1.455 | 5.27 | 8924.61 | 2.363 | 98.1 | 78.4 | 1419 | 21.15 | 5801 | 3253.2 | 3175.3 | 4649 | 1205.8 | 0.68345 | 6.727
2024-12-09 | 20:52 | Data | 0 | 31.258 | 28.808 | 220.689 | 7.62 | 206.738 | 2181.85 | 25.89 | 42.387 | 6.32 | 1.457 | 5.277 | 8911.05 | 2.491 | 98.1 | 78.4 | 1418 | 21.24 | 5792.2 | 3251.9 | 3194.5 | 4658.6 | 1205.8 | 0.68227 | 6.735
2024-12-09 | 20:52 | Data | 0 | 31.272 | 28.801 | 220.463 | 7.62 | 206.784 | 2182.75 | 25.89 | 42.297 | 6.32 | 1.454 | 5.305 | 8911.05 | 2.525 | 98.1 | 78.5 | 1419 | 21.24 | 5792.2 | 3255.6 | 3192.9 | 4662 | 1205.8 | 0.68181 | 6.759
2024-12-09 | 20:52 | Data | 0 | 31.731 | 28.922 | 220.599 | 7.62 | 206.829 | 2183.66 | 25.88 | 42.387 | 6.32 | 1.445 | 5.287 | 8920.09 | 2.559 | 98.1 | 78.5 | 1418 | 21.19 | 5798.1 | 3248.4 | 3191 | 4655.9 | 1205.8 | 0.68174 | 6.734
2024-12-09 | 20:52 | Data | 0 | 31.333 | 28.781 | 220.508 | 7.62 | 206.829 | 2180.95 | 25.89 | 42.477 | 6.32 | 1.46 | 5.319 | 8920.09 | 2.586 | 98.1 | 78.5 | 1418 | 21.24 | 5798.1 | 3243.2 | 3186 | 4648.6 | 1205.8 | 0.68136 | 6.777
2024-12-09 | 20:53 | Data | 0 | 31.454 | 28.835 | 220.599 | 7.62 | 206.738 | 2180.95 | 25.89 | 42.387 | 6.32 | 1.46 | 5.323 | 8924.61 | 2.586 | 98.1 | 78.5 | 1418 | 21.24 | 5801 | 3245 | 3158 | 4631.2 | 1205.8 | 0.68424 | 6.782
2024-12-09 | 20:53 | Data | 0 | 31.67 | 28.706 | 220.78 | 7.62 | 206.829 | 2180.95 | 25.88 | 42.387 | 6.32 | 1.455 | 5.309 | 8924.61 | 2.592 | 98.1 | 78.5 | 1417 | 21.24 | 5801 | 3243.8 | 3188.4 | 4652.2 | 1205.8 | 0.68115 | 6.762
2024-12-09 | 20:53 | Data | 0 | 31.339 | 28.598 | 220.599 | 7.62 | 206.784 | 2180.95 | 25.89 | 42.387 | 6.32 | 1.454 | 5.278 | 8888.44 | 2.538 | 98.1 | 78.4 | 1418 | 21.15 | 5777.5 | 3255.6 | 3168.2 | 4643.9 | 1205.8 | 0.68592 | 6.732
2024-12-09 | 20:53 | Data | 0 | 31.555 | 28.652 | 220.78 | 7.62 | 206.919 | 2180.04 | 25.89 | 42.387 | 6.32 | 1.448 | 5.277 | 8897.48 | 2.917 | 98.1 | 78.5 | 1418 | 21.19 | 5783.4 | 3246.6 | 3189.2 | 4649.2 | 1205.8 | 0.68312 | 6.725
2024-12-09 | 20:53 | Data | 0 | 31.117 | 28.673 | 220.418 | 7.62 | 206.784 | 2180.04 | 25.89 | 42.297 | 6.32 | 1.453 | 5.279 | 9064.8 | 2.592 | 98.1 | 78.4 | 1418 | 21.15 | 5892.1 | 3244.7 | 3171.9 | 4640.9 | 1205.8 | 0.68357 | 6.733
2024-12-09 | 20:53 | Data | 0 | 31.333 | 29.004 | 220.644 | 7.62 | 206.693 | 2177.33 | 25.88 | 42.387 | 6.32 | 1.453 | 5.287 | 9064.8 | 2.43 | 98.1 | 78.4 | 1415 | 21.19 | 5892.1 | 3230 | 3185.4 | 4644.7 | 1205.8 | 0.68 | 6.738
2024-12-09 | 20:53 | Data | 0 | 31.691 | 28.693 | 220.78 | 7.62 | 206.738 | 2182.75 | 25.88 | 42.387 | 6.32 | 1.45 | 5.314 | 9091.94 | 2.322 | 98.1 | 78.6 | 1417 | 21.19 | 5909.8 | 3230 | 3210.2 | 4657.6 | 1205.8 | 0.6776 | 6.765
2024-12-09 | 20:53 | Data | 0 | 31.117 | 28.598 | 220.508 | 7.62 | 206.738 | 2179.14 | 25.89 | 42.297 | 6.33 | 1.452 | 5.307 | 9100.98 | 2.511 | 98.1 | 78.5 | 1416 | 21.19 | 5915.6 | 3238.9 | 3215.3 | 4667.5 | 1205.8 | 0.67826 | 6.759
2024-12-09 | 20:53 | Data | 0 | 31.137 | 28.578 | 220.599 | 7.62 | 206.784 | 2182.75 | 25.89 | 42.477 | 6.32 | 1.443 | 5.304 | 8897.48 | 2.532 | 98.1 | 78.6 | 1419 | 21.24 | 5783.4 | 3228.6 | 3236.4 | 4684.8 | 1205.8 | 0.67621 | 6.747
2024-12-09 | 20:53 | Data | 0 | 31.258 | 28.578 | 220.599 | 7.62 | 206.693 | 2186.37 | 25.88 | 42.206 | 6.32 | 1.452 | 5.29 | 8879.39 | 2.538 | 98.1 | 78.5 | 1422 | 21.15 | 5771.6 | 3248 | 3225.1 | 4680.8 | 1205.8 | 0.67754 | 6.746
2024-12-09 | 20:53 | Data | 0 | 31.285 | 29.179 | 220.508 | 7.62 | 206.738 | 2188.18 | 25.89 | 42.477 | 6.32 | 1.444 | 5.288 | 8883.91 | 2.734 | 98.1 | 78.6 | 1421 | 21.19 | 5774.5 | 3217 | 3233.6 | 4668.6 | 1205.8 | 0.67326 | 6.73
2024-12-09 | 20:53 | Data | 0 | 31.225 | 28.578 | 220.599 | 7.62 | 206.784 | 2186.37 | 25.88 | 42.297 | 6.32 | 1.45 | 5.282 | 8883.91 | 2.687 | 98.1 | 78.5 | 1421 | 21.19 | 5774.5 | 3255.2 | 3184.1 | 4654.8 | 1205.8 | 0.68271 | 6.732
2024-12-09 | 20:53 | Data | 0 | 31.724 | 29.091 | 220.78 | 7.62 | 206.784 | 2186.37 | 25.89 | 42.297 | 6.32 | 1.455 | 5.284 | 8933.66 | 2.674 | 98.1 | 78.4 | 1421 | 21.15 | 5806.9 | 3251.4 | 3210.2 | 4668.4 | 1205.8 | 0.68175 | 6.738
2024-12-09 | 20:53 | Data | 0 | 31.778 | 28.922 | 220.961 | 7.62 | 206.829 | 2189.08 | 25.89 | 42.387 | 6.32 | 1.46 | 5.295 | 8956.27 | 2.674 | 98.1 | 78.4 | 1422 | 21.19 | 5821.6 | 3248.1 | 3181.1 | 4647.8 | 1205.8 | 0.683 | 6.754
2024-12-09 | 20:53 | Data | 0 | 31.677 | 28.808 | 220.644 | 7.62 | 206.784 | 2189.08 | 25.88 | 42.387 | 6.32 | 1.461 | 5.311 | 8951.75 | 2.255 | 98.1 | 78.4 | 1423 | 21.24 | 5818.6 | 3256.2 | 3158.9 | 4639.1 | 1205.8 | 0.68575 | 6.772
2024-12-09 | 20:53 | Data | 0 | 31.454 | 29.085 | 220.599 | 7.62 | 206.784 | 2190.89 | 25.88 | 42.387 | 6.32 | 1.452 | 5.305 | 8951.75 | 2.424 | 98.1 | 78.5 | 1423 | 21.19 | 5818.6 | 3271.6 | 3182.4 | 4662.3 | 1205.8 | 0.68606 | 6.757
2024-12-09 | 20:53 | Data | 0 | 31.117 | 28.801 | 220.463 | 7.62 | 206.738 | 2189.99 | 25.88 | 42.387 | 6.32 | 1.449 | 5.304 | 8883.91 | 2.336 | 98.1 | 78.5 | 1423 | 21.24 | 5774.5 | 3236.8 | 3165 | 4632.6 | 1205.8 | 0.68527 | 6.754
2024-12-09 | 20:54 | Data | 0 | 31.393 | 28.693 | 220.508 | 7.62 | 206.829 | 2194.5 | 25.89 | 42.387 | 6.32 | 1.45 | 5.289 | 8902 | 2.559 | 98.1 | 78.5 | 1426 | 21.19 | 5786.3 | 3244.3 | 3186.1 | 4651 | 1205.8 | 0.68091 | 6.739
2024-12-09 | 20:54 | Data | 0 | 31.339 | 28.619 | 220.373 | 7.62 | 206.693 | 2194.5 | 25.89 | 42.477 | 6.32 | 1.446 | 5.317 | 8902 | 2.674 | 98.1 | 78.6 | 1426 | 21.19 | 5786.3 | 3248.6 | 3200.5 | 4661.8 | 1205.8 | 0.68095 | 6.763
2024-12-09 | 20:54 | Data | 0 | 31.454 | 29.031 | 220.644 | 7.62 | 206.829 | 2194.5 | 25.89 | 42.387 | 6.32 | 1.457 | 5.314 | 8897.48 | 2.626 | 98.1 | 78.5 | 1427 | 21.15 | 5783.4 | 3243.2 | 3202 | 4656.5 | 1205.8 | 0.68086 | 6.769
2024-12-09 | 20:54 | Data | 0 | 31.562 | 29.037 | 220.689 | 7.62 | 206.829 | 2196.31 | 25.88 | 42.387 | 6.32 | 1.452 | 5.317 | 8906.53 | 2.538 | 98.1 | 78.6 | 1428 | 21.19 | 5789.2 | 3238.1 | 3189.7 | 4648.4 | 1205.8 | 0.68187 | 6.767
2024-12-09 | 20:54 | Data | 0 | 31.326 | 28.977 | 220.508 | 7.62 | 206.784 | 2199.93 | 25.89 | 42.387 | 6.32 | 1.46 | 5.306 | 8920.09 | 2.586 | 98.1 | 78.4 | 1430 | 21.19 | 5798.1 | 3239.1 | 3182.4 | 4645.7 | 1205.8 | 0.68155 | 6.765
2024-12-09 | 20:54 | Data | 0 | 31.569 | 29.125 | 220.689 | 7.63 | 206.874 | 2203.54 | 25.88 | 42.387 | 6.32 | 1.46 | 5.327 | 8929.14 | 2.565 | 98.1 | 78.5 | 1431 | 21.24 | 5803.9 | 3245 | 3198.9 | 4658.2 | 1205.8 | 0.68063 | 6.788
2024-12-09 | 20:54 | Data | 0 | 31.616 | 28.666 | 220.599 | 7.62 | 206.738 | 2201.74 | 25.89 | 42.477 | 6.32 | 1.45 | 5.311 | 8956.27 | 2.613 | 98.1 | 78.5 | 1431 | 21.24 | 5821.6 | 3248.4 | 3212.4 | 4662.4 | 1205.8 | 0.68109 | 6.761
2024-12-09 | 20:54 | Data | 0 | 31.339 | 29.118 | 220.599 | 7.62 | 206.874 | 2203.54 | 25.89 | 42.297 | 6.32 | 1.452 | 5.294 | 8956.27 | 2.545 | 98.1 | 78.5 | 1432 | 21.15 | 5821.6 | 3251.4 | 3216.6 | 4674.3 | 1205.8 | 0.68007 | 6.746
2024-12-09 | 20:54 | Data | 0 | 31.508 | 29.031 | 220.644 | 7.62 | 206.738 | 2199.93 | 25.89 | 42.387 | 6.33 | 1.45 | 5.287 | 8969.84 | 2.538 | 98.1 | 78.5 | 1430 | 21.19 | 5830.4 | 3271.3 | 3217.6 | 4689.2 | 1205.8 | 0.68134 | 6.736
2024-12-09 | 20:54 | Data | 0 | 31.623 | 28.835 | 220.78 | 7.62 | 206.919 | 2192.7 | 25.88 | 42.297 | 6.32 | 1.451 | 5.303 | 8969.84 | 2.336 | 98.1 | 78.5 | 1425 | 21.24 | 5830.4 | 3239.7 | 3202 | 4657 | 1205.9 | 0.67977 | 6.755
2024-12-09 | 20:54 | Data | 0 | 31.123 | 28.578 | 220.463 | 7.62 | 206.738 | 2198.12 | 25.86 | 42.477 | 6.32 | 1.445 | 5.289 | 8947.23 | 2.511 | 98.1 | 78.5 | 1428 | 21.24 | 5815.7 | 3261.7 | 3207.1 | 4675.5 | 1205.9 | 0.68137 | 6.735
2024-12-09 | 20:54 | Data | 0 | 31.333 | 28.585 | 220.418 | 7.62 | 206.738 | 2198.12 | 25.88 | 42.297 | 6.32 | 1.45 | 5.298 | 8965.31 | 2.741 | 98.1 | 78.5 | 1429 | 21.19 | 5827.5 | 3235.2 | 3217.4 | 4662.1 | 1205.9 | 0.67695 | 6.744
2024-12-09 | 20:54 | Data | 0 | 31.555 | 28.835 | 220.599 | 7.62 | 206.784 | 2189.99 | 25.88 | 42.387 | 6.32 | 1.45 | 5.297 | 8974.36 | 2.701 | 98.1 | 78.5 | 1423 | 21.24 | 5833.3 | 3249 | 3230.2 | 4679.6 | 1205.9 | 0.6789 | 6.747
2024-12-09 | 20:54 | Data | 0 | 31.562 | 28.727 | 220.508 | 7.62 | 206.874 | 2189.08 | 25.89 | 42.477 | 6.32 | 1.447 | 5.275 | 9006.01 | 2.849 | 98.1 | 78.5 | 1422 | 21.19 | 5853.9 | 3249.7 | 3249.9 | 4693.9 | 1205.9 | 0.67662 | 6.722
2024-12-09 | 20:54 | Data | 0 | 31.569 | 28.821 | 220.689 | 7.62 | 206.829 | 2195.41 | 25.88 | 42.387 | 6.32 | 1.443 | 5.307 | 8951.75 | 2.707 | 98.1 | 78.6 | 1426 | 21.19 | 5818.6 | 3246.3 | 3241.8 | 4689.8 | 1205.9 | 0.67624 | 6.749
2024-12-09 | 20:54 | Data | 0 | 31.312 | 28.808 | 220.644 | 7.63 | 206.874 | 2194.5 | 25.88 | 42.387 | 6.32 | 1.443 | 5.278 | 8951.75 | 2.701 | 98.1 | 78.5 | 1426 | 21.19 | 5818.6 | 3258.1 | 3254.7 | 4704.6 | 1205.9 | 0.6763 | 6.72
2024-12-09 | 20:54 | Data | 0 | 31.157 | 29.064 | 220.916 | 7.62 | 206.964 | 2194.5 | 25.89 | 42.297 | 6.33 | 1.451 | 5.248 | 8938.18 | 2.363 | 98.1 | 78.3 | 1426 | 21.24 | 5809.8 | 3236.4 | 3242.4 | 4681.9 | 1205.9 | 0.67527 | 6.7
2024-12-09 | 20:54 | Data | 0 | 31.333 | 28.808 | 220.87 | 7.62 | 207.055 | 2194.5 | 25.86 | 42.387 | 6.32 | 1.448 | 5.279 | 8947.23 | 2.532 | 98.1 | 78.5 | 1426 | 21.19 | 5815.7 | 3255.5 | 3213.9 | 4675.1 | 1205.9 | 0.68054 | 6.729
2024-12-09 | 20:55 | Data | 0 | 31.461 | 28.578 | 220.689 | 7.62 | 207.01 | 2193.6 | 25.88 | 42.477 | 6.32 | 1.451 | 5.294 | 8960.79 | 2.545 | 98.1 | 78.5 | 1426 | 21.24 | 5824.5 | 3250.6 | 3209 | 4670.6 | 1205.9 | 0.67953 | 6.744
2024-12-09 | 20:55 | Data | 0 | 31.211 | 28.808 | 220.87 | 7.62 | 206.964 | 2195.41 | 25.89 | 42.206 | 6.32 | 1.453 | 5.299 | 8960.79 | 2.316 | 98.1 | 78.5 | 1426 | 21.15 | 5824.5 | 3254.1 | 3219 | 4681.7 | 1205.9 | 0.67856 | 6.754
2024-12-09 | 20:55 | Data | 0 | 31.454 | 29.01 | 220.916 | 7.62 | 207.01 | 2192.7 | 25.89 | 42.387 | 6.32 | 1.451 | 5.278 | 8956.27 | 2.565 | 98.1 | 78.4 | 1426 | 21.19 | 5821.6 | 3293.2 | 3215.1 | 4701.4 | 1205.9 | 0.68254 | 6.728
2024-12-09 | 20:55 | Data | 0 | 31.562 | 29.064 | 220.825 | 7.62 | 207.19 | 2194.5 | 25.89 | 42.387 | 6.33 | 1.451 | 5.298 | 8951.75 | 2.43 | 98.1 | 78.5 | 1427 | 21.19 | 5818.6 | 3257.6 | 3201 | 4668.2 | 1205.9 | 0.68112 | 6.749
2024-12-09 | 20:55 | Data | 0 | 31.42 | 28.808 | 220.78 | 7.62 | 207.01 | 2193.6 | 25.88 | 42.387 | 6.32 | 1.452 | 5.32 | 8933.66 | 2.322 | 98.1 | 78.6 | 1425 | 21.15 | 5806.9 | 3269.9 | 3237.1 | 4700.4 | 1205.9 | 0.6811 | 6.771
2024-12-09 | 20:55 | Data | 0 | 31.697 | 28.814 | 220.825 | 7.62 | 207.01 | 2192.7 | 25.88 | 42.477 | 6.32 | 1.453 | 5.293 | 8938.18 | 2.579 | 98.1 | 78.5 | 1425 | 21.24 | 5809.8 | 3274.1 | 3202.9 | 4685.9 | 1205.9 | 0.68126 | 6.746
2024-12-09 | 20:55 | Data | 0 | 31.339 | 28.706 | 220.735 | 7.62 | 207.01 | 2189.99 | 25.89 | 42.477 | 6.32 | 1.44 | 5.298 | 8951.75 | 2.707 | 98.1 | 78.6 | 1423 | 21.19 | 5818.6 | 3287.2 | 3242.6 | 4716.6 | 1205.9 | 0.68105 | 6.739
2024-12-09 | 20:55 | Data | 0 | 31.015 | 28.571 | 220.735 | 7.62 | 207.01 | 2186.37 | 25.89 | 42.387 | 6.32 | 1.437 | 5.276 | 8929.14 | 2.511 | 98.1 | 78.6 | 1421 | 21.19 | 5803.9 | 3250.8 | 3225.6 | 4684.1 | 1205.9 | 0.67739 | 6.714
2024-12-09 | 20:55 | Data | 0 | 31.751 | 28.875 | 220.87 | 7.62 | 207.01 | 2183.66 | 25.89 | 42.387 | 6.32 | 1.435 | 5.29 | 8924.61 | 2.633 | 98.1 | 78.6 | 1419 | 21.19 | 5801 | 3248 | 3222.4 | 4683.1 | 1205.9 | 0.67628 | 6.727
2024-12-09 | 20:55 | Data | 0 | 31.414 | 28.922 | 220.78 | 7.62 | 207.01 | 2183.66 | 25.88 | 42.387 | 6.32 | 1.448 | 5.303 | 8906.53 | 2.545 | 98.1 | 78.5 | 1419 | 21.19 | 5789.2 | 3267.7 | 3242.1 | 4713.2 | 1205.9 | 0.67716 | 6.752
2024-12-09 | 20:55 | Data | 0 | 31.495 | 29.037 | 221.051 | 7.62 | 207.055 | 2182.75 | 25.89 | 42.387 | 6.32 | 1.462 | 5.292 | 8911.05 | 2.728 | 98.1 | 78.3 | 1419 | 21.19 | 5792.2 | 3271.5 | 3229.7 | 4705 | 1205.9 | 0.67985 | 6.755
2024-12-09 | 20:55 | Data | 0 | 31.225 | 28.571 | 220.644 | 7.62 | 206.964 | 2187.27 | 25.88 | 42.387 | 6.32 | 1.453 | 5.322 | 8902 | 2.559 | 98.1 | 78.5 | 1422 | 21.24 | 5786.3 | 3266.4 | 3221.6 | 4692.8 | 1205.9 | 0.67952 | 6.775
2024-12-09 | 20:55 | Data | 0 | 31.555 | 28.922 | 220.87 | 7.62 | 207.055 | 2186.37 | 25.88 | 42.387 | 6.32 | 1.455 | 5.299 | 8924.61 | 2.619 | 98.1 | 78.5 | 1422 | 21.19 | 5801 | 3295.7 | 3226.3 | 4725.8 | 1205.9 | 0.68515 | 6.755
2024-12-09 | 20:55 | Data | 0 | 31.231 | 28.571 | 220.825 | 7.62 | 206.964 | 2186.37 | 25.88 | 42.387 | 6.32 | 1.452 | 5.313 | 8906.53 | 2.545 | 98.1 | 78.5 | 1422 | 21.24 | 5789.2 | 3299 | 3215.3 | 4711.5 | 1205.9 | 0.68511 | 6.766
2024-12-09 | 20:55 | Data | 0 | 31.164 | 28.571 | 220.78 | 7.62 | 206.919 | 2188.18 | 25.88 | 42.387 | 6.32 | 1.457 | 5.307 | 8897.48 | 2.565 | 98.1 | 78.5 | 1423 | 21.19 | 5783.4 | 3274.8 | 3216.7 | 4695.7 | 1205.9 | 0.68083 | 6.764
2024-12-09 | 20:55 | Data | 0 | 31.117 | 28.598 | 220.825 | 7.62 | 206.964 | 2191.79 | 25.89 | 42.477 | 6.32 | 1.457 | 5.308 | 8897.48 | 2.478 | 98.1 | 78.5 | 1425 | 21.19 | 5783.4 | 3284.8 | 3223.1 | 4704.2 | 1205.9 | 0.68211 | 6.765
2024-12-09 | 20:55 | Data | 0 | 31.393 | 29.01 | 220.961 | 7.62 | 207.01 | 2189.99 | 25.88 | 42.297 | 6.32 | 1.454 | 5.323 | 8911.05 | 2.356 | 98.1 | 78.5 | 1423 | 21.15 | 5792.2 | 3282.7 | 3234.7 | 4714.8 | 1205.9 | 0.6807 | 6.777
2024-12-09 | 20:55 | Data | 0 | 31.664 | 28.922 | 220.825 | 7.62 | 206.964 | 2189.08 | 25.89 | 42.477 | 6.33 | 1.453 | 5.327 | 8906.53 | 2.606 | 98.1 | 78.6 | 1423 | 21.19 | 5789.2 | 3273.7 | 3218.2 | 4696.1 | 1205.9 | 0.68075 | 6.778
2024-12-09 | 20:56 | Data | 0 | 31.339 | 28.571 | 220.689 | 7.62 | 206.919 | 2189.99 | 25.89 | 42.387 | 6.31 | 1.452 | 5.284 | 8911.05 | 2.761 | 98.1 | 78.4 | 1423 | 21.19 | 5792.2 | 3295.2 | 3237.1 | 4720.2 | 1205.9 | 0.68259 | 6.735
2024-12-09 | 20:56 | Data | 0 | 31.13 | 28.895 | 220.78 | 7.62 | 207.01 | 2186.37 | 25.88 | 42.387 | 6.32 | 1.448 | 5.27 | 8924.61 | 2.424 | 98.1 | 78.4 | 1421 | 21.19 | 5801 | 3306.1 | 3226.6 | 4724.2 | 1205.9 | 0.68394 | 6.717
2024-12-09 | 20:56 | Data | 0 | 31.339 | 28.781 | 220.78 | 7.62 | 206.919 | 2182.75 | 25.89 | 42.297 | 6.32 | 1.442 | 5.267 | 8915.57 | 2.64 | 98.1 | 78.5 | 1419 | 21.15 | 5795.1 | 3297.2 | 3188.9 | 4687.2 | 1205.9 | 0.68707 | 6.708
2024-12-09 | 20:56 | Data | 0 | 31.501 | 28.916 | 220.87 | 7.62 | 207.055 | 2180.95 | 25.88 | 42.387 | 6.32 | 1.448 | 5.282 | 8911.05 | 2.647 | 98.1 | 78.5 | 1417 | 21.19 | 5792.2 | 3283.8 | 3221.5 | 4704 | 1205.9 | 0.68292 | 6.731
2024-12-09 | 20:56 | Data | 0 | 31.225 | 28.808 | 220.689 | 7.62 | 206.919 | 2180.04 | 25.88 | 42.387 | 6.32 | 1.452 | 5.336 | 8911.05 | 2.484 | 98.1 | 78.6 | 1418 | 21.19 | 5792.2 | 3281.7 | 3201 | 4689.6 | 1205.9 | 0.68394 | 6.788
2024-12-09 | 20:56 | Data | 0 | 31.366 | 28.754 | 220.689 | 7.62 | 207.01 | 2180.95 | 25.86 | 42.297 | 6.31 | 1.443 | 5.33 | 8902 | 2.775 | 98.1 | 78.7 | 1418 | 21.19 | 5786.3 | 3306.7 | 3200.7 | 4705.8 | 1205.9 | 0.6845 | 6.774
2024-12-09 | 20:56 | Data | 0 | 31.137 | 28.598 | 220.735 | 7.63 | 206.919 | 2177.33 | 25.88 | 42.297 | 6.32 | 1.441 | 5.316 | 8911.05 | 2.444 | 98.1 | 78.7 | 1416 | 21.1 | 5792.2 | 3284.4 | 3194.5 | 4682.5 | 1206 | 0.68549 | 6.755
2024-12-09 | 20:56 | Data | 0 | 31.117 | 28.693 | 220.78 | 7.62 | 206.964 | 2181.85 | 25.89 | 42.387 | 6.32 | 1.45 | 5.302 | 8906.53 | 2.545 | 98.1 | 78.5 | 1418 | 21.19 | 5789.2 | 3271.5 | 3230 | 4706.7 | 1206 | 0.67881 | 6.751
2024-12-09 | 20:56 | Data | 0 | 31.447 | 28.605 | 220.825 | 7.62 | 207.01 | 2180.95 | 25.86 | 42.387 | 6.33 | 1.457 | 5.3 | 8915.57 | 2.599 | 98.1 | 78.5 | 1418 | 21.15 | 5795.1 | 3274.7 | 3237.9 | 4708.8 | 1206 | 0.67939 | 6.756
2024-12-09 | 20:56 | Data | 0 | 31.495 | 29.031 | 220.825 | 7.62 | 207.1 | 2180.04 | 25.89 | 42.387 | 6.32 | 1.451 | 5.288 | 8920.09 | 2.734 | 98.1 | 78.5 | 1416 | 21.19 | 5798.1 | 3263 | 3246.5 | 4701.1 | 1206 | 0.67876 | 6.738
2024-12-09 | 20:56 | Data | 0 | 31.238 | 28.754 | 220.87 | 7.62 | 206.919 | 2180.95 | 25.88 | 42.387 | 6.32 | 1.45 | 5.267 | 8911.05 | 2.444 | 98.1 | 78.4 | 1418 | 21.15 | 5792.2 | 3205.3 | 3202.8 | 4630.6 | 1206 | 0.6752 | 6.717
2024-12-09 | 20:56 | Data | 0 | 31.339 | 28.585 | 220.735 | 7.62 | 207.01 | 2178.24 | 25.88 | 42.477 | 6.33 | 1.443 | 5.301 | 8920.09 | 2.707 | 98.1 | 78.6 | 1416 | 21.19 | 5798.1 | 3194.5 | 3200.3 | 4624 | 1206 | 0.67606 | 6.745
2024-12-09 | 20:56 | Data | 0 | 31.339 | 28.578 | 220.735 | 7.62 | 206.919 | 2179.14 | 25.89 | 42.387 | 6.32 | 1.449 | 5.313 | 8924.61 | 2.755 | 98 | 78.6 | 1416 | 21.19 | 5801 | 3179.7 | 3179.9 | 4603.8 | 1206 | 0.67625 | 6.762
2024-12-09 | 20:56 | Data | 0 | 31.535 | 28.598 | 220.735 | 7.62 | 206.919 | 2173.72 | 25.88 | 42.477 | 6.32 | 1.46 | 5.34 | 8956.27 | 2.795 | 98 | 78.5 | 1412 | 21.19 | 5821.6 | 3197.5 | 3177.1 | 4605.4 | 1206 | 0.67883 | 6.8
2024-12-09 | 20:56 | Data | 0 | 31.555 | 28.639 | 220.78 | 7.62 | 207.01 | 2178.24 | 25.88 | 42.387 | 6.32 | 1.45 | 5.314 | 8938.18 | 2.667 | 98.1 | 78.6 | 1415 | 21.19 | 5809.8 | 3218.7 | 3213.5 | 4636.8 | 1206 | 0.67732 | 6.764
2024-12-09 | 20:56 | Data | 0 | 31.326 | 28.598 | 220.78 | 7.62 | 206.919 | 2176.43 | 25.89 | 42.297 | 6.33 | 1.45 | 5.311 | 8938.18 | 2.707 | 98.1 | 78.6 | 1414 | 21.15 | 5809.8 | 3199.4 | 3205.2 | 4631.8 | 1206 | 0.67455 | 6.762
2024-12-09 | 20:56 | Data | 0 | 31.339 | 28.781 | 220.78 | 7.62 | 207.055 | 2172.81 | 25.88 | 42.387 | 6.32 | 1.445 | 5.261 | 8947.23 | 2.586 | 98.1 | 78.4 | 1413 | 21.19 | 5815.7 | 3192.2 | 3206.2 | 4624.2 | 1206 | 0.67451 | 6.708
2024-12-09 | 20:56 | Data | 0 | 31.117 | 28.565 | 220.735 | 7.62 | 206.919 | 2170.1 | 25.89 | 42.387 | 6.32 | 1.446 | 5.279 | 8897.48 | 2.545 | 98 | 78.5 | 1411 | 21.19 | 5783.4 | 3207.2 | 3219.6 | 4645.3 | 1206 | 0.67445 | 6.726
2024-12-09 | 20:57 | Data | 0 | 31.225 | 28.524 | 220.825 | 7.62 | 206.874 | 2171.91 | 25.88 | 42.387 | 6.32 | 1.449 | 5.308 | 8902 | 2.66 | 98 | 78.6 | 1411 | 21.24 | 5786.3 | 3264.7 | 3229.3 | 4695.1 | 1206 | 0.67904 | 6.755
2024-12-09 | 20:57 | Data | 0 | 31.117 | 28.7 | 220.644 | 7.62 | 207.01 | 2169.2 | 25.88 | 42.477 | 6.32 | 1.457 | 5.288 | 8906.53 | 2.701 | 98 | 78.4 | 1409 | 21.28 | 5789.2 | 3263.2 | 3216.4 | 4686.5 | 1206 | 0.68017 | 6.743
2024-12-09 | 20:57 | Data | 0 | 31.481 | 29.017 | 220.87 | 7.62 | 207.01 | 2170.1 | 25.88 | 42.387 | 6.32 | 1.452 | 5.311 | 8911.05 | 2.714 | 98 | 78.5 | 1411 | 21.24 | 5792.2 | 3255.8 | 3194.9 | 4662.3 | 1206 | 0.68282 | 6.764
2024-12-09 | 20:57 | Data | 0 | 31.306 | 28.76 | 220.78 | 7.63 | 206.964 | 2170.1 | 25.89 | 42.387 | 6.32 | 1.45 | 5.29 | 8888.44 | 2.728 | 98 | 78.5 | 1410 | 21.19 | 5777.5 | 3262.6 | 3179.6 | 4658.8 | 1206 | 0.68414 | 6.74
2024-12-09 | 20:57 | Data | 0 | 30.907 | 28.571 | 220.825 | 7.62 | 206.919 | 2175.52 | 25.88 | 42.387 | 6.32 | 1.446 | 5.312 | 8892.96 | 2.626 | 98.1 | 78.6 | 1414 | 21.15 | 5780.4 | 3262.6 | 3181.3 | 4658.2 | 1206 | 0.68356 | 6.759
2024-12-09 | 20:57 | Data | 0 | 31.218 | 28.74 | 220.916 | 7.62 | 206.919 | 2176.43 | 25.88 | 42.387 | 6.32 | 1.455 | 5.307 | 8897.48 | 2.728 | 98.1 | 78.5 | 1414 | 21.19 | 5783.4 | 3253.1 | 3210.8 | 4672.2 | 1206 | 0.68053 | 6.763
2024-12-09 | 20:57 | Data | 0 | 31.11 | 28.403 | 220.689 | 7.62 | 206.829 | 2180.04 | 25.89 | 42.477 | 6.32 | 1.45 | 5.285 | 8897.48 | 2.538 | 98.1 | 78.5 | 1418 | 21.15 | 5783.4 | 3272.6 | 3222.3 | 4693.6 | 1206 | 0.68286 | 6.736
2024-12-09 | 20:57 | Data | 0 | 30.907 | 28.571 | 220.644 | 7.62 | 206.874 | 2180.95 | 25.89 | 42.477 | 6.32 | 1.458 | 5.301 | 8920.09 | 2.424 | 98.1 | 78.4 | 1418 | 21.19 | 5798.1 | 3281.5 | 3210.5 | 4691.1 | 1206 | 0.6824 | 6.758
2024-12-09 | 20:57 | Data | 0 | 31.285 | 28.794 | 220.689 | 7.62 | 206.829 | 2180.04 | 25.89 | 42.477 | 6.32 | 1.45 | 5.316 | 8924.61 | 2.545 | 98.1 | 78.6 | 1418 | 21.19 | 5801 | 3265.3 | 3236.2 | 4702.1 | 1206 | 0.67936 | 6.765
2024-12-09 | 20:57 | Data | 0 | 30.948 | 28.403 | 220.735 | 7.62 | 206.874 | 2180.95 | 25.86 | 42.477 | 6.32 | 1.444 | 5.293 | 8938.18 | 2.606 | 98.1 | 78.6 | 1418 | 21.19 | 5809.8 | 3273 | 3217.9 | 4698 | 1206 | 0.68129 | 6.738
2024-12-09 | 20:57 | Data | 0 | 31.562 | 28.862 | 220.87 | 7.62 | 207.055 | 2180.95 | 25.89 | 42.297 | 6.32 | 1.449 | 5.292 | 8933.66 | 2.417 | 98.1 | 78.5 | 1417 | 21.19 | 5806.9 | 3255.8 | 3198.1 | 4664.8 | 1206 | 0.68166 | 6.742
2024-12-09 | 20:57 | Data | 0 | 31.285 | 29.193 | 220.87 | 7.62 | 206.919 | 2175.52 | 25.89 | 42.206 | 6.32 | 1.445 | 5.286 | 8951.75 | 2.491 | 98.1 | 78.5 | 1414 | 21.24 | 5818.6 | 3250.8 | 3204.9 | 4665.5 | 1206 | 0.67956 | 6.731
2024-12-09 | 20:57 | Data | 0 | 31.279 | 28.97 | 220.916 | 7.62 | 207.01 | 2180.04 | 25.88 | 42.477 | 6.32 | 1.441 | 5.287 | 8965.31 | 2.64 | 98.1 | 78.6 | 1418 | 21.19 | 5827.5 | 3277.3 | 3212.4 | 4689.8 | 1206 | 0.68259 | 6.727
2024-12-09 | 20:57 | Data | 0 | 31.13 | 28.666 | 220.825 | 7.62 | 206.964 | 2183.66 | 25.88 | 42.477 | 6.32 | 1.45 | 5.267 | 8965.31 | 2.444 | 98.1 | 78.4 | 1419 | 21.24 | 5827.5 | 3263.7 | 3206.6 | 4677.1 | 1206 | 0.6839 | 6.717
2024-12-09 | 20:57 | Data | 0 | 31.056 | 28.848 | 220.78 | 7.62 | 206.874 | 2187.27 | 25.89 | 42.387 | 6.32 | 1.446 | 5.307 | 8965.31 | 2.383 | 98.1 | 78.6 | 1422 | 21.19 | 5827.5 | 3255 | 3190.3 | 4663.3 | 1206 | 0.68177 | 6.752
2024-12-09 | 20:57 | Data | 0 | 31.447 | 28.571 | 220.78 | 7.62 | 206.964 | 2186.37 | 25.89 | 42.387 | 6.32 | 1.452 | 5.318 | 8951.75 | 2.484 | 98.1 | 78.6 | 1421 | 21.24 | 5818.6 | 3257.5 | 3178.9 | 4653.9 | 1206 | 0.68438 | 6.773
2024-12-09 | 20:57 | Data | 0 | 31.292 | 28.497 | 220.735 | 7.62 | 207.01 | 2189.08 | 25.86 | 42.387 | 6.32 | 1.442 | 5.309 | 8526.66 | 2.694 | 98.1 | 78.7 | 1422 | 21.24 | 5542.3 | 3267.8 | 3212.5 | 4685.6 | 1206 | 0.68177 | 6.75
2024-12-09 | 20:58 | Data | 0 | 31.002 | 28.571 | 220.735 | 7.62 | 206.964 | 2189.08 | 25.86 | 42.387 | 6.32 | 1.441 | 5.303 | 8883.91 | 2.64 | 98.1 | 78.6 | 1423 | 21.24 | 5774.5 | 3264.2 | 3220.4 | 4690.1 | 1206 | 0.67973 | 6.744
2024-12-09 | 20:58 | Data | 0 | 31.225 | 28.794 | 220.735 | 7.63 | 206.874 | 2188.18 | 25.89 | 42.297 | 6.32 | 1.45 | 5.281 | 8920.09 | 2.532 | 98.1 | 78.5 | 1423 | 21.19 | 5798.1 | 3217.6 | 3208.3 | 4657.4 | 1206 | 0.68013 | 6.729
2024-12-09 | 20:58 | Data | 0 | 31.339 | 28.862 | 220.689 | 7.62 | 206.919 | 2189.08 | 25.86 | 42.387 | 6.32 | 1.452 | 5.298 | 8933.66 | 2.478 | 98.1 | 78.5 | 1423 | 21.19 | 5806.9 | 3261.9 | 3224.6 | 4691.3 | 1206 | 0.67961 | 6.75
2024-12-09 | 20:58 | Data | 0 | 31.103 | 28.801 | 220.735 | 7.62 | 206.874 | 2186.37 | 25.88 | 42.477 | 6.32 | 1.451 | 5.289 | 8924.61 | 2.505 | 98.1 | 78.5 | 1420 | 21.24 | 5801 | 3236.4 | 3204 | 4656.9 | 1206.1 | 0.67759 | 6.739
2024-12-09 | 20:58 | Data | 0 | 31.393 | 28.409 | 220.689 | 7.63 | 206.919 | 2186.37 | 25.89 | 42.297 | 6.32 | 1.443 | 5.304 | 8920.09 | 2.37 | 98.1 | 78.6 | 1421 | 21.15 | 5798.1 | 3247.6 | 3235.2 | 4682.3 | 1206.1 | 0.67738 | 6.746
2024-12-09 | 20:58 | Data | 0 | 31.333 | 28.693 | 220.825 | 7.62 | 206.919 | 2189.08 | 25.88 | 42.387 | 6.32 | 1.458 | 5.303 | 8929.14 | 2.647 | 98.1 | 78.4 | 1423 | 21.24 | 5803.9 | 3259.8 | 3224.4 | 4685.6 | 1206.1 | 0.67877 | 6.762
2024-12-09 | 20:58 | Data | 0 | 31.339 | 28.686 | 220.599 | 7.62 | 206.919 | 2191.79 | 25.89 | 42.477 | 6.32 | 1.445 | 5.321 | 8929.14 | 2.532 | 98.1 | 78.6 | 1425 | 21.19 | 5803.9 | 3247.7 | 3207.1 | 4668.9 | 1206.1 | 0.67854 | 6.767
2024-12-09 | 20:58 | Data | 0 | 30.921 | 28.457 | 220.599 | 7.62 | 206.964 | 2191.79 | 25.88 | 42.387 | 6.32 | 1.433 | 5.282 | 8938.18 | 2.322 | 98.1 | 78.7 | 1425 | 21.24 | 5809.8 | 3231.7 | 3220.9 | 4665.2 | 1206.1 | 0.67684 | 6.716
2024-12-09 | 20:58 | Data | 0 | 31.225 | 28.909 | 220.735 | 7.62 | 206.874 | 2191.79 | 25.88 | 42.387 | 6.32 | 1.437 | 5.273 | 8938.18 | 2.545 | 98.1 | 78.6 | 1425 | 21.19 | 5809.8 | 3271.1 | 3227.8 | 4702 | 1206.1 | 0.68051 | 6.71
2024-12-09 | 20:58 | Data | 0 | 30.901 | 28.551 | 220.735 | 7.62 | 206.874 | 2191.79 | 25.88 | 42.387 | 6.33 | 1.447 | 5.284 | 8956.27 | 2.525 | 98.1 | 78.5 | 1425 | 21.19 | 5821.6 | 3234 | 3206.4 | 4657.4 | 1206.1 | 0.6811 | 6.732
2024-12-09 | 20:58 | Data | 0 | 31.15 | 28.463 | 220.599 | 7.62 | 206.829 | 2190.89 | 25.89 | 42.387 | 6.32 | 1.455 | 5.304 | 8933.66 | 2.653 | 98.1 | 78.5 | 1425 | 21.19 | 5806.9 | 3228 | 3191.4 | 4642.2 | 1206.1 | 0.67814 | 6.759
2024-12-09 | 20:58 | Data | 0 | 31.339 | 28.585 | 220.689 | 7.62 | 206.829 | 2191.79 | 25.88 | 42.477 | 6.32 | 1.451 | 5.296 | 8965.31 | 2.538 | 98.1 | 78.5 | 1425 | 21.19 | 5827.5 | 3263.1 | 3214 | 4680 | 1206.1 | 0.68153 | 6.746
2024-12-09 | 20:58 | Data | 0 | 31.225 | 28.774 | 220.599 | 7.62 | 206.919 | 2191.79 | 25.88 | 42.387 | 6.31 | 1.442 | 5.29 | 8960.79 | 2.599 | 98.1 | 78.6 | 1425 | 21.19 | 5824.5 | 3254.6 | 3199.5 | 4663 | 1206.1 | 0.68528 | 6.733
2024-12-09 | 20:58 | Data | 0 | 31.495 | 28.585 | 220.599 | 7.62 | 206.919 | 2191.79 | 25.89 | 42.477 | 6.32 | 1.448 | 5.281 | 8969.84 | 2.741 | 98.1 | 78.5 | 1425 | 21.19 | 5830.4 | 3246.9 | 3209.2 | 4669.3 | 1206.1 | 0.67943 | 6.728
2024-12-09 | 20:58 | Data | 0 | 31.002 | 28.747 | 220.825 | 7.62 | 206.919 | 2191.79 | 25.88 | 42.387 | 6.32 | 1.458 | 5.293 | 8965.31 | 2.484 | 98.1 | 78.4 | 1425 | 21.19 | 5827.5 | 3233.4 | 3215.1 | 4662 | 1206.1 | 0.67695 | 6.751
2024-12-09 | 20:58 | Data | 0 | 31.42 | 28.821 | 220.825 | 7.63 | 206.919 | 2114.97 | 25.89 | 42.387 | 6.32 | 1.445 | 5.31 | 8951.75 | 2.647 | 98 | 78.6 | 1370 | 21.19 | 5818.6 | 3249.6 | 3224.2 | 4680.1 | 1206.1 | 0.67787 | 6.755
2024-12-09 | 20:58 | Data | 0 | 31.117 | 28.693 | 220.735 | 7.62 | 206.874 | 2142.99 | 25.9 | 42.387 | 6.32 | 1.444 | 5.315 | 8960.79 | 2.417 | 98 | 78.6 | 1396 | 21.19 | 5824.5 | 3262.3 | 3218.2 | 4684.4 | 1206.1 | 0.68098 | 6.759
2024-12-09 | 20:58 | Data | 0 | 31.117 | 28.531 | 220.735 | 7.62 | 206.829 | 2170.1 | 25.88 | 42.477 | 6.32 | 1.452 | 5.298 | 8947.23 | 2.707 | 98 | 78.5 | 1411 | 21.24 | 5815.7 | 3241.5 | 3184.4 | 4648.6 | 1206.1 | 0.68204 | 6.749
2024-12-09 | 20:59 | Data | 0 | 31.333 | 28.747 | 220.689 | 7.62 | 206.964 | 2170.1 | 25.89 | 42.387 | 6.32 | 1.437 | 5.334 | 8938.18 | 2.424 | 98 | 78.8 | 1410 | 21.24 | 5809.8 | 3256.1 | 3202.4 | 4669.1 | 1206.1 | 0.68022 | 6.771
2024-12-09 | 20:59 | Data | 0 | 31.312 | 29.004 | 220.735 | 7.62 | 206.919 | 2166.49 | 25.88 | 42.477 | 6.32 | 1.455 | 5.327 | 8938.18 | 2.532 | 98 | 78.5 | 1409 | 21.19 | 5809.8 | 3257.1 | 3189.6 | 4662.3 | 1206.1 | 0.68258 | 6.783
2024-12-09 | 20:59 | Data | 0 | 30.901 | 28.673 | 220.78 | 7.62 | 206.964 | 2189.08 | 25.89 | 42.387 | 6.32 | 1.462 | 5.303 | 8929.14 | 2.39 | 98.1 | 78.4 | 1423 | 21.24 | 5803.9 | 3246.2 | 3182.3 | 4653.5 | 1206.1 | 0.68205 | 6.766
2024-12-09 | 20:59 | Data | 0 | 31.245 | 28.673 | 220.735 | 7.62 | 206.919 | 2189.08 | 25.89 | 42.297 | 6.31 | 1.453 | 5.317 | 8920.09 | 2.856 | 98.1 | 78.5 | 1423 | 21.15 | 5798.1 | 3244.4 | 3150.6 | 4626.8 | 1206.1 | 0.68432 | 6.771
2024-12-09 | 20:59 | Data | 0 | 31.333 | 28.909 | 220.689 | 7.62 | 206.964 | 2187.27 | 25.89 | 42.477 | 6.32 | 1.452 | 5.322 | 8924.61 | 2.518 | 98.1 | 78.6 | 1422 | 21.19 | 5801 | 3257.7 | 3171.6 | 4650.1 | 1206.1 | 0.68014 | 6.774
2024-12-09 | 20:59 | Data | 0 | 31.002 | 28.571 | 220.689 | 7.62 | 206.964 | 2189.08 | 25.89 | 42.387 | 6.32 | 1.442 | 5.311 | 8978.88 | 2.525 | 98.1 | 78.7 | 1423 | 21.19 | 5836.3 | 3246.9 | 3161.5 | 4634.3 | 1206.1 | 0.68496 | 6.753
2024-12-09 | 20:59 | Data | 0 | 31.333 | 28.484 | 220.735 | 7.62 | 207.01 | 2187.27 | 25.88 | 42.477 | 6.32 | 1.445 | 5.297 | 8992.45 | 2.599 | 98.1 | 78.6 | 1422 | 21.24 | 5845.1 | 3236.8 | 3172.8 | 4636.6 | 1206.1 | 0.68281 | 6.742
2024-12-09 | 20:59 | Data | 0 | 30.887 | 28.349 | 220.599 | 7.62 | 206.874 | 2189.99 | 25.88 | 42.387 | 6.32 | 1.449 | 5.315 | 8992.45 | 2.701 | 98.1 | 78.6 | 1423 | 21.19 | 5845.1 | 3238.3 | 3188.6 | 4642.8 | 1206.1 | 0.68212 | 6.765
2024-12-09 | 20:59 | Data | 0 | 30.948 | 28.349 | 220.825 | 7.63 | 206.874 | 2186.37 | 25.89 | 42.387 | 6.32 | 1.46 | 5.289 | 8992.45 | 2.545 | 98.1 | 78.4 | 1421 | 21.19 | 5845.1 | 3260.8 | 3194.1 | 4665.8 | 1206.1 | 0.68337 | 6.748
2024-12-09 | 20:59 | Data | 0 | 31.326 | 28.484 | 220.644 | 7.62 | 206.874 | 2188.18 | 25.88 | 42.387 | 6.32 | 1.46 | 5.304 | 8969.84 | 2.592 | 98.1 | 78.4 | 1423 | 21.15 | 5830.4 | 3255.9 | 3211.7 | 4676.9 | 1206.1 | 0.68009 | 6.764
2024-12-09 | 20:59 | Data | 0 | 31.245 | 28.754 | 220.735 | 7.62 | 206.874 | 2189.08 | 25.88 | 42.206 | 6.32 | 1.444 | 5.326 | 8983.4 | 2.633 | 98.1 | 78.7 | 1423 | 21.15 | 5839.2 | 3243.4 | 3192.7 | 4654.3 | 1206.1 | 0.68058 | 6.768
2024-12-09 | 20:59 | Data | 0 | 30.84 | 28.747 | 220.735 | 7.62 | 206.784 | 2189.08 | 25.89 | 42.387 | 6.32 | 1.448 | 5.29 | 8974.36 | 2.403 | 98.1 | 78.5 | 1423 | 21.19 | 5833.3 | 3256.9 | 3186.5 | 4658.7 | 1206.1 | 0.68306 | 6.739
2024-12-09 | 20:59 | Data | 0 | 31.272 | 28.808 | 220.644 | 7.62 | 206.964 | 2189.08 | 25.89 | 42.477 | 6.32 | 1.442 | 5.295 | 8969.84 | 2.694 | 98.1 | 78.6 | 1423 | 21.19 | 5830.4 | 3251.7 | 3182.1 | 4650.4 | 1206.1 | 0.68301 | 6.736
2024-12-09 | 20:59 | Data | 0 | 31.339 | 28.977 | 220.78 | 7.62 | 206.919 | 2189.99 | 25.88 | 42.387 | 6.32 | 1.433 | 5.282 | 8969.84 | 2.532 | 98.1 | 78.6 | 1423 | 21.24 | 5830.4 | 3241.7 | 3179.6 | 4646.2 | 1206.1 | 0.68151 | 6.714
2024-12-09 | 20:59 | Data | 0 | 31.225 | 28.828 | 220.87 | 7.62 | 206.919 | 2192.7 | 25.88 | 42.387 | 6.32 | 1.437 | 5.294 | 8956.27 | 2.457 | 98.1 | 78.7 | 1426 | 21.24 | 5821.6 | 3268.3 | 3208.6 | 4680.1 | 1206.1 | 0.68293 | 6.73
2024-12-09 | 20:59 | Data | 0 | 31.157 | 28.693 | 220.644 | 7.62 | 206.874 | 2184.56 | 25.88 | 42.387 | 6.32 | 1.444 | 5.301 | 8978.88 | 2.559 | 98.1 | 78.6 | 1419 | 21.15 | 5836.3 | 3249.7 | 3192.7 | 4659.8 | 1206.1 | 0.68037 | 6.745
2024-12-09 | 20:59 | Data | 0 | 31.279 | 28.463 | 220.78 | 7.62 | 206.964 | 2189.08 | 25.88 | 42.387 | 6.31 | 1.445 | 5.284 | 8960.79 | 2.592 | 98.1 | 78.5 | 1422 | 21.19 | 5824.5 | 3249.5 | 3207.6 | 4666.3 | 1206.1 | 0.68013 | 6.729
2024-12-09 | 20:59 | Data | 0 | 31.393 | 28.578 | 220.735 | 7.63 | 206.919 | 2189.08 | 25.88 | 42.387 | 6.33 | 1.443 | 5.278 | 8797.99 | 2.451 | 98.1 | 78.5 | 1423 | 21.15 | 5718.7 | 3263.1 | 3225.7 | 4670.4 | 1206.1 | 0.67906 | 6.719
2024-12-09 | 21:00 | Data | 0 | 31.718 | 28.929 | 220.78 | 7.62 | 206.964 | 2189.99 | 25.88 | 42.477 | 6.32 | 1.452 | 5.292 | 8748.25 | 2.606 | 98.1 | 78.5 | 1423 | 21.19 | 5686.4 | 3250.2 | 3222.7 | 4677.8 | 1206.2 | 0.67802 | 6.744
2024-12-09 | 21:00 | Data | 0 | 31.306 | 28.821 | 220.735 | 7.62 | 207.055 | 2189.08 | 25.88 | 42.387 | 6.32 | 1.454 | 5.312 | 8752.77 | 2.667 | 98.1 | 78.5 | 1423 | 21.19 | 5689.3 | 3272.5 | 3214 | 4689 | 1206.2 | 0.68107 | 6.765
2024-12-09 | 21:00 | Data | 0 | 31.447 | 28.578 | 220.825 | 7.63 | 207.01 | 2189.08 | 25.88 | 42.297 | 6.32 | 1.455 | 5.328 | 8761.81 | 2.572 | 98.1 | 78.5 | 1423 | 21.19 | 5695.2 | 3252.1 | 3228.8 | 4685.3 | 1206.2 | 0.67887 | 6.784
2024-12-09 | 21:00 | Data | 0 | 31.13 | 28.578 | 220.735 | 7.62 | 206.919 | 2191.79 | 25.89 | 42.387 | 6.32 | 1.457 | 5.306 | 8847.74 | 2.532 | 98.1 | 78.5 | 1425 | 21.19 | 5751 | 3257.1 | 3210.2 | 4678.3 | 1206.2 | 0.67922 | 6.763
2024-12-09 | 21:00 | Data | 0 | 31.184 | 28.686 | 220.735 | 7.62 | 206.919 | 2189.08 | 25.89 | 42.387 | 6.32 | 1.459 | 5.265 | 9019.58 | 2.505 | 98.1 | 78.3 | 1423 | 21.19 | 5862.7 | 3258.8 | 3204 | 4673.3 | 1206.2 | 0.68213 | 6.725
2024-12-09 | 21:00 | Data | 0 | 31.306 | 28.585 | 220.689 | 7.62 | 206.919 | 2187.27 | 25.88 | 42.387 | 6.32 | 1.442 | 5.29 | 9042.19 | 2.437 | 98.1 | 78.6 | 1421 | 21.1 | 5877.4 | 3251.4 | 3192.4 | 4656.2 | 1206.2 | 0.68316 | 6.732
2024-12-09 | 21:00 | Data | 0 | 31.339 | 28.808 | 220.735 | 7.62 | 206.964 | 2186.37 | 25.89 | 42.387 | 6.32 | 1.448 | 5.314 | 9046.71 | 2.532 | 98.1 | 78.6 | 1421 | 21.19 | 5880.4 | 3242.5 | 3188.2 | 4651.5 | 1206.2 | 0.68087 | 6.761
2024-12-09 | 21:00 | Data | 0 | 31.454 | 28.497 | 220.916 | 7.62 | 207.19 | 2187.27 | 25.86 | 41.936 | 6.32 | 1.446 | 5.335 | 9033.15 | 2.694 | 98.1 | 78.7 | 1422 | 20.97 | 5871.5 | 3262.7 | 3192.2 | 4663.2 | 1206.2 | 0.68228 | 6.782
2024-12-09 | 21:00 | Data | 0 | 31.555 | 28.592 | 220.735 | 7.62 | 206.964 | 2182.75 | 25.88 | 42.387 | 6.32 | 1.446 | 5.308 | 9006.01 | 2.647 | 98.1 | 78.6 | 1420 | 21.19 | 5853.9 | 3244.4 | 3217 | 4668.1 | 1206.2 | 0.67948 | 6.754
2024-12-09 | 21:00 | Data | 0 | 31.339 | 28.808 | 220.825 | 7.62 | 207.01 | 2182.75 | 25.89 | 42.387 | 6.32 | 1.445 | 5.318 | 9006.01 | 2.532 | 98.1 | 78.6 | 1419 | 21.15 | 5853.9 | 3257.4 | 3221.5 | 4680.5 | 1206.2 | 0.6802 | 6.764
2024-12-09 | 21:00 | Data | 0 | 31.036 | 28.517 | 220.599 | 7.63 | 206.964 | 2186.37 | 25.89 | 42.387 | 6.33 | 1.452 | 5.307 | 9006.01 | 2.383 | 98.1 | 78.5 | 1421 | 21.19 | 5853.9 | 3243.2 | 3223.7 | 4675.1 | 1206.2 | 0.67719 | 6.76
2024-12-09 | 21:00 | Data | 0 | 31.258 | 28.578 | 220.644 | 7.62 | 207.01 | 2182.75 | 25.89 | 42.387 | 6.33 | 1.462 | 5.292 | 9006.01 | 2.37 | 98.1 | 78.3 | 1419 | 21.19 | 5853.9 | 3246.7 | 3202.1 | 4658.9 | 1206.2 | 0.68153 | 6.755
2024-12-09 | 21:00 | Data | 0 | 31.285 | 28.706 | 220.689 | 7.62 | 206.919 | 2189.08 | 25.88 | 42.387 | 6.32 | 1.458 | 5.301 | 8960.79 | 2.802 | 98.1 | 78.4 | 1423 | 21.15 | 5824.5 | 3258 | 3194.2 | 4665 | 1206.2 | 0.68114 | 6.76
2024-12-09 | 21:00 | Data | 0 | 31.306 | 28.632 | 220.825 | 7.62 | 207.01 | 2189.99 | 25.88 | 42.477 | 6.33 | 1.451 | 5.296 | 8933.66 | 2.701 | 98.1 | 78.5 | 1423 | 21.19 | 5806.9 | 3248.8 | 3207.9 | 4666.9 | 1206.2 | 0.68018 | 6.746
2024-12-09 | 21:00 | Data | 0 | 31.339 | 28.801 | 220.689 | 7.62 | 206.964 | 2189.08 | 25.88 | 42.297 | 6.32 | 1.445 | 5.282 | 8960.79 | 2.538 | 98.1 | 78.5 | 1423 | 21.15 | 5824.5 | 3242.9 | 3200.6 | 4659.7 | 1206.2 | 0.6805 | 6.727
2024-12-09 | 21:00 | Data | 0 | 31.069 | 28.571 | 220.78 | 7.62 | 206.829 | 2188.18 | 25.88 | 42.477 | 6.32 | 1.445 | 5.288 | 8938.18 | 2.653 | 98.1 | 78.5 | 1423 | 21.19 | 5809.8 | 3270.4 | 3225.4 | 4696.5 | 1206.2 | 0.68022 | 6.735
2024-12-09 | 21:00 | Data | 0 | 31.117 | 28.571 | 220.644 | 7.62 | 206.829 | 2189.08 | 25.88 | 42.387 | 6.32 | 1.453 | 5.296 | 8933.66 | 2.532 | 98.1 | 78.5 | 1423 | 21.19 | 5806.9 | 3268.6 | 3213.4 | 4683 | 1206.2 | 0.68255 | 6.748
2024-12-09 | 21:00 | Data | 0 | 31.508 | 28.598 | 220.87 | 7.62 | 206.964 | 2189.08 | 25.88 | 42.297 | 6.32 | 1.449 | 5.307 | 8499.53 | 2.755 | 98.1 | 78.6 | 1423 | 21.24 | 5524.7 | 3275.4 | 3213.1 | 4677.5 | 1206.2 | 0.68133 | 6.755
2024-12-09 | 21:01 | Data | 0 | 31.333 | 28.571 | 220.599 | 7.62 | 206.874 | 2189.08 | 25.89 | 42.297 | 6.32 | 1.454 | 5.302 | 8933.66 | 2.397 | 98.1 | 78.5 | 1423 | 21.19 | 5806.9 | 3257.6 | 3179.3 | 4651.2 | 1206.2 | 0.68441 | 6.755
2024-12-09 | 21:01 | Data | 0 | 31.211 | 28.895 | 220.825 | 7.62 | 206.919 | 2189.99 | 25.88 | 42.387 | 6.32 | 1.452 | 5.329 | 8915.57 | 2.694 | 98.1 | 78.6 | 1423 | 21.24 | 5795.1 | 3257.3 | 3184.1 | 4654.8 | 1206.2 | 0.68272 | 6.782
2024-12-09 | 21:01 | Data | 0 | 31.11 | 28.781 | 220.825 | 7.62 | 206.874 | 2191.79 | 25.89 | 42.477 | 6.32 | 1.447 | 5.307 | 8951.75 | 2.424 | 98.1 | 78.6 | 1424 | 21.24 | 5818.6 | 3247.6 | 3203.7 | 4666.2 | 1206.2 | 0.68012 | 6.754
2024-12-09 | 21:01 | Data | 0 | 31.474 | 28.436 | 220.825 | 7.62 | 207.055 | 2191.79 | 25.88 | 42.387 | 6.32 | 1.446 | 5.279 | 8947.23 | 2.572 | 98.1 | 78.5 | 1425 | 21.24 | 5815.7 | 3268.7 | 3211.8 | 4688.7 | 1206.2 | 0.68178 | 6.726
2024-12-09 | 21:01 | Data | 0 | 30.901 | 28.558 | 220.599 | 7.62 | 206.829 | 2191.79 | 25.88 | 42.206 | 6.32 | 1.452 | 5.272 | 8956.27 | 2.363 | 98.1 | 78.4 | 1425 | 21.1 | 5821.6 | 3241.3 | 3195 | 4652.4 | 1206.2 | 0.68073 | 6.724
2024-12-09 | 21:01 | Data | 0 | 30.833 | 28.544 | 220.689 | 7.62 | 206.964 | 2191.79 | 25.89 | 42.387 | 6.32 | 1.451 | 5.296 | 8938.18 | 2.647 | 98.1 | 78.5 | 1425 | 21.19 | 5809.8 | 3233.6 | 3230.6 | 4671.9 | 1206.2 | 0.67573 | 6.746
2024-12-09 | 21:01 | Data | 0 | 31.184 | 28.578 | 220.78 | 7.62 | 206.919 | 2190.89 | 25.89 | 42.477 | 6.32 | 1.452 | 5.306 | 8956.27 | 2.457 | 98.1 | 78.5 | 1425 | 21.24 | 5821.6 | 3267.9 | 3233.1 | 4694.7 | 1206.2 | 0.68011 | 6.757
2024-12-09 | 21:01 | Data | 0 | 31.339 | 28.693 | 220.78 | 7.62 | 207.01 | 2194.5 | 25.89 | 42.477 | 6.32 | 1.446 | 5.277 | 9403.97 | 2.647 | 98.1 | 78.5 | 1426 | 21.19 | 6112.6 | 3241.4 | 3227.6 | 4675.9 | 1206.2 | 0.67737 | 6.72
2024-12-09 | 21:01 | Data | 0 | 31.211 | 28.97 | 220.825 | 7.62 | 206.874 | 2197.22 | 25.89 | 42.297 | 6.32 | 1.44 | 5.281 | 9385.88 | 2.606 | 98.1 | 78.6 | 1428 | 21.15 | 6100.8 | 3257.3 | 3231.5 | 4691.1 | 1206.2 | 0.67797 | 6.721
2024-12-09 | 21:01 | Data | 0 | 31.333 | 28.808 | 220.78 | 7.62 | 206.874 | 2199.02 | 25.88 | 42.477 | 6.32 | 1.452 | 5.307 | 9390.4 | 2.538 | 98.1 | 78.5 | 1429 | 21.24 | 6103.8 | 3285.1 | 3244.2 | 4711.5 | 1206.2 | 0.68009 | 6.757
2024-12-09 | 21:01 | Data | 0 | 31.258 | 28.868 | 220.87 | 7.62 | 207.01 | 2197.22 | 25.88 | 42.387 | 6.32 | 1.44 | 5.295 | 8906.53 | 2.626 | 98.1 | 78.6 | 1428 | 21.19 | 5789.2 | 3246.2 | 3232.6 | 4682 | 1206.2 | 0.6766 | 6.736
2024-12-09 | 21:01 | Data | 0 | 31.36 | 28.47 | 220.735 | 7.62 | 206.964 | 2197.22 | 25.86 | 42.387 | 6.32 | 1.446 | 5.293 | 8892.96 | 2.606 | 98.1 | 78.5 | 1428 | 21.15 | 5780.4 | 3252.4 | 3254.2 | 4705.3 | 1206.2 | 0.67564 | 6.74
2024-12-09 | 21:01 | Data | 0 | 31.225 | 28.997 | 220.735 | 7.62 | 206.964 | 2197.22 | 25.88 | 42.387 | 6.32 | 1.458 | 5.299 | 8883.91 | 2.363 | 98.1 | 78.4 | 1429 | 21.19 | 5774.5 | 3258.3 | 3190.7 | 4666.8 | 1206.2 | 0.68148 | 6.758
2024-12-09 | 21:01 | Data | 0 | 31.454 | 29.118 | 220.78 | 7.62 | 207.01 | 2195.41 | 25.89 | 42.206 | 6.32 | 1.455 | 5.286 | 8902 | 2.552 | 98.1 | 78.4 | 1427 | 21.15 | 5786.3 | 3244 | 3203.3 | 4675.8 | 1206.2 | 0.6796 | 6.741
2024-12-09 | 21:01 | Data | 0 | 31.339 | 29.118 | 220.825 | 7.62 | 206.919 | 2198.12 | 25.88 | 42.387 | 6.32 | 1.443 | 5.281 | 8938.18 | 2.572 | 98.1 | 78.5 | 1428 | 21.19 | 5809.8 | 3277 | 3204.7 | 4684.3 | 1206.2 | 0.68341 | 6.724
2024-12-09 | 21:01 | Data | 0 | 31.11 | 28.571 | 220.689 | 7.62 | 206.874 | 2198.12 | 25.88 | 42.477 | 6.32 | 1.446 | 5.278 | 8933.66 | 2.538 | 98.1 | 78.5 | 1428 | 21.24 | 5806.9 | 3246.2 | 3205 | 4667.3 | 1206.3 | 0.67922 | 6.724
2024-12-09 | 21:01 | Data | 0 | 31.495 | 28.97 | 220.508 | 7.62 | 206.919 | 2195.41 | 25.88 | 42.477 | 6.32 | 1.452 | 5.294 | 8920.09 | 2.653 | 98.1 | 78.5 | 1426 | 21.19 | 5798.1 | 3270.3 | 3217.8 | 4688.9 | 1206.3 | 0.68189 | 6.746
2024-12-09 | 21:02 | Data | 0 | 31.393 | 28.922 | 220.735 | 7.62 | 207.01 | 2189.08 | 25.88 | 42.387 | 6.32 | 1.44 | 5.316 | 8924.61 | 2.424 | 98.1 | 78.7 | 1423 | 21.24 | 5801 | 3258 | 3196.8 | 4665.9 | 1206.3 | 0.68206 | 6.756
2024-12-09 | 21:02 | Data | 0 | 31.366 | 28.808 | 220.916 | 7.62 | 207.01 | 2194.5 | 25.89 | 42.387 | 6.32 | 1.444 | 5.284 | 8960.79 | 2.424 | 98.1 | 78.5 | 1426 | 21.19 | 5824.5 | 3230.6 | 3202.2 | 4651.6 | 1206.3 | 0.6787 | 6.727
2024-12-09 | 21:02 | Data | 0 | 31.117 | 28.571 | 220.689 | 7.62 | 206.874 | 2197.22 | 25.88 | 42.387 | 6.32 | 1.443 | 5.288 | 8960.79 | 2.491 | 98.1 | 78.6 | 1428 | 21.19 | 5824.5 | 3248.1 | 3198.4 | 4660.3 | 1206.3 | 0.68097 | 6.729
2024-12-09 | 21:02 | Data | 0 | 31.117 | 28.693 | 220.825 | 7.62 | 207.01 | 2197.22 | 25.89 | 42.297 | 6.32 | 1.445 | 5.29 | 8951.75 | 2.592 | 98.1 | 78.5 | 1428 | 21.19 | 5818.6 | 3276.4 | 3229.6 | 4702.3 | 1206.3 | 0.68091 | 6.736
2024-12-09 | 21:02 | Data | 0 | 31.339 | 28.673 | 220.78 | 7.62 | 206.874 | 2197.22 | 25.88 | 42.387 | 6.32 | 1.451 | 5.287 | 8956.27 | 2.471 | 98.1 | 78.5 | 1428 | 21.24 | 5821.6 | 3252.1 | 3215 | 4674.3 | 1206.3 | 0.67934 | 6.737
2024-12-09 | 21:02 | Data | 0 | 31.09 | 28.801 | 220.689 | 7.62 | 207.01 | 2194.5 | 25.88 | 42.297 | 6.33 | 1.452 | 5.266 | 8947.23 | 2.619 | 98.1 | 78.4 | 1426 | 21.19 | 5815.7 | 3248 | 3214.5 | 4669.7 | 1206.3 | 0.67897 | 6.718
2024-12-09 | 21:02 | Data | 0 | 31.758 | 28.612 | 220.825 | 7.62 | 206.964 | 2192.7 | 25.86 | 42.387 | 6.32 | 1.441 | 5.298 | 8951.75 | 2.734 | 98.1 | 78.6 | 1425 | 21.19 | 5818.6 | 3252.2 | 3196 | 4655.2 | 1206.3 | 0.68084 | 6.74
2024-12-09 | 21:02 | Data | 0 | 31.123 | 28.457 | 220.735 | 7.62 | 206.964 | 2191.79 | 25.88 | 42.477 | 6.32 | 1.445 | 5.272 | 8951.75 | 2.538 | 98.1 | 78.5 | 1425 | 21.19 | 5818.6 | 3268.6 | 3184.2 | 4661.4 | 1206.3 | 0.6829 | 6.717
2024-12-09 | 21:02 | Data | 0 | 31.184 | 28.693 | 220.644 | 7.62 | 206.964 | 2191.79 | 25.89 | 42.387 | 6.32 | 1.452 | 5.283 | 8956.27 | 2.538 | 98.1 | 78.4 | 1425 | 21.19 | 5821.6 | 3246.8 | 3203.9 | 4673.8 | 1206.3 | 0.68035 | 6.733
2024-12-09 | 21:02 | Data | 0 | 31.454 | 28.592 | 220.916 | 7.62 | 207.01 | 2192.7 | 25.88 | 42.387 | 6.32 | 1.452 | 5.266 | 9403.97 | 2.633 | 98.1 | 78.4 | 1425 | 21.24 | 6112.6 | 3271.1 | 3210.8 | 4686 | 1206.3 | 0.68203 | 6.718
2024-12-09 | 21:02 | Data | 0 | 31.285 | 28.828 | 220.78 | 7.62 | 207.01 | 2189.99 | 25.89 | 42.297 | 6.32 | 1.444 | 5.301 | 8698.5 | 2.707 | 98.1 | 78.6 | 1423 | 21.19 | 5654 | 3256.8 | 3217.3 | 4679.4 | 1206.3 | 0.68031 | 6.746
2024-12-09 | 21:02 | Data | 0 | 30.907 | 28.747 | 220.735 | 7.62 | 207.055 | 2189.08 | 25.89 | 42.387 | 6.32 | 1.432 | 5.293 | 8721.11 | 2.505 | 98.1 | 78.7 | 1423 | 21.19 | 5668.7 | 3261.7 | 3200.9 | 4671.4 | 1206.3 | 0.6819 | 6.726
2024-12-09 | 21:02 | Data | 0 | 31.09 | 28.585 | 220.87 | 7.62 | 207.01 | 2193.6 | 25.86 | 42.387 | 6.32 | 1.434 | 5.288 | 8730.16 | 2.721 | 98.1 | 78.7 | 1426 | 21.19 | 5674.6 | 3247.4 | 3199.8 | 4658.4 | 1206.3 | 0.68077 | 6.722
2024-12-09 | 21:02 | Data | 0 | 31.339 | 28.74 | 220.78 | 7.62 | 206.919 | 2189.08 | 25.88 | 42.297 | 6.32 | 1.439 | 5.304 | 9146.2 | 2.424 | 98.1 | 78.7 | 1423 | 21.15 | 5945 | 3251.2 | 3195.2 | 4660.4 | 1206.3 | 0.68145 | 6.744
2024-12-09 | 21:02 | Data | 0 | 31.123 | 28.794 | 220.825 | 7.62 | 207.055 | 2189.99 | 25.88 | 42.297 | 6.32 | 1.448 | 5.286 | 9173.34 | 2.356 | 98.1 | 78.5 | 1423 | 21.15 | 5962.7 | 3274.5 | 3218.1 | 4690.5 | 1206.3 | 0.68158 | 6.734
2024-12-09 | 21:02 | Data | 0 | 31.117 | 28.801 | 220.78 | 7.62 | 206.874 | 2189.08 | 25.89 | 42.387 | 6.33 | 1.453 | 5.252 | 9159.77 | 2.43 | 98.1 | 78.3 | 1423 | 21.19 | 5953.9 | 3267.9 | 3214.2 | 4687.5 | 1206.3 | 0.68157 | 6.705
2024-12-09 | 21:02 | Data | 0 | 31.117 | 28.922 | 220.825 | 7.62 | 207.01 | 2188.18 | 25.89 | 42.387 | 6.32 | 1.454 | 5.3 | 9164.29 | 2.424 | 98.1 | 78.5 | 1422 | 21.19 | 5956.8 | 3244 | 3184.1 | 4643.2 | 1206.3 | 0.68252 | 6.755
2024-12-09 | 21:02 | Data | 0 | 31.164 | 28.855 | 220.825 | 7.62 | 206.919 | 2189.08 | 25.88 | 42.477 | 6.32 | 1.447 | 5.289 | 9141.68 | 2.647 | 98.1 | 78.5 | 1423 | 21.19 | 5942.1 | 3260 | 3205.4 | 4676.4 | 1206.3 | 0.68002 | 6.734
2024-12-09 | 21:03 | Data | 0 | 31.333 | 28.7 | 220.689 | 7.62 | 206.964 | 2191.79 | 25.88 | 42.297 | 6.32 | 1.449 | 5.284 | 9141.68 | 2.599 | 98.1 | 78.5 | 1425 | 21.19 | 5942.1 | 3249.4 | 3203.5 | 4666 | 1206.3 | 0.68037 | 6.733
2024-12-09 | 21:03 | Data | 0 | 31.056 | 28.801 | 220.689 | 7.62 | 206.874 | 2193.6 | 25.88 | 42.477 | 6.32 | 1.442 | 5.293 | 9132.64 | 2.619 | 98.1 | 78.6 | 1427 | 21.19 | 5936.2 | 3272.9 | 3207.3 | 4682.3 | 1206.3 | 0.68342 | 6.735
2024-12-09 | 21:03 | Data | 0 | 31.225 | 28.578 | 220.78 | 7.62 | 206.964 | 2197.22 | 25.88 | 42.387 | 6.33 | 1.44 | 5.307 | 9137.16 | 2.579 | 98.1 | 78.7 | 1428 | 21.19 | 5939.2 | 3253 | 3170.2 | 4647.6 | 1206.3 | 0.6834 | 6.746
2024-12-09 | 21:03 | Data | 0 | 31.562 | 28.605 | 220.735 | 7.62 | 207.055 | 2197.22 | 25.88 | 42.387 | 6.32 | 1.445 | 5.305 | 9105.5 | 2.498 | 98.1 | 78.6 | 1428 | 21.19 | 5918.6 | 3272.9 | 3214 | 4688.7 | 1206.3 | 0.68161 | 6.75
2024-12-09 | 21:03 | Data | 0 | 31.13 | 28.578 | 220.689 | 7.62 | 206.964 | 2190.89 | 25.89 | 42.387 | 6.32 | 1.461 | 5.284 | 9051.24 | 2.525 | 98.1 | 78.3 | 1423 | 21.15 | 5883.3 | 3239.6 | 3209.2 | 4661.5 | 1206.3 | 0.679 | 6.746
2024-12-09 | 21:03 | Data | 0 | 31.042 | 28.598 | 220.87 | 7.62 | 206.874 | 2191.79 | 25.88 | 42.297 | 6.32 | 1.461 | 5.281 | 9046.71 | 2.424 | 98.1 | 78.3 | 1425 | 21.15 | 5880.4 | 3224.8 | 3184.6 | 4639.2 | 1206.3 | 0.67843 | 6.743
2024-12-09 | 21:03 | Data | 0 | 31.11 | 28.963 | 220.735 | 7.63 | 206.964 | 2192.7 | 25.89 | 42.477 | 6.32 | 1.455 | 5.294 | 9024.1 | 2.545 | 98.1 | 78.4 | 1424 | 21.19 | 5865.7 | 3231.3 | 3201 | 4652.6 | 1206.3 | 0.67663 | 6.749
2024-12-09 | 21:03 | Data | 0 | 31.393 | 28.72 | 220.825 | 7.62 | 207.055 | 2192.7 | 25.88 | 42.387 | 6.32 | 1.455 | 5.288 | 9019.58 | 2.484 | 98.1 | 78.4 | 1425 | 21.19 | 5862.7 | 3259.5 | 3221 | 4686.2 | 1206.3 | 0.67864 | 6.742
2024-12-09 | 21:03 | Data | 0 | 31.11 | 28.598 | 220.78 | 7.62 | 206.829 | 2191.79 | 25.88 | 42.387 | 6.32 | 1.446 | 5.303 | 9064.8 | 2.653 | 98.1 | 78.6 | 1425 | 21.19 | 5892.1 | 3256.1 | 3216.9 | 4676.9 | 1206.3 | 0.67906 | 6.748
2024-12-09 | 21:03 | Data | 0 | 31.339 | 29.004 | 220.78 | 7.62 | 206.829 | 2194.5 | 25.89 | 42.477 | 6.32 | 1.445 | 5.276 | 9055.76 | 2.37 | 98.1 | 78.5 | 1426 | 21.24 | 5886.2 | 3251 | 3215.3 | 4672.3 | 1206.3 | 0.67674 | 6.722
2024-12-09 | 21:03 | Data | 0 | 31.123 | 28.571 | 220.735 | 7.62 | 206.964 | 2194.5 | 25.88 | 42.387 | 6.32 | 1.446 | 5.27 | 9051.24 | 2.538 | 98.1 | 78.5 | 1426 | 21.19 | 5883.3 | 3246.5 | 3230.5 | 4685 | 1206.3 | 0.67665 | 6.717
2024-12-09 | 21:03 | Data | 0 | 31.117 | 28.922 | 220.961 | 7.62 | 206.964 | 2193.6 | 25.88 | 42.387 | 6.32 | 1.434 | 5.301 | 9051.24 | 2.363 | 98.1 | 78.7 | 1426 | 21.24 | 5883.3 | 3251.1 | 3235.7 | 4687.7 | 1206.3 | 0.67777 | 6.735
2024-12-09 | 21:03 | Data | 0 | 31.11 | 28.558 | 220.916 | 7.62 | 206.964 | 2192.7 | 25.89 | 42.297 | 6.32 | 1.453 | 5.279 | 9033.15 | 2.647 | 98.1 | 78.4 | 1425 | 21.15 | 5871.5 | 3265.4 | 3212.3 | 4680.8 | 1206.4 | 0.67843 | 6.733
2024-12-09 | 21:03 | Data | 0 | 31.11 | 28.571 | 220.644 | 7.62 | 206.964 | 2193.6 | 25.89 | 42.387 | 6.32 | 1.462 | 5.292 | 9037.67 | 2.714 | 98.1 | 78.4 | 1426 | 21.24 | 5874.5 | 3233 | 3232.3 | 4675.5 | 1206.4 | 0.67513 | 6.754
2024-12-09 | 21:03 | Data | 0 | 31.508 | 29.105 | 220.87 | 7.62 | 207.055 | 2192.7 | 25.89 | 42.387 | 6.33 | 1.447 | 5.302 | 9033.15 | 2.457 | 98.1 | 78.6 | 1425 | 21.1 | 5871.5 | 3235.1 | 3215.7 | 4666 | 1206.4 | 0.67808 | 6.748
2024-12-09 | 21:03 | Data | 0 | 31.454 | 28.605 | 220.87 | 7.62 | 207.055 | 2191.79 | 25.86 | 42.297 | 6.32 | 1.436 | 5.287 | 9006.01 | 2.667 | 98.1 | 78.6 | 1425 | 21.24 | 5853.9 | 3271.2 | 3211.9 | 4674.8 | 1206.4 | 0.68123 | 6.722
2024-12-09 | 21:03 | Data | 0 | 31.339 | 28.794 | 220.78 | 7.63 | 206.919 | 2187.27 | 25.88 | 42.387 | 6.32 | 1.448 | 5.293 | 8983.4 | 2.647 | 98.1 | 78.5 | 1422 | 21.24 | 5839.2 | 3240.9 | 3193 | 4655.3 | 1206.4 | 0.67982 | 6.738
2024-12-09 | 21:03 | Data | 0 | 31.461 | 28.43 | 220.916 | 7.62 | 207.01 | 2195.41 | 25.88 | 42.297 | 6.32 | 1.45 | 5.297 | 8987.93 | 2.68 | 98.1 | 78.5 | 1427 | 21.19 | 5842.2 | 3241.4 | 3196.5 | 4654.6 | 1206.4 | 0.67863 | 6.746
2024-12-09 | 21:04 | Data | 0 | 31.11 | 28.571 | 220.735 | 7.62 | 206.964 | 2195.41 | 25.88 | 42.387 | 6.32 | 1.446 | 5.297 | 8992.45 | 2.37 | 98.1 | 78.5 | 1426 | 21.19 | 5845.1 | 3242.2 | 3223.6 | 4677.4 | 1206.4 | 0.67819 | 6.741
2024-12-09 | 21:04 | Data | 0 | 31.11 | 28.578 | 220.916 | 7.62 | 207.055 | 2197.22 | 25.88 | 42.387 | 6.32 | 1.448 | 5.294 | 8983.4 | 2.532 | 98.1 | 78.5 | 1428 | 21.19 | 5839.2 | 3230.4 | 3218.1 | 4663.2 | 1206.4 | 0.67671 | 6.744
2024-12-09 | 21:04 | Data | 0 | 31.333 | 28.632 | 220.78 | 7.62 | 206.919 | 2196.31 | 25.88 | 42.477 | 6.32 | 1.463 | 5.301 | 8978.88 | 2.653 | 98.1 | 78.4 | 1427 | 21.24 | 5836.3 | 3244.3 | 3223.7 | 4677.1 | 1206.4 | 0.68263 | 6.763
2024-12-09 | 21:04 | Data | 0 | 31.454 | 28.632 | 220.87 | 7.62 | 207.01 | 2197.22 | 25.88 | 42.387 | 6.32 | 1.458 | 5.286 | 8978.88 | 2.565 | 98.1 | 78.4 | 1428 | 21.24 | 5836.3 | 3237.6 | 3189.4 | 4649.8 | 1206.4 | 0.68018 | 6.744
2024-12-09 | 21:04 | Data | 0 | 31.117 | 28.585 | 220.78 | 7.62 | 206.964 | 2198.12 | 25.89 | 42.387 | 6.32 | 1.458 | 5.279 | 8983.4 | 2.511 | 98.1 | 78.4 | 1428 | 21.15 | 5839.2 | 3244.3 | 3207.5 | 4661.4 | 1206.4 | 0.67796 | 6.737
2024-12-09 | 21:04 | Data | 0 | 31.211 | 28.571 | 220.689 | 7.62 | 206.874 | 2197.22 | 25.89 | 42.387 | 6.32 | 1.446 | 5.312 | 8983.4 | 2.565 | 98.1 | 78.6 | 1428 | 21.19 | 5839.2 | 3241.5 | 3204.8 | 4661.3 | 1206.4 | 0.67935 | 6.758
2024-12-09 | 21:04 | Data | 0 | 30.941 | 28.747 | 220.689 | 7.62 | 206.829 | 2201.74 | 25.89 | 42.297 | 6.32 | 1.446 | 5.298 | 8987.93 | 2.518 | 98.1 | 78.6 | 1431 | 21.15 | 5842.2 | 3243.3 | 3204 | 4659.1 | 1206.4 | 0.67907 | 6.746
2024-12-09 | 21:04 | Data | 0 | 31.285 | 28.376 | 220.78 | 7.62 | 206.919 | 2197.22 | 25.88 | 42.387 | 6.32 | 1.441 | 5.317 | 8996.97 | 2.748 | 98.1 | 78.7 | 1428 | 21.19 | 5848 | 3234.7 | 3202.6 | 4655.9 | 1206.4 | 0.67916 | 6.758
2024-12-09 | 21:04 | Data | 0 | 31.454 | 28.646 | 220.735 | 7.63 | 207.01 | 2197.22 | 25.89 | 42.387 | 6.32 | 1.439 | 5.308 | 9001.49 | 2.592 | 98.1 | 78.7 | 1429 | 21.19 | 5851 | 3246.6 | 3194 | 4653.6 | 1206.4 | 0.68218 | 6.746
2024-12-09 | 21:04 | Data | 0 | 31.117 | 28.457 | 220.599 | 7.62 | 206.919 | 2197.22 | 25.88 | 42.387 | 6.32 | 1.44 | 5.32 | 9006.01 | 2.538 | 98.1 | 78.7 | 1429 | 21.19 | 5853.9 | 3262.7 | 3218.3 | 4685.7 | 1206.4 | 0.68128 | 6.759
2024-12-09 | 21:04 | Data | 0 | 31.366 | 28.592 | 220.735 | 7.62 | 207.1 | 2197.22 | 25.89 | 42.477 | 6.33 | 1.446 | 5.268 | 8987.93 | 2.552 | 98.1 | 78.5 | 1428 | 21.19 | 5842.2 | 3233.8 | 3207.1 | 4660.5 | 1206.4 | 0.67751 | 6.714
2024-12-09 | 21:04 | Data | 0 | 31.123 | 28.571 | 220.78 | 7.63 | 207.01 | 2194.5 | 25.88 | 42.297 | 6.32 | 1.447 | 5.297 | 8987.93 | 2.532 | 98.1 | 78.5 | 1426 | 21.15 | 5842.2 | 3235.1 | 3191.3 | 4645 | 1206.4 | 0.68022 | 6.743
2024-12-09 | 21:04 | Data | 0 | 31.164 | 28.578 | 220.78 | 7.62 | 206.964 | 2192.7 | 25.88 | 42.387 | 6.32 | 1.443 | 5.293 | 8987.93 | 2.538 | 98.1 | 78.6 | 1424 | 21.19 | 5842.2 | 3273.1 | 3213.4 | 4685.4 | 1206.4 | 0.68307 | 6.736
2024-12-09 | 21:04 | Data | 0 | 31.123 | 28.781 | 220.916 | 7.62 | 207.055 | 2191.79 | 25.89 | 42.206 | 6.32 | 1.452 | 5.304 | 8978.88 | 2.424 | 98.1 | 78.5 | 1425 | 21.15 | 5836.3 | 3248.1 | 3198.3 | 4657.5 | 1206.4 | 0.68152 | 6.755
2024-12-09 | 21:04 | Data | 0 | 31.562 | 28.922 | 220.735 | 7.62 | 206.964 | 2197.22 | 25.88 | 42.477 | 6.32 | 1.451 | 5.324 | 8969.84 | 2.471 | 98.1 | 78.6 | 1428 | 21.19 | 5830.4 | 3256.3 | 3205.7 | 4664.9 | 1206.4 | 0.6791 | 6.774
2024-12-09 | 21:04 | Data | 0 | 31.117 | 28.693 | 220.78 | 7.63 | 206.919 | 2197.22 | 25.88 | 42.477 | 6.32 | 1.45 | 5.296 | 8920.09 | 2.545 | 98.1 | 78.5 | 1428 | 21.24 | 5798.1 | 3231.9 | 3211.4 | 4662.4 | 1206.4 | 0.67566 | 6.745
2024-12-09 | 21:04 | Data | 0 | 31.61 | 28.868 | 220.916 | 7.62 | 207.01 | 2197.22 | 25.88 | 42.387 | 6.32 | 1.435 | 5.26 | 8951.75 | 2.532 | 98.1 | 78.6 | 1428 | 21.15 | 5818.6 | 3238.9 | 3216.6 | 4668.3 | 1206.4 | 0.67999 | 6.695
2024-12-09 | 21:05 | Data | 0 | 31.083 | 28.47 | 220.735 | 7.62 | 206.874 | 2197.22 | 25.89 | 42.387 | 6.32 | 1.434 | 5.295 | 8951.75 | 2.586 | 98.1 | 78.7 | 1428 | 21.19 | 5818.6 | 3235.7 | 3225 | 4671.1 | 1206.4 | 0.6767 | 6.729
2024-12-09 | 21:05 | Data | 0 | 31.164 | 28.571 | 220.689 | 7.62 | 206.964 | 2197.22 | 25.88 | 42.297 | 6.32 | 1.445 | 5.301 | 8956.27 | 2.559 | 98.1 | 78.6 | 1428 | 21.24 | 5821.6 | 3230.9 | 3196.5 | 4646.7 | 1206.4 | 0.67887 | 6.747
2024-12-09 | 21:05 | Data | 0 | 31.11 | 28.801 | 220.735 | 7.62 | 206.829 | 2197.22 | 25.88 | 42.387 | 6.32 | 1.451 | 5.286 | 8969.84 | 2.565 | 98.1 | 78.5 | 1428 | 21.19 | 5830.4 | 3250 | 3172.4 | 4646.5 | 1206.4 | 0.68276 | 6.736
2024-12-09 | 21:05 | Data | 0 | 31.583 | 28.7 | 220.87 | 7.62 | 207.055 | 2196.31 | 25.89 | 42.387 | 6.33 | 1.45 | 5.301 | 8951.75 | 2.579 | 98.1 | 78.5 | 1428 | 21.24 | 5818.6 | 3241.5 | 3210.1 | 4661.6 | 1206.4 | 0.67933 | 6.75
2024-12-09 | 21:05 | Data | 0 | 31.056 | 28.571 | 220.78 | 7.62 | 206.829 | 2197.22 | 25.88 | 42.206 | 6.32 | 1.455 | 5.311 | 8951.75 | 2.511 | 98.1 | 78.5 | 1428 | 21.15 | 5818.6 | 3266.9 | 3188.2 | 4668.3 | 1206.4 | 0.68341 | 6.765
2024-12-09 | 21:05 | Data | 0 | 31.407 | 28.605 | 220.689 | 7.62 | 206.919 | 2196.31 | 25.88 | 42.206 | 6.32 | 1.46 | 5.304 | 8956.27 | 2.538 | 98.1 | 78.4 | 1428 | 21.1 | 5821.6 | 3235.7 | 3207.2 | 4661.4 | 1206.4 | 0.67827 | 6.764
2024-12-09 | 21:05 | Data | 0 | 31.643 | 28.612 | 220.916 | 7.62 | 207.01 | 2195.41 | 25.89 | 42.026 | 6.32 | 1.45 | 5.327 | 8965.31 | 2.66 | 98.1 | 78.6 | 1427 | 20.97 | 5827.5 | 3240.6 | 3209.5 | 4661.2 | 1206.4 | 0.67822 | 6.777
2024-12-09 | 21:05 | Data | 0 | 31.333 | 28.808 | 220.825 | 7.62 | 207.01 | 2194.5 | 25.88 | 42.116 | 6.32 | 1.448 | 5.298 | 8965.31 | 2.532 | 98.1 | 78.5 | 1426 | 21.1 | 5827.5 | 3256.8 | 3201.4 | 4673.3 | 1206.4 | 0.68089 | 6.746
2024-12-09 | 21:05 | Data | 0 | 31.333 | 28.693 | 220.825 | 7.62 | 206.919 | 2194.5 | 25.89 | 42.206 | 6.32 | 1.447 | 5.298 | 8983.4 | 2.559 | 98.1 | 78.6 | 1426 | 21.01 | 5839.2 | 3231.2 | 3218.5 | 4666.3 | 1206.4 | 0.67651 | 6.746
2024-12-09 | 21:05 | Data | 0 | 31.427 | 29.024 | 220.78 | 7.62 | 206.919 | 2196.31 | 25.86 | 42.206 | 6.32 | 1.451 | 5.313 | 8969.84 | 2.525 | 98.1 | 78.6 | 1427 | 21.06 | 5830.4 | 3267.7 | 3201 | 4676.4 | 1206.4 | 0.68262 | 6.764
2024-12-09 | 21:05 | Data | 0 | 31.211 | 28.693 | 220.78 | 7.62 | 206.919 | 2194.5 | 25.89 | 42.206 | 6.32 | 1.458 | 5.333 | 8965.31 | 2.755 | 98.1 | 78.5 | 1427 | 21.1 | 5827.5 | 3241.8 | 3206.2 | 4656.5 | 1206.5 | 0.68093 | 6.791
2024-12-09 | 21:05 | Data | 0 | 31.664 | 29.031 | 220.825 | 7.62 | 207.01 | 2197.22 | 25.88 | 42.116 | 6.32 | 1.452 | 5.303 | 8965.31 | 2.707 | 98.1 | 78.5 | 1429 | 21.06 | 5827.5 | 3254.1 | 3176.6 | 4651 | 1206.5 | 0.68334 | 6.755
2024-12-09 | 21:05 | Data | 0 | 31.225 | 28.794 | 220.87 | 7.62 | 207.01 | 2196.31 | 25.88 | 42.116 | 6.32 | 1.45 | 5.299 | 8951.75 | 2.545 | 98.1 | 78.5 | 1428 | 21.06 | 5818.6 | 3227.5 | 3227.1 | 4668.9 | 1206.5 | 0.67647 | 6.75
2024-12-09 | 21:05 | Data | 0 | 31.312 | 28.693 | 220.689 | 7.62 | 206.919 | 2199.02 | 25.88 | 42.026 | 6.32 | 1.46 | 5.317 | 8969.84 | 2.755 | 98.1 | 78.5 | 1430 | 21.01 | 5830.4 | 3235.3 | 3252 | 4686.2 | 1206.5 | 0.67511 | 6.775
2024-12-09 | 21:05 | Data | 0 | 31.393 | 28.895 | 220.916 | 7.62 | 207.1 | 2199.02 | 25.88 | 42.116 | 6.32 | 1.45 | 5.317 | 8960.79 | 2.653 | 98.1 | 78.6 | 1429 | 21.01 | 5824.5 | 3275.5 | 3229 | 4699.7 | 1206.5 | 0.68169 | 6.765
2024-12-09 | 21:05 | Data | 0 | 31.724 | 28.673 | 220.961 | 7.62 | 207.1 | 2199.93 | 25.89 | 42.206 | 6.32 | 1.443 | 5.312 | 8951.75 | 2.619 | 98.1 | 78.6 | 1429 | 21.1 | 5818.6 | 3253.2 | 3213.6 | 4675.9 | 1206.5 | 0.68013 | 6.755
2024-12-09 | 21:05 | Data | 0 | 31.474 | 28.808 | 221.006 | 7.62 | 207.055 | 2203.54 | 25.88 | 42.116 | 6.32 | 1.449 | 5.294 | 8969.84 | 2.309 | 98.1 | 78.5 | 1432 | 21.1 | 5830.4 | 3242.5 | 3215.6 | 4671.4 | 1206.5 | 0.67709 | 6.742
2024-12-09 | 21:05 | Data | 0 | 31.11 | 28.74 | 220.735 | 7.62 | 207.01 | 2205.35 | 25.89 | 42.116 | 6.32 | 1.448 | 5.282 | 8978.88 | 2.559 | 98.1 | 78.5 | 1433 | 21.06 | 5836.3 | 3252.9 | 3210.3 | 4672.8 | 1206.5 | 0.68036 | 6.729
2024-12-09 | 21:06 | Data | 0 | 31.339 | 28.585 | 220.78 | 7.62 | 207.01 | 2206.25 | 25.89 | 42.297 | 6.32 | 1.443 | 5.308 | 9006.01 | 2.545 | 98.1 | 78.6 | 1434 | 21.06 | 5853.9 | 3244.2 | 3226.8 | 4678.9 | 1206.5 | 0.67684 | 6.752
2024-12-09 | 21:06 | Data | 0 | 31.333 | 28.794 | 220.689 | 7.62 | 207.01 | 2204.45 | 25.88 | 42.116 | 6.32 | 1.448 | 5.316 | 9006.01 | 2.633 | 98.1 | 78.6 | 1433 | 21.06 | 5853.9 | 3245.1 | 3212.2 | 4667.8 | 1206.5 | 0.6784 | 6.764
2024-12-09 | 21:06 | Data | 0 | 31.427 | 28.855 | 220.78 | 7.62 | 206.919 | 2208.97 | 25.88 | 42.568 | 6.32 | 1.453 | 5.308 | 8992.45 | 2.66 | 98.1 | 78.5 | 1436 | 21.33 | 5845.1 | 3246.4 | 3217.3 | 4670.7 | 1206.5 | 0.67831 | 6.761
2024-12-09 | 21:06 | Data | 0 | 31.866 | 28.929 | 220.825 | 7.62 | 207.055 | 2209.87 | 25.89 | 42.387 | 6.31 | 1.45 | 5.302 | 8992.45 | 2.755 | 98.1 | 78.5 | 1436 | 21.15 | 5845.1 | 3251.5 | 3211.8 | 4671.2 | 1206.5 | 0.68037 | 6.753
2024-12-09 | 21:06 | Data | 0 | 31.333 | 28.747 | 220.735 | 7.62 | 207.01 | 2208.06 | 25.88 | 42.116 | 6.32 | 1.451 | 5.289 | 8974.36 | 2.586 | 98.1 | 78.5 | 1436 | 21.06 | 5833.3 | 3233 | 3206.4 | 4655.4 | 1206.5 | 0.6776 | 6.741
2024-12-09 | 21:06 | Data | 0 | 31.387 | 28.423 | 220.825 | 7.62 | 207.055 | 2203.54 | 25.89 | 42.026 | 6.32 | 1.451 | 5.281 | 8960.79 | 2.599 | 98.1 | 78.5 | 1432 | 21.06 | 5824.5 | 3242.5 | 3228 | 4680.5 | 1206.5 | 0.67815 | 6.732
2024-12-09 | 21:06 | Data | 0 | 31.11 | 28.349 | 220.689 | 7.62 | 206.874 | 2203.54 | 25.88 | 42.477 | 6.33 | 1.449 | 5.319 | 8956.27 | 2.559 | 98.1 | 78.6 | 1432 | 21.24 | 5821.6 | 3242.7 | 3230.2 | 4679.7 | 1206.5 | 0.67608 | 6.768
2024-12-09 | 21:06 | Data | 0 | 31.562 | 28.632 | 220.825 | 7.62 | 207.055 | 2199.02 | 25.88 | 42.387 | 6.33 | 1.447 | 5.299 | 8965.31 | 2.64 | 98.1 | 78.6 | 1431 | 21.19 | 5827.5 | 3248.7 | 3215 | 4670.2 | 1206.5 | 0.67968 | 6.746
2024-12-09 | 21:06 | Data | 0 | 31.029 | 28.49 | 220.644 | 7.62 | 207.01 | 2199.93 | 25.88 | 42.387 | 6.32 | 1.45 | 5.268 | 8969.84 | 2.505 | 98.1 | 78.4 | 1430 | 21.15 | 5830.4 | 3250.1 | 3232.1 | 4688.4 | 1206.5 | 0.67701 | 6.718
2024-12-09 | 21:06 | Data | 0 | 31.117 | 29.024 | 220.916 | 7.62 | 207.055 | 2199.93 | 25.88 | 42.477 | 6.32 | 1.451 | 5.288 | 8951.75 | 2.43 | 98.1 | 78.5 | 1430 | 21.19 | 5818.6 | 3234.5 | 3229.7 | 4670.2 | 1206.5 | 0.67553 | 6.738
2024-12-09 | 21:06 | Data | 0 | 31.333 | 28.571 | 220.735 | 7.62 | 206.964 | 2199.93 | 25.89 | 42.477 | 6.32 | 1.448 | 5.304 | 8960.79 | 2.592 | 98.1 | 78.5 | 1430 | 21.15 | 5824.5 | 3254.4 | 3240.4 | 4696.4 | 1206.5 | 0.67789 | 6.753
2024-12-09 | 21:06 | Data | 0 | 31.009 | 28.895 | 220.825 | 7.62 | 206.919 | 2199.93 | 25.88 | 42.387 | 6.32 | 1.45 | 5.308 | 8960.79 | 2.64 | 98.1 | 78.5 | 1429 | 21.19 | 5824.5 | 3235.1 | 3229.4 | 4675.2 | 1206.5 | 0.67539 | 6.758
2024-12-09 | 21:06 | Data | 0 | 31.137 | 28.578 | 220.78 | 7.62 | 206.964 | 2200.83 | 25.88 | 42.297 | 6.32 | 1.449 | 5.294 | 8947.23 | 2.538 | 98.1 | 78.5 | 1431 | 21.15 | 5815.7 | 3265.5 | 3241.6 | 4699.9 | 1206.5 | 0.67939 | 6.743
2024-12-09 | 21:06 | Data | 0 | 31.184 | 28.362 | 220.825 | 7.62 | 207.055 | 2195.41 | 25.88 | 42.297 | 6.32 | 1.449 | 5.298 | 8938.18 | 2.626 | 98.1 | 78.5 | 1427 | 21.19 | 5809.8 | 3233.9 | 3227.4 | 4669.9 | 1206.5 | 0.67685 | 6.747
2024-12-09 | 21:06 | Data | 0 | 31.002 | 28.571 | 220.735 | 7.62 | 206.919 | 2191.79 | 25.89 | 42.477 | 6.32 | 1.452 | 5.284 | 8938.18 | 2.498 | 98.1 | 78.4 | 1425 | 21.19 | 5809.8 | 3256.8 | 3218.6 | 4678.7 | 1206.5 | 0.68011 | 6.737
2024-12-09 | 21:06 | Data | 0 | 31.339 | 28.585 | 220.825 | 7.62 | 206.964 | 2189.08 | 25.88 | 42.297 | 6.32 | 1.443 | 5.259 | 8938.18 | 2.626 | 98.1 | 78.5 | 1423 | 21.19 | 5809.8 | 3276.2 | 3223.4 | 4691.6 | 1206.5 | 0.68186 | 6.701
2024-12-09 | 21:06 | Data | 0 | 31.468 | 28.7 | 220.87 | 7.62 | 207.055 | 2188.18 | 25.88 | 42.387 | 6.32 | 1.45 | 5.276 | 8938.18 | 2.761 | 98.1 | 78.4 | 1423 | 21.19 | 5809.8 | 3247.7 | 3209.7 | 4666.8 | 1206.5 | 0.67994 | 6.726
2024-12-09 | 21:06 | Data | 0 | 31.346 | 28.922 | 220.916 | 7.62 | 207.055 | 2189.99 | 25.89 | 42.297 | 6.32 | 1.45 | 5.283 | 8920.09 | 2.532 | 98.1 | 78.5 | 1423 | 21.15 | 5798.1 | 3252 | 3202.2 | 4665.9 | 1206.5 | 0.68078 | 6.734
2024-12-09 | 21:07 | Data | 0 | 30.921 | 28.349 | 220.735 | 7.62 | 206.964 | 2189.08 | 25.88 | 42.387 | 6.32 | 1.449 | 5.309 | 8924.61 | 2.511 | 98.1 | 78.6 | 1423 | 21.24 | 5801 | 3263.1 | 3208.8 | 4679.8 | 1206.5 | 0.6807 | 6.759
2024-12-09 | 21:07 | Data | 0 | 31.312 | 28.801 | 220.916 | 7.62 | 206.874 | 2189.08 | 25.88 | 42.387 | 6.32 | 1.455 | 5.317 | 9399.45 | 2.586 | 98.1 | 78.5 | 1423 | 21.19 | 6109.6 | 3238.6 | 3179 | 4640.6 | 1206.5 | 0.6808 | 6.773
2024-12-09 | 21:07 | Data | 0 | 31.555 | 29.031 | 220.78 | 7.62 | 207.055 | 2189.08 | 25.88 | 42.387 | 6.32 | 1.452 | 5.301 | 8938.18 | 2.538 | 98.1 | 78.5 | 1423 | 21.19 | 5809.8 | 3243 | 3191.4 | 4653.1 | 1206.5 | 0.68043 | 6.753
2024-12-09 | 21:07 | Data | 0 | 31.225 | 29.118 | 220.825 | 7.62 | 206.964 | 2189.08 | 25.89 | 42.387 | 6.32 | 1.455 | 5.289 | 8969.84 | 2.647 | 98.1 | 78.4 | 1423 | 21.19 | 5830.4 | 3256.7 | 3208.9 | 4672.5 | 1206.5 | 0.68006 | 6.743
2024-12-09 | 21:07 | Data | 0 | 31.373 | 29.348 | 214.945 | 7.62 | 201.677 | 2187.27 | 25.89 | 42.297 | 6.32 | 1.44 | 5.4 | 8969.84 | 2.329 | 98.1 | 79 | 1422 | 21.19 | 5830.4 | 3202.9 | 3169.5 | 4609.1 | 1206.5 | 0.67887 | 6.85
2024-12-09 | 21:07 | Data | 0 | 31.515 | 29.348 | 215.171 | 7.62 | 201.767 | 2187.27 | 25.89 | 42.387 | 6.32 | 1.43 | 5.218 | 8978.88 | 2.498 | 98.1 | 78.5 | 1421 | 21.19 | 5836.3 | 3192.5 | 3153.1 | 4589.2 | 1206.5 | 0.67909 | 6.65
2024-12-09 | 21:07 | Data | 0 | 31.339 | 29.125 | 216.257 | 7.62 | 202.897 | 2186.37 | 25.88 | 42.297 | 6.32 | 1.434 | 5.19 | 8965.31 | 2.525 | 98.1 | 78.3 | 1421 | 21.19 | 5827.5 | 3211.2 | 3180.5 | 4621.5 | 1206.5 | 0.67816 | 6.624
2024-12-09 | 21:07 | Data | 0 | 31.353 | 28.814 | 217.885 | 7.62 | 204.253 | 2189.08 | 25.88 | 42.658 | 6.32 | 1.436 | 5.191 | 8978.88 | 2.511 | 98.1 | 78.3 | 1422 | 21.33 | 5836.3 | 3210.4 | 3171.4 | 4616.4 | 1206.6 | 0.67887 | 6.626
2024-12-09 | 21:07 | Data | 0 | 31.11 | 28.963 | 219.061 | 7.62 | 205.473 | 2189.08 | 25.89 | 42.658 | 6.32 | 1.44 | 5.235 | 8960.79 | 2.559 | 98.1 | 78.4 | 1423 | 21.28 | 5824.5 | 3227.8 | 3192.4 | 4639.8 | 1206.6 | 0.67943 | 6.675
2024-12-09 | 21:07 | Data | 0 | 31.11 | 28.74 | 219.106 | 7.62 | 205.473 | 2187.27 | 25.88 | 42.658 | 6.33 | 1.432 | 5.253 | 8951.75 | 2.592 | 98 | 78.6 | 1421 | 21.28 | 5818.6 | 3226 | 3170.2 | 4623.9 | 1206.6 | 0.6821 | 6.685
2024-12-09 | 21:07 | Data | 0 | 31.454 | 29.226 | 219.287 | 7.62 | 205.654 | 2188.18 | 25.88 | 42.658 | 6.32 | 1.435 | 5.253 | 8938.18 | 2.437 | 98.1 | 78.6 | 1423 | 21.37 | 5809.8 | 3240.8 | 3169 | 4638.9 | 1206.6 | 0.68194 | 6.688
2024-12-09 | 21:07 | Data | 0 | 31.15 | 28.808 | 219.197 | 7.62 | 205.563 | 2189.99 | 25.89 | 42.568 | 6.33 | 1.445 | 5.276 | 8920.09 | 2.309 | 98.1 | 78.5 | 1423 | 21.33 | 5798.1 | 3237.5 | 3187.1 | 4650 | 1206.6 | 0.68037 | 6.721
2024-12-09 | 21:07 | Data | 0 | 31.846 | 28.949 | 219.287 | 7.62 | 205.654 | 2186.37 | 25.89 | 42.658 | 6.32 | 1.453 | 5.254 | 8924.61 | 2.565 | 98.1 | 78.3 | 1422 | 21.33 | 5801 | 3250 | 3173.7 | 4642.4 | 1206.6 | 0.68568 | 6.708
2024-12-09 | 21:07 | Data | 0 | 31.623 | 29.037 | 219.242 | 7.62 | 205.744 | 2186.37 | 25.89 | 42.658 | 6.33 | 1.447 | 5.279 | 8938.18 | 2.329 | 98 | 78.5 | 1421 | 21.37 | 5809.8 | 3224.4 | 3177.8 | 4629 | 1206.6 | 0.68024 | 6.727
2024-12-09 | 21:07 | Data | 0 | 31.549 | 28.706 | 219.151 | 7.62 | 205.699 | 2182.75 | 25.88 | 42.658 | 6.32 | 1.441 | 5.28 | 8929.14 | 2.687 | 98 | 78.6 | 1419 | 21.37 | 5803.9 | 3241.2 | 3166.3 | 4633.1 | 1206.6 | 0.6833 | 6.72
2024-12-09 | 21:07 | Data | 0 | 31.346 | 29.125 | 219.287 | 7.62 | 205.699 | 2180.95 | 25.88 | 42.658 | 6.33 | 1.449 | 5.255 | 8906.53 | 2.532 | 98 | 78.4 | 1417 | 21.33 | 5789.2 | 3249.5 | 3170.1 | 4642.6 | 1206.6 | 0.68353 | 6.705
2024-12-09 | 21:07 | Data | 0 | 31.569 | 29.125 | 219.332 | 7.62 | 205.654 | 2186.37 | 25.89 | 42.568 | 6.32 | 1.449 | 5.247 | 8911.05 | 2.363 | 98 | 78.4 | 1422 | 21.33 | 5792.2 | 3226 | 3191.3 | 4642.1 | 1206.6 | 0.67876 | 6.696
2024-12-09 | 21:08 | Data | 0 | 31.393 | 28.767 | 219.106 | 7.62 | 205.563 | 2188.18 | 25.88 | 42.748 | 6.32 | 1.453 | 5.244 | 8906.53 | 2.424 | 98 | 78.3 | 1423 | 21.33 | 5789.2 | 3221.8 | 3195.2 | 4652.7 | 1206.6 | 0.6788 | 6.698
2024-12-09 | 21:08 | Data | 0 | 31.569 | 28.632 | 219.332 | 7.62 | 205.789 | 2189.08 | 25.89 | 42.297 | 6.33 | 1.437 | 5.268 | 8911.05 | 2.633 | 98.1 | 78.6 | 1422 | 21.19 | 5792.2 | 3225.9 | 3198.1 | 4648.1 | 1206.6 | 0.67792 | 6.704
2024-12-09 | 21:08 | Data | 0 | 31.468 | 28.612 | 219.423 | 7.62 | 205.744 | 2189.08 | 25.88 | 42.387 | 6.32 | 1.45 | 5.289 | 8874.87 | 2.721 | 98.1 | 78.5 | 1422 | 21.19 | 5768.7 | 3233.4 | 3171.1 | 4629.4 | 1206.6 | 0.68186 | 6.739
2024-12-09 | 21:08 | Data | 0 | 31.339 | 28.808 | 219.287 | 7.62 | 205.654 | 2186.37 | 25.89 | 42.387 | 6.33 | 1.451 | 5.261 | 8883.91 | 2.532 | 98.1 | 78.4 | 1422 | 21.19 | 5774.5 | 3244.2 | 3197.9 | 4658.5 | 1206.6 | 0.68032 | 6.712
2024-12-09 | 21:08 | Data | 0 | 31.036 | 29.017 | 219.332 | 7.62 | 205.744 | 2180.95 | 25.89 | 42.387 | 6.32 | 1.454 | 5.273 | 8888.44 | 2.201 | 98.1 | 78.4 | 1418 | 21.19 | 5777.5 | 3233.8 | 3190 | 4645.5 | 1206.6 | 0.6792 | 6.728
2024-12-09 | 21:08 | Data | 0 | 31.542 | 29.051 | 219.423 | 7.62 | 205.654 | 2183.66 | 25.89 | 42.387 | 6.33 | 1.455 | 5.281 | 8897.48 | 2.478 | 98.1 | 78.4 | 1419 | 21.19 | 5783.4 | 3218.3 | 3184.3 | 4632.9 | 1206.6 | 0.67729 | 6.736
2024-12-09 | 21:08 | Data | 0 | 31.569 | 28.646 | 219.287 | 7.62 | 205.609 | 2180.04 | 25.89 | 42.477 | 6.33 | 1.449 | 5.27 | 8951.75 | 2.626 | 98.1 | 78.4 | 1418 | 21.15 | 5818.6 | 3237.1 | 3203.1 | 4655.6 | 1206.6 | 0.67978 | 6.719
2024-12-09 | 21:08 | Data | 0 | 31.427 | 29.186 | 219.332 | 7.62 | 205.609 | 2182.75 | 25.88 | 42.297 | 6.32 | 1.445 | 5.253 | 8951.75 | 2.538 | 98.1 | 78.4 | 1419 | 21.19 | 5818.6 | 3240.2 | 3200.2 | 4656.8 | 1206.6 | 0.68042 | 6.698
2024-12-09 | 21:08 | Data | 0 | 31.339 | 28.808 | 219.559 | 7.62 | 205.925 | 2182.75 | 25.89 | 42.387 | 6.32 | 1.447 | 5.253 | 8951.75 | 2.532 | 98.1 | 78.4 | 1419 | 21.19 | 5818.6 | 3237.5 | 3163.9 | 4631.1 | 1206.6 | 0.68356 | 6.7
2024-12-09 | 21:08 | Data | 0 | 31.339 | 28.808 | 219.559 | 7.62 | 205.925 | 2182.75 | 25.88 | 42.387 | 6.32 | 1.437 | 5.276 | 8965.31 | 2.417 | 98.1 | 78.6 | 1419 | 21.19 | 5827.5 | 3249.8 | 3196.9 | 4659.7 | 1206.6 | 0.68075 | 6.713
2024-12-09 | 21:08 | Data | 0 | 31.765 | 28.922 | 219.559 | 7.62 | 205.925 | 2181.85 | 25.88 | 42.477 | 6.33 | 1.444 | 5.28 | 8965.31 | 2.64 | 98.1 | 78.5 | 1419 | 21.24 | 5827.5 | 3238.1 | 3181.7 | 4639.8 | 1206.6 | 0.67757 | 6.723
2024-12-09 | 21:08 | Data | 0 | 31.117 | 28.754 | 219.423 | 7.62 | 205.88 | 2183.66 | 25.88 | 42.387 | 6.32 | 1.446 | 5.278 | 8969.84 | 2.532 | 98.1 | 78.5 | 1419 | 21.28 | 5830.4 | 3233.3 | 3176.7 | 4643.4 | 1206.6 | 0.68315 | 6.725
2024-12-09 | 21:08 | Data | 0 | 31.393 | 28.585 | 219.649 | 7.62 | 205.835 | 2187.27 | 25.88 | 42.297 | 6.32 | 1.437 | 5.268 | 8960.79 | 2.545 | 98.1 | 78.6 | 1421 | 21.19 | 5824.5 | 3231.6 | 3183.1 | 4637.4 | 1206.6 | 0.68073 | 6.706
2024-12-09 | 21:08 | Data | 0 | 31.299 | 29.01 | 219.785 | 7.62 | 205.97 | 2182.75 | 25.89 | 42.477 | 6.32 | 1.445 | 5.285 | 8969.84 | 2.464 | 98.1 | 78.5 | 1419 | 21.19 | 5830.4 | 3234 | 3196.6 | 4655.5 | 1206.6 | 0.68088 | 6.73
2024-12-09 | 21:08 | Data | 0 | 31.501 | 28.922 | 219.739 | 7.62 | 205.97 | 2178.24 | 25.88 | 42.387 | 6.32 | 1.448 | 5.269 | 8947.23 | 2.532 | 98.1 | 78.4 | 1416 | 21.15 | 5815.7 | 3234.5 | 3209.9 | 4661.6 | 1206.6 | 0.6774 | 6.717
2024-12-09 | 21:08 | Data | 0 | 31.285 | 28.977 | 219.604 | 7.62 | 205.88 | 2182.75 | 25.89 | 42.387 | 6.32 | 1.443 | 5.26 | 8933.66 | 2.505 | 98.1 | 78.5 | 1418 | 21.24 | 5806.9 | 3222 | 3186.2 | 4637.6 | 1206.6 | 0.67812 | 6.702
2024-12-09 | 21:08 | Data | 0 | 31.11 | 28.747 | 219.604 | 7.62 | 205.88 | 2186.37 | 25.89 | 42.387 | 6.33 | 1.435 | 5.27 | 8915.57 | 2.532 | 98.1 | 78.6 | 1422 | 21.19 | 5795.1 | 3238.4 | 3197.2 | 4651.6 | 1206.6 | 0.67992 | 6.705
2024-12-09 | 21:08 | Data | 0 | 31.13 | 28.585 | 219.468 | 7.62 | 205.88 | 2187.27 | 25.88 | 42.387 | 6.32 | 1.445 | 5.267 | 8911.05 | 2.511 | 98.1 | 78.5 | 1422 | 21.19 | 5792.2 | 3233.4 | 3181 | 4636.9 | 1206.6 | 0.68117 | 6.713
2024-12-09 | 21:09 | Data | 0 | 31.731 | 28.774 | 219.559 | 7.62 | 206.015 | 2192.7 | 25.88 | 42.387 | 6.32 | 1.435 | 5.276 | 8911.05 | 2.701 | 98.1 | 78.6 | 1425 | 21.19 | 5792.2 | 3223.8 | 3167.9 | 4625.1 | 1206.6 | 0.68127 | 6.711
2024-12-09 | 21:09 | Data | 0 | 31.346 | 29.064 | 219.649 | 7.62 | 206.015 | 2191.79 | 25.88 | 42.387 | 6.32 | 1.441 | 5.276 | 8924.61 | 2.647 | 98.1 | 78.5 | 1425 | 21.24 | 5801 | 3227.3 | 3195 | 4646.5 | 1206.6 | 0.67833 | 6.716
2024-12-09 | 21:09 | Data | 0 | 31.454 | 28.646 | 219.649 | 7.62 | 206.015 | 2190.89 | 25.88 | 42.387 | 6.32 | 1.444 | 5.285 | 8924.61 | 2.478 | 98.1 | 78.5 | 1425 | 21.19 | 5801 | 3227.4 | 3203.5 | 4648.9 | 1206.6 | 0.67746 | 6.731
2024-12-09 | 21:09 | Data | 0 | 31.65 | 28.747 | 219.739 | 7.62 | 206.015 | 2194.5 | 25.89 | 42.206 | 6.32 | 1.433 | 5.248 | 8906.53 | 2.579 | 98.1 | 78.5 | 1426 | 21.15 | 5789.2 | 3254.1 | 3144.4 | 4626.6 | 1206.6 | 0.68828 | 6.682
2024-12-09 | 21:09 | Data | 0 | 31.535 | 28.808 | 219.604 | 7.62 | 206.015 | 2194.5 | 25.88 | 42.387 | 6.31 | 1.428 | 5.27 | 8924.61 | 2.748 | 98.1 | 78.7 | 1426 | 21.19 | 5801 | 3233.2 | 3147.4 | 4620.4 | 1206.6 | 0.68392 | 6.698
2024-12-09 | 21:09 | Data | 0 | 31.576 | 29.206 | 219.739 | 7.62 | 206.06 | 2197.22 | 25.89 | 42.387 | 6.32 | 1.443 | 5.278 | 8712.07 | 2.43 | 98.1 | 78.5 | 1428 | 21.19 | 5662.8 | 3221.7 | 3186.5 | 4633.3 | 1206.7 | 0.67787 | 6.721
2024-12-09 | 21:09 | Data | 0 | 31.346 | 28.605 | 219.513 | 7.62 | 205.97 | 2199.02 | 25.88 | 42.477 | 6.32 | 1.45 | 5.289 | 8716.59 | 2.707 | 98.1 | 78.5 | 1430 | 21.19 | 5665.8 | 3221.5 | 3177 | 4630.7 | 1206.7 | 0.68067 | 6.739
2024-12-09 | 21:09 | Data | 0 | 31.454 | 28.808 | 219.559 | 7.62 | 205.97 | 2199.02 | 25.88 | 42.387 | 6.32 | 1.451 | 5.266 | 8712.07 | 2.694 | 98.1 | 78.4 | 1429 | 21.19 | 5662.8 | 3232.2 | 3174.1 | 4633.1 | 1206.7 | 0.68116 | 6.717
2024-12-09 | 21:09 | Data | 0 | 31.339 | 28.686 | 219.513 | 7.62 | 205.925 | 2199.93 | 25.88 | 42.387 | 6.32 | 1.45 | 5.254 | 8707.55 | 2.532 | 98.1 | 78.4 | 1430 | 21.15 | 5659.9 | 3231.6 | 3178.6 | 4637.2 | 1206.7 | 0.68068 | 6.705
2024-12-09 | 21:09 | Data | 0 | 31.15 | 28.639 | 219.649 | 7.62 | 205.925 | 2199.93 | 25.89 | 42.387 | 6.32 | 1.445 | 5.252 | 8911.05 | 2.41 | 98.1 | 78.4 | 1429 | 21.19 | 5792.2 | 3237.5 | 3172.6 | 4638.3 | 1206.7 | 0.68207 | 6.698
2024-12-09 | 21:09 | Data | 0 | 31.15 | 28.754 | 219.559 | 7.62 | 205.88 | 2199.02 | 25.88 | 42.387 | 6.33 | 1.444 | 5.247 | 8888.44 | 2.538 | 98.1 | 78.4 | 1429 | 21.24 | 5777.5 | 3254.7 | 3181.4 | 4654.4 | 1206.7 | 0.68297 | 6.69
2024-12-09 | 21:09 | Data | 0 | 31.339 | 28.977 | 219.649 | 7.62 | 206.015 | 2273.14 | 25.88 | 42.387 | 6.32 | 1.434 | 5.271 | 8888.44 | 2.565 | 98.1 | 78.6 | 1481 | 21.19 | 5777.5 | 3232.8 | 3185.7 | 4641.2 | 1206.7 | 0.68017 | 6.706
2024-12-09 | 21:09 | Data | 0 | 31.117 | 28.808 | 219.649 | 7.62 | 205.925 | 2294.83 | 25.89 | 42.477 | 6.32 | 1.441 | 5.267 | 8888.44 | 2.478 | 98.1 | 78.5 | 1485 | 21.19 | 5777.5 | 3243.1 | 3188.2 | 4650.4 | 1206.7 | 0.68142 | 6.708
2024-12-09 | 21:09 | Data | 0 | 31.292 | 28.632 | 219.785 | 7.62 | 206.106 | 2193.6 | 25.89 | 42.387 | 6.33 | 1.445 | 5.247 | 8888.44 | 2.262 | 98.1 | 78.4 | 1426 | 21.19 | 5777.5 | 3248.9 | 3185.4 | 4653.6 | 1206.7 | 0.68163 | 6.69
2024-12-09 | 21:09 | Data | 0 | 31.339 | 29.01 | 219.875 | 7.62 | 206.241 | 2193.6 | 25.88 | 42.387 | 6.32 | 1.449 | 5.267 | 8865.83 | 2.478 | 98.1 | 78.4 | 1426 | 21.19 | 5762.8 | 3224.1 | 3180 | 4634.7 | 1206.7 | 0.67936 | 6.716
2024-12-09 | 21:09 | Data | 0 | 31.312 | 28.808 | 219.875 | 7.62 | 206.06 | 2194.5 | 25.89 | 42.297 | 6.32 | 1.448 | 5.279 | 8897.48 | 2.701 | 98.1 | 78.5 | 1426 | 21.15 | 5783.4 | 3240.6 | 3167.2 | 4632.8 | 1206.7 | 0.6826 | 6.725
2024-12-09 | 21:09 | Data | 0 | 31.231 | 28.808 | 219.83 | 7.62 | 206.06 | 2193.6 | 25.88 | 42.297 | 6.32 | 1.446 | 5.278 | 8920.09 | 2.505 | 98.1 | 78.5 | 1426 | 21.15 | 5798.1 | 3244.5 | 3168.1 | 4633.4 | 1206.7 | 0.68364 | 6.725
2024-12-09 | 21:09 | Data | 0 | 31.339 | 28.963 | 220.101 | 7.62 | 206.151 | 2189.08 | 25.89 | 42.477 | 6.32 | 1.443 | 5.257 | 8911.05 | 2.491 | 98.1 | 78.5 | 1423 | 21.15 | 5792.2 | 3232.1 | 3178.8 | 4638.7 | 1206.7 | 0.67996 | 6.7
2024-12-09 | 21:10 | Data | 0 | 31.542 | 29.058 | 219.875 | 7.62 | 206.241 | 2194.5 | 25.89 | 42.568 | 6.32 | 1.442 | 5.243 | 8911.05 | 2.484 | 98.1 | 78.4 | 1426 | 21.19 | 5792.2 | 3245 | 3182 | 4650.2 | 1206.7 | 0.68134 | 6.685
2024-12-09 | 21:10 | Data | 0 | 31.542 | 28.929 | 219.966 | 7.63 | 206.241 | 2193.6 | 25.88 | 42.387 | 6.32 | 1.448 | 5.253 | 8915.57 | 2.545 | 98.1 | 78.4 | 1426 | 21.24 | 5795.1 | 3252.4 | 3182.3 | 4651.2 | 1206.7 | 0.68362 | 6.702
2024-12-09 | 21:10 | Data | 0 | 31.171 | 28.794 | 220.056 | 7.62 | 206.151 | 2196.31 | 25.89 | 42.477 | 6.32 | 1.446 | 5.273 | 8897.48 | 2.451 | 98.1 | 78.5 | 1428 | 21.15 | 5783.4 | 3239.4 | 3194.8 | 4651.8 | 1206.7 | 0.68042 | 6.719
2024-12-09 | 21:10 | Data | 0 | 31.191 | 28.578 | 219.875 | 7.62 | 206.151 | 2194.5 | 25.89 | 42.477 | 6.32 | 1.436 | 5.267 | 8883.91 | 2.525 | 98.1 | 78.6 | 1426 | 21.19 | 5774.5 | 3258.1 | 3176.5 | 4654.8 | 1206.7 | 0.68339 | 6.703
2024-12-09 | 21:10 | Data | 0 | 31.873 | 29.037 | 220.011 | 7.62 | 206.241 | 2191.79 | 25.89 | 42.387 | 6.32 | 1.44 | 5.279 | 8883.91 | 2.457 | 98.1 | 78.6 | 1425 | 21.19 | 5774.5 | 3234.7 | 3168.9 | 4630.4 | 1206.7 | 0.68223 | 6.718
2024-12-09 | 21:10 | Data | 0 | 31.117 | 28.808 | 219.875 | 7.62 | 206.106 | 2191.79 | 25.86 | 42.387 | 6.32 | 1.441 | 5.277 | 8902 | 2.424 | 98.1 | 78.6 | 1425 | 21.19 | 5786.3 | 3233.6 | 3187.4 | 4644 | 1206.7 | 0.67964 | 6.717
2024-12-09 | 21:10 | Data | 0 | 31.711 | 29.091 | 219.92 | 7.62 | 206.241 | 2197.22 | 25.89 | 42.387 | 6.32 | 1.449 | 5.285 | 9354.23 | 2.532 | 98.1 | 78.5 | 1429 | 21.19 | 6080.2 | 3240.2 | 3185.1 | 4648 | 1206.7 | 0.68111 | 6.734
2024-12-09 | 21:10 | Data | 0 | 31.333 | 29.078 | 219.92 | 7.62 | 206.196 | 2197.22 | 25.88 | 42.387 | 6.32 | 1.452 | 5.283 | 8974.36 | 2.424 | 98.1 | 78.4 | 1428 | 21.19 | 5833.3 | 3247.2 | 3199.4 | 4660.6 | 1206.7 | 0.68127 | 6.735
2024-12-09 | 21:10 | Data | 0 | 31.812 | 28.848 | 219.966 | 7.62 | 206.377 | 2196.31 | 25.88 | 42.387 | 6.32 | 1.453 | 5.28 | 8956.27 | 2.741 | 98.1 | 78.4 | 1428 | 21.19 | 5821.6 | 3220.6 | 3186.4 | 4636.8 | 1206.7 | 0.67858 | 6.735
2024-12-09 | 21:10 | Data | 0 | 31.339 | 28.808 | 219.92 | 7.62 | 206.106 | 2196.31 | 25.89 | 42.387 | 6.33 | 1.454 | 5.264 | 8965.31 | 2.538 | 98.1 | 78.4 | 1428 | 21.19 | 5827.5 | 3242.6 | 3193.5 | 4652.3 | 1206.7 | 0.68166 | 6.719
2024-12-09 | 21:10 | Data | 0 | 31.184 | 28.794 | 219.92 | 7.62 | 206.196 | 2200.83 | 25.88 | 42.387 | 6.32 | 1.443 | 5.259 | 8965.31 | 2.437 | 98.1 | 78.5 | 1431 | 21.19 | 5827.5 | 3229.8 | 3186.7 | 4639 | 1206.7 | 0.67967 | 6.702
2024-12-09 | 21:10 | Data | 0 | 31.542 | 28.659 | 219.92 | 7.62 | 206.241 | 2193.6 | 25.89 | 42.387 | 6.32 | 1.443 | 5.255 | 8915.57 | 2.707 | 98.1 | 78.5 | 1426 | 21.19 | 5795.1 | 3223 | 3195.8 | 4642.2 | 1206.7 | 0.67791 | 6.698
2024-12-09 | 21:10 | Data | 0 | 31.339 | 28.646 | 219.785 | 7.62 | 206.06 | 2197.22 | 25.88 | 42.387 | 6.32 | 1.448 | 5.27 | 8906.53 | 2.518 | 98.1 | 78.5 | 1429 | 21.19 | 5789.2 | 3226.2 | 3153.6 | 4630.7 | 1206.7 | 0.68434 | 6.717
2024-12-09 | 21:10 | Data | 0 | 31.339 | 28.7 | 219.875 | 7.62 | 206.151 | 2309.29 | 25.88 | 42.477 | 6.32 | 1.452 | 5.233 | 8911.05 | 2.505 | 98.2 | 78.3 | 1499 | 21.24 | 5792.2 | 3240.2 | 3193.4 | 4654.8 | 1206.7 | 0.67898 | 6.685
2024-12-09 | 21:10 | Data | 0 | 31.36 | 28.808 | 220.011 | 7.63 | 206.332 | 2191.79 | 25.88 | 42.387 | 6.32 | 1.441 | 5.253 | 8915.57 | 2.532 | 98.1 | 78.5 | 1425 | 21.15 | 5795.1 | 3237.4 | 3234.4 | 4679.5 | 1206.7 | 0.67537 | 6.694
2024-12-09 | 21:10 | Data | 0 | 31.11 | 28.686 | 219.92 | 7.62 | 206.241 | 2190.89 | 25.88 | 42.297 | 6.32 | 1.448 | 5.253 | 8920.09 | 2.484 | 98.1 | 78.4 | 1425 | 21.19 | 5798.1 | 3243.3 | 3215.5 | 4669.4 | 1206.7 | 0.6783 | 6.702
2024-12-09 | 21:10 | Data | 0 | 31.13 | 28.963 | 220.192 | 7.62 | 206.422 | 2192.7 | 25.89 | 42.477 | 6.32 | 1.451 | 5.268 | 8929.14 | 2.329 | 98.1 | 78.4 | 1425 | 21.19 | 5803.9 | 3232.8 | 3204.9 | 4655.8 | 1206.7 | 0.67737 | 6.717
2024-12-09 | 21:10 | Data | 0 | 31.245 | 28.571 | 220.101 | 7.62 | 206.422 | 2190.89 | 25.88 | 42.568 | 6.32 | 1.455 | 5.294 | 8924.61 | 2.545 | 98.1 | 78.4 | 1425 | 21.24 | 5801 | 3236.2 | 3218.1 | 4664.9 | 1206.7 | 0.67548 | 6.747
2024-12-09 | 21:11 | Data | 0 | 31.731 | 28.97 | 220.101 | 7.62 | 206.332 | 2190.89 | 25.88 | 42.658 | 6.32 | 1.451 | 5.279 | 8892.96 | 2.532 | 98.1 | 78.4 | 1425 | 21.33 | 5780.4 | 3225.1 | 3213.2 | 4655.9 | 1206.7 | 0.67627 | 6.729
2024-12-09 | 21:11 | Data | 0 | 31.184 | 28.403 | 220.011 | 7.62 | 206.467 | 2192.7 | 25.86 | 42.748 | 6.32 | 1.442 | 5.28 | 8938.18 | 2.653 | 98.1 | 78.5 | 1425 | 21.33 | 5809.8 | 3243 | 3206.5 | 4661.9 | 1206.8 | 0.67948 | 6.723
2024-12-09 | 21:11 | Data | 0 | 31.508 | 29.017 | 220.056 | 7.62 | 206.377 | 2189.99 | 25.88 | 42.658 | 6.32 | 1.447 | 5.287 | 8965.31 | 2.552 | 98.1 | 78.5 | 1423 | 21.33 | 5827.5 | 3243 | 3182.6 | 4647.9 | 1206.8 | 0.68149 | 6.734
2024-12-09 | 21:11 | Data | 0 | 31.778 | 28.97 | 220.237 | 7.62 | 206.512 | 2183.66 | 25.89 | 42.387 | 6.32 | 1.453 | 5.293 | 8956.27 | 2.444 | 98.1 | 78.5 | 1419 | 21.15 | 5821.6 | 3236.3 | 3204.4 | 4658.1 | 1206.8 | 0.67828 | 6.747
2024-12-09 | 21:11 | Data | 0 | 31.677 | 28.652 | 220.147 | 7.62 | 206.422 | 2190.89 | 25.88 | 42.477 | 6.32 | 1.45 | 5.298 | 8969.84 | 2.748 | 98.1 | 78.5 | 1424 | 21.19 | 5830.4 | 3255.9 | 3233.6 | 4687.5 | 1206.8 | 0.67825 | 6.747
2024-12-09 | 21:11 | Data | 0 | 31.339 | 28.902 | 220.101 | 7.62 | 206.422 | 2191.79 | 25.88 | 42.387 | 6.32 | 1.448 | 5.286 | 8965.31 | 2.613 | 98.1 | 78.5 | 1425 | 21.24 | 5827.5 | 3254.9 | 3283.2 | 4720.7 | 1206.8 | 0.6761 | 6.733
2024-12-09 | 21:11 | Data | 0 | 31.252 | 28.949 | 220.101 | 7.62 | 206.467 | 2189.08 | 25.88 | 42.477 | 6.32 | 1.436 | 5.284 | 8911.05 | 2.599 | 98.1 | 78.6 | 1423 | 21.15 | 5792.2 | 3237.7 | 3260.6 | 4698.5 | 1206.8 | 0.67213 | 6.719
2024-12-09 | 21:11 | Data | 0 | 31.792 | 29.037 | 220.282 | 7.62 | 206.512 | 2189.08 | 25.88 | 42.387 | 6.32 | 1.445 | 5.286 | 8924.61 | 2.532 | 98.1 | 78.5 | 1422 | 21.19 | 5801 | 3238.6 | 3243.1 | 4683.6 | 1206.8 | 0.67509 | 6.73
2024-12-09 | 21:11 | Data | 0 | 31.312 | 28.808 | 220.011 | 7.62 | 206.422 | 2191.79 | 25.89 | 42.387 | 6.32 | 1.448 | 5.266 | 8915.57 | 2.532 | 98.1 | 78.4 | 1425 | 21.19 | 5795.1 | 3237.6 | 3252.1 | 4690.9 | 1206.8 | 0.67431 | 6.714
2024-12-09 | 21:11 | Data | 0 | 31.096 | 28.625 | 220.147 | 7.62 | 206.377 | 2191.79 | 25.88 | 42.387 | 6.32 | 1.45 | 5.292 | 8920.09 | 2.64 | 98.1 | 78.5 | 1425 | 21.19 | 5798.1 | 3251.4 | 3222.1 | 4675.9 | 1206.8 | 0.67907 | 6.741
2024-12-09 | 21:11 | Data | 0 | 31.792 | 29.037 | 220.192 | 7.62 | 206.512 | 2191.79 | 25.88 | 42.387 | 6.33 | 1.449 | 5.298 | 8969.84 | 2.552 | 98.1 | 78.5 | 1425 | 21.19 | 5830.4 | 3253 | 3217.3 | 4677 | 1206.8 | 0.67821 | 6.746
2024-12-09 | 21:11 | Data | 0 | 31.117 | 28.97 | 219.966 | 7.61 | 206.241 | 2194.5 | 25.88 | 42.387 | 6.32 | 1.457 | 5.268 | 8974.36 | 2.619 | 98.1 | 78.3 | 1427 | 21.19 | 5833.3 | 3230.3 | 3203.8 | 4654.3 | 1206.8 | 0.67749 | 6.725
2024-12-09 | 21:11 | Data | 0 | 31.481 | 28.814 | 219.92 | 7.62 | 206.422 | 2194.5 | 25.88 | 42.658 | 6.32 | 1.454 | 5.286 | 8996.97 | 2.437 | 98.1 | 78.4 | 1426 | 21.33 | 5848 | 3246.5 | 3231 | 4681.4 | 1206.8 | 0.67784 | 6.738
2024-12-09 | 21:11 | Data | 0 | 31.339 | 28.922 | 220.282 | 7.62 | 206.422 | 2194.5 | 25.88 | 42.477 | 6.32 | 1.451 | 5.277 | 8978.88 | 2.647 | 98.1 | 78.4 | 1426 | 21.24 | 5836.3 | 3221.2 | 3218.7 | 4658.6 | 1206.8 | 0.67504 | 6.727
2024-12-09 | 21:11 | Data | 0 | 31.454 | 29.037 | 220.192 | 7.62 | 206.467 | 2193.6 | 25.89 | 42.477 | 6.32 | 1.45 | 5.263 | 8969.84 | 2.525 | 98.1 | 78.4 | 1426 | 21.24 | 5830.4 | 3240.5 | 3190.9 | 4655.2 | 1206.8 | 0.67905 | 6.713
2024-12-09 | 21:11 | Data | 0 | 31.13 | 28.808 | 220.147 | 7.62 | 206.512 | 2197.22 | 25.88 | 42.477 | 6.32 | 1.454 | 5.269 | 8938.18 | 2.424 | 98.1 | 78.4 | 1428 | 21.28 | 5809.8 | 3239.2 | 3235.9 | 4678.1 | 1206.8 | 0.67595 | 6.722
2024-12-09 | 21:11 | Data | 0 | 31.117 | 28.578 | 220.011 | 7.62 | 206.377 | 2194.5 | 25.86 | 42.477 | 6.32 | 1.443 | 5.307 | 8951.75 | 2.511 | 98.1 | 78.6 | 1426 | 21.19 | 5818.6 | 3230.8 | 3213.4 | 4656.5 | 1206.8 | 0.67602 | 6.75
2024-12-09 | 21:12 | Data | 0 | 31.346 | 28.949 | 220.192 | 7.62 | 206.467 | 2194.5 | 25.89 | 42.477 | 6.32 | 1.441 | 5.258 | 8951.75 | 2.478 | 98.1 | 78.5 | 1426 | 21.15 | 5818.6 | 3249.4 | 3248.9 | 4698.5 | 1206.8 | 0.67548 | 6.698
2024-12-09 | 21:12 | Data | 0 | 31.117 | 28.808 | 220.011 | 7.62 | 206.332 | 2195.41 | 25.88 | 42.477 | 6.32 | 1.434 | 5.267 | 8947.23 | 2.478 | 98.1 | 78.6 | 1426 | 21.19 | 5815.7 | 3233.5 | 3206 | 4651.9 | 1206.8 | 0.67896 | 6.701
2024-12-09 | 21:12 | Data | 0 | 31.177 | 28.578 | 220.147 | 7.62 | 206.377 | 2194.5 | 25.88 | 42.387 | 6.31 | 1.447 | 5.252 | 8951.75 | 2.538 | 98.1 | 78.4 | 1426 | 21.19 | 5818.6 | 3259 | 3213.3 | 4681.4 | 1206.8 | 0.67962 | 6.7
2024-12-09 | 21:12 | Data | 0 | 31.339 | 28.808 | 220.192 | 7.62 | 206.377 | 2194.5 | 25.88 | 42.297 | 6.32 | 1.453 | 5.279 | 8951.75 | 2.532 | 98.1 | 78.4 | 1426 | 21.15 | 5818.6 | 3249.7 | 3222.9 | 4678.7 | 1206.8 | 0.67829 | 6.732
2024-12-09 | 21:12 | Data | 0 | 31.454 | 28.646 | 220.056 | 7.62 | 206.422 | 2193.6 | 25.88 | 42.387 | 6.32 | 1.462 | 5.267 | 8933.66 | 2.538 | 98.1 | 78.3 | 1426 | 21.24 | 5806.9 | 3258.8 | 3217.2 | 4677.5 | 1206.8 | 0.68026 | 6.729
2024-12-09 | 21:12 | Data | 0 | 31.326 | 28.808 | 220.101 | 7.62 | 206.377 | 2194.5 | 25.88 | 42.477 | 6.32 | 1.46 | 5.281 | 8960.79 | 2.647 | 98.1 | 78.4 | 1426 | 21.19 | 5824.5 | 3248.1 | 3226.9 | 4679 | 1206.8 | 0.67759 | 6.74
2024-12-09 | 21:12 | Data | 0 | 31.339 | 28.814 | 220.056 | 7.62 | 206.422 | 2203.54 | 25.88 | 42.387 | 6.32 | 1.443 | 5.264 | 8938.18 | 2.525 | 98.1 | 78.5 | 1432 | 21.19 | 5809.8 | 3241.1 | 3235.2 | 4681.9 | 1206.8 | 0.67612 | 6.707
2024-12-09 | 21:12 | Data | 0 | 31.339 | 28.808 | 220.192 | 7.62 | 206.422 | 2199.93 | 25.88 | 42.387 | 6.32 | 1.449 | 5.263 | 8951.75 | 2.532 | 98.1 | 78.4 | 1429 | 21.24 | 5818.6 | 3227 | 3250.9 | 4688.3 | 1206.8 | 0.67199 | 6.712
2024-12-09 | 21:12 | Data | 0 | 31.245 | 28.895 | 220.101 | 7.62 | 206.467 | 2197.22 | 25.89 | 42.297 | 6.32 | 1.449 | 5.28 | 8951.75 | 2.424 | 98.1 | 78.5 | 1429 | 21.19 | 5818.6 | 3242.8 | 3233.1 | 4683.9 | 1206.8 | 0.67633 | 6.729
2024-12-09 | 21:12 | Data | 0 | 31.339 | 28.754 | 219.966 | 7.62 | 206.332 | 2195.41 | 25.88 | 42.387 | 6.32 | 1.454 | 5.281 | 8911.05 | 2.437 | 98.1 | 78.4 | 1428 | 21.19 | 5792.2 | 3249 | 3243.1 | 4692 | 1206.8 | 0.67619 | 6.736
2024-12-09 | 21:12 | Data | 0 | 31.339 | 29.01 | 220.011 | 7.63 | 206.377 | 2203.54 | 25.89 | 42.387 | 6.32 | 1.458 | 5.267 | 8906.53 | 2.471 | 98.1 | 78.3 | 1432 | 21.15 | 5789.2 | 3250.4 | 3243.7 | 4694.9 | 1206.8 | 0.67429 | 6.726
2024-12-09 | 21:12 | Data | 0 | 31.562 | 28.909 | 220.056 | 7.62 | 206.422 | 2201.74 | 25.88 | 42.387 | 6.32 | 1.445 | 5.275 | 8897.48 | 2.471 | 98.1 | 78.5 | 1431 | 21.19 | 5783.4 | 3248.4 | 3259.2 | 4703.4 | 1206.8 | 0.67449 | 6.72
2024-12-09 | 21:12 | Data | 0 | 31.474 | 28.814 | 220.101 | 7.62 | 206.467 | 2199.93 | 25.88 | 42.387 | 6.33 | 1.435 | 5.312 | 8902 | 2.37 | 98.1 | 78.7 | 1431 | 21.24 | 5786.3 | 3243.9 | 3223.7 | 4672.6 | 1206.8 | 0.67845 | 6.747
2024-12-09 | 21:12 | Data | 0 | 31.11 | 28.801 | 220.147 | 7.62 | 206.467 | 2199.02 | 25.88 | 42.477 | 6.32 | 1.445 | 5.294 | 8911.05 | 2.444 | 98.1 | 78.6 | 1429 | 21.19 | 5792.2 | 3236.9 | 3232.3 | 4674.4 | 1206.8 | 0.67596 | 6.739
2024-12-09 | 21:12 | Data | 0 | 31.501 | 29.017 | 219.966 | 7.62 | 206.467 | 2196.31 | 25.89 | 42.477 | 6.32 | 1.452 | 5.252 | 8920.09 | 2.559 | 98.1 | 78.3 | 1428 | 21.24 | 5798.1 | 3260.7 | 3225.8 | 4687.6 | 1206.8 | 0.67904 | 6.706
2024-12-09 | 21:12 | Data | 0 | 31.353 | 28.646 | 219.966 | 7.62 | 206.332 | 2197.22 | 25.89 | 42.387 | 6.32 | 1.443 | 5.286 | 8920.09 | 2.525 | 98.1 | 78.5 | 1428 | 21.15 | 5798.1 | 3237.6 | 3207.9 | 4663.8 | 1206.8 | 0.67682 | 6.729
2024-12-09 | 21:12 | Data | 0 | 31.555 | 29.024 | 220.147 | 7.63 | 206.467 | 2196.31 | 25.89 | 42.297 | 6.32 | 1.433 | 5.287 | 8920.09 | 2.586 | 98.1 | 78.7 | 1428 | 21.19 | 5798.1 | 3246.1 | 3181.5 | 4659.6 | 1206.8 | 0.68142 | 6.72
2024-12-09 | 21:12 | Data | 0 | 31.339 | 28.706 | 220.147 | 7.62 | 206.377 | 2197.22 | 25.88 | 42.387 | 6.33 | 1.434 | 5.278 | 8924.61 | 2.707 | 98.1 | 78.6 | 1428 | 21.24 | 5801 | 3246.7 | 3216.8 | 4673.6 | 1206.9 | 0.67772 | 6.711
2024-12-09 | 21:13 | Data | 0 | 31.366 | 28.814 | 220.011 | 7.62 | 206.377 | 2197.22 | 25.88 | 42.387 | 6.32 | 1.458 | 5.268 | 8951.75 | 2.525 | 98.1 | 78.3 | 1428 | 21.19 | 5818.6 | 3248.4 | 3217.7 | 4671.3 | 1206.9 | 0.67874 | 6.725
2024-12-09 | 21:13 | Data | 0 | 31.258 | 28.808 | 220.101 | 7.62 | 206.467 | 2191.79 | 25.88 | 42.387 | 6.32 | 1.447 | 5.255 | 8951.75 | 2.437 | 98.1 | 78.4 | 1425 | 21.24 | 5818.6 | 3252.6 | 3248.8 | 4696.3 | 1206.9 | 0.67717 | 6.701
2024-12-09 | 21:13 | Data | 0 | 31.238 | 28.632 | 220.237 | 7.63 | 206.512 | 2197.22 | 25.88 | 42.477 | 6.32 | 1.446 | 5.292 | 8956.27 | 2.316 | 98.1 | 78.5 | 1428 | 21.19 | 5821.6 | 3229.1 | 3221.3 | 4662.9 | 1206.9 | 0.67594 | 6.735
2024-12-09 | 21:13 | Data | 0 | 31.339 | 28.808 | 220.056 | 7.62 | 206.332 | 2197.22 | 25.88 | 42.387 | 6.32 | 1.448 | 5.298 | 8951.75 | 2.532 | 98.1 | 78.5 | 1428 | 21.19 | 5818.6 | 3242.5 | 3211.5 | 4665.4 | 1206.9 | 0.67787 | 6.746
2024-12-09 | 21:13 | Data | 0 | 31.454 | 29.139 | 220.147 | 7.62 | 206.377 | 2199.02 | 25.89 | 42.116 | 6.31 | 1.443 | 5.298 | 8933.66 | 2.68 | 98.1 | 78.6 | 1429 | 21.01 | 5806.9 | 3248.5 | 3260.4 | 4707.7 | 1206.9 | 0.67509 | 6.741
2024-12-09 | 21:13 | Data | 0 | 31.542 | 29.361 | 220.282 | 7.62 | 206.467 | 2200.83 | 25.88 | 42.387 | 6.32 | 1.447 | 5.293 | 8924.61 | 2.484 | 98.1 | 78.5 | 1430 | 21.15 | 5801 | 3232.3 | 3234.1 | 4673.9 | 1206.9 | 0.67436 | 6.74
2024-12-09 | 21:13 | Data | 0 | 31.184 | 28.808 | 220.192 | 7.62 | 206.467 | 2199.93 | 25.89 | 42.387 | 6.32 | 1.435 | 5.29 | 8911.05 | 2.322 | 98.1 | 78.7 | 1429 | 21.19 | 5792.2 | 3246.4 | 3209.6 | 4666.3 | 1206.9 | 0.68073 | 6.727
2024-12-09 | 21:13 | Data | 0 | 31.11 | 28.571 | 220.147 | 7.63 | 206.377 | 2199.93 | 25.88 | 42.387 | 6.33 | 1.436 | 5.27 | 8924.61 | 2.538 | 98.1 | 78.6 | 1431 | 21.24 | 5801 | 3243.9 | 3208 | 4666.5 | 1206.9 | 0.67871 | 6.706
2024-12-09 | 21:13 | Data | 0 | 31.117 | 28.828 | 220.011 | 7.62 | 206.377 | 2195.41 | 25.88 | 42.477 | 6.32 | 1.44 | 5.242 | 8892.96 | 2.484 | 98.1 | 78.5 | 1427 | 21.19 | 5780.4 | 3237.8 | 3189.8 | 4647.7 | 1206.9 | 0.6806 | 6.682
2024-12-09 | 21:13 | Data | 0 | 31.339 | 29.01 | 220.056 | 7.62 | 206.467 | 2194.5 | 25.88 | 42.387 | 6.33 | 1.442 | 5.26 | 8883.91 | 2.505 | 98.1 | 78.5 | 1426 | 21.19 | 5774.5 | 3246.2 | 3188.1 | 4652.3 | 1206.9 | 0.68167 | 6.702
2024-12-09 | 21:13 | Data | 0 | 31.562 | 28.808 | 220.282 | 7.62 | 206.377 | 2194.5 | 25.89 | 42.297 | 6.32 | 1.446 | 5.281 | 8897.48 | 2.586 | 98.1 | 78.5 | 1426 | 21.19 | 5783.4 | 3252.2 | 3193.3 | 4661 | 1206.9 | 0.68138 | 6.727
2024-12-09 | 21:13 | Data | 0 | 31.15 | 28.895 | 220.147 | 7.62 | 206.512 | 2193.6 | 25.89 | 42.387 | 6.32 | 1.447 | 5.264 | 8911.05 | 2.221 | 98.1 | 78.4 | 1426 | 21.19 | 5792.2 | 3247.7 | 3194.7 | 4661.1 | 1206.9 | 0.68038 | 6.712
2024-12-09 | 21:13 | Data | 0 | 31.508 | 29.01 | 220.056 | 7.62 | 206.467 | 2194.5 | 25.88 | 42.297 | 6.32 | 1.452 | 5.249 | 8965.31 | 2.748 | 98.1 | 78.3 | 1426 | 21.15 | 5827.5 | 3261.2 | 3213.3 | 4677 | 1206.9 | 0.68055 | 6.699
2024-12-09 | 21:13 | Data | 0 | 31.333 | 28.754 | 220.101 | 7.62 | 206.332 | 2194.5 | 25.88 | 42.477 | 6.32 | 1.449 | 5.279 | 8947.23 | 2.532 | 98.1 | 78.5 | 1426 | 21.24 | 5815.7 | 3241.3 | 3235.5 | 4678.2 | 1206.9 | 0.67662 | 6.727
2024-12-09 | 21:13 | Data | 0 | 31.427 | 29.01 | 220.011 | 7.62 | 206.377 | 2194.5 | 25.88 | 42.387 | 6.32 | 1.444 | 5.287 | 8956.27 | 2.579 | 98.1 | 78.5 | 1426 | 21.28 | 5821.6 | 3242.5 | 3253.7 | 4698.8 | 1206.9 | 0.67454 | 6.732
2024-12-09 | 21:13 | Data | 0 | 31.299 | 28.632 | 220.282 | 7.62 | 206.512 | 2192.7 | 25.88 | 42.387 | 6.32 | 1.441 | 5.267 | 8956.27 | 2.498 | 98.1 | 78.5 | 1425 | 21.19 | 5821.6 | 3232.7 | 3244.8 | 4680.5 | 1206.9 | 0.67444 | 6.708
2024-12-09 | 21:13 | Data | 0 | 31.339 | 28.72 | 220.101 | 7.62 | 206.422 | 2197.22 | 25.89 | 42.387 | 6.32 | 1.444 | 5.268 | 8947.23 | 2.707 | 98.1 | 78.5 | 1428 | 21.24 | 5815.7 | 3241.2 | 3226.1 | 4675.4 | 1206.9 | 0.67699 | 6.713
2024-12-09 | 21:14 | Data | 0 | 31.285 | 29.024 | 220.101 | 7.62 | 206.422 | 2191.79 | 25.89 | 42.387 | 6.33 | 1.436 | 5.273 | 8951.75 | 2.464 | 98.1 | 78.6 | 1425 | 21.19 | 5818.6 | 3246.3 | 3237 | 4685.8 | 1206.9 | 0.67638 | 6.71
2024-12-09 | 21:14 | Data | 0 | 31.346 | 28.848 | 220.011 | 7.62 | 206.422 | 2196.31 | 25.89 | 42.387 | 6.32 | 1.449 | 5.293 | 8956.27 | 2.491 | 98.1 | 78.5 | 1428 | 21.19 | 5821.6 | 3230.5 | 3220 | 4667.5 | 1206.9 | 0.67573 | 6.743
2024-12-09 | 21:14 | Data | 0 | 31.569 | 28.814 | 220.101 | 7.62 | 206.512 | 2197.22 | 25.88 | 42.387 | 6.32 | 1.451 | 5.276 | 8938.18 | 2.559 | 98.1 | 78.4 | 1428 | 21.19 | 5809.8 | 3227.6 | 3223 | 4665.1 | 1206.9 | 0.67542 | 6.727
2024-12-09 | 21:14 | Data | 0 | 31.353 | 28.646 | 220.192 | 7.62 | 206.512 | 2197.22 | 25.86 | 42.387 | 6.32 | 1.453 | 5.273 | 8906.53 | 2.484 | 98.1 | 78.4 | 1429 | 21.24 | 5789.2 | 3247.5 | 3195.3 | 4660.3 | 1206.9 | 0.68035 | 6.726
2024-12-09 | 21:14 | Data | 0 | 31.61 | 29.206 | 220.011 | 7.62 | 206.512 | 2196.31 | 25.89 | 42.477 | 6.32 | 1.464 | 5.288 | 8906.53 | 2.741 | 98.1 | 78.3 | 1428 | 21.19 | 5789.2 | 3255.2 | 3208.7 | 4672.2 | 1206.9 | 0.68081 | 6.75
2024-12-09 | 21:14 | Data | 0 | 31.339 | 28.814 | 220.101 | 7.62 | 206.467 | 2197.22 | 25.88 | 42.748 | 6.32 | 1.457 | 5.305 | 8902 | 2.525 | 98.1 | 78.5 | 1428 | 21.28 | 5786.3 | 3244.2 | 3194.5 | 4656.1 | 1206.9 | 0.68036 | 6.762
2024-12-09 | 21:14 | Data | 0 | 31.117 | 28.578 | 219.966 | 7.62 | 206.377 | 2196.31 | 25.89 | 42.387 | 6.32 | 1.448 | 5.316 | 8897.48 | 2.532 | 98.1 | 78.6 | 1428 | 21.19 | 5783.4 | 3259.2 | 3213.3 | 4680 | 1206.9 | 0.67986 | 6.764
2024-12-09 | 21:14 | Data | 0 | 31.225 | 28.808 | 220.056 | 7.62 | 206.332 | 2192.7 | 25.89 | 42.297 | 6.33 | 1.448 | 5.27 | 8947.23 | 2.532 | 98.1 | 78.5 | 1425 | 21.15 | 5815.7 | 3238.7 | 3199.8 | 4654.9 | 1206.9 | 0.67852 | 6.717
2024-12-09 | 21:14 | Data | 0 | 31.117 | 28.808 | 220.147 | 7.62 | 206.377 | 2196.31 | 25.88 | 42.387 | 6.32 | 1.446 | 5.289 | 8938.18 | 2.505 | 98.1 | 78.5 | 1428 | 21.24 | 5809.8 | 3244.2 | 3203.6 | 4661.7 | 1206.9 | 0.6791 | 6.736
2024-12-09 | 21:14 | Data | 0 | 31.164 | 28.794 | 220.056 | 7.62 | 206.377 | 2197.22 | 25.88 | 42.658 | 6.31 | 1.443 | 5.241 | 8951.75 | 2.16 | 98.1 | 78.4 | 1429 | 21.33 | 5818.6 | 3245.5 | 3227 | 4680.4 | 1206.9 | 0.67717 | 6.682
2024-12-09 | 21:14 | Data | 0 | 31.67 | 28.774 | 220.327 | 7.62 | 206.558 | 2197.22 | 25.88 | 42.477 | 6.32 | 1.445 | 5.265 | 8951.75 | 2.457 | 98.1 | 78.5 | 1428 | 21.24 | 5818.6 | 3247.5 | 3211 | 4668.9 | 1206.9 | 0.67879 | 6.71
2024-12-09 | 21:14 | Data | 0 | 31.231 | 28.578 | 220.282 | 7.62 | 206.648 | 2192.7 | 25.88 | 42.387 | 6.32 | 1.455 | 5.294 | 8924.61 | 2.545 | 98.1 | 78.4 | 1425 | 21.19 | 5801 | 3235.8 | 3245.2 | 4689.7 | 1206.9 | 0.67397 | 6.751
2024-12-09 | 21:14 | Data | 0 | 31.623 | 28.598 | 220.418 | 7.62 | 206.648 | 2195.41 | 25.89 | 42.206 | 6.32 | 1.443 | 5.319 | 8911.05 | 2.619 | 98.1 | 78.7 | 1427 | 21.19 | 5792.2 | 3243.8 | 3207.3 | 4672.3 | 1206.9 | 0.67916 | 6.762
2024-12-09 | 21:14 | Data | 0 | 31.285 | 29.118 | 220.373 | 7.62 | 206.558 | 2197.22 | 25.89 | 42.387 | 6.32 | 1.449 | 5.305 | 8924.61 | 2.647 | 98.1 | 78.5 | 1428 | 21.19 | 5801 | 3212.8 | 3204.8 | 4641.3 | 1206.9 | 0.67649 | 6.753
2024-12-09 | 21:14 | Data | 0 | 31.15 | 28.585 | 220.373 | 7.62 | 206.603 | 2197.22 | 25.89 | 42.477 | 6.33 | 1.459 | 5.252 | 8911.05 | 2.518 | 98.1 | 78.3 | 1428 | 21.19 | 5792.2 | 3248.8 | 3227.9 | 4677.6 | 1206.9 | 0.68043 | 6.711
2024-12-09 | 21:14 | Data | 0 | 31.339 | 29.024 | 220.327 | 7.62 | 206.603 | 2197.22 | 25.88 | 42.387 | 6.32 | 1.462 | 5.294 | 8906.53 | 2.356 | 98.1 | 78.4 | 1428 | 21.24 | 5789.2 | 3240.4 | 3203.2 | 4657.2 | 1207 | 0.6804 | 6.756
2024-12-09 | 21:14 | Data | 0 | 31.353 | 29.199 | 220.237 | 7.62 | 206.603 | 2195.41 | 25.89 | 42.387 | 6.32 | 1.458 | 5.282 | 8911.05 | 2.329 | 98.1 | 78.4 | 1426 | 21.19 | 5792.2 | 3252.6 | 3209.8 | 4668.9 | 1207 | 0.6825 | 6.739
2024-12-09 | 21:14 | Data | 0 | 31.144 | 28.868 | 220.373 | 7.62 | 206.512 | 2195.41 | 25.88 | 42.568 | 6.32 | 1.44 | 5.287 | 8915.57 | 2.538 | 98.1 | 78.6 | 1427 | 21.28 | 5795.1 | 3261.4 | 3215.5 | 4683.2 | 1207 | 0.68116 | 6.727
2024-12-09 | 21:15 | Data | 0 | 31.117 | 28.7 | 220.327 | 7.62 | 206.603 | 2189.99 | 25.89 | 42.387 | 6.32 | 1.453 | 5.285 | 8933.66 | 2.403 | 98.1 | 78.4 | 1425 | 21.19 | 5806.9 | 3245.1 | 3188.3 | 4653.2 | 1207 | 0.68129 | 6.741
2024-12-09 | 21:15 | Data | 0 | 31.299 | 28.598 | 220.373 | 7.62 | 206.603 | 2191.79 | 25.89 | 42.387 | 6.32 | 1.452 | 5.292 | 8947.23 | 2.701 | 98.1 | 78.5 | 1425 | 21.19 | 5815.7 | 3269.7 | 3213.1 | 4684.1 | 1207 | 0.68164 | 6.745
2024-12-09 | 21:15 | Data | 0 | 31.67 | 28.922 | 220.237 | 7.62 | 206.603 | 2195.41 | 25.88 | 42.477 | 6.32 | 1.446 | 5.273 | 8974.36 | 2.586 | 98.1 | 78.5 | 1427 | 21.19 | 5833.3 | 3258.5 | 3202.9 | 4669.9 | 1207 | 0.68199 | 6.719
2024-12-09 | 21:15 | Data | 0 | 31.225 | 28.794 | 220.282 | 7.62 | 206.558 | 2191.79 | 25.88 | 42.387 | 6.32 | 1.449 | 5.269 | 8956.27 | 2.545 | 98.1 | 78.4 | 1425 | 21.24 | 5821.6 | 3227.2 | 3198.4 | 4646.4 | 1207 | 0.6793 | 6.718
2024-12-09 | 21:15 | Data | 0 | 31.569 | 28.922 | 220.373 | 7.62 | 206.603 | 2191.79 | 25.88 | 42.477 | 6.32 | 1.46 | 5.287 | 8969.84 | 2.525 | 98.1 | 78.4 | 1425 | 21.19 | 5830.4 | 3244.2 | 3227.8 | 4680.3 | 1207 | 0.67747 | 6.746
2024-12-09 | 21:15 | Data | 0 | 31.117 | 28.686 | 220.327 | 7.62 | 206.558 | 2191.79 | 25.89 | 42.387 | 6.32 | 1.458 | 5.318 | 8960.79 | 2.599 | 98.1 | 78.5 | 1424 | 21.19 | 5824.5 | 3226.2 | 3225.1 | 4666.1 | 1207 | 0.67546 | 6.775
2024-12-09 | 21:15 | Data | 0 | 31.562 | 28.814 | 220.327 | 7.61 | 206.738 | 2207.16 | 25.89 | 42.387 | 6.33 | 1.443 | 5.293 | 8911.05 | 2.619 | 98.1 | 78.6 | 1435 | 21.15 | 5792.2 | 3239.2 | 3221.1 | 4673 | 1207 | 0.67673 | 6.736
2024-12-09 | 21:15 | Data | 0 | 31.117 | 28.794 | 220.282 | 7.62 | 206.558 | 2197.22 | 25.89 | 42.387 | 6.32 | 1.452 | 5.264 | 8911.05 | 2.444 | 98.1 | 78.4 | 1428 | 21.19 | 5792.2 | 3227.1 | 3207.9 | 4655.7 | 1207 | 0.67703 | 6.715
2024-12-09 | 21:15 | Data | 0 | 31.339 | 29.004 | 220.373 | 7.62 | 206.648 | 2197.22 | 25.89 | 42.387 | 6.32 | 1.452 | 5.28 | 8906.53 | 2.376 | 98.1 | 78.4 | 1428 | 21.24 | 5789.2 | 3237.1 | 3205.2 | 4657.6 | 1207 | 0.67882 | 6.732
2024-12-09 | 21:15 | Data | 0 | 31.346 | 28.808 | 220.463 | 7.62 | 206.648 | 2197.22 | 25.88 | 42.387 | 6.33 | 1.452 | 5.27 | 8902 | 2.532 | 98.1 | 78.4 | 1428 | 21.19 | 5786.3 | 3245 | 3215.7 | 4669.1 | 1207 | 0.67912 | 6.722
2024-12-09 | 21:15 | Data | 0 | 31.204 | 28.605 | 220.373 | 7.62 | 206.603 | 2195.41 | 25.86 | 42.387 | 6.32 | 1.458 | 5.276 | 8911.05 | 2.383 | 98.1 | 78.4 | 1426 | 21.19 | 5792.2 | 3241 | 3186 | 4655.2 | 1207 | 0.68297 | 6.735
2024-12-09 | 21:15 | Data | 0 | 31.339 | 28.571 | 220.282 | 7.62 | 206.558 | 2195.41 | 25.89 | 42.297 | 6.32 | 1.453 | 5.298 | 8911.05 | 2.647 | 98.1 | 78.5 | 1426 | 21.15 | 5792.2 | 3259.6 | 3204.5 | 4672.6 | 1207 | 0.68182 | 6.75
2024-12-09 | 21:15 | Data | 0 | 31.123 | 28.808 | 220.327 | 7.62 | 206.558 | 2193.6 | 25.88 | 42.387 | 6.33 | 1.451 | 5.288 | 8902 | 2.43 | 98.1 | 78.5 | 1428 | 21.19 | 5786.3 | 3249.5 | 3178.6 | 4646.3 | 1207 | 0.68322 | 6.739
2024-12-09 | 21:15 | Data | 0 | 31.333 | 29.064 | 220.735 | 7.62 | 207.1 | 2193.6 | 25.89 | 42.387 | 6.32 | 1.442 | 5.219 | 8906.53 | 2.478 | 98.1 | 78.4 | 1426 | 21.19 | 5789.2 | 3250.4 | 3192.1 | 4661.6 | 1207 | 0.68116 | 6.661
2024-12-09 | 21:15 | Data | 0 | 31.542 | 28.693 | 221.368 | 7.62 | 207.597 | 2192.7 | 25.86 | 42.387 | 6.32 | 1.443 | 5.279 | 8897.48 | 2.626 | 98.1 | 78.5 | 1425 | 21.19 | 5783.4 | 3269.1 | 3229.8 | 4697.6 | 1207 | 0.68046 | 6.723
2024-12-09 | 21:15 | Data | 0 | 31.11 | 28.571 | 221.368 | 7.62 | 207.642 | 2199.02 | 25.88 | 42.387 | 6.32 | 1.451 | 5.296 | 8883.91 | 2.714 | 98.1 | 78.5 | 1429 | 21.19 | 5774.5 | 3257 | 3238.3 | 4696 | 1207 | 0.67766 | 6.746
2024-12-09 | 21:15 | Data | 0 | 31.15 | 28.97 | 221.504 | 7.62 | 207.597 | 2199.02 | 25.86 | 42.387 | 6.32 | 1.45 | 5.316 | 8902 | 2.37 | 98.1 | 78.6 | 1430 | 21.19 | 5786.3 | 3234.2 | 3222.8 | 4677.4 | 1207 | 0.6767 | 6.765
2024-12-09 | 21:15 | Data | 0 | 31.616 | 29.085 | 221.549 | 7.62 | 207.687 | 2199.02 | 25.89 | 42.477 | 6.32 | 1.453 | 5.322 | 8902 | 2.701 | 98.1 | 78.5 | 1429 | 21.19 | 5786.3 | 3262.1 | 3245.5 | 4700.1 | 1207 | 0.67759 | 6.775
2024-12-09 | 21:16 | Data | 0 | 31.312 | 28.801 | 221.504 | 7.62 | 207.597 | 2199.93 | 25.89 | 42.297 | 6.32 | 1.452 | 5.329 | 8951.75 | 2.532 | 98.1 | 78.6 | 1430 | 21.1 | 5818.6 | 3242.4 | 3217.3 | 4670.2 | 1207 | 0.67701 | 6.781
2024-12-09 | 21:16 | Data | 0 | 31.562 | 28.808 | 221.549 | 7.62 | 207.597 | 2199.93 | 25.89 | 42.387 | 6.31 | 1.453 | 5.33 | 8947.23 | 2.559 | 98.1 | 78.6 | 1431 | 21.19 | 5815.7 | 3271.2 | 3235.1 | 4700.8 | 1207 | 0.67998 | 6.784
2024-12-09 | 21:16 | Data | 0 | 31.454 | 29.024 | 221.458 | 7.62 | 207.597 | 2199.93 | 25.89 | 42.206 | 6.31 | 1.447 | 5.328 | 8951.75 | 2.701 | 98.1 | 78.6 | 1430 | 21.01 | 5818.6 | 3244.8 | 3211.2 | 4671.2 | 1207 | 0.67856 | 6.776
2024-12-09 | 21:16 | Data | 0 | 31.285 | 28.578 | 221.277 | 7.62 | 207.552 | 2199.93 | 25.88 | 42.206 | 6.32 | 1.451 | 5.267 | 8951.75 | 2.734 | 98.1 | 78.4 | 1430 | 21.1 | 5818.6 | 3256.1 | 3222.8 | 4685.4 | 1207 | 0.67897 | 6.717
2024-12-09 | 21:16 | Data | 0 | 31.731 | 28.828 | 221.458 | 7.62 | 207.687 | 2199.02 | 25.88 | 42.116 | 6.31 | 1.457 | 5.285 | 8951.75 | 2.707 | 98.1 | 78.4 | 1429 | 21.06 | 5818.6 | 3257.6 | 3198.4 | 4666.4 | 1207 | 0.68268 | 6.744
2024-12-09 | 21:16 | Data | 0 | 31.576 | 29.179 | 221.549 | 7.62 | 207.733 | 2203.54 | 25.89 | 42.116 | 6.32 | 1.463 | 5.284 | 8956.27 | 2.667 | 98.1 | 78.3 | 1432 | 21.06 | 5821.6 | 3255.9 | 3217.6 | 4681.4 | 1207 | 0.68065 | 6.746
2024-12-09 | 21:16 | Data | 0 | 31.339 | 28.578 | 221.504 | 7.62 | 207.733 | 2201.74 | 25.89 | 42.116 | 6.32 | 1.459 | 5.286 | 8960.79 | 2.701 | 98.1 | 78.4 | 1431 | 21.06 | 5824.5 | 3265.4 | 3192.8 | 4657.8 | 1207 | 0.6819 | 6.745
2024-12-09 | 21:16 | Data | 0 | 31.393 | 28.679 | 221.504 | 7.62 | 207.733 | 2201.74 | 25.88 | 42.206 | 6.32 | 1.446 | 5.311 | 8978.88 | 2.437 | 98.1 | 78.6 | 1432 | 21.06 | 5836.3 | 3263.5 | 3199.2 | 4672.6 | 1207 | 0.68318 | 6.755
2024-12-09 | 21:16 | Data | 0 | 31.339 | 28.794 | 221.639 | 7.62 | 207.733 | 2203.54 | 25.86 | 42.116 | 6.32 | 1.449 | 5.319 | 8978.88 | 2.667 | 98.1 | 78.6 | 1432 | 21.06 | 5836.3 | 3257.1 | 3181.6 | 4655.9 | 1207 | 0.68214 | 6.768
2024-12-09 | 21:16 | Data | 0 | 31.778 | 28.72 | 221.775 | 7.62 | 207.778 | 2199.93 | 25.88 | 42.387 | 6.32 | 1.451 | 5.325 | 8974.36 | 2.586 | 98.1 | 78.6 | 1431 | 21.19 | 5833.3 | 3241.6 | 3230.6 | 4696.4 | 1207 | 0.67719 | 6.776
2024-12-09 | 21:16 | Data | 0 | 31.569 | 28.814 | 221.684 | 7.62 | 207.778 | 2199.93 | 25.89 | 42.297 | 6.32 | 1.462 | 5.298 | 8996.97 | 2.552 | 98.1 | 78.4 | 1430 | 21.15 | 5848 | 3250 | 3235 | 4690.6 | 1207 | 0.67638 | 6.76
2024-12-09 | 21:16 | Data | 0 | 31.231 | 28.909 | 221.639 | 7.62 | 207.733 | 2199.02 | 25.89 | 42.387 | 6.32 | 1.459 | 5.326 | 9006.01 | 2.626 | 98.1 | 78.5 | 1429 | 21.19 | 5853.9 | 3254.7 | 3246.7 | 4704 | 1207 | 0.67758 | 6.784
2024-12-09 | 21:16 | Data | 0 | 30.961 | 28.781 | 221.594 | 7.62 | 207.687 | 2199.93 | 25.89 | 42.477 | 6.32 | 1.462 | 5.308 | 8996.97 | 2.329 | 98.1 | 78.4 | 1430 | 21.15 | 5848 | 3252.6 | 3216.5 | 4675.1 | 1207.1 | 0.67874 | 6.773
2024-12-09 | 21:16 | Data | 0 | 31.569 | 28.646 | 221.594 | 7.62 | 207.823 | 2201.74 | 25.86 | 42.387 | 6.31 | 1.458 | 5.287 | 9001.49 | 2.674 | 98.1 | 78.4 | 1432 | 21.24 | 5851 | 3245.1 | 3222.2 | 4676.2 | 1207.1 | 0.67842 | 6.746
2024-12-09 | 21:16 | Data | 0 | 31.657 | 28.835 | 221.323 | 7.62 | 207.687 | 2199.02 | 25.89 | 42.387 | 6.32 | 1.451 | 5.297 | 9019.58 | 2.613 | 98.1 | 78.5 | 1430 | 21.19 | 5862.7 | 3237.4 | 3207.6 | 4656.4 | 1207.1 | 0.68007 | 6.748
2024-12-09 | 21:16 | Data | 0 | 31.245 | 28.578 | 221.458 | 7.62 | 207.733 | 2199.93 | 25.89 | 42.297 | 6.32 | 1.457 | 5.304 | 9024.1 | 2.545 | 98.1 | 78.4 | 1430 | 21.1 | 5865.7 | 3259.9 | 3201 | 4670.5 | 1207.1 | 0.68153 | 6.76
2024-12-09 | 21:16 | Data | 0 | 31.454 | 28.916 | 221.504 | 7.62 | 207.733 | 2199.02 | 25.86 | 42.387 | 6.32 | 1.453 | 5.311 | 8996.97 | 2.525 | 98.1 | 78.5 | 1429 | 21.19 | 5848 | 3256.3 | 3205.5 | 4673.8 | 1207.1 | 0.68186 | 6.764
2024-12-09 | 21:16 | Data | 0 | 31.569 | 28.862 | 221.73 | 7.62 | 207.733 | 2201.74 | 25.89 | 42.297 | 6.32 | 1.451 | 5.333 | 8983.4 | 2.532 | 98.1 | 78.6 | 1431 | 21.19 | 5839.2 | 3242.1 | 3203.7 | 4662.5 | 1207.1 | 0.67983 | 6.783
2024-12-09 | 21:17 | Data | 0 | 31.535 | 28.808 | 221.458 | 7.62 | 207.733 | 2201.74 | 25.88 | 42.297 | 6.32 | 1.462 | 5.332 | 8987.93 | 2.64 | 98.1 | 78.5 | 1431 | 21.19 | 5842.2 | 3266.6 | 3217.4 | 4685.2 | 1207.1 | 0.6823 | 6.793
2024-12-09 | 21:17 | Data | 0 | 31.596 | 28.605 | 221.504 | 7.62 | 207.733 | 2204.45 | 25.88 | 42.387 | 6.31 | 1.457 | 5.32 | 8983.4 | 2.619 | 98.1 | 78.5 | 1432 | 21.24 | 5839.2 | 3253.8 | 3210.8 | 4671.4 | 1207.1 | 0.68099 | 6.778
2024-12-09 | 21:17 | Data | 0 | 31.366 | 28.693 | 221.594 | 7.62 | 207.733 | 2203.54 | 25.86 | 42.387 | 6.31 | 1.457 | 5.3 | 8974.36 | 2.525 | 98.1 | 78.4 | 1433 | 21.19 | 5833.3 | 3253.8 | 3176.5 | 4652.2 | 1207.1 | 0.68345 | 6.757
2024-12-09 | 21:17 | Data | 0 | 31.555 | 29.037 | 221.549 | 7.62 | 207.733 | 2203.54 | 25.88 | 41.936 | 6.32 | 1.451 | 5.299 | 8987.93 | 2.532 | 98.1 | 78.5 | 1431 | 20.97 | 5842.2 | 3259.5 | 3212.3 | 4687.7 | 1207.1 | 0.6804 | 6.75
2024-12-09 | 21:17 | Data | 0 | 31.339 | 28.686 | 221.594 | 7.62 | 207.733 | 2199.93 | 25.89 | 42.297 | 6.32 | 1.447 | 5.296 | 8992.45 | 2.647 | 98.1 | 78.5 | 1431 | 21.15 | 5845.1 | 3271.3 | 3214.2 | 4686 | 1207.1 | 0.68282 | 6.742
2024-12-09 | 21:17 | Data | 0 | 31.616 | 28.983 | 221.549 | 7.62 | 207.687 | 2199.93 | 25.88 | 42.387 | 6.32 | 1.452 | 5.307 | 8978.88 | 2.626 | 98.1 | 78.5 | 1429 | 21.19 | 5836.3 | 3249 | 3192.1 | 4659 | 1207.1 | 0.68133 | 6.761
2024-12-09 | 21:17 | Data | 0 | 31.555 | 28.835 | 221.639 | 7.62 | 207.733 | 2197.22 | 25.88 | 42.387 | 6.31 | 1.449 | 5.297 | 8974.36 | 2.707 | 98.1 | 78.5 | 1428 | 21.15 | 5833.3 | 3267.6 | 3201.1 | 4674.5 | 1207.1 | 0.68278 | 6.746
2024-12-09 | 21:17 | Data | 0 | 31.353 | 28.598 | 221.549 | 7.62 | 207.687 | 2199.93 | 25.88 | 42.206 | 6.33 | 1.449 | 5.313 | 8978.88 | 2.322 | 98.1 | 78.6 | 1430 | 21.1 | 5836.3 | 3261.7 | 3198 | 4670.2 | 1207.1 | 0.68237 | 6.761
2024-12-09 | 21:17 | Data | 0 | 31.393 | 28.801 | 221.458 | 7.62 | 207.687 | 2199.02 | 25.88 | 42.116 | 6.32 | 1.453 | 5.287 | 8978.88 | 2.559 | 98.1 | 78.4 | 1429 | 21.06 | 5836.3 | 3250.9 | 3203.5 | 4662.8 | 1207.1 | 0.68163 | 6.739
2024-12-09 | 21:17 | Data | 0 | 31.569 | 29.139 | 221.549 | 7.62 | 207.778 | 2199.93 | 25.86 | 42.297 | 6.32 | 1.453 | 5.312 | 8974.36 | 2.437 | 98.1 | 78.5 | 1430 | 21.15 | 5833.3 | 3254 | 3201.6 | 4664.7 | 1207.1 | 0.68153 | 6.765
2024-12-09 | 21:17 | Data | 0 | 31.684 | 29.044 | 221.639 | 7.62 | 207.778 | 2199.02 | 25.89 | 42.387 | 6.32 | 1.452 | 5.314 | 8978.88 | 2.538 | 98.1 | 78.5 | 1431 | 21.19 | 5836.3 | 3242.8 | 3201.5 | 4661.9 | 1207.1 | 0.6799 | 6.766
2024-12-09 | 21:17 | Data | 0 | 31.569 | 29.078 | 221.684 | 7.62 | 207.823 | 2197.22 | 25.88 | 42.297 | 6.32 | 1.449 | 5.298 | 8951.75 | 2.491 | 98.1 | 78.5 | 1428 | 21.15 | 5818.6 | 3247.2 | 3222.2 | 4675.5 | 1207.1 | 0.67813 | 6.747
2024-12-09 | 21:17 | Data | 0 | 31.366 | 28.578 | 221.458 | 7.62 | 207.733 | 2196.31 | 25.88 | 42.387 | 6.32 | 1.458 | 5.297 | 8951.75 | 2.552 | 98.1 | 78.4 | 1427 | 21.19 | 5818.6 | 3255.3 | 3209.4 | 4676.5 | 1207.1 | 0.67784 | 6.756
2024-12-09 | 21:17 | Data | 0 | 31.171 | 28.781 | 221.368 | 7.62 | 207.597 | 2191.79 | 25.88 | 42.387 | 6.31 | 1.466 | 5.305 | 8951.75 | 2.538 | 98.1 | 78.3 | 1425 | 21.19 | 5818.6 | 3244.5 | 3195.1 | 4659.2 | 1207.1 | 0.68133 | 6.77
2024-12-09 | 21:17 | Data | 0 | 31.508 | 28.808 | 221.368 | 7.62 | 207.778 | 2197.22 | 25.88 | 42.387 | 6.31 | 1.449 | 5.301 | 8933.66 | 2.734 | 98.1 | 78.5 | 1428 | 21.19 | 5806.9 | 3254.5 | 3198.5 | 4666.4 | 1207.1 | 0.68143 | 6.751
2024-12-09 | 21:17 | Data | 0 | 31.117 | 28.571 | 221.504 | 7.62 | 207.687 | 2196.31 | 25.88 | 42.387 | 6.31 | 1.441 | 5.285 | 8983.4 | 2.538 | 98.1 | 78.6 | 1428 | 21.24 | 5839.2 | 3255.7 | 3205.7 | 4670.2 | 1207.1 | 0.68108 | 6.725
2024-12-09 | 21:17 | Data | 0 | 31.15 | 28.666 | 221.504 | 7.62 | 207.687 | 2197.22 | 25.88 | 42.297 | 6.32 | 1.447 | 5.3 | 8974.36 | 2.363 | 98.1 | 78.6 | 1429 | 21.19 | 5833.3 | 3251.6 | 3178.1 | 4651.1 | 1207.1 | 0.68348 | 6.746
2024-12-09 | 21:18 | Data | 0 | 31.225 | 28.693 | 221.323 | 7.62 | 207.597 | 2197.22 | 25.88 | 42.387 | 6.32 | 1.449 | 5.297 | 8956.27 | 2.755 | 98.1 | 78.5 | 1428 | 21.19 | 5821.6 | 3256.6 | 3187.5 | 4656.2 | 1207.1 | 0.68282 | 6.746
2024-12-09 | 21:18 | Data | 0 | 31.225 | 28.922 | 221.684 | 7.62 | 207.642 | 2197.22 | 25.89 | 42.387 | 6.32 | 1.45 | 5.303 | 8947.23 | 2.322 | 98.1 | 78.5 | 1428 | 21.15 | 5815.7 | 3264 | 3210.1 | 4682.4 | 1207.1 | 0.68172 | 6.753
2024-12-09 | 21:18 | Data | 0 | 31.285 | 29.078 | 221.504 | 7.62 | 207.597 | 2197.22 | 25.89 | 42.387 | 6.32 | 1.443 | 5.289 | 8960.79 | 2.68 | 98.1 | 78.6 | 1428 | 21.19 | 5824.5 | 3275 | 3267.1 | 4729.3 | 1207.1 | 0.6767 | 6.732
2024-12-09 | 21:18 | Data | 0 | 31.13 | 28.895 | 221.639 | 7.62 | 207.642 | 2197.22 | 25.89 | 42.477 | 6.32 | 1.449 | 5.286 | 8951.75 | 2.221 | 98.1 | 78.5 | 1428 | 21.24 | 5818.6 | 3279.5 | 3226.2 | 4699.9 | 1207.1 | 0.68111 | 6.735
2024-12-09 | 21:18 | Data | 0 | 31.393 | 28.821 | 221.504 | 7.62 | 207.687 | 2194.5 | 25.88 | 42.297 | 6.31 | 1.45 | 5.317 | 8965.31 | 2.505 | 98.1 | 78.6 | 1427 | 21.19 | 5827.5 | 3264.3 | 3228.5 | 4695.8 | 1207.1 | 0.67873 | 6.767
2024-12-09 | 21:18 | Data | 0 | 31.285 | 28.808 | 221.549 | 7.62 | 207.687 | 2193.6 | 25.88 | 42.477 | 6.32 | 1.457 | 5.303 | 8969.84 | 2.505 | 98.1 | 78.4 | 1426 | 21.24 | 5830.4 | 3289.7 | 3239.9 | 4721.5 | 1207.1 | 0.67835 | 6.759
2024-12-09 | 21:18 | Data | 0 | 31.339 | 28.801 | 221.594 | 7.62 | 207.687 | 2191.79 | 25.89 | 42.387 | 6.32 | 1.458 | 5.284 | 8933.66 | 2.538 | 98.1 | 78.4 | 1425 | 21.24 | 5806.9 | 3280.5 | 3202.4 | 4686 | 1207.1 | 0.68361 | 6.742
2024-12-09 | 21:18 | Data | 0 | 31.339 | 28.706 | 221.594 | 7.62 | 207.733 | 2190.89 | 25.89 | 42.387 | 6.32 | 1.449 | 5.285 | 8924.61 | 2.842 | 98.1 | 78.5 | 1424 | 21.19 | 5801 | 3261.5 | 3219.2 | 4687.2 | 1207.1 | 0.67896 | 6.736
2024-12-09 | 21:18 | Data | 0 | 31.414 | 28.808 | 221.73 | 7.62 | 207.687 | 2190.89 | 25.89 | 42.387 | 6.32 | 1.46 | 5.307 | 8938.18 | 2.741 | 98.1 | 78.4 | 1424 | 21.19 | 5809.8 | 3282.5 | 3232.7 | 4708.3 | 1207.1 | 0.68097 | 6.766
2024-12-09 | 21:18 | Data | 0 | 31.117 | 28.801 | 221.504 | 7.62 | 207.733 | 2191.79 | 25.89 | 42.387 | 6.31 | 1.458 | 5.323 | 8956.27 | 2.518 | 98.1 | 78.5 | 1425 | 21.19 | 5821.6 | 3265.7 | 3223.2 | 4693.4 | 1207.2 | 0.68012 | 6.781
2024-12-09 | 21:18 | Data | 0 | 31.373 | 28.814 | 221.594 | 7.62 | 207.778 | 2191.79 | 25.89 | 42.387 | 6.32 | 1.453 | 5.302 | 8969.84 | 2.545 | 98.1 | 78.5 | 1425 | 21.19 | 5830.4 | 3271.4 | 3242.5 | 4712.2 | 1207.2 | 0.67763 | 6.755
2024-12-09 | 21:18 | Data | 0 | 31.285 | 28.72 | 221.368 | 7.62 | 207.597 | 2186.37 | 25.89 | 42.387 | 6.32 | 1.46 | 5.305 | 8965.31 | 2.903 | 98.1 | 78.4 | 1422 | 21.19 | 5827.5 | 3280.1 | 3257.7 | 4728.8 | 1207.2 | 0.67708 | 6.764
2024-12-09 | 21:18 | Data | 0 | 31.42 | 28.578 | 221.323 | 7.62 | 207.687 | 2184.56 | 25.88 | 42.387 | 6.31 | 1.457 | 5.311 | 8965.31 | 2.653 | 98.1 | 78.5 | 1421 | 21.15 | 5827.5 | 3278.2 | 3226.1 | 4699.6 | 1207.2 | 0.68112 | 6.769
2024-12-09 | 21:18 | Data | 0 | 31.657 | 29.206 | 221.684 | 7.62 | 207.868 | 2186.37 | 25.89 | 42.387 | 6.32 | 1.448 | 5.293 | 8960.79 | 2.687 | 98.1 | 78.5 | 1421 | 21.19 | 5824.5 | 3283.7 | 3241.6 | 4719.3 | 1207.2 | 0.67951 | 6.741
2024-12-09 | 21:18 | Data | 0 | 31.11 | 28.747 | 221.639 | 7.62 | 207.597 | 2184.56 | 25.88 | 42.387 | 6.32 | 1.449 | 5.297 | 8951.75 | 2.647 | 98.1 | 78.5 | 1419 | 21.15 | 5818.6 | 3284.4 | 3236 | 4713.1 | 1207.2 | 0.68116 | 6.745
2024-12-09 | 21:18 | Data | 0 | 31.339 | 28.598 | 221.504 | 7.62 | 207.733 | 2193.6 | 25.89 | 42.387 | 6.32 | 1.453 | 5.296 | 8951.75 | 2.707 | 98.1 | 78.5 | 1426 | 21.19 | 5818.6 | 3269.9 | 3226.3 | 4698.6 | 1207.2 | 0.67949 | 6.749
2024-12-09 | 21:18 | Data | 0 | 31.515 | 28.7 | 221.458 | 7.62 | 207.642 | 2195.41 | 25.88 | 42.387 | 6.31 | 1.462 | 5.296 | 8938.18 | 2.748 | 98.1 | 78.4 | 1426 | 21.19 | 5809.8 | 3277.3 | 3231.3 | 4707.2 | 1207.2 | 0.67935 | 6.758
2024-12-09 | 21:19 | Data | 0 | 31.326 | 28.747 | 221.458 | 7.62 | 207.687 | 2199.93 | 25.88 | 42.297 | 6.32 | 1.464 | 5.282 | 8992.45 | 2.64 | 98.1 | 78.3 | 1430 | 21.15 | 5845.1 | 3275.4 | 3239.4 | 4711.3 | 1207.2 | 0.68032 | 6.747
2024-12-09 | 21:19 | Data | 0 | 31.13 | 28.808 | 221.504 | 7.62 | 207.733 | 2198.12 | 25.89 | 42.297 | 6.32 | 1.462 | 5.303 | 8983.4 | 2.417 | 98.1 | 78.4 | 1429 | 21.19 | 5839.2 | 3284.8 | 3227.6 | 4707.5 | 1207.2 | 0.68126 | 6.764
2024-12-09 | 21:19 | Data | 0 | 31.832 | 28.936 | 221.684 | 7.62 | 207.778 | 2199.93 | 25.88 | 42.297 | 6.32 | 1.451 | 5.308 | 9019.58 | 2.491 | 98.1 | 78.5 | 1430 | 21.19 | 5862.7 | 3274.3 | 3223.6 | 4698.6 | 1207.2 | 0.67983 | 6.758
2024-12-09 | 21:19 | Data | 0 | 31.481 | 28.592 | 221.639 | 7.62 | 207.823 | 2199.93 | 25.89 | 42.387 | 6.32 | 1.451 | 5.328 | 9033.15 | 2.66 | 98.1 | 78.6 | 1430 | 21.15 | 5871.5 | 3289.4 | 3245.4 | 4729 | 1207.2 | 0.68135 | 6.779
2024-12-09 | 21:19 | Data | 0 | 31.123 | 28.625 | 221.504 | 7.62 | 207.687 | 2198.12 | 25.86 | 42.387 | 6.32 | 1.444 | 5.311 | 8965.31 | 2.336 | 98.1 | 78.6 | 1428 | 21.19 | 5827.5 | 3276.5 | 3229.7 | 4706.7 | 1207.2 | 0.67931 | 6.756
2024-12-09 | 21:19 | Data | 0 | 31.339 | 28.639 | 221.594 | 7.62 | 207.733 | 2197.22 | 25.88 | 42.387 | 6.31 | 1.452 | 5.316 | 8956.27 | 2.505 | 98.1 | 78.5 | 1428 | 21.15 | 5821.6 | 3290.2 | 3260.2 | 4735.8 | 1207.2 | 0.67845 | 6.768
2024-12-09 | 21:19 | Data | 0 | 31.319 | 29.004 | 221.549 | 7.62 | 207.687 | 2199.93 | 25.88 | 42.477 | 6.32 | 1.442 | 5.312 | 8951.75 | 2.538 | 98.1 | 78.7 | 1429 | 21.24 | 5818.6 | 3275.5 | 3228.8 | 4705.7 | 1207.2 | 0.68032 | 6.753
2024-12-09 | 21:19 | Data | 0 | 31.123 | 28.686 | 221.684 | 7.62 | 207.687 | 2199.93 | 25.86 | 42.116 | 6.31 | 1.453 | 5.296 | 8983.4 | 2.451 | 98.1 | 78.5 | 1430 | 21.24 | 5839.2 | 3278.2 | 3248.7 | 4720.8 | 1207.2 | 0.67864 | 6.747
2024-12-09 | 21:19 | Data | 0 | 31.495 | 28.808 | 221.504 | 7.62 | 207.687 | 2203.54 | 25.88 | 42.297 | 6.32 | 1.452 | 5.289 | 9019.58 | 2.579 | 98.1 | 78.5 | 1431 | 21.15 | 5862.7 | 3282.9 | 3212.5 | 4697.5 | 1207.2 | 0.6819 | 6.741
2024-12-09 | 21:19 | Data | 0 | 31.339 | 28.922 | 221.549 | 7.62 | 207.733 | 2201.74 | 25.88 | 42.387 | 6.32 | 1.451 | 5.28 | 9024.1 | 2.653 | 98.1 | 78.4 | 1432 | 21.19 | 5865.7 | 3222.7 | 3219.4 | 4651 | 1207.2 | 0.67745 | 6.73
2024-12-09 | 21:19 | Data | 0 | 31.474 | 28.592 | 221.504 | 7.62 | 207.733 | 2203.54 | 25.86 | 42.387 | 6.32 | 1.446 | 5.321 | 9019.58 | 2.552 | 98.1 | 78.6 | 1432 | 21.19 | 5862.7 | 3200.1 | 3220.7 | 4640.7 | 1207.2 | 0.6732 | 6.765
2024-12-09 | 21:19 | Data | 0 | 31.339 | 28.808 | 221.639 | 7.62 | 207.733 | 2201.74 | 25.88 | 42.477 | 6.31 | 1.451 | 5.31 | 9015.06 | 2.532 | 98.1 | 78.5 | 1431 | 21.28 | 5859.8 | 3208.6 | 3199 | 4630.9 | 1207.2 | 0.67496 | 6.761
2024-12-09 | 21:19 | Data | 0 | 31.204 | 28.578 | 221.549 | 7.63 | 207.733 | 2203.54 | 25.88 | 42.297 | 6.32 | 1.455 | 5.295 | 8793.47 | 2.552 | 98.1 | 78.4 | 1432 | 21.19 | 5715.8 | 3215.7 | 3223.5 | 4652.3 | 1207.2 | 0.67581 | 6.75
2024-12-09 | 21:19 | Data | 0 | 31.366 | 28.747 | 221.639 | 7.62 | 207.597 | 2201.74 | 25.86 | 42.387 | 6.31 | 1.451 | 5.307 | 8779.9 | 2.478 | 98.1 | 78.5 | 1432 | 21.19 | 5706.9 | 3203.1 | 3208.6 | 4631.4 | 1207.2 | 0.67837 | 6.757
2024-12-09 | 21:19 | Data | 0 | 31.366 | 28.571 | 221.458 | 7.62 | 207.642 | 2199.93 | 25.89 | 42.387 | 6.31 | 1.453 | 5.292 | 8775.38 | 2.545 | 98.1 | 78.5 | 1430 | 21.19 | 5704 | 3193.2 | 3184 | 4612.9 | 1207.2 | 0.67627 | 6.745
2024-12-09 | 21:19 | Data | 0 | 31.468 | 28.578 | 221.594 | 7.62 | 207.733 | 2199.93 | 25.88 | 42.387 | 6.31 | 1.444 | 5.3 | 8770.86 | 2.579 | 98.1 | 78.6 | 1430 | 21.24 | 5701.1 | 3198.6 | 3170.2 | 4601 | 1207.2 | 0.68004 | 6.746
2024-12-09 | 21:19 | Data | 0 | 31.137 | 28.578 | 221.504 | 7.62 | 207.687 | 2196.31 | 25.89 | 42.387 | 6.31 | 1.453 | 5.314 | 8951.75 | 2.532 | 98.1 | 78.5 | 1428 | 21.19 | 5818.6 | 3201.2 | 3182.9 | 4612.4 | 1207.2 | 0.6802 | 6.768
2024-12-09 | 21:20 | Data | 0 | 31.724 | 28.916 | 221.684 | 7.62 | 207.733 | 2198.12 | 25.86 | 42.387 | 6.31 | 1.446 | 5.33 | 8987.93 | 2.559 | 98.1 | 78.7 | 1428 | 21.15 | 5842.2 | 3186.6 | 3190.8 | 4613.2 | 1207.2 | 0.67632 | 6.775
2024-12-09 | 21:20 | Data | 0 | 31.137 | 28.571 | 221.504 | 7.62 | 207.687 | 2199.02 | 25.88 | 42.568 | 6.32 | 1.453 | 5.311 | 8987.93 | 2.538 | 98.1 | 78.5 | 1429 | 21.33 | 5842.2 | 3256.7 | 3183.9 | 4660.1 | 1207.2 | 0.68281 | 6.763
2024-12-09 | 21:20 | Data | 0 | 30.955 | 28.524 | 221.684 | 7.62 | 207.733 | 2196.31 | 25.85 | 42.297 | 6.32 | 1.458 | 5.317 | 8969.84 | 2.545 | 98.1 | 78.5 | 1428 | 21.15 | 5830.4 | 3257.2 | 3201.8 | 4673.7 | 1207.2 | 0.68064 | 6.776
2024-12-09 | 21:20 | Data | 0 | 31.508 | 29.024 | 221.549 | 7.62 | 207.687 | 2195.41 | 25.88 | 42.297 | 6.32 | 1.462 | 5.279 | 8969.84 | 2.714 | 98.1 | 78.3 | 1427 | 21.15 | 5830.4 | 3266.9 | 3223.8 | 4692.7 | 1207.2 | 0.68025 | 6.742
2024-12-09 | 21:20 | Data | 0 | 31.4 | 28.808 | 221.458 | 7.62 | 207.733 | 2193.6 | 25.88 | 42.387 | 6.32 | 1.458 | 5.289 | 8992.45 | 2.552 | 98.1 | 78.4 | 1426 | 21.19 | 5845.1 | 3250.8 | 3227.8 | 4681.8 | 1207.2 | 0.67793 | 6.747
2024-12-09 | 21:20 | Data | 0 | 31.555 | 29.024 | 221.323 | 7.63 | 207.687 | 2191.79 | 25.85 | 42.387 | 6.32 | 1.458 | 5.298 | 8974.36 | 2.552 | 98.1 | 78.4 | 1425 | 21.19 | 5833.3 | 3264.5 | 3235.2 | 4702.6 | 1207.2 | 0.67906 | 6.757
2024-12-09 | 21:20 | Data | 0 | 31.326 | 28.578 | 221.277 | 7.62 | 207.642 | 2191.79 | 25.86 | 42.477 | 6.31 | 1.44 | 5.317 | 8965.31 | 2.586 | 98.1 | 78.7 | 1425 | 21.24 | 5827.5 | 3261.6 | 3229.7 | 4692.7 | 1207.3 | 0.67857 | 6.756
2024-12-09 | 21:20 | Data | 0 | 31.123 | 28.477 | 221.368 | 7.62 | 207.597 | 2194.5 | 25.85 | 42.387 | 6.31 | 1.441 | 5.309 | 8974.36 | 2.64 | 98.1 | 78.6 | 1426 | 21.19 | 5833.3 | 3247.8 | 3222.8 | 4681 | 1207.3 | 0.67737 | 6.751
2024-12-09 | 21:20 | Data | 0 | 31.569 | 28.747 | 221.368 | 7.62 | 207.642 | 2196.31 | 25.86 | 42.297 | 6.32 | 1.457 | 5.303 | 8969.84 | 2.505 | 98.1 | 78.4 | 1428 | 21.19 | 5830.4 | 3279.1 | 3215.3 | 4695.4 | 1207.3 | 0.68213 | 6.76
2024-12-09 | 21:20 | Data | 0 | 30.887 | 28.571 | 221.458 | 7.62 | 207.507 | 2196.31 | 25.86 | 42.206 | 6.32 | 1.455 | 5.305 | 8996.97 | 2.626 | 98.1 | 78.5 | 1428 | 21.06 | 5848 | 3268.5 | 3208 | 4685.5 | 1207.3 | 0.68223 | 6.762
2024-12-09 | 21:20 | Data | 0 | 31.441 | 29.004 | 221.684 | 7.62 | 207.778 | 2197.22 | 25.86 | 42.116 | 6.31 | 1.461 | 5.304 | 8978.88 | 2.586 | 98.1 | 78.4 | 1428 | 21.06 | 5836.3 | 3261.8 | 3207.6 | 4676 | 1207.3 | 0.67951 | 6.765
2024-12-09 | 21:20 | Data | 0 | 31.164 | 28.578 | 221.368 | 7.62 | 207.733 | 2196.31 | 25.86 | 42.116 | 6.31 | 1.463 | 5.317 | 8992.45 | 2.532 | 98.1 | 78.4 | 1428 | 21.06 | 5845.1 | 3266.3 | 3227.5 | 4694.2 | 1207.3 | 0.68008 | 6.783
2024-12-09 | 21:20 | Data | 0 | 31.319 | 28.977 | 221.504 | 7.62 | 207.687 | 2198.12 | 25.86 | 42.387 | 6.32 | 1.461 | 5.33 | 8951.75 | 2.532 | 98.1 | 78.5 | 1428 | 21.15 | 5818.6 | 3260.2 | 3189.8 | 4662.6 | 1207.3 | 0.68268 | 6.791
2024-12-09 | 21:20 | Data | 0 | 31.164 | 28.693 | 221.458 | 7.62 | 207.552 | 2195.41 | 25.85 | 42.387 | 6.32 | 1.448 | 5.296 | 8951.75 | 2.538 | 98.1 | 78.5 | 1426 | 21.19 | 5818.6 | 3263.8 | 3230.6 | 4695.6 | 1207.3 | 0.67921 | 6.743
2024-12-09 | 21:20 | Data | 0 | 31.272 | 28.889 | 221.594 | 7.62 | 207.642 | 2194.5 | 25.86 | 42.116 | 6.31 | 1.439 | 5.303 | 8965.31 | 2.565 | 98.1 | 78.7 | 1426 | 21.01 | 5827.5 | 3268.9 | 3216.1 | 4689.4 | 1207.3 | 0.68129 | 6.743
2024-12-09 | 21:20 | Data | 0 | 31.11 | 28.544 | 221.323 | 7.62 | 207.597 | 2194.5 | 25.83 | 42.206 | 6.32 | 1.441 | 5.326 | 8951.75 | 2.565 | 98.1 | 78.7 | 1427 | 21.15 | 5818.6 | 3265.6 | 3224.9 | 4691.5 | 1207.3 | 0.67964 | 6.767
2024-12-09 | 21:20 | Data | 0 | 31.285 | 28.571 | 221.504 | 7.62 | 207.642 | 2192.7 | 25.85 | 42.568 | 6.32 | 1.447 | 5.279 | 8992.45 | 2.647 | 98.1 | 78.5 | 1425 | 21.28 | 5845.1 | 3264 | 3245.5 | 4705.8 | 1207.3 | 0.67779 | 6.726
2024-12-09 | 21:20 | Data | 0 | 31.4 | 28.598 | 221.549 | 7.62 | 207.733 | 2192.7 | 25.85 | 42.387 | 6.31 | 1.437 | 5.28 | 8992.45 | 2.336 | 98.1 | 78.6 | 1425 | 21.24 | 5845.1 | 3265.6 | 3223.9 | 4691.7 | 1207.3 | 0.67971 | 6.718
2024-12-09 | 21:21 | Data | 0 | 31.225 | 28.781 | 221.458 | 7.62 | 207.552 | 2194.5 | 25.85 | 42.387 | 6.31 | 1.443 | 5.3 | 8983.4 | 2.633 | 98.1 | 78.6 | 1426 | 21.19 | 5839.2 | 3270.9 | 3229.4 | 4695.9 | 1207.3 | 0.68008 | 6.742
2024-12-09 | 21:21 | Data | 0 | 31.177 | 28.693 | 221.549 | 7.62 | 207.778 | 2195.41 | 25.84 | 42.477 | 6.32 | 1.442 | 5.313 | 8969.84 | 2.538 | 98.1 | 78.7 | 1426 | 21.19 | 5830.4 | 3245.6 | 3211.9 | 4668.1 | 1207.3 | 0.67923 | 6.755
2024-12-09 | 21:21 | Data | 0 | 31.15 | 28.963 | 221.594 | 7.62 | 207.642 | 2192.7 | 25.83 | 42.387 | 6.32 | 1.449 | 5.301 | 8992.45 | 2.478 | 98.1 | 78.5 | 1425 | 21.15 | 5845.1 | 3263.1 | 3219.4 | 4674.2 | 1207.3 | 0.67863 | 6.749
2024-12-09 | 21:21 | Data | 0 | 31.11 | 28.571 | 221.458 | 7.62 | 207.597 | 2189.08 | 25.84 | 42.477 | 6.32 | 1.453 | 5.294 | 8992.45 | 2.538 | 98.1 | 78.5 | 1422 | 21.19 | 5845.1 | 3261.8 | 3215 | 4679.4 | 1207.3 | 0.68141 | 6.747
2024-12-09 | 21:21 | Data | 0 | 31.589 | 28.639 | 221.504 | 7.62 | 207.642 | 2189.08 | 25.85 | 42.116 | 6.32 | 1.444 | 5.307 | 8992.45 | 2.43 | 98.1 | 78.6 | 1423 | 21.01 | 5845.1 | 3258.7 | 3217.1 | 4679.8 | 1207.3 | 0.68086 | 6.75
2024-12-09 | 21:21 | Data | 0 | 31.083 | 28.517 | 221.504 | 7.62 | 207.642 | 2189.08 | 25.88 | 42.206 | 6.31 | 1.447 | 5.315 | 9001.49 | 2.586 | 98.1 | 78.6 | 1423 | 21.06 | 5851 | 3266.8 | 3204.5 | 4675.5 | 1207.3 | 0.68298 | 6.761
2024-12-09 | 21:21 | Data | 0 | 31.123 | 28.808 | 221.323 | 7.62 | 207.642 | 2188.18 | 25.89 | 42.116 | 6.32 | 1.444 | 5.289 | 9010.54 | 2.505 | 98.1 | 78.5 | 1423 | 21.06 | 5856.8 | 3247.8 | 3236.5 | 4690.6 | 1207.3 | 0.67666 | 6.734
2024-12-09 | 21:21 | Data | 0 | 31.339 | 28.598 | 221.368 | 7.62 | 207.687 | 2189.08 | 25.89 | 42.116 | 6.31 | 1.443 | 5.305 | 8996.97 | 2.532 | 98.1 | 78.6 | 1422 | 21.06 | 5848 | 3252.7 | 3229.1 | 4688.8 | 1207.3 | 0.67774 | 6.747
2024-12-09 | 21:21 | Data | 0 | 31.11 | 28.571 | 221.368 | 7.62 | 207.552 | 2187.27 | 25.89 | 42.387 | 6.32 | 1.433 | 5.292 | 8992.45 | 2.538 | 98.1 | 78.7 | 1422 | 21.19 | 5845.1 | 3254.4 | 3217.5 | 4679.7 | 1207.3 | 0.67864 | 6.724
2024-12-09 | 21:21 | Data | 0 | 31.137 | 28.396 | 221.187 | 7.62 | 207.597 | 2187.27 | 25.89 | 42.116 | 6.32 | 1.445 | 5.298 | 8992.45 | 2.552 | 98.1 | 78.6 | 1422 | 21.01 | 5845.1 | 3258.5 | 3205.6 | 4672.4 | 1207.3 | 0.68171 | 6.741
2024-12-09 | 21:21 | Data | 0 | 31.312 | 29.004 | 221.684 | 7.62 | 207.687 | 2180.95 | 25.88 | 42.387 | 6.31 | 1.445 | 5.301 | 8960.79 | 2.532 | 98.1 | 78.6 | 1417 | 21.19 | 5824.5 | 3268.5 | 3190.8 | 4668 | 1207.3 | 0.6838 | 6.746
2024-12-09 | 21:21 | Data | 0 | 31.461 | 28.409 | 221.368 | 7.62 | 207.642 | 2187.27 | 25.88 | 42.387 | 6.31 | 1.449 | 5.302 | 8978.88 | 2.552 | 98.1 | 78.5 | 1421 | 21.19 | 5836.3 | 3250.5 | 3199.2 | 4661.1 | 1207.3 | 0.68225 | 6.751
2024-12-09 | 21:21 | Data | 0 | 31.326 | 28.416 | 221.458 | 7.62 | 207.597 | 2187.27 | 25.88 | 42.387 | 6.32 | 1.453 | 5.317 | 8996.97 | 2.68 | 98.1 | 78.5 | 1422 | 21.19 | 5848 | 3257.4 | 3203.3 | 4673.3 | 1207.3 | 0.68042 | 6.771
2024-12-09 | 21:21 | Data | 0 | 31.488 | 28.693 | 221.594 | 7.63 | 207.642 | 2188.18 | 25.89 | 42.116 | 6.31 | 1.453 | 5.314 | 8965.31 | 2.768 | 98.1 | 78.5 | 1422 | 21.01 | 5827.5 | 3257.8 | 3207 | 4674.9 | 1207.3 | 0.68062 | 6.768
2024-12-09 | 21:21 | Data | 0 | 31.569 | 28.646 | 221.549 | 7.62 | 207.778 | 2189.08 | 25.89 | 42.116 | 6.32 | 1.452 | 5.298 | 8992.45 | 2.592 | 98.1 | 78.5 | 1423 | 21.15 | 5845.1 | 3257.3 | 3242.5 | 4693.5 | 1207.3 | 0.67763 | 6.749
2024-12-09 | 21:21 | Data | 0 | 31.137 | 28.781 | 221.277 | 7.62 | 207.552 | 2188.18 | 25.89 | 42.387 | 6.31 | 1.45 | 5.278 | 8969.84 | 2.37 | 98.1 | 78.5 | 1423 | 21.24 | 5830.4 | 3251 | 3242.8 | 4692.2 | 1207.3 | 0.67664 | 6.727
2024-12-09 | 21:21 | Data | 0 | 31.691 | 28.592 | 221.594 | 7.62 | 207.778 | 2191.79 | 25.89 | 42.387 | 6.32 | 1.436 | 5.284 | 8965.31 | 2.478 | 98.1 | 78.6 | 1424 | 21.15 | 5827.5 | 3242 | 3255.3 | 4694 | 1207.3 | 0.67498 | 6.719
2024-12-09 | 21:21 | Data | 0 | 31.562 | 28.612 | 221.549 | 7.62 | 207.733 | 2191.79 | 25.86 | 42.387 | 6.32 | 1.448 | 5.281 | 8969.84 | 2.606 | 98.1 | 78.5 | 1424 | 21.19 | 5830.4 | 3254.6 | 3241.2 | 4697.1 | 1207.3 | 0.67666 | 6.73
2024-12-09 | 21:22 | Data | 0 | 31.312 | 28.74 | 221.594 | 7.62 | 207.687 | 2192.7 | 25.89 | 42.297 | 6.31 | 1.457 | 5.302 | 8965.31 | 2.64 | 98.1 | 78.4 | 1425 | 21.15 | 5827.5 | 3241 | 3231.1 | 4678.7 | 1207.3 | 0.67905 | 6.758
2024-12-09 | 21:22 | Data | 0 | 31.528 | 28.801 | 221.458 | 7.62 | 207.552 | 2089.66 | 25.89 | 42.206 | 6.32 | 1.452 | 5.301 | 8960.79 | 2.755 | 98 | 78.5 | 1359 | 21.1 | 5824.5 | 3253.6 | 3216.8 | 4674.5 | 1207.3 | 0.67974 | 6.754
2024-12-09 | 21:22 | Data | 0 | 30.901 | 28.369 | 221.458 | 7.62 | 207.597 | 2179.14 | 25.89 | 42.387 | 6.32 | 1.447 | 5.321 | 8960.79 | 2.484 | 98.1 | 78.6 | 1417 | 21.15 | 5824.5 | 3257.1 | 3190.1 | 4661.4 | 1207.3 | 0.68269 | 6.768
2024-12-09 | 21:22 | Data | 0 | 31.555 | 28.747 | 221.504 | 7.62 | 207.733 | 2180.95 | 25.89 | 42.387 | 6.31 | 1.446 | 5.317 | 8965.31 | 2.538 | 98.1 | 78.6 | 1418 | 21.19 | 5827.5 | 3270.9 | 3206.4 | 4680 | 1207.4 | 0.6824 | 6.765
2024-12-09 | 21:22 | Data | 0 | 31.339 | 28.814 | 221.549 | 7.62 | 207.733 | 2189.08 | 25.88 | 42.116 | 6.32 | 1.45 | 5.314 | 8965.31 | 2.518 | 98.1 | 78.6 | 1423 | 21.06 | 5827.5 | 3247.9 | 3214.6 | 4669.4 | 1207.4 | 0.67948 | 6.765
2024-12-09 | 21:22 | Data | 0 | 31.11 | 28.949 | 221.458 | 7.62 | 207.687 | 2182.75 | 25.89 | 42.387 | 6.32 | 1.453 | 5.317 | 8969.84 | 2.424 | 98.1 | 78.5 | 1419 | 21.19 | 5830.4 | 3251.1 | 3216.6 | 4676.9 | 1207.4 | 0.68039 | 6.769
2024-12-09 | 21:22 | Data | 0 | 30.894 | 28.558 | 221.187 | 7.62 | 207.552 | 2199.02 | 25.88 | 42.477 | 6.32 | 1.453 | 5.325 | 8978.88 | 2.511 | 98.1 | 78.6 | 1430 | 21.19 | 5836.3 | 3262.8 | 3235.9 | 4694.7 | 1207.4 | 0.67819 | 6.778
2024-12-09 | 21:22 | Data | 0 | 31.211 | 28.625 | 221.594 | 7.62 | 207.642 | 2199.93 | 25.88 | 42.116 | 6.31 | 1.446 | 5.312 | 8965.31 | 2.782 | 98.1 | 78.6 | 1430 | 21.06 | 5827.5 | 3246.9 | 3243 | 4691.5 | 1207.4 | 0.67631 | 6.758
2024-12-09 | 21:22 | Data | 0 | 30.887 | 28.544 | 221.323 | 7.62 | 207.597 | 2199.02 | 25.89 | 42.026 | 6.32 | 1.461 | 5.313 | 8938.18 | 2.43 | 98.1 | 78.4 | 1430 | 21.01 | 5809.8 | 3254 | 3259.2 | 4702.5 | 1207.4 | 0.67471 | 6.773
2024-12-09 | 21:22 | Data | 0 | 31.555 | 28.605 | 221.458 | 7.61 | 207.642 | 2199.02 | 25.88 | 42.116 | 6.32 | 1.454 | 5.297 | 8965.31 | 2.694 | 98.1 | 78.5 | 1429 | 21.06 | 5827.5 | 3266.4 | 3250.9 | 4706.9 | 1207.4 | 0.67782 | 6.751
2024-12-09 | 21:22 | Data | 0 | 30.955 | 28.625 | 221.368 | 7.62 | 207.687 | 2197.22 | 25.89 | 42.116 | 6.31 | 1.441 | 5.283 | 8947.23 | 2.221 | 98.1 | 78.6 | 1428 | 21.06 | 5815.7 | 3257.2 | 3234.5 | 4706.8 | 1207.4 | 0.67887 | 6.725
2024-12-09 | 21:22 | Data | 0 | 31.501 | 28.835 | 221.639 | 7.62 | 207.778 | 2197.22 | 25.89 | 42.206 | 6.32 | 1.451 | 5.289 | 8969.84 | 2.532 | 98.1 | 78.5 | 1429 | 21.06 | 5830.4 | 3263.9 | 3234.5 | 4694.5 | 1207.4 | 0.67731 | 6.738
2024-12-09 | 21:22 | Data | 0 | 31.326 | 28.747 | 221.323 | 7.62 | 207.507 | 2197.22 | 25.89 | 42.116 | 6.32 | 1.454 | 5.307 | 8969.84 | 2.592 | 98.1 | 78.5 | 1428 | 21.06 | 5830.4 | 3278.9 | 3236.2 | 4707 | 1207.4 | 0.68082 | 6.76
2024-12-09 | 21:22 | Data | 0 | 31.427 | 28.801 | 221.504 | 7.62 | 207.642 | 2199.02 | 25.89 | 42.116 | 6.32 | 1.453 | 5.286 | 8978.88 | 2.734 | 98.1 | 78.4 | 1429 | 21.01 | 5836.3 | 3244 | 3223.3 | 4671.9 | 1207.4 | 0.67824 | 6.739
2024-12-09 | 21:22 | Data | 0 | 31.346 | 28.7 | 221.639 | 7.62 | 207.778 | 2198.12 | 25.88 | 42.206 | 6.32 | 1.46 | 5.289 | 8965.31 | 2.478 | 98.1 | 78.3 | 1429 | 21.06 | 5827.5 | 3266.5 | 3201.6 | 4673.9 | 1207.4 | 0.68233 | 6.75
2024-12-09 | 21:22 | Data | 0 | 30.928 | 28.544 | 221.458 | 7.62 | 207.597 | 2199.93 | 25.89 | 42.206 | 6.32 | 1.461 | 5.281 | 8974.36 | 2.37 | 98.1 | 78.3 | 1430 | 21.06 | 5833.3 | 3247.5 | 3207.8 | 4659.7 | 1207.4 | 0.68002 | 6.741
2024-12-09 | 21:22 | Data | 0 | 31.339 | 28.625 | 221.684 | 7.62 | 207.733 | 2199.02 | 25.88 | 42.116 | 6.31 | 1.45 | 5.29 | 8983.4 | 2.545 | 98.1 | 78.5 | 1430 | 21.1 | 5839.2 | 3257.3 | 3240.1 | 4674.5 | 1207.4 | 0.6789 | 6.739
2024-12-09 | 21:22 | Data | 0 | 31.333 | 28.571 | 221.458 | 7.62 | 207.597 | 2200.83 | 25.89 | 42.206 | 6.31 | 1.468 | 5.296 | 8965.31 | 2.761 | 98.1 | 78.3 | 1431 | 21.01 | 5827.5 | 3276.9 | 3241.7 | 4710.5 | 1207.4 | 0.67896 | 6.764
2024-12-09 | 21:23 | Data | 0 | 31.117 | 28.585 | 221.504 | 7.62 | 207.597 | 2196.31 | 25.86 | 42.116 | 6.31 | 1.464 | 5.316 | 8969.84 | 2.701 | 98.1 | 78.4 | 1428 | 21.06 | 5830.4 | 3265.3 | 3240.9 | 4704.3 | 1207.4 | 0.67676 | 6.781
2024-12-09 | 21:23 | Data | 0 | 31.184 | 28.355 | 221.323 | 7.62 | 207.642 | 2199.02 | 25.89 | 42.116 | 6.32 | 1.459 | 5.296 | 8978.88 | 2.559 | 98.1 | 78.4 | 1429 | 21.1 | 5836.3 | 3260.9 | 3237.1 | 4695.8 | 1207.4 | 0.67856 | 6.755
2024-12-09 | 21:23 | Data | 0 | 31.333 | 28.598 | 221.368 | 7.62 | 207.733 | 2197.22 | 25.88 | 42.116 | 6.31 | 1.446 | 5.27 | 8965.31 | 2.538 | 98.1 | 78.5 | 1429 | 21.06 | 5827.5 | 3274.7 | 3211.3 | 4685.6 | 1207.4 | 0.6836 | 6.717
2024-12-09 | 21:23 | Data | 0 | 31.339 | 28.632 | 221.504 | 7.62 | 207.687 | 2197.22 | 25.88 | 42.206 | 6.32 | 1.455 | 5.31 | 8969.84 | 2.592 | 98.1 | 78.5 | 1428 | 21.01 | 5830.4 | 3265.7 | 3227.3 | 4693.7 | 1207.4 | 0.68338 | 6.767
2024-12-09 | 21:23 | Data | 0 | 31.427 | 28.909 | 221.504 | 7.62 | 207.642 | 2194.5 | 25.88 | 42.116 | 6.32 | 1.455 | 5.29 | 8974.36 | 2.525 | 98.1 | 78.4 | 1426 | 21.06 | 5833.3 | 3261.7 | 3202.6 | 4674.7 | 1207.4 | 0.6816 | 6.747
2024-12-09 | 21:23 | Data | 0 | 31.211 | 28.571 | 221.323 | 7.62 | 207.597 | 2194.5 | 25.88 | 42.206 | 6.31 | 1.449 | 5.283 | 8956.27 | 2.545 | 98.1 | 78.5 | 1427 | 21.1 | 5821.6 | 3255.9 | 3205.7 | 4671.9 | 1207.4 | 0.68076 | 6.732
2024-12-09 | 21:23 | Data | 0 | 31.11 | 28.74 | 221.594 | 7.61 | 207.642 | 2189.99 | 25.88 | 42.206 | 6.31 | 1.444 | 5.31 | 8951.75 | 2.633 | 98.1 | 78.6 | 1423 | 21.06 | 5818.6 | 3264.7 | 3217.7 | 4688 | 1207.4 | 0.68036 | 6.755
2024-12-09 | 21:23 | Data | 0 | 31.61 | 28.706 | 221.594 | 7.62 | 207.597 | 2191.79 | 25.86 | 42.026 | 6.31 | 1.447 | 5.255 | 8951.75 | 2.572 | 98.1 | 78.4 | 1425 | 21.06 | 5818.6 | 3258.7 | 3219.1 | 4680.8 | 1207.4 | 0.6802 | 6.705
2024-12-09 | 21:23 | Data | 0 | 31.312 | 28.571 | 221.458 | 7.62 | 207.687 | 2193.6 | 25.89 | 42.116 | 6.32 | 1.457 | 5.257 | 8956.27 | 2.647 | 98.1 | 78.3 | 1426 | 21.06 | 5821.6 | 3272.5 | 3223.7 | 4696.6 | 1207.4 | 0.68073 | 6.712
2024-12-09 | 21:23 | Data | 0 | 31.211 | 28.416 | 221.458 | 7.62 | 207.597 | 2194.5 | 25.89 | 42.477 | 6.32 | 1.45 | 5.281 | 8951.75 | 2.586 | 98.1 | 78.5 | 1426 | 21.1 | 5818.6 | 3251.2 | 3208.5 | 4666.6 | 1207.4 | 0.6811 | 6.731
2024-12-09 | 21:23 | Data | 0 | 31.036 | 28.571 | 221.458 | 7.62 | 207.552 | 2194.5 | 25.89 | 42.387 | 6.31 | 1.463 | 5.298 | 8983.4 | 2.329 | 98.1 | 78.4 | 1426 | 21.19 | 5839.2 | 3246.3 | 3203.7 | 4653.3 | 1207.4 | 0.68258 | 6.76
2024-12-09 | 21:23 | Data | 0 | 31.306 | 28.585 | 221.549 | 7.63 | 207.778 | 2194.5 | 25.88 | 42.206 | 6.31 | 1.462 | 5.305 | 9390.4 | 2.869 | 98.1 | 78.4 | 1427 | 21.1 | 6103.8 | 3254.7 | 3172.8 | 4647.9 | 1207.4 | 0.68281 | 6.767
2024-12-09 | 21:23 | Data | 0 | 31.137 | 28.551 | 221.368 | 7.62 | 207.642 | 2247.83 | 25.88 | 42.116 | 6.32 | 1.45 | 5.3 | 9060.28 | 2.41 | 98.1 | 78.5 | 1462 | 21.06 | 5889.2 | 3251.3 | 3205.2 | 4671.7 | 1207.4 | 0.68 | 6.748
2024-12-09 | 21:23 | Data | 0 | 31.542 | 29.085 | 221.504 | 7.62 | 207.687 | 2245.12 | 25.88 | 42.206 | 6.31 | 1.444 | 5.3 | 9006.01 | 2.424 | 98.1 | 78.6 | 1459 | 21.1 | 5853.9 | 3246.8 | 3201.7 | 4663 | 1207.4 | 0.68008 | 6.745
2024-12-09 | 21:23 | Data | 0 | 31.13 | 28.625 | 221.504 | 7.62 | 207.687 | 2246.93 | 25.88 | 42.206 | 6.32 | 1.45 | 5.295 | 8996.97 | 2.43 | 98.1 | 78.5 | 1461 | 21.15 | 5848 | 3241.2 | 3230.6 | 4677.4 | 1207.4 | 0.67631 | 6.744
2024-12-09 | 21:23 | Data | 0 | 31.42 | 28.571 | 221.504 | 7.62 | 207.597 | 2246.02 | 25.89 | 42.387 | 6.32 | 1.454 | 5.27 | 8974.36 | 2.484 | 98.1 | 78.4 | 1460 | 21.19 | 5833.3 | 3263.1 | 3205.2 | 4677.6 | 1207.4 | 0.68082 | 6.724
2024-12-09 | 21:23 | Data | 0 | 31.312 | 28.571 | 221.368 | 7.62 | 207.552 | 2191.79 | 25.89 | 42.387 | 6.31 | 1.461 | 5.295 | 8960.79 | 2.586 | 98.1 | 78.4 | 1425 | 21.19 | 5824.5 | 3243.6 | 3232.8 | 4681.4 | 1207.4 | 0.67721 | 6.755
2024-12-09 | 21:24 | Data | 0 | 30.995 | 28.747 | 221.368 | 7.62 | 207.552 | 2187.27 | 25.88 | 42.477 | 6.31 | 1.463 | 5.289 | 8951.75 | 2.633 | 98.1 | 78.3 | 1422 | 21.15 | 5818.6 | 3256.6 | 3219.6 | 4682.1 | 1207.4 | 0.67998 | 6.753
2024-12-09 | 21:24 | Data | 0 | 31.481 | 29.044 | 221.323 | 7.62 | 207.597 | 2191.79 | 25.89 | 42.477 | 6.32 | 1.446 | 5.3 | 8965.31 | 2.478 | 98.1 | 78.6 | 1425 | 21.19 | 5827.5 | 3254.2 | 3223.3 | 4676.8 | 1207.5 | 0.67999 | 6.746
2024-12-09 | 21:24 | Data | 0 | 31.427 | 28.585 | 221.504 | 7.62 | 207.687 | 2192.7 | 25.88 | 42.477 | 6.32 | 1.453 | 5.292 | 8969.84 | 2.606 | 98.1 | 78.4 | 1425 | 21.15 | 5830.4 | 3259 | 3208.7 | 4674.5 | 1207.5 | 0.68191 | 6.744
2024-12-09 | 21:24 | Data | 0 | 31.508 | 28.74 | 221.594 | 7.62 | 207.687 | 2189.08 | 25.88 | 42.387 | 6.32 | 1.447 | 5.266 | 8965.31 | 2.532 | 98.1 | 78.5 | 1422 | 21.19 | 5827.5 | 3259.3 | 3195.2 | 4662.3 | 1207.5 | 0.68406 | 6.711
2024-12-09 | 21:24 | Data | 0 | 31.508 | 28.605 | 221.594 | 7.62 | 207.687 | 2183.66 | 25.89 | 42.477 | 6.31 | 1.448 | 5.289 | 8960.79 | 2.687 | 98.1 | 78.5 | 1419 | 21.19 | 5824.5 | 3255.7 | 3184.3 | 4653.8 | 1207.5 | 0.68369 | 6.736
2024-12-09 | 21:24 | Data | 0 | 30.887 | 28.625 | 221.549 | 7.62 | 207.597 | 2186.37 | 25.89 | 42.387 | 6.31 | 1.443 | 5.287 | 8978.88 | 2.316 | 98.1 | 78.6 | 1421 | 21.19 | 5836.3 | 3235.1 | 3197.1 | 4651.3 | 1207.5 | 0.6791 | 6.73
2024-12-09 | 21:24 | Data | 0 | 31.198 | 28.794 | 221.594 | 7.62 | 207.778 | 2186.37 | 25.88 | 42.477 | 6.32 | 1.446 | 5.311 | 8978.88 | 2.525 | 98.1 | 78.6 | 1421 | 21.19 | 5836.3 | 3260.8 | 3195.4 | 4664.9 | 1207.5 | 0.68335 | 6.757
2024-12-09 | 21:24 | Data | 0 | 30.995 | 28.895 | 221.504 | 7.62 | 207.687 | 2187.27 | 25.88 | 42.387 | 6.31 | 1.452 | 5.283 | 8969.84 | 2.518 | 98.1 | 78.4 | 1422 | 21.19 | 5830.4 | 3255.8 | 3187.6 | 4668.7 | 1207.5 | 0.68031 | 6.736
2024-12-09 | 21:24 | Data | 0 | 31.339 | 28.862 | 221.594 | 7.62 | 207.778 | 2183.66 | 25.88 | 42.387 | 6.32 | 1.455 | 5.28 | 8956.27 | 2.498 | 98.1 | 78.4 | 1419 | 21.24 | 5821.6 | 3259.4 | 3228.6 | 4695.2 | 1207.5 | 0.67891 | 6.736
2024-12-09 | 21:24 | Data | 0 | 31.252 | 28.909 | 221.458 | 7.63 | 207.642 | 2189.99 | 25.89 | 42.387 | 6.32 | 1.452 | 5.304 | 8965.31 | 2.721 | 98.1 | 78.5 | 1423 | 21.15 | 5827.5 | 3241.4 | 3208.1 | 4679.4 | 1207.5 | 0.67879 | 6.756
2024-12-09 | 21:24 | Data | 0 | 31.549 | 28.585 | 221.639 | 7.62 | 207.733 | 2186.37 | 25.88 | 42.206 | 6.32 | 1.452 | 5.296 | 8956.27 | 2.815 | 98.1 | 78.5 | 1420 | 21.06 | 5821.6 | 3250.4 | 3207.6 | 4668.3 | 1207.5 | 0.67999 | 6.749
2024-12-09 | 21:24 | Data | 0 | 30.955 | 28.693 | 221.368 | 7.61 | 207.642 | 2105.93 | 25.89 | 42.116 | 6.32 | 1.454 | 5.303 | 8983.4 | 2.518 | 98 | 78.5 | 1368 | 21.06 | 5839.2 | 3244.2 | 3206.9 | 4665.2 | 1207.5 | 0.679 | 6.758
2024-12-09 | 21:24 | Data | 0 | 31.252 | 28.585 | 221.549 | 7.62 | 207.687 | 2166.49 | 25.86 | 42.116 | 6.31 | 1.453 | 5.3 | 8983.4 | 2.532 | 98.1 | 78.5 | 1411 | 21.06 | 5839.2 | 3233.3 | 3222.9 | 4668.3 | 1207.5 | 0.67581 | 6.754
2024-12-09 | 21:24 | Data | 0 | 31.171 | 28.693 | 221.504 | 7.62 | 207.642 | 2182.75 | 25.88 | 42.116 | 6.32 | 1.441 | 5.284 | 8965.31 | 2.538 | 98.1 | 78.6 | 1419 | 21.06 | 5827.5 | 3238.4 | 3219 | 4669.3 | 1207.5 | 0.6775 | 6.725
2024-12-09 | 21:24 | Data | 0 | 31.772 | 28.72 | 221.458 | 7.62 | 207.778 | 2182.75 | 25.88 | 42.116 | 6.32 | 1.458 | 5.326 | 8956.27 | 2.741 | 98.1 | 78.5 | 1419 | 21.06 | 5821.6 | 3260.3 | 3226.5 | 4685.2 | 1207.5 | 0.68009 | 6.783
2024-12-09 | 21:24 | Data | 0 | 31.677 | 28.767 | 221.504 | 7.62 | 207.778 | 2182.75 | 25.88 | 42.116 | 6.31 | 1.457 | 5.322 | 8938.18 | 2.653 | 98.1 | 78.5 | 1419 | 21.1 | 5809.8 | 3257.7 | 3206.9 | 4664.2 | 1207.5 | 0.67927 | 6.777
2024-12-09 | 21:24 | Data | 0 | 31.312 | 28.605 | 221.594 | 7.62 | 207.778 | 2203.54 | 25.88 | 42.206 | 6.31 | 1.453 | 5.318 | 8938.18 | 2.403 | 98.1 | 78.5 | 1433 | 21.19 | 5809.8 | 3248.7 | 3208 | 4667.9 | 1207.5 | 0.67923 | 6.772
2024-12-09 | 21:24 | Data | 0 | 31.42 | 28.909 | 221.549 | 7.62 | 207.597 | 2205.35 | 25.88 | 42.297 | 6.31 | 1.453 | 5.331 | 8951.75 | 2.815 | 98.1 | 78.6 | 1433 | 21.15 | 5818.6 | 3260.5 | 3204.9 | 4673.5 | 1207.5 | 0.6807 | 6.784
2024-12-09 | 21:25 | Data | 0 | 31.218 | 28.794 | 221.549 | 7.62 | 207.778 | 2205.35 | 25.89 | 42.116 | 6.31 | 1.447 | 5.327 | 8947.23 | 2.714 | 98.1 | 78.7 | 1433 | 21.06 | 5815.7 | 3246.1 | 3196.3 | 4675.9 | 1207.5 | 0.6807 | 6.774
2024-12-09 | 21:25 | Data | 0 | 31.643 | 28.835 | 221.639 | 7.62 | 207.687 | 2206.25 | 25.88 | 42.116 | 6.31 | 1.447 | 5.315 | 8951.75 | 2.748 | 98.1 | 78.6 | 1433 | 21.01 | 5818.6 | 3248.4 | 3207.2 | 4665.7 | 1207.5 | 0.68056 | 6.763
2024-12-09 | 21:25 | Data | 0 | 31.11 | 28.571 | 221.458 | 7.62 | 207.552 | 2205.35 | 25.88 | 42.477 | 6.31 | 1.452 | 5.279 | 8951.75 | 2.538 | 98.1 | 78.4 | 1433 | 21.19 | 5818.6 | 3237.4 | 3183.2 | 4642.1 | 1207.5 | 0.68061 | 6.73
2024-12-09 | 21:25 | Data | 0 | 31.11 | 28.571 | 221.368 | 7.62 | 207.642 | 2203.54 | 25.88 | 42.297 | 6.31 | 1.457 | 5.282 | 8956.27 | 2.741 | 98.1 | 78.4 | 1432 | 21.06 | 5821.6 | 3239.1 | 3197.8 | 4652.4 | 1207.5 | 0.67981 | 6.737
2024-12-09 | 21:25 | Data | 0 | 31.387 | 28.646 | 221.323 | 7.62 | 207.687 | 2203.54 | 25.89 | 42.116 | 6.31 | 1.454 | 5.313 | 8951.75 | 2.525 | 98.1 | 78.5 | 1432 | 21.1 | 5818.6 | 3258.1 | 3202.1 | 4670.7 | 1207.5 | 0.68157 | 6.767
2024-12-09 | 21:25 | Data | 0 | 31.333 | 28.808 | 221.323 | 7.62 | 207.552 | 2203.54 | 25.89 | 42.206 | 6.31 | 1.452 | 5.27 | 8960.79 | 2.532 | 98.1 | 78.4 | 1432 | 21.06 | 5824.5 | 3264.9 | 3220.5 | 4683.7 | 1207.5 | 0.68093 | 6.724
2024-12-09 | 21:25 | Data | 0 | 31.495 | 28.76 | 221.504 | 7.62 | 207.642 | 2203.54 | 25.88 | 42.116 | 6.31 | 1.451 | 5.302 | 8974.36 | 2.37 | 98.1 | 78.5 | 1432 | 21.01 | 5833.3 | 3250.5 | 3226.5 | 4684 | 1207.5 | 0.67719 | 6.753
2024-12-09 | 21:25 | Data | 0 | 30.975 | 28.747 | 221.549 | 7.62 | 207.733 | 2197.22 | 25.89 | 42.116 | 6.31 | 1.452 | 5.281 | 8951.75 | 2.309 | 98.1 | 78.4 | 1428 | 21.06 | 5818.6 | 3259.8 | 3246.9 | 4703.1 | 1207.5 | 0.67658 | 6.735
2024-12-09 | 21:25 | Data | 0 | 31.204 | 28.578 | 221.639 | 7.62 | 207.778 | 2203.54 | 25.88 | 42.116 | 6.32 | 1.457 | 5.282 | 8965.31 | 2.383 | 98.1 | 78.4 | 1432 | 21.06 | 5827.5 | 3262.1 | 3235.4 | 4694 | 1207.5 | 0.67841 | 6.738
2024-12-09 | 21:25 | Data | 0 | 31.326 | 28.808 | 221.594 | 7.62 | 207.687 | 2201.74 | 25.89 | 42.206 | 6.31 | 1.457 | 5.275 | 8956.27 | 2.532 | 98.1 | 78.3 | 1432 | 21.1 | 5821.6 | 3265.6 | 3215.3 | 4680.8 | 1207.5 | 0.68167 | 6.733
2024-12-09 | 21:25 | Data | 0 | 31.528 | 28.706 | 221.549 | 7.62 | 207.687 | 2203.54 | 25.88 | 42.116 | 6.31 | 1.455 | 5.298 | 8951.75 | 2.802 | 98.1 | 78.5 | 1431 | 21.06 | 5818.6 | 3251.6 | 3227.7 | 4685.6 | 1207.5 | 0.67837 | 6.754
2024-12-09 | 21:25 | Data | 0 | 31.11 | 28.571 | 221.458 | 7.62 | 207.597 | 2206.25 | 25.89 | 42.206 | 6.31 | 1.436 | 5.277 | 8960.79 | 2.424 | 98.1 | 78.6 | 1434 | 21.06 | 5824.5 | 3262.2 | 3222.4 | 4687.2 | 1207.5 | 0.68003 | 6.713
2024-12-09 | 21:25 | Data | 0 | 31.225 | 28.625 | 221.458 | 7.62 | 207.687 | 2203.54 | 25.88 | 42.297 | 6.32 | 1.452 | 5.292 | 8965.31 | 2.633 | 98.1 | 78.5 | 1432 | 21.15 | 5827.5 | 3235 | 3212.5 | 4660.5 | 1207.5 | 0.67852 | 6.745
2024-12-09 | 21:25 | Data | 0 | 31.542 | 28.592 | 221.549 | 7.62 | 207.687 | 2203.54 | 25.89 | 42.387 | 6.3 | 1.443 | 5.281 | 8951.75 | 2.707 | 98.1 | 78.5 | 1432 | 21.19 | 5818.6 | 3246.2 | 3222.2 | 4681.1 | 1207.5 | 0.6787 | 6.727
2024-12-09 | 21:25 | Data | 0 | 31.11 | 28.551 | 221.368 | 7.62 | 207.687 | 2199.02 | 25.88 | 42.206 | 6.31 | 1.441 | 5.307 | 8960.79 | 2.579 | 98.1 | 78.6 | 1429 | 21.1 | 5824.5 | 3256.4 | 3233.2 | 4687 | 1207.5 | 0.67898 | 6.747
2024-12-09 | 21:25 | Data | 0 | 31.339 | 28.821 | 221.504 | 7.62 | 207.733 | 2199.93 | 25.88 | 42.387 | 6.32 | 1.45 | 5.281 | 8965.31 | 2.505 | 98.1 | 78.5 | 1431 | 21.19 | 5827.5 | 3248.8 | 3194 | 4655.7 | 1207.6 | 0.68165 | 6.732
2024-12-09 | 21:25 | Data | 0 | 31.272 | 28.578 | 221.504 | 7.63 | 207.733 | 2200.83 | 25.88 | 42.297 | 6.31 | 1.447 | 5.294 | 8965.31 | 2.707 | 98.1 | 78.5 | 1430 | 21.15 | 5827.5 | 3248.8 | 3215.4 | 4674.6 | 1207.6 | 0.67849 | 6.739
2024-12-09 | 21:25 | Data | 0 | 31.164 | 28.693 | 221.549 | 7.62 | 207.642 | 2198.12 | 25.88 | 42.387 | 6.31 | 1.45 | 5.28 | 8978.88 | 2.538 | 98.1 | 78.5 | 1429 | 21.19 | 5836.3 | 3247.9 | 3205.3 | 4669.8 | 1207.6 | 0.68113 | 6.73
2024-12-09 | 21:26 | Data | 0 | 31.123 | 28.794 | 221.458 | 7.62 | 207.778 | 2199.93 | 25.88 | 42.387 | 6.32 | 1.454 | 5.297 | 8969.84 | 2.316 | 98.1 | 78.5 | 1430 | 21.15 | 5830.4 | 3264.8 | 3196.6 | 4668.6 | 1207.6 | 0.68314 | 6.751
2024-12-09 | 21:26 | Data | 0 | 31.326 | 28.794 | 221.323 | 7.62 | 207.597 | 2197.22 | 25.89 | 42.477 | 6.31 | 1.451 | 5.293 | 8965.31 | 2.559 | 98.1 | 78.5 | 1428 | 21.19 | 5827.5 | 3246.8 | 3188.5 | 4661.4 | 1207.6 | 0.68297 | 6.743
2024-12-09 | 21:26 | Data | 0 | 31.508 | 28.821 | 221.594 | 7.62 | 207.778 | 2197.22 | 25.89 | 42.387 | 6.31 | 1.45 | 5.287 | 8951.75 | 2.626 | 98.1 | 78.5 | 1428 | 21.19 | 5818.6 | 3262.6 | 3176.7 | 4654.6 | 1207.6 | 0.68375 | 6.736
2024-12-09 | 21:26 | Data | 0 | 31.366 | 28.632 | 221.458 | 7.62 | 207.687 | 2199.93 | 25.89 | 42.387 | 6.31 | 1.452 | 5.316 | 8965.31 | 2.66 | 98.1 | 78.5 | 1429 | 21.15 | 5827.5 | 3261.4 | 3191.6 | 4662.2 | 1207.6 | 0.6837 | 6.769
2024-12-09 | 21:26 | Data | 0 | 31.562 | 28.646 | 221.549 | 7.61 | 207.733 | 2201.74 | 25.89 | 42.387 | 6.31 | 1.462 | 5.321 | 8992.45 | 2.599 | 98.1 | 78.5 | 1431 | 21.19 | 5845.1 | 3254.4 | 3196.4 | 4663 | 1207.6 | 0.68243 | 6.783
2024-12-09 | 21:26 | Data | 0 | 31.535 | 28.754 | 221.549 | 7.62 | 207.687 | 2199.93 | 25.88 | 42.387 | 6.31 | 1.447 | 5.301 | 8992.45 | 2.701 | 98.1 | 78.6 | 1430 | 21.19 | 5845.1 | 3242 | 3160 | 4625.5 | 1207.6 | 0.68397 | 6.748
2024-12-09 | 21:26 | Data | 0 | 31.333 | 28.693 | 221.639 | 7.62 | 207.823 | 2199.93 | 25.88 | 42.387 | 6.31 | 1.443 | 5.295 | 8992.45 | 2.768 | 98.1 | 78.6 | 1429 | 21.19 | 5845.1 | 3270.9 | 3204.5 | 4679.7 | 1207.6 | 0.68278 | 6.738
2024-12-09 | 21:26 | Data | 0 | 30.955 | 28.457 | 221.458 | 7.62 | 207.597 | 2199.02 | 25.88 | 42.387 | 6.31 | 1.449 | 5.303 | 8996.97 | 2.329 | 98.1 | 78.5 | 1429 | 21.19 | 5848 | 3269 | 3189.6 | 4665.4 | 1207.6 | 0.68445 | 6.752
2024-12-09 | 21:26 | Data | 0 | 31.184 | 28.835 | 221.684 | 7.62 | 207.778 | 2200.83 | 25.88 | 42.387 | 6.31 | 1.448 | 5.311 | 8748.25 | 2.282 | 98.1 | 78.6 | 1430 | 21.19 | 5686.4 | 3256.6 | 3198.6 | 4666.9 | 1207.6 | 0.68323 | 6.76
2024-12-09 | 21:26 | Data | 0 | 31.13 | 28.571 | 221.549 | 7.62 | 207.642 | 2199.93 | 25.88 | 42.387 | 6.31 | 1.451 | 5.304 | 8752.77 | 2.457 | 98.1 | 78.5 | 1430 | 21.19 | 5689.3 | 3275.1 | 3181.3 | 4668.1 | 1207.6 | 0.68591 | 6.755
2024-12-09 | 21:26 | Data | 0 | 31.61 | 28.72 | 221.368 | 7.62 | 207.687 | 2203.54 | 25.89 | 42.658 | 6.32 | 1.454 | 5.27 | 8915.57 | 2.822 | 98.1 | 78.4 | 1431 | 21.33 | 5795.1 | 3253 | 3184 | 4656.4 | 1207.6 | 0.68221 | 6.725
2024-12-09 | 21:26 | Data | 0 | 31.117 | 28.571 | 221.323 | 7.62 | 207.642 | 2203.54 | 25.88 | 42.387 | 6.31 | 1.47 | 5.321 | 8965.31 | 2.498 | 98.1 | 78.4 | 1432 | 21.15 | 5827.5 | 3258.1 | 3189.5 | 4658.2 | 1207.6 | 0.68296 | 6.79
2024-12-09 | 21:26 | Data | 0 | 31.015 | 28.571 | 221.504 | 7.62 | 207.597 | 2199.02 | 25.88 | 42.477 | 6.31 | 1.462 | 5.292 | 8956.27 | 2.525 | 98.1 | 78.4 | 1431 | 21.24 | 5821.6 | 3253.2 | 3171.4 | 4642.2 | 1207.6 | 0.6848 | 6.753
2024-12-09 | 21:26 | Data | 0 | 31.279 | 28.801 | 221.504 | 7.62 | 207.687 | 2206.25 | 25.88 | 42.387 | 6.31 | 1.446 | 5.273 | 8956.27 | 2.532 | 98.1 | 78.5 | 1434 | 21.19 | 5821.6 | 3243.2 | 3185 | 4651 | 1207.6 | 0.681 | 6.719
2024-12-09 | 21:26 | Data | 0 | 31.447 | 28.585 | 221.368 | 7.62 | 207.778 | 2203.54 | 25.88 | 42.387 | 6.31 | 1.447 | 5.281 | 8960.79 | 2.444 | 98.1 | 78.5 | 1431 | 21.19 | 5824.5 | 3262.5 | 3195.7 | 4669.8 | 1207.6 | 0.68173 | 6.727
2024-12-09 | 21:26 | Data | 0 | 31.117 | 28.781 | 221.458 | 7.62 | 207.733 | 2203.54 | 25.88 | 42.297 | 6.31 | 1.452 | 5.318 | 8965.31 | 2.417 | 98.1 | 78.6 | 1432 | 21.19 | 5827.5 | 3250.2 | 3211.2 | 4671.6 | 1207.6 | 0.67851 | 6.77
2024-12-09 | 21:27 | Data | 0 | 31.13 | 28.571 | 221.368 | 7.62 | 207.687 | 2199.93 | 25.88 | 42.387 | 6.31 | 1.449 | 5.303 | 8974.36 | 2.532 | 98.1 | 78.5 | 1430 | 21.24 | 5833.3 | 3250 | 3224.4 | 4684 | 1207.6 | 0.67735 | 6.751
2024-12-09 | 21:27 | Data | 0 | 31.123 | 28.619 | 221.549 | 7.62 | 207.687 | 2199.02 | 25.89 | 42.387 | 6.31 | 1.452 | 5.315 | 8965.31 | 2.424 | 98.1 | 78.5 | 1430 | 21.15 | 5827.5 | 3255.2 | 3219 | 4676.4 | 1207.6 | 0.67967 | 6.767
2024-12-09 | 21:27 | Data | 0 | 31.09 | 28.895 | 221.368 | 7.62 | 207.687 | 2199.93 | 25.86 | 42.387 | 6.32 | 1.451 | 5.312 | 8956.27 | 2.498 | 98.1 | 78.5 | 1430 | 21.19 | 5821.6 | 3262.9 | 3205.4 | 4676.4 | 1207.6 | 0.68087 | 6.763
2024-12-09 | 21:27 | Data | 0 | 31.339 | 28.808 | 221.594 | 7.62 | 207.868 | 2199.02 | 25.89 | 42.387 | 6.32 | 1.446 | 5.286 | 8965.31 | 2.532 | 98.1 | 78.5 | 1429 | 21.19 | 5827.5 | 3250.5 | 3230.4 | 4685.7 | 1207.6 | 0.67777 | 6.732
2024-12-09 | 21:27 | Data | 0 | 31.333 | 28.693 | 221.504 | 7.62 | 207.733 | 2196.31 | 25.88 | 42.477 | 6.32 | 1.46 | 5.305 | 8965.31 | 2.761 | 98.1 | 78.4 | 1428 | 21.28 | 5827.5 | 3261 | 3219.6 | 4678.2 | 1207.6 | 0.68101 | 6.765
2024-12-09 | 21:27 | Data | 0 | 30.921 | 28.895 | 221.368 | 7.63 | 207.687 | 2195.41 | 25.88 | 42.387 | 6.31 | 1.461 | 5.293 | 8965.31 | 2.478 | 98.1 | 78.4 | 1426 | 21.19 | 5827.5 | 3257.8 | 3232.6 | 4690.7 | 1207.6 | 0.67644 | 6.755
2024-12-09 | 21:27 | Data | 0 | 31.61 | 28.686 | 221.458 | 7.62 | 207.687 | 2191.79 | 25.89 | 42.116 | 6.31 | 1.445 | 5.292 | 8965.31 | 2.775 | 98.1 | 78.5 | 1425 | 21.06 | 5827.5 | 3266.1 | 3231.9 | 4694.9 | 1207.6 | 0.68012 | 6.735
2024-12-09 | 21:27 | Data | 0 | 31.184 | 28.808 | 221.639 | 7.62 | 207.778 | 2194.5 | 25.88 | 42.116 | 6.32 | 1.452 | 5.336 | 8929.14 | 2.309 | 98.1 | 78.6 | 1426 | 21.06 | 5803.9 | 3272.6 | 3202.5 | 4679.2 | 1207.6 | 0.68343 | 6.784
2024-12-09 | 21:27 | Data | 0 | 31.144 | 28.754 | 221.368 | 7.62 | 207.687 | 2194.5 | 25.89 | 42.116 | 6.32 | 1.451 | 5.308 | 8924.61 | 2.525 | 98.1 | 78.5 | 1427 | 21.06 | 5801 | 3262.2 | 3211.7 | 4679.6 | 1207.6 | 0.68182 | 6.758
2024-12-09 | 21:27 | Data | 0 | 31.13 | 28.922 | 221.368 | 7.62 | 207.733 | 2194.5 | 25.89 | 42.116 | 6.32 | 1.45 | 5.31 | 8924.61 | 2.478 | 98.1 | 78.6 | 1426 | 21.06 | 5801 | 3263.6 | 3234.5 | 4699.3 | 1207.6 | 0.6775 | 6.759
2024-12-09 | 21:27 | Data | 0 | 31.272 | 29.017 | 221.549 | 7.62 | 207.687 | 2194.5 | 25.88 | 42.206 | 6.31 | 1.452 | 5.298 | 8915.57 | 2.626 | 98.1 | 78.5 | 1426 | 21.06 | 5795.1 | 3253.4 | 3215.5 | 4674.6 | 1207.6 | 0.67767 | 6.75
2024-12-09 | 21:27 | Data | 0 | 31.123 | 28.673 | 221.277 | 7.62 | 207.642 | 2194.5 | 25.88 | 42.116 | 6.32 | 1.453 | 5.263 | 8924.61 | 2.444 | 98.1 | 78.4 | 1426 | 21.06 | 5801 | 3266.4 | 3228.9 | 4695.1 | 1207.6 | 0.67911 | 6.717
2024-12-09 | 21:27 | Data | 0 | 31.393 | 28.592 | 221.549 | 7.63 | 207.778 | 2194.5 | 25.88 | 42.206 | 6.31 | 1.462 | 5.288 | 8911.05 | 2.552 | 98.1 | 78.3 | 1426 | 21.01 | 5792.2 | 3276 | 3255 | 4718.9 | 1207.7 | 0.67878 | 6.75
2024-12-09 | 21:27 | Data | 0 | 31.042 | 28.794 | 221.639 | 7.62 | 207.642 | 2192.7 | 25.89 | 42.206 | 6.31 | 1.461 | 5.298 | 8924.61 | 2.491 | 98.1 | 78.4 | 1426 | 21.06 | 5801 | 3248.8 | 3252.4 | 4700.3 | 1207.7 | 0.67453 | 6.756
2024-12-09 | 21:27 | Data | 0 | 31.508 | 28.862 | 221.504 | 7.62 | 207.778 | 2194.5 | 25.88 | 42.116 | 6.31 | 1.461 | 5.311 | 8915.57 | 2.647 | 98.1 | 78.5 | 1426 | 21.1 | 5795.1 | 3253.6 | 3236.8 | 4689.5 | 1207.7 | 0.67765 | 6.771
2024-12-09 | 21:27 | Data | 0 | 30.894 | 28.848 | 221.458 | 7.62 | 207.778 | 2194.5 | 25.86 | 42.116 | 6.31 | 1.457 | 5.3 | 8965.31 | 2.282 | 98.1 | 78.4 | 1426 | 21.06 | 5827.5 | 3251.8 | 3235.8 | 4689.2 | 1207.7 | 0.67742 | 6.756
2024-12-09 | 21:27 | Data | 0 | 31.346 | 28.808 | 221.594 | 7.62 | 207.778 | 2194.5 | 25.89 | 41.936 | 6.31 | 1.458 | 5.311 | 8960.79 | 2.417 | 98.1 | 78.4 | 1426 | 20.97 | 5824.5 | 3243.4 | 3203.3 | 4661.1 | 1207.7 | 0.67942 | 6.772
2024-12-09 | 21:27 | Data | 0 | 31.339 | 28.808 | 221.504 | 7.62 | 207.687 | 2194.5 | 25.88 | 42.206 | 6.32 | 1.45 | 5.325 | 8960.79 | 2.532 | 98.1 | 78.6 | 1426 | 21.1 | 5824.5 | 3254.6 | 3183.9 | 4653.6 | 1207.7 | 0.68198 | 6.775
2024-12-09 | 21:28 | Data | 0 | 31.15 | 28.72 | 221.639 | 7.62 | 207.823 | 2096.89 | 25.89 | 42.116 | 6.31 | 1.446 | 5.308 | 8969.84 | 2.424 | 98 | 78.6 | 1363 | 21.06 | 5830.4 | 3268.6 | 3205.7 | 4676.9 | 1207.7 | 0.68311 | 6.753
2024-12-09 | 21:28 | Data | 0 | 31.225 | 28.781 | 221.277 | 7.62 | 207.687 | 2206.25 | 25.88 | 42.116 | 6.31 | 1.452 | 5.31 | 8965.31 | 2.39 | 98.1 | 78.6 | 1434 | 21.06 | 5827.5 | 3268.8 | 3184.8 | 4664.7 | 1207.7 | 0.68524 | 6.76
2024-12-09 | 21:28 | Data | 0 | 31.184 | 28.585 | 221.594 | 7.62 | 207.778 | 2199.02 | 25.88 | 42.116 | 6.31 | 1.453 | 5.328 | 8978.88 | 2.511 | 98.1 | 78.6 | 1429 | 21.06 | 5836.3 | 3263 | 3187 | 4658.9 | 1207.7 | 0.68492 | 6.782
2024-12-09 | 21:28 | Data | 0 | 31.474 | 28.571 | 221.504 | 7.62 | 207.687 | 2201.74 | 25.89 | 42.116 | 6.32 | 1.448 | 5.3 | 8978.88 | 2.383 | 98.1 | 78.5 | 1432 | 21.06 | 5836.3 | 3265.6 | 3196.3 | 4670.8 | 1207.7 | 0.68319 | 6.751
2024-12-09 | 21:28 | Data | 0 | 31.123 | 28.97 | 221.639 | 7.62 | 207.823 | 2201.74 | 25.88 | 42.116 | 6.31 | 1.458 | 5.307 | 8987.93 | 2.518 | 98.1 | 78.5 | 1432 | 21.01 | 5842.2 | 3278.6 | 3170.3 | 4658.1 | 1207.7 | 0.68531 | 6.764
2024-12-09 | 21:28 | Data | 0 | 31.4 | 29.031 | 221.368 | 7.62 | 207.733 | 2199.93 | 25.88 | 42.116 | 6.31 | 1.447 | 5.307 | 8983.4 | 2.478 | 98.1 | 78.6 | 1431 | 21.06 | 5839.2 | 3250.7 | 3176.5 | 4645.6 | 1207.7 | 0.68138 | 6.754
2024-12-09 | 21:28 | Data | 0 | 31.015 | 28.625 | 221.323 | 7.62 | 207.642 | 2198.12 | 25.88 | 42.116 | 6.31 | 1.445 | 5.317 | 8987.93 | 2.484 | 98.1 | 78.6 | 1428 | 21.01 | 5842.2 | 3258.7 | 3202.4 | 4669.2 | 1207.7 | 0.68122 | 6.762
2024-12-09 | 21:28 | Data | 0 | 31.508 | 29.044 | 221.639 | 7.62 | 207.733 | 2194.5 | 25.88 | 42.116 | 6.3 | 1.445 | 5.329 | 8983.4 | 2.572 | 98.1 | 78.7 | 1426 | 21.06 | 5839.2 | 3253 | 3203.4 | 4665.6 | 1207.7 | 0.68068 | 6.775
2024-12-09 | 21:28 | Data | 0 | 31.225 | 28.828 | 221.368 | 7.62 | 207.733 | 2198.12 | 25.88 | 42.477 | 6.31 | 1.448 | 5.322 | 9001.49 | 2.417 | 98.1 | 78.6 | 1428 | 21.15 | 5851 | 3265.7 | 3228.2 | 4692 | 1207.7 | 0.68031 | 6.769
2024-12-09 | 21:28 | Data | 0 | 31.164 | 28.571 | 221.458 | 7.62 | 207.733 | 2196.31 | 25.85 | 42.477 | 6.32 | 1.446 | 5.297 | 8969.84 | 2.565 | 98.1 | 78.5 | 1427 | 21.24 | 5830.4 | 3247 | 3209.9 | 4667.6 | 1207.7 | 0.67919 | 6.742
2024-12-09 | 21:28 | Data | 0 | 31.427 | 29.031 | 221.684 | 7.62 | 207.823 | 2197.22 | 25.89 | 42.387 | 6.32 | 1.446 | 5.3 | 8933.66 | 2.525 | 98.1 | 78.6 | 1428 | 21.15 | 5806.9 | 3254.7 | 3204 | 4667.6 | 1207.7 | 0.68105 | 6.746
2024-12-09 | 21:28 | Data | 0 | 31.61 | 28.916 | 221.594 | 7.62 | 207.778 | 2194.5 | 25.89 | 42.297 | 6.32 | 1.459 | 5.279 | 8933.66 | 2.721 | 98.1 | 78.3 | 1426 | 21.19 | 5806.9 | 3248.2 | 3208.2 | 4668 | 1207.7 | 0.67963 | 6.737
2024-12-09 | 21:28 | Data | 0 | 31.218 | 28.801 | 221.458 | 7.62 | 207.733 | 2194.5 | 25.89 | 42.387 | 6.31 | 1.452 | 5.286 | 8938.18 | 2.505 | 98.1 | 78.5 | 1426 | 21.19 | 5809.8 | 3254.3 | 3194.8 | 4659.1 | 1207.7 | 0.68098 | 6.737
2024-12-09 | 21:28 | Data | 0 | 31.117 | 28.571 | 221.458 | 7.62 | 207.642 | 2193.6 | 25.88 | 42.297 | 6.31 | 1.452 | 5.309 | 8960.79 | 2.538 | 98.1 | 78.5 | 1426 | 21.24 | 5824.5 | 3251.8 | 3182 | 4663.8 | 1207.7 | 0.68264 | 6.76
2024-12-09 | 21:28 | Data | 0 | 31.441 | 28.889 | 221.549 | 7.62 | 207.733 | 2196.31 | 25.88 | 42.387 | 6.31 | 1.459 | 5.283 | 8983.4 | 2.565 | 98.1 | 78.4 | 1428 | 21.19 | 5839.2 | 3241.4 | 3172.5 | 4638.1 | 1207.7 | 0.68266 | 6.741
2024-12-09 | 21:28 | Data | 0 | 30.955 | 28.571 | 221.549 | 7.62 | 207.823 | 2194.5 | 25.88 | 42.477 | 6.31 | 1.445 | 5.311 | 8956.27 | 2.322 | 98.1 | 78.6 | 1426 | 21.24 | 5821.6 | 3258 | 3194.4 | 4661 | 1207.7 | 0.68354 | 6.757
2024-12-09 | 21:28 | Data | 0 | 31.225 | 28.862 | 221.549 | 7.62 | 207.642 | 2187.27 | 25.88 | 42.387 | 6.32 | 1.454 | 5.302 | 8965.31 | 2.714 | 98.1 | 78.5 | 1422 | 21.19 | 5827.5 | 3249.3 | 3198.7 | 4659.2 | 1207.7 | 0.68191 | 6.757
2024-12-09 | 21:28 | Data | 0 | 31.117 | 28.571 | 221.368 | 7.62 | 207.733 | 2192.7 | 25.89 | 42.477 | 6.31 | 1.453 | 5.297 | 8978.88 | 2.532 | 98.1 | 78.5 | 1425 | 21.24 | 5836.3 | 3260.6 | 3181.4 | 4654.3 | 1207.7 | 0.68314 | 6.749
2024-12-09 | 21:29 | Data | 0 | 31.393 | 28.808 | 221.323 | 7.62 | 207.733 | 2192.7 | 25.89 | 42.387 | 6.32 | 1.449 | 5.289 | 8992.45 | 2.559 | 98.1 | 78.5 | 1425 | 21.19 | 5845.1 | 3272.4 | 3227.5 | 4697.2 | 1207.7 | 0.67962 | 6.737
2024-12-09 | 21:29 | Data | 0 | 31.339 | 28.808 | 221.504 | 7.62 | 207.778 | 2190.89 | 25.89 | 42.387 | 6.32 | 1.44 | 5.266 | 9006.01 | 2.532 | 98.1 | 78.5 | 1425 | 21.24 | 5853.9 | 3253.3 | 3213.6 | 4677.1 | 1207.7 | 0.67903 | 6.706
2024-12-09 | 21:29 | Data | 0 | 31.333 | 28.808 | 221.549 | 7.62 | 207.642 | 2191.79 | 25.89 | 42.387 | 6.32 | 1.454 | 5.297 | 8978.88 | 2.532 | 98.1 | 78.4 | 1425 | 21.15 | 5836.3 | 3276.7 | 3222.6 | 4694.4 | 1207.7 | 0.68164 | 6.752
2024-12-09 | 21:29 | Data | 0 | 31.11 | 28.571 | 221.504 | 7.62 | 207.733 | 2189.08 | 25.86 | 42.387 | 6.31 | 1.452 | 5.303 | 8992.45 | 2.532 | 98.1 | 78.5 | 1423 | 21.19 | 5845.1 | 3262 | 3209.8 | 4675.3 | 1207.7 | 0.68218 | 6.757
2024-12-09 | 21:29 | Data | 0 | 31.042 | 28.693 | 221.639 | 7.62 | 207.687 | 2186.37 | 25.88 | 42.387 | 6.31 | 1.454 | 5.279 | 8933.66 | 2.343 | 98.1 | 78.4 | 1421 | 21.19 | 5806.9 | 3261.6 | 3203.9 | 4670.7 | 1207.7 | 0.68228 | 6.734
2024-12-09 | 21:29 | Data | 0 | 31.542 | 28.862 | 221.73 | 7.62 | 207.868 | 2187.27 | 25.86 | 42.477 | 6.31 | 1.459 | 5.307 | 8951.75 | 2.532 | 98.1 | 78.4 | 1421 | 21.19 | 5818.6 | 3247 | 3213.1 | 4670.1 | 1207.7 | 0.67891 | 6.765
2024-12-09 | 21:29 | Data | 0 | 31.117 | 28.571 | 221.458 | 7.62 | 207.597 | 2186.37 | 25.89 | 42.387 | 6.31 | 1.454 | 5.295 | 8956.27 | 2.545 | 98.1 | 78.5 | 1421 | 21.19 | 5821.6 | 3261.2 | 3210.2 | 4677.3 | 1207.7 | 0.68187 | 6.75
2024-12-09 | 21:29 | Data | 0 | 31.441 | 28.949 | 221.73 | 7.62 | 207.913 | 2189.08 | 25.89 | 42.297 | 6.31 | 1.46 | 5.304 | 8956.27 | 2.68 | 98.1 | 78.4 | 1423 | 21.15 | 5821.6 | 3255.3 | 3185.8 | 4656.1 | 1207.7 | 0.68248 | 6.763
2024-12-09 | 21:29 | Data | 0 | 31.117 | 28.679 | 221.368 | 7.62 | 207.687 | 2191.79 | 25.89 | 42.387 | 6.31 | 1.448 | 5.302 | 8956.27 | 2.451 | 98.1 | 78.5 | 1425 | 21.19 | 5821.6 | 3257.6 | 3175.6 | 4648.8 | 1207.7 | 0.68548 | 6.748
2024-12-09 | 21:29 | Data | 0 | 31.4 | 28.7 | 221.639 | 7.62 | 207.913 | 2195.41 | 25.86 | 41.845 | 6.31 | 1.455 | 5.273 | 8978.88 | 2.525 | 98.1 | 78.4 | 1426 | 20.92 | 5836.3 | 3252.9 | 3165.8 | 4636 | 1207.8 | 0.68612 | 6.727
2024-12-09 | 21:29 | Data | 0 | 31.117 | 28.571 | 221.504 | 7.62 | 207.733 | 2195.41 | 25.88 | 42.387 | 6.31 | 1.444 | 5.285 | 8965.31 | 2.653 | 98.1 | 78.5 | 1427 | 21.19 | 5827.5 | 3262.1 | 3180 | 4654.7 | 1207.8 | 0.68294 | 6.729
2024-12-09 | 21:29 | Data | 0 | 31.164 | 28.571 | 221.368 | 7.62 | 207.642 | 2193.6 | 25.89 | 42.387 | 6.31 | 1.448 | 5.296 | 8951.75 | 2.545 | 98.1 | 78.5 | 1426 | 21.24 | 5818.6 | 3250.8 | 3185.2 | 4654.5 | 1207.8 | 0.68481 | 6.744
2024-12-09 | 21:29 | Data | 0 | 31.258 | 28.639 | 221.549 | 7.62 | 207.778 | 2194.5 | 25.88 | 42.297 | 6.31 | 1.451 | 5.325 | 8951.75 | 2.478 | 98.1 | 78.6 | 1426 | 21.15 | 5818.6 | 3237.5 | 3200.9 | 4655.5 | 1207.8 | 0.6802 | 6.776
2024-12-09 | 21:29 | Data | 0 | 31.427 | 29.024 | 221.594 | 7.62 | 207.778 | 2192.7 | 25.88 | 42.297 | 6.31 | 1.45 | 5.312 | 8960.79 | 2.167 | 98.1 | 78.6 | 1425 | 21.19 | 5824.5 | 3251.3 | 3191 | 4656.9 | 1207.8 | 0.68176 | 6.762
2024-12-09 | 21:29 | Data | 0 | 31.454 | 28.808 | 221.865 | 7.62 | 207.823 | 2190.89 | 25.89 | 42.387 | 6.31 | 1.447 | 5.293 | 8965.31 | 2.538 | 98.1 | 78.5 | 1424 | 21.24 | 5827.5 | 3259.6 | 3174.6 | 4647.1 | 1207.8 | 0.6857 | 6.742
2024-12-09 | 21:29 | Data | 0 | 31.272 | 28.693 | 221.368 | 7.62 | 207.778 | 2194.5 | 25.88 | 42.387 | 6.31 | 1.444 | 5.299 | 8965.31 | 2.329 | 98.1 | 78.6 | 1426 | 21.15 | 5827.5 | 3253.7 | 3187.2 | 4654.9 | 1207.8 | 0.68344 | 6.746
2024-12-09 | 21:29 | Data | 0 | 31.164 | 28.571 | 221.458 | 7.62 | 207.597 | 2193.6 | 25.88 | 42.477 | 6.31 | 1.453 | 5.299 | 9033.15 | 2.545 | 98.1 | 78.5 | 1426 | 21.19 | 5871.5 | 3257.9 | 3202 | 4670.4 | 1207.8 | 0.68167 | 6.753
2024-12-09 | 21:30 | Data | 0 | 31.225 | 28.808 | 221.504 | 7.62 | 207.733 | 2189.08 | 25.89 | 42.297 | 6.31 | 1.454 | 5.315 | 9485.37 | 2.444 | 98.1 | 78.5 | 1423 | 21.1 | 6165.5 | 3250.6 | 3218.4 | 4673.2 | 1207.8 | 0.67948 | 6.77
2024-12-09 | 21:30 | Data | 0 | 31.562 | 28.949 | 221.594 | 7.62 | 207.687 | 2196.31 | 25.86 | 42.387 | 6.31 | 1.445 | 5.289 | 9001.49 | 2.552 | 98.1 | 78.5 | 1428 | 21.15 | 5851 | 3244.1 | 3194.6 | 4654.2 | 1207.8 | 0.68051 | 6.735
2024-12-09 | 21:30 | Data | 0 | 31.144 | 28.578 | 221.82 | 7.62 | 207.868 | 2189.08 | 25.89 | 42.477 | 6.31 | 1.452 | 5.278 | 9019.58 | 2.538 | 98.1 | 78.4 | 1423 | 21.15 | 5862.7 | 3248.6 | 3184.3 | 4651.3 | 1207.8 | 0.68203 | 6.73
2024-12-09 | 21:30 | Data | 0 | 31.765 | 29.044 | 221.684 | 7.62 | 207.823 | 2194.5 | 25.88 | 42.387 | 6.32 | 1.452 | 5.294 | 8585.45 | 2.552 | 98.1 | 78.5 | 1426 | 21.19 | 5580.5 | 3253.5 | 3195.9 | 4662.8 | 1207.8 | 0.68254 | 6.747
2024-12-09 | 21:30 | Data | 0 | 31.117 | 28.571 | 221.549 | 7.62 | 207.733 | 2193.6 | 25.89 | 42.387 | 6.32 | 1.44 | 5.3 | 8978.88 | 2.538 | 98.1 | 78.6 | 1427 | 21.19 | 5836.3 | 3257.3 | 3197.9 | 4665.9 | 1207.8 | 0.68241 | 6.744
2024-12-09 | 21:30 | Data | 0 | 31.339 | 28.673 | 221.504 | 7.62 | 207.642 | 2195.41 | 25.88 | 42.477 | 6.32 | 1.447 | 5.298 | 8983.4 | 2.586 | 98.1 | 78.6 | 1426 | 21.24 | 5839.2 | 3242.5 | 3191.4 | 4654.2 | 1207.8 | 0.68007 | 6.746
2024-12-09 | 21:30 | Data | 0 | 31.718 | 28.619 | 221.639 | 7.62 | 207.823 | 2197.22 | 25.89 | 42.387 | 6.31 | 1.453 | 5.288 | 8933.66 | 2.734 | 98.1 | 78.4 | 1428 | 21.19 | 5806.9 | 3262.4 | 3205.3 | 4676 | 1207.8 | 0.68135 | 6.742
2024-12-09 | 21:30 | Data | 0 | 30.961 | 28.376 | 221.368 | 7.62 | 207.733 | 2199.93 | 25.89 | 42.387 | 6.31 | 1.454 | 5.302 | 8938.18 | 2.484 | 98.1 | 78.5 | 1430 | 21.15 | 5809.8 | 3257.4 | 3187.7 | 4660.2 | 1207.8 | 0.68216 | 6.756
2024-12-09 | 21:30 | Data | 0 | 31.164 | 28.808 | 221.549 | 7.62 | 207.733 | 2201.74 | 25.89 | 42.297 | 6.32 | 1.445 | 5.303 | 8978.88 | 2.329 | 98.1 | 78.6 | 1431 | 21.19 | 5836.3 | 3247.1 | 3162.4 | 4632.1 | 1207.8 | 0.68513 | 6.749
2024-12-09 | 21:30 | Data | 0 | 31.11 | 28.571 | 221.458 | 7.62 | 207.687 | 2203.54 | 25.86 | 42.477 | 6.31 | 1.457 | 5.283 | 8978.88 | 2.538 | 98.1 | 78.4 | 1432 | 21.19 | 5836.3 | 3241.1 | 3183.7 | 4645 | 1207.8 | 0.68235 | 6.74
2024-12-09 | 21:30 | Data | 0 | 31.11 | 28.801 | 221.323 | 7.62 | 207.642 | 2201.74 | 25.88 | 42.387 | 6.31 | 1.463 | 5.295 | 8965.31 | 2.505 | 98.1 | 78.4 | 1432 | 21.24 | 5827.5 | 3254.2 | 3167.9 | 4640.6 | 1207.8 | 0.68564 | 6.757
2024-12-09 | 21:30 | Data | 0 | 31.123 | 29.031 | 221.639 | 7.62 | 207.778 | 2199.02 | 25.88 | 42.387 | 6.31 | 1.457 | 5.32 | 8992.45 | 2.41 | 98.1 | 78.5 | 1430 | 21.15 | 5845.1 | 3276.8 | 3152.6 | 4644.3 | 1207.8 | 0.68927 | 6.777
2024-12-09 | 21:30 | Data | 0 | 30.961 | 28.571 | 221.594 | 7.62 | 207.733 | 2199.93 | 25.89 | 42.387 | 6.31 | 1.441 | 5.278 | 8996.97 | 2.322 | 98.1 | 78.6 | 1430 | 21.19 | 5848 | 3250.5 | 3171 | 4643.6 | 1207.8 | 0.68439 | 6.719
2024-12-09 | 21:30 | Data | 0 | 31.123 | 28.571 | 221.639 | 7.62 | 207.687 | 2195.41 | 25.88 | 42.477 | 6.31 | 1.441 | 5.297 | 8992.45 | 2.37 | 98.1 | 78.6 | 1428 | 21.28 | 5845.1 | 3254.4 | 3168.7 | 4644.9 | 1207.8 | 0.68579 | 6.736
2024-12-09 | 21:30 | Data | 0 | 31.339 | 28.781 | 221.504 | 7.62 | 207.597 | 2199.93 | 25.88 | 42.297 | 6.32 | 1.446 | 5.276 | 8983.4 | 2.647 | 98.1 | 78.5 | 1429 | 21.15 | 5839.2 | 3258.6 | 3151.3 | 4634.9 | 1207.8 | 0.68709 | 6.722
2024-12-09 | 21:30 | Data | 0 | 31.427 | 28.916 | 221.775 | 7.62 | 207.733 | 2198.12 | 25.86 | 42.387 | 6.32 | 1.453 | 5.289 | 9006.01 | 2.633 | 98.1 | 78.4 | 1429 | 21.19 | 5853.9 | 3257.6 | 3144.4 | 4631.5 | 1207.8 | 0.68827 | 6.742
2024-12-09 | 21:30 | Data | 0 | 31.252 | 28.808 | 221.594 | 7.62 | 207.913 | 2203.54 | 25.89 | 42.387 | 6.31 | 1.464 | 5.299 | 9033.15 | 2.633 | 98.1 | 78.4 | 1432 | 21.19 | 5871.5 | 3230.7 | 3146.9 | 4614.1 | 1207.8 | 0.68475 | 6.764
2024-12-09 | 21:30 | Data | 0 | 31.454 | 28.646 | 221.368 | 7.62 | 207.778 | 2201.74 | 25.88 | 42.297 | 6.31 | 1.458 | 5.297 | 9033.15 | 2.626 | 98.1 | 78.4 | 1431 | 21.15 | 5871.5 | 3259.8 | 3155.3 | 4642.5 | 1207.8 | 0.68664 | 6.753
2024-12-09 | 21:31 | Data | 0 | 31.569 | 28.598 | 221.639 | 7.62 | 207.823 | 2201.74 | 25.88 | 42.477 | 6.31 | 1.457 | 5.295 | 9019.58 | 2.68 | 98.1 | 78.4 | 1431 | 21.24 | 5862.7 | 3248.9 | 3155.8 | 4636 | 1207.8 | 0.68456 | 6.753
2024-12-09 | 21:31 | Data | 0 | 31.123 | 28.808 | 221.594 | 7.62 | 207.823 | 2206.25 | 25.88 | 42.297 | 6.31 | 1.462 | 5.286 | 9033.15 | 2.424 | 98.1 | 78.3 | 1434 | 21.19 | 5871.5 | 3244.1 | 3164.1 | 4634 | 1207.8 | 0.68454 | 6.746
2024-12-09 | 21:31 | Data | 0 | 31.339 | 28.578 | 221.549 | 7.62 | 207.868 | 2203.54 | 25.88 | 42.297 | 6.31 | 1.458 | 5.279 | 8992.45 | 2.741 | 98.1 | 78.4 | 1432 | 21.19 | 5845.1 | 3260.4 | 3174.4 | 4650.2 | 1207.8 | 0.68546 | 6.736
2024-12-09 | 21:31 | Data | 0 | 31.515 | 28.821 | 221.504 | 7.62 | 207.687 | 2199.02 | 25.89 | 42.387 | 6.31 | 1.446 | 5.284 | 8978.88 | 2.701 | 98.1 | 78.5 | 1430 | 21.19 | 5836.3 | 3251.1 | 3161.4 | 4637 | 1207.8 | 0.68481 | 6.729
2024-12-09 | 21:31 | Data | 0 | 31.029 | 28.754 | 221.594 | 7.63 | 207.778 | 2203.54 | 25.86 | 42.387 | 6.31 | 1.454 | 5.298 | 8956.27 | 2.633 | 98.1 | 78.5 | 1432 | 21.15 | 5821.6 | 3261.9 | 3163.5 | 4645.6 | 1207.8 | 0.68551 | 6.753
2024-12-09 | 21:31 | Data | 0 | 31.427 | 28.828 | 221.504 | 7.62 | 207.868 | 2201.74 | 25.88 | 42.387 | 6.3 | 1.452 | 5.301 | 8978.88 | 2.802 | 98.1 | 78.5 | 1431 | 21.19 | 5836.3 | 3256.8 | 3161.4 | 4639.9 | 1207.8 | 0.68619 | 6.755
2024-12-09 | 21:31 | Data | 0 | 31.623 | 28.632 | 221.684 | 7.62 | 207.913 | 2205.35 | 25.89 | 42.297 | 6.32 | 1.461 | 5.298 | 8965.31 | 2.579 | 98.1 | 78.4 | 1433 | 21.1 | 5827.5 | 3234.5 | 3164.5 | 4631 | 1207.8 | 0.68429 | 6.76
2024-12-09 | 21:31 | Data | 0 | 31.339 | 28.808 | 221.504 | 7.62 | 207.778 | 2206.25 | 25.88 | 42.387 | 6.31 | 1.455 | 5.286 | 8956.27 | 2.532 | 98.1 | 78.4 | 1433 | 21.19 | 5821.6 | 3251.5 | 3156 | 4641.6 | 1207.9 | 0.68538 | 6.741
2024-12-09 | 21:31 | Data | 0 | 31.285 | 28.801 | 221.594 | 7.62 | 207.687 | 2208.97 | 25.88 | 42.477 | 6.31 | 1.452 | 5.298 | 8965.31 | 2.532 | 98.1 | 78.5 | 1435 | 21.19 | 5827.5 | 3251.3 | 3178.4 | 4647.3 | 1207.9 | 0.68338 | 6.749
2024-12-09 | 21:31 | Data | 0 | 31.353 | 29.01 | 221.684 | 7.62 | 207.733 | 2208.97 | 25.86 | 42.387 | 6.31 | 1.443 | 5.307 | 8978.88 | 2.538 | 98.1 | 78.6 | 1436 | 21.19 | 5836.3 | 3264 | 3187.7 | 4664.1 | 1207.9 | 0.68401 | 6.75
2024-12-09 | 21:31 | Data | 0 | 31.481 | 29.226 | 221.73 | 7.63 | 207.823 | 2207.16 | 25.88 | 42.477 | 6.31 | 1.447 | 5.276 | 8978.88 | 2.532 | 98.1 | 78.5 | 1435 | 21.19 | 5836.3 | 3278.3 | 3196.1 | 4678.4 | 1207.9 | 0.68496 | 6.724
2024-12-09 | 21:31 | Data | 0 | 31.535 | 28.821 | 221.684 | 7.62 | 207.823 | 2211.68 | 25.88 | 42.297 | 6.31 | 1.458 | 5.297 | 8978.88 | 2.613 | 98.1 | 78.4 | 1438 | 21.15 | 5836.3 | 3265.1 | 3206.1 | 4674 | 1207.9 | 0.68126 | 6.754
2024-12-09 | 21:31 | Data | 0 | 31.225 | 28.909 | 221.504 | 7.62 | 207.642 | 2208.97 | 25.88 | 42.387 | 6.31 | 1.451 | 5.302 | 8987.93 | 2.532 | 98.1 | 78.5 | 1436 | 21.24 | 5842.2 | 3263.1 | 3183.1 | 4659.2 | 1207.9 | 0.68428 | 6.753
2024-12-09 | 21:31 | Data | 0 | 31.616 | 28.578 | 221.549 | 7.62 | 207.823 | 2210.77 | 25.89 | 42.297 | 6.32 | 1.462 | 5.3 | 8974.36 | 2.599 | 98.1 | 78.4 | 1437 | 21.15 | 5833.3 | 3259.6 | 3206.1 | 4672.1 | 1207.9 | 0.68168 | 6.763
2024-12-09 | 21:31 | Data | 0 | 31.562 | 29.152 | 221.504 | 7.62 | 207.778 | 2216.2 | 25.88 | 42.477 | 6.32 | 1.464 | 5.311 | 8920.09 | 2.538 | 98.1 | 78.4 | 1441 | 21.19 | 5798.1 | 3248.7 | 3183.7 | 4650.7 | 1207.9 | 0.68556 | 6.774
2024-12-09 | 21:31 | Data | 0 | 31.225 | 28.801 | 221.368 | 7.62 | 207.733 | 2210.77 | 25.88 | 42.387 | 6.31 | 1.46 | 5.312 | 8929.14 | 2.356 | 98.1 | 78.4 | 1438 | 21.24 | 5803.9 | 3253.1 | 3199.5 | 4665.9 | 1207.9 | 0.68167 | 6.772
2024-12-09 | 21:31 | Data | 0 | 31.339 | 28.754 | 221.458 | 7.62 | 207.687 | 2210.77 | 25.88 | 42.477 | 6.31 | 1.453 | 5.299 | 8938.18 | 2.741 | 98.1 | 78.5 | 1437 | 21.24 | 5809.8 | 3252.2 | 3171.3 | 4644.7 | 1207.9 | 0.68364 | 6.752
2024-12-09 | 21:32 | Data | 0 | 31.447 | 29.193 | 221.594 | 7.62 | 207.823 | 2210.77 | 25.88 | 42.387 | 6.31 | 1.449 | 5.311 | 8929.14 | 2.606 | 98.1 | 78.6 | 1437 | 21.19 | 5803.9 | 3262.6 | 3168.6 | 4649.4 | 1207.9 | 0.68538 | 6.76
2024-12-09 | 21:32 | Data | 0 | 31.441 | 29.145 | 221.639 | 7.62 | 207.868 | 2208.06 | 25.88 | 42.206 | 6.32 | 1.453 | 5.307 | 8965.31 | 2.701 | 98.1 | 78.5 | 1435 | 21.19 | 5827.5 | 3264.1 | 3177.4 | 4657.2 | 1207.9 | 0.68526 | 6.76
2024-12-09 | 21:32 | Data | 0 | 31.454 | 28.814 | 221.639 | 7.62 | 207.778 | 2208.97 | 25.88 | 42.477 | 6.32 | 1.451 | 5.29 | 8965.31 | 2.606 | 98.1 | 78.5 | 1436 | 21.19 | 5827.5 | 3258.4 | 3162.4 | 4643.3 | 1207.9 | 0.68611 | 6.742
2024-12-09 | 21:32 | Data | 0 | 31.805 | 28.727 | 221.549 | 7.62 | 207.823 | 2208.97 | 25.88 | 42.387 | 6.31 | 1.449 | 5.286 | 8965.31 | 2.552 | 98.1 | 78.5 | 1435 | 21.19 | 5827.5 | 3241.8 | 3176.9 | 4643.4 | 1207.9 | 0.68016 | 6.735
2024-12-09 | 21:32 | Data | 0 | 31.339 | 29.031 | 221.458 | 7.62 | 207.823 | 2208.97 | 25.88 | 42.477 | 6.31 | 1.452 | 5.312 | 8965.31 | 2.329 | 98.1 | 78.5 | 1436 | 21.19 | 5827.5 | 3249.5 | 3161.5 | 4639.9 | 1207.9 | 0.68593 | 6.762
2024-12-09 | 21:32 | Data | 0 | 31.508 | 28.828 | 221.639 | 7.62 | 207.733 | 2205.35 | 25.85 | 42.477 | 6.31 | 1.446 | 5.311 | 8992.45 | 2.545 | 98.1 | 78.6 | 1433 | 21.19 | 5845.1 | 3263.2 | 3182.6 | 4662.8 | 1207.9 | 0.6839 | 6.757
2024-12-09 | 21:32 | Data | 0 | 31.231 | 28.977 | 221.775 | 7.62 | 207.778 | 2206.25 | 25.88 | 42.477 | 6.31 | 1.459 | 5.288 | 8992.45 | 2.525 | 98.1 | 78.4 | 1434 | 21.19 | 5845.1 | 3257.3 | 3181.1 | 4652.9 | 1207.9 | 0.68509 | 6.746
2024-12-09 | 21:32 | Data | 0 | 31.569 | 29.233 | 221.684 | 7.62 | 207.913 | 2208.06 | 25.88 | 42.116 | 6.31 | 1.442 | 5.297 | 8992.45 | 2.478 | 98.1 | 78.6 | 1435 | 21.06 | 5845.1 | 3233.2 | 3175.4 | 4636.5 | 1207.9 | 0.68127 | 6.738
2024-12-09 | 21:32 | Data | 0 | 31.015 | 28.7 | 221.458 | 7.62 | 207.687 | 2208.06 | 25.89 | 42.116 | 6.31 | 1.447 | 5.298 | 9006.01 | 2.68 | 98.1 | 78.5 | 1435 | 21.06 | 5853.9 | 3262.4 | 3187.4 | 4659.8 | 1207.9 | 0.68432 | 6.745
2024-12-09 | 21:32 | Data | 0 | 31.42 | 28.814 | 221.549 | 7.62 | 207.868 | 2206.25 | 25.88 | 42.026 | 6.31 | 1.453 | 5.277 | 8951.75 | 2.532 | 98.1 | 78.4 | 1433 | 21.06 | 5818.6 | 3270.7 | 3166.6 | 4655.1 | 1207.9 | 0.68667 | 6.729
2024-12-09 | 21:32 | Data | 0 | 31.569 | 28.983 | 221.639 | 7.62 | 207.823 | 2205.35 | 25.89 | 42.116 | 6.31 | 1.455 | 5.279 | 8951.75 | 2.586 | 98.1 | 78.4 | 1434 | 21.1 | 5818.6 | 3258.2 | 3169.7 | 4647 | 1207.9 | 0.68526 | 6.736
2024-12-09 | 21:32 | Data | 0 | 31.596 | 29.058 | 221.639 | 7.62 | 207.868 | 2206.25 | 25.89 | 42.116 | 6.31 | 1.454 | 5.278 | 8956.27 | 2.714 | 98.1 | 78.4 | 1434 | 21.06 | 5821.6 | 3256.2 | 3185.6 | 4643.2 | 1207.9 | 0.68271 | 6.732
2024-12-09 | 21:32 | Data | 0 | 31.711 | 28.646 | 221.504 | 7.62 | 207.823 | 2204.45 | 25.88 | 42.116 | 6.31 | 1.449 | 5.302 | 8951.75 | 2.572 | 98.1 | 78.5 | 1432 | 21.1 | 5818.6 | 3254.3 | 3179.3 | 4650.8 | 1207.9 | 0.6835 | 6.75
2024-12-09 | 21:32 | Data | 0 | 31.366 | 28.922 | 221.594 | 7.62 | 207.778 | 2203.54 | 25.88 | 42.116 | 6.31 | 1.455 | 5.277 | 8965.31 | 2.417 | 98.1 | 78.4 | 1432 | 21.1 | 5827.5 | 3245.5 | 3167.1 | 4637.1 | 1207.9 | 0.68403 | 6.732
2024-12-09 | 21:32 | Data | 0 | 31.218 | 28.578 | 221.594 | 7.62 | 207.823 | 2206.25 | 25.89 | 42.116 | 6.31 | 1.457 | 5.287 | 8978.88 | 2.923 | 98.1 | 78.4 | 1434 | 21.06 | 5836.3 | 3251.8 | 3185.5 | 4650.7 | 1207.9 | 0.68409 | 6.743
2024-12-09 | 21:32 | Data | 0 | 31.339 | 29.031 | 221.549 | 7.62 | 207.778 | 2205.35 | 25.88 | 42.116 | 6.31 | 1.443 | 5.308 | 8960.79 | 2.701 | 98.1 | 78.6 | 1433 | 21.06 | 5824.5 | 3275.8 | 3192.1 | 4665.3 | 1207.9 | 0.68415 | 6.751
2024-12-09 | 21:32 | Data | 0 | 31.231 | 28.983 | 221.504 | 7.62 | 207.687 | 2205.35 | 25.89 | 42.116 | 6.31 | 1.45 | 5.295 | 8978.88 | 2.478 | 98.1 | 78.5 | 1434 | 21.06 | 5836.3 | 3229 | 3179.9 | 4634.8 | 1207.9 | 0.68018 | 6.746
2024-12-09 | 21:32 | Data | 0 | 31.468 | 29.044 | 221.368 | 7.62 | 207.823 | 2204.45 | 25.88 | 42.297 | 6.31 | 1.445 | 5.282 | 8992.45 | 2.701 | 98.1 | 78.5 | 1432 | 21.1 | 5845.1 | 3276.1 | 3196.5 | 4678.3 | 1207.9 | 0.68465 | 6.726
2024-12-09 | 21:32 | Data | 0 | 31.346 | 28.895 | 221.504 | 7.62 | 207.823 | 2206.25 | 25.88 | 42.116 | 6.31 | 1.447 | 5.294 | 8978.88 | 2.444 | 98.1 | 78.5 | 1434 | 21.06 | 5836.3 | 3273.7 | 3205.6 | 4679.6 | 1207.9 | 0.68426 | 6.742
2024-12-09 | 21:33 | Data | 0 | 31.468 | 29.064 | 221.639 | 7.62 | 207.868 | 2210.77 | 25.85 | 42.116 | 6.32 | 1.454 | 5.306 | 8974.36 | 2.66 | 98.1 | 78.5 | 1437 | 21.06 | 5833.3 | 3247.9 | 3164.9 | 4636.6 | 1207.9 | 0.68338 | 6.76
2024-12-09 | 21:33 | Data | 0 | 31.461 | 29.024 | 221.684 | 7.62 | 207.823 | 2200.83 | 25.88 | 42.116 | 6.31 | 1.461 | 5.282 | 8965.31 | 2.532 | 98.1 | 78.3 | 1431 | 21.06 | 5827.5 | 3246.5 | 3199.2 | 4659.3 | 1207.9 | 0.68173 | 6.742
2024-12-09 | 21:33 | Data | 0 | 31.339 | 28.808 | 221.549 | 7.62 | 207.733 | 2205.35 | 25.89 | 42.026 | 6.3 | 1.453 | 5.311 | 8983.4 | 2.532 | 98.1 | 78.5 | 1433 | 21.01 | 5839.2 | 3251 | 3184.5 | 4652.9 | 1207.9 | 0.68289 | 6.765
2024-12-09 | 21:33 | Data | 0 | 31.225 | 28.585 | 221.549 | 7.62 | 207.733 | 2099.6 | 25.88 | 42.116 | 6.31 | 1.457 | 5.323 | 8965.31 | 2.538 | 98 | 78.5 | 1364 | 21.06 | 5827.5 | 3253.6 | 3194.4 | 4657 | 1208 | 0.68264 | 6.78
2024-12-09 | 21:33 | Data | 0 | 31.225 | 28.693 | 221.549 | 7.63 | 207.778 | 2208.97 | 25.89 | 42.206 | 6.32 | 1.444 | 5.315 | 8969.84 | 2.714 | 98.1 | 78.6 | 1435 | 21.1 | 5830.4 | 3247.8 | 3177.4 | 4645.7 | 1208 | 0.68252 | 6.759
2024-12-09 | 21:33 | Data | 0 | 31.312 | 28.909 | 221.594 | 7.62 | 207.733 | 2208.97 | 25.88 | 42.116 | 6.31 | 1.452 | 5.277 | 8965.31 | 2.498 | 98.1 | 78.4 | 1436 | 21.01 | 5827.5 | 3259.5 | 3199.6 | 4666.2 | 1208 | 0.6827 | 6.729
2024-12-09 | 21:33 | Data | 0 | 31.225 | 28.585 | 221.639 | 7.62 | 207.733 | 2208.06 | 25.89 | 42.116 | 6.31 | 1.46 | 5.297 | 8974.36 | 2.728 | 98.1 | 78.4 | 1435 | 21.06 | 5833.3 | 3252.5 | 3169 | 4641.4 | 1208 | 0.68431 | 6.756
2024-12-09 | 21:33 | Data | 0 | 31.204 | 29.017 | 221.684 | 7.62 | 207.823 | 2208.06 | 25.88 | 42.026 | 6.31 | 1.461 | 5.295 | 8965.31 | 2.491 | 98.1 | 78.4 | 1435 | 21.01 | 5827.5 | 3260.5 | 3156.5 | 4640.2 | 1208 | 0.6867 | 6.757
2024-12-09 | 21:33 | Data | 0 | 31.353 | 28.808 | 221.639 | 7.62 | 207.778 | 2208.97 | 25.88 | 42.026 | 6.31 | 1.445 | 5.293 | 8965.31 | 2.363 | 98.1 | 78.6 | 1435 | 21.06 | 5827.5 | 3255.7 | 3179.1 | 4648.8 | 1208 | 0.68496 | 6.738
2024-12-09 | 21:33 | Data | 0 | 31.339 | 28.794 | 221.639 | 7.62 | 207.778 | 2208.06 | 25.88 | 42.297 | 6.3 | 1.444 | 5.283 | 8983.4 | 2.559 | 98.1 | 78.5 | 1435 | 21.19 | 5839.2 | 3249.3 | 3159.9 | 4635.6 | 1208 | 0.6848 | 6.727
2024-12-09 | 21:33 | Data | 0 | 31.238 | 28.814 | 221.504 | 7.62 | 207.733 | 2208.06 | 25.88 | 42.387 | 6.31 | 1.446 | 5.3 | 9006.01 | 2.356 | 98.1 | 78.6 | 1436 | 21.19 | 5853.9 | 3260 | 3168.9 | 4649.5 | 1208 | 0.68555 | 6.746
2024-12-09 | 21:33 | Data | 0 | 31.583 | 28.666 | 221.684 | 7.62 | 207.778 | 2208.06 | 25.86 | 42.477 | 6.31 | 1.442 | 5.293 | 9010.54 | 2.64 | 98.1 | 78.6 | 1435 | 21.24 | 5856.8 | 3242 | 3174.1 | 4638.7 | 1208 | 0.68299 | 6.735
2024-12-09 | 21:33 | Data | 0 | 31.36 | 28.632 | 221.911 | 7.62 | 207.778 | 2210.77 | 25.88 | 42.387 | 6.31 | 1.453 | 5.302 | 9001.49 | 2.565 | 98.1 | 78.4 | 1438 | 21.15 | 5851 | 3240.1 | 3164.6 | 4631.3 | 1208 | 0.68262 | 6.758
2024-12-09 | 21:33 | Data | 0 | 31.117 | 28.673 | 221.504 | 7.62 | 207.778 | 2211.68 | 25.88 | 42.387 | 6.31 | 1.455 | 5.325 | 9006.01 | 2.329 | 98.1 | 78.5 | 1438 | 21.15 | 5853.9 | 3267.2 | 3192.4 | 4669.2 | 1208 | 0.68341 | 6.779
2024-12-09 | 21:33 | Data | 0 | 31.515 | 28.814 | 221.368 | 7.62 | 207.778 | 2101.41 | 25.89 | 42.387 | 6.31 | 1.449 | 5.332 | 9019.58 | 2.707 | 98 | 78.6 | 1366 | 21.15 | 5862.7 | 3270.3 | 3163.1 | 4648.7 | 1208 | 0.688 | 6.779
2024-12-09 | 21:34 | Data | 0 | 31.819 | 29.085 | 221.684 | 7.62 | 207.913 | 2188.18 | 25.89 | 42.297 | 6.31 | 1.453 | 5.311 | 9015.06 | 2.397 | 98.1 | 78.5 | 1422 | 21.19 | 5859.8 | 3247.5 | 3171.4 | 4639.9 | 1208 | 0.6841 | 6.765
2024-12-09 | 21:34 | Data | 0 | 31.549 | 29.024 | 221.594 | 7.62 | 207.733 | 2189.08 | 25.88 | 42.387 | 6.31 | 1.453 | 5.295 | 9051.24 | 2.545 | 98.1 | 78.5 | 1423 | 21.19 | 5883.3 | 3255.1 | 3167.8 | 4643.5 | 1208 | 0.68506 | 6.748
2024-12-09 | 21:34 | Data | 0 | 30.961 | 28.544 | 221.504 | 7.62 | 207.733 | 2189.99 | 25.89 | 42.477 | 6.31 | 1.45 | 5.313 | 9024.1 | 2.538 | 98.1 | 78.6 | 1423 | 21.1 | 5865.7 | 3249.7 | 3157.8 | 4631.9 | 1208 | 0.68551 | 6.762
2024-12-09 | 21:34 | Data | 0 | 31.225 | 28.808 | 221.504 | 7.62 | 207.778 | 2192.7 | 25.88 | 42.297 | 6.31 | 1.451 | 5.304 | 9037.67 | 2.694 | 98.1 | 78.5 | 1425 | 21.19 | 5874.5 | 3258.2 | 3176.6 | 4648.7 | 1208 | 0.68585 | 6.755
2024-12-09 | 21:34 | Data | 0 | 31.515 | 29.402 | 221.639 | 7.62 | 207.913 | 2208.06 | 25.89 | 42.387 | 6.31 | 1.454 | 5.317 | 9042.19 | 2.572 | 98.1 | 78.5 | 1435 | 21.24 | 5877.4 | 3257.8 | 3197.6 | 4667.2 | 1208 | 0.68123 | 6.771
2024-12-09 | 21:34 | Data | 0 | 31.481 | 28.828 | 221.639 | 7.62 | 207.868 | 2211.68 | 25.88 | 42.387 | 6.31 | 1.453 | 5.315 | 9037.67 | 2.356 | 98.1 | 78.5 | 1437 | 21.24 | 5874.5 | 3277.3 | 3170.7 | 4661.3 | 1208 | 0.68739 | 6.768
2024-12-09 | 21:34 | Data | 0 | 30.975 | 28.781 | 221.684 | 7.62 | 207.778 | 2211.68 | 25.88 | 42.387 | 6.31 | 1.451 | 5.279 | 9019.58 | 2.262 | 98.1 | 78.4 | 1436 | 21.19 | 5862.7 | 3272.2 | 3172.3 | 4659.2 | 1208 | 0.68521 | 6.728
2024-12-09 | 21:34 | Data | 0 | 31.447 | 28.632 | 221.549 | 7.62 | 207.778 | 2208.97 | 25.88 | 42.387 | 6.32 | 1.459 | 5.285 | 9019.58 | 2.653 | 98.1 | 78.4 | 1436 | 21.19 | 5862.7 | 3258.7 | 3194.4 | 4663.9 | 1208 | 0.68264 | 6.744
2024-12-09 | 21:34 | Data | 0 | 31.333 | 28.781 | 221.594 | 7.62 | 207.733 | 2210.77 | 25.89 | 42.297 | 6.31 | 1.452 | 5.301 | 9024.1 | 2.586 | 98.1 | 78.5 | 1438 | 21.15 | 5865.7 | 3230.1 | 3180.5 | 4636.3 | 1208 | 0.68167 | 6.754
2024-12-09 | 21:34 | Data | 0 | 31.231 | 29.247 | 221.684 | 7.62 | 207.778 | 2210.77 | 25.89 | 42.297 | 6.31 | 1.45 | 5.309 | 8978.88 | 2.457 | 98.1 | 78.6 | 1437 | 21.19 | 5836.3 | 3252.6 | 3169.7 | 4639.9 | 1208 | 0.68461 | 6.76
2024-12-09 | 21:34 | Data | 0 | 31.704 | 28.875 | 221.639 | 7.62 | 207.778 | 2210.77 | 25.89 | 42.477 | 6.31 | 1.452 | 5.278 | 9399.45 | 2.707 | 98.1 | 78.4 | 1437 | 21.24 | 6109.6 | 3249.9 | 3163.4 | 4637.5 | 1208 | 0.6852 | 6.728
2024-12-09 | 21:34 | Data | 0 | 31.339 | 28.598 | 221.594 | 7.62 | 207.823 | 2210.77 | 25.88 | 42.116 | 6.31 | 1.453 | 5.289 | 9033.15 | 2.653 | 98.1 | 78.4 | 1437 | 21.06 | 5871.5 | 3253.8 | 3187.2 | 4655.2 | 1208 | 0.68391 | 6.742
2024-12-09 | 21:34 | Data | 0 | 31.339 | 28.632 | 221.368 | 7.62 | 207.642 | 2210.77 | 25.88 | 42.387 | 6.31 | 1.455 | 5.262 | 8969.84 | 2.532 | 98.1 | 78.3 | 1437 | 21.19 | 5830.4 | 3254.5 | 3181.3 | 4650.6 | 1208 | 0.68354 | 6.718
2024-12-09 | 21:34 | Data | 0 | 31.907 | 29.267 | 221.956 | 7.62 | 208.004 | 2209.87 | 25.88 | 42.297 | 6.31 | 1.462 | 5.293 | 8987.93 | 2.444 | 98.1 | 78.4 | 1436 | 21.15 | 5842.2 | 3267.7 | 3153.8 | 4643.4 | 1208 | 0.68782 | 6.755
2024-12-09 | 21:34 | Data | 0 | 31.339 | 28.794 | 221.368 | 7.62 | 207.778 | 2206.25 | 25.89 | 42.387 | 6.31 | 1.454 | 5.322 | 9006.01 | 2.417 | 98.1 | 78.5 | 1435 | 21.15 | 5853.9 | 3245.6 | 3181.3 | 4653.5 | 1208 | 0.68115 | 6.776
2024-12-09 | 21:34 | Data | 0 | 31.535 | 28.814 | 221.639 | 7.62 | 207.868 | 2208.06 | 25.89 | 42.206 | 6.31 | 1.454 | 5.302 | 8983.4 | 2.376 | 98.1 | 78.5 | 1435 | 21.06 | 5839.2 | 3273.1 | 3197.2 | 4675.2 | 1208 | 0.68474 | 6.758
2024-12-09 | 21:34 | Data | 0 | 31.11 | 28.808 | 221.549 | 7.62 | 207.823 | 2208.97 | 25.88 | 42.026 | 6.31 | 1.458 | 5.279 | 8983.4 | 2.478 | 98.1 | 78.3 | 1436 | 20.97 | 5839.2 | 3239 | 3192.1 | 4649.4 | 1208 | 0.67983 | 6.738
2024-12-09 | 21:35 | Data | 0 | 31.623 | 29.199 | 221.684 | 7.62 | 207.778 | 2208.97 | 25.88 | 42.116 | 6.31 | 1.457 | 5.289 | 8978.88 | 2.64 | 98.1 | 78.4 | 1436 | 21.06 | 5836.3 | 3258.8 | 3163.2 | 4647.1 | 1208 | 0.68508 | 6.746
2024-12-09 | 21:35 | Data | 0 | 31.596 | 28.821 | 221.594 | 7.62 | 207.868 | 2208.97 | 25.86 | 42.206 | 6.31 | 1.455 | 5.276 | 8965.31 | 2.707 | 98.1 | 78.4 | 1435 | 21.1 | 5827.5 | 3251.3 | 3166.6 | 4630.2 | 1208.1 | 0.68324 | 6.732
2024-12-09 | 21:35 | Data | 0 | 31.643 | 28.943 | 221.639 | 7.62 | 207.913 | 2208.06 | 25.89 | 42.206 | 6.31 | 1.454 | 5.303 | 8956.27 | 2.525 | 98.1 | 78.5 | 1435 | 21.1 | 5821.6 | 3264 | 3165.9 | 4641.8 | 1208.1 | 0.6875 | 6.758
2024-12-09 | 21:35 | Data | 0 | 31.339 | 28.977 | 221.549 | 7.62 | 207.733 | 2208.97 | 25.88 | 42.116 | 6.31 | 1.452 | 5.28 | 8938.18 | 2.532 | 98.1 | 78.4 | 1436 | 21.06 | 5809.8 | 3268.9 | 3171.2 | 4653.1 | 1208.1 | 0.68642 | 6.732
2024-12-09 | 21:35 | Data | 0 | 31.272 | 28.801 | 221.458 | 7.62 | 207.687 | 2203.54 | 25.89 | 42.116 | 6.31 | 1.452 | 5.279 | 8960.79 | 2.755 | 98.1 | 78.4 | 1431 | 21.06 | 5824.5 | 3241.8 | 3159.7 | 4627.7 | 1208.1 | 0.68514 | 6.732
2024-12-09 | 21:35 | Data | 0 | 31.508 | 28.808 | 221.775 | 7.62 | 207.868 | 2208.97 | 25.89 | 42.116 | 6.31 | 1.446 | 5.287 | 8938.18 | 2.329 | 98.1 | 78.5 | 1435 | 21.06 | 5809.8 | 3235.4 | 3184.4 | 4628 | 1208.1 | 0.68271 | 6.733
2024-12-09 | 21:35 | Data | 0 | 31.339 | 28.686 | 221.594 | 7.62 | 207.823 | 2208.06 | 25.88 | 42.206 | 6.31 | 1.446 | 5.286 | 8951.75 | 2.538 | 98.1 | 78.5 | 1435 | 21.06 | 5818.6 | 3266.7 | 3175 | 4654.1 | 1208.1 | 0.68602 | 6.734
2024-12-09 | 21:35 | Data | 0 | 31.447 | 28.612 | 221.549 | 7.62 | 207.868 | 2205.35 | 25.88 | 42.206 | 6.31 | 1.45 | 5.276 | 8951.75 | 2.653 | 98.1 | 78.4 | 1434 | 21.1 | 5818.6 | 3252.6 | 3168.5 | 4641.3 | 1208.1 | 0.6844 | 6.726
2024-12-09 | 21:35 | Data | 0 | 31.927 | 28.841 | 221.684 | 7.62 | 207.913 | 2206.25 | 25.89 | 42.026 | 6.31 | 1.448 | 5.273 | 8956.27 | 2.647 | 98.1 | 78.5 | 1434 | 21.06 | 5821.6 | 3245.8 | 3163.1 | 4636 | 1208.1 | 0.68536 | 6.722
2024-12-09 | 21:35 | Data | 0 | 31.447 | 28.949 | 221.549 | 7.62 | 207.733 | 2205.35 | 25.89 | 42.116 | 6.31 | 1.455 | 5.319 | 8924.61 | 2.592 | 98.1 | 78.5 | 1434 | 21.1 | 5801 | 3253.8 | 3171.1 | 4645.4 | 1208.1 | 0.68374 | 6.774
2024-12-09 | 21:35 | Data | 0 | 31.238 | 28.754 | 221.549 | 7.62 | 207.868 | 2206.25 | 25.89 | 42.116 | 6.32 | 1.457 | 5.284 | 8924.61 | 2.538 | 98.1 | 78.4 | 1434 | 21.06 | 5801 | 3258.8 | 3185.2 | 4659.7 | 1208.1 | 0.68257 | 6.742
2024-12-09 | 21:35 | Data | 0 | 31.623 | 28.612 | 221.549 | 7.62 | 207.868 | 2205.35 | 25.88 | 42.116 | 6.31 | 1.462 | 5.254 | 8933.66 | 2.647 | 98.1 | 78.2 | 1434 | 21.1 | 5806.9 | 3250.3 | 3184.1 | 4647.4 | 1208.1 | 0.6815 | 6.715
2024-12-09 | 21:35 | Data | 0 | 31.225 | 28.808 | 221.639 | 7.62 | 207.778 | 2199.93 | 25.88 | 42.116 | 6.31 | 1.464 | 5.289 | 8924.61 | 2.505 | 98.1 | 78.3 | 1431 | 21.06 | 5801 | 3251.5 | 3181.1 | 4651 | 1208.1 | 0.68237 | 6.753
2024-12-09 | 21:35 | Data | 0 | 31.988 | 28.949 | 221.865 | 7.62 | 207.913 | 2200.83 | 25.86 | 42.116 | 6.31 | 1.453 | 5.329 | 8947.23 | 2.586 | 98.1 | 78.6 | 1431 | 21.06 | 5815.7 | 3282.2 | 3208.7 | 4688.4 | 1208.1 | 0.68393 | 6.782
2024-12-09 | 21:35 | Data | 0 | 31.339 | 29.085 | 221.639 | 7.62 | 207.778 | 2199.02 | 25.89 | 42.116 | 6.32 | 1.443 | 5.309 | 8969.84 | 2.552 | 98.1 | 78.6 | 1429 | 21.06 | 5830.4 | 3241.7 | 3187.3 | 4649.9 | 1208.1 | 0.68105 | 6.753
2024-12-09 | 21:35 | Data | 0 | 31.792 | 28.625 | 221.73 | 7.62 | 207.868 | 2199.93 | 25.89 | 42.116 | 6.31 | 1.443 | 5.293 | 8978.88 | 2.647 | 98.1 | 78.6 | 1430 | 21.06 | 5836.3 | 3238.9 | 3196.2 | 4654.4 | 1208.1 | 0.68094 | 6.736
2024-12-09 | 21:35 | Data | 0 | 31.562 | 29.01 | 221.594 | 7.62 | 207.823 | 2199.93 | 25.88 | 42.116 | 6.31 | 1.457 | 5.314 | 8965.31 | 2.586 | 98.1 | 78.5 | 1431 | 21.06 | 5827.5 | 3245.7 | 3185.8 | 4648.8 | 1208.1 | 0.68138 | 6.772
2024-12-09 | 21:36 | Data | 0 | 31.333 | 29.078 | 221.639 | 7.62 | 207.868 | 2204.45 | 25.88 | 42.116 | 6.31 | 1.447 | 5.315 | 8965.31 | 2.383 | 98.1 | 78.6 | 1433 | 21.1 | 5827.5 | 3248.6 | 3199.5 | 4659.4 | 1208.1 | 0.68163 | 6.764
2024-12-09 | 21:36 | Data | 0 | 31.339 | 28.585 | 221.549 | 7.62 | 207.778 | 2206.25 | 25.88 | 42.297 | 6.31 | 1.446 | 5.299 | 8535.7 | 2.647 | 98.1 | 78.6 | 1434 | 21.24 | 5548.2 | 3253.8 | 3220 | 4680.1 | 1208.1 | 0.67919 | 6.745
2024-12-09 | 21:36 | Data | 0 | 31.407 | 28.808 | 221.639 | 7.62 | 207.823 | 2204.45 | 25.89 | 42.116 | 6.31 | 1.462 | 5.303 | 8987.93 | 2.336 | 98.1 | 78.4 | 1434 | 21.06 | 5842.2 | 3255.5 | 3248.5 | 4698.1 | 1208.1 | 0.67597 | 6.765
2024-12-09 | 21:36 | Data | 0 | 31.339 | 28.922 | 221.684 | 7.62 | 207.687 | 2206.25 | 25.89 | 42.297 | 6.31 | 1.452 | 5.309 | 8974.36 | 2.532 | 98.1 | 78.5 | 1433 | 21.19 | 5833.3 | 3255.3 | 3240.5 | 4692.4 | 1208.1 | 0.67765 | 6.761
2024-12-09 | 21:36 | Data | 0 | 31.225 | 28.936 | 221.73 | 7.62 | 207.868 | 2204.45 | 25.86 | 42.387 | 6.31 | 1.457 | 5.289 | 9010.54 | 2.856 | 98.1 | 78.4 | 1433 | 21.19 | 5856.8 | 3250.2 | 3229.2 | 4682.1 | 1208.1 | 0.67792 | 6.745
2024-12-09 | 21:36 | Data | 0 | 31.664 | 28.841 | 221.504 | 7.62 | 207.868 | 2206.25 | 25.89 | 42.387 | 6.31 | 1.442 | 5.298 | 9019.58 | 2.667 | 98.1 | 78.6 | 1434 | 21.19 | 5862.7 | 3257 | 3212.4 | 4663.7 | 1208.1 | 0.67997 | 6.74
2024-12-09 | 21:36 | Data | 0 | 31.339 | 29.01 | 222.363 | 7.62 | 208.501 | 2205.35 | 25.88 | 42.387 | 6.31 | 1.443 | 5.299 | 9019.58 | 2.532 | 98.1 | 78.6 | 1433 | 21.19 | 5862.7 | 3264 | 3213 | 4680.6 | 1208.1 | 0.68123 | 6.743
2024-12-09 | 21:36 | Data | 0 | 31.569 | 28.794 | 225.665 | 7.62 | 211.303 | 2206.25 | 25.88 | 42.387 | 6.3 | 1.446 | 5.327 | 9503.46 | 2.755 | 98.1 | 78.7 | 1434 | 21.19 | 6177.2 | 3303.8 | 3256.1 | 4739.1 | 1208.1 | 0.68157 | 6.774
2024-12-09 | 21:36 | Data | 0 | 30.907 | 28.342 | 228.243 | 7.62 | 213.834 | 2210.77 | 25.89 | 42.297 | 6.31 | 1.46 | 5.374 | 8956.27 | 2.545 | 98.1 | 78.6 | 1437 | 21.24 | 5821.6 | 3326.1 | 3278.2 | 4770.9 | 1208.1 | 0.68136 | 6.834
2024-12-09 | 21:36 | Data | 0 | 31.117 | 28.436 | 230.55 | 7.62 | 215.958 | 2203.54 | 25.88 | 42.477 | 6.31 | 1.468 | 5.457 | 9431.1 | 2.809 | 98.1 | 78.8 | 1431 | 21.19 | 6130.2 | 3349.2 | 3276.3 | 4779.8 | 1208.1 | 0.68539 | 6.926
2024-12-09 | 21:36 | Data | 0 | 30.853 | 28.025 | 232.178 | 7.62 | 217.54 | 2208.06 | 25.88 | 42.477 | 6.31 | 1.482 | 5.453 | 8965.31 | 2.768 | 98.1 | 78.6 | 1436 | 21.28 | 5827.5 | 3379.8 | 3295.8 | 4821 | 1208.1 | 0.68513 | 6.935
2024-12-09 | 21:36 | Data | 0 | 31.211 | 28.335 | 233.988 | 7.62 | 219.031 | 2208.06 | 25.86 | 42.206 | 6.31 | 1.483 | 5.507 | 8978.88 | 2.944 | 98.1 | 78.8 | 1435 | 21.1 | 5836.3 | 3382.9 | 3318.7 | 4835.9 | 1208.1 | 0.68441 | 6.99
2024-12-09 | 21:36 | Data | 0 | 30.658 | 27.998 | 234.802 | 7.62 | 219.754 | 2208.06 | 25.86 | 41.845 | 6.3 | 1.494 | 5.55 | 8992.45 | 2.768 | 98.1 | 78.8 | 1435 | 20.97 | 5845.1 | 3402.5 | 3327.1 | 4857 | 1208.1 | 0.68588 | 7.044
2024-12-09 | 21:36 | Data | 0 | 30.934 | 27.89 | 234.757 | 7.62 | 219.845 | 2208.06 | 25.88 | 41.575 | 6.3 | 1.492 | 5.59 | 8996.97 | 2.788 | 98.1 | 78.9 | 1435 | 20.79 | 5848 | 3415 | 3294.8 | 4843 | 1208.1 | 0.69014 | 7.083
2024-12-09 | 21:36 | Data | 0 | 30.948 | 27.903 | 234.847 | 7.62 | 219.98 | 2208.97 | 25.88 | 41.575 | 6.3 | 1.493 | 5.563 | 9019.58 | 2.829 | 98.1 | 78.8 | 1435 | 20.79 | 5862.7 | 3418.8 | 3393.6 | 4910.3 | 1208.1 | 0.68038 | 7.056
2024-12-09 | 21:36 | Data | 0 | 30.57 | 27.883 | 234.666 | 7.62 | 219.799 | 2208.06 | 25.86 | 41.213 | 6.3 | 1.487 | 5.555 | 9042.19 | 2.538 | 98.1 | 78.9 | 1435 | 20.56 | 5877.4 | 3406.1 | 3401.6 | 4911.5 | 1208.1 | 0.67694 | 7.042
2024-12-09 | 21:36 | Data | 0 | 30.772 | 28.328 | 234.892 | 7.62 | 219.89 | 2208.06 | 25.86 | 41.304 | 6.29 | 1.485 | 5.553 | 9060.28 | 2.545 | 98.1 | 78.9 | 1436 | 20.65 | 5889.2 | 3411.9 | 3373.8 | 4892.7 | 1208.2 | 0.68196 | 7.037
2024-12-09 | 21:36 | Data | 0 | 31.265 | 28.153 | 234.847 | 7.62 | 219.89 | 2208.06 | 25.86 | 41.304 | 6.3 | 1.492 | 5.574 | 9064.8 | 2.937 | 98.1 | 78.9 | 1436 | 20.61 | 5892.1 | 3416.4 | 3356 | 4880.3 | 1208.2 | 0.68438 | 7.067
2024-12-09 | 21:37 | Data | 0 | 30.725 | 28.2 | 234.802 | 7.62 | 219.845 | 2208.97 | 25.84 | 41.033 | 6.3 | 1.485 | 5.588 | 9073.85 | 2.599 | 98.1 | 79 | 1436 | 20.47 | 5898 | 3414.8 | 3375.7 | 4896.1 | 1208.2 | 0.68034 | 7.075
2024-12-09 | 21:37 | Data | 0 | 30.678 | 28.112 | 234.847 | 7.62 | 219.89 | 2208.97 | 25.85 | 41.033 | 6.3 | 1.488 | 5.573 | 9087.41 | 2.653 | 98.1 | 78.9 | 1436 | 20.52 | 5906.8 | 3419.7 | 3367 | 4891.9 | 1208.2 | 0.68375 | 7.061
2024-12-09 | 21:37 | Data | 0 | 30.874 | 28.112 | 234.847 | 7.62 | 219.845 | 2208.06 | 25.86 | 40.943 | 6.3 | 1.49 | 5.557 | 9078.37 | 2.768 | 98.1 | 78.9 | 1435 | 20.47 | 5900.9 | 3405.7 | 3350.1 | 4871.1 | 1208.2 | 0.68455 | 7.047
2024-12-09 | 21:37 | Data | 0 | 30.658 | 28.281 | 234.711 | 7.62 | 219.89 | 2208.06 | 25.86 | 40.943 | 6.29 | 1.492 | 5.562 | 9073.85 | 2.741 | 98.1 | 78.8 | 1435 | 20.47 | 5898 | 3436.1 | 3364.8 | 4903.6 | 1208.2 | 0.6861 | 7.054
2024-12-09 | 21:37 | Data | 0 | 30.867 | 28.058 | 234.666 | 7.62 | 219.754 | 2208.97 | 25.86 | 40.852 | 6.29 | 1.492 | 5.557 | 9064.8 | 2.984 | 98.1 | 78.8 | 1435 | 20.43 | 5892.1 | 3409.8 | 3356.2 | 4876 | 1208.2 | 0.6827 | 7.049
2024-12-09 | 21:37 | Data | 0 | 30.826 | 28.281 | 234.711 | 7.62 | 219.89 | 2203.54 | 25.86 | 40.943 | 6.29 | 1.497 | 5.553 | 9064.8 | 2.883 | 98.1 | 78.8 | 1433 | 20.47 | 5892.1 | 3410.8 | 3353.8 | 4879.4 | 1208.2 | 0.68465 | 7.049
2024-12-09 | 21:37 | Data | 0 | 30.583 | 27.883 | 234.847 | 7.62 | 219.799 | 2208.97 | 25.84 | 41.033 | 6.29 | 1.483 | 5.556 | 9069.33 | 2.552 | 98.1 | 78.9 | 1436 | 20.47 | 5895.1 | 3400 | 3355.3 | 4876.1 | 1208.2 | 0.68179 | 7.039
2024-12-09 | 21:37 | Data | 0 | 30.651 | 27.883 | 234.666 | 7.62 | 219.799 | 2206.25 | 25.84 | 41.033 | 6.3 | 1.491 | 5.545 | 9046.71 | 2.768 | 98.1 | 78.8 | 1434 | 20.52 | 5880.4 | 3411.1 | 3352.4 | 4879.6 | 1208.2 | 0.68318 | 7.034
2024-12-09 | 21:37 | Data | 0 | 31.211 | 27.971 | 234.802 | 7.62 | 219.89 | 2205.35 | 25.85 | 40.943 | 6.29 | 1.487 | 5.54 | 9064.8 | 2.937 | 98.1 | 78.8 | 1434 | 20.52 | 5892.1 | 3410.5 | 3327.7 | 4858.9 | 1208.2 | 0.68604 | 7.027
2024-12-09 | 21:37 | Data | 0 | 31.15 | 27.809 | 235.616 | 7.62 | 220.703 | 2206.25 | 25.86 | 40.943 | 6.29 | 1.481 | 5.545 | 9073.85 | 2.998 | 98.1 | 78.9 | 1434 | 20.52 | 5898 | 3399.6 | 3328.4 | 4854 | 1208.2 | 0.68526 | 7.025
2024-12-09 | 21:37 | Data | 0 | 30.88 | 28.281 | 235.661 | 7.62 | 220.658 | 2207.16 | 25.86 | 40.943 | 6.29 | 1.494 | 5.553 | 9073.85 | 2.782 | 98.1 | 78.8 | 1435 | 20.52 | 5898 | 3420.2 | 3352.7 | 4880.5 | 1208.2 | 0.6861 | 7.049
2024-12-09 | 21:37 | Data | 0 | 31.076 | 27.829 | 235.752 | 7.62 | 220.613 | 2207.16 | 25.86 | 41.033 | 6.29 | 1.496 | 5.582 | 9100.98 | 2.809 | 98.1 | 78.9 | 1435 | 20.52 | 5915.6 | 3424.4 | 3356.7 | 4887.9 | 1208.2 | 0.68655 | 7.077
2024-12-09 | 21:37 | Data | 0 | 30.651 | 27.883 | 235.616 | 7.62 | 220.613 | 2208.97 | 25.85 | 40.852 | 6.29 | 1.498 | 5.605 | 9096.46 | 2.775 | 98.1 | 78.9 | 1436 | 20.52 | 5912.7 | 3403.9 | 3351.1 | 4890.2 | 1208.2 | 0.68226 | 7.104
2024-12-09 | 21:37 | Data | 0 | 31.083 | 28.139 | 235.616 | 7.62 | 220.703 | 2208.06 | 25.86 | 40.943 | 6.3 | 1.493 | 5.583 | 9110.03 | 2.822 | 98.1 | 78.9 | 1435 | 20.52 | 5921.5 | 3423 | 3367.5 | 4892.1 | 1208.2 | 0.68369 | 7.077
2024-12-09 | 21:37 | Data | 0 | 30.88 | 28.423 | 235.752 | 7.62 | 220.703 | 2210.77 | 25.85 | 41.033 | 6.29 | 1.488 | 5.578 | 9100.98 | 2.728 | 98.1 | 78.9 | 1437 | 20.52 | 5915.6 | 3421.1 | 3355.1 | 4880.9 | 1208.2 | 0.68663 | 7.067
2024-12-09 | 21:37 | Data | 0 | 31.015 | 28.106 | 235.571 | 7.62 | 220.703 | 2205.35 | 25.85 | 41.033 | 6.29 | 1.48 | 5.586 | 9123.59 | 2.957 | 98.1 | 79.1 | 1433 | 20.52 | 5930.3 | 3403.1 | 3348.2 | 4872.3 | 1208.2 | 0.68233 | 7.064
2024-12-09 | 21:37 | Data | 0 | 31.036 | 28.335 | 235.616 | 7.62 | 220.794 | 2206.25 | 25.86 | 40.943 | 6.29 | 1.488 | 5.6 | 9119.07 | 2.957 | 98.1 | 79 | 1434 | 20.52 | 5927.4 | 3412.6 | 3347.1 | 4873.9 | 1208.2 | 0.68567 | 7.088
2024-12-09 | 21:37 | Data | 0 | 30.968 | 28.322 | 235.661 | 7.62 | 220.613 | 2207.16 | 25.86 | 40.852 | 6.29 | 1.501 | 5.582 | 9119.07 | 2.768 | 98.1 | 78.8 | 1435 | 20.47 | 5927.4 | 3397.5 | 3338.1 | 4859.1 | 1208.2 | 0.68409 | 7.082
2024-12-09 | 21:38 | Data | 0 | 30.799 | 27.998 | 235.752 | 7.62 | 220.658 | 2205.35 | 25.88 | 41.033 | 6.28 | 1.509 | 5.595 | 9110.03 | 2.653 | 98.1 | 78.8 | 1433 | 20.52 | 5921.5 | 3426.8 | 3337.1 | 4880.5 | 1208.2 | 0.68707 | 7.104
2024-12-09 | 21:38 | Data | 0 | 31.036 | 28.126 | 235.707 | 7.62 | 220.703 | 2206.25 | 25.88 | 41.033 | 6.29 | 1.493 | 5.587 | 9146.2 | 2.937 | 98.1 | 78.9 | 1435 | 20.56 | 5945 | 3411.6 | 3336 | 4867.3 | 1208.2 | 0.68575 | 7.078
2024-12-09 | 21:38 | Data | 0 | 31.319 | 28.011 | 235.797 | 7.62 | 220.884 | 2208.97 | 25.85 | 41.033 | 6.29 | 1.497 | 5.575 | 8693.98 | 2.876 | 98.1 | 78.8 | 1436 | 20.52 | 5651.1 | 3420.1 | 3335.2 | 4871.2 | 1208.2 | 0.6868 | 7.072
2024-12-09 | 21:38 | Data | 0 | 30.867 | 27.896 | 235.661 | 7.62 | 220.839 | 2211.68 | 25.85 | 40.852 | 6.29 | 1.493 | 5.588 | 9119.07 | 2.923 | 98.1 | 78.9 | 1438 | 20.47 | 5927.4 | 3411 | 3353.7 | 4876.9 | 1208.2 | 0.68435 | 7.078
2024-12-09 | 21:38 | Data | 0 | 30.658 | 28.058 | 235.661 | 7.62 | 220.703 | 2210.77 | 25.86 | 40.852 | 6.3 | 1.496 | 5.604 | 9132.64 | 2.822 | 98.1 | 78.9 | 1437 | 20.47 | 5936.2 | 3413.1 | 3336.4 | 4866.5 | 1208.2 | 0.68388 | 7.1
2024-12-09 | 21:38 | Data | 0 | 30.921 | 27.89 | 235.661 | 7.62 | 220.703 | 2210.77 | 25.86 | 40.943 | 6.29 | 1.498 | 5.601 | 9110.03 | 3.004 | 98.1 | 78.9 | 1437 | 20.52 | 5921.5 | 3408.8 | 3337.3 | 4866.8 | 1208.2 | 0.68476 | 7.097
2024-12-09 | 21:38 | Data | 0 | 31.049 | 28.22 | 235.707 | 7.62 | 220.839 | 2210.77 | 25.86 | 41.033 | 6.29 | 1.485 | 5.555 | 9087.41 | 2.775 | 98.1 | 78.9 | 1438 | 20.47 | 5906.8 | 3416.4 | 3370.9 | 4897.1 | 1208.2 | 0.68286 | 7.041
2024-12-09 | 21:38 | Data | 0 | 30.914 | 28.524 | 235.797 | 7.62 | 220.974 | 2206.25 | 25.88 | 41.033 | 6.29 | 1.481 | 5.579 | 9087.41 | 2.511 | 98.1 | 79 | 1433 | 20.52 | 5906.8 | 3424.5 | 3368.4 | 4907.5 | 1208.2 | 0.68347 | 7.059
2024-12-09 | 21:38 | Data | 0 | 30.712 | 28.227 | 235.661 | 7.62 | 220.703 | 2211.68 | 25.85 | 40.943 | 6.29 | 1.491 | 5.584 | 9100.98 | 2.755 | 98.1 | 78.9 | 1438 | 20.52 | 5915.6 | 3415 | 3368.8 | 4885.4 | 1208.2 | 0.68165 | 7.076
2024-12-09 | 21:38 | Data | 0 | 30.88 | 27.89 | 235.661 | 7.62 | 220.658 | 2211.68 | 25.86 | 41.033 | 6.29 | 1.496 | 5.586 | 8662.33 | 2.802 | 98.1 | 78.9 | 1437 | 20.47 | 5630.5 | 3403.4 | 3357.3 | 4876 | 1208.2 | 0.68072 | 7.082
2024-12-09 | 21:38 | Data | 0 | 30.651 | 27.883 | 235.661 | 7.62 | 220.748 | 2210.77 | 25.88 | 40.943 | 6.29 | 1.493 | 5.599 | 9046.71 | 2.883 | 98.1 | 78.9 | 1437 | 20.52 | 5880.4 | 3410.1 | 3377.3 | 4891.8 | 1208.2 | 0.68176 | 7.091
2024-12-09 | 21:38 | Data | 0 | 30.928 | 27.809 | 235.797 | 7.62 | 220.794 | 2210.77 | 25.86 | 40.943 | 6.3 | 1.481 | 5.615 | 9046.71 | 2.876 | 98.1 | 79.1 | 1438 | 20.47 | 5880.4 | 3389.3 | 3341.3 | 4855.3 | 1208.3 | 0.68234 | 7.096
2024-12-09 | 21:38 | Data | 0 | 31.049 | 28.126 | 235.571 | 7.62 | 220.748 | 2210.77 | 25.86 | 40.943 | 6.29 | 1.489 | 5.58 | 9046.71 | 2.802 | 98.1 | 78.9 | 1437 | 20.47 | 5880.4 | 3405.2 | 3344.2 | 4874.3 | 1208.3 | 0.683 | 7.069
2024-12-09 | 21:38 | Data | 0 | 30.651 | 27.883 | 235.616 | 7.62 | 220.794 | 2208.97 | 25.86 | 40.943 | 6.28 | 1.49 | 5.547 | 9100.98 | 2.883 | 98.1 | 78.8 | 1436 | 20.47 | 5915.6 | 3412.7 | 3366.3 | 4887 | 1208.3 | 0.6835 | 7.039
2024-12-09 | 21:38 | Data | 0 | 30.482 | 27.883 | 235.661 | 7.62 | 220.658 | 2203.54 | 25.85 | 40.943 | 6.3 | 1.498 | 5.569 | 9155.25 | 2.552 | 98.1 | 78.8 | 1432 | 20.52 | 5950.9 | 3412.3 | 3365.2 | 4888.7 | 1208.3 | 0.68256 | 7.068
2024-12-09 | 21:38 | Data | 0 | 30.671 | 28.085 | 235.707 | 7.62 | 220.703 | 2203.54 | 25.86 | 41.033 | 6.29 | 1.491 | 5.569 | 9146.2 | 2.761 | 98.1 | 78.9 | 1432 | 20.47 | 5945 | 3426.2 | 3383.8 | 4911.4 | 1208.3 | 0.68274 | 7.062
2024-12-09 | 21:38 | Data | 0 | 30.853 | 28.106 | 235.707 | 7.62 | 220.748 | 2203.54 | 25.85 | 41.033 | 6.29 | 1.496 | 5.598 | 9137.16 | 2.944 | 98.1 | 78.9 | 1431 | 20.47 | 5939.2 | 3420.6 | 3420.6 | 4930.9 | 1208.3 | 0.67873 | 7.094
2024-12-09 | 21:38 | Data | 0 | 30.968 | 28.335 | 235.707 | 7.62 | 220.794 | 2203.54 | 25.86 | 41.033 | 6.29 | 1.501 | 5.587 | 9164.29 | 2.984 | 98.1 | 78.8 | 1432 | 20.52 | 5956.8 | 3408 | 3420.1 | 4923 | 1208.3 | 0.67724 | 7.088
2024-12-09 | 21:39 | Data | 0 | 30.826 | 28.47 | 235.752 | 7.62 | 220.703 | 2208.97 | 25.86 | 40.943 | 6.29 | 1.495 | 5.582 | 9168.81 | 2.572 | 98.1 | 78.9 | 1436 | 20.47 | 5959.7 | 3431.6 | 3435.7 | 4949.7 | 1208.3 | 0.67774 | 7.077
2024-12-09 | 21:39 | Data | 0 | 30.543 | 28.247 | 235.707 | 7.62 | 220.748 | 2206.25 | 25.85 | 41.033 | 6.29 | 1.499 | 5.562 | 9168.81 | 2.579 | 98.1 | 78.8 | 1434 | 20.52 | 5959.7 | 3451.5 | 3405.6 | 4943.3 | 1208.3 | 0.68314 | 7.06
2024-12-09 | 21:39 | Data | 0 | 31.076 | 27.944 | 235.752 | 7.62 | 220.839 | 2208.97 | 25.86 | 40.943 | 6.29 | 1.485 | 5.573 | 9164.29 | 2.768 | 98.1 | 78.9 | 1435 | 20.47 | 5956.8 | 3419.3 | 3404.4 | 4918.5 | 1208.3 | 0.68051 | 7.058
2024-12-09 | 21:39 | Data | 0 | 30.914 | 28.2 | 235.707 | 7.62 | 220.748 | 2206.25 | 25.86 | 40.943 | 6.29 | 1.497 | 5.615 | 9159.77 | 2.876 | 98.1 | 79 | 1434 | 20.52 | 5953.9 | 3420.7 | 3376.7 | 4901.7 | 1208.3 | 0.68287 | 7.112
2024-12-09 | 21:39 | Data | 0 | 30.658 | 28.058 | 235.526 | 7.62 | 220.703 | 2204.45 | 25.86 | 40.943 | 6.29 | 1.495 | 5.601 | 9155.25 | 2.822 | 98.1 | 78.9 | 1433 | 20.47 | 5950.9 | 3427.8 | 3359.4 | 4890.3 | 1208.3 | 0.68365 | 7.095
2024-12-09 | 21:39 | Data | 0 | 31.015 | 28.025 | 235.707 | 7.62 | 220.794 | 2201.74 | 25.86 | 40.852 | 6.29 | 1.494 | 5.557 | 9146.2 | 2.701 | 98.1 | 78.8 | 1431 | 20.52 | 5945 | 3419.6 | 3340.3 | 4873.9 | 1208.3 | 0.68662 | 7.051
2024-12-09 | 21:39 | Data | 0 | 30.604 | 27.883 | 235.616 | 7.62 | 220.658 | 2201.74 | 25.86 | 41.033 | 6.29 | 1.494 | 5.566 | 9159.77 | 2.883 | 98.1 | 78.8 | 1431 | 20.47 | 5953.9 | 3392.6 | 3365.8 | 4877.5 | 1208.3 | 0.6806 | 7.06
2024-12-09 | 21:39 | Data | 0 | 30.766 | 28.322 | 235.661 | 7.62 | 220.794 | 2203.54 | 25.86 | 40.943 | 6.29 | 1.494 | 5.592 | 9155.25 | 2.559 | 98.1 | 78.9 | 1431 | 20.52 | 5950.9 | 3439.4 | 3351.2 | 4898.5 | 1208.3 | 0.68692 | 7.086
2024-12-09 | 21:39 | Data | 0 | 31.076 | 28.281 | 235.707 | 7.61 | 220.748 | 2203.54 | 25.84 | 41.033 | 6.29 | 1.484 | 5.579 | 9173.34 | 2.876 | 98.1 | 79 | 1432 | 20.47 | 5962.7 | 3418.6 | 3369.5 | 4896.2 | 1208.3 | 0.68332 | 7.064
2024-12-09 | 21:39 | Data | 0 | 30.806 | 27.89 | 235.707 | 7.62 | 220.839 | 2203.54 | 25.85 | 40.762 | 6.29 | 1.496 | 5.577 | 9146.2 | 2.829 | 98.1 | 78.9 | 1431 | 20.38 | 5945 | 3410.9 | 3393.8 | 4909.6 | 1208.3 | 0.67916 | 7.074
2024-12-09 | 21:39 | Data | 0 | 30.577 | 27.782 | 235.661 | 7.62 | 220.703 | 2199.93 | 25.88 | 40.943 | 6.29 | 1.497 | 5.562 | 9173.34 | 2.795 | 98.1 | 78.8 | 1430 | 20.47 | 5962.7 | 3406.1 | 3410.7 | 4917.6 | 1208.3 | 0.67725 | 7.058
2024-12-09 | 21:39 | Data | 0 | 30.766 | 28.382 | 235.797 | 7.62 | 220.794 | 2199.93 | 25.86 | 41.033 | 6.29 | 1.48 | 5.586 | 9155.25 | 2.876 | 98.1 | 79.1 | 1429 | 20.52 | 5950.9 | 3402.8 | 3413.7 | 4915.7 | 1208.3 | 0.67671 | 7.066
2024-12-09 | 21:39 | Data | 0 | 30.799 | 27.944 | 235.707 | 7.62 | 220.794 | 2199.93 | 25.84 | 40.943 | 6.29 | 1.488 | 5.573 | 9159.77 | 2.572 | 98.1 | 78.9 | 1429 | 20.47 | 5953.9 | 3415.7 | 3401.5 | 4916.7 | 1208.3 | 0.67975 | 7.061
2024-12-09 | 21:39 | Data | 0 | 30.799 | 27.883 | 235.752 | 7.62 | 220.703 | 2199.02 | 25.86 | 41.033 | 6.29 | 1.486 | 5.554 | 9186.9 | 2.545 | 98.1 | 78.9 | 1430 | 20.52 | 5971.5 | 3429 | 3406.7 | 4926.8 | 1208.3 | 0.68097 | 7.039
2024-12-09 | 21:39 | Data | 0 | 30.826 | 28.004 | 235.707 | 7.62 | 220.658 | 2199.93 | 25.84 | 40.943 | 6.29 | 1.491 | 5.567 | 9186.9 | 3.085 | 98.1 | 78.9 | 1429 | 20.52 | 5971.5 | 3428.2 | 3380.8 | 4907.6 | 1208.3 | 0.68309 | 7.058
2024-12-09 | 21:39 | Data | 0 | 31.11 | 28.389 | 235.933 | 7.62 | 220.839 | 2199.93 | 25.86 | 41.033 | 6.29 | 1.495 | 5.565 | 9186.9 | 2.836 | 98.1 | 78.8 | 1429 | 20.52 | 5971.5 | 2319.9 | 2893.8 | 3724.7 | 1208.3 | 0.62232 | 7.06
2024-12-09 | 21:39 | Data | 0 | 31.373 | 28.038 | 235.887 | 7.62 | 220.839 | 2199.02 | 25.85 | 41.033 | 6.29 | 1.482 | 5.584 | 9159.77 | 3.018 | 98.1 | 79.1 | 1429 | 20.52 | 5953.9 | 2332.2 | 2849.4 | 3690 | 1208.3 | 0.62991 | 7.064
2024-12-09 | 21:40 | Data | 0 | 31.09 | 28.153 | 235.752 | 7.62 | 220.794 | 2204.45 | 25.86 | 40.943 | 6.29 | 1.493 | 5.584 | 9168.81 | 2.957 | 98.1 | 78.9 | 1432 | 20.43 | 5959.7 | 2331.4 | 2870.3 | 3706.8 | 1208.3 | 0.62694 | 7.078
2024-12-09 | 21:40 | Data | 0 | 30.88 | 28.268 | 235.797 | 7.61 | 220.748 | 2201.74 | 25.84 | 40.943 | 6.29 | 1.487 | 5.579 | 9168.81 | 2.68 | 98.1 | 79 | 1433 | 20.52 | 5959.7 | 2332.6 | 2857 | 3696.5 | 1208.3 | 0.62902 | 7.066
2024-12-09 | 21:40 | Data | 0 | 30.806 | 28.099 | 235.797 | 7.62 | 220.748 | 2201.74 | 25.84 | 41.123 | 6.29 | 1.49 | 5.578 | 9173.34 | 2.984 | 98.1 | 78.9 | 1431 | 20.47 | 5962.7 | 2324.5 | 2869.7 | 3701.3 | 1208.3 | 0.626 | 7.068
2024-12-09 | 21:40 | Data | 0 | 30.651 | 27.883 | 235.571 | 7.62 | 220.658 | 2200.83 | 25.83 | 40.852 | 6.29 | 1.494 | 5.576 | 9141.68 | 2.768 | 98.1 | 78.9 | 1431 | 20.52 | 5942.1 | 2332.8 | 2909.1 | 3737.3 | 1208.3 | 0.62225 | 7.071
2024-12-09 | 21:40 | Data | 0 | 31.164 | 27.809 | 235.887 | 7.62 | 220.703 | 2201.74 | 25.84 | 41.033 | 6.29 | 1.498 | 5.606 | 9132.64 | 2.971 | 98.1 | 78.9 | 1432 | 20.56 | 5936.2 | 2337.7 | 2922.6 | 3750.3 | 1208.3 | 0.62142 | 7.104
2024-12-09 | 21:40 | Data | 0 | 30.455 | 27.856 | 235.707 | 7.62 | 220.748 | 2203.54 | 25.84 | 40.943 | 6.29 | 1.492 | 5.619 | 9137.16 | 2.741 | 98.1 | 79 | 1431 | 20.47 | 5939.2 | 2335.7 | 2918 | 3744.9 | 1208.3 | 0.62187 | 7.111
2024-12-09 | 21:40 | Data | 0 | 31.049 | 28.22 | 235.842 | 7.62 | 220.794 | 2194.5 | 25.84 | 41.033 | 6.29 | 1.49 | 5.615 | 9123.59 | 2.883 | 98.1 | 79 | 1426 | 20.52 | 5930.3 | 2349.8 | 2905.2 | 3743.7 | 1208.3 | 0.62593 | 7.105
2024-12-09 | 21:40 | Data | 0 | 30.867 | 27.89 | 235.707 | 7.62 | 220.884 | 2206.25 | 25.84 | 40.943 | 6.3 | 1.495 | 5.563 | 9051.24 | 2.957 | 98.1 | 78.8 | 1434 | 20.52 | 5883.3 | 2327.4 | 2914.6 | 3739 | 1208.3 | 0.62023 | 7.056
2024-12-09 | 21:40 | Data | 0 | 31.076 | 28.214 | 235.752 | 7.62 | 220.794 | 2206.25 | 25.84 | 40.943 | 6.29 | 1.487 | 5.583 | 9033.15 | 2.721 | 98.1 | 78.9 | 1434 | 20.52 | 5871.5 | 2340.3 | 2890.4 | 3726.8 | 1208.3 | 0.62597 | 7.073
2024-12-09 | 21:40 | Data | 0 | 30.88 | 27.89 | 235.707 | 7.62 | 220.884 | 2203.54 | 25.84 | 41.033 | 6.29 | 1.504 | 5.592 | 9046.71 | 2.863 | 98.1 | 78.8 | 1432 | 20.52 | 5880.4 | 2333.9 | 2903.6 | 3733.8 | 1208.3 | 0.62292 | 7.097
2024-12-09 | 21:40 | Data | 0 | 30.671 | 28.018 | 235.661 | 7.62 | 220.703 | 2201.74 | 25.83 | 40.943 | 6.29 | 1.497 | 5.591 | 9051.24 | 2.674 | 98.1 | 78.9 | 1431 | 20.52 | 5883.3 | 2324.6 | 2908.8 | 3729.3 | 1208.3 | 0.62052 | 7.087
2024-12-09 | 21:40 | Data | 0 | 30.88 | 28.227 | 235.797 | 7.62 | 220.748 | 2203.54 | 25.84 | 41.033 | 6.29 | 1.496 | 5.586 | 9100.98 | 2.768 | 98.1 | 78.9 | 1431 | 20.47 | 5915.6 | 2309.6 | 2887.8 | 3706.9 | 1208.3 | 0.62106 | 7.082
2024-12-09 | 21:40 | Data | 0 | 30.739 | 27.883 | 235.707 | 7.62 | 220.748 | 2199.93 | 25.84 | 40.943 | 6.29 | 1.492 | 5.562 | 9119.07 | 2.93 | 98.1 | 78.8 | 1430 | 20.47 | 5927.4 | 2334.1 | 2900.3 | 3729.6 | 1208.4 | 0.62398 | 7.054
2024-12-09 | 21:40 | Data | 0 | 30.651 | 27.883 | 235.39 | 7.62 | 220.613 | 2199.93 | 25.84 | 40.943 | 6.28 | 1.491 | 5.558 | 9100.98 | 2.775 | 98.1 | 78.9 | 1430 | 20.47 | 5915.6 | 2346.1 | 2905.8 | 3742.5 | 1208.4 | 0.62499 | 7.047
2024-12-09 | 21:40 | Data | 0 | 30.705 | 28.335 | 235.797 | 7.62 | 220.794 | 2201.74 | 25.84 | 41.033 | 6.29 | 1.491 | 5.592 | 9141.68 | 2.849 | 98.1 | 78.9 | 1431 | 20.47 | 5942.1 | 2334.2 | 2911.6 | 3740.6 | 1208.4 | 0.62083 | 7.085
2024-12-09 | 21:40 | Data | 0 | 30.874 | 28.274 | 235.797 | 7.62 | 220.748 | 2203.54 | 25.83 | 40.943 | 6.29 | 1.49 | 5.596 | 9119.07 | 2.849 | 98.1 | 79 | 1432 | 20.52 | 5927.4 | 2327.5 | 2904.4 | 3730 | 1208.4 | 0.62213 | 7.087
2024-12-09 | 21:40 | Data | 0 | 31.191 | 28.139 | 235.752 | 7.62 | 220.703 | 2199.02 | 25.84 | 40.943 | 6.28 | 1.489 | 5.582 | 9100.98 | 2.923 | 98.1 | 78.9 | 1430 | 20.52 | 5915.6 | 2340.3 | 2921.8 | 3751 | 1208.4 | 0.62202 | 7.071
2024-12-09 | 21:40 | Data | 0 | 30.617 | 27.66 | 235.752 | 7.62 | 220.748 | 2199.93 | 25.84 | 40.943 | 6.29 | 1.5 | 5.573 | 9110.03 | 2.822 | 98.1 | 78.8 | 1430 | 20.47 | 5921.5 | 2339.9 | 2905.6 | 3738.4 | 1208.4 | 0.62372 | 7.074
2024-12-09 | 21:41 | Data | 0 | 30.853 | 27.937 | 235.661 | 7.62 | 220.703 | 2199.93 | 25.84 | 40.943 | 6.29 | 1.5 | 5.545 | 9105.5 | 2.775 | 98.1 | 78.7 | 1429 | 20.52 | 5918.6 | 2335.7 | 2909 | 3737.9 | 1208.4 | 0.62281 | 7.046
2024-12-09 | 21:41 | Data | 0 | 30.658 | 27.66 | 235.707 | 7.62 | 220.703 | 2199.93 | 25.84 | 41.033 | 6.29 | 1.496 | 5.571 | 9137.16 | 2.971 | 98.1 | 78.8 | 1430 | 20.52 | 5939.2 | 2343.1 | 2919.7 | 3751.6 | 1208.4 | 0.62245 | 7.067
2024-12-09 | 21:41 | Data | 0 | 30.88 | 28.112 | 235.842 | 7.62 | 220.839 | 2203.54 | 25.84 | 41.033 | 6.29 | 1.49 | 5.59 | 9141.68 | 2.768 | 98.1 | 79 | 1432 | 20.47 | 5942.1 | 2345.5 | 2910.7 | 3746 | 1208.4 | 0.62416 | 7.079
2024-12-09 | 21:41 | Data | 0 | 30.428 | 27.883 | 235.842 | 7.62 | 220.748 | 2203.54 | 25.84 | 41.033 | 6.29 | 1.5 | 5.587 | 9146.2 | 2.863 | 98.1 | 78.9 | 1432 | 20.47 | 5945 | 2349 | 2948.1 | 3778.3 | 1208.4 | 0.61985 | 7.087
2024-12-09 | 21:41 | Data | 0 | 30.536 | 27.667 | 235.661 | 7.62 | 220.703 | 2206.25 | 25.85 | 41.033 | 6.29 | 1.495 | 5.578 | 9132.64 | 2.748 | 98.1 | 78.9 | 1434 | 20.52 | 5936.2 | 2339.7 | 2919.4 | 3749.8 | 1208.4 | 0.62155 | 7.074
2024-12-09 | 21:41 | Data | 0 | 31.231 | 27.917 | 235.933 | 7.62 | 220.839 | 2205.35 | 25.84 | 41.033 | 6.3 | 1.493 | 5.583 | 9132.64 | 2.674 | 98.1 | 78.9 | 1433 | 20.52 | 5936.2 | 2344.9 | 2906.8 | 3741.7 | 1208.4 | 0.62259 | 7.077
2024-12-09 | 21:41 | Data | 0 | 31.103 | 27.856 | 235.707 | 7.62 | 220.748 | 2205.35 | 25.84 | 40.852 | 6.29 | 1.492 | 5.56 | 9128.11 | 2.741 | 98.2 | 78.8 | 1434 | 20.47 | 5933.3 | 2353.9 | 2939.7 | 3774.1 | 1208.4 | 0.6217 | 7.053
2024-12-09 | 21:41 | Data | 0 | 30.88 | 27.91 | 235.887 | 7.62 | 220.794 | 2206.25 | 25.84 | 40.943 | 6.29 | 1.5 | 5.571 | 9119.07 | 2.883 | 98.1 | 78.8 | 1434 | 20.47 | 5927.4 | 2337.7 | 2931.6 | 3759 | 1208.4 | 0.61789 | 7.071
2024-12-09 | 21:41 | Data | 0 | 30.556 | 28.126 | 235.661 | 7.62 | 220.794 | 2208.97 | 25.84 | 41.304 | 6.29 | 1.502 | 5.569 | 9146.2 | 2.626 | 98.1 | 78.8 | 1436 | 20.61 | 5945 | 2350.6 | 2932.4 | 3775 | 1208.4 | 0.62161 | 7.071
2024-12-09 | 21:41 | Data | 0 | 31.083 | 27.95 | 235.752 | 7.62 | 220.839 | 2208.06 | 25.84 | 41.304 | 6.29 | 1.488 | 5.565 | 9128.11 | 2.984 | 98.1 | 78.9 | 1436 | 20.7 | 5933.3 | 2408.2 | 2952 | 3819.1 | 1208.4 | 0.62862 | 7.053
2024-12-09 | 21:41 | Data | 0 | 30.415 | 27.768 | 235.797 | 7.62 | 220.794 | 2208.06 | 25.84 | 41.213 | 6.29 | 1.497 | 5.537 | 9155.25 | 2.883 | 98.1 | 78.7 | 1435 | 20.61 | 5950.9 | 2361.2 | 2926.2 | 3770.2 | 1208.4 | 0.62359 | 7.035
2024-12-09 | 21:41 | Data | 0 | 30.941 | 28.193 | 236.204 | 7.61 | 221.246 | 2212.58 | 25.84 | 41.213 | 6.29 | 1.495 | 5.573 | 9146.2 | 2.802 | 98.1 | 78.8 | 1439 | 20.7 | 5945 | 2371.6 | 2945.3 | 3790.6 | 1208.4 | 0.62349 | 7.068
2024-12-09 | 21:41 | Data | 0 | 30.766 | 27.714 | 236.068 | 7.62 | 221.2 | 2213.49 | 25.84 | 41.213 | 6.29 | 1.493 | 5.58 | 9150.73 | 2.815 | 98.1 | 78.9 | 1439 | 20.56 | 5948 | 2375.9 | 2955.2 | 3800.1 | 1208.4 | 0.62326 | 7.073
2024-12-09 | 21:41 | Data | 0 | 30.651 | 28.038 | 236.068 | 7.62 | 221.11 | 2213.49 | 25.84 | 41.394 | 6.29 | 1.485 | 5.59 | 9146.2 | 2.822 | 98.1 | 79 | 1439 | 20.65 | 5945 | 2355.9 | 2946.2 | 3780.9 | 1208.4 | 0.62104 | 7.072
2024-12-09 | 21:41 | Data | 0 | 30.793 | 28.004 | 236.249 | 7.62 | 221.246 | 2214.39 | 25.83 | 41.304 | 6.29 | 1.491 | 5.586 | 9110.03 | 2.667 | 98.1 | 78.9 | 1439 | 20.7 | 5921.5 | 2359.8 | 2951.1 | 3787.2 | 1208.4 | 0.6209 | 7.077
2024-12-09 | 21:41 | Data | 0 | 30.988 | 27.66 | 236.34 | 7.62 | 221.291 | 2213.49 | 25.83 | 41.123 | 6.29 | 1.502 | 5.579 | 9119.07 | 2.653 | 98.1 | 78.8 | 1439 | 20.56 | 5927.4 | 2372.7 | 2974.5 | 3813.7 | 1208.4 | 0.62026 | 7.082
2024-12-09 | 21:41 | Data | 0 | 30.516 | 27.559 | 236.159 | 7.62 | 221.2 | 2213.49 | 25.84 | 40.943 | 6.29 | 1.504 | 5.582 | 9105.5 | 2.761 | 98.2 | 78.8 | 1439 | 20.47 | 5918.6 | 2366 | 2984.7 | 3817.2 | 1208.4 | 0.61779 | 7.087
2024-12-09 | 21:41 | Data | 0 | 30.88 | 27.782 | 236.159 | 7.62 | 221.2 | 2213.49 | 25.84 | 41.033 | 6.29 | 1.492 | 5.601 | 9105.5 | 2.896 | 98.1 | 79 | 1439 | 20.52 | 5918.6 | 2368.5 | 2966.1 | 3807.5 | 1208.4 | 0.62083 | 7.095
2024-12-09 | 21:42 | Data | 0 | 30.415 | 28.079 | 236.249 | 7.62 | 221.2 | 2212.58 | 25.84 | 40.852 | 6.29 | 1.492 | 5.586 | 9123.59 | 2.66 | 98.2 | 78.9 | 1439 | 20.52 | 5930.3 | 2378.2 | 2970.2 | 3813.4 | 1208.4 | 0.62161 | 7.078
2024-12-09 | 21:42 | Data | 0 | 30.644 | 27.64 | 236.114 | 7.62 | 221.065 | 2213.49 | 25.83 | 41.033 | 6.29 | 1.487 | 5.611 | 9137.16 | 3.031 | 98.1 | 79.1 | 1439 | 20.52 | 5939.2 | 2368.4 | 2930.3 | 3776.9 | 1208.4 | 0.62502 | 7.097
2024-12-09 | 21:42 | Data | 0 | 30.651 | 27.68 | 236.114 | 7.62 | 221.065 | 2214.39 | 25.84 | 41.213 | 6.29 | 1.49 | 5.611 | 9146.2 | 2.998 | 98.1 | 79 | 1439 | 20.56 | 5945 | 3696.9 | 3965.8 | 5483.2 | 1208.4 | 0.65864 | 7.099
2024-12-09 | 21:42 | Data | 0 | 30.415 | 27.667 | 236.114 | 7.62 | 221.02 | 2214.39 | 25.83 | 40.852 | 6.29 | 1.5 | 5.613 | 9141.68 | 2.957 | 98.1 | 78.9 | 1439 | 20.52 | 5942.1 | 3453.9 | 3398.3 | 4941.1 | 1208.4 | 0.68358 | 7.113
2024-12-09 | 21:42 | Data | 0 | 30.415 | 27.822 | 235.933 | 7.62 | 220.884 | 2214.39 | 25.84 | 40.762 | 6.29 | 1.493 | 5.597 | 9168.81 | 2.768 | 98.2 | 78.9 | 1438 | 20.38 | 5959.7 | 3457.3 | 3398.6 | 4951.4 | 1208.4 | 0.68189 | 7.09
2024-12-09 | 21:42 | Data | 0 | 31.083 | 27.89 | 236.34 | 7.62 | 221.2 | 2222.52 | 25.83 | 40.943 | 6.29 | 1.484 | 5.591 | 9177.86 | 2.586 | 98.2 | 79 | 1444 | 20.43 | 5965.6 | 3469.2 | 3426.1 | 4973.8 | 1208.4 | 0.68191 | 7.074
2024-12-09 | 21:42 | Data | 0 | 30.198 | 27.741 | 236.114 | 7.62 | 221.02 | 2216.2 | 25.84 | 40.943 | 6.29 | 1.481 | 5.582 | 9173.34 | 2.842 | 98.2 | 79 | 1441 | 20.52 | 5962.7 | 3448.6 | 3460.3 | 4982.8 | 1208.4 | 0.67626 | 7.063
2024-12-09 | 21:42 | Data | 0 | 30.563 | 27.775 | 235.978 | 7.62 | 221.11 | 2213.49 | 25.83 | 40.943 | 6.29 | 1.491 | 5.61 | 9177.86 | 2.741 | 98.2 | 79 | 1439 | 20.47 | 5965.6 | 3477.3 | 3456.5 | 5000 | 1208.4 | 0.67956 | 7.103
2024-12-09 | 21:42 | Data | 0 | 31.036 | 27.917 | 236.385 | 7.62 | 221.11 | 2211.68 | 25.84 | 41.033 | 6.29 | 1.499 | 5.606 | 8698.5 | 2.869 | 98.1 | 78.9 | 1438 | 20.47 | 5654 | 3454.1 | 3449.2 | 4980 | 1208.4 | 0.6777 | 7.106
2024-12-09 | 21:42 | Data | 0 | 30.651 | 27.653 | 236.068 | 7.62 | 221.11 | 2211.68 | 25.83 | 40.943 | 6.29 | 1.5 | 5.58 | 9055.76 | 2.788 | 98.1 | 78.8 | 1437 | 20.52 | 5886.2 | 3373.6 | 3449 | 4915.5 | 1208.4 | 0.67163 | 7.078
2024-12-09 | 21:42 | Data | 0 | 30.793 | 27.66 | 235.978 | 7.62 | 221.065 | 2210.77 | 25.84 | 40.943 | 6.29 | 1.506 | 5.576 | 9060.28 | 2.788 | 98.1 | 78.7 | 1438 | 20.47 | 5889.2 | 3361.1 | 3395.8 | 4869.6 | 1208.4 | 0.67548 | 7.082
2024-12-09 | 21:42 | Data | 0 | 30.421 | 27.647 | 236.068 | 7.62 | 221.065 | 2208.06 | 25.83 | 40.943 | 6.29 | 1.498 | 5.581 | 9051.24 | 2.768 | 98.1 | 78.8 | 1436 | 20.52 | 5883.3 | 3371.6 | 3427.2 | 4903.9 | 1208.4 | 0.67315 | 7.078
2024-12-09 | 21:42 | Data | 0 | 30.995 | 27.728 | 236.159 | 7.62 | 221.2 | 2207.16 | 25.84 | 41.033 | 6.29 | 1.495 | 5.596 | 9073.85 | 2.971 | 98.1 | 78.9 | 1435 | 20.47 | 5898 | 3382 | 3438.1 | 4913.6 | 1208.4 | 0.67323 | 7.092
2024-12-09 | 21:42 | Data | 0 | 30.428 | 27.653 | 236.114 | 7.62 | 221.11 | 2208.97 | 25.84 | 40.943 | 6.29 | 1.501 | 5.595 | 9132.64 | 2.761 | 98.1 | 78.8 | 1435 | 20.52 | 5936.2 | 3377.3 | 3424.4 | 4902.1 | 1208.4 | 0.67354 | 7.096
2024-12-09 | 21:42 | Data | 0 | 30.232 | 27.68 | 236.023 | 7.62 | 221.2 | 2208.06 | 25.84 | 40.943 | 6.29 | 1.501 | 5.592 | 9128.11 | 2.653 | 98.1 | 78.8 | 1435 | 20.52 | 5933.3 | 3370.6 | 3411.5 | 4891 | 1208.4 | 0.67434 | 7.094
2024-12-09 | 21:42 | Data | 0 | 30.415 | 27.653 | 235.887 | 7.62 | 221.065 | 2208.97 | 25.83 | 40.943 | 6.29 | 1.501 | 5.573 | 9119.07 | 2.768 | 98.1 | 78.8 | 1436 | 20.47 | 5927.4 | 3379.9 | 3415.4 | 4901.7 | 1208.5 | 0.67381 | 7.074
2024-12-09 | 21:42 | Data | 0 | 30.415 | 27.964 | 236.023 | 7.62 | 221.246 | 2208.97 | 25.84 | 41.033 | 6.29 | 1.493 | 5.602 | 9123.59 | 2.782 | 98.1 | 79 | 1435 | 20.47 | 5930.3 | 3372.4 | 3409.3 | 4890.6 | 1208.5 | 0.67647 | 7.095
2024-12-09 | 21:43 | Data | 0 | 30.361 | 27.876 | 236.249 | 7.62 | 221.11 | 2208.06 | 25.84 | 40.943 | 6.29 | 1.494 | 5.592 | 9132.64 | 2.707 | 98.2 | 78.9 | 1436 | 20.47 | 5936.2 | 3385.7 | 3440.1 | 4919.7 | 1208.5 | 0.67369 | 7.086
2024-12-09 | 21:43 | Data | 0 | 31.009 | 27.93 | 235.933 | 7.62 | 221.065 | 2208.06 | 25.84 | 40.943 | 6.29 | 1.487 | 5.586 | 9132.64 | 2.998 | 98.1 | 79 | 1435 | 20.43 | 5936.2 | 3427.9 | 3419.1 | 4941.5 | 1208.5 | 0.67802 | 7.074
2024-12-09 | 21:43 | Data | 0 | 30.955 | 27.721 | 236.068 | 7.62 | 221.11 | 2208.97 | 25.84 | 40.943 | 6.28 | 1.493 | 5.603 | 9132.64 | 2.998 | 98.1 | 79 | 1435 | 20.52 | 5936.2 | 3431.4 | 3437.2 | 4948.1 | 1208.5 | 0.67633 | 7.096
2024-12-09 | 21:43 | Data | 0 | 30.874 | 27.89 | 236.159 | 7.62 | 221.2 | 2208.06 | 25.84 | 40.943 | 6.3 | 1.492 | 5.582 | 8983.4 | 2.795 | 98.1 | 78.9 | 1435 | 20.47 | 5839.2 | 3416.5 | 3443.8 | 4949.8 | 1208.5 | 0.67453 | 7.074
2024-12-09 | 21:43 | Data | 0 | 30.198 | 27.437 | 236.023 | 7.62 | 220.974 | 2208.06 | 25.84 | 41.033 | 6.28 | 1.499 | 5.591 | 8906.53 | 2.701 | 98.1 | 78.9 | 1435 | 20.52 | 5789.2 | 3422.8 | 3432 | 4945.5 | 1208.5 | 0.67699 | 7.089
2024-12-09 | 21:43 | Data | 0 | 30.563 | 27.768 | 236.114 | 7.62 | 221.065 | 2208.97 | 25.84 | 41.033 | 6.29 | 1.494 | 5.592 | 8906.53 | 2.667 | 98.2 | 78.9 | 1436 | 20.38 | 5789.2 | 3426.2 | 3406.3 | 4929.5 | 1208.5 | 0.68006 | 7.087
2024-12-09 | 21:43 | Data | 0 | 30.853 | 27.511 | 236.023 | 7.62 | 221.11 | 2208.06 | 25.83 | 41.033 | 6.29 | 1.5 | 5.576 | 8902 | 2.971 | 98.1 | 78.8 | 1435 | 20.43 | 5786.3 | 3418.3 | 3412 | 4929.5 | 1208.5 | 0.67884 | 7.077
2024-12-09 | 21:43 | Data | 0 | 30.536 | 27.484 | 235.887 | 7.62 | 221.065 | 2208.97 | 25.84 | 41.123 | 6.29 | 1.495 | 5.568 | 8924.61 | 2.714 | 98.1 | 78.8 | 1435 | 20.52 | 5801 | 3441.2 | 3468.2 | 4980.7 | 1208.5 | 0.67548 | 7.061
2024-12-09 | 21:43 | Data | 0 | 30.489 | 27.545 | 235.978 | 7.62 | 221.11 | 2206.25 | 25.84 | 41.033 | 6.29 | 1.489 | 5.57 | 9146.2 | 2.788 | 98.1 | 78.9 | 1434 | 20.47 | 5945 | 3451.4 | 3459.5 | 4981.5 | 1208.5 | 0.67718 | 7.058
2024-12-09 | 21:43 | Data | 0 | 30.415 | 27.599 | 235.887 | 7.62 | 220.794 | 2209.87 | 25.84 | 41.033 | 6.29 | 1.479 | 5.596 | 9621.04 | 2.815 | 98.1 | 79.1 | 1437 | 20.52 | 6253.7 | 3428 | 3436.3 | 4951.8 | 1208.5 | 0.67664 | 7.077
2024-12-09 | 21:43 | Data | 0 | 30.252 | 27.451 | 236.068 | 7.62 | 221.065 | 2205.35 | 25.84 | 40.943 | 6.29 | 1.492 | 5.593 | 9146.2 | 2.66 | 98.1 | 78.9 | 1434 | 20.52 | 5945 | 3446.8 | 3452.4 | 4974.2 | 1208.5 | 0.67738 | 7.086
2024-12-09 | 21:43 | Data | 0 | 30.536 | 27.964 | 236.114 | 7.62 | 221.065 | 2211.68 | 25.83 | 40.943 | 6.29 | 1.491 | 5.592 | 9141.68 | 2.775 | 98.1 | 79 | 1437 | 20.52 | 5942.1 | 3422.2 | 3448.8 | 4955.8 | 1208.5 | 0.67443 | 7.081
2024-12-09 | 21:43 | Data | 0 | 30.327 | 27.43 | 235.842 | 7.62 | 221.02 | 2204.45 | 25.84 | 41.033 | 6.28 | 1.483 | 5.596 | 9141.68 | 2.721 | 98.1 | 79 | 1433 | 20.52 | 5942.1 | 3441.9 | 3438.8 | 4959.7 | 1208.5 | 0.67924 | 7.079
2024-12-09 | 21:43 | Data | 0 | 30.624 | 27.667 | 236.159 | 7.62 | 221.11 | 2208.97 | 25.85 | 40.943 | 6.29 | 1.494 | 5.562 | 9146.2 | 2.964 | 98.1 | 78.8 | 1435 | 20.52 | 5945 | 3434.2 | 3429 | 4948.5 | 1208.5 | 0.67903 | 7.054
2024-12-09 | 21:43 | Data | 0 | 30.462 | 28.052 | 236.204 | 7.62 | 221.11 | 2208.06 | 25.84 | 40.943 | 6.3 | 1.491 | 5.554 | 9141.68 | 2.545 | 98.1 | 78.8 | 1435 | 20.52 | 5942.1 | 3444.1 | 3408 | 4942.1 | 1208.5 | 0.68154 | 7.045
2024-12-09 | 21:43 | Data | 0 | 30.867 | 27.505 | 235.933 | 7.62 | 221.065 | 2208.06 | 25.84 | 40.943 | 6.29 | 1.496 | 5.584 | 9137.16 | 3.126 | 98.1 | 78.9 | 1435 | 20.47 | 5939.2 | 3414.8 | 3406.3 | 4924.2 | 1208.5 | 0.67825 | 7.081
2024-12-09 | 21:43 | Data | 0 | 30.813 | 28.133 | 236.159 | 7.61 | 221.246 | 2208.06 | 25.85 | 40.943 | 6.29 | 1.497 | 5.556 | 9132.64 | 2.883 | 98.1 | 78.8 | 1435 | 20.47 | 5936.2 | 3428.7 | 3444.8 | 4958.1 | 1208.5 | 0.67573 | 7.052
2024-12-09 | 21:43 | Data | 0 | 30.624 | 27.768 | 236.023 | 7.62 | 221.2 | 2206.25 | 25.84 | 40.762 | 6.29 | 1.507 | 5.581 | 9119.07 | 2.937 | 98.2 | 78.7 | 1433 | 20.38 | 5927.4 | 3444.7 | 3434.9 | 4961.9 | 1208.5 | 0.67898 | 7.087
2024-12-09 | 21:44 | Data | 0 | 30.239 | 27.538 | 235.978 | 7.62 | 220.974 | 2206.25 | 25.83 | 41.033 | 6.29 | 1.49 | 5.599 | 9100.98 | 2.775 | 98.1 | 79 | 1434 | 20.52 | 5915.6 | 3436.6 | 3432.1 | 4952.1 | 1208.5 | 0.67818 | 7.09
2024-12-09 | 21:44 | Data | 0 | 30.246 | 27.795 | 235.933 | 7.62 | 220.974 | 2205.35 | 25.84 | 40.943 | 6.29 | 1.498 | 5.569 | 9096.46 | 2.592 | 98.1 | 78.8 | 1434 | 20.56 | 5912.7 | 3426.1 | 3432.8 | 4947.4 | 1208.5 | 0.67726 | 7.068
2024-12-09 | 21:44 | Data | 0 | 30.205 | 27.842 | 236.068 | 7.62 | 221.065 | 2205.35 | 25.84 | 40.943 | 6.29 | 1.503 | 5.568 | 9141.68 | 2.586 | 98.1 | 78.7 | 1434 | 20.47 | 5942.1 | 3422.8 | 3406.1 | 4919.7 | 1208.5 | 0.68074 | 7.071
2024-12-09 | 21:44 | Data | 0 | 30.415 | 27.538 | 235.933 | 7.62 | 220.974 | 2205.35 | 25.85 | 40.943 | 6.28 | 1.49 | 5.601 | 9132.64 | 2.876 | 98.1 | 79 | 1434 | 20.47 | 5936.2 | 3412.2 | 3398.4 | 4910.7 | 1208.5 | 0.67944 | 7.09
2024-12-09 | 21:44 | Data | 0 | 30.759 | 27.457 | 236.023 | 7.62 | 221.02 | 2206.25 | 25.85 | 41.033 | 6.29 | 1.484 | 5.55 | 9132.64 | 2.883 | 98.1 | 78.9 | 1433 | 20.52 | 5936.2 | 3417.4 | 3391.6 | 4910.2 | 1208.5 | 0.68085 | 7.034
2024-12-09 | 21:44 | Data | 0 | 30.428 | 27.559 | 235.978 | 7.62 | 221.02 | 2205.35 | 25.83 | 41.033 | 6.3 | 1.483 | 5.568 | 9159.77 | 2.721 | 98.1 | 79 | 1433 | 20.52 | 5953.9 | 3429 | 3431 | 4946.5 | 1208.5 | 0.67812 | 7.052
2024-12-09 | 21:44 | Data | 0 | 30.59 | 27.707 | 235.933 | 7.62 | 221.065 | 2203.54 | 25.84 | 41.033 | 6.29 | 1.498 | 5.56 | 9091.94 | 2.775 | 98.1 | 78.8 | 1432 | 20.47 | 5909.8 | 3430.5 | 3397.7 | 4920 | 1208.5 | 0.68215 | 7.058
2024-12-09 | 21:44 | Data | 0 | 30.273 | 27.653 | 236.068 | 7.62 | 220.974 | 2206.25 | 25.84 | 40.852 | 6.29 | 1.499 | 5.574 | 9073.85 | 2.579 | 98.1 | 78.8 | 1434 | 20.47 | 5898 | 3411.2 | 3401.8 | 4914.6 | 1208.5 | 0.67931 | 7.073
2024-12-09 | 21:44 | Data | 0 | 30.529 | 28.038 | 235.978 | 7.62 | 221.065 | 2205.35 | 25.84 | 41.033 | 6.29 | 1.482 | 5.593 | 9073.85 | 2.768 | 98.1 | 79.1 | 1434 | 20.52 | 5898 | 3431.8 | 3391.7 | 4923.3 | 1208.5 | 0.68295 | 7.076
2024-12-09 | 21:44 | Data | 0 | 30.313 | 27.532 | 235.933 | 7.62 | 220.794 | 2205.35 | 25.86 | 41.033 | 6.29 | 1.492 | 5.592 | 9073.85 | 2.822 | 98.1 | 79 | 1433 | 20.47 | 5898 | 3418 | 3403 | 4919.3 | 1208.5 | 0.67961 | 7.081
2024-12-09 | 21:44 | Data | 0 | 30.428 | 27.755 | 235.933 | 7.62 | 220.974 | 2207.16 | 25.85 | 41.033 | 6.29 | 1.495 | 5.586 | 9060.28 | 2.586 | 98.1 | 78.9 | 1434 | 20.52 | 5889.2 | 3411.9 | 3413 | 4921.7 | 1208.5 | 0.67627 | 7.082
2024-12-09 | 21:44 | Data | 0 | 30.86 | 27.721 | 236.023 | 7.62 | 221.02 | 2208.06 | 25.86 | 40.943 | 6.29 | 1.496 | 5.598 | 9051.24 | 2.971 | 98.1 | 78.9 | 1436 | 20.47 | 5883.3 | 3427.5 | 3431.3 | 4940 | 1208.6 | 0.67931 | 7.095
2024-12-09 | 21:44 | Data | 0 | 30.401 | 27.647 | 235.842 | 7.62 | 220.974 | 2208.97 | 25.85 | 40.943 | 6.29 | 1.494 | 5.586 | 9033.15 | 2.795 | 98.1 | 78.9 | 1436 | 20.52 | 5871.5 | 3434.9 | 3417.8 | 4938.3 | 1208.6 | 0.68048 | 7.081
2024-12-09 | 21:44 | Data | 0 | 30.644 | 27.444 | 236.159 | 7.62 | 220.974 | 2208.06 | 25.86 | 41.033 | 6.29 | 1.501 | 5.56 | 9060.28 | 3.018 | 98.1 | 78.7 | 1435 | 20.52 | 5889.2 | 3423.8 | 3444.2 | 4946 | 1208.6 | 0.67661 | 7.061
2024-12-09 | 21:44 | Data | 0 | 30.408 | 27.653 | 235.887 | 7.62 | 220.974 | 2204.45 | 25.85 | 41.033 | 6.29 | 1.493 | 5.576 | 9110.03 | 2.761 | 98.1 | 78.9 | 1432 | 20.52 | 5921.5 | 3417.1 | 3410.8 | 4924.5 | 1208.6 | 0.67799 | 7.069
2024-12-09 | 21:44 | Data | 0 | 30.205 | 27.599 | 236.023 | 7.62 | 221.02 | 2208.97 | 25.85 | 41.033 | 6.29 | 1.5 | 5.595 | 9132.64 | 2.761 | 98.1 | 78.9 | 1436 | 20.47 | 5936.2 | 3430.2 | 3395.4 | 4923.1 | 1208.6 | 0.68113 | 7.095
2024-12-09 | 21:44 | Data | 0 | 30.408 | 27.815 | 235.933 | 7.62 | 220.974 | 2208.97 | 25.86 | 40.943 | 6.29 | 1.493 | 5.606 | 9150.73 | 2.775 | 98.1 | 78.9 | 1435 | 20.47 | 5948 | 3440.2 | 3419.9 | 4944.5 | 1208.6 | 0.68102 | 7.1
2024-12-09 | 21:44 | Data | 0 | 30.759 | 27.714 | 236.068 | 7.62 | 221.2 | 2208.97 | 25.88 | 41.033 | 6.28 | 1.496 | 5.577 | 8969.84 | 2.721 | 98.1 | 78.9 | 1435 | 20.47 | 5830.4 | 3422.3 | 3377.1 | 4904.6 | 1208.6 | 0.68262 | 7.072
2024-12-09 | 21:45 | Data | 0 | 30.651 | 27.66 | 236.159 | 7.62 | 221.11 | 2206.25 | 25.85 | 41.033 | 6.28 | 1.494 | 5.557 | 8933.66 | 2.863 | 98.1 | 78.8 | 1433 | 20.52 | 5806.9 | 3434.2 | 3403.8 | 4927.5 | 1208.6 | 0.67999 | 7.051
2024-12-09 | 21:45 | Data | 0 | 30.401 | 27.701 | 236.521 | 7.62 | 221.471 | 2206.25 | 25.88 | 40.943 | 6.29 | 1.491 | 5.533 | 9132.64 | 2.842 | 98.1 | 78.8 | 1433 | 20.43 | 5936.2 | 3422 | 3464 | 4978.2 | 1208.6 | 0.6746 | 7.024
2024-12-09 | 21:45 | Data | 0 | 30.388 | 27.424 | 236.837 | 7.62 | 221.743 | 2205.35 | 25.85 | 41.033 | 6.29 | 1.496 | 5.585 | 9132.64 | 2.984 | 98.1 | 78.9 | 1433 | 20.47 | 5936.2 | 3430.6 | 3434.1 | 4952.2 | 1208.6 | 0.67607 | 7.082
2024-12-09 | 21:45 | Data | 0 | 30.813 | 27.545 | 236.883 | 7.62 | 221.788 | 2206.25 | 25.85 | 41.033 | 6.29 | 1.489 | 5.608 | 9132.64 | 3.065 | 98.1 | 79 | 1434 | 20.47 | 5936.2 | 3444.3 | 3436.1 | 4956.5 | 1208.6 | 0.679 | 7.094
2024-12-09 | 21:45 | Data | 0 | 30.408 | 27.647 | 236.928 | 7.62 | 221.788 | 2206.25 | 25.84 | 40.943 | 6.28 | 1.489 | 5.601 | 9132.64 | 2.768 | 98.1 | 79 | 1434 | 20.52 | 5936.2 | 3414.2 | 3443.4 | 4943.7 | 1208.6 | 0.67511 | 7.088
2024-12-09 | 21:45 | Data | 0 | 30.212 | 27.761 | 236.747 | 7.62 | 221.788 | 2205.35 | 25.84 | 41.033 | 6.29 | 1.491 | 5.616 | 9128.11 | 2.626 | 98.1 | 79 | 1433 | 20.47 | 5933.3 | 3420.3 | 3426.2 | 4935.3 | 1208.6 | 0.67745 | 7.105
2024-12-09 | 21:45 | Data | 0 | 30.651 | 27.511 | 236.973 | 7.62 | 221.969 | 2199.93 | 25.84 | 40.852 | 6.29 | 1.495 | 5.596 | 9132.64 | 2.768 | 98.1 | 78.9 | 1430 | 20.47 | 5936.2 | 3440.8 | 3448.9 | 4962.5 | 1208.6 | 0.67698 | 7.09
2024-12-09 | 21:45 | Data | 0 | 30.198 | 27.43 | 236.792 | 7.62 | 221.833 | 2199.02 | 25.84 | 41.033 | 6.29 | 1.491 | 5.596 | 9128.11 | 2.809 | 98.1 | 78.9 | 1430 | 20.52 | 5933.3 | 3434.6 | 3430.1 | 4948.4 | 1208.6 | 0.67822 | 7.088
2024-12-09 | 21:45 | Data | 0 | 30.556 | 27.768 | 236.928 | 7.62 | 221.878 | 2203.54 | 25.85 | 41.033 | 6.28 | 1.5 | 5.605 | 9132.64 | 2.775 | 98.1 | 78.9 | 1431 | 20.43 | 5936.2 | 3415.4 | 3425.3 | 4931.7 | 1208.6 | 0.67747 | 7.105
2024-12-09 | 21:45 | Data | 0 | 30.57 | 27.532 | 236.792 | 7.62 | 221.833 | 2204.45 | 25.84 | 40.943 | 6.29 | 1.5 | 5.604 | 9128.11 | 2.984 | 98.1 | 78.9 | 1432 | 20.52 | 5933.3 | 3434.6 | 3439.1 | 4952.2 | 1208.6 | 0.67818 | 7.104
2024-12-09 | 21:45 | Data | 0 | 30.529 | 27.538 | 236.792 | 7.62 | 221.743 | 2206.25 | 25.84 | 41.033 | 6.29 | 1.499 | 5.61 | 9132.64 | 2.971 | 98.1 | 78.9 | 1434 | 20.52 | 5936.2 | 3439.1 | 3441.3 | 4961.7 | 1208.6 | 0.67743 | 7.108
2024-12-09 | 21:45 | Data | 0 | 30.415 | 27.599 | 236.837 | 7.62 | 221.833 | 2206.25 | 25.84 | 41.033 | 6.29 | 1.498 | 5.601 | 9137.16 | 2.991 | 98.1 | 78.9 | 1433 | 20.52 | 5939.2 | 3430.6 | 3442 | 4946.8 | 1208.6 | 0.67472 | 7.099
2024-12-09 | 21:45 | Data | 0 | 30.691 | 27.761 | 236.973 | 7.62 | 221.923 | 2206.25 | 25.84 | 41.033 | 6.29 | 1.49 | 5.601 | 9110.03 | 2.869 | 98.1 | 79 | 1433 | 20.52 | 5921.5 | 3424.2 | 3434.6 | 4942.7 | 1208.6 | 0.67752 | 7.093
2024-12-09 | 21:45 | Data | 0 | 30.644 | 27.545 | 236.747 | 7.62 | 221.788 | 2205.35 | 25.85 | 40.943 | 6.29 | 1.487 | 5.618 | 9146.2 | 2.93 | 98.1 | 79.1 | 1434 | 20.43 | 5945 | 3416.2 | 3437.2 | 4939.4 | 1208.6 | 0.67648 | 7.106
2024-12-09 | 21:45 | Data | 0 | 30.415 | 27.822 | 236.837 | 7.62 | 221.743 | 2199.02 | 25.83 | 41.033 | 6.28 | 1.494 | 5.601 | 9155.25 | 2.714 | 98.1 | 79 | 1429 | 20.52 | 5950.9 | 3431.5 | 3452.8 | 4964.2 | 1208.6 | 0.67595 | 7.093
2024-12-09 | 21:45 | Data | 0 | 30.313 | 27.451 | 236.883 | 7.62 | 221.833 | 2203.54 | 25.84 | 41.033 | 6.29 | 1.486 | 5.611 | 9155.25 | 2.734 | 98.1 | 79.1 | 1432 | 20.52 | 5950.9 | 3442.2 | 3467.4 | 4977.3 | 1208.6 | 0.67628 | 7.097
2024-12-09 | 21:45 | Data | 0 | 30.543 | 27.653 | 236.837 | 7.62 | 221.833 | 2203.54 | 25.83 | 41.033 | 6.29 | 1.494 | 5.615 | 9159.77 | 2.68 | 98.1 | 79 | 1432 | 20.47 | 5953.9 | 3420.7 | 3461.9 | 4963.5 | 1208.6 | 0.67382 | 7.109
2024-12-09 | 21:46 | Data | 0 | 30.388 | 27.64 | 236.611 | 7.62 | 221.743 | 2201.74 | 25.84 | 41.033 | 6.28 | 1.492 | 5.595 | 9146.2 | 2.809 | 98.1 | 78.9 | 1431 | 20.52 | 5945 | 3431.3 | 3439.9 | 4953.7 | 1208.6 | 0.67733 | 7.087
2024-12-09 | 21:46 | Data | 0 | 29.996 | 27.397 | 236.837 | 7.62 | 221.788 | 2199.93 | 25.84 | 40.943 | 6.3 | 1.492 | 5.568 | 9146.2 | 2.592 | 98.1 | 78.9 | 1430 | 20.52 | 5945 | 3421.9 | 3477.9 | 4974.5 | 1208.6 | 0.6729 | 7.059
2024-12-09 | 21:46 | Data | 0 | 30.428 | 27.795 | 236.747 | 7.62 | 221.833 | 2199.02 | 25.84 | 40.943 | 6.29 | 1.496 | 5.575 | 9128.11 | 2.869 | 98.1 | 78.8 | 1429 | 20.47 | 5933.3 | 3435.7 | 3472.5 | 4977.5 | 1208.6 | 0.67399 | 7.07
2024-12-09 | 21:46 | Data | 0 | 30.874 | 27.944 | 236.973 | 7.62 | 221.923 | 2206.25 | 25.84 | 40.943 | 6.3 | 1.495 | 5.6 | 9146.2 | 2.707 | 98.1 | 78.9 | 1434 | 20.43 | 5945 | 3420.3 | 3438.5 | 4943.9 | 1208.6 | 0.67612 | 7.096
2024-12-09 | 21:46 | Data | 0 | 30.415 | 27.228 | 236.883 | 7.62 | 221.878 | 2201.74 | 25.83 | 41.033 | 6.29 | 1.5 | 5.6 | 9119.07 | 2.903 | 98.1 | 78.9 | 1432 | 20.47 | 5927.4 | 3417.1 | 3412.3 | 4923 | 1208.6 | 0.67764 | 7.099
2024-12-09 | 21:46 | Data | 0 | 30.185 | 27.626 | 236.792 | 7.62 | 221.697 | 2206.25 | 25.84 | 40.762 | 6.3 | 1.492 | 5.588 | 9146.2 | 2.761 | 98.2 | 78.9 | 1433 | 20.38 | 5945 | 3421.2 | 3415.4 | 4928.1 | 1208.6 | 0.67907 | 7.082
2024-12-09 | 21:46 | Data | 0 | 30.185 | 27.417 | 236.792 | 7.62 | 221.833 | 2208.97 | 25.83 | 40.943 | 6.29 | 1.49 | 5.573 | 9146.2 | 2.775 | 98.1 | 78.9 | 1435 | 20.43 | 5945 | 3422.8 | 3449.1 | 4954.9 | 1208.6 | 0.67489 | 7.065
2024-12-09 | 21:46 | Data | 0 | 30.334 | 27.444 | 236.747 | 7.62 | 221.743 | 2208.06 | 25.84 | 41.033 | 6.29 | 1.487 | 5.596 | 9128.11 | 2.768 | 98.1 | 79 | 1436 | 20.52 | 5933.3 | 3447.4 | 3453.8 | 4970.4 | 1208.7 | 0.67893 | 7.082
2024-12-09 | 21:46 | Data | 0 | 30.759 | 27.66 | 236.883 | 7.62 | 221.923 | 2208.97 | 25.84 | 40.852 | 6.29 | 1.497 | 5.604 | 9164.29 | 3.018 | 98.1 | 78.9 | 1435 | 20.43 | 5956.8 | 3436.6 | 3463.1 | 4978.4 | 1208.7 | 0.67594 | 7.101
2024-12-09 | 21:46 | Data | 0 | 30.698 | 27.653 | 237.018 | 7.62 | 221.833 | 2205.35 | 25.83 | 41.033 | 6.29 | 1.494 | 5.6 | 9182.38 | 2.674 | 98.1 | 78.9 | 1433 | 20.52 | 5968.5 | 3441.9 | 3449 | 4965.4 | 1208.7 | 0.67811 | 7.094
2024-12-09 | 21:46 | Data | 0 | 30.327 | 27.545 | 236.883 | 7.62 | 221.923 | 2210.77 | 25.84 | 40.943 | 6.28 | 1.496 | 5.615 | 9182.38 | 2.815 | 98.1 | 79 | 1438 | 20.47 | 5968.5 | 3424.7 | 3449.9 | 4956.4 | 1208.7 | 0.67542 | 7.111
2024-12-09 | 21:46 | Data | 0 | 30.408 | 27.701 | 236.883 | 7.62 | 221.743 | 2211.68 | 25.84 | 41.033 | 6.29 | 1.508 | 5.626 | 9191.43 | 2.667 | 98.1 | 78.9 | 1438 | 20.52 | 5974.4 | 3437.4 | 3468.6 | 4977.1 | 1208.7 | 0.67583 | 7.134
2024-12-09 | 21:46 | Data | 0 | 30.347 | 27.424 | 236.837 | 7.62 | 221.788 | 2209.87 | 25.84 | 41.033 | 6.28 | 1.494 | 5.619 | 9146.2 | 2.984 | 98.1 | 79 | 1436 | 20.52 | 5945 | 3417.3 | 3436.1 | 4943.5 | 1208.7 | 0.67553 | 7.113
2024-12-09 | 21:46 | Data | 0 | 30.212 | 27.228 | 236.792 | 7.62 | 221.788 | 2213.49 | 25.84 | 40.672 | 6.29 | 1.503 | 5.592 | 9146.2 | 2.917 | 98.2 | 78.8 | 1439 | 20.34 | 5945 | 3447.4 | 3410.6 | 4940.9 | 1208.7 | 0.68275 | 7.095
2024-12-09 | 21:46 | Data | 0 | 30.185 | 27.64 | 236.883 | 7.62 | 221.788 | 2213.49 | 25.84 | 41.033 | 6.29 | 1.499 | 5.6 | 9146.2 | 2.647 | 98.1 | 78.9 | 1439 | 20.52 | 5945 | 3436.4 | 3442 | 4956.4 | 1208.7 | 0.67799 | 7.098
2024-12-09 | 21:46 | Data | 0 | 30.185 | 27.741 | 236.973 | 7.62 | 221.833 | 2213.49 | 25.84 | 40.943 | 6.29 | 1.5 | 5.601 | 9146.2 | 2.849 | 98.2 | 78.9 | 1439 | 20.47 | 5945 | 3461.4 | 3428 | 4965.2 | 1208.7 | 0.67905 | 7.104
2024-12-09 | 21:46 | Data | 0 | 30.617 | 27.437 | 236.837 | 7.62 | 221.833 | 2213.49 | 25.83 | 40.943 | 6.29 | 1.503 | 5.626 | 9132.64 | 3.018 | 98.2 | 78.9 | 1439 | 20.47 | 5936.2 | 3445.4 | 3443.1 | 4965.1 | 1208.7 | 0.67826 | 7.129
2024-12-09 | 21:46 | Data | 0 | 30.374 | 27.647 | 236.747 | 7.63 | 221.743 | 2210.77 | 25.84 | 41.033 | 6.29 | 1.504 | 5.588 | 9141.68 | 2.768 | 98.1 | 78.8 | 1437 | 20.52 | 5942.1 | 3432.9 | 3421.9 | 4942.4 | 1208.7 | 0.67976 | 7.091
2024-12-09 | 21:46 | Data | 0 | 30.529 | 27.444 | 236.883 | 7.62 | 221.878 | 2213.49 | 25.84 | 40.943 | 6.29 | 1.503 | 5.606 | 9137.16 | 2.944 | 98.2 | 78.9 | 1439 | 20.52 | 5939.2 | 3435 | 3450.1 | 4961.2 | 1208.7 | 0.67767 | 7.109
2024-12-09 | 21:47 | Data | 0 | 30.421 | 27.829 | 236.611 | 7.62 | 221.697 | 2215.29 | 25.83 | 41.033 | 6.29 | 1.499 | 5.566 | 9137.16 | 2.647 | 98.2 | 78.8 | 1440 | 20.47 | 5939.2 | 3448 | 3449.6 | 4970.3 | 1208.7 | 0.67864 | 7.063
2024-12-09 | 21:47 | Data | 0 | 30.583 | 27.761 | 236.883 | 7.62 | 221.833 | 2213.49 | 25.84 | 41.033 | 6.29 | 1.495 | 5.582 | 9141.68 | 2.768 | 98.2 | 78.9 | 1439 | 20.47 | 5942.1 | 3432.5 | 3433.1 | 4951.4 | 1208.7 | 0.67773 | 7.076
2024-12-09 | 21:47 | Data | 0 | 30.415 | 27.538 | 236.928 | 7.62 | 221.833 | 2216.2 | 25.85 | 41.033 | 6.29 | 1.493 | 5.597 | 9177.86 | 2.768 | 98.1 | 78.9 | 1441 | 20.47 | 5965.6 | 3418.1 | 3446.8 | 4952.5 | 1208.7 | 0.67473 | 7.089
2024-12-09 | 21:47 | Data | 0 | 30.516 | 27.707 | 236.928 | 7.62 | 221.923 | 2215.29 | 25.84 | 40.943 | 6.29 | 1.494 | 5.577 | 9182.38 | 2.721 | 98.1 | 78.9 | 1441 | 20.52 | 5968.5 | 3441.9 | 3414.4 | 4944.5 | 1208.7 | 0.68106 | 7.071
2024-12-09 | 21:47 | Data | 0 | 30.651 | 27.741 | 236.973 | 7.62 | 221.833 | 2216.2 | 25.85 | 40.943 | 6.29 | 1.49 | 5.594 | 9191.43 | 2.883 | 98.2 | 79 | 1441 | 20.47 | 5974.4 | 3428.3 | 3375.7 | 4910.3 | 1208.7 | 0.68214 | 7.085
2024-12-09 | 21:47 | Data | 0 | 30.192 | 27.538 | 236.702 | 7.62 | 221.743 | 2217.1 | 25.84 | 41.033 | 6.29 | 1.498 | 5.59 | 9186.9 | 2.937 | 98.1 | 78.9 | 1441 | 20.52 | 5971.5 | 3436.2 | 3391 | 4921.8 | 1208.7 | 0.68311 | 7.086
2024-12-09 | 21:47 | Data | 0 | 30.644 | 27.444 | 236.928 | 7.62 | 221.833 | 2216.2 | 25.85 | 40.943 | 6.29 | 1.491 | 5.586 | 9155.25 | 3.011 | 98.2 | 78.9 | 1441 | 20.47 | 5950.9 | 3411.8 | 3393.9 | 4923 | 1208.7 | 0.68257 | 7.077
2024-12-09 | 21:47 | Data | 0 | 30.826 | 27.687 | 236.883 | 7.62 | 221.878 | 2216.2 | 25.83 | 41.033 | 6.29 | 1.493 | 5.592 | 9155.25 | 2.984 | 98.1 | 78.9 | 1441 | 20.52 | 5950.9 | 3422.9 | 3401.2 | 4921.1 | 1208.7 | 0.68005 | 7.084
2024-12-09 | 21:47 | Data | 0 | 30.374 | 27.214 | 236.837 | 7.61 | 221.878 | 2218 | 25.85 | 40.943 | 6.29 | 1.484 | 5.614 | 9159.77 | 2.795 | 98.2 | 79.1 | 1442 | 20.47 | 5953.9 | 3417 | 3383 | 4904.8 | 1208.7 | 0.6808 | 7.098
2024-12-09 | 21:47 | Data | 0 | 30.192 | 27.647 | 236.928 | 7.62 | 221.923 | 2218.91 | 25.84 | 40.943 | 6.29 | 1.496 | 5.581 | 9173.34 | 2.721 | 98.2 | 78.9 | 1443 | 20.47 | 5962.7 | 3433.7 | 3414.2 | 4941.1 | 1208.7 | 0.67963 | 7.077
2024-12-09 | 21:47 | Data | 0 | 30.185 | 27.444 | 236.656 | 7.62 | 221.697 | 2218.91 | 25.84 | 41.033 | 6.29 | 1.485 | 5.577 | 9259.26 | 2.741 | 98.2 | 79 | 1442 | 20.52 | 6018.5 | 3430 | 3417.9 | 4934.7 | 1208.7 | 0.68013 | 7.061
2024-12-09 | 21:47 | Data | 0 | 30.415 | 27.626 | 236.747 | 7.62 | 221.788 | 2217.1 | 25.85 | 41.033 | 6.29 | 1.487 | 5.61 | 9223.08 | 2.613 | 98.1 | 79.1 | 1441 | 20.52 | 5995 | 3430 | 3407.6 | 4924.6 | 1208.7 | 0.67883 | 7.096
2024-12-09 | 21:47 | Data | 0 | 30.455 | 27.43 | 236.883 | 7.62 | 221.969 | 2217.1 | 25.85 | 41.123 | 6.28 | 1.496 | 5.594 | 9227.6 | 2.66 | 98.1 | 78.9 | 1441 | 20.52 | 5997.9 | 3419.3 | 3402.4 | 4919.5 | 1208.7 | 0.67943 | 7.09
2024-12-09 | 21:47 | Data | 0 | 30.59 | 27.653 | 236.973 | 7.62 | 221.923 | 2216.2 | 25.83 | 41.033 | 6.29 | 1.499 | 5.596 | 9227.6 | 2.782 | 98.2 | 78.9 | 1441 | 20.47 | 5997.9 | 3439.7 | 3411.8 | 4939.6 | 1208.7 | 0.6803 | 7.094
2024-12-09 | 21:47 | Data | 0 | 30.415 | 27.329 | 236.928 | 7.62 | 221.743 | 2216.2 | 25.86 | 40.762 | 6.29 | 1.497 | 5.581 | 9182.38 | 3.187 | 98.2 | 78.9 | 1441 | 20.38 | 5968.5 | 3417.9 | 3374 | 4896.2 | 1208.7 | 0.68279 | 7.077
2024-12-09 | 21:47 | Data | 0 | 30.192 | 27.424 | 236.702 | 7.62 | 221.743 | 2218.91 | 25.88 | 41.033 | 6.29 | 1.491 | 5.601 | 9182.38 | 2.761 | 98.2 | 79 | 1442 | 20.47 | 5968.5 | 3428.9 | 3353.8 | 4895.1 | 1208.7 | 0.68479 | 7.092
2024-12-09 | 21:47 | Data | 0 | 30.59 | 27.694 | 236.837 | 7.62 | 221.878 | 2216.2 | 25.84 | 40.943 | 6.29 | 1.498 | 5.628 | 9200.47 | 2.802 | 98.2 | 79 | 1441 | 20.43 | 5980.3 | 3414 | 3390 | 4908.2 | 1208.7 | 0.68032 | 7.125
2024-12-09 | 21:48 | Data | 0 | 30.583 | 27.984 | 237.018 | 7.62 | 221.923 | 2218 | 25.84 | 41.033 | 6.29 | 1.499 | 5.602 | 9186.9 | 2.822 | 98.2 | 78.9 | 1441 | 20.52 | 5971.5 | 3438.9 | 3371.9 | 4912.6 | 1208.7 | 0.68565 | 7.099
2024-12-09 | 21:48 | Data | 0 | 30.475 | 27.505 | 236.837 | 7.62 | 221.878 | 2217.1 | 25.85 | 41.033 | 6.29 | 1.488 | 5.611 | 9186.9 | 2.863 | 98.1 | 79 | 1441 | 20.52 | 5971.5 | 3428.6 | 3368.5 | 4900.1 | 1208.7 | 0.68487 | 7.099
2024-12-09 | 21:48 | Data | 0 | 30.185 | 27.424 | 236.837 | 7.62 | 221.833 | 2217.1 | 25.84 | 40.943 | 6.29 | 1.493 | 5.621 | 9186.9 | 2.876 | 98.2 | 79 | 1441 | 20.47 | 5971.5 | 3419.4 | 3368.4 | 4897 | 1208.8 | 0.68212 | 7.115
2024-12-09 | 21:48 | Data | 0 | 30.388 | 27.424 | 236.656 | 7.62 | 221.697 | 2215.29 | 25.84 | 40.943 | 6.29 | 1.502 | 5.61 | 9177.86 | 2.977 | 98.1 | 78.9 | 1440 | 20.47 | 5965.6 | 3427.4 | 3388.9 | 4918.4 | 1208.8 | 0.68194 | 7.111
2024-12-09 | 21:48 | Data | 0 | 30.003 | 27.41 | 236.837 | 7.62 | 221.833 | 2216.2 | 25.84 | 40.943 | 6.29 | 1.498 | 5.582 | 9173.34 | 2.565 | 98.1 | 78.8 | 1441 | 20.52 | 5962.7 | 3424.8 | 3431.9 | 4940.6 | 1208.8 | 0.67799 | 7.082
2024-12-09 | 21:48 | Data | 0 | 30.61 | 27.653 | 236.792 | 7.62 | 221.833 | 2215.29 | 25.85 | 40.762 | 6.29 | 1.494 | 5.573 | 9159.77 | 2.788 | 98.2 | 78.9 | 1441 | 20.34 | 5953.9 | 3432.9 | 3443.2 | 4962.8 | 1208.8 | 0.67894 | 7.067
2024-12-09 | 21:48 | Data | 0 | 30.361 | 27.437 | 236.837 | 7.62 | 221.833 | 2217.1 | 25.84 | 40.943 | 6.29 | 1.491 | 5.602 | 9146.2 | 2.903 | 98.2 | 79 | 1441 | 20.47 | 5945 | 3415.5 | 3424.7 | 4931.3 | 1208.8 | 0.67771 | 7.095
2024-12-09 | 21:48 | Data | 0 | 30.583 | 27.856 | 236.973 | 7.62 | 221.923 | 2213.49 | 25.84 | 41.033 | 6.29 | 1.492 | 5.598 | 9159.77 | 2.957 | 98.2 | 78.9 | 1439 | 20.52 | 5953.9 | 3416.2 | 3419.3 | 4926.3 | 1208.8 | 0.67834 | 7.091
2024-12-09 | 21:48 | Data | 0 | 30.556 | 27.43 | 236.702 | 7.62 | 221.788 | 2213.49 | 25.85 | 41.033 | 6.29 | 1.496 | 5.608 | 9141.68 | 2.836 | 98.1 | 79 | 1439 | 20.52 | 5942.1 | 3413.2 | 3414.6 | 4924.8 | 1208.8 | 0.67732 | 7.104
2024-12-09 | 21:48 | Data | 0 | 30.192 | 27.647 | 236.837 | 7.62 | 221.788 | 2213.49 | 25.85 | 41.033 | 6.29 | 1.498 | 5.601 | 9191.43 | 2.714 | 98.1 | 78.9 | 1439 | 20.47 | 5974.4 | 3427.8 | 3407.8 | 4930 | 1208.8 | 0.67998 | 7.099
2024-12-09 | 21:48 | Data | 0 | 30.421 | 27.869 | 236.883 | 7.62 | 221.923 | 2212.58 | 25.84 | 41.033 | 6.28 | 1.5 | 5.611 | 9214.04 | 2.734 | 98.1 | 78.9 | 1438 | 20.52 | 5989.1 | 3432.2 | 3409.3 | 4933.5 | 1208.8 | 0.68013 | 7.111
2024-12-09 | 21:48 | Data | 0 | 30.212 | 27.815 | 236.837 | 7.62 | 221.923 | 2214.39 | 25.86 | 41.033 | 6.29 | 1.493 | 5.6 | 9214.04 | 2.565 | 98.2 | 79 | 1439 | 20.47 | 5989.1 | 3423.3 | 3377.9 | 4902.6 | 1208.8 | 0.68275 | 7.094
2024-12-09 | 21:48 | Data | 0 | 30.55 | 27.444 | 236.928 | 7.62 | 221.833 | 2210.77 | 25.86 | 40.943 | 6.29 | 1.498 | 5.612 | 9214.04 | 2.775 | 98.1 | 78.9 | 1438 | 20.52 | 5989.1 | 3434.7 | 3373 | 4907.8 | 1208.8 | 0.68523 | 7.109
2024-12-09 | 21:48 | Data | 0 | 30.529 | 27.653 | 236.883 | 7.62 | 221.788 | 2210.77 | 25.85 | 41.033 | 6.29 | 1.509 | 5.602 | 9195.95 | 2.944 | 98.1 | 78.8 | 1437 | 20.47 | 5977.4 | 3437.9 | 3367.4 | 4908.4 | 1208.8 | 0.68566 | 7.113
2024-12-09 | 21:48 | Data | 0 | 30.651 | 27.68 | 236.837 | 7.62 | 221.923 | 2213.49 | 25.85 | 40.943 | 6.29 | 1.494 | 5.595 | 9195.95 | 2.775 | 98.1 | 78.9 | 1438 | 20.52 | 5977.4 | 3429.6 | 3434.9 | 4949.7 | 1208.8 | 0.67668 | 7.091
2024-12-09 | 21:48 | Data | 0 | 30.637 | 27.478 | 236.792 | 7.62 | 221.878 | 2213.49 | 25.85 | 40.943 | 6.29 | 1.488 | 5.615 | 9173.34 | 2.991 | 98.1 | 79.1 | 1438 | 20.52 | 5962.7 | 3445.2 | 3409.6 | 4936.4 | 1208.8 | 0.68285 | 7.103
2024-12-09 | 21:48 | Data | 0 | 30.415 | 27.43 | 236.973 | 7.62 | 221.923 | 2211.68 | 25.86 | 41.033 | 6.29 | 1.502 | 5.611 | 9164.29 | 2.964 | 98.1 | 78.9 | 1438 | 20.47 | 5956.8 | 3429.2 | 3422.6 | 4940.9 | 1208.8 | 0.67956 | 7.114
2024-12-09 | 21:48 | Data | 0 | 30.388 | 27.653 | 236.702 | 7.62 | 221.697 | 2210.77 | 25.86 | 41.033 | 6.28 | 1.493 | 5.614 | 9177.86 | 2.768 | 98.1 | 79 | 1438 | 20.52 | 5965.6 | 3427.8 | 3454.2 | 4951.4 | 1208.8 | 0.67614 | 7.106
2024-12-09 | 21:49 | Data | 0 | 30.637 | 27.457 | 236.973 | 7.62 | 221.923 | 2206.25 | 25.86 | 41.033 | 6.29 | 1.486 | 5.601 | 9159.77 | 3.031 | 98.1 | 79 | 1434 | 20.52 | 5953.9 | 3443.6 | 3470.6 | 4979.2 | 1208.8 | 0.67559 | 7.087
2024-12-09 | 21:49 | Data | 0 | 30.185 | 27.424 | 236.702 | 7.62 | 221.697 | 2213.49 | 25.85 | 40.943 | 6.29 | 1.498 | 5.601 | 9155.25 | 2.768 | 98.2 | 78.9 | 1439 | 20.52 | 5950.9 | 3416.3 | 3452.8 | 4953.7 | 1208.8 | 0.67379 | 7.098
2024-12-09 | 21:49 | Data | 0 | 30.03 | 27.262 | 236.747 | 7.62 | 221.788 | 2213.49 | 25.85 | 41.033 | 6.29 | 1.502 | 5.592 | 9173.34 | 2.714 | 98.1 | 78.8 | 1439 | 20.52 | 5962.7 | 3419.1 | 3461.9 | 4957.7 | 1208.8 | 0.67461 | 7.095
2024-12-09 | 21:49 | Data | 0 | 30.617 | 27.883 | 237.109 | 7.62 | 221.833 | 2218.91 | 25.86 | 40.943 | 6.29 | 1.5 | 5.603 | 9159.77 | 2.849 | 98.2 | 78.9 | 1442 | 20.47 | 5953.9 | 3446.8 | 3465.8 | 4979.7 | 1208.8 | 0.67716 | 7.104
2024-12-09 | 21:49 | Data | 0 | 30.475 | 27.559 | 236.837 | 7.62 | 221.923 | 2215.29 | 25.86 | 41.033 | 6.29 | 1.493 | 5.623 | 9146.2 | 2.971 | 98.2 | 79 | 1440 | 20.47 | 5945 | 3432.9 | 3462.6 | 4967.4 | 1208.8 | 0.6762 | 7.115
2024-12-09 | 21:49 | Data | 0 | 30.475 | 28.119 | 236.973 | 7.62 | 221.923 | 2217.1 | 25.86 | 40.852 | 6.29 | 1.491 | 5.613 | 9173.34 | 2.89 | 98.2 | 79 | 1441 | 20.47 | 5962.7 | 3433.5 | 3426 | 4946.7 | 1208.8 | 0.67835 | 7.106
2024-12-09 | 21:49 | Data | 0 | 30.252 | 27.64 | 236.837 | 7.62 | 221.833 | 2216.2 | 25.86 | 41.033 | 6.29 | 1.49 | 5.609 | 9159.77 | 2.68 | 98.1 | 79 | 1441 | 20.52 | 5953.9 | 3439.5 | 3468.3 | 4980.7 | 1208.8 | 0.67538 | 7.098
2024-12-09 | 21:49 | Data | 0 | 30.185 | 27.424 | 236.837 | 7.62 | 221.788 | 2216.2 | 25.86 | 40.943 | 6.29 | 1.489 | 5.609 | 9150.73 | 2.869 | 98.1 | 79 | 1441 | 20.52 | 5948 | 3420.1 | 3490.9 | 4976.8 | 1208.8 | 0.67291 | 7.097
2024-12-09 | 21:49 | Data | 0 | 30.509 | 27.457 | 236.883 | 7.62 | 221.923 | 2218 | 25.85 | 40.943 | 6.29 | 1.5 | 5.603 | 9119.07 | 2.592 | 98.2 | 78.9 | 1442 | 20.47 | 5927.4 | 3447.9 | 3469.4 | 4987.5 | 1208.8 | 0.67554 | 7.104
2024-12-09 | 21:49 | Data | 0 | 30.192 | 27.424 | 237.064 | 7.62 | 221.923 | 2218.91 | 25.86 | 40.943 | 6.29 | 1.502 | 5.601 | 9119.07 | 2.761 | 98.2 | 78.9 | 1442 | 20.47 | 5927.4 | 3417.5 | 3491.2 | 4979.3 | 1208.8 | 0.66994 | 7.104
2024-12-09 | 21:49 | Data | 0 | 30.509 | 27.667 | 237.018 | 7.62 | 222.059 | 2220.72 | 25.86 | 40.943 | 6.29 | 1.497 | 5.608 | 9132.64 | 3.099 | 98.2 | 78.9 | 1443 | 20.47 | 5936.2 | 3444 | 3473.7 | 4970.7 | 1208.8 | 0.67242 | 7.104
2024-12-09 | 21:49 | Data | 0 | 30.259 | 27.255 | 236.837 | 7.62 | 221.788 | 2222.52 | 25.86 | 40.943 | 6.29 | 1.493 | 5.611 | 9105.5 | 2.876 | 98.2 | 79 | 1445 | 20.47 | 5918.6 | 3435.8 | 3454.6 | 4963.5 | 1208.8 | 0.6765 | 7.104
2024-12-09 | 21:49 | Data | 0 | 30.455 | 27.653 | 236.883 | 7.62 | 221.833 | 2217.1 | 25.85 | 40.943 | 6.29 | 1.496 | 5.611 | 9146.2 | 2.775 | 98.1 | 78.9 | 1441 | 20.52 | 5945 | 3424.8 | 3475.7 | 4977.5 | 1208.8 | 0.67606 | 7.108
2024-12-09 | 21:49 | Data | 0 | 30.313 | 27.43 | 236.837 | 7.62 | 221.878 | 2216.2 | 25.85 | 40.943 | 6.29 | 1.488 | 5.596 | 9128.11 | 2.761 | 98.1 | 79 | 1441 | 20.52 | 5933.3 | 3448.5 | 3456.9 | 4975.5 | 1208.8 | 0.67802 | 7.086
2024-12-09 | 21:49 | Data | 0 | 30.644 | 27.653 | 236.837 | 7.62 | 221.923 | 2216.2 | 25.86 | 41.033 | 6.28 | 1.497 | 5.621 | 9132.64 | 2.674 | 98.1 | 79 | 1441 | 20.47 | 5936.2 | 3422.3 | 3419.6 | 4936.5 | 1208.8 | 0.67789 | 7.118
2024-12-09 | 21:49 | Data | 0 | 30.347 | 27.647 | 237.064 | 7.62 | 221.833 | 2218.91 | 25.86 | 40.943 | 6.29 | 1.506 | 5.598 | 9119.07 | 2.971 | 98.2 | 78.8 | 1442 | 20.47 | 5927.4 | 3426.6 | 3437.8 | 4951 | 1208.9 | 0.67698 | 7.104
2024-12-09 | 21:49 | Data | 0 | 30.219 | 27.491 | 236.792 | 7.62 | 221.743 | 2217.1 | 25.86 | 41.123 | 6.29 | 1.491 | 5.592 | 9132.64 | 3.045 | 98.1 | 78.9 | 1442 | 20.56 | 5936.2 | 3443 | 3446.4 | 4965 | 1208.9 | 0.6784 | 7.084
2024-12-09 | 21:50 | Data | 0 | 30.415 | 27.66 | 236.928 | 7.62 | 221.878 | 2216.2 | 25.86 | 40.943 | 6.29 | 1.5 | 5.602 | 9128.11 | 2.748 | 98.2 | 78.9 | 1441 | 20.47 | 5933.3 | 3431.6 | 3474.2 | 4977.5 | 1208.9 | 0.674 | 7.103
2024-12-09 | 21:50 | Data | 0 | 30.752 | 28.025 | 236.973 | 7.62 | 221.923 | 2215.29 | 25.85 | 40.943 | 6.29 | 1.499 | 5.599 | 9159.77 | 2.822 | 98.2 | 78.9 | 1441 | 20.47 | 5953.9 | 3459.8 | 3435.2 | 4962.6 | 1208.9 | 0.68222 | 7.096
2024-12-09 | 21:50 | Data | 0 | 30.59 | 27.64 | 236.837 | 7.62 | 221.788 | 2217.1 | 25.88 | 41.033 | 6.28 | 1.49 | 5.619 | 9159.77 | 2.795 | 98.2 | 79 | 1441 | 20.52 | 5953.9 | 3455.2 | 3462.7 | 4981.3 | 1208.9 | 0.67966 | 7.108
2024-12-09 | 21:50 | Data | 0 | 30.428 | 27.741 | 236.883 | 7.62 | 221.878 | 2216.2 | 25.86 | 40.943 | 6.29 | 1.489 | 5.595 | 9186.9 | 2.701 | 98.2 | 79 | 1441 | 20.47 | 5971.5 | 3423.5 | 3385.7 | 4911.9 | 1208.9 | 0.68101 | 7.085
2024-12-09 | 21:50 | Data | 0 | 30.185 | 27.417 | 236.702 | 7.62 | 221.697 | 2215.29 | 25.85 | 40.943 | 6.29 | 1.49 | 5.623 | 9200.47 | 2.775 | 98.2 | 79.1 | 1441 | 20.47 | 5980.3 | 3422 | 3429.8 | 4938.5 | 1208.9 | 0.6789 | 7.112
2024-12-09 | 21:50 | Data | 0 | 30.475 | 27.424 | 236.656 | 7.62 | 221.878 | 2217.1 | 25.86 | 41.033 | 6.29 | 1.499 | 5.613 | 9195.95 | 2.788 | 98.2 | 78.9 | 1441 | 20.47 | 5977.4 | 3423.6 | 3409.2 | 4927.7 | 1208.9 | 0.67963 | 7.112
2024-12-09 | 21:50 | Data | 0 | 30.212 | 27.383 | 236.747 | 7.62 | 221.743 | 2218.91 | 25.86 | 41.033 | 6.29 | 1.497 | 5.605 | 9195.95 | 2.809 | 98.2 | 78.9 | 1442 | 20.52 | 5977.4 | 3424.4 | 3372.5 | 4901.7 | 1208.9 | 0.68308 | 7.101
2024-12-09 | 21:50 | Data | 0 | 30.475 | 27.457 | 236.792 | 7.62 | 221.923 | 2216.2 | 25.86 | 41.033 | 6.29 | 1.501 | 5.619 | 9146.2 | 2.788 | 98.2 | 78.9 | 1441 | 20.52 | 5945 | 3437.9 | 3379.5 | 4913 | 1208.9 | 0.68443 | 7.121
2024-12-09 | 21:50 | Data | 0 | 30.307 | 27.647 | 236.973 | 7.62 | 221.743 | 2214.39 | 25.86 | 40.943 | 6.29 | 1.506 | 5.575 | 9155.25 | 2.863 | 98.1 | 78.7 | 1439 | 20.52 | 5950.9 | 3447.1 | 3404.2 | 4939.5 | 1208.9 | 0.68304 | 7.081
2024-12-09 | 21:50 | Data | 0 | 30.185 | 27.579 | 236.837 | 7.62 | 221.788 | 2213.49 | 25.86 | 41.033 | 6.29 | 1.49 | 5.574 | 9173.34 | 2.788 | 98.1 | 78.9 | 1438 | 20.52 | 5962.7 | 3405.1 | 3424.3 | 4927.4 | 1208.9 | 0.67552 | 7.063
2024-12-09 | 21:50 | Data | 0 | 30.516 | 27.653 | 236.837 | 7.62 | 221.923 | 2214.39 | 25.85 | 41.033 | 6.28 | 1.494 | 5.604 | 9155.25 | 2.991 | 98.2 | 79 | 1439 | 20.47 | 5950.9 | 3425.7 | 3470.4 | 4970.8 | 1208.9 | 0.67408 | 7.096
2024-12-09 | 21:50 | Data | 0 | 30.577 | 27.437 | 236.837 | 7.62 | 221.833 | 2213.49 | 25.85 | 41.033 | 6.28 | 1.497 | 5.609 | 9173.34 | 3.011 | 98.2 | 78.9 | 1439 | 20.52 | 5962.7 | 3441.4 | 3453.7 | 4968.4 | 1208.9 | 0.67705 | 7.105
2024-12-09 | 21:50 | Data | 0 | 30.408 | 27.43 | 236.747 | 7.62 | 221.833 | 2213.49 | 25.86 | 41.033 | 6.29 | 1.495 | 5.564 | 9168.81 | 2.984 | 98.1 | 78.8 | 1438 | 20.52 | 5959.7 | 3442.1 | 3463.1 | 4976.1 | 1208.9 | 0.67709 | 7.059
2024-12-09 | 21:50 | Data | 0 | 30.327 | 27.376 | 236.837 | 7.62 | 221.833 | 2214.39 | 25.84 | 41.033 | 6.29 | 1.5 | 5.563 | 9173.34 | 2.984 | 98.1 | 78.8 | 1439 | 20.52 | 5962.7 | 3431.1 | 3445.4 | 4958.9 | 1208.9 | 0.67673 | 7.063
2024-12-09 | 21:50 | Data | 0 | 30.131 | 27.532 | 236.837 | 7.62 | 221.743 | 2212.58 | 25.86 | 41.033 | 6.29 | 1.501 | 5.586 | 9186.9 | 2.876 | 98.1 | 78.8 | 1439 | 20.52 | 5971.5 | 3443.9 | 3425.6 | 4955.5 | 1208.9 | 0.67973 | 7.087
2024-12-09 | 21:50 | Data | 0 | 30.239 | 27.43 | 237.018 | 7.62 | 221.833 | 2213.49 | 25.86 | 40.852 | 6.29 | 1.5 | 5.598 | 9150.73 | 2.876 | 98.2 | 78.9 | 1439 | 20.43 | 5948 | 3409.1 | 3403.4 | 4911.1 | 1208.9 | 0.67966 | 7.097
2024-12-09 | 21:50 | Data | 0 | 30.59 | 27.876 | 236.973 | 7.62 | 221.969 | 2216.2 | 25.86 | 41.033 | 6.29 | 1.495 | 5.614 | 9168.81 | 2.944 | 98.2 | 79 | 1441 | 20.47 | 5959.7 | 3436.8 | 3387.7 | 4920.5 | 1208.9 | 0.68312 | 7.11
2024-12-09 | 21:50 | Data | 0 | 30.847 | 27.68 | 236.792 | 7.62 | 222.059 | 2216.2 | 25.86 | 40.852 | 6.29 | 1.507 | 5.599 | 9191.43 | 2.971 | 98.2 | 78.8 | 1440 | 20.47 | 5974.4 | 3430.5 | 3385.8 | 4906.3 | 1208.9 | 0.68322 | 7.106
2024-12-09 | 21:51 | Data | 0 | 30.185 | 27.424 | 236.792 | 7.62 | 221.743 | 2216.2 | 25.85 | 41.033 | 6.29 | 1.494 | 5.592 | 9177.86 | 2.761 | 98.2 | 78.9 | 1441 | 20.52 | 5965.6 | 3428 | 3387 | 4914.5 | 1208.9 | 0.68237 | 7.087
2024-12-09 | 21:51 | Data | 0 | 30.421 | 27.653 | 236.973 | 7.62 | 221.878 | 2216.2 | 25.85 | 40.943 | 6.28 | 1.503 | 5.596 | 9173.34 | 2.761 | 98.2 | 78.8 | 1441 | 20.47 | 5962.7 | 3442.7 | 3419 | 4945 | 1208.9 | 0.68138 | 7.099
2024-12-09 | 21:51 | Data | 0 | 30.185 | 27.417 | 236.837 | 7.62 | 221.743 | 2216.2 | 25.85 | 41.123 | 6.29 | 1.493 | 5.604 | 9177.86 | 2.768 | 98.2 | 79 | 1441 | 20.47 | 5965.6 | 3429.9 | 3408 | 4930 | 1208.9 | 0.68047 | 7.097
2024-12-09 | 21:51 | Data | 0 | 30.415 | 27.478 | 236.792 | 7.62 | 221.697 | 2213.49 | 25.86 | 40.943 | 6.29 | 1.494 | 5.609 | 9182.38 | 2.788 | 98.2 | 79 | 1439 | 20.47 | 5968.5 | 3431.7 | 3432.1 | 4947.2 | 1208.9 | 0.68062 | 7.101
2024-12-09 | 21:51 | Data | 0 | 30.28 | 27.538 | 236.792 | 7.62 | 221.833 | 2208.06 | 25.86 | 40.943 | 6.28 | 1.492 | 5.59 | 9173.34 | 2.775 | 98.1 | 78.9 | 1435 | 20.47 | 5962.7 | 3434.1 | 3438.4 | 4954 | 1208.9 | 0.67777 | 7.083
2024-12-09 | 21:51 | Data | 0 | 30.361 | 27.755 | 236.837 | 7.62 | 221.788 | 2208.06 | 25.85 | 40.943 | 6.29 | 1.5 | 5.591 | 9173.34 | 2.883 | 98.1 | 78.9 | 1436 | 20.47 | 5962.7 | 3436.2 | 3467.3 | 4976.2 | 1208.9 | 0.67572 | 7.09
2024-12-09 | 21:51 | Data | 0 | 30.361 | 27.977 | 236.747 | 7.62 | 221.833 | 2213.49 | 25.86 | 41.033 | 6.29 | 1.494 | 5.596 | 9214.04 | 2.849 | 98.1 | 78.9 | 1439 | 20.47 | 5989.1 | 3438.1 | 3482.9 | 4989 | 1208.9 | 0.67376 | 7.09
2024-12-09 | 21:51 | Data | 0 | 30.32 | 27.653 | 237.018 | 7.62 | 221.969 | 2213.49 | 25.86 | 41.033 | 6.28 | 1.49 | 5.604 | 9218.56 | 2.545 | 98.1 | 79 | 1439 | 20.52 | 5992.1 | 3438.7 | 3443.3 | 4960.8 | 1208.9 | 0.67814 | 7.094
2024-12-09 | 21:51 | Data | 0 | 30.428 | 27.647 | 236.973 | 7.62 | 221.878 | 2211.68 | 25.86 | 41.123 | 6.29 | 1.495 | 5.597 | 9227.6 | 2.768 | 98.1 | 78.9 | 1439 | 20.56 | 5997.9 | 3437.8 | 3414.4 | 4945.1 | 1208.9 | 0.67998 | 7.091
2024-12-09 | 21:51 | Data | 0 | 30.077 | 27.424 | 236.883 | 7.62 | 221.833 | 2213.49 | 25.85 | 40.943 | 6.29 | 1.506 | 5.593 | 9232.13 | 2.849 | 98.2 | 78.8 | 1439 | 20.47 | 6000.9 | 3429.2 | 3405.1 | 4929.8 | 1208.9 | 0.68011 | 7.098
2024-12-09 | 21:51 | Data | 0 | 30.644 | 27.653 | 236.973 | 7.62 | 221.923 | 2212.58 | 25.88 | 41.033 | 6.28 | 1.5 | 5.569 | 9214.04 | 2.869 | 98.1 | 78.8 | 1439 | 20.47 | 5989.1 | 3441.1 | 3382.1 | 4919.8 | 1208.9 | 0.6847 | 7.068
2024-12-09 | 21:51 | Data | 0 | 30.415 | 27.545 | 236.883 | 7.62 | 221.833 | 2210.77 | 25.86 | 40.943 | 6.28 | 1.501 | 5.598 | 9227.6 | 3.099 | 98.1 | 78.9 | 1437 | 20.47 | 5997.9 | 3451.7 | 3380.1 | 4921 | 1209 | 0.68338 | 7.097
2024-12-09 | 21:51 | Data | 0 | 30.556 | 27.491 | 236.883 | 7.62 | 221.788 | 2209.87 | 25.85 | 41.033 | 6.28 | 1.498 | 5.602 | 9195.95 | 2.782 | 98.1 | 78.9 | 1437 | 20.47 | 5977.4 | 3432 | 3400 | 4926.9 | 1209 | 0.68185 | 7.1
2024-12-09 | 21:51 | Data | 0 | 30.745 | 27.498 | 236.973 | 7.62 | 221.788 | 2209.87 | 25.88 | 40.943 | 6.28 | 1.49 | 5.611 | 9168.81 | 2.93 | 98.1 | 79 | 1436 | 20.52 | 5959.7 | 3424.8 | 3415.9 | 4929 | 1209 | 0.67919 | 7.101
2024-12-09 | 21:51 | Data | 0 | 30.165 | 27.208 | 236.792 | 7.62 | 221.833 | 2208.97 | 25.85 | 40.943 | 6.28 | 1.494 | 5.608 | 9182.38 | 2.917 | 98.1 | 79 | 1436 | 20.52 | 5968.5 | 3438.5 | 3447.5 | 4962.4 | 1209 | 0.6775 | 7.102
2024-12-09 | 21:51 | Data | 0 | 30.185 | 27.451 | 236.883 | 7.62 | 221.878 | 2206.25 | 25.85 | 41.033 | 6.28 | 1.501 | 5.583 | 9182.38 | 2.917 | 98.1 | 78.8 | 1434 | 20.52 | 5968.5 | 3429.4 | 3433 | 4947.1 | 1209 | 0.67788 | 7.085
2024-12-09 | 21:51 | Data | 0 | 30.212 | 27.552 | 236.747 | 7.62 | 221.833 | 2206.25 | 25.86 | 41.123 | 6.28 | 1.497 | 5.596 | 9177.86 | 2.741 | 98.1 | 78.9 | 1433 | 20.56 | 5965.6 | 3427.8 | 3465.6 | 4971.1 | 1209 | 0.67506 | 7.093
2024-12-09 | 21:51 | Data | 0 | 30.185 | 27.464 | 236.792 | 7.62 | 221.743 | 2206.25 | 25.85 | 40.943 | 6.29 | 1.496 | 5.595 | 9173.34 | 2.937 | 98.1 | 78.9 | 1433 | 20.47 | 5962.7 | 3426.4 | 3464.9 | 4965.3 | 1209 | 0.67657 | 7.091
2024-12-09 | 21:52 | Data | 0 | 30.509 | 27.849 | 236.883 | 7.62 | 221.923 | 2206.25 | 25.86 | 41.033 | 6.29 | 1.499 | 5.574 | 9227.6 | 2.795 | 98.1 | 78.8 | 1434 | 20.47 | 5997.9 | 3415.8 | 3423.8 | 4931.3 | 1209 | 0.67783 | 7.073
2024-12-09 | 21:52 | Data | 0 | 30.644 | 27.565 | 237.018 | 7.62 | 221.878 | 2206.25 | 25.88 | 40.852 | 6.29 | 1.491 | 5.582 | 9232.13 | 2.822 | 98.1 | 78.9 | 1434 | 20.47 | 6000.9 | 3433.7 | 3406.8 | 4932 | 1209 | 0.68132 | 7.073
2024-12-09 | 21:52 | Data | 0 | 30.671 | 27.876 | 236.883 | 7.62 | 221.969 | 2206.25 | 25.88 | 40.943 | 6.29 | 1.488 | 5.613 | 9232.13 | 2.991 | 98.1 | 79 | 1433 | 20.52 | 6000.9 | 3432.2 | 3383.4 | 4913.4 | 1209 | 0.68285 | 7.101
2024-12-09 | 21:52 | Data | 0 | 30.361 | 27.964 | 236.883 | 7.62 | 221.788 | 2195.41 | 25.86 | 40.943 | 6.29 | 1.494 | 5.623 | 9232.13 | 2.917 | 98.1 | 79 | 1426 | 20.52 | 6000.9 | 3450.7 | 3402.6 | 4940.4 | 1209 | 0.68353 | 7.121
2024-12-09 | 21:52 | Data | 0 | 29.989 | 27.633 | 236.792 | 7.62 | 221.697 | 2205.35 | 25.86 | 40.943 | 6.28 | 1.496 | 5.594 | 9223.08 | 2.559 | 98.1 | 78.9 | 1433 | 20.52 | 5995 | 3435.9 | 3391 | 4923 | 1209 | 0.68259 | 7.09
2024-12-09 | 21:52 | Data | 0 | 30.401 | 27.478 | 236.702 | 7.62 | 221.697 | 2205.35 | 25.86 | 41.033 | 6.3 | 1.499 | 5.561 | 9214.04 | 2.883 | 98.1 | 78.8 | 1433 | 20.52 | 5989.1 | 3438 | 3403.2 | 4933 | 1209 | 0.6821 | 7.058
2024-12-09 | 21:52 | Data | 0 | 30.198 | 27.444 | 236.792 | 7.62 | 221.923 | 2208.06 | 25.85 | 41.033 | 6.29 | 1.499 | 5.576 | 9227.6 | 2.68 | 98.1 | 78.8 | 1435 | 20.52 | 5997.9 | 3426.4 | 3408.9 | 4928 | 1209 | 0.68017 | 7.075
2024-12-09 | 21:52 | Data | 0 | 30.394 | 27.471 | 236.792 | 7.62 | 221.833 | 2212.58 | 25.89 | 41.033 | 6.29 | 1.484 | 5.598 | 9227.6 | 2.883 | 98.1 | 79 | 1438 | 20.52 | 5997.9 | 3419.8 | 3431.6 | 4944 | 1209 | 0.67624 | 7.081
2024-12-09 | 21:52 | Data | 0 | 30.496 | 27.43 | 236.973 | 7.62 | 221.923 | 2208.06 | 25.86 | 41.033 | 6.28 | 1.492 | 5.576 | 9186.9 | 2.782 | 98.1 | 78.9 | 1436 | 20.52 | 5971.5 | 3438 | 3451.4 | 4967.3 | 1209 | 0.67733 | 7.068
2024-12-09 | 21:52 | Data | 0 | 30.516 | 28.038 | 237.064 | 7.62 | 221.833 | 2208.97 | 25.88 | 40.943 | 6.29 | 1.492 | 5.628 | 9168.81 | 2.775 | 98.1 | 79.1 | 1435 | 20.47 | 5959.7 | 3427.3 | 3428.6 | 4953.8 | 1209 | 0.67672 | 7.119
2024-12-09 | 21:52 | Data | 0 | 30.415 | 27.552 | 236.792 | 7.62 | 221.878 | 2208.97 | 25.88 | 40.943 | 6.28 | 1.477 | 5.601 | 9173.34 | 2.964 | 98.1 | 79.1 | 1436 | 20.47 | 5962.7 | 3435.1 | 3471 | 4974.5 | 1209 | 0.67656 | 7.078
2024-12-09 | 21:52 | Data | 0 | 30.307 | 27.336 | 236.973 | 7.62 | 221.923 | 2203.54 | 25.88 | 41.033 | 6.29 | 1.485 | 5.606 | 9173.34 | 2.734 | 98.1 | 79.1 | 1432 | 20.52 | 5962.7 | 3413.7 | 3419.3 | 4927.8 | 1209 | 0.67756 | 7.093
2024-12-09 | 21:52 | Data | 0 | 30.415 | 27.674 | 236.928 | 7.62 | 221.878 | 2208.97 | 25.86 | 41.484 | 6.28 | 1.488 | 5.596 | 9141.68 | 2.896 | 98.1 | 79 | 1436 | 20.74 | 5942.1 | 3418.6 | 3383.7 | 4896.9 | 1209 | 0.68189 | 7.085
2024-12-09 | 21:52 | Data | 0 | 30.3 | 27.599 | 236.792 | 7.62 | 221.923 | 2210.77 | 25.86 | 40.943 | 6.29 | 1.489 | 5.601 | 9123.59 | 2.849 | 98.1 | 79 | 1438 | 20.47 | 5930.3 | 3430.3 | 3358.8 | 4898.5 | 1209 | 0.68477 | 7.089
2024-12-09 | 21:52 | Data | 0 | 30.529 | 27.538 | 236.883 | 7.62 | 221.923 | 2213.49 | 25.88 | 41.033 | 6.29 | 1.492 | 5.587 | 9146.2 | 2.829 | 98.2 | 78.9 | 1440 | 20.47 | 5945 | 3435.9 | 3364.8 | 4903.8 | 1209 | 0.68616 | 7.079
2024-12-09 | 21:52 | Data | 0 | 30.536 | 27.768 | 236.883 | 7.62 | 221.969 | 2214.39 | 25.89 | 41.033 | 6.28 | 1.488 | 5.593 | 9150.73 | 2.761 | 98.2 | 79 | 1439 | 20.47 | 5948 | 3433 | 3349.7 | 4891.8 | 1209 | 0.68694 | 7.083
2024-12-09 | 21:52 | Data | 0 | 30.644 | 27.498 | 236.747 | 7.62 | 221.878 | 2216.2 | 25.85 | 40.943 | 6.28 | 1.498 | 5.58 | 9182.38 | 2.91 | 98.1 | 78.8 | 1441 | 20.52 | 5968.5 | 3432.4 | 3371.9 | 4906 | 1209 | 0.68457 | 7.077
2024-12-09 | 21:52 | Data | 0 | 30.212 | 27.538 | 236.747 | 7.62 | 221.697 | 2221.62 | 25.86 | 41.033 | 6.29 | 1.5 | 5.592 | 9218.56 | 2.822 | 98.2 | 78.9 | 1443 | 20.47 | 5992.1 | 3420.9 | 3369.1 | 4900.9 | 1209 | 0.6845 | 7.091
2024-12-09 | 21:53 | Data | 0 | 30.252 | 27.43 | 236.928 | 7.62 | 221.878 | 2223.43 | 25.85 | 40.943 | 6.28 | 1.504 | 5.58 | 9214.04 | 2.748 | 98.2 | 78.8 | 1445 | 20.52 | 5989.1 | 3425.1 | 3362.8 | 4891.6 | 1209 | 0.68527 | 7.083
2024-12-09 | 21:53 | Data | 0 | 30.705 | 27.667 | 236.973 | 7.62 | 222.104 | 2222.52 | 25.88 | 40.943 | 6.29 | 1.491 | 5.611 | 9214.04 | 2.782 | 98.2 | 79 | 1444 | 20.52 | 5989.1 | 3432.5 | 3389.5 | 4917.3 | 1209 | 0.68229 | 7.102
2024-12-09 | 21:53 | Data | 0 | 30.725 | 27.788 | 236.973 | 7.62 | 221.923 | 2222.52 | 25.86 | 40.943 | 6.28 | 1.482 | 5.622 | 9214.04 | 2.917 | 98.2 | 79.1 | 1444 | 20.52 | 5989.1 | 3434.8 | 3412.2 | 4937.5 | 1209 | 0.68045 | 7.106
2024-12-09 | 21:53 | Data | 0 | 30.428 | 27.437 | 236.883 | 7.62 | 221.878 | 2218.91 | 25.85 | 40.943 | 6.28 | 1.487 | 5.588 | 9200.47 | 2.971 | 98.2 | 79 | 1442 | 20.52 | 5980.3 | 3436.4 | 3388 | 4918.7 | 1209 | 0.6815 | 7.075
2024-12-09 | 21:53 | Data | 0 | 30.246 | 27.626 | 236.837 | 7.62 | 221.788 | 2220.72 | 25.88 | 40.943 | 6.28 | 1.489 | 5.577 | 9186.9 | 2.599 | 98.2 | 78.9 | 1444 | 20.47 | 5971.5 | 3426.2 | 3381.1 | 4900.7 | 1209 | 0.68264 | 7.065
2024-12-09 | 21:53 | Data | 0 | 30.442 | 27.741 | 236.973 | 7.62 | 221.878 | 2218.91 | 25.89 | 40.943 | 6.28 | 1.498 | 5.566 | 9200.47 | 2.68 | 98.2 | 78.8 | 1442 | 20.52 | 5980.3 | 3435.6 | 3368.6 | 4905.7 | 1209 | 0.68542 | 7.063
2024-12-09 | 21:53 | Data | 0 | 30.428 | 27.809 | 237.064 | 7.62 | 221.969 | 2218 | 25.89 | 41.033 | 6.28 | 1.49 | 5.591 | 9182.38 | 2.667 | 98.2 | 78.9 | 1442 | 20.52 | 5968.5 | 3437.4 | 3381.8 | 4917.9 | 1209.1 | 0.68393 | 7.082
2024-12-09 | 21:53 | Data | 0 | 30.394 | 27.43 | 236.792 | 7.62 | 221.878 | 2218.91 | 25.86 | 41.033 | 6.29 | 1.483 | 5.595 | 9186.9 | 2.674 | 98.2 | 79 | 1442 | 20.52 | 5971.5 | 3443.1 | 3369 | 4912.8 | 1209.1 | 0.68572 | 7.078
2024-12-09 | 21:53 | Data | 0 | 30.313 | 27.768 | 236.837 | 7.62 | 221.878 | 2218.91 | 25.88 | 40.852 | 6.28 | 1.489 | 5.595 | 9186.9 | 2.761 | 98.2 | 79 | 1442 | 20.38 | 5971.5 | 3448.4 | 3367.2 | 4909.3 | 1209.1 | 0.68844 | 7.084
2024-12-09 | 21:53 | Data | 0 | 30.415 | 27.653 | 236.702 | 7.62 | 221.833 | 2218.91 | 25.88 | 41.033 | 6.28 | 1.496 | 5.597 | 9182.38 | 2.761 | 98.2 | 78.9 | 1442 | 20.47 | 5968.5 | 3423.7 | 3380 | 4904.5 | 1209.1 | 0.68304 | 7.093
2024-12-09 | 21:53 | Data | 0 | 30.523 | 27.457 | 236.928 | 7.62 | 221.833 | 2218.91 | 25.88 | 41.033 | 6.29 | 1.492 | 5.601 | 9159.77 | 2.944 | 98.2 | 79 | 1442 | 20.52 | 5953.9 | 3426.4 | 3395.9 | 4920.1 | 1209.1 | 0.6812 | 7.094
2024-12-09 | 21:53 | Data | 0 | 30.421 | 27.971 | 237.109 | 7.62 | 222.104 | 2218.91 | 25.88 | 41.033 | 6.28 | 1.497 | 5.576 | 9214.04 | 2.964 | 98.2 | 78.8 | 1442 | 20.52 | 5989.1 | 3435.9 | 3387.9 | 4919.1 | 1209.1 | 0.68394 | 7.072
2024-12-09 | 21:53 | Data | 0 | 30.192 | 27.424 | 236.702 | 7.62 | 221.878 | 2211.68 | 25.89 | 40.943 | 6.28 | 1.495 | 5.577 | 9191.43 | 2.937 | 98.2 | 78.9 | 1438 | 20.43 | 5974.4 | 3446.7 | 3408.7 | 4940.7 | 1209.1 | 0.68234 | 7.073
2024-12-09 | 21:53 | Data | 0 | 30.266 | 27.572 | 236.973 | 7.61 | 221.969 | 2216.2 | 25.86 | 41.033 | 6.29 | 1.5 | 5.586 | 9209.51 | 2.619 | 98.2 | 78.8 | 1441 | 20.47 | 5986.2 | 3438.9 | 3375.4 | 4911.9 | 1209.1 | 0.68746 | 7.087
2024-12-09 | 21:53 | Data | 0 | 30.536 | 27.856 | 236.837 | 7.62 | 221.878 | 2218.91 | 25.88 | 41.033 | 6.28 | 1.507 | 5.608 | 9200.47 | 2.977 | 98.2 | 78.8 | 1443 | 20.47 | 5980.3 | 3436.2 | 3400.7 | 4932.3 | 1209.1 | 0.68119 | 7.115
2024-12-09 | 21:53 | Data | 0 | 30.59 | 27.545 | 236.973 | 7.62 | 221.923 | 2216.2 | 25.86 | 41.033 | 6.29 | 1.498 | 5.596 | 9159.77 | 2.802 | 98.1 | 78.9 | 1441 | 20.52 | 5953.9 | 3419.2 | 3394.7 | 4913 | 1209.1 | 0.67948 | 7.095
2024-12-09 | 21:53 | Data | 0 | 30.415 | 28.031 | 236.883 | 7.62 | 221.923 | 2218 | 25.88 | 41.033 | 6.28 | 1.496 | 5.592 | 9164.29 | 2.633 | 98.2 | 78.9 | 1442 | 20.43 | 5956.8 | 3451.9 | 3386.5 | 4927.5 | 1209.1 | 0.68607 | 7.087
2024-12-09 | 21:54 | Data | 0 | 30.482 | 27.43 | 236.883 | 7.62 | 221.878 | 2217.1 | 25.88 | 41.033 | 6.28 | 1.508 | 5.597 | 9168.81 | 2.815 | 98.1 | 78.8 | 1441 | 20.56 | 5959.7 | 3414.3 | 3375.8 | 4897.5 | 1209.1 | 0.68181 | 7.105
2024-12-09 | 21:54 | Data | 0 | 30.428 | 27.653 | 236.837 | 7.62 | 221.833 | 2216.2 | 25.88 | 41.033 | 6.28 | 1.492 | 5.611 | 9164.29 | 2.768 | 98.2 | 79 | 1440 | 20.47 | 5956.8 | 3433.6 | 3394.8 | 4919.8 | 1209.1 | 0.68304 | 7.103
2024-12-09 | 21:54 | Data | 0 | 30.421 | 27.809 | 236.928 | 7.62 | 221.923 | 2214.39 | 25.89 | 41.123 | 6.28 | 1.506 | 5.6 | 9173.34 | 2.674 | 98.1 | 78.8 | 1440 | 20.52 | 5962.7 | 3431.3 | 3388.1 | 4921.2 | 1209.1 | 0.68103 | 7.106
2024-12-09 | 21:54 | Data | 0 | 30.219 | 27.471 | 236.792 | 7.62 | 221.969 | 2208.97 | 25.89 | 40.762 | 6.28 | 1.498 | 5.601 | 9200.47 | 2.565 | 98.2 | 78.9 | 1436 | 20.38 | 5980.3 | 3452.2 | 3404.2 | 4938.1 | 1209.1 | 0.68465 | 7.099
2024-12-09 | 21:54 | Data | 0 | 30.556 | 27.653 | 236.928 | 7.62 | 221.969 | 2208.97 | 25.86 | 40.943 | 6.28 | 1.492 | 5.612 | 9182.38 | 2.782 | 98.1 | 79 | 1436 | 20.47 | 5968.5 | 3429.4 | 3393.8 | 4918.9 | 1209.1 | 0.68248 | 7.105
2024-12-09 | 21:54 | Data | 0 | 30.185 | 27.424 | 237.018 | 7.62 | 221.878 | 2208.06 | 25.88 | 40.943 | 6.29 | 1.501 | 5.592 | 9191.43 | 2.937 | 98.1 | 78.8 | 1435 | 20.47 | 5974.4 | 3424 | 3398.5 | 4917.9 | 1209.1 | 0.68156 | 7.093
2024-12-09 | 21:54 | Data | 0 | 30.34 | 27.633 | 236.973 | 7.62 | 221.833 | 2210.77 | 25.86 | 41.033 | 6.29 | 1.49 | 5.582 | 9168.81 | 2.599 | 98.1 | 78.9 | 1438 | 20.52 | 5959.7 | 3431.5 | 3413.4 | 4933.2 | 1209.1 | 0.67966 | 7.07
2024-12-09 | 21:54 | Data | 0 | 30.205 | 27.383 | 236.837 | 7.62 | 221.788 | 2214.39 | 25.86 | 40.943 | 6.29 | 1.493 | 5.575 | 9182.38 | 2.802 | 98.2 | 78.9 | 1439 | 20.47 | 5968.5 | 3437.2 | 3432 | 4950.8 | 1209.1 | 0.6792 | 7.068
2024-12-09 | 21:54 | Data | 0 | 30.415 | 27.653 | 236.837 | 7.62 | 221.788 | 2213.49 | 25.85 | 41.033 | 6.28 | 1.488 | 5.611 | 9182.38 | 2.761 | 98.1 | 79 | 1439 | 20.52 | 5968.5 | 3441.1 | 3435.4 | 4956.8 | 1209.1 | 0.6796 | 7.1
2024-12-09 | 21:54 | Data | 0 | 30.739 | 27.809 | 237.064 | 7.62 | 221.878 | 2214.39 | 25.88 | 41.033 | 6.29 | 1.494 | 5.582 | 9186.9 | 2.768 | 98.1 | 78.9 | 1439 | 20.52 | 5971.5 | 3422.8 | 3415.3 | 4930.3 | 1209.1 | 0.6775 | 7.076
2024-12-09 | 21:54 | Data | 0 | 30.529 | 27.66 | 236.928 | 7.62 | 221.833 | 2213.49 | 25.86 | 40.943 | 6.29 | 1.5 | 5.595 | 9173.34 | 2.498 | 98.1 | 78.8 | 1439 | 20.52 | 5962.7 | 3424.4 | 3421.4 | 4936.4 | 1209.1 | 0.6782 | 7.095
2024-12-09 | 21:54 | Data | 0 | 31.029 | 27.68 | 237.018 | 7.62 | 221.923 | 2213.49 | 25.88 | 41.033 | 6.28 | 1.5 | 5.623 | 9173.34 | 3.079 | 98.2 | 78.9 | 1439 | 20.47 | 5962.7 | 3441 | 3394.4 | 4928.3 | 1209.1 | 0.6817 | 7.124
2024-12-09 | 21:54 | Data | 0 | 30.104 | 27.599 | 236.792 | 7.62 | 221.923 | 2213.49 | 25.85 | 40.852 | 6.28 | 1.494 | 5.609 | 9177.86 | 2.626 | 98.2 | 79 | 1439 | 20.43 | 5965.6 | 3426.8 | 3400.4 | 4919.5 | 1209.1 | 0.68205 | 7.102
2024-12-09 | 21:54 | Data | 0 | 30.617 | 27.653 | 236.928 | 7.62 | 221.969 | 2213.49 | 25.89 | 41.033 | 6.28 | 1.495 | 5.599 | 9159.77 | 2.876 | 98.2 | 78.9 | 1439 | 20.52 | 5953.9 | 3414.3 | 3388 | 4898.1 | 1209.1 | 0.68136 | 7.093
2024-12-09 | 21:54 | Data | 0 | 30.225 | 27.424 | 237.018 | 7.62 | 221.969 | 2214.39 | 25.89 | 41.033 | 6.28 | 1.498 | 5.595 | 9214.04 | 2.775 | 98.2 | 78.9 | 1439 | 20.52 | 5989.1 | 3444.2 | 3378.1 | 4919.1 | 1209.1 | 0.68237 | 7.092
2024-12-09 | 21:54 | Data | 0 | 30.59 | 27.782 | 237.018 | 7.62 | 221.878 | 2213.49 | 25.88 | 41.033 | 6.28 | 1.5 | 5.594 | 9214.04 | 2.788 | 98.2 | 78.9 | 1439 | 20.52 | 5989.1 | 3414.3 | 3383.7 | 4900.9 | 1209.1 | 0.68111 | 7.095
2024-12-09 | 21:54 | Data | 0 | 30.421 | 27.714 | 236.883 | 7.62 | 221.833 | 2216.2 | 25.88 | 40.943 | 6.29 | 1.506 | 5.578 | 9218.56 | 2.647 | 98.1 | 78.7 | 1441 | 20.52 | 5992.1 | 3430.7 | 3378.6 | 4909 | 1209.1 | 0.68461 | 7.084
2024-12-09 | 21:54 | Data | 0 | 30.415 | 27.768 | 237.018 | 7.62 | 221.878 | 2216.2 | 25.86 | 40.943 | 6.29 | 1.509 | 5.615 | 9209.51 | 2.89 | 98.1 | 78.8 | 1441 | 20.47 | 5986.2 | 3450.5 | 3420.8 | 4951.1 | 1209.1 | 0.68179 | 7.125
2024-12-09 | 21:55 | Data | 0 | 30.469 | 27.856 | 236.973 | 7.62 | 221.878 | 2215.29 | 25.88 | 40.943 | 6.29 | 1.514 | 5.635 | 9218.56 | 2.741 | 98.1 | 78.8 | 1441 | 20.52 | 5992.1 | 3443.7 | 3382 | 4918.9 | 1209.1 | 0.68478 | 7.148
2024-12-09 | 21:55 | Data | 0 | 30.651 | 27.707 | 236.883 | 7.62 | 221.923 | 2216.2 | 25.86 | 41.033 | 6.28 | 1.5 | 5.616 | 9186.9 | 2.795 | 98.2 | 78.9 | 1441 | 20.47 | 5971.5 | 3443.8 | 3401.4 | 4934.1 | 1209.1 | 0.68236 | 7.115
2024-12-09 | 21:55 | Data | 0 | 30.583 | 27.532 | 236.792 | 7.62 | 221.833 | 2214.39 | 25.88 | 40.943 | 6.28 | 1.5 | 5.597 | 9182.38 | 2.869 | 98.1 | 78.9 | 1439 | 20.47 | 5968.5 | 3437 | 3390.9 | 4923 | 1209.2 | 0.68289 | 7.098
2024-12-09 | 21:55 | Data | 0 | 30.448 | 27.768 | 236.928 | 7.62 | 221.878 | 2213.49 | 25.85 | 41.033 | 6.28 | 1.505 | 5.6 | 9186.9 | 2.653 | 98.2 | 78.8 | 1439 | 20.56 | 5971.5 | 3426.1 | 3385.6 | 4911.3 | 1209.2 | 0.6827 | 7.106
2024-12-09 | 21:55 | Data | 0 | 31.063 | 27.721 | 237.109 | 7.62 | 222.104 | 2215.29 | 25.88 | 40.943 | 6.28 | 1.5 | 5.57 | 9182.38 | 2.903 | 98.1 | 78.8 | 1441 | 20.47 | 5968.5 | 3428.8 | 3367.8 | 4903.7 | 1209.2 | 0.68395 | 7.07
2024-12-09 | 21:55 | Data | 0 | 30.415 | 27.511 | 236.792 | 7.62 | 221.833 | 2213.49 | 25.89 | 40.943 | 6.29 | 1.49 | 5.582 | 9195.95 | 2.863 | 98.2 | 78.9 | 1438 | 20.52 | 5977.4 | 3407.1 | 3263.2 | 4811 | 1209.2 | 0.69419 | 7.072
2024-12-09 | 21:55 | Data | 0 | 30.34 | 27.653 | 236.883 | 7.62 | 221.969 | 2213.49 | 25.88 | 40.943 | 6.28 | 1.495 | 5.598 | 9209.51 | 2.545 | 98.1 | 78.9 | 1439 | 20.52 | 5986.2 | 3431 | 3375.6 | 4911 | 1209.2 | 0.68344 | 7.093
2024-12-09 | 21:55 | Data | 0 | 30.394 | 27.809 | 236.973 | 7.62 | 221.923 | 2208.97 | 25.89 | 41.033 | 6.29 | 1.494 | 5.6 | 9200.47 | 2.674 | 98.1 | 78.9 | 1435 | 20.47 | 5980.3 | 3435.7 | 3385.3 | 4919.7 | 1209.2 | 0.68306 | 7.093
2024-12-09 | 21:55 | Data | 0 | 30.246 | 27.856 | 236.883 | 7.62 | 221.878 | 2214.39 | 25.88 | 41.033 | 6.29 | 1.489 | 5.584 | 9191.43 | 2.565 | 98.1 | 78.9 | 1439 | 20.52 | 5974.4 | 3420.4 | 3372.6 | 4898 | 1209.2 | 0.68256 | 7.074
2024-12-09 | 21:55 | Data | 0 | 30.475 | 27.653 | 236.973 | 7.62 | 221.969 | 2214.39 | 25.89 | 41.033 | 6.28 | 1.493 | 5.604 | 9173.34 | 2.775 | 98.2 | 79 | 1439 | 20.52 | 5962.7 | 3428.3 | 3408.2 | 4929.4 | 1209.2 | 0.68027 | 7.096
2024-12-09 | 21:55 | Data | 0 | 30.705 | 27.66 | 237.109 | 7.62 | 221.969 | 2214.39 | 25.89 | 41.033 | 6.28 | 1.492 | 5.588 | 9173.34 | 2.856 | 98.1 | 78.9 | 1438 | 20.56 | 5962.7 | 3416.8 | 3390.2 | 4908 | 1209.2 | 0.68077 | 7.08
2024-12-09 | 21:55 | Data | 0 | 30.502 | 27.66 | 236.883 | 7.62 | 221.923 | 2213.49 | 25.89 | 40.852 | 6.28 | 1.482 | 5.573 | 9164.29 | 2.674 | 98.2 | 79 | 1439 | 20.47 | 5956.8 | 3425.4 | 3462.6 | 4963.7 | 1209.2 | 0.67555 | 7.056
2024-12-09 | 21:55 | Data | 0 | 30.415 | 27.653 | 236.883 | 7.62 | 221.833 | 2212.58 | 25.86 | 41.033 | 6.29 | 1.498 | 5.587 | 9173.34 | 2.761 | 98.1 | 78.9 | 1438 | 20.52 | 5962.7 | 3414.8 | 3434.6 | 4938.5 | 1209.2 | 0.67662 | 7.087
2024-12-09 | 21:55 | Data | 0 | 30.563 | 27.444 | 236.928 | 7.62 | 221.878 | 2216.2 | 25.89 | 40.852 | 6.28 | 1.503 | 5.575 | 9200.47 | 2.768 | 98.2 | 78.8 | 1441 | 20.43 | 5980.3 | 3428.9 | 3415.2 | 4935.8 | 1209.2 | 0.67948 | 7.077
2024-12-09 | 21:55 | Data | 0 | 30.421 | 27.822 | 236.837 | 7.62 | 221.878 | 2215.29 | 25.88 | 41.123 | 6.28 | 1.507 | 5.587 | 9195.95 | 2.714 | 98.1 | 78.8 | 1441 | 20.52 | 5977.4 | 3416.8 | 3412.5 | 4923.1 | 1209.2 | 0.67796 | 7.093
2024-12-09 | 21:55 | Data | 0 | 30.745 | 27.68 | 237.109 | 7.62 | 221.969 | 2211.68 | 25.88 | 41.033 | 6.29 | 1.507 | 5.593 | 9214.04 | 2.937 | 98.1 | 78.8 | 1438 | 20.52 | 5989.1 | 3423.2 | 3393 | 4917.1 | 1209.2 | 0.68078 | 7.099
2024-12-09 | 21:55 | Data | 0 | 30.131 | 27.869 | 236.883 | 7.62 | 221.969 | 2214.39 | 25.88 | 41.033 | 6.28 | 1.499 | 5.583 | 9214.04 | 2.869 | 98.1 | 78.8 | 1439 | 20.52 | 5989.1 | 3424.8 | 3381.6 | 4907.6 | 1209.2 | 0.68338 | 7.082
2024-12-09 | 21:56 | Data | 0 | 30.779 | 27.788 | 237.064 | 7.62 | 221.878 | 2214.39 | 25.88 | 41.033 | 6.28 | 1.482 | 5.611 | 9200.47 | 2.876 | 98.2 | 79.1 | 1439 | 20.47 | 5980.3 | 3440.7 | 3404.4 | 4932.2 | 1209.2 | 0.68316 | 7.093
2024-12-09 | 21:56 | Data | 0 | 30.529 | 27.484 | 236.973 | 7.62 | 221.969 | 2209.87 | 25.89 | 40.943 | 6.28 | 1.481 | 5.614 | 9182.38 | 2.896 | 98.1 | 79.1 | 1436 | 20.47 | 5968.5 | 3426.4 | 3395.1 | 4920.3 | 1209.2 | 0.68448 | 7.095
2024-12-09 | 21:56 | Data | 0 | 30.529 | 27.653 | 236.928 | 7.62 | 221.833 | 2208.06 | 25.88 | 41.033 | 6.28 | 1.492 | 5.614 | 9200.47 | 2.775 | 98.1 | 79 | 1436 | 20.52 | 5980.3 | 3424.7 | 3409.9 | 4928.5 | 1209.2 | 0.68013 | 7.106
2024-12-09 | 21:56 | Data | 0 | 30.219 | 27.647 | 236.747 | 7.62 | 221.878 | 2220.72 | 25.86 | 41.213 | 6.28 | 1.492 | 5.582 | 9191.43 | 2.728 | 98.2 | 78.9 | 1443 | 20.52 | 5974.4 | 3426.4 | 3404 | 4924.5 | 1209.2 | 0.68023 | 7.075
2024-12-09 | 21:56 | Data | 0 | 30.597 | 27.984 | 237.018 | 7.63 | 221.923 | 2216.2 | 25.88 | 40.943 | 6.28 | 1.495 | 5.602 | 9200.47 | 2.896 | 98.1 | 78.9 | 1441 | 20.47 | 5980.3 | 3438.5 | 3426.2 | 4947.2 | 1209.2 | 0.67891 | 7.099
2024-12-09 | 21:56 | Data | 0 | 30.739 | 27.822 | 236.883 | 7.62 | 221.878 | 2221.62 | 25.89 | 41.033 | 6.28 | 1.492 | 5.606 | 9191.43 | 2.93 | 98.2 | 79 | 1443 | 20.52 | 5974.4 | 3426.8 | 3452.2 | 4956.3 | 1209.2 | 0.67606 | 7.099
2024-12-09 | 21:56 | Data | 0 | 30.678 | 27.572 | 236.837 | 7.62 | 221.923 | 2222.52 | 25.89 | 40.943 | 6.28 | 1.496 | 5.609 | 9191.43 | 2.964 | 98.2 | 78.9 | 1445 | 20.47 | 5974.4 | 3417.8 | 3416.4 | 4925.5 | 1209.2 | 0.6787 | 7.106
2024-12-09 | 21:56 | Data | 0 | 30.138 | 28.045 | 236.883 | 7.62 | 221.788 | 2221.62 | 25.88 | 41.033 | 6.28 | 1.495 | 5.609 | 9214.04 | 2.653 | 98.2 | 79 | 1445 | 20.52 | 5989.1 | 3423.1 | 3423 | 4934.9 | 1209.2 | 0.67901 | 7.105
2024-12-09 | 21:56 | Data | 0 | 30.705 | 27.66 | 236.837 | 7.62 | 222.059 | 2218.91 | 25.89 | 40.943 | 6.28 | 1.496 | 5.581 | 9232.13 | 2.782 | 98.2 | 78.9 | 1443 | 20.43 | 6000.9 | 3434.8 | 3419.4 | 4942.2 | 1209.2 | 0.67955 | 7.077
2024-12-09 | 21:56 | Data | 0 | 30.651 | 27.687 | 236.928 | 7.62 | 222.059 | 2213.49 | 25.86 | 41.033 | 6.28 | 1.494 | 5.6 | 9223.08 | 2.964 | 98.1 | 78.9 | 1438 | 20.61 | 5995 | 3421.2 | 3388.2 | 4910 | 1209.2 | 0.68087 | 7.094
2024-12-09 | 21:56 | Data | 0 | 30.3 | 27.626 | 236.837 | 7.62 | 221.878 | 2218.91 | 25.89 | 41.033 | 6.29 | 1.495 | 5.609 | 9223.08 | 2.89 | 98.1 | 79 | 1442 | 20.52 | 5995 | 3441.3 | 3413.1 | 4940.7 | 1209.2 | 0.68175 | 7.103
2024-12-09 | 21:56 | Data | 0 | 30.415 | 27.741 | 236.702 | 7.62 | 221.878 | 2222.52 | 25.86 | 41.033 | 6.28 | 1.492 | 5.614 | 9227.6 | 2.998 | 98.1 | 79 | 1445 | 20.52 | 5997.9 | 3418.9 | 3370.3 | 4898.7 | 1209.2 | 0.68234 | 7.108
2024-12-09 | 21:56 | Data | 0 | 30.462 | 27.653 | 237.018 | 7.62 | 221.969 | 2226.14 | 25.88 | 40.943 | 6.28 | 1.505 | 5.601 | 9223.08 | 2.971 | 98.2 | 78.8 | 1446 | 20.47 | 5995 | 3424.1 | 3384.6 | 4911 | 1209.2 | 0.68195 | 7.105
2024-12-09 | 21:56 | Data | 0 | 30.617 | 27.667 | 236.973 | 7.62 | 222.059 | 2225.23 | 25.89 | 40.943 | 6.28 | 1.5 | 5.599 | 9218.56 | 2.91 | 98.2 | 78.9 | 1446 | 20.43 | 5992.1 | 3437.4 | 3393.6 | 4927 | 1209.2 | 0.68237 | 7.096
2024-12-09 | 21:56 | Data | 0 | 30.759 | 27.66 | 236.973 | 7.63 | 221.969 | 2224.33 | 25.89 | 40.943 | 6.28 | 1.496 | 5.616 | 9218.56 | 2.876 | 98.2 | 79 | 1446 | 20.47 | 5992.1 | 3417.9 | 3396.5 | 4916.4 | 1209.2 | 0.67968 | 7.112
2024-12-09 | 21:56 | Data | 0 | 30.766 | 27.923 | 237.018 | 7.62 | 221.969 | 2224.33 | 25.89 | 41.123 | 6.28 | 1.495 | 5.593 | 9223.08 | 2.755 | 98.2 | 78.9 | 1446 | 20.56 | 5995 | 3417.4 | 3386.7 | 4908.9 | 1209.2 | 0.681 | 7.089
2024-12-09 | 21:56 | Data | 0 | 30.415 | 27.674 | 236.656 | 7.62 | 221.878 | 2226.14 | 25.88 | 40.943 | 6.29 | 1.506 | 5.583 | 9227.6 | 2.68 | 98.2 | 78.8 | 1446 | 20.47 | 5997.9 | 3435 | 3394.3 | 4923.9 | 1209.3 | 0.68256 | 7.089
2024-12-09 | 21:56 | Data | 0 | 30.435 | 27.457 | 237.018 | 7.62 | 221.923 | 2225.23 | 25.88 | 41.033 | 6.28 | 1.495 | 5.592 | 9670.78 | 2.856 | 98.2 | 78.9 | 1446 | 20.52 | 6286 | 3427.5 | 3389.3 | 4914.8 | 1209.3 | 0.68274 | 7.086
2024-12-09 | 21:57 | Data | 0 | 30.509 | 27.545 | 236.973 | 7.62 | 221.969 | 2226.14 | 25.89 | 40.943 | 6.29 | 1.498 | 5.567 | 9245.69 | 2.788 | 98.2 | 78.8 | 1446 | 20.47 | 6009.7 | 3422.4 | 3390.2 | 4915 | 1209.3 | 0.68076 | 7.065
2024-12-09 | 21:57 | Data | 0 | 30.307 | 27.559 | 236.973 | 7.62 | 221.878 | 2225.23 | 25.89 | 41.033 | 6.29 | 1.496 | 5.603 | 9227.6 | 3.018 | 98.2 | 78.9 | 1445 | 20.52 | 5997.9 | 3418.5 | 3404.2 | 4920.5 | 1209.3 | 0.67969 | 7.098
2024-12-09 | 21:57 | Data | 0 | 30.529 | 27.653 | 236.837 | 7.62 | 221.878 | 2117.68 | 25.88 | 40.943 | 6.29 | 1.503 | 5.582 | 9232.13 | 2.849 | 98.1 | 78.8 | 1376 | 20.47 | 6000.9 | 3422.1 | 3420.7 | 4932.5 | 1209.3 | 0.67779 | 7.084
2024-12-09 | 21:57 | Data | 0 | 30.192 | 27.599 | 236.973 | 7.62 | 221.923 | 2228.85 | 25.86 | 40.943 | 6.29 | 1.508 | 5.556 | 9214.04 | 2.761 | 98.2 | 78.7 | 1449 | 20.52 | 5989.1 | 3446.7 | 3418.6 | 4948.1 | 1209.3 | 0.68149 | 7.064
2024-12-09 | 21:57 | Data | 0 | 30.3 | 27.437 | 236.792 | 7.62 | 221.743 | 2224.33 | 25.89 | 40.943 | 6.29 | 1.516 | 5.576 | 9195.95 | 2.755 | 98.2 | 78.6 | 1445 | 20.52 | 5977.4 | 3447 | 3424 | 4952.4 | 1209.3 | 0.68094 | 7.092
2024-12-09 | 21:57 | Data | 0 | 30.583 | 27.714 | 236.928 | 7.62 | 222.059 | 2222.52 | 25.88 | 41.033 | 6.29 | 1.509 | 5.6 | 9195.95 | 3.025 | 98.2 | 78.8 | 1445 | 20.47 | 5977.4 | 3436.9 | 3422.8 | 4945.4 | 1209.3 | 0.67962 | 7.108
2024-12-09 | 21:57 | Data | 0 | 30.759 | 27.667 | 236.973 | 7.62 | 221.969 | 2222.52 | 25.88 | 41.123 | 6.29 | 1.498 | 5.609 | 9195.95 | 2.815 | 98.2 | 78.9 | 1444 | 20.52 | 5977.4 | 3434.3 | 3423.7 | 4936 | 1209.3 | 0.67748 | 7.106
2024-12-09 | 21:57 | Data | 0 | 30.59 | 28.045 | 237.018 | 7.62 | 222.059 | 2225.23 | 25.89 | 41.123 | 6.29 | 1.51 | 5.59 | 9200.47 | 2.991 | 98.2 | 78.7 | 1446 | 20.52 | 5980.3 | 3453.5 | 3407.1 | 4947.1 | 1209.3 | 0.68262 | 7.098
2024-12-09 | 21:57 | Data | 0 | 30.651 | 27.869 | 236.973 | 7.63 | 222.104 | 2225.23 | 25.88 | 40.852 | 6.29 | 1.5 | 5.59 | 9191.43 | 2.822 | 98.2 | 78.8 | 1447 | 20.47 | 5974.4 | 3420.7 | 3402.7 | 4940.6 | 1209.3 | 0.67969 | 7.09
2024-12-09 | 21:57 | Data | 0 | 30.482 | 27.538 | 236.883 | 7.62 | 221.923 | 2224.33 | 25.89 | 40.943 | 6.28 | 1.499 | 5.591 | 9195.95 | 2.565 | 98.2 | 78.9 | 1446 | 20.52 | 5977.4 | 3430.1 | 3420.6 | 4938.1 | 1209.3 | 0.67719 | 7.089
2024-12-09 | 21:57 | Data | 0 | 30.664 | 27.883 | 237.018 | 7.62 | 222.149 | 2225.23 | 25.89 | 40.943 | 6.29 | 1.497 | 5.594 | 9200.47 | 2.775 | 98.2 | 78.9 | 1446 | 20.47 | 5980.3 | 3443.8 | 3433.6 | 4956.6 | 1209.3 | 0.6796 | 7.09
2024-12-09 | 21:57 | Data | 0 | 30.334 | 27.64 | 236.883 | 7.62 | 221.878 | 2232.47 | 25.88 | 41.033 | 6.29 | 1.495 | 5.6 | 9173.34 | 2.565 | 98.2 | 78.9 | 1452 | 20.52 | 5962.7 | 3440.2 | 3395.5 | 4928.8 | 1209.3 | 0.6827 | 7.094
2024-12-09 | 21:57 | Data | 0 | 30.415 | 27.768 | 236.973 | 7.62 | 221.833 | 2228.85 | 25.89 | 41.033 | 6.28 | 1.499 | 5.588 | 9679.83 | 2.761 | 98.2 | 78.8 | 1449 | 20.47 | 6291.9 | 3448 | 3414.7 | 4949.6 | 1209.3 | 0.68161 | 7.087
2024-12-09 | 21:57 | Data | 0 | 30.786 | 27.842 | 237.018 | 7.62 | 221.969 | 2227.95 | 25.86 | 40.943 | 6.28 | 1.491 | 5.582 | 9679.83 | 2.971 | 98.2 | 78.9 | 1448 | 20.47 | 6291.9 | 3433.5 | 3388.5 | 4916.1 | 1209.3 | 0.68308 | 7.074
2024-12-09 | 21:57 | Data | 0 | 30.415 | 27.43 | 236.702 | 7.62 | 221.923 | 2227.04 | 25.88 | 40.943 | 6.28 | 1.498 | 5.599 | 9200.47 | 2.984 | 98.2 | 78.9 | 1448 | 20.52 | 5980.3 | 3439.2 | 3387.5 | 4921.7 | 1209.3 | 0.6827 | 7.096
2024-12-09 | 21:57 | Data | 0 | 30.833 | 27.721 | 237.018 | 7.62 | 221.969 | 2217.1 | 25.85 | 41.033 | 6.28 | 1.495 | 5.606 | 9164.29 | 2.964 | 98.1 | 78.9 | 1441 | 20.47 | 5956.8 | 3437.8 | 3388.7 | 4923.2 | 1209.3 | 0.68338 | 7.101
2024-12-09 | 21:57 | Data | 0 | 30.583 | 27.876 | 237.109 | 7.62 | 221.878 | 2227.04 | 25.88 | 40.943 | 6.28 | 1.494 | 5.631 | 9173.34 | 2.775 | 98.2 | 79 | 1448 | 20.47 | 5962.7 | 3418.7 | 3402.2 | 4920.1 | 1209.3 | 0.67976 | 7.125
2024-12-09 | 21:57 | Data | 0 | 30.651 | 28.038 | 236.973 | 7.62 | 222.104 | 2233.37 | 25.88 | 40.943 | 6.28 | 1.491 | 5.613 | 9182.38 | 2.883 | 98.2 | 79 | 1451 | 20.47 | 5968.5 | 3439.5 | 3426.3 | 4946.1 | 1209.3 | 0.68035 | 7.106
2024-12-09 | 21:58 | Data | 0 | 30.293 | 27.43 | 236.973 | 7.62 | 221.923 | 2227.04 | 25.88 | 41.123 | 6.29 | 1.5 | 5.597 | 9182.38 | 2.755 | 98.2 | 78.9 | 1448 | 20.52 | 5968.5 | 3435.8 | 3442.3 | 4955.2 | 1209.3 | 0.67825 | 7.097
2024-12-09 | 21:58 | Data | 0 | 30.874 | 28.052 | 236.973 | 7.62 | 222.059 | 2227.95 | 25.89 | 40.943 | 6.28 | 1.503 | 5.595 | 9195.95 | 2.883 | 98.2 | 78.8 | 1448 | 20.47 | 5977.4 | 3433.4 | 3459.2 | 4966.6 | 1209.3 | 0.67593 | 7.099
2024-12-09 | 21:58 | Data | 0 | 30.192 | 27.599 | 236.928 | 7.62 | 221.833 | 2227.95 | 25.88 | 40.943 | 6.28 | 1.503 | 5.601 | 9200.47 | 2.937 | 98.2 | 78.9 | 1448 | 20.52 | 5980.3 | 3447.3 | 3499.4 | 5004 | 1209.3 | 0.67395 | 7.103
2024-12-09 | 21:58 | Data | 0 | 30.415 | 27.653 | 236.928 | 7.62 | 221.878 | 2225.23 | 25.89 | 41.304 | 6.28 | 1.5 | 5.598 | 9195.95 | 2.761 | 98.1 | 78.9 | 1446 | 20.65 | 5977.4 | 3409.5 | 3450.1 | 4948.6 | 1209.3 | 0.67266 | 7.099
2024-12-09 | 21:58 | Data | 0 | 30.577 | 27.478 | 236.837 | 7.62 | 221.788 | 2225.23 | 25.89 | 41.304 | 6.28 | 1.502 | 5.58 | 9195.95 | 2.903 | 98.1 | 78.8 | 1446 | 20.65 | 5977.4 | 3426.7 | 3462.3 | 4966.4 | 1209.3 | 0.67407 | 7.082
2024-12-09 | 21:58 | Data | 0 | 30.421 | 27.66 | 237.018 | 7.62 | 221.833 | 2225.23 | 25.88 | 41.304 | 6.28 | 1.501 | 5.611 | 9186.9 | 2.741 | 98.1 | 78.9 | 1446 | 20.65 | 5971.5 | 3451.2 | 3430.4 | 4957 | 1209.3 | 0.68136 | 7.111
2024-12-09 | 21:58 | Data | 0 | 30.313 | 27.647 | 237.018 | 7.62 | 222.059 | 2220.72 | 25.89 | 41.213 | 6.28 | 1.496 | 5.599 | 9186.9 | 2.741 | 98.1 | 78.9 | 1442 | 20.56 | 5971.5 | 3417.9 | 3381.2 | 4903.9 | 1209.3 | 0.68225 | 7.095
2024-12-09 | 21:58 | Data | 0 | 30.225 | 27.424 | 236.883 | 7.62 | 221.833 | 2214.39 | 25.86 | 41.213 | 6.29 | 1.496 | 5.601 | 9177.86 | 2.768 | 98.1 | 78.9 | 1439 | 20.65 | 5965.6 | 3442.1 | 3365.7 | 4906.4 | 1209.3 | 0.68544 | 7.096
2024-12-09 | 21:58 | Data | 0 | 30.644 | 27.707 | 236.747 | 7.62 | 221.969 | 2217.1 | 25.88 | 41.304 | 6.28 | 1.5 | 5.604 | 9186.9 | 2.768 | 98.1 | 78.9 | 1441 | 20.65 | 5971.5 | 3435.6 | 3387.4 | 4916.6 | 1209.3 | 0.68395 | 7.103
2024-12-09 | 21:58 | Data | 0 | 30.421 | 27.599 | 236.792 | 7.62 | 221.923 | 2217.1 | 25.88 | 41.213 | 6.29 | 1.502 | 5.598 | 9241.17 | 2.869 | 98.1 | 78.8 | 1441 | 20.61 | 6006.8 | 3411.9 | 3388.7 | 4907.1 | 1209.3 | 0.67997 | 7.1
2024-12-09 | 21:58 | Data | 0 | 30.421 | 27.937 | 237.018 | 7.62 | 221.969 | 2215.29 | 25.89 | 41.304 | 6.29 | 1.505 | 5.618 | 9214.04 | 2.937 | 98.1 | 78.9 | 1439 | 20.61 | 5989.1 | 3428.1 | 3411.6 | 4930.7 | 1209.3 | 0.68021 | 7.122
2024-12-09 | 21:58 | Data | 0 | 30.631 | 27.876 | 236.883 | 7.62 | 222.059 | 2216.2 | 25.89 | 41.213 | 6.28 | 1.497 | 5.591 | 9227.6 | 2.775 | 98.1 | 78.9 | 1440 | 20.65 | 5997.9 | 3443.2 | 3445.1 | 4962.8 | 1209.4 | 0.67807 | 7.087
2024-12-09 | 21:58 | Data | 0 | 30.415 | 27.876 | 236.883 | 7.62 | 221.923 | 2216.2 | 25.88 | 40.943 | 6.28 | 1.498 | 5.598 | 9232.13 | 2.755 | 98.1 | 78.9 | 1441 | 20.52 | 6000.9 | 3445.8 | 3449.2 | 4971.7 | 1209.4 | 0.67857 | 7.096
2024-12-09 | 21:58 | Data | 0 | 30.198 | 27.626 | 236.973 | 7.62 | 221.833 | 2216.2 | 25.89 | 41.033 | 6.28 | 1.494 | 5.588 | 9168.81 | 2.586 | 98.2 | 78.9 | 1441 | 20.52 | 5959.7 | 3435.7 | 3453 | 4963.5 | 1209.4 | 0.67687 | 7.084
2024-12-09 | 21:58 | Data | 0 | 30.442 | 27.457 | 236.792 | 7.63 | 221.878 | 2213.49 | 25.88 | 41.394 | 6.29 | 1.496 | 5.598 | 9173.34 | 2.937 | 98.1 | 78.9 | 1439 | 20.65 | 5962.7 | 3425.8 | 3452.5 | 4960.4 | 1209.4 | 0.67521 | 7.094
2024-12-09 | 21:58 | Data | 0 | 30.307 | 27.653 | 236.973 | 7.62 | 221.878 | 2213.49 | 25.89 | 41.033 | 6.28 | 1.496 | 5.597 | 9155.25 | 2.923 | 98.1 | 78.9 | 1439 | 20.52 | 5950.9 | 3429.2 | 3463.1 | 4967 | 1209.4 | 0.67448 | 7.094
2024-12-09 | 21:58 | Data | 0 | 30.421 | 27.653 | 236.883 | 7.62 | 221.878 | 2214.39 | 25.88 | 41.033 | 6.28 | 1.482 | 5.611 | 9168.81 | 2.883 | 98.1 | 79.1 | 1439 | 20.52 | 5959.7 | 3434.7 | 3438 | 4955.9 | 1209.4 | 0.67848 | 7.093
2024-12-09 | 21:58 | Data | 0 | 30.448 | 27.829 | 237.064 | 7.62 | 222.059 | 2213.49 | 25.88 | 41.033 | 6.28 | 1.492 | 5.621 | 9195.95 | 2.592 | 98.1 | 79 | 1439 | 20.47 | 5977.4 | 3449.6 | 3431.7 | 4959.4 | 1209.4 | 0.68036 | 7.114
2024-12-09 | 21:59 | Data | 0 | 30.833 | 27.923 | 237.018 | 7.62 | 221.923 | 2213.49 | 25.89 | 41.033 | 6.29 | 1.505 | 5.604 | 9195.95 | 2.815 | 98.1 | 78.8 | 1439 | 20.47 | 5977.4 | 3445.2 | 3417.1 | 4936.6 | 1209.4 | 0.67968 | 7.109
2024-12-09 | 21:59 | Data | 0 | 30.55 | 27.653 | 236.928 | 7.62 | 221.969 | 2208.97 | 25.88 | 40.943 | 6.28 | 1.501 | 5.608 | 9195.95 | 2.788 | 98.1 | 78.9 | 1436 | 20.52 | 5977.4 | 3428.9 | 3393.5 | 4921.8 | 1209.4 | 0.68106 | 7.109
2024-12-09 | 21:59 | Data | 0 | 30.442 | 27.971 | 236.928 | 7.62 | 221.969 | 2209.87 | 25.88 | 41.033 | 6.29 | 1.486 | 5.612 | 9195.95 | 2.714 | 98.1 | 79.1 | 1436 | 20.52 | 5977.4 | 3429.7 | 3382.5 | 4909.3 | 1209.4 | 0.68337 | 7.099
2024-12-09 | 21:59 | Data | 0 | 30.806 | 27.876 | 236.973 | 7.62 | 222.059 | 2217.1 | 25.88 | 40.943 | 6.28 | 1.495 | 5.582 | 9200.47 | 2.984 | 98.2 | 78.9 | 1441 | 20.43 | 5980.3 | 3424 | 3397.4 | 4917.3 | 1209.4 | 0.68013 | 7.077
2024-12-09 | 21:59 | Data | 0 | 30.624 | 27.93 | 237.109 | 7.62 | 221.923 | 2216.2 | 25.88 | 40.943 | 6.29 | 1.5 | 5.585 | 9177.86 | 2.842 | 98.1 | 78.8 | 1441 | 20.47 | 5965.6 | 3445.7 | 3414.8 | 4946.4 | 1209.4 | 0.6815 | 7.086
2024-12-09 | 21:59 | Data | 0 | 30.975 | 27.842 | 236.883 | 7.62 | 222.104 | 2218.91 | 25.89 | 40.943 | 6.28 | 1.496 | 5.588 | 9186.9 | 2.761 | 98.2 | 78.9 | 1443 | 20.56 | 5971.5 | 3427 | 3470 | 4968.1 | 1209.4 | 0.6755 | 7.085
2024-12-09 | 21:59 | Data | 0 | 30.361 | 27.694 | 236.928 | 7.62 | 221.833 | 2222.52 | 25.88 | 41.033 | 6.29 | 1.498 | 5.598 | 9200.47 | 2.869 | 98.2 | 78.9 | 1445 | 20.52 | 5980.3 | 3438.6 | 3438 | 4955.8 | 1209.4 | 0.67773 | 7.096
2024-12-09 | 21:59 | Data | 0 | 30.759 | 27.687 | 237.109 | 7.62 | 222.059 | 2218 | 25.89 | 41.033 | 6.28 | 1.496 | 5.6 | 9177.86 | 2.842 | 98.2 | 78.9 | 1442 | 20.52 | 5965.6 | 3445.1 | 3445.4 | 4965.3 | 1209.4 | 0.67848 | 7.096
2024-12-09 | 21:59 | Data | 0 | 30.847 | 27.694 | 237.064 | 7.62 | 222.059 | 2222.52 | 25.88 | 41.033 | 6.28 | 1.486 | 5.595 | 9195.95 | 2.984 | 98.2 | 79 | 1445 | 20.52 | 5977.4 | 3443.1 | 3434.7 | 4954.5 | 1209.4 | 0.67914 | 7.082
2024-12-09 | 21:59 | Data | 0 | 30.563 | 27.883 | 237.109 | 7.62 | 222.104 | 2222.52 | 25.89 | 41.033 | 6.28 | 1.484 | 5.599 | 9182.38 | 2.748 | 98.1 | 79 | 1444 | 20.56 | 5968.5 | 3421.5 | 3440.4 | 4947.1 | 1209.4 | 0.67656 | 7.084
2024-12-09 | 21:59 | Data | 0 | 30.678 | 27.66 | 237.018 | 7.62 | 222.104 | 2225.23 | 25.88 | 41.033 | 6.28 | 1.497 | 5.6 | 9182.38 | 2.788 | 98.2 | 78.9 | 1446 | 20.52 | 5968.5 | 3433.4 | 3382.2 | 4913 | 1209.4 | 0.68179 | 7.096
2024-12-09 | 21:59 | Data | 0 | 30.651 | 27.93 | 236.792 | 7.62 | 221.969 | 2226.14 | 25.88 | 41.033 | 6.28 | 1.504 | 5.584 | 9182.38 | 2.869 | 98.2 | 78.8 | 1447 | 20.52 | 5968.5 | 3430.4 | 3392.3 | 4920.3 | 1209.4 | 0.68225 | 7.088
2024-12-09 | 21:59 | Data | 0 | 30.739 | 28.004 | 237.109 | 7.63 | 221.969 | 2225.23 | 25.89 | 40.943 | 6.28 | 1.5 | 5.588 | 9146.2 | 2.619 | 98.2 | 78.8 | 1446 | 20.52 | 5945 | 3440.5 | 3387.5 | 4923.3 | 1209.4 | 0.68346 | 7.088
2024-12-09 | 21:59 | Data | 0 | 30.421 | 27.653 | 236.837 | 7.62 | 222.059 | 2224.33 | 25.86 | 41.304 | 6.29 | 1.498 | 5.601 | 9132.64 | 2.768 | 98.1 | 78.9 | 1446 | 20.7 | 5936.2 | 3442.1 | 3416.8 | 4940 | 1209.4 | 0.68204 | 7.096
2024-12-09 | 21:59 | Data | 0 | 30.347 | 27.876 | 236.973 | 7.62 | 221.969 | 2221.62 | 25.88 | 41.304 | 6.28 | 1.495 | 5.582 | 9141.68 | 2.667 | 98.1 | 78.9 | 1445 | 20.65 | 5942.1 | 3433.5 | 3410.6 | 4938.7 | 1209.4 | 0.67964 | 7.077
2024-12-09 | 21:59 | Data | 0 | 30.435 | 27.863 | 236.973 | 7.62 | 221.923 | 2222.52 | 25.88 | 41.213 | 6.28 | 1.493 | 5.57 | 9132.64 | 2.721 | 98.1 | 78.9 | 1445 | 20.56 | 5936.2 | 3434.7 | 3403.5 | 4928.5 | 1209.4 | 0.68019 | 7.062
2024-12-09 | 21:59 | Data | 0 | 30.739 | 27.977 | 236.792 | 7.62 | 221.878 | 2222.52 | 25.88 | 41.213 | 6.28 | 1.488 | 5.612 | 9173.34 | 2.896 | 98.1 | 79 | 1445 | 20.61 | 5962.7 | 3423.1 | 3395.3 | 4913.9 | 1209.4 | 0.68193 | 7.1
2024-12-09 | 22:00 | Data | 0 | 30.624 | 27.768 | 237.018 | 7.62 | 221.923 | 2222.52 | 25.89 | 41.304 | 6.28 | 1.494 | 5.603 | 9177.86 | 2.768 | 98.1 | 79 | 1445 | 20.65 | 5965.6 | 3429.9 | 3389.2 | 4917.7 | 1209.4 | 0.68162 | 7.098
2024-12-09 | 22:00 | Data | 0 | 30.691 | 27.43 | 237.018 | 7.62 | 221.923 | 2222.52 | 25.88 | 41.304 | 6.28 | 1.497 | 5.611 | 9693.39 | 2.869 | 98.1 | 78.9 | 1445 | 20.61 | 6300.7 | 3432.7 | 3415.5 | 4936.4 | 1209.4 | 0.68102 | 7.107
2024-12-09 | 22:00 | Data | 0 | 30.192 | 27.647 | 237.064 | 7.62 | 221.878 | 2221.62 | 25.88 | 40.852 | 6.28 | 1.5 | 5.604 | 9195.95 | 2.714 | 98.2 | 78.9 | 1445 | 20.43 | 5977.4 | 3429.6 | 3425.2 | 4930.9 | 1209.4 | 0.67868 | 7.104
2024-12-09 | 22:00 | Data | 0 | 30.536 | 27.829 | 236.973 | 7.62 | 221.833 | 2221.62 | 25.89 | 41.123 | 6.29 | 1.498 | 5.593 | 9173.34 | 2.984 | 98.1 | 78.9 | 1444 | 20.56 | 5962.7 | 3464.4 | 3448.2 | 4982.3 | 1209.4 | 0.67924 | 7.09
2024-12-09 | 22:00 | Data | 0 | 30.415 | 27.43 | 236.792 | 7.62 | 221.923 | 2221.62 | 25.89 | 41.213 | 6.28 | 1.49 | 5.623 | 9182.38 | 2.782 | 98.1 | 79.1 | 1444 | 20.61 | 5968.5 | 3433.2 | 3430.2 | 4946.1 | 1209.4 | 0.67935 | 7.113
2024-12-09 | 22:00 | Data | 0 | 31.083 | 27.721 | 236.928 | 7.62 | 222.104 | 2222.52 | 25.89 | 41.123 | 6.28 | 1.492 | 5.603 | 9173.34 | 3.025 | 98.1 | 79 | 1445 | 20.61 | 5962.7 | 3432.9 | 3414.2 | 4935.3 | 1209.4 | 0.68098 | 7.095
2024-12-09 | 22:00 | Data | 0 | 31.022 | 27.728 | 237.064 | 7.62 | 222.059 | 2222.52 | 25.88 | 41.304 | 6.28 | 1.494 | 5.585 | 9173.34 | 2.991 | 98.1 | 78.9 | 1445 | 20.65 | 5962.7 | 3417.9 | 3390.6 | 4915 | 1209.4 | 0.68021 | 7.078
2024-12-09 | 22:00 | Data | 0 | 30.361 | 27.647 | 236.837 | 7.62 | 221.878 | 2218.91 | 25.89 | 41.213 | 6.29 | 1.509 | 5.582 | 9159.77 | 2.761 | 98.1 | 78.7 | 1442 | 20.65 | 5953.9 | 3442.5 | 3416.6 | 4942.5 | 1209.5 | 0.68194 | 7.092
2024-12-09 | 22:00 | Data | 0 | 30.421 | 27.68 | 236.837 | 7.62 | 221.923 | 2218.91 | 25.89 | 41.213 | 6.28 | 1.51 | 5.558 | 9195.95 | 2.538 | 98.1 | 78.6 | 1443 | 20.65 | 5977.4 | 3434.4 | 3400.5 | 4929.3 | 1209.5 | 0.6822 | 7.07
2024-12-09 | 22:00 | Data | 0 | 30.192 | 27.599 | 236.928 | 7.62 | 221.878 | 2224.33 | 25.89 | 41.213 | 6.28 | 1.492 | 5.57 | 9195.95 | 2.768 | 98.1 | 78.9 | 1446 | 20.61 | 5977.4 | 3431.3 | 3455.4 | 4964.4 | 1209.5 | 0.6752 | 7.061
2024-12-09 | 22:00 | Data | 0 | 30.766 | 27.788 | 236.928 | 7.62 | 221.923 | 2216.2 | 25.89 | 41.213 | 6.29 | 1.491 | 5.604 | 9200.47 | 2.944 | 98.1 | 79 | 1441 | 20.61 | 5980.3 | 3432.1 | 3443.7 | 4955.4 | 1209.5 | 0.67776 | 7.096
2024-12-09 | 22:00 | Data | 0 | 30.192 | 27.424 | 236.792 | 7.62 | 221.923 | 2218.91 | 25.88 | 41.304 | 6.28 | 1.5 | 5.597 | 9200.47 | 2.876 | 98.1 | 78.9 | 1442 | 20.61 | 5980.3 | 3441.7 | 3417 | 4943.6 | 1209.5 | 0.68092 | 7.096
2024-12-09 | 22:00 | Data | 0 | 30.536 | 27.883 | 237.064 | 7.62 | 222.104 | 2220.72 | 25.88 | 41.304 | 6.28 | 1.502 | 5.57 | 9214.04 | 2.984 | 98.1 | 78.8 | 1443 | 20.7 | 5989.1 | 3432 | 3447.7 | 4957.6 | 1209.5 | 0.67854 | 7.072
2024-12-09 | 22:00 | Data | 0 | 30.82 | 27.667 | 237.109 | 7.63 | 222.149 | 2220.72 | 25.89 | 41.394 | 6.28 | 1.497 | 5.594 | 9200.47 | 2.809 | 98.1 | 78.9 | 1442 | 20.56 | 5980.3 | 3411.2 | 3371.7 | 4891.3 | 1209.5 | 0.68286 | 7.092
2024-12-09 | 22:00 | Data | 0 | 30.637 | 27.565 | 237.018 | 7.62 | 222.059 | 2218 | 25.88 | 41.304 | 6.28 | 1.496 | 5.598 | 9182.38 | 2.944 | 98.1 | 78.9 | 1442 | 20.65 | 5968.5 | 3418.8 | 3380.2 | 4904.4 | 1209.5 | 0.68157 | 7.093
2024-12-09 | 22:00 | Data | 0 | 30.448 | 27.626 | 237.109 | 7.62 | 222.059 | 2216.2 | 25.89 | 41.213 | 6.28 | 1.493 | 5.6 | 9186.9 | 2.647 | 98.1 | 78.9 | 1441 | 20.61 | 5971.5 | 3426.6 | 3388.9 | 4914.5 | 1209.5 | 0.68226 | 7.093
2024-12-09 | 22:00 | Data | 0 | 30.415 | 27.424 | 236.883 | 7.62 | 221.833 | 2216.2 | 25.89 | 41.213 | 6.29 | 1.484 | 5.592 | 9173.34 | 2.991 | 98.1 | 79 | 1440 | 20.56 | 5962.7 | 3435.7 | 3390 | 4925.2 | 1209.5 | 0.68218 | 7.077
2024-12-09 | 22:00 | Data | 0 | 30.529 | 28.038 | 236.883 | 7.62 | 221.923 | 2216.2 | 25.89 | 41.304 | 6.28 | 1.492 | 5.616 | 9168.81 | 2.775 | 98.1 | 79 | 1441 | 20.61 | 5959.7 | 3438.2 | 3390.5 | 4921.6 | 1209.5 | 0.68314 | 7.107
2024-12-09 | 22:01 | Data | 0 | 30.833 | 27.788 | 236.973 | 7.62 | 221.969 | 2223.43 | 25.88 | 41.304 | 6.28 | 1.5 | 5.592 | 9173.34 | 2.903 | 98.1 | 78.8 | 1445 | 20.65 | 5962.7 | 3434.3 | 3396.6 | 4923.3 | 1209.5 | 0.68243 | 7.093
2024-12-09 | 22:01 | Data | 0 | 30.529 | 28.038 | 237.064 | 7.62 | 221.923 | 2222.52 | 25.88 | 41.304 | 6.28 | 1.498 | 5.591 | 9182.38 | 2.815 | 98.1 | 78.8 | 1445 | 20.65 | 5968.5 | 3433.8 | 3382.4 | 4915.3 | 1209.5 | 0.68257 | 7.089
2024-12-09 | 22:01 | Data | 0 | 31.022 | 27.748 | 237.064 | 7.62 | 222.059 | 2225.23 | 25.88 | 41.213 | 6.28 | 1.503 | 5.582 | 9159.77 | 2.971 | 98.2 | 78.8 | 1446 | 20.61 | 5953.9 | 3417.6 | 3401.6 | 4917.2 | 1209.5 | 0.67993 | 7.086
2024-12-09 | 22:01 | Data | 0 | 30.415 | 27.43 | 236.837 | 7.62 | 221.833 | 2226.14 | 25.89 | 41.033 | 6.28 | 1.494 | 5.594 | 9159.77 | 2.957 | 98.2 | 78.9 | 1446 | 20.52 | 5953.9 | 3424.6 | 3375.3 | 4899.4 | 1209.5 | 0.68382 | 7.088
2024-12-09 | 22:01 | Data | 0 | 30.637 | 27.829 | 236.883 | 7.62 | 221.878 | 2225.23 | 25.89 | 41.033 | 6.29 | 1.492 | 5.601 | 9155.25 | 2.998 | 98.2 | 79 | 1446 | 20.52 | 5950.9 | 3445.7 | 3411.2 | 4943.8 | 1209.5 | 0.68047 | 7.093
2024-12-09 | 22:01 | Data | 0 | 30.185 | 27.626 | 236.837 | 7.62 | 221.923 | 2227.04 | 25.88 | 40.943 | 6.29 | 1.487 | 5.612 | 9146.2 | 2.788 | 98.2 | 79.1 | 1448 | 20.52 | 5945 | 3434.1 | 3379.9 | 4908.7 | 1209.5 | 0.6849 | 7.098
2024-12-09 | 22:01 | Data | 0 | 30.536 | 28.065 | 237.064 | 7.62 | 221.923 | 2227.95 | 25.88 | 41.213 | 6.29 | 1.494 | 5.612 | 9100.98 | 2.815 | 98.2 | 79 | 1448 | 20.61 | 5915.6 | 3423.1 | 3385.4 | 4907.4 | 1209.5 | 0.68293 | 7.108
2024-12-09 | 22:01 | Data | 0 | 30.32 | 27.43 | 236.973 | 7.62 | 221.923 | 2228.85 | 25.88 | 41.033 | 6.28 | 1.501 | 5.614 | 9105.5 | 2.768 | 98.2 | 78.9 | 1448 | 20.52 | 5918.6 | 3419.5 | 3414 | 4931.1 | 1209.5 | 0.67837 | 7.115
2024-12-09 | 22:01 | Data | 0 | 30.651 | 27.876 | 236.973 | 7.62 | 221.969 | 2227.04 | 25.89 | 41.304 | 6.28 | 1.499 | 5.61 | 9119.07 | 2.782 | 98.1 | 78.9 | 1448 | 20.65 | 5927.4 | 3413.1 | 3393.5 | 4910.2 | 1209.5 | 0.67891 | 7.107
2024-12-09 | 22:01 | Data | 0 | 30.874 | 27.606 | 236.973 | 7.62 | 221.923 | 2227.95 | 25.88 | 41.213 | 6.28 | 1.496 | 5.619 | 9128.11 | 2.768 | 98.2 | 79 | 1448 | 20.61 | 5933.3 | 3426.6 | 3411.9 | 4930.1 | 1209.5 | 0.68005 | 7.115
2024-12-09 | 22:01 | Data | 0 | 30.543 | 27.626 | 237.018 | 7.62 | 222.059 | 2223.43 | 25.88 | 40.852 | 6.28 | 1.5 | 5.577 | 9173.34 | 2.896 | 98.2 | 78.8 | 1445 | 20.47 | 5962.7 | 3421.6 | 3423.3 | 4930.8 | 1209.5 | 0.67913 | 7.076
2024-12-09 | 22:01 | Data | 0 | 30.651 | 27.66 | 236.973 | 7.62 | 221.833 | 2221.62 | 25.88 | 41.213 | 6.28 | 1.495 | 5.591 | 9128.11 | 2.971 | 98.1 | 78.9 | 1445 | 20.61 | 5933.3 | 3419.6 | 3437.6 | 4944.1 | 1209.5 | 0.67814 | 7.085
2024-12-09 | 22:01 | Data | 0 | 29.976 | 27.417 | 236.837 | 7.62 | 221.969 | 2229.75 | 25.88 | 41.123 | 6.28 | 1.497 | 5.597 | 9105.5 | 2.728 | 98.1 | 78.9 | 1449 | 20.61 | 5918.6 | 3436 | 3423.8 | 4946.5 | 1209.5 | 0.67693 | 7.094
2024-12-09 | 22:01 | Data | 0 | 30.415 | 27.599 | 236.973 | 7.62 | 221.923 | 2230.66 | 25.88 | 41.304 | 6.28 | 1.498 | 5.604 | 9132.64 | 2.984 | 98.1 | 78.9 | 1450 | 20.65 | 5936.2 | 3418.8 | 3420.5 | 4927.8 | 1209.5 | 0.67965 | 7.102
2024-12-09 | 22:01 | Data | 0 | 30.671 | 27.667 | 236.928 | 7.62 | 221.923 | 2230.66 | 25.88 | 41.213 | 6.28 | 1.505 | 5.608 | 9132.64 | 2.836 | 98.1 | 78.8 | 1450 | 20.65 | 5936.2 | 3445.2 | 3390.8 | 4935.8 | 1209.5 | 0.68431 | 7.113
2024-12-09 | 22:01 | Data | 0 | 30.415 | 27.957 | 236.747 | 7.62 | 221.833 | 2232.47 | 25.86 | 41.213 | 6.28 | 1.502 | 5.596 | 9132.64 | 2.667 | 98.1 | 78.8 | 1451 | 20.61 | 5936.2 | 3429.7 | 3381.3 | 4910.7 | 1209.5 | 0.6833 | 7.098
2024-12-09 | 22:01 | Data | 0 | 30.415 | 27.93 | 236.973 | 7.62 | 221.923 | 2232.47 | 25.89 | 41.123 | 6.28 | 1.505 | 5.573 | 9128.11 | 2.809 | 98.2 | 78.7 | 1451 | 20.56 | 5933.3 | 3438.6 | 3429.5 | 4952.2 | 1209.5 | 0.67943 | 7.077
2024-12-09 | 22:01 | Data | 0 | 30.739 | 27.923 | 237.064 | 7.62 | 222.059 | 2229.75 | 25.88 | 41.394 | 6.28 | 1.505 | 5.596 | 9159.77 | 2.768 | 98.1 | 78.8 | 1450 | 20.65 | 5953.9 | 3435.2 | 3397.6 | 4925.5 | 1209.5 | 0.68241 | 7.102
2024-12-09 | 22:02 | Data | 0 | 30.307 | 27.424 | 236.928 | 7.62 | 221.833 | 2235.18 | 25.89 | 41.213 | 6.29 | 1.496 | 5.585 | 9177.86 | 2.795 | 98.2 | 78.9 | 1452 | 20.65 | 5965.6 | 3430.3 | 3411.3 | 4935 | 1209.5 | 0.67956 | 7.081
2024-12-09 | 22:02 | Data | 0 | 30.624 | 27.565 | 237.154 | 7.62 | 221.969 | 2234.27 | 25.88 | 41.213 | 6.28 | 1.496 | 5.583 | 9200.47 | 2.876 | 98.2 | 78.9 | 1452 | 20.65 | 5980.3 | 3426.6 | 3412.2 | 4931.6 | 1209.5 | 0.67878 | 7.078
2024-12-09 | 22:02 | Data | 0 | 30.421 | 27.424 | 236.837 | 7.62 | 221.923 | 2232.47 | 25.89 | 41.213 | 6.28 | 1.488 | 5.605 | 9191.43 | 2.991 | 98.1 | 79 | 1451 | 20.65 | 5974.4 | 3439.8 | 3449.4 | 4967 | 1209.6 | 0.67683 | 7.091
2024-12-09 | 22:02 | Data | 0 | 30.637 | 27.707 | 236.792 | 7.62 | 221.923 | 2226.14 | 25.88 | 41.304 | 6.28 | 1.494 | 5.611 | 9182.38 | 2.883 | 98.1 | 79 | 1447 | 20.61 | 5968.5 | 3425.5 | 3426.2 | 4936.2 | 1209.6 | 0.67997 | 7.106
2024-12-09 | 22:02 | Data | 0 | 30.455 | 27.538 | 236.837 | 7.62 | 221.969 | 2230.66 | 25.86 | 41.304 | 6.29 | 1.498 | 5.598 | 9132.64 | 2.788 | 98.2 | 78.9 | 1450 | 20.65 | 5936.2 | 3427.8 | 3473.8 | 4976.3 | 1209.6 | 0.67578 | 7.096
2024-12-09 | 22:02 | Data | 0 | 30.34 | 28.038 | 237.018 | 7.62 | 222.149 | 2227.04 | 25.88 | 41.033 | 6.28 | 1.496 | 5.566 | 9110.03 | 2.545 | 98.2 | 78.8 | 1448 | 20.52 | 5921.5 | 3421.8 | 3476.9 | 4971.8 | 1209.6 | 0.6727 | 7.063
2024-12-09 | 22:02 | Data | 0 | 30.448 | 27.457 | 236.883 | 7.62 | 221.969 | 2227.04 | 25.88 | 40.943 | 6.28 | 1.501 | 5.584 | 9132.64 | 2.869 | 98.2 | 78.8 | 1448 | 20.47 | 5936.2 | 3432.3 | 3432.5 | 4949.4 | 1209.6 | 0.67814 | 7.085
2024-12-09 | 22:02 | Data | 0 | 30.55 | 27.788 | 237.018 | 7.62 | 222.059 | 2229.75 | 25.88 | 40.943 | 6.29 | 1.504 | 5.565 | 9128.11 | 2.802 | 98.2 | 78.7 | 1448 | 20.47 | 5933.3 | 3428.3 | 3433.4 | 4941.5 | 1209.6 | 0.67736 | 7.068
2024-12-09 | 22:02 | Data | 0 | 30.435 | 27.768 | 236.928 | 7.62 | 222.059 | 2225.23 | 25.89 | 41.033 | 6.28 | 1.506 | 5.593 | 9168.81 | 2.768 | 98.2 | 78.8 | 1446 | 20.43 | 5959.7 | 3418.3 | 3429.9 | 4935.7 | 1209.6 | 0.67775 | 7.099
2024-12-09 | 22:02 | Data | 0 | 30.205 | 27.984 | 236.973 | 7.62 | 221.969 | 2225.23 | 25.88 | 41.033 | 6.28 | 1.504 | 5.6 | 8757.29 | 2.66 | 98.2 | 78.8 | 1446 | 20.56 | 5692.2 | 3443.4 | 3380.6 | 4922.3 | 1209.6 | 0.68475 | 7.106
2024-12-09 | 22:02 | Data | 0 | 30.408 | 27.863 | 236.883 | 7.63 | 221.923 | 2225.23 | 25.88 | 41.033 | 6.28 | 1.515 | 5.615 | 8752.77 | 2.795 | 98.2 | 78.8 | 1447 | 20.47 | 5689.3 | 3440.5 | 3410.6 | 4938.8 | 1209.6 | 0.68097 | 7.13
2024-12-09 | 22:02 | Data | 0 | 30.489 | 28.038 | 236.973 | 7.62 | 221.923 | 2225.23 | 25.88 | 40.852 | 6.28 | 1.496 | 5.616 | 9186.9 | 2.592 | 98.2 | 79 | 1446 | 20.52 | 5971.5 | 3440.2 | 3375.9 | 4913 | 1209.6 | 0.68417 | 7.113
2024-12-09 | 22:02 | Data | 0 | 30.482 | 27.647 | 236.928 | 7.62 | 222.059 | 2225.23 | 25.89 | 41.033 | 6.28 | 1.5 | 5.595 | 9241.17 | 2.579 | 98.2 | 78.9 | 1446 | 20.52 | 6006.8 | 3427.2 | 3398.9 | 4918.5 | 1209.6 | 0.68182 | 7.096
2024-12-09 | 22:02 | Data | 0 | 30.766 | 27.498 | 237.064 | 7.62 | 222.059 | 2225.23 | 25.88 | 41.033 | 6.28 | 1.509 | 5.593 | 9232.13 | 2.977 | 98.2 | 78.7 | 1446 | 20.52 | 6000.9 | 3430.8 | 3405.5 | 4929.3 | 1209.6 | 0.68099 | 7.103
2024-12-09 | 22:02 | Data | 0 | 30.421 | 27.964 | 236.973 | 7.62 | 222.104 | 2225.23 | 25.88 | 41.033 | 6.28 | 1.513 | 5.561 | 9223.08 | 2.559 | 98.2 | 78.6 | 1446 | 20.52 | 5995 | 3420.3 | 3425.5 | 4934.7 | 1209.6 | 0.67736 | 7.074
2024-12-09 | 22:02 | Data | 0 | 30.739 | 28.025 | 236.973 | 7.63 | 221.969 | 2225.23 | 25.89 | 41.033 | 6.29 | 1.495 | 5.601 | 9254.74 | 2.876 | 98.2 | 78.9 | 1447 | 20.47 | 6015.6 | 3421.2 | 3428 | 4937.3 | 1209.6 | 0.67779 | 7.095
2024-12-09 | 22:02 | Data | 0 | 30.259 | 27.653 | 236.928 | 7.62 | 222.104 | 2225.23 | 25.89 | 40.943 | 6.28 | 1.493 | 5.62 | 9227.6 | 2.68 | 98.2 | 79 | 1446 | 20.52 | 5997.9 | 3431.6 | 3446.5 | 4955.8 | 1209.6 | 0.67744 | 7.114
2024-12-09 | 22:02 | Data | 0 | 30.334 | 27.451 | 236.928 | 7.62 | 221.923 | 2224.33 | 25.88 | 41.213 | 6.28 | 1.489 | 5.582 | 9241.17 | 2.721 | 98.1 | 78.9 | 1446 | 20.61 | 6006.8 | 3439.4 | 3448.4 | 4963.2 | 1209.6 | 0.6775 | 7.07
2024-12-09 | 22:03 | Data | 0 | 30.475 | 27.538 | 236.883 | 7.62 | 221.878 | 2222.52 | 25.88 | 41.033 | 6.28 | 1.496 | 5.611 | 9250.21 | 2.883 | 98.2 | 79 | 1445 | 20.52 | 6012.6 | 3415 | 3448.1 | 4944.7 | 1209.6 | 0.67508 | 7.107
2024-12-09 | 22:03 | Data | 0 | 30.428 | 27.606 | 236.928 | 7.62 | 221.878 | 2222.52 | 25.88 | 41.033 | 6.28 | 1.495 | 5.635 | 9259.26 | 2.971 | 98.2 | 79 | 1445 | 20.47 | 6018.5 | 3434.8 | 3442.7 | 4957.2 | 1209.6 | 0.67731 | 7.129
2024-12-09 | 22:03 | Data | 0 | 30.752 | 27.991 | 236.973 | 7.62 | 222.149 | 2224.33 | 25.89 | 41.033 | 6.28 | 1.487 | 5.611 | 9250.21 | 2.775 | 98.2 | 79.1 | 1446 | 20.47 | 6012.6 | 3448 | 3436.9 | 4962.7 | 1209.6 | 0.68003 | 7.099
2024-12-09 | 22:03 | Data | 0 | 30.651 | 28.079 | 236.837 | 7.62 | 221.923 | 2222.52 | 25.88 | 41.033 | 6.29 | 1.5 | 5.612 | 9223.08 | 2.775 | 98.2 | 78.9 | 1445 | 20.52 | 5995 | 3416.1 | 3400.7 | 4917.3 | 1209.6 | 0.67914 | 7.114
2024-12-09 | 22:03 | Data | 0 | 30.198 | 27.626 | 236.928 | 7.62 | 221.923 | 2218.91 | 25.88 | 41.033 | 6.27 | 1.5 | 5.609 | 9227.6 | 2.674 | 98.2 | 78.9 | 1442 | 20.52 | 5997.9 | 3430.6 | 3429.4 | 4946 | 1209.6 | 0.67821 | 7.109
2024-12-09 | 22:03 | Data | 0 | 30.847 | 27.674 | 236.928 | 7.62 | 222.059 | 2218.91 | 25.88 | 41.033 | 6.28 | 1.497 | 5.582 | 9227.6 | 3.065 | 98.2 | 78.9 | 1443 | 20.43 | 5997.9 | 3431 | 3402.4 | 4925.6 | 1209.6 | 0.68129 | 7.077
2024-12-09 | 22:03 | Data | 0 | 30.745 | 27.869 | 236.973 | 7.62 | 222.104 | 2218 | 25.89 | 41.033 | 6.28 | 1.486 | 5.6 | 9218.56 | 2.856 | 98.2 | 79 | 1442 | 20.47 | 5992.1 | 3424.7 | 3413.6 | 4928.2 | 1209.6 | 0.6794 | 7.086
2024-12-09 | 22:03 | Data | 0 | 30.401 | 27.653 | 236.928 | 7.63 | 221.969 | 2222.52 | 25.89 | 40.943 | 6.29 | 1.497 | 5.616 | 9241.17 | 2.937 | 98.2 | 78.9 | 1445 | 20.47 | 6006.8 | 3458.2 | 3408.5 | 4943.6 | 1209.6 | 0.68165 | 7.114
2024-12-09 | 22:03 | Data | 0 | 30.435 | 27.707 | 237.018 | 7.62 | 221.923 | 2225.23 | 25.88 | 41.304 | 6.28 | 1.499 | 5.612 | 9254.74 | 2.565 | 98.1 | 78.9 | 1446 | 20.65 | 6015.6 | 3426.2 | 3440.3 | 4964.6 | 1209.6 | 0.67674 | 7.111
2024-12-09 | 22:03 | Data | 0 | 30.867 | 27.937 | 237.018 | 7.62 | 222.059 | 2225.23 | 25.89 | 41.213 | 6.28 | 1.497 | 5.591 | 9241.17 | 2.829 | 98.1 | 78.9 | 1446 | 20.65 | 6006.8 | 3437 | 3453 | 4966 | 1209.6 | 0.67686 | 7.087
2024-12-09 | 22:03 | Data | 0 | 30.475 | 27.667 | 236.747 | 7.62 | 221.878 | 2225.23 | 25.89 | 41.213 | 6.28 | 1.496 | 5.585 | 9227.6 | 2.748 | 98.1 | 78.9 | 1446 | 20.61 | 5997.9 | 3411.3 | 3454.5 | 4953.6 | 1209.6 | 0.67313 | 7.081
2024-12-09 | 22:03 | Data | 0 | 30.658 | 27.707 | 237.064 | 7.62 | 221.969 | 2224.33 | 25.89 | 41.213 | 6.28 | 1.498 | 5.615 | 9218.56 | 2.606 | 98.1 | 79 | 1446 | 20.65 | 5992.1 | 3434.2 | 3474.5 | 4982 | 1209.6 | 0.67368 | 7.112
2024-12-09 | 22:03 | Data | 0 | 30.617 | 27.869 | 236.973 | 7.62 | 222.059 | 2225.23 | 25.88 | 41.213 | 6.28 | 1.502 | 5.602 | 9218.56 | 3.018 | 98.1 | 78.9 | 1447 | 20.56 | 5992.1 | 3425.7 | 3472.7 | 4975 | 1209.6 | 0.67347 | 7.105
2024-12-09 | 22:03 | Data | 0 | 30.442 | 27.829 | 237.018 | 7.62 | 222.059 | 2225.23 | 25.89 | 41.304 | 6.28 | 1.507 | 5.562 | 9227.6 | 2.896 | 98.1 | 78.7 | 1446 | 20.65 | 5997.9 | 3454.5 | 3449.3 | 4973.8 | 1209.6 | 0.67713 | 7.069
2024-12-09 | 22:03 | Data | 0 | 30.644 | 27.775 | 237.018 | 7.62 | 222.24 | 2225.23 | 25.89 | 41.304 | 6.28 | 1.499 | 5.582 | 9232.13 | 3.079 | 98.1 | 78.8 | 1448 | 20.61 | 6000.9 | 3434.8 | 3408.7 | 4933.3 | 1209.6 | 0.67978 | 7.08
2024-12-09 | 22:03 | Data | 0 | 30.415 | 28.025 | 236.792 | 7.61 | 221.969 | 2226.14 | 25.88 | 41.304 | 6.28 | 1.502 | 5.622 | 9186.9 | 2.653 | 98.1 | 78.9 | 1447 | 20.65 | 5971.5 | 3427.1 | 3385.4 | 4910.5 | 1209.7 | 0.68228 | 7.125
2024-12-09 | 22:03 | Data | 0 | 30.415 | 27.653 | 236.883 | 7.62 | 221.923 | 2224.33 | 25.88 | 41.304 | 6.29 | 1.497 | 5.606 | 9200.47 | 2.775 | 98.1 | 78.9 | 1446 | 20.65 | 5980.3 | 3434 | 3392.6 | 4920.9 | 1209.7 | 0.68264 | 7.106
2024-12-09 | 22:04 | Data | 0 | 30.415 | 27.424 | 236.883 | 7.62 | 221.969 | 2227.95 | 25.88 | 41.304 | 6.29 | 1.5 | 5.574 | 9200.47 | 2.991 | 98.1 | 78.8 | 1448 | 20.65 | 5980.3 | 3445.2 | 3436.4 | 4961.3 | 1209.7 | 0.6791 | 7.075
2024-12-09 | 22:04 | Data | 0 | 30.867 | 27.795 | 237.154 | 7.62 | 222.059 | 2225.23 | 25.88 | 41.213 | 6.28 | 1.502 | 5.574 | 9200.47 | 2.883 | 98.1 | 78.8 | 1446 | 20.65 | 5980.3 | 3447 | 3449.7 | 4971.5 | 1209.7 | 0.67921 | 7.075
2024-12-09 | 22:04 | Data | 0 | 30.428 | 27.653 | 236.973 | 7.62 | 221.969 | 2225.23 | 25.89 | 41.304 | 6.28 | 1.501 | 5.585 | 8743.73 | 2.761 | 98.1 | 78.8 | 1446 | 20.56 | 5683.4 | 3459.2 | 3477.2 | 4999.1 | 1209.7 | 0.67691 | 7.087
2024-12-09 | 22:04 | Data | 0 | 30.759 | 27.518 | 236.928 | 7.62 | 222.104 | 2222.52 | 25.88 | 41.304 | 6.28 | 1.499 | 5.585 | 9159.77 | 3.025 | 98.1 | 78.9 | 1445 | 20.61 | 5953.9 | 3454.4 | 3508.5 | 5010 | 1209.7 | 0.67567 | 7.083
2024-12-09 | 22:04 | Data | 0 | 30.442 | 27.64 | 236.928 | 7.62 | 221.878 | 2225.23 | 25.89 | 41.304 | 6.28 | 1.49 | 5.598 | 9159.77 | 2.66 | 98.1 | 79 | 1446 | 20.65 | 5953.9 | 3461.2 | 3511 | 5024 | 1209.7 | 0.67377 | 7.087
2024-12-09 | 22:04 | Data | 0 | 30.509 | 27.66 | 237.29 | 7.62 | 222.195 | 2227.95 | 25.88 | 41.213 | 6.28 | 1.499 | 5.583 | 9159.77 | 2.775 | 98.2 | 78.8 | 1448 | 20.65 | 5953.9 | 3456.2 | 3488.3 | 5004.3 | 1209.7 | 0.67468 | 7.081
2024-12-09 | 22:04 | Data | 0 | 30.529 | 27.498 | 237.018 | 7.62 | 222.104 | 2227.04 | 25.89 | 41.304 | 6.28 | 1.497 | 5.571 | 9227.6 | 2.876 | 98.1 | 78.8 | 1448 | 20.65 | 5997.9 | 3440.3 | 3476.8 | 4986.7 | 1209.7 | 0.67436 | 7.068
2024-12-09 | 22:04 | Data | 0 | 30.415 | 27.532 | 236.792 | 7.62 | 221.878 | 2227.04 | 25.89 | 41.213 | 6.28 | 1.492 | 5.598 | 9263.78 | 2.775 | 98.2 | 79 | 1448 | 20.61 | 6021.5 | 3436.5 | 3471.1 | 4984.7 | 1209.7 | 0.67352 | 7.089
2024-12-09 | 22:04 | Data | 0 | 30.192 | 27.849 | 236.928 | 7.62 | 221.969 | 2227.95 | 25.88 | 41.304 | 6.29 | 1.502 | 5.595 | 9281.87 | 2.748 | 98.2 | 78.8 | 1448 | 20.61 | 6033.2 | 3458.4 | 3445.1 | 4977.6 | 1209.7 | 0.68009 | 7.097
2024-12-09 | 22:04 | Data | 0 | 30.583 | 27.856 | 236.973 | 7.62 | 222.059 | 2230.66 | 25.88 | 41.304 | 6.28 | 1.501 | 5.601 | 9277.35 | 2.788 | 98.1 | 78.9 | 1449 | 20.61 | 6030.3 | 3467.6 | 3438.1 | 4980.3 | 1209.7 | 0.68105 | 7.101
2024-12-09 | 22:04 | Data | 0 | 30.887 | 27.728 | 236.883 | 7.62 | 222.104 | 2229.75 | 25.88 | 41.213 | 6.29 | 1.496 | 5.621 | 9232.13 | 2.836 | 98.2 | 79 | 1450 | 20.61 | 6000.9 | 3466.8 | 3437.4 | 4979.3 | 1209.7 | 0.68184 | 7.119
2024-12-09 | 22:04 | Data | 0 | 30.523 | 27.93 | 237.018 | 7.62 | 222.149 | 2227.95 | 25.88 | 41.213 | 6.28 | 1.49 | 5.615 | 9232.13 | 2.856 | 98.1 | 79 | 1448 | 20.65 | 6000.9 | 3466.5 | 3450.7 | 4991 | 1209.7 | 0.67827 | 7.106
2024-12-09 | 22:04 | Data | 0 | 30.361 | 27.552 | 237.064 | 7.62 | 221.878 | 2227.95 | 25.89 | 41.213 | 6.28 | 1.489 | 5.598 | 9227.6 | 2.755 | 98.1 | 79 | 1448 | 20.61 | 5997.9 | 3474.4 | 3451 | 4990.1 | 1209.7 | 0.68106 | 7.087
2024-12-09 | 22:04 | Data | 0 | 31.076 | 27.795 | 237.018 | 7.62 | 222.149 | 2227.95 | 25.89 | 41.304 | 6.28 | 1.505 | 5.603 | 9241.17 | 2.977 | 98.1 | 78.9 | 1448 | 20.65 | 6006.8 | 3465 | 3480.8 | 5009.6 | 1209.7 | 0.67578 | 7.107
2024-12-09 | 22:04 | Data | 0 | 30.867 | 27.842 | 237.064 | 7.62 | 221.969 | 2227.95 | 25.88 | 41.033 | 6.28 | 1.502 | 5.601 | 9245.69 | 3.079 | 98.2 | 78.9 | 1448 | 20.52 | 6009.7 | 3467.4 | 3519 | 5039.9 | 1209.7 | 0.67263 | 7.102
2024-12-09 | 22:04 | Data | 0 | 30.523 | 27.491 | 236.928 | 7.62 | 221.969 | 2236.08 | 25.86 | 40.943 | 6.28 | 1.495 | 5.596 | 9245.69 | 2.842 | 98.2 | 78.9 | 1454 | 20.47 | 6009.7 | 3449.7 | 3492.8 | 5009.8 | 1209.7 | 0.67311 | 7.089
2024-12-09 | 22:04 | Data | 0 | 30.313 | 27.599 | 237.018 | 7.62 | 221.923 | 2232.47 | 25.89 | 41.033 | 6.28 | 1.497 | 5.617 | 9223.08 | 2.768 | 98.2 | 78.9 | 1451 | 20.52 | 5995 | 3468.3 | 3490.2 | 5016.6 | 1209.7 | 0.67324 | 7.115
2024-12-09 | 22:04 | Data | 0 | 30.651 | 27.498 | 236.928 | 7.62 | 221.923 | 2228.85 | 25.89 | 40.943 | 6.28 | 1.5 | 5.599 | 9209.51 | 2.93 | 98.2 | 78.9 | 1449 | 20.47 | 5986.2 | 3473.9 | 3477.8 | 5013.2 | 1209.7 | 0.67642 | 7.098
2024-12-09 | 22:05 | Data | 0 | 30.617 | 28.018 | 237.064 | 7.62 | 222.149 | 2221.62 | 25.88 | 40.943 | 6.29 | 1.502 | 5.584 | 9209.51 | 2.613 | 98.2 | 78.8 | 1444 | 20.52 | 5986.2 | 3473.8 | 3489.1 | 5022.1 | 1209.7 | 0.67502 | 7.086
2024-12-09 | 22:05 | Data | 0 | 30.192 | 27.647 | 236.883 | 7.62 | 221.969 | 2226.14 | 25.88 | 40.943 | 6.28 | 1.49 | 5.609 | 9195.95 | 2.748 | 98.2 | 79 | 1447 | 20.47 | 5977.4 | 3465 | 3464.8 | 4996.3 | 1209.7 | 0.67745 | 7.096
2024-12-09 | 22:05 | Data | 0 | 30.205 | 27.484 | 237.018 | 7.62 | 221.833 | 2227.95 | 25.89 | 41.033 | 6.28 | 1.482 | 5.628 | 9186.9 | 2.701 | 98.2 | 79.2 | 1448 | 20.52 | 5971.5 | 3461.7 | 3430 | 4971.6 | 1209.7 | 0.68086 | 7.11
2024-12-09 | 22:05 | Data | 0 | 30.415 | 28.031 | 236.928 | 7.62 | 222.059 | 2227.95 | 25.88 | 41.033 | 6.28 | 1.498 | 5.623 | 9182.38 | 2.748 | 98.2 | 79 | 1448 | 20.52 | 5968.5 | 3461.9 | 3459.7 | 4992 | 1209.7 | 0.67744 | 7.121
2024-12-09 | 22:05 | Data | 0 | 30.421 | 27.653 | 236.928 | 7.62 | 222.059 | 2227.95 | 25.88 | 40.943 | 6.28 | 1.495 | 5.604 | 9195.95 | 2.761 | 98.2 | 78.9 | 1448 | 20.52 | 5977.4 | 3460.2 | 3475.4 | 4999.5 | 1209.7 | 0.67685 | 7.101
2024-12-09 | 22:05 | Data | 0 | 30.523 | 27.768 | 236.973 | 7.62 | 221.878 | 2224.33 | 25.89 | 40.943 | 6.28 | 1.497 | 5.601 | 9191.43 | 2.964 | 98.2 | 78.9 | 1446 | 20.52 | 5974.4 | 3441.7 | 3467.6 | 4985.7 | 1209.7 | 0.67507 | 7.097
2024-12-09 | 22:05 | Data | 0 | 30.766 | 27.687 | 237.109 | 7.62 | 222.104 | 2221.62 | 25.89 | 40.852 | 6.28 | 1.503 | 5.578 | 9218.56 | 2.761 | 98.2 | 78.8 | 1445 | 20.47 | 5992.1 | 3466.6 | 3502.8 | 5023.6 | 1209.7 | 0.67453 | 7.081
2024-12-09 | 22:05 | Data | 0 | 30.415 | 27.903 | 236.973 | 7.62 | 221.878 | 2222.52 | 25.89 | 40.943 | 6.28 | 1.505 | 5.563 | 9195.95 | 2.626 | 98.2 | 78.7 | 1444 | 20.47 | 5977.4 | 3457.1 | 3473.4 | 5000.7 | 1209.7 | 0.67537 | 7.068
2024-12-09 | 22:05 | Data | 0 | 30.651 | 28.146 | 237.109 | 7.62 | 222.104 | 2228.85 | 25.88 | 41.033 | 6.29 | 1.5 | 5.568 | 9195.95 | 2.883 | 98.2 | 78.8 | 1450 | 20.52 | 5977.4 | 3456.7 | 3464.8 | 4996.2 | 1209.7 | 0.67554 | 7.068
2024-12-09 | 22:05 | Data | 0 | 30.806 | 27.984 | 236.973 | 7.62 | 221.923 | 2225.23 | 25.88 | 41.213 | 6.28 | 1.503 | 5.582 | 9177.86 | 2.782 | 98.1 | 78.8 | 1446 | 20.65 | 5965.6 | 3450.6 | 3467.5 | 4989.9 | 1209.7 | 0.67551 | 7.085
2024-12-09 | 22:05 | Data | 0 | 30.361 | 27.829 | 236.973 | 7.62 | 222.059 | 2225.23 | 25.89 | 41.304 | 6.28 | 1.5 | 5.577 | 9209.51 | 2.788 | 98.1 | 78.8 | 1446 | 20.61 | 5986.2 | 3391.3 | 3434.1 | 4918.4 | 1209.7 | 0.67469 | 7.078
2024-12-09 | 22:05 | Data | 0 | 30.577 | 27.964 | 236.928 | 7.62 | 221.878 | 2222.52 | 25.89 | 41.213 | 6.28 | 1.499 | 5.595 | 9186.9 | 2.802 | 98.1 | 78.9 | 1445 | 20.56 | 5971.5 | 3387.8 | 3446.4 | 4922.4 | 1209.8 | 0.67296 | 7.093
2024-12-09 | 22:05 | Data | 0 | 30.415 | 27.43 | 236.837 | 7.62 | 221.833 | 2221.62 | 25.89 | 41.213 | 6.28 | 1.503 | 5.62 | 9177.86 | 2.984 | 98.1 | 78.9 | 1443 | 20.65 | 5965.6 | 3394.5 | 3416 | 4908.8 | 1209.8 | 0.67672 | 7.122
2024-12-09 | 22:05 | Data | 0 | 30.806 | 27.464 | 236.973 | 7.62 | 222.149 | 2222.52 | 25.88 | 41.213 | 6.28 | 1.503 | 5.605 | 9182.38 | 2.849 | 98.1 | 78.9 | 1444 | 20.65 | 5968.5 | 3386.8 | 3404.9 | 4894 | 1209.8 | 0.67664 | 7.106
2024-12-09 | 22:05 | Data | 0 | 30.063 | 27.626 | 236.973 | 7.62 | 221.878 | 2217.1 | 25.86 | 41.304 | 6.28 | 1.494 | 5.564 | 9186.9 | 2.606 | 98.1 | 78.8 | 1441 | 20.65 | 5971.5 | 3399.1 | 3422 | 4917 | 1209.8 | 0.67622 | 7.058
2024-12-09 | 22:05 | Data | 0 | 30.59 | 28.038 | 237.018 | 7.62 | 222.059 | 2216.2 | 25.88 | 41.213 | 6.29 | 1.507 | 5.599 | 9177.86 | 2.802 | 98.1 | 78.8 | 1441 | 20.65 | 5965.6 | 3380.5 | 3411.2 | 4896.6 | 1209.8 | 0.67507 | 7.105
2024-12-09 | 22:05 | Data | 0 | 30.415 | 27.856 | 236.883 | 7.62 | 221.923 | 2217.1 | 25.88 | 41.213 | 6.28 | 1.495 | 5.591 | 9177.86 | 2.856 | 98.1 | 78.9 | 1441 | 20.56 | 5965.6 | 3393 | 3411.3 | 4904.5 | 1209.8 | 0.67693 | 7.086
2024-12-09 | 22:05 | Data | 0 | 31.029 | 27.674 | 236.883 | 7.62 | 222.059 | 2215.29 | 25.88 | 41.213 | 6.28 | 1.492 | 5.582 | 9146.2 | 2.903 | 98.1 | 78.9 | 1440 | 20.65 | 5945 | 3373.5 | 3459.4 | 4926 | 1209.8 | 0.66973 | 7.075
2024-12-09 | 22:06 | Data | 0 | 30.192 | 27.43 | 236.747 | 7.62 | 221.923 | 2216.2 | 25.86 | 41.213 | 6.28 | 1.498 | 5.593 | 9150.73 | 2.863 | 98.1 | 78.9 | 1440 | 20.65 | 5948 | 3411.9 | 3447.3 | 4945.7 | 1209.8 | 0.67429 | 7.091
2024-12-09 | 22:06 | Data | 0 | 30.529 | 27.822 | 236.747 | 7.62 | 221.923 | 2216.2 | 25.88 | 41.304 | 6.28 | 1.512 | 5.602 | 9159.77 | 2.815 | 98.1 | 78.7 | 1441 | 20.65 | 5953.9 | 3444.6 | 3446.2 | 4969.5 | 1209.8 | 0.67772 | 7.115
2024-12-09 | 22:06 | Data | 0 | 30.286 | 27.592 | 237.018 | 7.63 | 221.743 | 2218.91 | 25.88 | 41.213 | 6.29 | 1.505 | 5.587 | 9168.81 | 2.91 | 98.1 | 78.8 | 1442 | 20.61 | 5959.7 | 3444.4 | 3435 | 4958.6 | 1209.8 | 0.67942 | 7.092
2024-12-09 | 22:06 | Data | 0 | 30.651 | 27.883 | 236.792 | 7.62 | 221.969 | 2218.91 | 25.88 | 41.213 | 6.28 | 1.494 | 5.581 | 9155.25 | 2.768 | 98.1 | 78.9 | 1442 | 20.61 | 5950.9 | 3445.3 | 3440.6 | 4964.8 | 1209.8 | 0.67809 | 7.075
2024-12-09 | 22:06 | Data | 0 | 30.219 | 27.37 | 236.928 | 7.62 | 221.878 | 2221.62 | 25.88 | 41.213 | 6.28 | 1.499 | 5.567 | 9159.77 | 2.856 | 98.1 | 78.8 | 1445 | 20.65 | 5953.9 | 3437.9 | 3471.5 | 4980.9 | 1209.8 | 0.67483 | 7.066
2024-12-09 | 22:06 | Data | 0 | 30.529 | 27.43 | 236.973 | 7.62 | 221.969 | 2222.52 | 25.88 | 41.304 | 6.29 | 1.506 | 5.587 | 9173.34 | 2.991 | 98.1 | 78.8 | 1444 | 20.56 | 5962.7 | 3442.3 | 3468.3 | 4981.6 | 1209.8 | 0.67577 | 7.093
2024-12-09 | 22:06 | Data | 0 | 30.415 | 27.849 | 236.837 | 7.62 | 221.923 | 2222.52 | 25.86 | 41.304 | 6.28 | 1.501 | 5.613 | 9173.34 | 2.788 | 98.1 | 78.9 | 1445 | 20.61 | 5962.7 | 3445.4 | 3426.2 | 4950.8 | 1209.8 | 0.6814 | 7.115
2024-12-09 | 22:06 | Data | 0 | 30.219 | 27.424 | 236.928 | 7.62 | 222.059 | 2222.52 | 25.86 | 41.304 | 6.29 | 1.499 | 5.601 | 9186.9 | 2.768 | 98.1 | 78.9 | 1445 | 20.65 | 5971.5 | 3431.3 | 3452.8 | 4965.7 | 1209.8 | 0.67563 | 7.102
2024-12-09 | 22:06 | Data | 0 | 30.388 | 27.647 | 236.792 | 7.62 | 221.878 | 2225.23 | 25.88 | 41.304 | 6.28 | 1.498 | 5.583 | 9173.34 | 2.755 | 98.1 | 78.8 | 1446 | 20.65 | 5962.7 | 3453.6 | 3430.1 | 4962.8 | 1209.8 | 0.68065 | 7.081
2024-12-09 | 22:06 | Data | 0 | 30.59 | 27.66 | 236.928 | 7.63 | 221.923 | 2226.14 | 25.89 | 41.304 | 6.28 | 1.505 | 5.608 | 9186.9 | 2.633 | 98.1 | 78.8 | 1446 | 20.61 | 5971.5 | 3447.8 | 3422.8 | 4949.9 | 1209.8 | 0.68308 | 7.113
2024-12-09 | 22:06 | Data | 0 | 30.705 | 27.397 | 236.973 | 7.62 | 222.149 | 2225.23 | 25.89 | 41.304 | 6.28 | 1.504 | 5.596 | 9195.95 | 2.734 | 98.1 | 78.8 | 1447 | 20.61 | 5977.4 | 3433.4 | 3411.8 | 4938.4 | 1209.8 | 0.68074 | 7.099
2024-12-09 | 22:06 | Data | 0 | 30.165 | 27.424 | 236.747 | 7.62 | 221.833 | 2225.23 | 25.86 | 41.213 | 6.28 | 1.5 | 5.588 | 9227.6 | 2.761 | 98.1 | 78.8 | 1446 | 20.61 | 5997.9 | 3450.6 | 3414.4 | 4949.6 | 1209.8 | 0.6824 | 7.089
2024-12-09 | 22:06 | Data | 0 | 30.428 | 27.653 | 236.792 | 7.62 | 221.923 | 2223.43 | 25.86 | 41.213 | 6.28 | 1.499 | 5.561 | 9227.6 | 2.944 | 98.1 | 78.8 | 1445 | 20.61 | 5997.9 | 3440.1 | 3416.5 | 4944.1 | 1209.8 | 0.68032 | 7.06
2024-12-09 | 22:06 | Data | 0 | 30.718 | 27.565 | 236.883 | 7.62 | 222.059 | 2222.52 | 25.86 | 41.304 | 6.28 | 1.504 | 5.564 | 9227.6 | 3.038 | 98.1 | 78.7 | 1445 | 20.61 | 5997.9 | 3450.7 | 3395.3 | 4936.6 | 1209.8 | 0.68377 | 7.068
2024-12-09 | 22:06 | Data | 0 | 30.502 | 27.451 | 236.928 | 7.62 | 221.878 | 2224.33 | 25.86 | 41.304 | 6.29 | 1.507 | 5.59 | 9232.13 | 2.917 | 98.1 | 78.8 | 1446 | 20.61 | 6000.9 | 3439 | 3421.9 | 4945 | 1209.8 | 0.68051 | 7.095
2024-12-09 | 22:06 | Data | 0 | 30.415 | 27.68 | 236.837 | 7.63 | 221.969 | 2225.23 | 25.85 | 41.213 | 6.28 | 1.509 | 5.595 | 9223.08 | 2.653 | 98.2 | 78.8 | 1446 | 20.56 | 5995 | 3454.6 | 3396.2 | 4941.1 | 1209.8 | 0.68368 | 7.104
2024-12-09 | 22:06 | Data | 0 | 30.3 | 28.031 | 237.018 | 7.62 | 221.833 | 2228.85 | 25.88 | 41.394 | 6.28 | 1.493 | 5.578 | 9214.04 | 2.721 | 98.2 | 78.9 | 1448 | 20.61 | 5989.1 | 3452.8 | 3417.9 | 4954 | 1209.8 | 0.68168 | 7.072
2024-12-09 | 22:06 | Data | 0 | 30.185 | 27.741 | 236.837 | 7.62 | 221.969 | 2226.14 | 25.85 | 40.852 | 6.28 | 1.494 | 5.586 | 9227.6 | 2.822 | 98.2 | 78.9 | 1447 | 20.43 | 5997.9 | 3438.6 | 3417.6 | 4946.3 | 1209.8 | 0.67859 | 7.08
2024-12-09 | 22:07 | Data | 0 | 30.219 | 27.228 | 236.837 | 7.62 | 222.059 | 2229.75 | 25.85 | 41.304 | 6.28 | 1.506 | 5.592 | 9241.17 | 2.768 | 98.1 | 78.8 | 1450 | 20.65 | 6006.8 | 3422.6 | 3401.3 | 4917.1 | 1209.8 | 0.67837 | 7.098
2024-12-09 | 22:07 | Data | 0 | 29.388 | 26.951 | 236.34 | 7.62 | 221.336 | 2229.75 | 25.86 | 41.213 | 6.28 | 1.5 | 5.606 | 9236.65 | 2.721 | 98.1 | 78.9 | 1449 | 20.65 | 6003.8 | 3410.6 | 3408.2 | 4918.3 | 1209.8 | 0.67873 | 7.105
2024-12-09 | 22:07 | Data | 0 | 28.47 | 25.729 | 235.254 | 7.62 | 220.522 | 2232.47 | 25.86 | 41.213 | 6.28 | 1.494 | 5.595 | 9241.17 | 3.038 | 98.2 | 78.9 | 1451 | 20.61 | 6006.8 | 3414.9 | 3450.4 | 4947.2 | 1209.8 | 0.67555 | 7.089
2024-12-09 | 22:07 | Data | 0 | 28.2 | 25.142 | 234.983 | 7.62 | 220.206 | 2229.75 | 25.86 | 41.304 | 6.28 | 1.5 | 5.56 | 9254.74 | 3.038 | 98.1 | 78.8 | 1449 | 20.65 | 6015.6 | 3442.6 | 3420 | 4948.6 | 1209.8 | 0.68022 | 7.06
2024-12-09 | 22:07 | Data | 0 | 27.316 | 24.743 | 234.892 | 7.62 | 220.161 | 2230.66 | 25.88 | 41.304 | 6.29 | 1.486 | 5.529 | 9223.08 | 2.883 | 98.2 | 78.8 | 1451 | 20.56 | 5995 | 3442.9 | 3418.7 | 4944.4 | 1209.8 | 0.68157 | 7.015
2024-12-09 | 22:07 | Data | 0 | 27.856 | 24.831 | 235.707 | 7.62 | 220.884 | 2229.75 | 25.88 | 41.213 | 6.28 | 1.494 | 5.551 | 9232.13 | 2.755 | 98.2 | 78.8 | 1450 | 20.61 | 6000.9 | 3466.1 | 3466.6 | 4993.8 | 1209.8 | 0.67838 | 7.045
2024-12-09 | 22:07 | Data | 0 | 27.68 | 24.662 | 235.887 | 7.62 | 220.929 | 2229.75 | 25.89 | 41.304 | 6.28 | 1.485 | 5.584 | 9259.26 | 2.822 | 98.1 | 79 | 1450 | 20.61 | 6018.5 | 3452.8 | 3409.2 | 4949.6 | 1209.9 | 0.68387 | 7.069
2024-12-09 | 22:07 | Data | 0 | 27.545 | 24.669 | 235.933 | 7.62 | 220.929 | 2233.37 | 25.89 | 41.213 | 6.28 | 1.495 | 5.573 | 9241.17 | 2.768 | 98.2 | 78.8 | 1452 | 20.61 | 6006.8 | 3444.7 | 3409.5 | 4942.4 | 1209.9 | 0.68201 | 7.068
2024-12-09 | 22:07 | Data | 0 | 27.66 | 24.669 | 235.752 | 7.62 | 221.02 | 2232.47 | 25.89 | 41.936 | 6.28 | 1.5 | 5.545 | 9254.74 | 2.944 | 98.1 | 78.7 | 1451 | 20.97 | 6015.6 | 3458.4 | 3423.4 | 4963.3 | 1209.9 | 0.68191 | 7.046
2024-12-09 | 22:07 | Data | 0 | 27.154 | 24.541 | 235.48 | 7.62 | 220.658 | 2230.66 | 25.89 | 41.213 | 6.28 | 1.49 | 5.573 | 9250.21 | 2.768 | 98.2 | 78.9 | 1451 | 20.61 | 6012.6 | 3446.6 | 3433.5 | 4959 | 1209.9 | 0.6792 | 7.062
2024-12-09 | 22:07 | Data | 0 | 27.653 | 24.946 | 235.752 | 7.62 | 220.839 | 2232.47 | 25.88 | 41.213 | 6.29 | 1.495 | 5.561 | 9241.17 | 2.998 | 98.1 | 78.8 | 1451 | 20.65 | 6006.8 | 3447.5 | 3432 | 4962.6 | 1209.9 | 0.68024 | 7.057
2024-12-09 | 22:07 | Data | 0 | 27.883 | 24.892 | 235.842 | 7.62 | 221.02 | 2233.37 | 25.89 | 41.304 | 6.28 | 1.489 | 5.55 | 9241.17 | 2.991 | 98.2 | 78.9 | 1452 | 20.65 | 6006.8 | 3445.3 | 3436.4 | 4965.4 | 1209.9 | 0.67888 | 7.039
2024-12-09 | 22:07 | Data | 0 | 28.112 | 25.749 | 236.385 | 7.62 | 221.381 | 2232.47 | 25.89 | 41.304 | 6.29 | 1.505 | 5.568 | 9232.13 | 2.748 | 98.2 | 78.7 | 1451 | 20.61 | 6000.9 | 3444.2 | 3457.7 | 4981.2 | 1209.9 | 0.67809 | 7.073
2024-12-09 | 22:07 | Data | 0 | 28.571 | 25.803 | 236.43 | 7.62 | 221.562 | 2227.95 | 25.89 | 41.213 | 6.28 | 1.5 | 5.573 | 9675.3 | 2.788 | 98.1 | 78.8 | 1449 | 20.65 | 6288.9 | 3447.6 | 3453.4 | 4976 | 1209.9 | 0.67779 | 7.073
2024-12-09 | 22:07 | Data | 0 | 28.585 | 25.385 | 236.385 | 7.62 | 221.517 | 2233.37 | 25.9 | 41.213 | 6.29 | 1.492 | 5.579 | 9200.47 | 2.917 | 98.2 | 78.9 | 1452 | 20.7 | 5980.3 | 3461.1 | 3461.8 | 4989.2 | 1209.9 | 0.6791 | 7.07
2024-12-09 | 22:07 | Data | 0 | 28.605 | 25.986 | 236.611 | 7.62 | 221.743 | 2236.08 | 25.89 | 41.304 | 6.28 | 1.496 | 5.595 | 9200.47 | 2.89 | 98.2 | 78.9 | 1453 | 20.65 | 5980.3 | 3445.7 | 3456.6 | 4976.1 | 1209.9 | 0.67755 | 7.091
2024-12-09 | 22:07 | Data | 0 | 28.868 | 25.992 | 236.702 | 7.62 | 221.833 | 2232.47 | 25.89 | 41.304 | 6.28 | 1.51 | 5.595 | 9200.47 | 2.971 | 98.2 | 78.8 | 1451 | 20.61 | 5980.3 | 3423 | 3458.5 | 4962.5 | 1209.9 | 0.67497 | 7.106
2024-12-09 | 22:08 | Data | 0 | 29.031 | 26.154 | 236.837 | 7.62 | 221.833 | 2239.7 | 25.89 | 41.213 | 6.29 | 1.506 | 5.566 | 9191.43 | 2.883 | 98.2 | 78.7 | 1456 | 20.65 | 5974.4 | 3445.8 | 3442.2 | 4968.3 | 1209.9 | 0.67862 | 7.072
2024-12-09 | 22:08 | Data | 0 | 28.922 | 25.844 | 236.702 | 7.62 | 221.788 | 2230.66 | 25.88 | 41.304 | 6.28 | 1.496 | 5.55 | 9209.51 | 2.944 | 98.1 | 78.7 | 1451 | 20.61 | 5986.2 | 3440 | 3466.3 | 4980.5 | 1209.9 | 0.67707 | 7.048
2024-12-09 | 22:08 | Data | 0 | 28.578 | 25.81 | 236.611 | 7.62 | 221.607 | 2233.37 | 25.89 | 41.123 | 6.28 | 1.492 | 5.573 | 9195.95 | 2.937 | 98.2 | 78.9 | 1452 | 20.61 | 5977.4 | 3438.3 | 3464.1 | 4984.5 | 1209.9 | 0.67841 | 7.066
2024-12-09 | 22:08 | Data | 0 | 28.423 | 25.486 | 236.249 | 7.62 | 221.336 | 2229.75 | 25.88 | 41.304 | 6.28 | 1.49 | 5.598 | 9214.04 | 2.944 | 98.2 | 79 | 1450 | 20.61 | 5989.1 | 3443.3 | 3493.3 | 4986.9 | 1209.9 | 0.67475 | 7.089
2024-12-09 | 22:08 | Data | 0 | 28.369 | 25.506 | 236.204 | 7.62 | 221.291 | 2230.66 | 25.88 | 41.304 | 6.28 | 1.496 | 5.609 | 9214.04 | 2.849 | 98.1 | 78.9 | 1450 | 20.65 | 5989.1 | 3460.1 | 3484.8 | 5003.1 | 1209.9 | 0.67636 | 7.106
2024-12-09 | 22:08 | Data | 0 | 27.579 | 25.061 | 235.978 | 7.62 | 221.065 | 2229.75 | 25.88 | 41.213 | 6.28 | 1.491 | 5.573 | 9227.6 | 2.869 | 98.2 | 78.9 | 1450 | 20.61 | 5997.9 | 3433.5 | 3484.1 | 4985.3 | 1209.9 | 0.67448 | 7.065
2024-12-09 | 22:08 | Data | 0 | 27.667 | 25.277 | 236.023 | 7.62 | 221.02 | 2218.91 | 25.89 | 41.304 | 6.29 | 1.504 | 5.58 | 9241.17 | 2.768 | 98.1 | 78.8 | 1443 | 20.61 | 6006.8 | 3441.7 | 3468.2 | 4977.4 | 1209.9 | 0.6757 | 7.084
2024-12-09 | 22:08 | Data | 0 | 27.653 | 24.777 | 235.752 | 7.62 | 220.929 | 2227.95 | 25.88 | 41.213 | 6.28 | 1.502 | 5.568 | 9223.08 | 2.815 | 98.1 | 78.7 | 1448 | 20.65 | 5995 | 3461.9 | 3478.9 | 5001.9 | 1209.9 | 0.67752 | 7.07
2024-12-09 | 22:08 | Data | 0 | 27.538 | 24.899 | 235.616 | 7.62 | 220.839 | 2227.95 | 25.88 | 41.304 | 6.28 | 1.491 | 5.578 | 9241.17 | 2.714 | 98.1 | 78.9 | 1448 | 20.65 | 6006.8 | 3479.2 | 3485.7 | 5018.5 | 1209.9 | 0.67855 | 7.069
2024-12-09 | 22:08 | Data | 0 | 28.085 | 25.122 | 235.887 | 7.62 | 221.065 | 2227.95 | 25.88 | 41.213 | 6.28 | 1.49 | 5.57 | 9209.51 | 2.863 | 98.2 | 78.9 | 1449 | 20.61 | 5986.2 | 3442.7 | 3450.3 | 4969.9 | 1209.9 | 0.67823 | 7.058
2024-12-09 | 22:08 | Data | 0 | 28.112 | 25.034 | 236.023 | 7.62 | 221.246 | 2231.56 | 25.88 | 41.304 | 6.28 | 1.486 | 5.575 | 9218.56 | 2.856 | 98.1 | 79 | 1450 | 20.61 | 5992.1 | 3451.2 | 3404.8 | 4941.1 | 1209.9 | 0.68329 | 7.06
2024-12-09 | 22:08 | Data | 0 | 28.058 | 25.135 | 236.068 | 7.63 | 221.246 | 2227.95 | 25.88 | 41.304 | 6.28 | 1.494 | 5.58 | 9209.51 | 2.95 | 98.2 | 78.9 | 1448 | 20.61 | 5986.2 | 3431.6 | 3396.8 | 4927.7 | 1209.9 | 0.68153 | 7.073
2024-12-09 | 22:08 | Data | 0 | 28.315 | 25.452 | 236.249 | 7.62 | 221.381 | 2225.23 | 25.89 | 41.213 | 6.28 | 1.492 | 5.561 | 9209.51 | 2.782 | 98.1 | 78.8 | 1446 | 20.61 | 5986.2 | 3416.4 | 3384.9 | 4902.3 | 1209.9 | 0.68245 | 7.051
2024-12-09 | 22:08 | Data | 0 | 27.701 | 24.919 | 235.978 | 7.62 | 221.246 | 2230.66 | 25.89 | 41.304 | 6.28 | 1.486 | 5.575 | 9186.9 | 2.721 | 98.2 | 79 | 1449 | 20.65 | 5971.5 | 3450.1 | 3395.2 | 4937.5 | 1209.9 | 0.68358 | 7.061
2024-12-09 | 22:08 | Data | 0 | 28.551 | 25.405 | 236.204 | 7.62 | 221.291 | 2230.66 | 25.89 | 41.213 | 6.29 | 1.494 | 5.574 | 9182.38 | 2.815 | 98.2 | 78.9 | 1450 | 20.61 | 5968.5 | 3425 | 3394.9 | 4918.8 | 1209.9 | 0.68025 | 7.068
2024-12-09 | 22:08 | Data | 0 | 28.578 | 26.06 | 236.747 | 7.62 | 221.652 | 2228.85 | 25.88 | 41.304 | 6.28 | 1.487 | 5.569 | 9182.38 | 2.842 | 98.1 | 78.9 | 1449 | 20.65 | 5968.5 | 3449.8 | 3420.7 | 4947.5 | 1209.9 | 0.68112 | 7.057
2024-12-09 | 22:08 | Data | 0 | 28.673 | 25.169 | 236.204 | 7.62 | 221.336 | 2229.75 | 25.89 | 41.123 | 6.28 | 1.479 | 5.548 | 9191.43 | 2.944 | 98.2 | 79 | 1450 | 20.61 | 5974.4 | 3430 | 3446.3 | 4961.5 | 1209.9 | 0.67602 | 7.028
2024-12-09 | 22:08 | Data | 0 | 28.794 | 25.817 | 236.43 | 7.62 | 221.517 | 2230.66 | 25.88 | 41.304 | 6.28 | 1.485 | 5.565 | 9186.9 | 2.991 | 98.1 | 78.9 | 1449 | 20.7 | 5971.5 | 3443.1 | 3452.8 | 4971.2 | 1209.9 | 0.67727 | 7.05
2024-12-09 | 22:09 | Data | 0 | 28.706 | 25.709 | 236.702 | 7.62 | 221.697 | 2232.47 | 25.89 | 41.304 | 6.28 | 1.496 | 5.576 | 9214.04 | 2.768 | 98.1 | 78.8 | 1452 | 20.65 | 5989.1 | 3436.9 | 3475.7 | 4984.7 | 1209.9 | 0.67451 | 7.072
2024-12-09 | 22:09 | Data | 0 | 29.26 | 26.269 | 236.792 | 7.62 | 221.743 | 2239.7 | 25.88 | 41.123 | 6.28 | 1.488 | 5.587 | 9200.47 | 2.998 | 98.2 | 79 | 1456 | 20.61 | 5980.3 | 3445.4 | 3455.7 | 4967.9 | 1209.9 | 0.67744 | 7.076
2024-12-09 | 22:09 | Data | 0 | 29.024 | 26.141 | 236.566 | 7.62 | 221.743 | 2231.56 | 25.89 | 41.304 | 6.29 | 1.494 | 5.582 | 9186.9 | 2.795 | 98.1 | 78.9 | 1451 | 20.65 | 5971.5 | 3436.1 | 3421.1 | 4937.7 | 1210 | 0.67965 | 7.076
2024-12-09 | 22:09 | Data | 0 | 29.105 | 26.303 | 236.566 | 7.62 | 221.652 | 2233.37 | 25.88 | 41.213 | 6.28 | 1.487 | 5.601 | 9186.9 | 2.829 | 98.1 | 79 | 1452 | 20.61 | 5971.5 | 3442.9 | 3418.4 | 4948.3 | 1210 | 0.68108 | 7.088
2024-12-09 | 22:09 | Data | 0 | 29.031 | 26.046 | 236.611 | 7.62 | 221.788 | 2233.37 | 25.88 | 41.304 | 6.29 | 1.497 | 5.596 | 9232.13 | 2.869 | 98.1 | 78.9 | 1451 | 20.65 | 6000.9 | 3448.6 | 3396 | 4932.7 | 1210 | 0.68406 | 7.093
2024-12-09 | 22:09 | Data | 0 | 28.97 | 26.148 | 236.611 | 7.62 | 221.697 | 2232.47 | 25.89 | 41.213 | 6.28 | 1.495 | 5.588 | 9227.6 | 2.957 | 98.2 | 78.9 | 1452 | 20.61 | 5997.9 | 3442.9 | 3372.1 | 4913.9 | 1210 | 0.6858 | 7.084
2024-12-09 | 22:09 | Data | 0 | 28.781 | 25.932 | 236.656 | 7.62 | 221.652 | 2232.47 | 25.89 | 41.213 | 6.28 | 1.494 | 5.584 | 9195.95 | 2.984 | 98.1 | 78.9 | 1451 | 20.65 | 5977.4 | 3438.3 | 3380.1 | 4917.6 | 1210 | 0.68406 | 7.079
2024-12-09 | 22:09 | Data | 0 | 28.895 | 26.425 | 236.883 | 7.62 | 221.833 | 2229.75 | 25.89 | 41.304 | 6.28 | 1.498 | 5.594 | 9236.65 | 2.775 | 98.2 | 78.9 | 1450 | 20.61 | 6003.8 | 3458.8 | 3382.2 | 4932.3 | 1210 | 0.68641 | 7.092
2024-12-09 | 22:09 | Data | 0 | 28.922 | 26.202 | 236.747 | 7.62 | 221.788 | 2235.18 | 25.88 | 41.213 | 6.28 | 1.504 | 5.605 | 9209.51 | 3.025 | 98.2 | 78.8 | 1453 | 20.65 | 5986.2 | 3442.1 | 3400.2 | 4944 | 1210 | 0.68393 | 7.109
2024-12-09 | 22:09 | Data | 0 | 29.213 | 26.587 | 236.747 | 7.63 | 221.878 | 2236.98 | 25.86 | 41.304 | 6.28 | 1.493 | 5.611 | 9214.04 | 2.728 | 98.2 | 79 | 1453 | 20.61 | 5989.1 | 3454.4 | 3398.4 | 4937.3 | 1210 | 0.68443 | 7.106
2024-12-09 | 22:09 | Data | 0 | 29.098 | 26.391 | 237.154 | 7.62 | 222.104 | 2240.6 | 25.88 | 41.304 | 6.28 | 1.482 | 5.626 | 9209.51 | 2.761 | 98.2 | 79.1 | 1456 | 20.7 | 5986.2 | 3439.2 | 3426.3 | 4948.9 | 1210 | 0.67988 | 7.108
2024-12-09 | 22:09 | Data | 0 | 29.726 | 27.167 | 237.471 | 7.62 | 222.466 | 2239.7 | 25.86 | 41.304 | 6.29 | 1.493 | 5.622 | 9195.95 | 2.761 | 98.2 | 79 | 1456 | 20.65 | 5977.4 | 3438.4 | 3400.9 | 4933.1 | 1210 | 0.68183 | 7.115
2024-12-09 | 22:09 | Data | 0 | 29.564 | 26.911 | 237.516 | 7.62 | 222.375 | 2235.18 | 25.88 | 41.304 | 6.28 | 1.487 | 5.62 | 9146.2 | 2.849 | 98.1 | 79.1 | 1453 | 20.65 | 5945 | 3442 | 3395.6 | 4929 | 1210 | 0.68296 | 7.108
2024-12-09 | 22:09 | Data | 0 | 30.178 | 27.511 | 237.561 | 7.62 | 222.601 | 2236.08 | 25.88 | 41.213 | 6.29 | 1.495 | 5.608 | 9123.59 | 2.984 | 98.2 | 79 | 1453 | 20.56 | 5930.3 | 3420 | 3398.7 | 4919.7 | 1210 | 0.67957 | 7.103
2024-12-09 | 22:09 | Data | 0 | 30.185 | 27.248 | 237.561 | 7.62 | 222.692 | 2236.98 | 25.89 | 41.213 | 6.28 | 1.493 | 5.613 | 9132.64 | 2.761 | 98.2 | 79 | 1455 | 20.65 | 5936.2 | 3475.3 | 3399 | 4955.7 | 1210 | 0.68661 | 7.106
2024-12-09 | 22:09 | Data | 0 | 30.3 | 27.201 | 237.742 | 7.63 | 222.782 | 2239.7 | 25.89 | 41.304 | 6.28 | 1.494 | 5.595 | 9123.59 | 2.998 | 98.2 | 78.9 | 1456 | 20.7 | 5930.3 | 3455 | 3394.6 | 4936.6 | 1210 | 0.68436 | 7.089
2024-12-09 | 22:09 | Data | 0 | 30.131 | 27.201 | 237.697 | 7.62 | 222.647 | 2238.79 | 25.86 | 41.213 | 6.28 | 1.5 | 5.603 | 9195.95 | 2.971 | 98.2 | 78.9 | 1456 | 20.61 | 5977.4 | 3456.9 | 3398.9 | 4938.4 | 1210 | 0.68428 | 7.103
2024-12-09 | 22:09 | Data | 0 | 30.239 | 27.424 | 237.742 | 7.63 | 222.827 | 2242.41 | 25.88 | 41.304 | 6.29 | 1.503 | 5.632 | 9195.95 | 2.768 | 98.2 | 78.9 | 1458 | 20.61 | 5977.4 | 3447.1 | 3409 | 4940.6 | 1210 | 0.6823 | 7.134
2024-12-09 | 22:10 | Data | 0 | 30.401 | 27.208 | 237.606 | 7.62 | 222.692 | 2241.5 | 25.88 | 41.304 | 6.28 | 1.497 | 5.643 | 9200.47 | 2.984 | 98.2 | 79 | 1457 | 20.61 | 5980.3 | 3449.9 | 3416 | 4950 | 1210 | 0.68232 | 7.142
2024-12-09 | 22:10 | Data | 0 | 30.293 | 27.424 | 237.832 | 7.63 | 222.737 | 2240.6 | 25.89 | 41.304 | 6.28 | 1.5 | 5.643 | 9214.04 | 2.977 | 98.2 | 79 | 1457 | 20.65 | 5989.1 | 3463.4 | 3389.6 | 4939.9 | 1210 | 0.68642 | 7.143
2024-12-09 | 22:10 | Data | 0 | 30.3 | 27.376 | 237.878 | 7.62 | 222.827 | 2238.79 | 25.88 | 40.943 | 6.28 | 1.5 | 5.62 | 9173.34 | 2.971 | 98.2 | 78.9 | 1455 | 20.47 | 5962.7 | 3451.8 | 3423.2 | 4956.1 | 1210 | 0.68155 | 7.119
2024-12-09 | 22:10 | Data | 0 | 30.408 | 27.532 | 237.742 | 7.62 | 222.782 | 2236.08 | 25.88 | 41.033 | 6.28 | 1.492 | 5.599 | 9173.34 | 2.998 | 98.2 | 79 | 1453 | 20.52 | 5962.7 | 3439.8 | 3422 | 4952.3 | 1210 | 0.67981 | 7.091
2024-12-09 | 22:10 | Data | 0 | 30.185 | 27.424 | 237.742 | 7.62 | 222.873 | 2236.08 | 25.88 | 41.033 | 6.28 | 1.5 | 5.606 | 9186.9 | 2.876 | 98.2 | 78.9 | 1453 | 20.52 | 5971.5 | 3448.5 | 3460.5 | 4983 | 1210 | 0.67618 | 7.106
2024-12-09 | 22:10 | Data | 0 | 30.415 | 27.322 | 237.787 | 7.62 | 222.737 | 2233.37 | 25.88 | 41.033 | 6.28 | 1.495 | 5.628 | 9186.9 | 2.761 | 98.2 | 79 | 1452 | 20.43 | 5971.5 | 3422.3 | 3452.3 | 4957.2 | 1210 | 0.67505 | 7.124
2024-12-09 | 22:10 | Data | 0 | 30.185 | 27.511 | 237.878 | 7.62 | 222.827 | 2233.37 | 25.88 | 41.033 | 6.28 | 1.505 | 5.621 | 9200.47 | 2.647 | 98.2 | 78.9 | 1452 | 20.52 | 5980.3 | 3445 | 3467.1 | 4984 | 1210 | 0.67617 | 7.126
2024-12-09 | 22:10 | Data | 0 | 30.158 | 27.788 | 237.878 | 7.62 | 222.873 | 2233.37 | 25.89 | 40.943 | 6.28 | 1.496 | 5.622 | 9186.9 | 2.775 | 98.2 | 79 | 1452 | 20.47 | 5971.5 | 3454.3 | 3476 | 4992.7 | 1210 | 0.67637 | 7.118
2024-12-09 | 22:10 | Data | 0 | 30.529 | 27.268 | 237.742 | 7.62 | 222.737 | 2229.75 | 25.89 | 40.943 | 6.29 | 1.498 | 5.613 | 9182.38 | 2.977 | 98.2 | 78.9 | 1449 | 20.47 | 5968.5 | 3428.2 | 3439.5 | 4953 | 1210 | 0.67634 | 7.111
2024-12-09 | 22:10 | Data | 0 | 30.408 | 27.424 | 237.742 | 7.62 | 222.827 | 2236.08 | 25.89 | 41.033 | 6.28 | 1.484 | 5.582 | 9186.9 | 2.876 | 98.2 | 79 | 1453 | 20.47 | 5971.5 | 3453.6 | 3407.8 | 4946.7 | 1210 | 0.68221 | 7.067
2024-12-09 | 22:10 | Data | 0 | 29.962 | 27.221 | 237.742 | 7.62 | 222.692 | 2236.08 | 25.88 | 41.033 | 6.28 | 1.49 | 5.583 | 9195.95 | 2.829 | 98.2 | 78.9 | 1453 | 20.52 | 5977.4 | 3447.4 | 3423.2 | 4951.2 | 1210 | 0.68101 | 7.073
2024-12-09 | 22:10 | Data | 0 | 30.536 | 27.343 | 237.968 | 7.62 | 222.873 | 2231.56 | 25.88 | 41.123 | 6.28 | 1.505 | 5.617 | 9209.51 | 2.937 | 98.2 | 78.9 | 1450 | 20.56 | 5986.2 | 3427.8 | 3388.2 | 4930.4 | 1210 | 0.68121 | 7.121
2024-12-09 | 22:10 | Data | 0 | 30.3 | 27.647 | 237.832 | 7.62 | 222.782 | 2233.37 | 25.88 | 40.943 | 6.29 | 1.514 | 5.594 | 9195.95 | 2.93 | 98.2 | 78.7 | 1452 | 20.52 | 5977.4 | 3435.1 | 3400.8 | 4931.1 | 1210 | 0.68181 | 7.109
2024-12-09 | 22:10 | Data | 0 | 30.793 | 27.734 | 237.787 | 7.62 | 222.827 | 2232.47 | 25.89 | 40.943 | 6.28 | 1.496 | 5.586 | 9218.56 | 3.011 | 98.2 | 78.9 | 1451 | 20.52 | 5992.1 | 3445.1 | 3448.6 | 4970.1 | 1210 | 0.68038 | 7.082
2024-12-09 | 22:10 | Data | 0 | 30.131 | 27.532 | 237.968 | 7.62 | 222.827 | 2236.08 | 25.89 | 40.943 | 6.28 | 1.489 | 5.608 | 9250.21 | 2.964 | 98.2 | 79 | 1453 | 20.47 | 6012.6 | 3440.3 | 3428.7 | 4950.9 | 1210 | 0.67946 | 7.098
2024-12-09 | 22:10 | Data | 0 | 30.354 | 27.653 | 237.742 | 7.62 | 222.827 | 2234.27 | 25.89 | 40.943 | 6.28 | 1.495 | 5.616 | 9227.6 | 2.741 | 98.2 | 79 | 1453 | 20.52 | 5997.9 | 3436.2 | 3420 | 4946.7 | 1210.1 | 0.67894 | 7.11
2024-12-09 | 22:10 | Data | 0 | 29.989 | 27.201 | 237.832 | 7.62 | 222.827 | 2235.18 | 25.88 | 40.943 | 6.28 | 1.493 | 5.606 | 9236.65 | 2.761 | 98.2 | 79 | 1453 | 20.52 | 6003.8 | 3445.1 | 3428.3 | 4954.4 | 1210.1 | 0.68038 | 7.099
2024-12-09 | 22:10 | Data | 0 | 30.131 | 27.194 | 237.742 | 7.63 | 222.782 | 2231.56 | 25.89 | 40.943 | 6.29 | 1.496 | 5.597 | 9214.04 | 2.977 | 98.2 | 78.9 | 1451 | 20.38 | 5989.1 | 3445.9 | 3413.6 | 4947.2 | 1210.1 | 0.68134 | 7.092
2024-12-09 | 22:11 | Data | 0 | 30.057 | 27.322 | 237.832 | 7.62 | 222.873 | 2230.66 | 25.88 | 41.033 | 6.29 | 1.499 | 5.578 | 9236.65 | 2.647 | 98.2 | 78.8 | 1450 | 20.47 | 6003.8 | 3418.1 | 3438.1 | 4944.2 | 1210.1 | 0.67699 | 7.077
2024-12-09 | 22:11 | Data | 0 | 30.543 | 27.565 | 237.968 | 7.62 | 223.008 | 2229.75 | 25.89 | 40.943 | 6.28 | 1.509 | 5.611 | 9236.65 | 2.721 | 98.2 | 78.8 | 1449 | 20.52 | 6003.8 | 3448.8 | 3413.3 | 4947.7 | 1210.1 | 0.68195 | 7.117
2024-12-09 | 22:11 | Data | 0 | 30.408 | 27.43 | 237.878 | 7.62 | 222.782 | 2229.75 | 25.86 | 41.213 | 6.28 | 1.492 | 5.596 | 9236.65 | 2.977 | 98.1 | 78.9 | 1451 | 20.65 | 6003.8 | 3444.9 | 3407.7 | 4938.3 | 1210.1 | 0.68224 | 7.088
2024-12-09 | 22:11 | Data | 0 | 30.192 | 27.248 | 237.652 | 7.62 | 222.737 | 2229.75 | 25.89 | 40.943 | 6.28 | 1.485 | 5.627 | 9241.17 | 2.883 | 98.2 | 79.1 | 1449 | 20.52 | 6006.8 | 3444.2 | 3406.5 | 4930 | 1210.1 | 0.68136 | 7.113
2024-12-09 | 22:11 | Data | 0 | 30.3 | 27.322 | 237.697 | 7.62 | 222.692 | 2227.04 | 25.88 | 40.943 | 6.28 | 1.489 | 5.626 | 9223.08 | 2.937 | 98.2 | 79.1 | 1448 | 20.43 | 5995 | 3451.4 | 3399.1 | 4938.9 | 1210.1 | 0.68449 | 7.115
2024-12-09 | 22:11 | Data | 0 | 30.178 | 27.417 | 237.742 | 7.62 | 222.647 | 2227.04 | 25.89 | 41.394 | 6.29 | 1.495 | 5.592 | 9254.74 | 2.768 | 98.1 | 78.9 | 1448 | 20.7 | 6015.6 | 3445 | 3402.7 | 4933.7 | 1210.1 | 0.68347 | 7.087
2024-12-09 | 22:11 | Data | 0 | 30.198 | 27.525 | 237.878 | 7.62 | 222.873 | 2227.95 | 25.88 | 41.304 | 6.29 | 1.492 | 5.592 | 9227.6 | 2.788 | 98.1 | 78.9 | 1448 | 20.61 | 5997.9 | 3447.4 | 3409 | 4941.7 | 1210.1 | 0.68243 | 7.083
2024-12-09 | 22:11 | Data | 0 | 30.556 | 27.694 | 237.923 | 7.62 | 222.827 | 2232.47 | 25.88 | 41.304 | 6.28 | 1.511 | 5.609 | 9232.13 | 2.944 | 98.2 | 78.8 | 1451 | 20.61 | 6000.9 | 3439.5 | 3416.7 | 4944 | 1210.1 | 0.6818 | 7.12
2024-12-09 | 22:11 | Data | 0 | 30.617 | 27.505 | 237.923 | 7.63 | 222.827 | 2238.79 | 25.89 | 41.304 | 6.28 | 1.509 | 5.617 | 9232.13 | 2.937 | 98.2 | 78.8 | 1455 | 20.61 | 6000.9 | 3434.1 | 3413.3 | 4938.2 | 1210.1 | 0.67936 | 7.125
2024-12-09 | 22:11 | Data | 0 | 30.577 | 27.43 | 237.878 | 7.63 | 222.963 | 2235.18 | 25.89 | 41.213 | 6.28 | 1.498 | 5.62 | 9245.69 | 2.957 | 98.2 | 78.9 | 1453 | 20.61 | 6009.7 | 3402.6 | 3431.2 | 4928.9 | 1210.1 | 0.67553 | 7.118
2024-12-09 | 22:11 | Data | 0 | 30.415 | 27.43 | 237.787 | 7.62 | 222.873 | 2233.37 | 25.89 | 41.213 | 6.28 | 1.497 | 5.601 | 9263.78 | 2.977 | 98.1 | 78.9 | 1452 | 20.65 | 6021.5 | 3442.9 | 3395.8 | 4930.6 | 1210.1 | 0.68249 | 7.097
2024-12-09 | 22:11 | Data | 0 | 30.185 | 27.424 | 237.697 | 7.63 | 222.647 | 2233.37 | 25.88 | 41.213 | 6.28 | 1.498 | 5.584 | 9254.74 | 2.761 | 98.2 | 78.9 | 1452 | 20.65 | 6015.6 | 3435.4 | 3417.9 | 4942.1 | 1210.1 | 0.67987 | 7.082
2024-12-09 | 22:11 | Data | 0 | 30.239 | 27.397 | 237.742 | 7.62 | 222.827 | 2233.37 | 25.88 | 41.304 | 6.28 | 1.497 | 5.616 | 9268.3 | 2.782 | 98.2 | 79 | 1452 | 20.65 | 6024.4 | 3433.1 | 3390.9 | 4921.8 | 1210.1 | 0.68214 | 7.113
2024-12-09 | 22:11 | Data | 0 | 30.185 | 27.397 | 237.697 | 7.62 | 222.692 | 2233.37 | 25.88 | 41.304 | 6.28 | 1.49 | 5.605 | 9725.05 | 2.788 | 98.2 | 79 | 1452 | 20.65 | 6321.3 | 3440.1 | 3362.4 | 4904.8 | 1210.1 | 0.68337 | 7.096
2024-12-09 | 22:11 | Data | 0 | 30.286 | 27.863 | 238.013 | 7.62 | 222.873 | 2238.79 | 25.89 | 41.304 | 6.28 | 1.498 | 5.592 | 9720.53 | 2.95 | 98.2 | 78.9 | 1454 | 20.65 | 6318.3 | 3433.1 | 3395.8 | 4923.9 | 1210.1 | 0.68168 | 7.09
2024-12-09 | 22:11 | Data | 0 | 30.28 | 27.606 | 237.968 | 7.62 | 222.963 | 2238.79 | 25.88 | 41.213 | 6.28 | 1.498 | 5.612 | 9725.05 | 2.707 | 98.2 | 78.9 | 1455 | 20.61 | 6321.3 | 3443.6 | 3412.6 | 4944.2 | 1210.1 | 0.6814 | 7.111
2024-12-09 | 22:11 | Data | 0 | 30.3 | 27.876 | 237.923 | 7.63 | 222.963 | 2239.7 | 25.88 | 41.213 | 6.28 | 1.5 | 5.621 | 9725.05 | 2.714 | 98.2 | 78.9 | 1455 | 20.61 | 6321.3 | 3439.4 | 3415.4 | 4944 | 1210.1 | 0.68034 | 7.121
2024-12-09 | 22:12 | Data | 0 | 30.185 | 27.626 | 237.652 | 7.62 | 222.737 | 2239.7 | 25.88 | 40.852 | 6.28 | 1.505 | 5.627 | 9304.48 | 2.761 | 98.2 | 78.9 | 1455 | 20.43 | 6047.9 | 3431.7 | 3443.8 | 4958.3 | 1210.1 | 0.67686 | 7.132
2024-12-09 | 22:12 | Data | 0 | 30.401 | 27.599 | 237.878 | 7.63 | 222.873 | 2235.18 | 25.88 | 41.213 | 6.28 | 1.515 | 5.62 | 9309 | 2.977 | 98.1 | 78.8 | 1453 | 20.65 | 6050.9 | 3431.9 | 3425.2 | 4942.2 | 1210.1 | 0.67893 | 7.134
2024-12-09 | 22:12 | Data | 0 | 30.469 | 27.322 | 237.923 | 7.62 | 222.873 | 2238.79 | 25.88 | 41.304 | 6.28 | 1.5 | 5.621 | 9309 | 2.842 | 98.2 | 78.9 | 1456 | 20.65 | 6050.9 | 3436.5 | 3411.3 | 4937.2 | 1210.1 | 0.68151 | 7.123
2024-12-09 | 22:12 | Data | 0 | 30.185 | 27.741 | 237.878 | 7.63 | 222.827 | 2241.5 | 25.89 | 41.304 | 6.28 | 1.497 | 5.62 | 9309 | 2.876 | 98.2 | 79 | 1457 | 20.61 | 6050.9 | 3433.1 | 3406.6 | 4935.2 | 1210.1 | 0.68063 | 7.117
2024-12-09 | 22:12 | Data | 0 | 29.996 | 27.788 | 238.013 | 7.63 | 223.008 | 2241.5 | 25.89 | 41.123 | 6.28 | 1.505 | 5.628 | 9295.44 | 2.633 | 98.2 | 78.9 | 1458 | 20.61 | 6042 | 3455 | 3416.6 | 4951.5 | 1210.1 | 0.68041 | 7.133
2024-12-09 | 22:12 | Data | 0 | 30.3 | 27.592 | 237.832 | 7.62 | 222.873 | 2240.6 | 25.89 | 41.304 | 6.28 | 1.512 | 5.62 | 9299.96 | 2.849 | 98.2 | 78.8 | 1457 | 20.61 | 6045 | 3461 | 3405.1 | 4948.1 | 1210.1 | 0.68422 | 7.134
2024-12-09 | 22:12 | Data | 0 | 30.185 | 27.484 | 237.832 | 7.63 | 222.782 | 2242.41 | 25.89 | 41.304 | 6.28 | 1.503 | 5.603 | 9281.87 | 2.701 | 98.2 | 78.8 | 1457 | 20.65 | 6033.2 | 3471.5 | 3427.6 | 4971.4 | 1210.1 | 0.68392 | 7.106
2024-12-09 | 22:12 | Data | 0 | 30.192 | 27.309 | 237.923 | 7.63 | 222.963 | 2241.5 | 25.88 | 41.304 | 6.28 | 1.5 | 5.573 | 9281.87 | 2.761 | 98.2 | 78.8 | 1458 | 20.61 | 6033.2 | 3447.8 | 3449.2 | 4969.8 | 1210.1 | 0.67963 | 7.071
2024-12-09 | 22:12 | Data | 0 | 30.07 | 27.194 | 237.787 | 7.62 | 222.692 | 2242.41 | 25.88 | 41.304 | 6.28 | 1.5 | 5.603 | 9250.21 | 2.977 | 98.2 | 78.9 | 1458 | 20.7 | 6012.6 | 3452.5 | 3447.7 | 4971.6 | 1210.1 | 0.67894 | 7.102
2024-12-09 | 22:12 | Data | 0 | 30.192 | 27.701 | 237.742 | 7.62 | 222.827 | 2242.41 | 25.88 | 41.213 | 6.28 | 1.492 | 5.615 | 9281.87 | 2.775 | 98.2 | 79 | 1458 | 20.61 | 6033.2 | 3431.8 | 3448.3 | 4958.7 | 1210.1 | 0.67682 | 7.108
2024-12-09 | 22:12 | Data | 0 | 30.583 | 27.424 | 237.697 | 7.62 | 222.782 | 2241.5 | 25.88 | 41.213 | 6.28 | 1.493 | 5.604 | 9241.17 | 3.031 | 98.2 | 79 | 1457 | 20.65 | 6006.8 | 3451 | 3459.2 | 4981.1 | 1210.2 | 0.67735 | 7.097
2024-12-09 | 22:12 | Data | 0 | 30.496 | 27.43 | 237.923 | 7.62 | 222.827 | 2235.18 | 25.89 | 41.304 | 6.28 | 1.496 | 5.586 | 9241.17 | 2.876 | 98.2 | 78.9 | 1453 | 20.61 | 6006.8 | 3438.4 | 3418.3 | 4943.7 | 1210.2 | 0.68103 | 7.082
2024-12-09 | 22:12 | Data | 0 | 29.962 | 27.309 | 237.787 | 7.62 | 222.827 | 2236.08 | 25.89 | 41.304 | 6.28 | 1.51 | 5.595 | 9241.17 | 2.822 | 98.2 | 78.8 | 1453 | 20.61 | 6006.8 | 3423.6 | 3427.2 | 4939.1 | 1210.2 | 0.6789 | 7.105
2024-12-09 | 22:12 | Data | 0 | 30.401 | 27.876 | 237.787 | 7.62 | 222.873 | 2230.66 | 25.88 | 41.213 | 6.28 | 1.507 | 5.574 | 9241.17 | 2.775 | 98.2 | 78.7 | 1450 | 20.61 | 6006.8 | 3433.7 | 3391.2 | 4924.7 | 1210.2 | 0.68176 | 7.08
2024-12-09 | 22:12 | Data | 0 | 30.239 | 27.194 | 237.606 | 7.62 | 222.737 | 2234.27 | 25.88 | 41.213 | 6.29 | 1.511 | 5.611 | 9254.74 | 2.869 | 98.2 | 78.8 | 1452 | 20.65 | 6015.6 | 3449.1 | 3414.1 | 4948.5 | 1210.2 | 0.68179 | 7.122
2024-12-09 | 22:12 | Data | 0 | 30.313 | 27.484 | 237.787 | 7.62 | 222.737 | 2238.79 | 25.89 | 41.394 | 6.29 | 1.507 | 5.588 | 9245.69 | 2.876 | 98.2 | 78.8 | 1455 | 20.65 | 6009.7 | 3439.8 | 3422.1 | 4947.4 | 1210.2 | 0.67986 | 7.096
2024-12-09 | 22:12 | Data | 0 | 30.381 | 27.579 | 237.832 | 7.63 | 222.647 | 2238.79 | 25.88 | 41.213 | 6.28 | 1.5 | 5.571 | 9675.3 | 2.829 | 98.2 | 78.8 | 1455 | 20.61 | 6288.9 | 3444.4 | 3403.6 | 4938.2 | 1210.2 | 0.68133 | 7.07
2024-12-09 | 22:12 | Data | 0 | 30.212 | 27.397 | 237.787 | 7.63 | 222.782 | 2238.79 | 25.88 | 41.213 | 6.28 | 1.498 | 5.569 | 9756.7 | 2.768 | 98.2 | 78.8 | 1455 | 20.61 | 6341.9 | 3423.8 | 3405.2 | 4930.6 | 1210.2 | 0.68134 | 7.068
2024-12-09 | 22:13 | Data | 0 | 30.185 | 27.592 | 237.878 | 7.63 | 222.827 | 2238.79 | 25.89 | 41.213 | 6.28 | 1.501 | 5.587 | 9394.93 | 2.707 | 98.2 | 78.8 | 1456 | 20.56 | 6106.7 | 3431.2 | 3384.5 | 4917.1 | 1210.2 | 0.68328 | 7.087
2024-12-09 | 22:13 | Data | 0 | 30.644 | 27.565 | 237.878 | 7.62 | 222.827 | 2229.75 | 25.88 | 41.304 | 6.28 | 1.5 | 5.61 | 9263.78 | 2.998 | 98.2 | 78.9 | 1450 | 20.61 | 6021.5 | 3441.9 | 3408.5 | 4941.8 | 1210.2 | 0.68084 | 7.11
2024-12-09 | 22:13 | Data | 0 | 30.644 | 27.437 | 237.878 | 7.62 | 222.873 | 2236.08 | 25.89 | 41.304 | 6.28 | 1.49 | 5.606 | 9259.26 | 2.957 | 98.2 | 79 | 1453 | 20.61 | 6018.5 | 3456.7 | 3395 | 4936.4 | 1210.2 | 0.6853 | 7.096
2024-12-09 | 22:13 | Data | 0 | 30.421 | 27.484 | 237.878 | 7.63 | 222.827 | 2233.37 | 25.88 | 41.484 | 6.28 | 1.503 | 5.606 | 9232.13 | 2.815 | 98.1 | 78.9 | 1452 | 20.74 | 6000.9 | 3444.1 | 3361.3 | 4908.7 | 1210.2 | 0.68722 | 7.109
2024-12-09 | 22:13 | Data | 0 | 30.415 | 27.471 | 237.878 | 7.63 | 222.827 | 2232.47 | 25.88 | 41.304 | 6.28 | 1.498 | 5.619 | 9227.6 | 2.829 | 98.2 | 79 | 1452 | 20.61 | 5997.9 | 3440 | 3388.2 | 4923.6 | 1210.2 | 0.68407 | 7.116
2024-12-09 | 22:13 | Data | 0 | 30.867 | 27.552 | 238.013 | 7.62 | 222.873 | 2233.37 | 25.88 | 41.304 | 6.28 | 1.495 | 5.594 | 9254.74 | 2.95 | 98.2 | 78.9 | 1451 | 20.61 | 6015.6 | 3441.1 | 3378 | 4918.4 | 1210.2 | 0.68456 | 7.089
2024-12-09 | 22:13 | Data | 0 | 30.185 | 27.322 | 237.697 | 7.63 | 222.737 | 2232.47 | 25.88 | 41.213 | 6.28 | 1.497 | 5.584 | 9259.26 | 2.863 | 98.2 | 78.9 | 1452 | 20.61 | 6018.5 | 3437.9 | 3375.4 | 4910.3 | 1210.2 | 0.68504 | 7.081
2024-12-09 | 22:13 | Data | 0 | 30.374 | 27.64 | 237.923 | 7.63 | 222.963 | 2232.47 | 25.89 | 41.213 | 6.28 | 1.495 | 5.599 | 9313.53 | 2.795 | 98.2 | 78.9 | 1451 | 20.65 | 6053.8 | 3441.3 | 3396.3 | 4934 | 1210.2 | 0.68231 | 7.094
2024-12-09 | 22:13 | Data | 0 | 30.516 | 27.93 | 237.923 | 7.63 | 223.053 | 2233.37 | 25.89 | 41.213 | 6.28 | 1.488 | 5.583 | 9299.96 | 2.775 | 98.2 | 79 | 1452 | 20.61 | 6045 | 3434.6 | 3391.6 | 4923.8 | 1210.2 | 0.68219 | 7.071
2024-12-09 | 22:13 | Data | 0 | 30.475 | 27.329 | 237.878 | 7.63 | 222.963 | 2236.08 | 25.88 | 41.304 | 6.28 | 1.496 | 5.608 | 9286.39 | 2.815 | 98.2 | 78.9 | 1453 | 20.61 | 6036.2 | 3441.7 | 3413.8 | 4943.7 | 1210.2 | 0.68291 | 7.105
2024-12-09 | 22:13 | Data | 0 | 30.165 | 27.815 | 237.878 | 7.62 | 222.782 | 2236.08 | 25.89 | 41.213 | 6.28 | 1.501 | 5.596 | 9295.44 | 2.775 | 98.2 | 78.8 | 1453 | 20.61 | 6042 | 3452.5 | 3428.3 | 4961.6 | 1210.2 | 0.68057 | 7.098
2024-12-09 | 22:13 | Data | 0 | 30.185 | 27.417 | 237.742 | 7.63 | 222.737 | 2233.37 | 25.88 | 41.213 | 6.28 | 1.499 | 5.584 | 9313.53 | 2.768 | 98.2 | 78.8 | 1452 | 20.61 | 6053.8 | 3465.5 | 3420.4 | 4962.4 | 1210.2 | 0.6846 | 7.083
2024-12-09 | 22:13 | Data | 0 | 30.178 | 27.41 | 237.832 | 7.62 | 222.782 | 2233.37 | 25.89 | 41.304 | 6.28 | 1.496 | 5.598 | 9313.53 | 2.775 | 98.2 | 78.9 | 1452 | 20.65 | 6053.8 | 3420.1 | 3394.8 | 4913.1 | 1210.2 | 0.68126 | 7.094
2024-12-09 | 22:13 | Data | 0 | 30.185 | 27.424 | 237.832 | 7.62 | 222.782 | 2235.18 | 25.89 | 41.213 | 6.29 | 1.494 | 5.591 | 9295.44 | 2.761 | 98.2 | 78.9 | 1453 | 20.65 | 6042 | 3422.8 | 3423.4 | 4935.1 | 1210.2 | 0.67908 | 7.086
2024-12-09 | 22:13 | Data | 0 | 30.401 | 27.43 | 237.923 | 7.62 | 222.827 | 2238.79 | 25.89 | 41.304 | 6.28 | 1.496 | 5.596 | 9304.48 | 2.957 | 98.2 | 78.9 | 1456 | 20.65 | 6047.9 | 3453.7 | 3414 | 4950.9 | 1210.2 | 0.68277 | 7.093
2024-12-09 | 22:13 | Data | 0 | 30.273 | 27.376 | 237.878 | 7.63 | 222.782 | 2238.79 | 25.88 | 41.213 | 6.29 | 1.512 | 5.618 | 9277.35 | 2.768 | 98.2 | 78.8 | 1455 | 20.61 | 6030.3 | 3450.7 | 3407.8 | 4945.8 | 1210.2 | 0.68341 | 7.13
2024-12-09 | 22:13 | Data | 0 | 30.212 | 27.424 | 237.832 | 7.63 | 222.692 | 2234.27 | 25.88 | 41.484 | 6.28 | 1.506 | 5.616 | 9259.26 | 2.565 | 98.1 | 78.9 | 1452 | 20.74 | 6018.5 | 3454.3 | 3395.5 | 4935 | 1210.2 | 0.6857 | 7.122
2024-12-09 | 22:13 | Data | 0 | 30.685 | 27.782 | 237.832 | 7.63 | 222.827 | 2236.08 | 25.88 | 41.304 | 6.28 | 1.498 | 5.617 | 9268.3 | 2.964 | 98.2 | 78.9 | 1453 | 20.65 | 6024.4 | 3458.8 | 3406.2 | 4946.2 | 1210.2 | 0.68348 | 7.115
2024-12-09 | 22:14 | Data | 0 | 30.577 | 27.552 | 238.013 | 7.63 | 222.827 | 2236.08 | 25.88 | 41.213 | 6.28 | 1.488 | 5.602 | 9268.3 | 2.984 | 98.2 | 79 | 1453 | 20.65 | 6024.4 | 3446.5 | 3425.4 | 4953.2 | 1210.2 | 0.68067 | 7.091
2024-12-09 | 22:14 | Data | 0 | 30.536 | 27.728 | 238.104 | 7.62 | 222.827 | 2235.18 | 25.89 | 41.213 | 6.28 | 1.499 | 5.6 | 9241.17 | 3.045 | 98.2 | 78.9 | 1453 | 20.65 | 6006.8 | 3436.1 | 3405 | 4931.3 | 1210.2 | 0.68104 | 7.097
2024-12-09 | 22:14 | Data | 0 | 30.806 | 27.498 | 237.923 | 7.62 | 223.053 | 2233.37 | 25.89 | 41.213 | 6.28 | 1.5 | 5.611 | 9236.65 | 3.126 | 98.1 | 78.9 | 1452 | 20.61 | 6003.8 | 3455 | 3462 | 4986.5 | 1210.2 | 0.67666 | 7.111
2024-12-09 | 22:14 | Data | 0 | 30.415 | 27.741 | 237.878 | 7.62 | 222.827 | 2233.37 | 25.89 | 41.213 | 6.28 | 1.507 | 5.592 | 9241.17 | 2.674 | 98.2 | 78.8 | 1451 | 20.61 | 6006.8 | 3470.4 | 3482.3 | 5007.7 | 1210.2 | 0.67822 | 7.098
2024-12-09 | 22:14 | Data | 0 | 30.644 | 27.653 | 237.878 | 7.62 | 222.873 | 2232.47 | 25.89 | 41.304 | 6.28 | 1.504 | 5.576 | 9227.6 | 2.674 | 98.2 | 78.7 | 1452 | 20.65 | 5997.9 | 3431.9 | 3463.5 | 4976.1 | 1210.2 | 0.67418 | 7.081
2024-12-09 | 22:14 | Data | 0 | 30.205 | 27.322 | 238.013 | 7.62 | 222.873 | 2233.37 | 25.88 | 41.213 | 6.28 | 1.485 | 5.569 | 9281.87 | 2.761 | 98.2 | 79 | 1452 | 20.61 | 6033.2 | 3438.6 | 3427.7 | 4953.5 | 1210.3 | 0.67867 | 7.055
2024-12-09 | 22:14 | Data | 0 | 30.273 | 27.836 | 237.968 | 7.62 | 222.782 | 2241.5 | 25.88 | 41.213 | 6.29 | 1.491 | 5.59 | 9304.48 | 2.903 | 98.2 | 79 | 1457 | 20.65 | 6047.9 | 3409.4 | 3409.9 | 4922.3 | 1210.3 | 0.67918 | 7.077
2024-12-09 | 22:14 | Data | 0 | 30.408 | 27.424 | 237.742 | 7.62 | 222.827 | 2242.41 | 25.89 | 41.213 | 6.28 | 1.497 | 5.608 | 9309 | 2.775 | 98.2 | 78.9 | 1458 | 20.61 | 6050.9 | 3443.8 | 3425.1 | 4954 | 1210.3 | 0.6809 | 7.103
2024-12-09 | 22:14 | Data | 0 | 30.185 | 27.424 | 237.878 | 7.63 | 222.782 | 2241.5 | 25.88 | 41.304 | 6.28 | 1.5 | 5.598 | 9268.3 | 2.761 | 98.2 | 78.9 | 1458 | 20.65 | 6024.4 | 3455.5 | 3398.3 | 4936.6 | 1210.3 | 0.68521 | 7.097
2024-12-09 | 22:14 | Data | 0 | 30.198 | 27.451 | 237.878 | 7.62 | 222.647 | 2241.5 | 25.89 | 41.123 | 6.28 | 1.506 | 5.604 | 9232.13 | 2.707 | 98.2 | 78.8 | 1456 | 20.61 | 6000.9 | 3434.2 | 3418.8 | 4943 | 1210.3 | 0.6788 | 7.111
2024-12-09 | 22:14 | Data | 0 | 29.982 | 27.37 | 237.742 | 7.62 | 222.692 | 2240.6 | 25.89 | 41.213 | 6.28 | 1.498 | 5.593 | 9241.17 | 2.815 | 98.2 | 78.9 | 1456 | 20.65 | 6006.8 | 3433.9 | 3420.6 | 4940.8 | 1210.3 | 0.68053 | 7.092
2024-12-09 | 22:14 | Data | 0 | 30.084 | 27.201 | 237.697 | 7.62 | 222.827 | 2242.41 | 25.89 | 41.304 | 6.27 | 1.499 | 5.604 | 9250.21 | 2.748 | 98.2 | 78.9 | 1457 | 20.56 | 6012.6 | 3448.7 | 3436.6 | 4945.3 | 1210.3 | 0.68016 | 7.104
2024-12-09 | 22:14 | Data | 0 | 30.57 | 27.43 | 237.923 | 7.63 | 222.963 | 2240.6 | 25.89 | 41.213 | 6.29 | 1.492 | 5.609 | 9227.6 | 2.687 | 98.2 | 79 | 1456 | 20.65 | 5997.9 | 3458.9 | 3414.8 | 4955.7 | 1210.3 | 0.68305 | 7.101
2024-12-09 | 22:14 | Data | 0 | 30.415 | 27.451 | 238.013 | 7.63 | 222.827 | 2240.6 | 25.89 | 41.304 | 6.28 | 1.49 | 5.621 | 9214.04 | 2.964 | 98.2 | 79.1 | 1456 | 20.65 | 5989.1 | 3434.5 | 3446.7 | 4958.6 | 1210.3 | 0.67768 | 7.109
2024-12-09 | 22:14 | Data | 0 | 30.671 | 27.545 | 238.149 | 7.62 | 222.963 | 2241.5 | 25.88 | 41.213 | 6.28 | 1.501 | 5.605 | 9214.04 | 3.166 | 98.2 | 78.9 | 1458 | 20.61 | 5989.1 | 3452.6 | 3438 | 4967.8 | 1210.3 | 0.67997 | 7.106
2024-12-09 | 22:14 | Data | 0 | 30.489 | 27.599 | 238.013 | 7.63 | 222.963 | 2242.41 | 25.88 | 41.213 | 6.28 | 1.509 | 5.595 | 9263.78 | 2.606 | 98.2 | 78.7 | 1458 | 20.61 | 6021.5 | 3442.9 | 3430 | 4956.1 | 1210.3 | 0.67938 | 7.106
2024-12-09 | 22:14 | Data | 0 | 30.185 | 27.424 | 237.742 | 7.63 | 222.873 | 2241.5 | 25.88 | 41.213 | 6.28 | 1.507 | 5.613 | 9232.13 | 2.822 | 98.2 | 78.8 | 1457 | 20.56 | 6000.9 | 3463.3 | 3451.2 | 4982.9 | 1210.3 | 0.68015 | 7.121
2024-12-09 | 22:14 | Data | 0 | 30.361 | 27.694 | 237.923 | 7.62 | 222.873 | 2244.22 | 25.88 | 41.304 | 6.29 | 1.5 | 5.62 | 9272.83 | 2.849 | 98.2 | 78.9 | 1460 | 20.65 | 6027.3 | 3473 | 3435.4 | 4974.7 | 1210.3 | 0.68089 | 7.119
2024-12-09 | 22:15 | Data | 0 | 30.502 | 27.647 | 237.923 | 7.62 | 222.873 | 2243.31 | 25.88 | 41.213 | 6.28 | 1.504 | 5.591 | 9313.53 | 2.795 | 98.2 | 78.8 | 1459 | 20.65 | 6053.8 | 3440.4 | 3431.9 | 4955.1 | 1210.3 | 0.67888 | 7.093
2024-12-09 | 22:15 | Data | 0 | 30.455 | 27.538 | 237.968 | 7.63 | 222.873 | 2244.22 | 25.88 | 41.213 | 6.28 | 1.491 | 5.611 | 9322.57 | 2.775 | 98.2 | 79 | 1459 | 20.65 | 6059.7 | 3446.4 | 3405.7 | 4939.9 | 1210.3 | 0.68294 | 7.099
2024-12-09 | 22:15 | Data | 0 | 30.05 | 27.424 | 237.923 | 7.62 | 222.873 | 2244.22 | 25.89 | 41.304 | 6.28 | 1.495 | 5.601 | 9336.14 | 2.545 | 98.2 | 78.9 | 1458 | 20.65 | 6068.5 | 3446.7 | 3393.7 | 4931.6 | 1210.3 | 0.684 | 7.095
2024-12-09 | 22:15 | Data | 0 | 30.077 | 27.41 | 237.878 | 7.63 | 222.782 | 2246.93 | 25.89 | 41.213 | 6.28 | 1.496 | 5.575 | 9318.05 | 2.775 | 98.2 | 78.9 | 1461 | 20.56 | 6056.7 | 3450.7 | 3417.6 | 4950 | 1210.3 | 0.68197 | 7.07
2024-12-09 | 22:15 | Data | 0 | 30.219 | 27.397 | 237.832 | 7.62 | 222.827 | 2246.02 | 25.89 | 41.304 | 6.29 | 1.504 | 5.602 | 9254.74 | 2.876 | 98.2 | 78.8 | 1460 | 20.65 | 6015.6 | 3444.7 | 3430 | 4944.6 | 1210.3 | 0.67762 | 7.106
2024-12-09 | 22:15 | Data | 0 | 30.212 | 27.613 | 237.832 | 7.62 | 222.737 | 2246.02 | 25.89 | 40.943 | 6.29 | 1.499 | 5.6 | 9259.26 | 2.883 | 98.2 | 78.9 | 1461 | 20.52 | 6018.5 | 3451.9 | 3457.1 | 4978.8 | 1210.3 | 0.67818 | 7.099
2024-12-09 | 22:15 | Data | 0 | 29.976 | 27.424 | 237.697 | 7.62 | 222.827 | 2247.83 | 25.86 | 41.033 | 6.29 | 1.495 | 5.603 | 9254.74 | 2.653 | 98.2 | 78.9 | 1461 | 20.47 | 6015.6 | 3438.9 | 3442.4 | 4958.5 | 1210.3 | 0.67852 | 7.098
2024-12-09 | 22:15 | Data | 0 | 30.415 | 27.43 | 237.878 | 7.62 | 222.963 | 2246.93 | 25.88 | 41.033 | 6.28 | 1.494 | 5.573 | 9250.21 | 2.964 | 98.2 | 78.9 | 1460 | 20.52 | 6012.6 | 3440.2 | 3452.5 | 4970.7 | 1210.3 | 0.67723 | 7.068
2024-12-09 | 22:15 | Data | 0 | 30.442 | 27.201 | 237.878 | 7.62 | 222.827 | 2244.22 | 25.88 | 41.033 | 6.28 | 1.487 | 5.563 | 9281.87 | 2.802 | 98.2 | 78.9 | 1459 | 20.52 | 6033.2 | 3467.6 | 3464.5 | 4992.7 | 1210.3 | 0.67928 | 7.048
2024-12-09 | 22:15 | Data | 0 | 30.388 | 27.863 | 238.013 | 7.62 | 222.873 | 2242.41 | 25.89 | 41.033 | 6.28 | 1.502 | 5.61 | 9295.44 | 2.714 | 98.2 | 78.9 | 1458 | 20.52 | 6042 | 3460.2 | 3439.1 | 4974.2 | 1210.3 | 0.68017 | 7.112
2024-12-09 | 22:15 | Data | 0 | 30.198 | 27.538 | 238.013 | 7.63 | 222.963 | 2244.22 | 25.88 | 41.213 | 6.28 | 1.498 | 5.63 | 9281.87 | 2.761 | 98.2 | 79 | 1458 | 20.65 | 6033.2 | 3417 | 3422.3 | 4933.3 | 1210.3 | 0.67803 | 7.128
2024-12-09 | 22:15 | Data | 0 | 30.388 | 27.424 | 238.149 | 7.62 | 222.963 | 2244.22 | 25.88 | 41.213 | 6.28 | 1.511 | 5.621 | 9299.96 | 2.984 | 98.2 | 78.8 | 1459 | 20.65 | 6045 | 3417.5 | 3428 | 4938.2 | 1210.3 | 0.67818 | 7.134
2024-12-09 | 22:15 | Data | 0 | 30.705 | 27.484 | 237.923 | 7.62 | 222.963 | 2246.93 | 25.89 | 41.033 | 6.28 | 1.512 | 5.63 | 9322.57 | 2.89 | 98.2 | 78.8 | 1461 | 20.47 | 6059.7 | 3429.7 | 3398.9 | 4921.5 | 1210.3 | 0.68184 | 7.141
2024-12-09 | 22:15 | Data | 0 | 30.192 | 27.255 | 237.923 | 7.62 | 222.827 | 2246.02 | 25.88 | 41.123 | 6.28 | 1.506 | 5.635 | 9309 | 2.869 | 98.2 | 78.9 | 1461 | 20.52 | 6050.9 | 3437.9 | 3431.4 | 4952.8 | 1210.3 | 0.68038 | 7.14
2024-12-09 | 22:15 | Data | 0 | 30.361 | 27.592 | 237.832 | 7.62 | 222.782 | 2246.93 | 25.88 | 41.033 | 6.28 | 1.504 | 5.63 | 9309 | 2.815 | 98.2 | 78.9 | 1461 | 20.52 | 6050.9 | 3453 | 3390.9 | 4932.8 | 1210.3 | 0.68528 | 7.134
2024-12-09 | 22:15 | Data | 0 | 30.428 | 27.869 | 237.878 | 7.62 | 223.053 | 2246.93 | 25.88 | 40.943 | 6.28 | 1.511 | 5.611 | 9313.53 | 2.714 | 98.2 | 78.8 | 1460 | 20.47 | 6053.8 | 3460.2 | 3426 | 4962.5 | 1210.3 | 0.68299 | 7.123
2024-12-09 | 22:15 | Data | 0 | 30.577 | 27.788 | 237.787 | 7.62 | 222.963 | 2246.02 | 25.89 | 40.943 | 6.28 | 1.507 | 5.593 | 9268.3 | 2.91 | 98.2 | 78.8 | 1460 | 20.47 | 6024.4 | 3471.2 | 3413.6 | 4977.1 | 1210.3 | 0.68737 | 7.101
2024-12-09 | 22:16 | Data | 0 | 30.036 | 27.37 | 237.787 | 7.63 | 222.827 | 2247.83 | 25.89 | 41.033 | 6.28 | 1.513 | 5.639 | 9268.3 | 2.647 | 98.2 | 78.9 | 1462 | 20.47 | 6024.4 | 3451.8 | 3406.9 | 4946.3 | 1210.3 | 0.68422 | 7.152
2024-12-09 | 22:16 | Data | 0 | 30.59 | 27.984 | 238.104 | 7.62 | 222.873 | 2246.93 | 25.88 | 41.123 | 6.28 | 1.5 | 5.615 | 9268.3 | 2.741 | 98.2 | 78.9 | 1461 | 20.56 | 6024.4 | 3435.3 | 3430.6 | 4956.1 | 1210.4 | 0.67728 | 7.115
2024-12-09 | 22:16 | Data | 0 | 30.361 | 27.714 | 238.104 | 7.63 | 223.008 | 2246.02 | 25.88 | 41.304 | 6.28 | 1.497 | 5.582 | 9263.78 | 2.863 | 98.2 | 78.9 | 1461 | 20.65 | 6021.5 | 3440.6 | 3449.9 | 4970 | 1210.4 | 0.67534 | 7.078
2024-12-09 | 22:16 | Data | 0 | 30.408 | 27.255 | 237.832 | 7.63 | 222.782 | 2245.12 | 25.88 | 41.304 | 6.28 | 1.504 | 5.594 | 9295.44 | 2.957 | 98.2 | 78.8 | 1459 | 20.61 | 6042 | 3453.6 | 3425.4 | 4949.9 | 1210.4 | 0.67999 | 7.097
2024-12-09 | 22:16 | Data | 0 | 30.421 | 27.815 | 238.013 | 7.63 | 222.827 | 2241.5 | 25.88 | 41.304 | 6.28 | 1.492 | 5.631 | 9299.96 | 2.788 | 98.2 | 79 | 1456 | 20.61 | 6045 | 3415.4 | 3433.3 | 4940.5 | 1210.4 | 0.6751 | 7.123
2024-12-09 | 22:16 | Data | 0 | 30.307 | 27.849 | 238.013 | 7.63 | 223.008 | 2244.22 | 25.89 | 41.213 | 6.29 | 1.485 | 5.603 | 9281.87 | 2.728 | 98.2 | 79 | 1459 | 20.61 | 6033.2 | 3461.3 | 3429 | 4965.3 | 1210.4 | 0.68161 | 7.088
2024-12-09 | 22:16 | Data | 0 | 30.016 | 27.424 | 237.787 | 7.62 | 222.873 | 2246.93 | 25.88 | 41.213 | 6.28 | 1.496 | 5.594 | 9277.35 | 2.728 | 98.2 | 78.9 | 1461 | 20.61 | 6030.3 | 3443.1 | 3403.8 | 4936.3 | 1210.4 | 0.68301 | 7.09
2024-12-09 | 22:16 | Data | 0 | 30.759 | 27.68 | 238.149 | 7.63 | 222.873 | 2245.12 | 25.88 | 41.304 | 6.28 | 1.507 | 5.633 | 9272.83 | 2.836 | 98.2 | 78.9 | 1459 | 20.61 | 6027.3 | 3459.4 | 3409.1 | 4953.6 | 1210.4 | 0.68359 | 7.139
2024-12-09 | 22:16 | Data | 0 | 30.205 | 27.538 | 238.013 | 7.63 | 222.782 | 2244.22 | 25.88 | 41.213 | 6.28 | 1.495 | 5.616 | 9286.39 | 2.768 | 98.2 | 79 | 1459 | 20.65 | 6036.2 | 3436.4 | 3438.9 | 4960.1 | 1210.4 | 0.6777 | 7.111
2024-12-09 | 22:16 | Data | 0 | 30.361 | 27.64 | 237.923 | 7.63 | 222.827 | 2241.5 | 25.88 | 41.304 | 6.28 | 1.5 | 5.601 | 9309 | 2.809 | 98.2 | 78.9 | 1457 | 20.65 | 6050.9 | 3466.6 | 3450.4 | 4981.6 | 1210.4 | 0.68139 | 7.1
2024-12-09 | 22:16 | Data | 0 | 30.408 | 27.424 | 237.878 | 7.62 | 222.963 | 2244.22 | 25.88 | 41.033 | 6.28 | 1.488 | 5.603 | 9277.35 | 2.991 | 98.2 | 79 | 1459 | 20.52 | 6030.3 | 3440.8 | 3450.9 | 4967.3 | 1210.4 | 0.67728 | 7.091
2024-12-09 | 22:16 | Data | 0 | 30.185 | 27.397 | 237.832 | 7.63 | 222.827 | 2246.02 | 25.88 | 40.943 | 6.29 | 1.493 | 5.604 | 9254.74 | 2.869 | 98.2 | 79 | 1460 | 20.47 | 6015.6 | 3452.9 | 3417.3 | 4953.5 | 1210.4 | 0.68257 | 7.097
2024-12-09 | 22:16 | Data | 0 | 30.219 | 27.538 | 237.968 | 7.62 | 222.963 | 2244.22 | 25.89 | 41.033 | 6.29 | 1.494 | 5.584 | 9268.3 | 2.653 | 98.2 | 78.9 | 1459 | 20.52 | 6024.4 | 3454.9 | 3416.6 | 4955.6 | 1210.4 | 0.68131 | 7.078
2024-12-09 | 22:16 | Data | 0 | 30.631 | 28.038 | 237.968 | 7.63 | 222.963 | 2244.22 | 25.89 | 41.213 | 6.28 | 1.495 | 5.599 | 9286.39 | 2.788 | 98.2 | 78.9 | 1459 | 20.61 | 6036.2 | 3443.1 | 3402.6 | 4935.8 | 1210.4 | 0.68288 | 7.093
2024-12-09 | 22:16 | Data | 0 | 30.786 | 27.329 | 237.878 | 7.62 | 222.963 | 2420.46 | 25.88 | 41.213 | 6.28 | 1.491 | 5.618 | 9268.3 | 2.822 | 98.3 | 79 | 1573 | 20.65 | 6024.4 | 3447.4 | 3410.5 | 4945 | 1210.4 | 0.68261 | 7.109
2024-12-09 | 22:16 | Data | 0 | 30.415 | 27.701 | 237.968 | 7.62 | 222.963 | 2242.41 | 25.89 | 41.213 | 6.28 | 1.503 | 5.599 | 9245.69 | 2.66 | 98.2 | 78.8 | 1458 | 20.61 | 6009.7 | 3442.2 | 3421.7 | 4945.9 | 1210.4 | 0.68128 | 7.102
2024-12-09 | 22:16 | Data | 0 | 30.252 | 27.511 | 238.104 | 7.62 | 223.008 | 2239.7 | 25.89 | 41.304 | 6.28 | 1.502 | 5.6 | 9254.74 | 2.674 | 98.2 | 78.8 | 1456 | 20.65 | 6015.6 | 3429.8 | 3412 | 4936.8 | 1210.4 | 0.67952 | 7.102
2024-12-09 | 22:16 | Data | 0 | 30.469 | 27.538 | 237.878 | 7.62 | 222.963 | 2241.5 | 25.88 | 41.304 | 6.28 | 1.502 | 5.576 | 9254.74 | 2.66 | 98.2 | 78.8 | 1456 | 20.65 | 6015.6 | 3455.8 | 3461.9 | 4985.5 | 1210.4 | 0.67788 | 7.08
2024-12-09 | 22:17 | Data | 0 | 30.415 | 27.424 | 237.923 | 7.63 | 222.782 | 2241.5 | 25.88 | 41.213 | 6.29 | 1.503 | 5.593 | 9250.21 | 2.788 | 98.2 | 78.8 | 1457 | 20.61 | 6012.6 | 3442.2 | 3430 | 4959 | 1210.4 | 0.67923 | 7.098
2024-12-09 | 22:17 | Data | 0 | 30.408 | 27.478 | 237.787 | 7.63 | 222.873 | 2244.22 | 25.89 | 41.304 | 6.28 | 1.502 | 5.583 | 9272.83 | 2.903 | 98.2 | 78.8 | 1458 | 20.65 | 6027.3 | 3440.7 | 3437.6 | 4955.8 | 1210.4 | 0.67929 | 7.085
2024-12-09 | 22:17 | Data | 0 | 30.529 | 27.538 | 237.968 | 7.63 | 223.008 | 2245.12 | 25.88 | 41.213 | 6.28 | 1.513 | 5.604 | 9281.87 | 2.984 | 98.2 | 78.7 | 1459 | 20.56 | 6033.2 | 3440.9 | 3425.6 | 4951.2 | 1210.4 | 0.68249 | 7.117
2024-12-09 | 22:17 | Data | 0 | 30.671 | 27.667 | 237.878 | 7.63 | 223.008 | 2246.02 | 25.88 | 41.123 | 6.29 | 1.499 | 5.604 | 9272.83 | 2.768 | 98.2 | 78.9 | 1461 | 20.65 | 6027.3 | 3442 | 3422.5 | 4952.4 | 1210.4 | 0.67983 | 7.104
2024-12-09 | 22:17 | Data | 0 | 30.759 | 27.667 | 238.104 | 7.63 | 223.008 | 2244.22 | 25.88 | 41.213 | 6.28 | 1.5 | 5.6 | 9272.83 | 2.809 | 98.2 | 78.9 | 1459 | 20.61 | 6027.3 | 3443.8 | 3438 | 4960.4 | 1210.4 | 0.68087 | 7.099
2024-12-09 | 22:17 | Data | 0 | 30.705 | 27.383 | 237.832 | 7.63 | 223.053 | 2244.22 | 25.86 | 41.213 | 6.28 | 1.495 | 5.582 | 9263.78 | 2.782 | 98.2 | 78.9 | 1459 | 20.61 | 6021.5 | 3436.7 | 3397 | 4941.4 | 1210.4 | 0.68152 | 7.076
2024-12-09 | 22:17 | Data | 0 | 30.185 | 27.586 | 237.923 | 7.63 | 222.827 | 2244.22 | 25.88 | 41.304 | 6.28 | 1.49 | 5.595 | 9476.33 | 2.876 | 98.2 | 79 | 1459 | 20.65 | 6159.6 | 3440.8 | 3406 | 4936.2 | 1210.4 | 0.68207 | 7.086
2024-12-09 | 22:17 | Data | 0 | 30.523 | 27.869 | 238.149 | 7.62 | 223.008 | 2244.22 | 25.89 | 41.213 | 6.28 | 1.497 | 5.576 | 9471.8 | 3.099 | 98.2 | 78.8 | 1459 | 20.56 | 6156.7 | 3450.4 | 3419 | 4952.7 | 1210.4 | 0.68116 | 7.074
2024-12-09 | 22:17 | Data | 0 | 30.671 | 27.505 | 237.742 | 7.63 | 222.737 | 2239.7 | 25.89 | 41.213 | 6.28 | 1.499 | 5.562 | 9480.85 | 3.031 | 98.2 | 78.8 | 1456 | 20.65 | 6162.6 | 3451.3 | 3408.1 | 4945.5 | 1210.4 | 0.68347 | 7.06
2024-12-09 | 22:17 | Data | 0 | 30.597 | 27.768 | 238.104 | 7.62 | 223.053 | 2244.22 | 25.89 | 41.304 | 6.28 | 1.503 | 5.605 | 9453.71 | 2.937 | 98.2 | 78.9 | 1458 | 20.65 | 6144.9 | 3477.1 | 3428 | 4980.1 | 1210.4 | 0.68302 | 7.108
2024-12-09 | 22:17 | Data | 0 | 30.475 | 27.43 | 238.194 | 7.62 | 222.827 | 2244.22 | 25.88 | 41.213 | 6.28 | 1.493 | 5.601 | 9241.17 | 2.822 | 98.2 | 79 | 1459 | 20.61 | 6006.8 | 3459.6 | 3410.2 | 4952 | 1210.4 | 0.68258 | 7.094
2024-12-09 | 22:17 | Data | 0 | 30.415 | 27.822 | 237.878 | 7.63 | 222.963 | 2243.31 | 25.89 | 41.304 | 6.29 | 1.495 | 5.611 | 9236.65 | 2.836 | 98.2 | 79 | 1459 | 20.65 | 6003.8 | 3434.7 | 3424.1 | 4948.8 | 1210.4 | 0.67922 | 7.106
2024-12-09 | 22:17 | Data | 0 | 30.307 | 27.795 | 238.013 | 7.62 | 222.873 | 2245.12 | 25.89 | 41.213 | 6.28 | 1.508 | 5.628 | 9241.17 | 2.944 | 98.2 | 78.9 | 1459 | 20.56 | 6006.8 | 3429.5 | 3414.5 | 4933.7 | 1210.4 | 0.68061 | 7.135
2024-12-09 | 22:17 | Data | 0 | 30.185 | 27.923 | 237.968 | 7.63 | 222.782 | 2245.12 | 25.89 | 41.304 | 6.28 | 1.489 | 5.618 | 9241.17 | 2.829 | 98.2 | 79 | 1459 | 20.65 | 6006.8 | 3425 | 3426.2 | 4941.9 | 1210.4 | 0.67787 | 7.107
2024-12-09 | 22:17 | Data | 0 | 30.192 | 27.647 | 237.742 | 7.62 | 222.827 | 2246.93 | 25.88 | 41.213 | 6.28 | 1.491 | 5.585 | 9236.65 | 2.748 | 98.2 | 78.9 | 1461 | 20.65 | 6003.8 | 3435.3 | 3391.4 | 4923.8 | 1210.5 | 0.68246 | 7.077
2024-12-09 | 22:17 | Data | 0 | 30.3 | 27.478 | 237.787 | 7.62 | 222.782 | 2247.83 | 25.89 | 41.304 | 6.28 | 1.494 | 5.581 | 9245.69 | 2.863 | 98.2 | 78.9 | 1461 | 20.65 | 6009.7 | 3437.8 | 3395.1 | 4924.6 | 1210.5 | 0.68276 | 7.075
2024-12-09 | 22:17 | Data | 0 | 30.3 | 27.505 | 237.968 | 7.63 | 222.873 | 2246.02 | 25.89 | 41.213 | 6.29 | 1.489 | 5.586 | 9223.08 | 2.599 | 98.2 | 79 | 1461 | 20.65 | 5995 | 3441.4 | 3408.2 | 4938.7 | 1210.5 | 0.68215 | 7.074
2024-12-09 | 22:18 | Data | 0 | 30.327 | 27.214 | 237.832 | 7.63 | 222.963 | 2246.93 | 25.86 | 41.304 | 6.28 | 1.495 | 5.562 | 9223.08 | 2.984 | 98.2 | 78.8 | 1461 | 20.65 | 5995 | 3459 | 3384.6 | 4933.2 | 1210.5 | 0.68638 | 7.058
2024-12-09 | 22:18 | Data | 0 | 30.556 | 27.43 | 237.878 | 7.62 | 223.008 | 2246.02 | 25.88 | 41.304 | 6.28 | 1.496 | 5.575 | 9227.6 | 2.667 | 98.2 | 78.8 | 1460 | 20.65 | 5997.9 | 3446.5 | 3379.2 | 4921 | 1210.5 | 0.68544 | 7.071
2024-12-09 | 22:18 | Data | 0 | 30.556 | 27.545 | 238.149 | 7.63 | 222.827 | 2242.41 | 25.88 | 41.213 | 6.28 | 1.5 | 5.621 | 9218.56 | 2.991 | 98.2 | 78.9 | 1457 | 20.65 | 5992.1 | 3444.2 | 3401.9 | 4938.8 | 1210.5 | 0.68231 | 7.121
2024-12-09 | 22:18 | Data | 0 | 30.415 | 27.653 | 237.923 | 7.62 | 222.827 | 2241.5 | 25.89 | 41.304 | 6.28 | 1.494 | 5.606 | 9245.69 | 2.761 | 98.2 | 78.9 | 1457 | 20.61 | 6009.7 | 3432.8 | 3374.9 | 4910.8 | 1210.5 | 0.68322 | 7.101
2024-12-09 | 22:18 | Data | 0 | 30.185 | 27.538 | 237.787 | 7.62 | 222.873 | 2242.41 | 25.89 | 41.304 | 6.28 | 1.485 | 5.62 | 9227.6 | 2.876 | 98.2 | 79.1 | 1457 | 20.61 | 5997.9 | 3441.6 | 3396.5 | 4930 | 1210.5 | 0.68231 | 7.106
2024-12-09 | 22:18 | Data | 0 | 30.131 | 27.417 | 237.878 | 7.63 | 222.827 | 2239.7 | 25.88 | 41.213 | 6.29 | 1.489 | 5.601 | 9277.35 | 2.748 | 98.2 | 79 | 1455 | 20.61 | 6030.3 | 3440.6 | 3428 | 4951.1 | 1210.5 | 0.6795 | 7.09
2024-12-09 | 22:18 | Data | 0 | 30.475 | 27.451 | 237.878 | 7.63 | 222.963 | 2238.79 | 25.89 | 41.304 | 6.28 | 1.493 | 5.623 | 8856.78 | 2.788 | 98.2 | 79 | 1455 | 20.65 | 5756.9 | 3451.7 | 3394.2 | 4934.1 | 1210.5 | 0.68467 | 7.116
2024-12-09 | 22:18 | Data | 0 | 30.171 | 27.424 | 237.742 | 7.63 | 222.827 | 2239.7 | 25.89 | 41.213 | 6.28 | 1.485 | 5.588 | 9295.44 | 2.815 | 98.2 | 79 | 1456 | 20.61 | 6042 | 3448.9 | 3417.7 | 4958.7 | 1210.5 | 0.6815 | 7.073
2024-12-09 | 22:18 | Data | 0 | 29.969 | 27.809 | 237.968 | 7.62 | 222.963 | 2238.79 | 25.88 | 41.304 | 6.28 | 1.502 | 5.603 | 9299.96 | 2.815 | 98.2 | 78.9 | 1454 | 20.61 | 6045 | 3434.3 | 3416 | 4939.3 | 1210.5 | 0.67901 | 7.106
2024-12-09 | 22:18 | Data | 0 | 30.361 | 27.694 | 237.878 | 7.62 | 222.827 | 2238.79 | 25.88 | 41.213 | 6.28 | 1.496 | 5.616 | 9281.87 | 2.761 | 98.2 | 79 | 1455 | 20.61 | 6033.2 | 3442.6 | 3417.1 | 4945.3 | 1210.5 | 0.68112 | 7.111
2024-12-09 | 22:18 | Data | 0 | 30.023 | 27.586 | 238.104 | 7.62 | 222.873 | 2239.7 | 25.89 | 41.304 | 6.28 | 1.5 | 5.62 | 9272.83 | 2.728 | 98.2 | 78.9 | 1455 | 20.65 | 6027.3 | 3448.1 | 3401.6 | 4937.5 | 1210.5 | 0.68355 | 7.121
2024-12-09 | 22:18 | Data | 0 | 30.516 | 27.383 | 237.878 | 7.62 | 222.782 | 2238.79 | 25.89 | 41.304 | 6.28 | 1.509 | 5.627 | 9277.35 | 2.998 | 98.2 | 78.9 | 1455 | 20.61 | 6030.3 | 3438.5 | 3383.5 | 4921.6 | 1210.5 | 0.68227 | 7.134
2024-12-09 | 22:18 | Data | 0 | 30.475 | 27.545 | 238.013 | 7.63 | 223.053 | 2239.7 | 25.88 | 41.213 | 6.28 | 1.501 | 5.605 | 9295.44 | 2.876 | 98.2 | 78.9 | 1456 | 20.56 | 6042 | 3429.6 | 3399.3 | 4925.3 | 1210.5 | 0.68099 | 7.106
2024-12-09 | 22:18 | Data | 0 | 30.185 | 27.532 | 237.923 | 7.63 | 222.827 | 2236.98 | 25.89 | 41.304 | 6.28 | 1.502 | 5.606 | 9309 | 2.957 | 98.2 | 78.9 | 1455 | 20.65 | 6050.9 | 3451.9 | 3379.2 | 4926.8 | 1210.5 | 0.68375 | 7.11
2024-12-09 | 22:18 | Data | 0 | 30.644 | 27.667 | 238.104 | 7.63 | 223.053 | 2238.79 | 25.88 | 41.123 | 6.28 | 1.504 | 5.636 | 9299.96 | 2.822 | 98.2 | 78.9 | 1456 | 20.61 | 6045 | 3439 | 3408.7 | 4938.1 | 1210.5 | 0.68161 | 7.138
2024-12-09 | 22:18 | Data | 0 | 30.847 | 27.903 | 238.149 | 7.63 | 223.144 | 2238.79 | 25.88 | 41.304 | 6.28 | 1.501 | 5.626 | 9299.96 | 2.809 | 98.2 | 78.9 | 1455 | 20.65 | 6045 | 3446.2 | 3393 | 4930 | 1210.5 | 0.68456 | 7.127
2024-12-09 | 22:18 | Data | 0 | 30.3 | 27.538 | 237.832 | 7.63 | 222.873 | 2236.08 | 25.89 | 41.304 | 6.28 | 1.5 | 5.613 | 9304.48 | 2.95 | 98.2 | 78.9 | 1454 | 20.65 | 6047.9 | 3412.5 | 3432.5 | 4939.3 | 1210.5 | 0.6756 | 7.113
2024-12-09 | 22:18 | Data | 0 | 30.388 | 27.457 | 237.923 | 7.62 | 222.963 | 2235.18 | 25.89 | 41.213 | 6.28 | 1.499 | 5.615 | 9295.44 | 2.734 | 98.2 | 78.9 | 1453 | 20.61 | 6042 | 3468.5 | 3430.1 | 4969.8 | 1210.5 | 0.68302 | 7.115
2024-12-09 | 22:19 | Data | 0 | 30.624 | 27.707 | 238.013 | 7.62 | 222.963 | 2234.27 | 25.88 | 41.304 | 6.28 | 1.495 | 5.614 | 9295.44 | 2.768 | 98.2 | 79 | 1452 | 20.65 | 6042 | 3447.4 | 3417.6 | 4951.7 | 1210.5 | 0.68017 | 7.108
2024-12-09 | 22:19 | Data | 0 | 30.415 | 27.424 | 237.968 | 7.63 | 222.963 | 2235.18 | 25.89 | 41.213 | 6.29 | 1.489 | 5.597 | 9309 | 2.991 | 98.2 | 79 | 1453 | 20.61 | 6050.9 | 3449.6 | 3419.4 | 4950.8 | 1210.5 | 0.68222 | 7.087
2024-12-09 | 22:19 | Data | 0 | 30.637 | 27.505 | 238.013 | 7.62 | 223.008 | 2235.18 | 25.86 | 41.213 | 6.29 | 1.5 | 5.627 | 9318.05 | 2.768 | 98.2 | 79 | 1454 | 20.65 | 6056.7 | 3430.6 | 3401 | 4928.7 | 1210.5 | 0.68044 | 7.125
2024-12-09 | 22:19 | Data | 0 | 30.307 | 27.836 | 237.878 | 7.62 | 223.053 | 2233.37 | 25.89 | 41.394 | 6.28 | 1.508 | 5.62 | 9331.61 | 2.782 | 98.2 | 78.8 | 1452 | 20.61 | 6065.5 | 3433.9 | 3403.5 | 4932.5 | 1210.5 | 0.68053 | 7.129
2024-12-09 | 22:19 | Data | 0 | 30.577 | 28.085 | 237.923 | 7.63 | 222.873 | 2238.79 | 25.88 | 41.213 | 6.28 | 1.495 | 5.625 | 9345.18 | 2.869 | 98.2 | 79 | 1456 | 20.61 | 6074.4 | 3435.1 | 3380.2 | 4921.6 | 1210.5 | 0.68312 | 7.121
2024-12-09 | 22:19 | Data | 0 | 30.28 | 27.383 | 237.968 | 7.62 | 223.053 | 2238.79 | 25.89 | 41.304 | 6.28 | 1.515 | 5.595 | 9327.09 | 2.633 | 98.2 | 78.7 | 1455 | 20.65 | 6062.6 | 3458.5 | 3410.3 | 4952.9 | 1210.5 | 0.68319 | 7.111
2024-12-09 | 22:19 | Data | 0 | 30.185 | 27.619 | 237.652 | 7.63 | 222.737 | 2238.79 | 25.88 | 41.213 | 6.28 | 1.505 | 5.61 | 9322.57 | 2.775 | 98.2 | 78.9 | 1455 | 20.52 | 6059.7 | 3438.4 | 3385.6 | 4921.3 | 1210.5 | 0.68427 | 7.114
2024-12-09 | 22:19 | Data | 0 | 30.104 | 27.309 | 237.832 | 7.63 | 222.827 | 2238.79 | 25.89 | 41.304 | 6.28 | 1.503 | 5.603 | 9277.35 | 2.552 | 98.2 | 78.8 | 1454 | 20.65 | 6030.3 | 3435.3 | 3393.7 | 4925.6 | 1210.5 | 0.68227 | 7.106
2024-12-09 | 22:19 | Data | 0 | 30.678 | 27.451 | 237.968 | 7.63 | 222.963 | 2238.79 | 25.89 | 41.304 | 6.28 | 1.501 | 5.604 | 9299.96 | 2.674 | 98.2 | 78.9 | 1455 | 20.61 | 6045 | 3434.5 | 3382.2 | 4916.1 | 1210.5 | 0.68202 | 7.106
2024-12-09 | 22:19 | Data | 0 | 30.205 | 27.424 | 237.923 | 7.62 | 222.827 | 2238.79 | 25.88 | 41.213 | 6.28 | 1.507 | 5.592 | 9299.96 | 2.68 | 98.2 | 78.8 | 1456 | 20.65 | 6045 | 3453.9 | 3380.8 | 4926.5 | 1210.5 | 0.6846 | 7.1
2024-12-09 | 22:19 | Data | 0 | 30.266 | 27.329 | 238.013 | 7.63 | 223.008 | 2239.7 | 25.88 | 41.213 | 6.28 | 1.51 | 5.628 | 9299.96 | 2.856 | 98.2 | 78.8 | 1454 | 20.65 | 6045 | 3441.8 | 3401 | 4933.3 | 1210.6 | 0.68329 | 7.137
2024-12-09 | 22:19 | Data | 0 | 30.3 | 27.451 | 237.923 | 7.62 | 222.873 | 2239.7 | 25.88 | 41.213 | 6.28 | 1.506 | 5.61 | 9299.96 | 2.971 | 98.2 | 78.9 | 1455 | 20.65 | 6045 | 3439.5 | 3399.3 | 4936.3 | 1210.6 | 0.68466 | 7.116
2024-12-09 | 22:19 | Data | 0 | 30.529 | 27.552 | 237.923 | 7.63 | 223.008 | 2238.79 | 25.89 | 41.213 | 6.28 | 1.502 | 5.579 | 9309 | 2.896 | 98.2 | 78.8 | 1455 | 20.61 | 6050.9 | 3428.5 | 3384.3 | 4916.6 | 1210.6 | 0.68207 | 7.08
2024-12-09 | 22:19 | Data | 0 | 30.185 | 27.815 | 237.832 | 7.62 | 222.827 | 2241.5 | 25.88 | 41.213 | 6.28 | 1.502 | 5.621 | 9322.57 | 2.761 | 98.2 | 78.9 | 1456 | 20.56 | 6059.7 | 3430.1 | 3406.3 | 4931 | 1210.6 | 0.68058 | 7.124
2024-12-09 | 22:19 | Data | 0 | 30.408 | 27.424 | 237.832 | 7.63 | 222.873 | 2244.22 | 25.88 | 41.304 | 6.28 | 1.506 | 5.621 | 9322.57 | 2.869 | 98.2 | 78.9 | 1458 | 20.61 | 6059.7 | 3444.6 | 3423.2 | 4951.5 | 1210.6 | 0.68011 | 7.126
2024-12-09 | 22:19 | Data | 0 | 30.185 | 27.424 | 237.832 | 7.63 | 223.008 | 2244.22 | 25.88 | 41.304 | 6.28 | 1.5 | 5.609 | 9313.53 | 2.93 | 98.2 | 78.9 | 1459 | 20.65 | 6053.8 | 3438.7 | 3373.3 | 4911.9 | 1210.6 | 0.68492 | 7.11
2024-12-09 | 22:19 | Data | 0 | 30.185 | 27.511 | 237.878 | 7.63 | 222.827 | 2244.22 | 25.88 | 41.304 | 6.28 | 1.503 | 5.591 | 9336.14 | 2.815 | 98.2 | 78.8 | 1459 | 20.61 | 6068.5 | 3448.3 | 3390.9 | 4921.9 | 1210.6 | 0.68146 | 7.094
2024-12-09 | 22:19 | Data | 0 | 30.192 | 27.538 | 237.832 | 7.62 | 222.782 | 2245.12 | 25.88 | 41.304 | 6.28 | 1.509 | 5.587 | 9322.57 | 2.761 | 98.2 | 78.7 | 1460 | 20.65 | 6059.7 | 3447 | 3387.2 | 4927.2 | 1210.6 | 0.68448 | 7.096
2024-12-09 | 22:20 | Data | 0 | 30.59 | 27.451 | 237.832 | 7.62 | 222.873 | 2248.73 | 25.88 | 41.213 | 6.29 | 1.494 | 5.606 | 9327.09 | 3.085 | 98.2 | 79 | 1462 | 20.61 | 6062.6 | 3432.7 | 3393.6 | 4922.2 | 1210.6 | 0.68293 | 7.1
2024-12-09 | 22:20 | Data | 0 | 30.415 | 27.309 | 237.923 | 7.63 | 222.873 | 2247.83 | 25.89 | 41.213 | 6.28 | 1.497 | 5.617 | 9327.09 | 2.93 | 98.2 | 78.9 | 1462 | 20.65 | 6062.6 | 3443.9 | 3368.7 | 4913.9 | 1210.6 | 0.6866 | 7.115
2024-12-09 | 22:20 | Data | 0 | 30.036 | 27.424 | 237.968 | 7.62 | 222.873 | 2252.35 | 25.89 | 41.213 | 6.28 | 1.511 | 5.596 | 9299.96 | 2.565 | 98.2 | 78.7 | 1464 | 20.56 | 6045 | 3435.1 | 3356.9 | 4896.8 | 1210.6 | 0.6864 | 7.106
2024-12-09 | 22:20 | Data | 0 | 30.388 | 27.43 | 237.923 | 7.62 | 223.053 | 2255.97 | 25.88 | 41.304 | 6.28 | 1.5 | 5.592 | 9304.48 | 2.775 | 98.2 | 78.9 | 1465 | 20.61 | 6047.9 | 3448.1 | 3353.6 | 4905 | 1210.6 | 0.68587 | 7.091
2024-12-09 | 22:20 | Data | 0 | 30.415 | 27.64 | 237.923 | 7.63 | 222.963 | 2255.97 | 25.89 | 41.304 | 6.28 | 1.493 | 5.588 | 9295.44 | 2.89 | 98.2 | 78.9 | 1466 | 20.7 | 6042 | 3443.2 | 3395.5 | 4931.4 | 1210.6 | 0.68337 | 7.085
2024-12-09 | 22:20 | Data | 0 | 30.131 | 27.424 | 237.878 | 7.63 | 222.827 | 2255.97 | 25.88 | 41.213 | 6.28 | 1.512 | 5.584 | 9309 | 2.923 | 98.2 | 78.7 | 1466 | 20.65 | 6050.9 | 3412 | 3395.2 | 4912.9 | 1210.6 | 0.67942 | 7.096
2024-12-09 | 22:20 | Data | 0 | 30.205 | 27.309 | 237.923 | 7.62 | 222.873 | 2253.25 | 25.88 | 41.213 | 6.28 | 1.504 | 5.592 | 9340.66 | 2.768 | 98.2 | 78.8 | 1465 | 20.65 | 6071.4 | 3434.1 | 3400.9 | 4927.3 | 1210.6 | 0.68189 | 7.096
2024-12-09 | 22:20 | Data | 0 | 30.293 | 27.626 | 237.878 | 7.62 | 222.827 | 2255.97 | 25.88 | 41.213 | 6.27 | 1.504 | 5.602 | 9358.75 | 2.775 | 98.2 | 78.8 | 1466 | 20.61 | 6083.2 | 3443.8 | 3397.9 | 4932.4 | 1210.6 | 0.68335 | 7.106
2024-12-09 | 22:20 | Data | 0 | 30.691 | 27.437 | 238.013 | 7.62 | 222.963 | 2255.97 | 25.89 | 41.304 | 6.28 | 1.502 | 5.619 | 9340.66 | 2.991 | 98.2 | 78.9 | 1465 | 20.65 | 6071.4 | 3441.2 | 3427.4 | 4946.4 | 1210.6 | 0.67835 | 7.121
2024-12-09 | 22:20 | Data | 0 | 30.185 | 27.633 | 237.832 | 7.63 | 222.827 | 2252.35 | 25.89 | 41.304 | 6.28 | 1.505 | 5.594 | 8888.44 | 2.734 | 98.2 | 78.8 | 1464 | 20.65 | 5777.5 | 3437.5 | 3447.2 | 4965.2 | 1210.6 | 0.67773 | 7.099
2024-12-09 | 22:20 | Data | 0 | 30.313 | 27.626 | 237.923 | 7.63 | 223.008 | 2252.35 | 25.88 | 41.213 | 6.29 | 1.505 | 5.571 | 9263.78 | 2.613 | 98.2 | 78.7 | 1464 | 20.61 | 6021.5 | 3435.8 | 3432.1 | 4954 | 1210.6 | 0.67836 | 7.075
2024-12-09 | 22:20 | Data | 0 | 30.462 | 27.316 | 237.878 | 7.62 | 223.053 | 2251.45 | 25.88 | 41.213 | 6.28 | 1.501 | 5.573 | 9263.78 | 2.809 | 98.2 | 78.8 | 1464 | 20.65 | 6021.5 | 3447.7 | 3420.7 | 4952.6 | 1210.6 | 0.68079 | 7.072
2024-12-09 | 22:20 | Data | 0 | 30.489 | 27.221 | 237.832 | 7.63 | 222.873 | 2252.35 | 25.89 | 41.213 | 6.28 | 1.497 | 5.592 | 9286.39 | 3.038 | 98.2 | 78.9 | 1464 | 20.56 | 6036.2 | 3423 | 3390.1 | 4914.4 | 1210.6 | 0.68084 | 7.089
2024-12-09 | 22:20 | Data | 0 | 30.408 | 27.626 | 237.787 | 7.62 | 222.827 | 2255.97 | 25.88 | 41.304 | 6.29 | 1.5 | 5.603 | 9281.87 | 2.815 | 98.2 | 78.9 | 1465 | 20.61 | 6033.2 | 3446.4 | 3384.2 | 4928.4 | 1210.6 | 0.68353 | 7.104
2024-12-09 | 22:20 | Data | 0 | 30.388 | 27.647 | 237.878 | 7.62 | 222.827 | 2254.16 | 25.89 | 41.213 | 6.28 | 1.503 | 5.602 | 9318.05 | 2.768 | 98.2 | 78.9 | 1465 | 20.61 | 6056.7 | 3436.8 | 3368.7 | 4908.7 | 1210.6 | 0.684 | 7.105
2024-12-09 | 22:20 | Data | 0 | 30.536 | 27.653 | 237.968 | 7.63 | 222.963 | 2252.35 | 25.86 | 41.213 | 6.28 | 1.492 | 5.592 | 9313.53 | 2.984 | 98.2 | 78.9 | 1465 | 20.61 | 6053.8 | 3437.1 | 3367.1 | 4906.7 | 1210.6 | 0.68635 | 7.086
2024-12-09 | 22:20 | Data | 0 | 30.921 | 27.478 | 238.013 | 7.62 | 223.008 | 2249.64 | 25.89 | 41.304 | 6.28 | 1.509 | 5.601 | 9322.57 | 2.977 | 98.2 | 78.8 | 1462 | 20.65 | 6059.7 | 3444.4 | 3379.2 | 4924.1 | 1210.6 | 0.68569 | 7.109
2024-12-09 | 22:20 | Data | 0 | 30.786 | 27.484 | 237.878 | 7.63 | 222.963 | 2246.93 | 25.89 | 41.213 | 6.28 | 1.496 | 5.62 | 9322.57 | 3.011 | 98.2 | 79 | 1461 | 20.56 | 6059.7 | 3474 | 3360.8 | 4926.8 | 1210.6 | 0.68956 | 7.116
2024-12-09 | 22:21 | Data | 0 | 30.212 | 27.376 | 237.968 | 7.63 | 222.827 | 2246.93 | 25.88 | 41.304 | 6.28 | 1.485 | 5.604 | 9309 | 2.971 | 98.2 | 79.1 | 1461 | 20.65 | 6050.9 | 3436.9 | 3358.9 | 4899.9 | 1210.6 | 0.68613 | 7.088
2024-12-09 | 22:21 | Data | 0 | 30.428 | 27.437 | 237.968 | 7.62 | 223.053 | 2246.93 | 25.89 | 41.213 | 6.28 | 1.491 | 5.599 | 9313.53 | 2.809 | 98.2 | 79 | 1461 | 20.61 | 6053.8 | 3439.4 | 3387.6 | 4920 | 1210.6 | 0.68517 | 7.09
2024-12-09 | 22:21 | Data | 0 | 30.428 | 27.255 | 237.923 | 7.63 | 223.053 | 2244.22 | 25.88 | 41.213 | 6.28 | 1.5 | 5.611 | 9313.53 | 2.883 | 98.2 | 78.9 | 1459 | 20.65 | 6053.8 | 3445.1 | 3404.6 | 4938.6 | 1210.6 | 0.6833 | 7.112
2024-12-09 | 22:21 | Data | 0 | 30.415 | 27.43 | 237.923 | 7.63 | 222.963 | 2246.93 | 25.89 | 41.213 | 6.28 | 1.511 | 5.612 | 9313.53 | 2.863 | 98.2 | 78.8 | 1460 | 20.65 | 6053.8 | 3461.8 | 3383.8 | 4935.4 | 1210.6 | 0.68603 | 7.125
2024-12-09 | 22:21 | Data | 0 | 30.55 | 27.667 | 238.104 | 7.63 | 223.008 | 2244.22 | 25.86 | 41.304 | 6.28 | 1.511 | 5.587 | 9313.53 | 2.775 | 98.2 | 78.7 | 1459 | 20.65 | 6053.8 | 3426.3 | 3378 | 4925.4 | 1210.6 | 0.68485 | 7.097
2024-12-09 | 22:21 | Data | 0 | 30.361 | 27.532 | 237.787 | 7.62 | 222.873 | 2245.12 | 25.88 | 41.304 | 6.28 | 1.5 | 5.601 | 9309 | 2.748 | 98.2 | 78.9 | 1459 | 20.61 | 6050.9 | 3458 | 3376.1 | 4907.8 | 1210.7 | 0.68396 | 7.1
2024-12-09 | 22:21 | Data | 0 | 30.806 | 27.457 | 237.968 | 7.62 | 222.963 | 2244.22 | 25.89 | 41.304 | 6.28 | 1.502 | 5.611 | 9313.53 | 2.944 | 98.2 | 78.9 | 1459 | 20.65 | 6053.8 | 3450.2 | 3408.9 | 4945.1 | 1210.7 | 0.68334 | 7.115
2024-12-09 | 22:21 | Data | 0 | 30.205 | 27.464 | 237.968 | 7.63 | 223.053 | 2245.12 | 25.88 | 41.304 | 6.28 | 1.505 | 5.598 | 9309 | 2.599 | 98.2 | 78.8 | 1459 | 20.61 | 6050.9 | 3451 | 3392.3 | 4943.7 | 1210.7 | 0.68753 | 7.102
2024-12-09 | 22:21 | Data | 0 | 30.415 | 27.599 | 237.878 | 7.63 | 222.963 | 2138.47 | 25.89 | 41.213 | 6.28 | 1.5 | 5.598 | 9309 | 2.876 | 98.1 | 78.9 | 1390 | 20.65 | 6050.9 | 3451.8 | 3381.5 | 4925.4 | 1210.7 | 0.68566 | 7.098
2024-12-09 | 22:21 | Data | 0 | 30.799 | 27.275 | 237.923 | 7.63 | 223.098 | 2242.41 | 25.88 | 41.213 | 6.28 | 1.509 | 5.582 | 9268.3 | 3.025 | 98.2 | 78.7 | 1458 | 20.61 | 6024.4 | 3427.1 | 3427 | 4942.1 | 1210.7 | 0.67847 | 7.088
2024-12-09 | 22:21 | Data | 0 | 30.874 | 27.991 | 238.013 | 7.63 | 223.053 | 2246.93 | 25.88 | 41.575 | 6.28 | 1.486 | 5.564 | 9268.3 | 2.89 | 98.1 | 78.9 | 1461 | 20.79 | 6024.4 | 3448.1 | 3414.3 | 4945.2 | 1210.7 | 0.68313 | 7.051
2024-12-09 | 22:21 | Data | 0 | 30.415 | 27.768 | 238.013 | 7.63 | 223.008 | 2244.22 | 25.89 | 41.304 | 6.28 | 1.495 | 5.604 | 9268.3 | 2.768 | 98.2 | 78.9 | 1459 | 20.61 | 6024.4 | 3439 | 3418.1 | 4942.1 | 1210.7 | 0.68165 | 7.096
2024-12-09 | 22:21 | Data | 0 | 30.637 | 27.653 | 237.832 | 7.63 | 222.963 | 2244.22 | 25.88 | 40.762 | 6.28 | 1.508 | 5.612 | 9263.78 | 2.876 | 98.2 | 78.8 | 1459 | 20.38 | 6021.5 | 3452 | 3403.1 | 4939.8 | 1210.7 | 0.68431 | 7.119
2024-12-09 | 22:21 | Data | 0 | 30.3 | 27.43 | 237.923 | 7.63 | 222.873 | 2246.93 | 25.89 | 41.304 | 6.28 | 1.512 | 5.6 | 9254.74 | 2.957 | 98.2 | 78.7 | 1461 | 20.61 | 6015.6 | 3442 | 3399 | 4932.6 | 1210.7 | 0.68243 | 7.113
2024-12-09 | 22:21 | Data | 0 | 30.644 | 27.768 | 238.013 | 7.63 | 223.098 | 2246.93 | 25.88 | 41.123 | 6.28 | 1.499 | 5.579 | 9250.21 | 2.937 | 98.2 | 78.8 | 1461 | 20.65 | 6012.6 | 3430.8 | 3376.1 | 4909.6 | 1210.7 | 0.68385 | 7.077
2024-12-09 | 22:21 | Data | 0 | 30.259 | 27.424 | 237.923 | 7.63 | 222.963 | 2241.5 | 25.89 | 41.304 | 6.28 | 1.499 | 5.575 | 9232.13 | 2.782 | 98.2 | 78.8 | 1457 | 20.65 | 6000.9 | 3439.4 | 3370.8 | 4912.8 | 1210.7 | 0.68509 | 7.074
2024-12-09 | 22:21 | Data | 0 | 30.415 | 27.856 | 237.923 | 7.62 | 222.963 | 2246.02 | 25.89 | 41.304 | 6.28 | 1.485 | 5.58 | 9254.74 | 2.802 | 98.2 | 79 | 1459 | 20.65 | 6015.6 | 3453.9 | 3347.4 | 4906.2 | 1210.7 | 0.69002 | 7.065
2024-12-09 | 22:22 | Data | 0 | 30.185 | 27.424 | 237.832 | 7.62 | 222.827 | 2245.12 | 25.89 | 41.304 | 6.28 | 1.492 | 5.611 | 9295.44 | 2.822 | 98.2 | 79 | 1458 | 20.65 | 6042 | 3463.9 | 3385.2 | 4936.7 | 1210.7 | 0.68759 | 7.105
2024-12-09 | 22:22 | Data | 0 | 30.415 | 27.977 | 238.013 | 7.63 | 223.008 | 2238.79 | 25.88 | 41.213 | 6.28 | 1.504 | 5.596 | 9295.44 | 2.68 | 98.2 | 78.8 | 1455 | 20.65 | 6042 | 3464.3 | 3380.1 | 4934.3 | 1210.7 | 0.68423 | 7.1
2024-12-09 | 22:22 | Data | 0 | 30.401 | 27.424 | 237.832 | 7.63 | 222.963 | 2242.41 | 25.88 | 41.213 | 6.28 | 1.498 | 5.633 | 9299.96 | 2.984 | 98.2 | 79 | 1458 | 20.65 | 6045 | 3444.7 | 3379.2 | 4916.2 | 1210.7 | 0.68519 | 7.131
2024-12-09 | 22:22 | Data | 0 | 30.529 | 28.038 | 238.149 | 7.63 | 223.053 | 2240.6 | 25.89 | 41.213 | 6.28 | 1.506 | 5.581 | 9281.87 | 2.714 | 98.2 | 78.8 | 1457 | 20.61 | 6033.2 | 3445 | 3403.8 | 4935.6 | 1210.7 | 0.68278 | 7.087
2024-12-09 | 22:22 | Data | 0 | 30.543 | 27.208 | 238.013 | 7.63 | 222.963 | 2241.5 | 25.89 | 41.304 | 6.28 | 1.5 | 5.586 | 9336.14 | 2.89 | 98.2 | 78.8 | 1457 | 20.56 | 6068.5 | 3427.8 | 3407.6 | 4930.1 | 1210.7 | 0.68035 | 7.084
2024-12-09 | 22:22 | Data | 0 | 30.624 | 27.876 | 237.923 | 7.63 | 223.008 | 2241.5 | 25.88 | 41.213 | 6.28 | 1.496 | 5.61 | 9327.09 | 2.883 | 98.2 | 78.9 | 1457 | 20.61 | 6062.6 | 3467.1 | 3412.8 | 4935.5 | 1210.7 | 0.68523 | 7.106
2024-12-09 | 22:22 | Data | 0 | 30.678 | 27.768 | 237.968 | 7.62 | 222.963 | 2242.41 | 25.89 | 41.213 | 6.28 | 1.502 | 5.599 | 9331.61 | 2.788 | 98.2 | 78.9 | 1458 | 20.61 | 6065.5 | 3440.9 | 3428.2 | 4946 | 1210.7 | 0.6793 | 7.099
2024-12-09 | 22:22 | Data | 0 | 30.394 | 27.822 | 237.832 | 7.62 | 222.873 | 2241.5 | 25.89 | 41.304 | 6.28 | 1.503 | 5.601 | 9318.05 | 2.883 | 98.2 | 78.8 | 1456 | 20.65 | 6056.7 | 3432.7 | 3424.9 | 4928.1 | 1210.7 | 0.67838 | 7.104
2024-12-09 | 22:22 | Data | 0 | 30.401 | 27.647 | 237.968 | 7.63 | 223.008 | 2241.5 | 25.88 | 41.304 | 6.28 | 1.498 | 5.585 | 9309 | 2.944 | 98.2 | 78.9 | 1458 | 20.65 | 6050.9 | 3455.9 | 3382.7 | 4927.3 | 1210.7 | 0.68656 | 7.084
2024-12-09 | 22:22 | Data | 0 | 30.192 | 27.538 | 237.923 | 7.62 | 223.008 | 2242.41 | 25.86 | 41.304 | 6.28 | 1.49 | 5.601 | 9313.53 | 2.761 | 98.2 | 79 | 1457 | 20.65 | 6053.8 | 3445.5 | 3403.3 | 4938.1 | 1210.7 | 0.68244 | 7.09
2024-12-09 | 22:22 | Data | 0 | 30.448 | 27.653 | 237.923 | 7.63 | 223.008 | 2241.5 | 25.88 | 41.304 | 6.28 | 1.5 | 5.611 | 9309 | 2.768 | 98.2 | 78.9 | 1457 | 20.65 | 6050.9 | 3423.4 | 3393.2 | 4917.8 | 1210.7 | 0.68086 | 7.111
2024-12-09 | 22:22 | Data | 0 | 30.252 | 27.43 | 238.104 | 7.63 | 223.053 | 2241.5 | 25.88 | 41.304 | 6.29 | 1.497 | 5.586 | 9309 | 2.761 | 98.2 | 78.9 | 1458 | 20.65 | 6050.9 | 3463.2 | 3362.8 | 4921.2 | 1210.7 | 0.68919 | 7.083
2024-12-09 | 22:22 | Data | 0 | 30.489 | 27.653 | 237.968 | 7.62 | 223.008 | 2243.31 | 25.88 | 41.304 | 6.28 | 1.503 | 5.591 | 9281.87 | 2.68 | 98.2 | 78.8 | 1459 | 20.56 | 6033.2 | 3428.2 | 3374.1 | 4904.9 | 1210.7 | 0.68373 | 7.093
2024-12-09 | 22:22 | Data | 0 | 30.415 | 27.653 | 237.832 | 7.63 | 222.782 | 2244.22 | 25.89 | 41.213 | 6.28 | 1.49 | 5.608 | 9281.87 | 2.761 | 98.2 | 79 | 1459 | 20.61 | 6033.2 | 3457.6 | 3404.9 | 4948 | 1210.7 | 0.68332 | 7.097
2024-12-09 | 22:22 | Data | 0 | 30.415 | 27.228 | 237.832 | 7.63 | 222.963 | 2245.12 | 25.88 | 41.213 | 6.28 | 1.501 | 5.618 | 9281.87 | 3.038 | 98.2 | 78.9 | 1459 | 20.65 | 6033.2 | 3435.1 | 3392.3 | 4922.2 | 1210.7 | 0.68324 | 7.117
2024-12-09 | 22:22 | Data | 0 | 30.361 | 27.538 | 237.787 | 7.62 | 222.873 | 2244.22 | 25.88 | 41.304 | 6.28 | 1.507 | 5.61 | 9277.35 | 2.565 | 98.2 | 78.8 | 1459 | 20.65 | 6030.3 | 3458.2 | 3388.7 | 4933.4 | 1210.7 | 0.68548 | 7.117
2024-12-09 | 22:22 | Data | 0 | 30.509 | 27.768 | 238.104 | 7.63 | 223.098 | 2244.22 | 25.88 | 41.213 | 6.28 | 1.503 | 5.584 | 9304.48 | 3.045 | 98.2 | 78.8 | 1459 | 20.61 | 6047.9 | 3419.6 | 3411.8 | 4926 | 1210.7 | 0.6795 | 7.087
2024-12-09 | 22:22 | Data | 0 | 30.415 | 27.424 | 237.832 | 7.62 | 223.008 | 2298.45 | 25.88 | 41.304 | 6.28 | 1.511 | 5.564 | 9322.57 | 2.788 | 98.2 | 78.6 | 1495 | 20.61 | 6059.7 | 3425.7 | 3384.3 | 4911.9 | 1210.7 | 0.68236 | 7.076
2024-12-09 | 22:23 | Data | 0 | 30.853 | 27.498 | 238.013 | 7.63 | 223.053 | 2298.45 | 25.89 | 41.213 | 6.29 | 1.499 | 5.577 | 9295.44 | 2.822 | 98.2 | 78.8 | 1493 | 20.61 | 6042 | 3425.5 | 3365 | 4897.9 | 1210.7 | 0.68379 | 7.075
2024-12-09 | 22:23 | Data | 0 | 30.928 | 27.694 | 238.104 | 7.62 | 223.053 | 2298.45 | 25.88 | 41.213 | 6.28 | 1.497 | 5.592 | 9309 | 2.977 | 98.2 | 78.9 | 1494 | 20.65 | 6050.9 | 3434.8 | 3393 | 4923.4 | 1210.8 | 0.68272 | 7.088
2024-12-09 | 22:23 | Data | 0 | 30.212 | 27.538 | 237.878 | 7.62 | 222.737 | 2295.73 | 25.88 | 41.304 | 6.28 | 1.489 | 5.587 | 9304.48 | 2.768 | 98.2 | 79 | 1493 | 20.65 | 6047.9 | 3442.3 | 3391.9 | 4930.5 | 1210.8 | 0.685 | 7.076
2024-12-09 | 22:23 | Data | 0 | 30.469 | 27.329 | 237.787 | 7.63 | 222.873 | 2242.41 | 25.89 | 41.123 | 6.28 | 1.5 | 5.586 | 9295.44 | 2.917 | 98.2 | 78.8 | 1458 | 20.56 | 6042 | 3416.6 | 3383.3 | 4905.5 | 1210.8 | 0.68087 | 7.086
2024-12-09 | 22:23 | Data | 0 | 30.205 | 27.626 | 238.104 | 7.63 | 222.963 | 2246.93 | 25.89 | 41.304 | 6.28 | 1.507 | 5.582 | 9295.44 | 2.66 | 98.2 | 78.7 | 1462 | 20.61 | 6042 | 3437.7 | 3390.9 | 4925.2 | 1210.8 | 0.6828 | 7.089
2024-12-09 | 22:23 | Data | 0 | 30.415 | 27.437 | 237.923 | 7.62 | 223.053 | 2246.93 | 25.88 | 41.213 | 6.28 | 1.513 | 5.578 | 9272.83 | 2.964 | 98.2 | 78.7 | 1461 | 20.65 | 6027.3 | 3458.3 | 3403.2 | 4944.8 | 1210.8 | 0.68369 | 7.09
2024-12-09 | 22:23 | Data | 0 | 30.374 | 27.43 | 237.968 | 7.63 | 223.098 | 2246.93 | 25.89 | 41.304 | 6.28 | 1.501 | 5.598 | 9272.83 | 2.775 | 98.2 | 78.9 | 1461 | 20.7 | 6027.3 | 3447.1 | 3401 | 4930.7 | 1210.8 | 0.68327 | 7.099
2024-12-09 | 22:23 | Data | 0 | 30.3 | 27.262 | 238.013 | 7.63 | 222.963 | 2246.93 | 25.89 | 41.213 | 6.28 | 1.504 | 5.602 | 9245.69 | 2.876 | 98.2 | 78.8 | 1461 | 20.56 | 6009.7 | 3434.3 | 3405.3 | 4932.6 | 1210.8 | 0.68246 | 7.106
2024-12-09 | 22:23 | Data | 0 | 30.705 | 27.511 | 238.013 | 7.62 | 223.008 | 2249.64 | 25.89 | 41.213 | 6.27 | 1.496 | 5.588 | 9268.3 | 2.937 | 98.2 | 78.9 | 1463 | 20.65 | 6024.4 | 3448.8 | 3422.7 | 4955.4 | 1210.8 | 0.68096 | 7.084
2024-12-09 | 22:23 | Data | 0 | 30.415 | 27.457 | 237.923 | 7.62 | 222.827 | 2248.73 | 25.89 | 41.213 | 6.28 | 1.502 | 5.563 | 9268.3 | 2.849 | 98.2 | 78.7 | 1462 | 20.65 | 6024.4 | 3429.6 | 3420.5 | 4940.4 | 1210.8 | 0.67887 | 7.067
2024-12-09 | 22:23 | Data | 0 | 30.3 | 27.626 | 237.968 | 7.62 | 222.873 | 2249.64 | 25.88 | 41.304 | 6.28 | 1.515 | 5.593 | 9268.3 | 2.977 | 98.2 | 78.7 | 1462 | 20.65 | 6024.4 | 3451.3 | 3396.7 | 4934.1 | 1210.8 | 0.68487 | 7.108
2024-12-09 | 22:23 | Data | 0 | 30.185 | 27.322 | 237.832 | 7.63 | 222.963 | 2247.83 | 25.88 | 41.213 | 6.28 | 1.496 | 5.626 | 9263.78 | 3.166 | 98.2 | 79 | 1462 | 20.61 | 6021.5 | 3433.9 | 3412.2 | 4935.4 | 1210.8 | 0.68115 | 7.123
2024-12-09 | 22:23 | Data | 0 | 30.334 | 27.424 | 237.968 | 7.62 | 223.053 | 2247.83 | 25.88 | 41.394 | 6.28 | 1.492 | 5.619 | 9277.35 | 2.795 | 98.2 | 79 | 1461 | 20.65 | 6030.3 | 3437.7 | 3386.7 | 4918.6 | 1210.8 | 0.68291 | 7.111
2024-12-09 | 22:23 | Data | 0 | 30.198 | 27.43 | 238.013 | 7.62 | 223.008 | 2246.93 | 25.89 | 41.123 | 6.28 | 1.502 | 5.599 | 9277.35 | 2.755 | 98.2 | 78.9 | 1461 | 20.61 | 6030.3 | 3462 | 3394.8 | 4925.1 | 1210.8 | 0.68613 | 7.1
2024-12-09 | 22:23 | Data | 0 | 29.982 | 27.809 | 238.104 | 7.62 | 222.963 | 2244.22 | 25.88 | 41.213 | 6.28 | 1.505 | 5.601 | 9281.87 | 2.64 | 98.2 | 78.8 | 1459 | 20.61 | 6033.2 | 3460 | 3406.8 | 4946.4 | 1210.8 | 0.68538 | 7.106
2024-12-09 | 22:23 | Data | 0 | 30.3 | 27.424 | 237.832 | 7.62 | 223.008 | 2244.22 | 25.89 | 41.123 | 6.28 | 1.505 | 5.6 | 9299.96 | 2.957 | 98.2 | 78.8 | 1459 | 20.61 | 6045 | 3433.1 | 3373.7 | 4905.2 | 1210.8 | 0.6854 | 7.106
2024-12-09 | 22:23 | Data | 0 | 30.759 | 27.565 | 237.878 | 7.62 | 222.873 | 2244.22 | 25.88 | 41.484 | 6.28 | 1.497 | 5.61 | 9277.35 | 2.849 | 98.1 | 78.9 | 1459 | 20.79 | 6030.3 | 3443.4 | 3386.1 | 4924.7 | 1210.8 | 0.68417 | 7.107
2024-12-09 | 22:23 | Data | 0 | 30.077 | 27.424 | 238.013 | 7.62 | 222.873 | 2244.22 | 25.88 | 41.304 | 6.28 | 1.5 | 5.592 | 9299.96 | 2.863 | 98.2 | 78.8 | 1459 | 20.7 | 6045 | 3436.5 | 3392.6 | 4921.7 | 1210.8 | 0.68268 | 7.092
2024-12-09 | 22:24 | Data | 0 | 30.3 | 27.336 | 237.878 | 7.63 | 222.827 | 2244.22 | 25.88 | 41.213 | 6.28 | 1.509 | 5.581 | 9304.48 | 3.038 | 98.2 | 78.7 | 1458 | 20.65 | 6047.9 | 3445.6 | 3399.1 | 4935.5 | 1210.8 | 0.68274 | 7.09
2024-12-09 | 22:24 | Data | 0 | 30.273 | 27.451 | 237.832 | 7.63 | 223.098 | 2244.22 | 25.88 | 41.304 | 6.28 | 1.51 | 5.567 | 9268.3 | 2.95 | 98.2 | 78.7 | 1459 | 20.61 | 6024.4 | 3459.9 | 3371.2 | 4927.3 | 1210.8 | 0.68365 | 7.077
2024-12-09 | 22:24 | Data | 0 | 30.266 | 28.025 | 238.194 | 7.62 | 223.053 | 2246.93 | 25.89 | 41.213 | 6.28 | 1.502 | 5.559 | 9281.87 | 2.626 | 98.2 | 78.7 | 1461 | 20.65 | 6033.2 | 3442.7 | 3403.7 | 4938.6 | 1210.8 | 0.68271 | 7.059
2024-12-09 | 22:24 | Data | 0 | 30.529 | 27.647 | 237.787 | 7.63 | 222.827 | 2245.12 | 25.89 | 41.304 | 6.28 | 1.502 | 5.583 | 8807.04 | 2.991 | 98.2 | 78.8 | 1460 | 20.65 | 5724.6 | 3427.3 | 3374.9 | 4908.2 | 1210.8 | 0.68386 | 7.087
2024-12-09 | 22:24 | Data | 0 | 30.415 | 27.761 | 237.923 | 7.63 | 222.873 | 2248.73 | 25.88 | 41.213 | 6.28 | 1.507 | 5.57 | 8834.17 | 2.775 | 98.2 | 78.7 | 1461 | 20.65 | 5742.2 | 3454 | 3394.3 | 4936.4 | 1210.8 | 0.68447 | 7.077
2024-12-09 | 22:24 | Data | 0 | 30.131 | 27.626 | 238.24 | 7.63 | 222.873 | 2235.18 | 25.89 | 41.123 | 6.28 | 1.511 | 5.592 | 9286.39 | 2.863 | 98.2 | 78.7 | 1454 | 20.61 | 6036.2 | 3442.8 | 3394.4 | 4927.4 | 1210.8 | 0.68442 | 7.105
2024-12-09 | 22:24 | Data | 0 | 30.415 | 27.437 | 237.832 | 7.62 | 222.963 | 2244.22 | 25.89 | 41.213 | 6.28 | 1.509 | 5.623 | 9313.53 | 2.795 | 98.2 | 78.8 | 1459 | 20.56 | 6053.8 | 3445.4 | 3367.2 | 4913.4 | 1210.8 | 0.68657 | 7.133
2024-12-09 | 22:24 | Data | 0 | 30.489 | 27.43 | 237.878 | 7.62 | 223.144 | 2244.22 | 25.88 | 41.033 | 6.28 | 1.505 | 5.619 | 9313.53 | 2.775 | 98.2 | 78.9 | 1459 | 20.56 | 6053.8 | 3439.1 | 3379.5 | 4912.9 | 1210.8 | 0.68645 | 7.123
2024-12-09 | 22:24 | Data | 0 | 30.361 | 27.849 | 237.968 | 7.63 | 223.008 | 2241.5 | 25.88 | 41.033 | 6.27 | 1.507 | 5.599 | 9774.79 | 2.923 | 98.2 | 78.8 | 1457 | 20.52 | 6353.6 | 3426.4 | 3384 | 4909.8 | 1210.8 | 0.6832 | 7.106
2024-12-09 | 22:24 | Data | 0 | 30.415 | 27.572 | 238.104 | 7.63 | 222.963 | 2241.5 | 25.89 | 40.943 | 6.28 | 1.497 | 5.592 | 9494.42 | 2.863 | 98.2 | 78.9 | 1458 | 20.47 | 6171.4 | 3447.3 | 3397.6 | 4934.9 | 1210.8 | 0.68373 | 7.087
2024-12-09 | 22:24 | Data | 0 | 30.583 | 27.613 | 237.968 | 7.63 | 223.053 | 2242.41 | 25.88 | 41.033 | 6.28 | 1.494 | 5.606 | 9498.94 | 2.822 | 98.2 | 78.9 | 1456 | 20.47 | 6174.3 | 3465.6 | 3444.9 | 4975.3 | 1210.8 | 0.68231 | 7.101
2024-12-09 | 22:24 | Data | 0 | 30.421 | 27.43 | 237.923 | 7.63 | 223.098 | 2235.18 | 25.89 | 40.943 | 6.28 | 1.498 | 5.646 | 9489.89 | 2.977 | 98.2 | 79 | 1453 | 20.56 | 6168.4 | 3437.3 | 3430.3 | 4954.3 | 1210.8 | 0.67919 | 7.144
2024-12-09 | 22:24 | Data | 0 | 30.529 | 28.038 | 238.149 | 7.63 | 223.053 | 2242.41 | 25.88 | 41.033 | 6.28 | 1.51 | 5.631 | 9485.37 | 2.775 | 98.2 | 78.9 | 1457 | 20.47 | 6165.5 | 3450.8 | 3433.3 | 4971.3 | 1210.8 | 0.68219 | 7.142
2024-12-09 | 22:24 | Data | 0 | 30.192 | 27.316 | 237.878 | 7.63 | 223.053 | 2240.6 | 25.88 | 41.033 | 6.28 | 1.514 | 5.615 | 9354.23 | 2.748 | 98.2 | 78.8 | 1457 | 20.52 | 6080.2 | 3446.8 | 3408.1 | 4946.2 | 1210.9 | 0.68216 | 7.128
2024-12-09 | 22:24 | Data | 0 | 30.448 | 27.64 | 237.968 | 7.63 | 222.963 | 2242.41 | 25.88 | 40.943 | 6.28 | 1.505 | 5.611 | 9336.14 | 2.714 | 98.2 | 78.9 | 1457 | 20.43 | 6068.5 | 3434.7 | 3420.7 | 4946.2 | 1210.9 | 0.68436 | 7.117
2024-12-09 | 22:24 | Data | 0 | 30.415 | 27.957 | 238.104 | 7.63 | 223.053 | 2240.6 | 25.88 | 41.033 | 6.28 | 1.51 | 5.597 | 9349.7 | 2.822 | 98.2 | 78.8 | 1456 | 20.52 | 6077.3 | 3438.5 | 3406.4 | 4934.7 | 1210.9 | 0.68181 | 7.108
2024-12-09 | 22:24 | Data | 0 | 30.415 | 27.876 | 237.923 | 7.63 | 223.053 | 2239.7 | 25.88 | 41.033 | 6.28 | 1.5 | 5.592 | 9349.7 | 2.714 | 98.2 | 78.8 | 1456 | 20.52 | 6077.3 | 3447.8 | 3403.9 | 4942.4 | 1210.9 | 0.6825 | 7.093
2024-12-09 | 22:24 | Data | 0 | 30.705 | 27.869 | 238.013 | 7.63 | 223.098 | 2242.41 | 25.88 | 41.033 | 6.28 | 1.495 | 5.601 | 9309 | 2.809 | 98.2 | 78.9 | 1458 | 20.52 | 6050.9 | 3452.4 | 3384.7 | 4928.2 | 1210.9 | 0.68571 | 7.096
2024-12-09 | 22:25 | Data | 0 | 30.428 | 27.856 | 238.013 | 7.62 | 223.053 | 2245.12 | 25.88 | 41.033 | 6.28 | 1.499 | 5.599 | 9272.83 | 2.66 | 98.2 | 78.9 | 1459 | 20.52 | 6027.3 | 3429.5 | 3390.8 | 4918 | 1210.9 | 0.68227 | 7.098
2024-12-09 | 22:25 | Data | 0 | 30.192 | 27.478 | 237.878 | 7.62 | 223.098 | 2245.12 | 25.86 | 41.213 | 6.28 | 1.507 | 5.592 | 9299.96 | 2.822 | 98.2 | 78.8 | 1459 | 20.56 | 6045 | 3438.3 | 3392.1 | 4928.7 | 1210.9 | 0.68183 | 7.099
2024-12-09 | 22:25 | Data | 0 | 30.496 | 28.045 | 237.878 | 7.63 | 223.053 | 2244.22 | 25.89 | 41.033 | 6.28 | 1.503 | 5.6 | 9286.39 | 2.856 | 98.2 | 78.8 | 1458 | 20.47 | 6036.2 | 3451.6 | 3398.7 | 4936.4 | 1210.9 | 0.6846 | 7.101
2024-12-09 | 22:25 | Data | 0 | 30.212 | 27.626 | 237.968 | 7.63 | 222.963 | 2244.22 | 25.88 | 41.033 | 6.28 | 1.5 | 5.616 | 9336.14 | 2.788 | 98.2 | 78.9 | 1459 | 20.52 | 6068.5 | 3459.5 | 3385.6 | 4933.2 | 1210.9 | 0.68697 | 7.115
2024-12-09 | 22:25 | Data | 0 | 30.543 | 27.829 | 238.24 | 7.63 | 222.963 | 2241.5 | 25.88 | 41.394 | 6.28 | 1.489 | 5.601 | 9327.09 | 2.863 | 98.2 | 79 | 1458 | 20.65 | 6062.6 | 3446.7 | 3396.9 | 4931.6 | 1210.9 | 0.68277 | 7.087
2024-12-09 | 22:25 | Data | 0 | 30.745 | 27.498 | 237.923 | 7.63 | 223.144 | 2242.41 | 25.88 | 41.304 | 6.29 | 1.499 | 5.617 | 9336.14 | 3.099 | 98.2 | 78.9 | 1458 | 20.7 | 6068.5 | 3457.8 | 3403.4 | 4933.2 | 1210.9 | 0.68399 | 7.116
2024-12-09 | 22:25 | Data | 0 | 30.59 | 28.065 | 238.013 | 7.62 | 223.008 | 2241.5 | 25.88 | 41.304 | 6.28 | 1.501 | 5.611 | 9254.74 | 2.694 | 98.2 | 78.9 | 1457 | 20.65 | 6015.6 | 3422.8 | 3421.8 | 4932.8 | 1210.9 | 0.67908 | 7.112
2024-12-09 | 22:25 | Data | 0 | 30.421 | 27.653 | 237.968 | 7.62 | 222.963 | 2235.18 | 25.88 | 41.213 | 6.28 | 1.496 | 5.611 | 9250.21 | 2.761 | 98.2 | 79 | 1453 | 20.56 | 6012.6 | 3436.3 | 3433 | 4954 | 1210.9 | 0.67904 | 7.106
2024-12-09 | 22:25 | Data | 0 | 30.583 | 27.444 | 238.149 | 7.63 | 223.098 | 2234.27 | 25.88 | 41.213 | 6.28 | 1.499 | 5.619 | 9254.74 | 2.809 | 98.2 | 79 | 1453 | 20.65 | 6015.6 | 3436.4 | 3392.2 | 4922.6 | 1210.9 | 0.68261 | 7.116
2024-12-09 | 22:25 | Data | 0 | 30.84 | 27.667 | 238.104 | 7.63 | 223.098 | 2238.79 | 25.89 | 41.304 | 6.29 | 1.497 | 5.603 | 9250.21 | 2.89 | 98.2 | 78.9 | 1455 | 20.61 | 6012.6 | 3436.1 | 3351.2 | 4899.3 | 1210.9 | 0.68608 | 7.1
2024-12-09 | 22:25 | Data | 0 | 30.442 | 27.43 | 238.013 | 7.62 | 222.873 | 2238.79 | 25.86 | 41.484 | 6.28 | 1.498 | 5.603 | 9263.78 | 2.815 | 98.1 | 78.9 | 1456 | 20.79 | 6021.5 | 3437.9 | 3364.1 | 4908 | 1210.9 | 0.68517 | 7.102
2024-12-09 | 22:25 | Data | 0 | 30.192 | 27.424 | 237.968 | 7.62 | 222.963 | 2242.41 | 25.89 | 41.213 | 6.28 | 1.507 | 5.614 | 9295.44 | 2.761 | 98.2 | 78.8 | 1458 | 20.61 | 6042 | 3458.1 | 3375.4 | 4930.2 | 1210.9 | 0.68624 | 7.122
2024-12-09 | 22:25 | Data | 0 | 30.3 | 27.923 | 237.878 | 7.63 | 222.963 | 2247.83 | 25.88 | 41.213 | 6.28 | 1.496 | 5.603 | 9281.87 | 2.903 | 98.2 | 78.9 | 1461 | 20.61 | 6033.2 | 3439.8 | 3373.7 | 4910.8 | 1210.9 | 0.68559 | 7.098
2024-12-09 | 22:25 | Data | 0 | 30.806 | 27.518 | 237.923 | 7.63 | 223.098 | 2240.6 | 25.88 | 41.213 | 6.28 | 1.503 | 5.599 | 9272.83 | 2.977 | 98.2 | 78.8 | 1457 | 20.65 | 6027.3 | 3419.4 | 3388.5 | 4911 | 1210.9 | 0.68102 | 7.102
2024-12-09 | 22:25 | Data | 0 | 30.408 | 27.498 | 238.104 | 7.62 | 223.008 | 2241.5 | 25.89 | 41.123 | 6.28 | 1.508 | 5.592 | 9060.28 | 2.937 | 98.2 | 78.8 | 1457 | 20.61 | 5889.2 | 3444.3 | 3377 | 4914.1 | 1210.9 | 0.68674 | 7.1
2024-12-09 | 22:25 | Data | 0 | 30.752 | 27.788 | 237.968 | 7.63 | 223.098 | 2241.5 | 25.89 | 41.213 | 6.28 | 1.491 | 5.582 | 9015.06 | 2.849 | 98.2 | 78.9 | 1456 | 20.65 | 5859.8 | 3438.2 | 3377.6 | 4918.6 | 1210.9 | 0.68349 | 7.075
2024-12-09 | 22:26 | Data | 0 | 30.624 | 27.876 | 237.968 | 7.63 | 223.053 | 2242.41 | 25.88 | 41.123 | 6.28 | 1.5 | 5.605 | 9019.58 | 2.768 | 98.2 | 78.9 | 1458 | 20.61 | 5862.7 | 3456.9 | 3394.1 | 4939.5 | 1210.9 | 0.68495 | 7.106
2024-12-09 | 22:26 | Data | 0 | 30.401 | 27.538 | 237.923 | 7.63 | 222.873 | 2242.41 | 25.89 | 41.394 | 6.28 | 1.51 | 5.603 | 8996.97 | 3.166 | 98.2 | 78.8 | 1458 | 20.65 | 5848 | 3438.8 | 3414.3 | 4940 | 1210.9 | 0.68129 | 7.115
2024-12-09 | 22:26 | Data | 0 | 30.259 | 27.424 | 237.923 | 7.62 | 223.008 | 2242.41 | 25.88 | 41.304 | 6.28 | 1.505 | 5.603 | 9186.9 | 2.795 | 98.2 | 78.8 | 1457 | 20.7 | 5971.5 | 3435.9 | 3396.7 | 4931.4 | 1210.9 | 0.68209 | 7.108
2024-12-09 | 22:26 | Data | 0 | 30.415 | 27.809 | 237.923 | 7.63 | 222.963 | 2241.5 | 25.88 | 41.123 | 6.28 | 1.499 | 5.617 | 9309 | 2.815 | 98.2 | 78.9 | 1457 | 20.7 | 6050.9 | 3454.3 | 3382.8 | 4930.5 | 1210.9 | 0.68521 | 7.115
2024-12-09 | 22:26 | Data | 0 | 30.651 | 27.498 | 238.013 | 7.63 | 223.053 | 2240.6 | 25.88 | 41.213 | 6.28 | 1.501 | 5.625 | 9309 | 2.822 | 98.2 | 78.9 | 1457 | 20.65 | 6050.9 | 3442 | 3393.3 | 4932.5 | 1210.9 | 0.68261 | 7.125
2024-12-09 | 22:26 | Data | 0 | 30.415 | 27.424 | 237.923 | 7.63 | 222.873 | 2241.5 | 25.88 | 41.213 | 6.28 | 1.514 | 5.63 | 9295.44 | 2.876 | 98.2 | 78.8 | 1458 | 20.56 | 6042 | 3425.8 | 3399.9 | 4919.9 | 1210.9 | 0.68237 | 7.143
2024-12-09 | 22:26 | Data | 0 | 30.388 | 27.532 | 237.923 | 7.62 | 222.827 | 2241.5 | 25.89 | 41.213 | 6.28 | 1.501 | 5.602 | 9309 | 2.782 | 98.2 | 78.9 | 1457 | 20.65 | 6050.9 | 3440.3 | 3394.8 | 4933 | 1210.9 | 0.6823 | 7.104
2024-12-09 | 22:26 | Data | 0 | 30.415 | 27.869 | 238.013 | 7.63 | 223.098 | 2241.5 | 25.88 | 41.304 | 6.28 | 1.494 | 5.622 | 9263.78 | 2.768 | 98.2 | 79 | 1456 | 20.65 | 6021.5 | 3427 | 3404.9 | 4931.1 | 1210.9 | 0.68038 | 7.115
2024-12-09 | 22:26 | Data | 0 | 30.664 | 28.052 | 238.285 | 7.63 | 223.144 | 2245.12 | 25.86 | 41.213 | 6.28 | 1.495 | 5.6 | 9286.39 | 2.775 | 98.2 | 78.9 | 1459 | 20.61 | 6036.2 | 3436.7 | 3393.9 | 4927.4 | 1210.9 | 0.68195 | 7.095
2024-12-09 | 22:26 | Data | 0 | 30.361 | 27.653 | 237.832 | 7.63 | 222.873 | 2244.22 | 25.88 | 41.213 | 6.28 | 1.494 | 5.609 | 9277.35 | 2.734 | 98.2 | 79 | 1459 | 20.65 | 6030.3 | 3447.8 | 3379.5 | 4924.9 | 1211 | 0.68462 | 7.104
2024-12-09 | 22:26 | Data | 0 | 30.246 | 27.64 | 237.923 | 7.63 | 223.053 | 2244.22 | 25.88 | 41.123 | 6.28 | 1.493 | 5.61 | 9281.87 | 2.734 | 98.2 | 79 | 1459 | 20.56 | 6033.2 | 3443.9 | 3384.5 | 4921.7 | 1211 | 0.68472 | 7.104
2024-12-09 | 22:26 | Data | 0 | 30.644 | 27.444 | 238.013 | 7.63 | 223.008 | 2241.5 | 25.88 | 41.304 | 6.28 | 1.499 | 5.603 | 9268.3 | 2.964 | 98.2 | 78.9 | 1458 | 20.61 | 6024.4 | 3419.2 | 3412.2 | 4926.4 | 1211 | 0.67902 | 7.1
2024-12-09 | 22:26 | Data | 0 | 30.252 | 27.538 | 238.013 | 7.63 | 223.008 | 2252.35 | 25.88 | 41.213 | 6.28 | 1.505 | 5.602 | 9281.87 | 2.572 | 98.2 | 78.8 | 1464 | 20.61 | 6033.2 | 3432.6 | 3398.8 | 4925.5 | 1211 | 0.68029 | 7.106
2024-12-09 | 22:26 | Data | 0 | 30.415 | 27.647 | 238.013 | 7.63 | 222.827 | 2246.93 | 25.88 | 41.213 | 6.28 | 1.501 | 5.59 | 9263.78 | 2.788 | 98.2 | 78.8 | 1461 | 20.56 | 6021.5 | 3444.3 | 3407.7 | 4940.2 | 1211 | 0.68355 | 7.094
2024-12-09 | 22:26 | Data | 0 | 30.489 | 27.451 | 238.149 | 7.62 | 223.008 | 2246.02 | 25.88 | 41.304 | 6.28 | 1.497 | 5.592 | 9281.87 | 2.761 | 98.2 | 78.9 | 1461 | 20.61 | 6033.2 | 3447 | 3369.6 | 4926.6 | 1211 | 0.68207 | 7.087
2024-12-09 | 22:26 | Data | 0 | 30.421 | 27.768 | 237.968 | 7.62 | 222.963 | 2249.64 | 25.88 | 41.213 | 6.28 | 1.512 | 5.612 | 9263.78 | 2.883 | 98.2 | 78.8 | 1462 | 20.56 | 6021.5 | 3429.6 | 3365.7 | 4903.8 | 1211 | 0.68367 | 7.125
2024-12-09 | 22:26 | Data | 0 | 30.59 | 28.072 | 237.968 | 7.63 | 223.144 | 2247.83 | 25.89 | 41.304 | 6.28 | 1.496 | 5.617 | 9263.78 | 2.701 | 98.2 | 79 | 1461 | 20.61 | 6021.5 | 3444.8 | 3355 | 4906.7 | 1211 | 0.68669 | 7.113
2024-12-09 | 22:26 | Data | 0 | 30.185 | 27.424 | 237.923 | 7.63 | 222.827 | 2243.31 | 25.88 | 41.394 | 6.28 | 1.494 | 5.592 | 9277.35 | 2.937 | 98.2 | 78.9 | 1458 | 20.65 | 6030.3 | 3450.9 | 3350.4 | 4903.2 | 1211 | 0.68943 | 7.087
2024-12-09 | 22:27 | Data | 0 | 30.759 | 27.68 | 238.013 | 7.63 | 223.234 | 2249.64 | 25.88 | 41.213 | 6.28 | 1.5 | 5.609 | 9304.48 | 2.802 | 98.2 | 78.9 | 1463 | 20.61 | 6047.9 | 3459.3 | 3376.6 | 4924.3 | 1211 | 0.68684 | 7.109
2024-12-09 | 22:27 | Data | 0 | 30.415 | 27.822 | 237.787 | 7.63 | 222.963 | 2248.73 | 25.89 | 41.213 | 6.28 | 1.51 | 5.628 | 9322.57 | 2.775 | 98.2 | 78.8 | 1462 | 20.65 | 6059.7 | 3472.6 | 3382.7 | 4948.5 | 1211 | 0.68807 | 7.138
2024-12-09 | 22:27 | Data | 0 | 30.489 | 27.856 | 238.013 | 7.63 | 223.098 | 2246.93 | 25.89 | 41.213 | 6.28 | 1.507 | 5.611 | 9322.57 | 2.647 | 98.2 | 78.8 | 1461 | 20.61 | 6059.7 | 3455.8 | 3370.1 | 4926.9 | 1211 | 0.68578 | 7.117
2024-12-09 | 22:27 | Data | 0 | 30.401 | 27.437 | 237.923 | 7.63 | 222.963 | 2247.83 | 25.88 | 41.304 | 6.28 | 1.501 | 5.569 | 9318.05 | 2.93 | 98.2 | 78.8 | 1461 | 20.65 | 6056.7 | 3450.5 | 3394.2 | 4937 | 1211 | 0.6831 | 7.07
2024-12-09 | 22:27 | Data | 0 | 30.813 | 27.761 | 237.832 | 7.63 | 223.098 | 2250.54 | 25.89 | 41.213 | 6.28 | 1.511 | 5.582 | 9327.09 | 2.876 | 98.2 | 78.7 | 1462 | 20.61 | 6062.6 | 3451.8 | 3378.9 | 4927.3 | 1211 | 0.68464 | 7.094
2024-12-09 | 22:27 | Data | 0 | 30.394 | 27.437 | 237.832 | 7.63 | 223.008 | 2249.64 | 25.88 | 41.213 | 6.28 | 1.505 | 5.569 | 9318.05 | 2.937 | 98.2 | 78.7 | 1462 | 20.61 | 6056.7 | 3457.2 | 3390.2 | 4939.8 | 1211 | 0.6852 | 7.074
2024-12-09 | 22:27 | Data | 0 | 30.759 | 27.444 | 238.013 | 7.62 | 223.098 | 2249.64 | 25.88 | 41.304 | 6.28 | 1.5 | 5.587 | 9327.09 | 2.842 | 98.2 | 78.8 | 1462 | 20.61 | 6062.6 | 3451.4 | 3385.6 | 4929.7 | 1211 | 0.6847 | 7.087
2024-12-09 | 22:27 | Data | 0 | 30.57 | 27.66 | 238.149 | 7.63 | 223.144 | 2249.64 | 25.88 | 41.304 | 6.28 | 1.505 | 5.603 | 9331.61 | 2.694 | 98.2 | 78.8 | 1462 | 20.65 | 6065.5 | 3450.5 | 3409.4 | 4945.8 | 1211 | 0.68411 | 7.108
2024-12-09 | 22:27 | Data | 0 | 29.969 | 27.376 | 237.878 | 7.63 | 222.963 | 2245.12 | 25.88 | 41.213 | 6.28 | 1.507 | 5.609 | 9327.09 | 2.856 | 98.2 | 78.8 | 1459 | 20.61 | 6062.6 | 3460.4 | 3382.2 | 4935.3 | 1211 | 0.68588 | 7.116
2024-12-09 | 22:27 | Data | 0 | 30.415 | 27.478 | 237.787 | 7.63 | 222.873 | 2249.64 | 25.89 | 40.943 | 6.28 | 1.503 | 5.584 | 9327.09 | 2.876 | 98.2 | 78.8 | 1462 | 20.47 | 6062.6 | 3455 | 3400.8 | 4957.3 | 1211 | 0.68403 | 7.087
2024-12-09 | 22:27 | Data | 0 | 30.415 | 27.43 | 238.149 | 7.62 | 223.098 | 2248.73 | 25.88 | 41.213 | 6.28 | 1.494 | 5.595 | 9322.57 | 2.984 | 98.2 | 78.9 | 1462 | 20.65 | 6059.7 | 3464.9 | 3399.8 | 4953.5 | 1211 | 0.68385 | 7.088
2024-12-09 | 22:27 | Data | 0 | 30.388 | 27.701 | 238.104 | 7.63 | 222.963 | 2249.64 | 25.88 | 41.394 | 6.29 | 1.508 | 5.604 | 9309 | 3.011 | 98.2 | 78.8 | 1462 | 20.65 | 6050.9 | 3487.6 | 3418.3 | 4981.5 | 1211 | 0.68507 | 7.113
2024-12-09 | 22:27 | Data | 0 | 30.401 | 27.565 | 237.832 | 7.63 | 222.873 | 2252.35 | 25.88 | 41.213 | 6.28 | 1.505 | 5.597 | 9313.53 | 2.876 | 98.2 | 78.8 | 1464 | 20.61 | 6053.8 | 3480.7 | 3389.1 | 4946.3 | 1211 | 0.68497 | 7.103
2024-12-09 | 22:27 | Data | 0 | 30.536 | 27.768 | 237.878 | 7.62 | 223.008 | 2248.73 | 25.88 | 41.213 | 6.28 | 1.505 | 5.59 | 9322.57 | 2.728 | 98.2 | 78.8 | 1462 | 20.65 | 6059.7 | 3459.9 | 3329.8 | 4903.8 | 1211 | 0.69123 | 7.093
2024-12-09 | 22:27 | Data | 0 | 30.415 | 27.849 | 238.013 | 7.63 | 223.053 | 2246.93 | 25.88 | 41.304 | 6.28 | 1.494 | 5.601 | 9309 | 2.788 | 98.2 | 78.9 | 1460 | 20.61 | 6050.9 | 3476.5 | 3311.8 | 4899.6 | 1211 | 0.69357 | 7.096
2024-12-09 | 22:27 | Data | 0 | 30.361 | 27.856 | 237.923 | 7.62 | 222.963 | 2246.02 | 25.88 | 41.304 | 6.29 | 1.491 | 5.599 | 9281.87 | 2.944 | 98.2 | 79 | 1460 | 20.65 | 6033.2 | 3466.5 | 3420.3 | 4962.4 | 1211 | 0.68311 | 7.09
2024-12-09 | 22:27 | Data | 0 | 30.192 | 27.741 | 238.149 | 7.62 | 223.008 | 2246.93 | 25.89 | 41.213 | 6.28 | 1.497 | 5.608 | 9313.53 | 2.761 | 98.2 | 79 | 1461 | 20.61 | 6053.8 | 3438 | 3383.3 | 4922.4 | 1211 | 0.68271 | 7.103
2024-12-09 | 22:28 | Data | 0 | 30.82 | 27.592 | 238.149 | 7.62 | 223.053 | 2246.93 | 25.88 | 41.213 | 6.28 | 1.507 | 5.591 | 9281.87 | 2.937 | 98.2 | 78.8 | 1461 | 20.61 | 6033.2 | 3478.2 | 3384.3 | 4950.4 | 1211 | 0.68737 | 7.097
2024-12-09 | 22:28 | Data | 0 | 30.786 | 28.045 | 238.104 | 7.63 | 223.053 | 2243.31 | 25.89 | 41.304 | 6.28 | 1.502 | 5.604 | 9268.3 | 2.876 | 98.2 | 78.9 | 1459 | 20.65 | 6024.4 | 3468.7 | 3406.9 | 4957.9 | 1211 | 0.68437 | 7.106
2024-12-09 | 22:28 | Data | 0 | 30.307 | 27.849 | 238.013 | 7.63 | 223.098 | 2245.12 | 25.88 | 41.213 | 6.28 | 1.503 | 5.594 | 9245.69 | 2.701 | 98.2 | 78.8 | 1459 | 20.65 | 6009.7 | 3479.6 | 3388.8 | 4953.7 | 1211 | 0.68438 | 7.097
2024-12-09 | 22:28 | Data | 0 | 30.415 | 27.768 | 237.923 | 7.63 | 223.008 | 2243.31 | 25.88 | 41.304 | 6.28 | 1.51 | 5.571 | 9241.17 | 2.856 | 98.2 | 78.7 | 1459 | 20.65 | 6006.8 | 3463 | 3392.7 | 4949.6 | 1211 | 0.68388 | 7.082
2024-12-09 | 22:28 | Data | 0 | 29.989 | 27.586 | 237.878 | 7.62 | 222.963 | 2245.12 | 25.89 | 41.213 | 6.28 | 1.505 | 5.593 | 9268.3 | 2.647 | 98.2 | 78.8 | 1459 | 20.56 | 6024.4 | 3463.8 | 3391.4 | 4942.4 | 1211 | 0.6862 | 7.099
2024-12-09 | 22:28 | Data | 0 | 30.361 | 27.532 | 237.923 | 7.63 | 222.963 | 2245.12 | 25.86 | 41.304 | 6.28 | 1.503 | 5.605 | 9263.78 | 2.755 | 98.2 | 78.9 | 1458 | 20.65 | 6021.5 | 3437.4 | 3389 | 4948.1 | 1211.1 | 0.68445 | 7.107
2024-12-09 | 22:28 | Data | 0 | 30.421 | 27.538 | 237.878 | 7.62 | 223.098 | 2245.12 | 25.89 | 41.304 | 6.28 | 1.499 | 5.577 | 9268.3 | 2.761 | 98.2 | 78.8 | 1459 | 20.65 | 6024.4 | 3471.3 | 3398.4 | 4952.9 | 1211.1 | 0.68588 | 7.075
2024-12-09 | 22:28 | Data | 0 | 30.678 | 27.707 | 238.149 | 7.62 | 223.189 | 2242.41 | 25.85 | 41.213 | 6.28 | 1.497 | 5.571 | 9259.26 | 2.782 | 98.2 | 78.8 | 1457 | 20.65 | 6018.5 | 3452.4 | 3410.6 | 4950.6 | 1211.1 | 0.68219 | 7.068
2024-12-09 | 22:28 | Data | 0 | 30.225 | 27.424 | 238.104 | 7.63 | 223.008 | 2241.5 | 25.88 | 41.304 | 6.28 | 1.493 | 5.578 | 9263.78 | 2.768 | 98.2 | 78.9 | 1457 | 20.65 | 6021.5 | 3479.9 | 3413.5 | 4972.5 | 1211.1 | 0.68342 | 7.071
2024-12-09 | 22:28 | Data | 0 | 30.745 | 27.66 | 238.013 | 7.62 | 223.008 | 2241.5 | 25.88 | 41.304 | 6.28 | 1.503 | 5.588 | 9259.26 | 3.018 | 98.2 | 78.8 | 1457 | 20.61 | 6018.5 | 3466.6 | 3402.2 | 4958.9 | 1211.1 | 0.68376 | 7.09
2024-12-09 | 22:28 | Data | 0 | 30.388 | 27.43 | 237.787 | 7.63 | 222.873 | 2236.08 | 25.89 | 41.304 | 6.28 | 1.498 | 5.601 | 9254.74 | 2.923 | 98.2 | 78.9 | 1453 | 20.61 | 6015.6 | 3396.1 | 3388.3 | 4889.1 | 1211.1 | 0.67938 | 7.099
2024-12-09 | 22:28 | Data | 0 | 30.577 | 27.478 | 237.923 | 7.63 | 222.963 | 2235.18 | 25.89 | 41.213 | 6.28 | 1.491 | 5.582 | 9254.74 | 2.971 | 98.2 | 78.9 | 1453 | 20.65 | 6015.6 | 3417.8 | 3377.9 | 4885.3 | 1211.1 | 0.68479 | 7.074
2024-12-09 | 22:28 | Data | 0 | 30.415 | 27.592 | 238.194 | 7.63 | 223.098 | 2241.5 | 25.88 | 41.213 | 6.29 | 1.503 | 5.592 | 9254.74 | 2.761 | 98.2 | 78.8 | 1458 | 20.65 | 6015.6 | 3387.6 | 3365.9 | 4867.6 | 1211.1 | 0.68098 | 7.097
2024-12-09 | 22:28 | Data | 0 | 30.415 | 27.964 | 237.968 | 7.63 | 223.098 | 2242.41 | 25.88 | 41.213 | 6.28 | 1.499 | 5.601 | 9281.87 | 2.775 | 98.2 | 78.9 | 1458 | 20.65 | 6033.2 | 3414.7 | 3389.7 | 4901.5 | 1211.1 | 0.68009 | 7.098
2024-12-09 | 22:28 | Data | 0 | 30.381 | 27.626 | 237.832 | 7.63 | 222.873 | 2241.5 | 25.88 | 41.123 | 6.28 | 1.488 | 5.612 | 9281.87 | 2.822 | 98.2 | 79 | 1457 | 20.61 | 6033.2 | 3392.4 | 3361.5 | 4865.5 | 1211.1 | 0.6831 | 7.099
2024-12-09 | 22:28 | Data | 0 | 30.759 | 27.565 | 237.878 | 7.63 | 222.963 | 2241.5 | 25.89 | 41.304 | 6.28 | 1.495 | 5.63 | 9299.96 | 2.809 | 98.2 | 79 | 1458 | 20.65 | 6045 | 3386.6 | 3390.6 | 4882.5 | 1211.1 | 0.67849 | 7.124
2024-12-09 | 22:28 | Data | 0 | 30.415 | 27.964 | 237.923 | 7.62 | 223.008 | 2242.41 | 25.89 | 41.213 | 6.28 | 1.505 | 5.601 | 9277.35 | 2.795 | 98.2 | 78.8 | 1457 | 20.61 | 6030.3 | 3392.6 | 3357.1 | 4867 | 1211.1 | 0.68422 | 7.106
2024-12-09 | 22:28 | Data | 0 | 30.131 | 27.255 | 237.697 | 7.63 | 222.873 | 2240.6 | 25.89 | 41.304 | 6.28 | 1.51 | 5.561 | 9299.96 | 2.93 | 98.2 | 78.6 | 1456 | 20.65 | 6045 | 3412.9 | 3366.1 | 4880.8 | 1211.1 | 0.68341 | 7.071
2024-12-09 | 22:29 | Data | 0 | 30.408 | 27.599 | 237.968 | 7.62 | 222.963 | 2244.22 | 25.89 | 41.304 | 6.28 | 1.504 | 5.591 | 9318.05 | 2.991 | 98.2 | 78.8 | 1459 | 20.65 | 6056.7 | 3425.2 | 3388.9 | 4913 | 1211.1 | 0.6819 | 7.094
2024-12-09 | 22:29 | Data | 0 | 30.185 | 27.41 | 237.923 | 7.63 | 223.053 | 2244.22 | 25.88 | 41.304 | 6.28 | 1.507 | 5.609 | 9313.53 | 2.775 | 98.2 | 78.8 | 1459 | 20.65 | 6053.8 | 3443.5 | 3400.3 | 4936.6 | 1211.1 | 0.6821 | 7.115
2024-12-09 | 22:29 | Data | 0 | 30.732 | 27.268 | 237.968 | 7.62 | 223.053 | 2244.22 | 25.89 | 41.304 | 6.29 | 1.503 | 5.597 | 9318.05 | 2.984 | 98.2 | 78.8 | 1460 | 20.65 | 6056.7 | 3436 | 3441.6 | 4963 | 1211.1 | 0.67636 | 7.099
2024-12-09 | 22:29 | Data | 0 | 30.698 | 27.565 | 238.013 | 7.62 | 223.053 | 2241.5 | 25.88 | 41.213 | 6.28 | 1.49 | 5.623 | 9322.57 | 2.917 | 98.2 | 79 | 1457 | 20.65 | 6059.7 | 3458 | 3419.8 | 4959.8 | 1211.1 | 0.67987 | 7.115
2024-12-09 | 22:29 | Data | 0 | 30.901 | 27.248 | 237.968 | 7.63 | 222.963 | 2245.12 | 25.88 | 41.213 | 6.29 | 1.494 | 5.601 | 9340.66 | 3.085 | 98.2 | 78.9 | 1459 | 20.65 | 6071.4 | 3454.1 | 3438.7 | 4964.3 | 1211.1 | 0.68075 | 7.096
2024-12-09 | 22:29 | Data | 0 | 30.084 | 27.316 | 237.787 | 7.63 | 222.873 | 2246.02 | 25.89 | 41.304 | 6.28 | 1.508 | 5.573 | 9340.66 | 2.782 | 98.2 | 78.7 | 1460 | 20.61 | 6071.4 | 3458.6 | 3407 | 4949.1 | 1211.1 | 0.68347 | 7.081
2024-12-09 | 22:29 | Data | 0 | 30.09 | 27.255 | 237.968 | 7.63 | 222.963 | 2246.93 | 25.88 | 41.484 | 6.29 | 1.514 | 5.577 | 9367.79 | 2.565 | 98.2 | 78.6 | 1461 | 20.7 | 6089.1 | 3447 | 3410.2 | 4945.6 | 1211.1 | 0.68101 | 7.09
2024-12-09 | 22:29 | Data | 0 | 30.239 | 27.43 | 237.923 | 7.63 | 222.963 | 2242.41 | 25.89 | 41.213 | 6.28 | 1.499 | 5.574 | 9390.4 | 2.755 | 98.2 | 78.8 | 1458 | 20.61 | 6103.8 | 3435.8 | 3392.8 | 4928 | 1211.1 | 0.6818 | 7.073
2024-12-09 | 22:29 | Data | 0 | 30.165 | 27.599 | 237.787 | 7.63 | 223.008 | 2246.93 | 25.88 | 41.304 | 6.28 | 1.501 | 5.597 | 9367.79 | 2.93 | 98.2 | 78.9 | 1461 | 20.65 | 6089.1 | 3455.3 | 3411.6 | 4947.3 | 1211.1 | 0.68427 | 7.096
2024-12-09 | 22:29 | Data | 0 | 30.361 | 27.95 | 238.013 | 7.63 | 222.963 | 2246.93 | 25.88 | 41.845 | 6.28 | 1.501 | 5.595 | 9349.7 | 2.782 | 98.1 | 78.8 | 1461 | 20.92 | 6077.3 | 3457.1 | 3438.1 | 4968.6 | 1211.1 | 0.68133 | 7.096
2024-12-09 | 22:29 | Data | 0 | 30.259 | 27.619 | 238.013 | 7.62 | 222.963 | 2247.83 | 25.88 | 41.213 | 6.28 | 1.5 | 5.597 | 9299.96 | 2.606 | 98.2 | 78.9 | 1461 | 20.61 | 6045 | 3466.5 | 3431.9 | 4987.1 | 1211.1 | 0.67852 | 7.097
2024-12-09 | 22:29 | Data | 0 | 30.192 | 27.424 | 238.013 | 7.63 | 222.873 | 2249.64 | 25.89 | 41.123 | 6.28 | 1.488 | 5.586 | 9322.57 | 2.822 | 98.2 | 79 | 1463 | 20.61 | 6059.7 | 3433.3 | 3446.7 | 4958 | 1211.1 | 0.67898 | 7.075
2024-12-09 | 22:29 | Data | 0 | 30.361 | 27.707 | 237.878 | 7.63 | 222.782 | 2245.12 | 25.88 | 41.304 | 6.28 | 1.5 | 5.619 | 9295.44 | 2.991 | 98.2 | 78.9 | 1459 | 20.65 | 6042 | 3436.7 | 3432.5 | 4955.7 | 1211.1 | 0.67903 | 7.119
2024-12-09 | 22:29 | Data | 0 | 30.185 | 27.309 | 237.697 | 7.63 | 222.873 | 2247.83 | 25.88 | 41.304 | 6.28 | 1.503 | 5.611 | 9295.44 | 2.876 | 98.2 | 78.9 | 1461 | 20.61 | 6042 | 3449.6 | 3435 | 4963.5 | 1211.1 | 0.68046 | 7.115
2024-12-09 | 22:29 | Data | 0 | 30.198 | 27.957 | 237.878 | 7.62 | 222.873 | 2244.22 | 25.88 | 41.213 | 6.28 | 1.497 | 5.601 | 9336.14 | 2.795 | 98.2 | 78.9 | 1459 | 20.61 | 6068.5 | 3442.7 | 3427.3 | 4953.8 | 1211.1 | 0.67913 | 7.097
2024-12-09 | 22:29 | Data | 0 | 30.759 | 27.68 | 237.923 | 7.63 | 223.008 | 2243.31 | 25.89 | 41.213 | 6.28 | 1.499 | 5.593 | 9327.09 | 2.788 | 98.2 | 78.9 | 1459 | 20.65 | 6062.6 | 3457.9 | 3412.7 | 4952.9 | 1211.1 | 0.68329 | 7.092
2024-12-09 | 22:30 | Data | 0 | 30.361 | 27.451 | 237.832 | 7.63 | 222.873 | 2243.31 | 25.89 | 41.213 | 6.28 | 1.496 | 5.605 | 9331.61 | 2.937 | 98.2 | 78.9 | 1459 | 20.56 | 6065.5 | 3467.7 | 3408.8 | 4956.1 | 1211.2 | 0.68502 | 7.1
2024-12-09 | 22:30 | Data | 0 | 30.185 | 27.336 | 237.697 | 7.63 | 222.827 | 2245.12 | 25.88 | 41.213 | 6.28 | 1.499 | 5.573 | 9313.53 | 2.761 | 98.2 | 78.8 | 1459 | 20.61 | 6053.8 | 3431.8 | 3410.8 | 4938.5 | 1211.2 | 0.67865 | 7.072
2024-12-09 | 22:30 | Data | 0 | 29.213 | 26.073 | 236.973 | 7.62 | 222.195 | 2246.02 | 25.89 | 41.213 | 6.28 | 1.507 | 5.601 | 9313.53 | 2.768 | 98.2 | 78.8 | 1460 | 20.65 | 6053.8 | 3450.2 | 3411.4 | 4946.6 | 1211.2 | 0.68203 | 7.109
2024-12-09 | 22:30 | Data | 0 | 27.451 | 24.629 | 235.661 | 7.63 | 220.929 | 2247.83 | 25.88 | 41.213 | 6.28 | 1.495 | 5.559 | 9295.44 | 2.991 | 98.2 | 78.8 | 1461 | 20.65 | 6042 | 3471.8 | 3408.6 | 4962.6 | 1211.2 | 0.68444 | 7.054
2024-12-09 | 22:30 | Data | 0 | 27.106 | 24.372 | 235.842 | 7.63 | 221.2 | 2246.93 | 25.88 | 41.304 | 6.28 | 1.486 | 5.528 | 9309 | 2.869 | 98.2 | 78.8 | 1461 | 20.65 | 6050.9 | 3455.8 | 3426.8 | 4958.9 | 1211.2 | 0.68139 | 7.013
2024-12-09 | 22:30 | Data | 0 | 27.309 | 24.629 | 236.521 | 7.63 | 221.652 | 2248.73 | 25.89 | 41.123 | 6.28 | 1.488 | 5.549 | 9318.05 | 2.734 | 98.2 | 78.9 | 1462 | 20.56 | 6056.7 | 3478.6 | 3479.3 | 5007.9 | 1211.2 | 0.67952 | 7.037
2024-12-09 | 22:30 | Data | 0 | 27.403 | 24.041 | 236.747 | 7.63 | 221.788 | 2252.35 | 25.89 | 41.304 | 6.28 | 1.487 | 5.527 | 9299.96 | 3.065 | 98.2 | 78.8 | 1463 | 20.61 | 6045 | 3478.6 | 3468.4 | 5004.4 | 1211.2 | 0.67846 | 7.014
2024-12-09 | 22:30 | Data | 0 | 26.168 | 23.494 | 237.335 | 7.63 | 222.466 | 2252.35 | 25.89 | 41.304 | 6.28 | 1.498 | 5.542 | 9304.48 | 2.788 | 98.2 | 78.7 | 1464 | 20.61 | 6047.9 | 3466.9 | 3482.7 | 5007.8 | 1211.2 | 0.67704 | 7.037
2024-12-09 | 22:30 | Data | 0 | 27.424 | 24.824 | 238.33 | 7.63 | 223.324 | 2250.54 | 25.91 | 41.213 | 6.28 | 1.507 | 5.602 | 9309 | 2.971 | 98.2 | 78.8 | 1463 | 20.61 | 6050.9 | 3470.7 | 3448.9 | 4986.2 | 1211.2 | 0.67983 | 7.109
2024-12-09 | 22:30 | Data | 0 | 28.058 | 25.398 | 238.692 | 7.63 | 223.641 | 2254.16 | 25.89 | 41.304 | 6.28 | 1.498 | 5.6 | 9281.87 | 2.829 | 98.2 | 78.9 | 1465 | 20.7 | 6033.2 | 3492.7 | 3436.3 | 4995.3 | 1211.2 | 0.68372 | 7.098
2024-12-09 | 22:30 | Data | 0 | 28.247 | 25.351 | 239.054 | 7.63 | 223.912 | 2255.97 | 25.89 | 41.123 | 6.28 | 1.494 | 5.603 | 9272.83 | 2.977 | 98.2 | 79 | 1466 | 20.52 | 6027.3 | 3467.6 | 3428.9 | 4970.3 | 1211.2 | 0.68308 | 7.096
2024-12-09 | 22:30 | Data | 0 | 26.789 | 24.008 | 237.923 | 7.63 | 223.008 | 2254.16 | 25.9 | 41.213 | 6.28 | 1.494 | 5.625 | 9295.44 | 2.896 | 98.2 | 79 | 1465 | 20.61 | 6042 | 3491 | 3454.5 | 5000.3 | 1211.2 | 0.68353 | 7.119
2024-12-09 | 22:30 | Data | 0 | 27.187 | 24.224 | 237.923 | 7.63 | 223.008 | 2249.64 | 25.89 | 41.123 | 6.28 | 1.495 | 5.575 | 9277.35 | 2.856 | 98.2 | 78.9 | 1462 | 20.61 | 6030.3 | 3484.7 | 3426 | 4984 | 1211.2 | 0.6835 | 7.07
2024-12-09 | 22:30 | Data | 0 | 27.194 | 24.426 | 238.194 | 7.63 | 223.098 | 2250.54 | 25.89 | 41.304 | 6.28 | 1.504 | 5.596 | 9281.87 | 2.768 | 98.2 | 78.8 | 1462 | 20.65 | 6033.2 | 3494 | 3492.4 | 5032.6 | 1211.2 | 0.6779 | 7.1
2024-12-09 | 22:30 | Data | 0 | 27.68 | 24.946 | 238.556 | 7.63 | 223.55 | 2248.73 | 25.89 | 41.304 | 6.28 | 1.506 | 5.62 | 9299.96 | 2.883 | 98.2 | 78.9 | 1462 | 20.61 | 6045 | 3474 | 3443.6 | 4985.3 | 1211.2 | 0.68181 | 7.125
2024-12-09 | 22:30 | Data | 0 | 27.565 | 25.014 | 238.601 | 7.63 | 223.55 | 2249.64 | 25.89 | 41.394 | 6.28 | 1.501 | 5.611 | 9295.44 | 3.052 | 98.2 | 78.9 | 1462 | 20.65 | 6042 | 3476.8 | 3461.8 | 4996.5 | 1211.2 | 0.68107 | 7.112
2024-12-09 | 22:30 | Data | 0 | 26.755 | 23.744 | 237.787 | 7.63 | 222.873 | 2249.64 | 25.89 | 41.304 | 6.28 | 1.509 | 5.588 | 9281.87 | 2.782 | 98.2 | 78.7 | 1463 | 20.65 | 6033.2 | 3488.4 | 3475.4 | 5012.7 | 1211.2 | 0.68148 | 7.097
2024-12-09 | 22:30 | Data | 0 | 27.309 | 24.622 | 238.149 | 7.64 | 223.189 | 2249.64 | 25.9 | 41.213 | 6.28 | 1.503 | 5.566 | 9268.3 | 2.93 | 98.2 | 78.7 | 1462 | 20.61 | 6024.4 | 3480.4 | 3452.7 | 4995.8 | 1211.2 | 0.68168 | 7.069
2024-12-09 | 22:31 | Data | 0 | 27.241 | 24.284 | 238.149 | 7.63 | 223.144 | 2249.64 | 25.89 | 41.304 | 6.28 | 1.511 | 5.58 | 9299.96 | 2.829 | 98.2 | 78.7 | 1462 | 20.61 | 6045 | 3474.7 | 3457.4 | 4992.7 | 1211.2 | 0.68127 | 7.089
2024-12-09 | 22:31 | Data | 0 | 27.451 | 24.629 | 238.194 | 7.63 | 223.234 | 2248.73 | 25.89 | 41.213 | 6.28 | 1.5 | 5.574 | 9309 | 2.714 | 98.2 | 78.8 | 1462 | 20.65 | 6050.9 | 3501.9 | 3435.8 | 4997.6 | 1211.2 | 0.6862 | 7.077
2024-12-09 | 22:31 | Data | 0 | 26.978 | 24.17 | 237.832 | 7.63 | 222.963 | 2249.64 | 25.89 | 41.304 | 6.28 | 1.502 | 5.578 | 9309 | 2.883 | 98.2 | 78.8 | 1463 | 20.61 | 6050.9 | 3487 | 3463.2 | 5004.4 | 1211.2 | 0.6824 | 7.08
2024-12-09 | 22:31 | Data | 0 | 27.194 | 23.987 | 238.104 | 7.63 | 223.098 | 2252.35 | 25.89 | 41.213 | 6.28 | 1.507 | 5.604 | 9313.53 | 2.768 | 98.2 | 78.8 | 1464 | 20.61 | 6053.8 | 3472.6 | 3451.6 | 4989.9 | 1211.2 | 0.6812 | 7.111
2024-12-09 | 22:31 | Data | 0 | 27.896 | 25.088 | 238.647 | 7.63 | 223.686 | 2252.35 | 25.89 | 41.213 | 6.28 | 1.498 | 5.617 | 9322.57 | 2.876 | 98.2 | 79 | 1464 | 20.61 | 6059.7 | 3463.8 | 3456.3 | 4987.4 | 1211.2 | 0.67957 | 7.114
2024-12-09 | 22:31 | Data | 0 | 27.43 | 24.966 | 238.556 | 7.63 | 223.46 | 2247.83 | 25.89 | 41.575 | 6.28 | 1.51 | 5.623 | 9322.57 | 3.045 | 98.2 | 78.8 | 1461 | 20.79 | 6059.7 | 3485.7 | 3482.5 | 5018 | 1211.2 | 0.68198 | 7.134
2024-12-09 | 22:31 | Data | 0 | 27.957 | 24.899 | 238.601 | 7.63 | 223.686 | 2246.93 | 25.89 | 41.123 | 6.28 | 1.507 | 5.63 | 9340.66 | 2.768 | 98.2 | 78.9 | 1461 | 20.61 | 6071.4 | 3475.5 | 3466.8 | 5001.6 | 1211.2 | 0.67937 | 7.136
2024-12-09 | 22:31 | Data | 0 | 27.221 | 24.203 | 238.285 | 7.63 | 223.234 | 2249.64 | 25.9 | 41.304 | 6.28 | 1.509 | 5.592 | 9327.09 | 2.788 | 98.2 | 78.8 | 1463 | 20.61 | 6062.6 | 3474.4 | 3444.7 | 4985.4 | 1211.2 | 0.68154 | 7.099
2024-12-09 | 22:31 | Data | 0 | 27.653 | 24.818 | 238.42 | 7.63 | 223.279 | 2246.93 | 25.89 | 41.213 | 6.28 | 1.486 | 5.553 | 9268.3 | 2.91 | 98.2 | 78.9 | 1461 | 20.65 | 6024.4 | 3468 | 3439.4 | 4987.9 | 1211.2 | 0.68342 | 7.039
2024-12-09 | 22:31 | Data | 0 | 27.208 | 24.318 | 238.194 | 7.63 | 223.189 | 2248.73 | 25.89 | 41.213 | 6.28 | 1.487 | 5.573 | 9245.69 | 2.876 | 98.2 | 78.9 | 1462 | 20.65 | 6009.7 | 3492.6 | 3454.8 | 5005.6 | 1211.2 | 0.68302 | 7.059
2024-12-09 | 22:31 | Data | 0 | 26.512 | 23.575 | 237.742 | 7.63 | 222.737 | 2244.22 | 25.89 | 41.304 | 6.28 | 1.508 | 5.604 | 9232.13 | 2.863 | 98.2 | 78.8 | 1459 | 20.61 | 6000.9 | 3486 | 3463.7 | 5007.6 | 1211.2 | 0.68183 | 7.113
2024-12-09 | 22:31 | Data | 0 | 27.437 | 24.635 | 238.285 | 7.63 | 223.234 | 2245.12 | 25.89 | 41.123 | 6.29 | 1.505 | 5.601 | 9236.65 | 2.728 | 98.2 | 78.8 | 1459 | 20.52 | 6003.8 | 3486.5 | 3416.1 | 4989.7 | 1211.2 | 0.6859 | 7.106
2024-12-09 | 22:31 | Data | 0 | 27.086 | 24.365 | 238.013 | 7.63 | 223.008 | 2242.41 | 25.89 | 41.304 | 6.29 | 1.5 | 5.579 | 9218.56 | 2.815 | 98.2 | 78.8 | 1458 | 20.61 | 5992.1 | 3499.7 | 3440 | 4996.4 | 1211.2 | 0.68543 | 7.078
2024-12-09 | 22:31 | Data | 0 | 27.842 | 25.344 | 238.828 | 7.63 | 223.641 | 2244.22 | 25.89 | 41.213 | 6.28 | 1.499 | 5.592 | 9254.74 | 2.687 | 98.2 | 78.9 | 1459 | 20.7 | 6015.6 | 3479.5 | 3437.1 | 4985.3 | 1211.3 | 0.68336 | 7.09
2024-12-09 | 22:31 | Data | 0 | 26.735 | 24.075 | 237.832 | 7.63 | 222.873 | 2246.93 | 25.89 | 41.304 | 6.28 | 1.502 | 5.628 | 9254.74 | 2.91 | 98.2 | 78.9 | 1461 | 20.61 | 6015.6 | 3488.1 | 3445.5 | 4994.3 | 1211.3 | 0.68391 | 7.129
2024-12-09 | 22:31 | Data | 0 | 27.91 | 24.892 | 238.737 | 7.63 | 223.596 | 2246.93 | 25.89 | 41.213 | 6.28 | 1.493 | 5.579 | 9254.74 | 2.977 | 98.2 | 78.9 | 1461 | 20.65 | 6015.6 | 3473.2 | 3421.3 | 4967.2 | 1211.3 | 0.68439 | 7.071
2024-12-09 | 22:31 | Data | 0 | 27.883 | 24.919 | 238.692 | 7.64 | 223.822 | 2247.83 | 25.9 | 41.213 | 6.28 | 1.505 | 5.595 | 9259.26 | 2.93 | 98.2 | 78.8 | 1461 | 20.61 | 6018.5 | 3475.4 | 3471.6 | 5005.9 | 1211.3 | 0.6802 | 7.101
2024-12-09 | 22:32 | Data | 0 | 27.883 | 25 | 238.737 | 7.64 | 223.686 | 2246.02 | 25.89 | 41.213 | 6.28 | 1.512 | 5.61 | 9268.3 | 2.768 | 98.2 | 78.8 | 1461 | 20.7 | 6024.4 | 3500.6 | 3440.6 | 5002.8 | 1211.3 | 0.68517 | 7.122
2024-12-09 | 22:32 | Data | 0 | 26.89 | 23.758 | 237.697 | 7.64 | 222.873 | 2246.93 | 25.89 | 41.213 | 6.28 | 1.509 | 5.626 | 9254.74 | 2.95 | 98.2 | 78.8 | 1461 | 20.61 | 6015.6 | 3485.2 | 3434.4 | 4987.1 | 1211.3 | 0.68438 | 7.135
2024-12-09 | 22:32 | Data | 0 | 27.43 | 24.581 | 238.375 | 7.64 | 223.324 | 2246.93 | 25.89 | 40.943 | 6.28 | 1.511 | 5.63 | 9245.69 | 2.687 | 98.2 | 78.8 | 1461 | 20.52 | 6009.7 | 3469.1 | 3444.9 | 4984.7 | 1211.3 | 0.68076 | 7.14
2024-12-09 | 22:32 | Data | 0 | 27.397 | 24.797 | 238.194 | 7.64 | 223.189 | 2246.93 | 25.89 | 41.304 | 6.28 | 1.498 | 5.615 | 9263.78 | 3.058 | 98.2 | 78.9 | 1461 | 20.61 | 6021.5 | 3474.8 | 3462.8 | 4998.3 | 1211.3 | 0.67989 | 7.114
2024-12-09 | 22:32 | Data | 0 | 27.302 | 24.001 | 238.149 | 7.63 | 223.279 | 2246.93 | 25.89 | 41.213 | 6.28 | 1.504 | 5.611 | 9254.74 | 3.166 | 98.2 | 78.9 | 1461 | 20.65 | 6015.6 | 3490.7 | 3443.8 | 4996 | 1211.3 | 0.68336 | 7.115
2024-12-09 | 22:32 | Data | 0 | 27.917 | 25.203 | 238.601 | 7.64 | 223.641 | 2248.73 | 25.89 | 41.033 | 6.28 | 1.508 | 5.625 | 9295.44 | 2.66 | 98.2 | 78.9 | 1462 | 20.52 | 6042 | 3474.5 | 3432.9 | 4979.6 | 1211.3 | 0.68304 | 7.131
2024-12-09 | 22:32 | Data | 0 | 27.559 | 24.743 | 238.285 | 7.64 | 223.144 | 2251.45 | 25.89 | 41.033 | 6.29 | 1.519 | 5.621 | 9286.39 | 2.944 | 98.2 | 78.7 | 1463 | 20.52 | 6036.2 | 3490.4 | 3449.6 | 5000.8 | 1211.3 | 0.68336 | 7.141
2024-12-09 | 22:32 | Data | 0 | 27.248 | 24.311 | 238.013 | 7.64 | 223.008 | 2253.25 | 25.88 | 41.033 | 6.28 | 1.506 | 5.594 | 9299.96 | 3.004 | 98.2 | 78.8 | 1465 | 20.56 | 6045 | 3478.9 | 3459.4 | 5000.1 | 1211.3 | 0.67993 | 7.1
2024-12-09 | 22:32 | Data | 0 | 27.268 | 24.433 | 238.33 | 7.63 | 223.37 | 2255.97 | 25.89 | 41.123 | 6.29 | 1.5 | 5.573 | 9268.3 | 2.775 | 98.2 | 78.8 | 1465 | 20.52 | 6024.4 | 3476.1 | 3454.1 | 4987.2 | 1211.3 | 0.68185 | 7.071
2024-12-09 | 22:32 | Data | 0 | 27.187 | 24.217 | 237.968 | 7.64 | 223.008 | 2258.68 | 25.91 | 40.943 | 6.29 | 1.502 | 5.601 | 9281.87 | 2.977 | 98.2 | 78.9 | 1468 | 20.47 | 6033.2 | 3485 | 3461.2 | 5005.7 | 1211.3 | 0.68083 | 7.104
2024-12-09 | 22:32 | Data | 0 | 27.444 | 24.48 | 238.285 | 7.64 | 223.189 | 2257.77 | 25.89 | 41.123 | 6.29 | 1.499 | 5.596 | 9286.39 | 2.782 | 98.2 | 78.9 | 1466 | 20.52 | 6036.2 | 3496.4 | 3453.1 | 5000.8 | 1211.3 | 0.6848 | 7.095
2024-12-09 | 22:32 | Data | 0 | 27.923 | 24.993 | 238.511 | 7.63 | 223.55 | 2255.97 | 25.89 | 40.943 | 6.29 | 1.499 | 5.626 | 9295.44 | 2.802 | 98.2 | 79 | 1465 | 20.47 | 6042 | 3469.3 | 3453.5 | 4990 | 1211.3 | 0.68079 | 7.126
2024-12-09 | 22:32 | Data | 0 | 27.424 | 24.541 | 238.33 | 7.63 | 223.098 | 2255.97 | 25.89 | 41.304 | 6.29 | 1.508 | 5.633 | 9336.14 | 2.883 | 98.2 | 78.9 | 1466 | 20.61 | 6068.5 | 3493.1 | 3437.4 | 4993.2 | 1211.3 | 0.68496 | 7.141
2024-12-09 | 22:32 | Data | 0 | 27.484 | 24.548 | 238.285 | 7.63 | 223.37 | 2258.68 | 25.9 | 41.123 | 6.29 | 1.5 | 5.601 | 9363.27 | 3.004 | 98.2 | 78.9 | 1468 | 20.52 | 6086.1 | 3486.5 | 3438.8 | 4990.5 | 1211.3 | 0.68379 | 7.103
2024-12-09 | 22:32 | Data | 0 | 27.316 | 24.284 | 238.24 | 7.64 | 223.279 | 2261.39 | 25.89 | 40.943 | 6.28 | 1.502 | 5.582 | 9367.79 | 2.923 | 98.2 | 78.8 | 1469 | 20.52 | 6089.1 | 3482.8 | 3435.1 | 4983.6 | 1211.3 | 0.68485 | 7.083
2024-12-09 | 22:32 | Data | 0 | 28.018 | 24.791 | 238.375 | 7.64 | 223.279 | 2260.48 | 25.89 | 41.304 | 6.29 | 1.497 | 5.578 | 9367.79 | 2.991 | 98.2 | 78.9 | 1469 | 20.61 | 6089.1 | 3474.5 | 3454 | 4989.5 | 1211.3 | 0.68088 | 7.075
2024-12-09 | 22:32 | Data | 0 | 27.822 | 24.986 | 238.692 | 7.64 | 223.596 | 2263.2 | 25.89 | 41.304 | 6.29 | 1.494 | 5.63 | 9367.79 | 2.937 | 98.2 | 79 | 1472 | 20.65 | 6089.1 | 3475.5 | 3482 | 5014.6 | 1211.3 | 0.67805 | 7.124
2024-12-09 | 22:32 | Data | 0 | 27.336 | 24.217 | 238.194 | 7.63 | 223.234 | 2268.62 | 25.89 | 41.213 | 6.28 | 1.495 | 5.612 | 9363.27 | 2.977 | 98.2 | 79 | 1475 | 20.65 | 6086.1 | 3500 | 3503.3 | 5045.8 | 1211.3 | 0.67881 | 7.107
2024-12-09 | 22:33 | Data | 0 | 27.424 | 24.338 | 238.285 | 7.63 | 223.324 | 2263.2 | 25.89 | 41.394 | 6.29 | 1.492 | 5.583 | 9381.36 | 2.944 | 98.2 | 78.9 | 1471 | 20.61 | 6097.9 | 3488.2 | 3458 | 5001.7 | 1211.3 | 0.68194 | 7.075
2024-12-09 | 22:33 | Data | 0 | 26.641 | 24.055 | 237.652 | 7.64 | 222.827 | 2271.33 | 25.89 | 41.213 | 6.29 | 1.5 | 5.62 | 9381.36 | 2.836 | 98.2 | 78.9 | 1476 | 20.61 | 6097.9 | 3470.2 | 3472.5 | 5001.7 | 1211.3 | 0.67874 | 7.119
2024-12-09 | 22:33 | Data | 0 | 27.741 | 25.135 | 238.42 | 7.64 | 223.505 | 2264.1 | 25.89 | 41.304 | 6.29 | 1.5 | 5.616 | 9313.53 | 2.89 | 98.2 | 78.9 | 1471 | 20.61 | 6053.8 | 3477.8 | 3485 | 5016.3 | 1211.3 | 0.67696 | 7.115
2024-12-09 | 22:33 | Data | 0 | 26.965 | 23.967 | 238.013 | 7.64 | 222.963 | 2259.58 | 25.89 | 41.304 | 6.29 | 1.504 | 5.601 | 9309 | 2.782 | 98.2 | 78.8 | 1468 | 20.61 | 6050.9 | 3477.3 | 3490.6 | 5025 | 1211.3 | 0.67697 | 7.106
2024-12-09 | 22:33 | Data | 0 | 27.187 | 24.028 | 237.878 | 7.63 | 223.008 | 2263.2 | 25.89 | 41.304 | 6.28 | 1.505 | 5.581 | 9322.57 | 2.93 | 98.2 | 78.8 | 1470 | 20.61 | 6059.7 | 3460.7 | 3474.4 | 5000.4 | 1211.3 | 0.67862 | 7.086
2024-12-09 | 22:33 | Data | 0 | 28.112 | 25.142 | 238.647 | 7.64 | 223.596 | 2265.91 | 25.89 | 41.213 | 6.29 | 1.505 | 5.606 | 9313.53 | 2.944 | 98.2 | 78.8 | 1473 | 20.65 | 6053.8 | 3488.8 | 3484.8 | 5023.5 | 1211.3 | 0.68025 | 7.109
2024-12-09 | 22:33 | Data | 0 | 28.349 | 25.176 | 239.054 | 7.64 | 223.731 | 2266.81 | 25.89 | 41.304 | 6.29 | 1.506 | 5.612 | 9322.57 | 2.788 | 98.2 | 78.8 | 1473 | 20.61 | 6059.7 | 3476.9 | 3468.2 | 5005.1 | 1211.3 | 0.67894 | 7.118
2024-12-09 | 22:33 | Data | 0 | 27.91 | 25.014 | 238.828 | 7.64 | 223.822 | 2263.2 | 25.89 | 41.304 | 6.29 | 1.505 | 5.596 | 9327.09 | 2.91 | 98.2 | 78.8 | 1470 | 20.61 | 6062.6 | 3492.5 | 3504.5 | 5040.6 | 1211.3 | 0.67797 | 7.102
2024-12-09 | 22:33 | Data | 0 | 27.511 | 24.723 | 238.194 | 7.64 | 223.234 | 2261.39 | 25.89 | 41.213 | 6.29 | 1.5 | 5.627 | 9309 | 2.89 | 98.2 | 78.9 | 1470 | 20.65 | 6050.9 | 3500.4 | 3469 | 5007.2 | 1211.4 | 0.68205 | 7.127
2024-12-09 | 22:33 | Data | 0 | 27.856 | 25.014 | 238.511 | 7.64 | 223.55 | 2256.87 | 25.89 | 41.304 | 6.29 | 1.499 | 5.606 | 9327.09 | 3.038 | 98.2 | 78.9 | 1468 | 20.7 | 6062.6 | 3473.3 | 3476.8 | 5008.6 | 1211.4 | 0.67824 | 7.105
2024-12-09 | 22:33 | Data | 0 | 27.464 | 24.75 | 238.511 | 7.64 | 223.505 | 2254.16 | 25.89 | 41.213 | 6.29 | 1.493 | 5.61 | 9340.66 | 2.849 | 98.2 | 79 | 1466 | 20.65 | 6071.4 | 3480.6 | 3466.9 | 5004.5 | 1211.4 | 0.67899 | 7.103
2024-12-09 | 22:33 | Data | 0 | 26.985 | 24.183 | 237.968 | 7.64 | 223.098 | 2254.16 | 25.89 | 41.304 | 6.29 | 1.5 | 5.599 | 9336.14 | 2.937 | 98.2 | 78.9 | 1465 | 20.65 | 6068.5 | 3489.4 | 3456 | 5006.9 | 1211.4 | 0.6817 | 7.1
2024-12-09 | 22:33 | Data | 0 | 28.43 | 24.986 | 238.828 | 7.64 | 223.731 | 2249.64 | 25.9 | 41.304 | 6.29 | 1.5 | 5.627 | 9336.14 | 2.876 | 98.2 | 78.9 | 1462 | 20.61 | 6068.5 | 3477.2 | 3466.2 | 5003.2 | 1211.4 | 0.6799 | 7.125
2024-12-09 | 22:33 | Data | 0 | 27.194 | 24.318 | 238.285 | 7.64 | 223.234 | 2255.97 | 25.9 | 41.213 | 6.29 | 1.494 | 5.616 | 9336.14 | 2.984 | 98.2 | 79 | 1466 | 20.61 | 6068.5 | 3469.4 | 3459.7 | 4992.9 | 1211.4 | 0.68004 | 7.11
2024-12-09 | 22:33 | Data | 0 | 26.384 | 23.272 | 237.516 | 7.64 | 222.556 | 2254.16 | 25.89 | 41.304 | 6.29 | 1.5 | 5.584 | 9327.09 | 2.991 | 98.2 | 78.8 | 1465 | 20.61 | 6062.6 | 3471 | 3475.7 | 5005.4 | 1211.4 | 0.67911 | 7.084
2024-12-09 | 22:33 | Data | 0 | 27.68 | 24.669 | 238.42 | 7.64 | 223.46 | 2252.35 | 25.89 | 41.213 | 6.29 | 1.501 | 5.613 | 9336.14 | 2.977 | 98.2 | 78.9 | 1465 | 20.65 | 6068.5 | 3478.5 | 3459.9 | 5000.4 | 1211.4 | 0.681 | 7.115
2024-12-09 | 22:33 | Data | 0 | 27.883 | 25 | 238.511 | 7.64 | 223.46 | 2249.64 | 25.89 | 41.304 | 6.29 | 1.498 | 5.617 | 9327.09 | 2.883 | 98.2 | 78.9 | 1462 | 20.61 | 6062.6 | 3472.6 | 3456.2 | 4993.7 | 1211.4 | 0.68027 | 7.115
2024-12-09 | 22:33 | Data | 0 | 27.761 | 24.473 | 238.556 | 7.64 | 223.55 | 2250.54 | 25.89 | 41.213 | 6.29 | 1.498 | 5.627 | 9318.05 | 2.883 | 98.2 | 79 | 1462 | 20.65 | 6056.7 | 3473 | 3480.9 | 5009.9 | 1211.4 | 0.67878 | 7.125
2024-12-09 | 22:34 | Data | 0 | 27.282 | 24.251 | 237.968 | 7.64 | 223.008 | 2249.64 | 25.89 | 41.213 | 6.29 | 1.505 | 5.594 | 9327.09 | 2.937 | 98.2 | 78.8 | 1462 | 20.61 | 6062.6 | 3482.5 | 3468.8 | 5008.3 | 1211.4 | 0.68122 | 7.099
2024-12-09 | 22:34 | Data | 0 | 27.025 | 24.143 | 238.149 | 7.64 | 223.144 | 2248.73 | 25.89 | 41.033 | 6.29 | 1.512 | 5.594 | 9318.05 | 3.004 | 98.2 | 78.7 | 1462 | 20.52 | 6056.7 | 3472.5 | 3465.9 | 4999.7 | 1211.4 | 0.6803 | 7.107
2024-12-09 | 22:34 | Data | 0 | 27.032 | 24.014 | 238.194 | 7.64 | 223.053 | 2249.64 | 25.9 | 41.033 | 6.29 | 1.51 | 5.605 | 9318.05 | 2.903 | 98.2 | 78.8 | 1462 | 20.47 | 6056.7 | 3477.1 | 3441.8 | 4975.9 | 1211.4 | 0.68151 | 7.115
2024-12-09 | 22:34 | Data | 0 | 27.896 | 25 | 238.692 | 7.63 | 223.55 | 2248.73 | 25.89 | 41.304 | 6.29 | 1.501 | 5.611 | 9299.96 | 2.782 | 98.2 | 78.9 | 1462 | 20.65 | 6045 | 3455.3 | 3415.1 | 4952.5 | 1211.4 | 0.68219 | 7.11
2024-12-09 | 22:34 | Data | 0 | 27.768 | 24.946 | 239.008 | 7.64 | 223.641 | 2250.54 | 25.89 | 41.304 | 6.29 | 1.504 | 5.597 | 9336.14 | 2.971 | 98.2 | 78.8 | 1463 | 20.65 | 6068.5 | 3472.8 | 3414.9 | 4963.8 | 1211.4 | 0.68439 | 7.102
2024-12-09 | 22:34 | Data | 0 | 27.154 | 24.224 | 238.013 | 7.64 | 222.963 | 2246.93 | 25.89 | 41.033 | 6.29 | 1.506 | 5.558 | 9340.66 | 2.829 | 98.2 | 78.7 | 1460 | 20.52 | 6071.4 | 3476.9 | 3424.5 | 4973.5 | 1211.4 | 0.68414 | 7.066
2024-12-09 | 22:34 | Data | 0 | 28.112 | 24.899 | 238.692 | 7.64 | 223.596 | 2247.83 | 25.9 | 40.943 | 6.29 | 1.5 | 5.599 | 9349.7 | 3.025 | 98.2 | 78.9 | 1461 | 20.52 | 6077.3 | 3463.3 | 3397.2 | 4944.5 | 1211.4 | 0.68488 | 7.1
2024-12-09 | 22:34 | Data | 0 | 27.917 | 25.29 | 238.737 | 7.64 | 223.731 | 2246.93 | 25.89 | 40.943 | 6.29 | 1.504 | 5.623 | 9336.14 | 2.66 | 98.2 | 78.9 | 1461 | 20.47 | 6068.5 | 3487.3 | 3424.3 | 4982 | 1211.4 | 0.68668 | 7.129
2024-12-09 | 22:34 | Data | 0 | 27.667 | 24.737 | 238.692 | 7.64 | 223.641 | 2247.83 | 25.89 | 41.033 | 6.29 | 1.51 | 5.613 | 9322.57 | 3.153 | 98.2 | 78.8 | 1462 | 20.52 | 6059.7 | 3485 | 3431.2 | 4980.3 | 1211.4 | 0.68539 | 7.125
2024-12-09 | 22:34 | Data | 0 | 26.965 | 24.143 | 237.878 | 7.64 | 223.098 | 2246.93 | 25.89 | 41.033 | 6.29 | 1.502 | 5.604 | 9322.57 | 2.998 | 98.2 | 78.9 | 1461 | 20.47 | 6059.7 | 3501.7 | 3444.8 | 4981.3 | 1211.4 | 0.68345 | 7.107
2024-12-09 | 22:34 | Data | 0 | 27.417 | 24.001 | 237.878 | 7.64 | 222.963 | 2250.54 | 25.89 | 41.033 | 6.29 | 1.499 | 5.601 | 9309 | 3.011 | 98.2 | 78.9 | 1462 | 20.52 | 6050.9 | 3473.2 | 3432.2 | 4975.2 | 1211.4 | 0.68318 | 7.099
2024-12-09 | 22:34 | Data | 0 | 27.424 | 24.433 | 238.104 | 7.64 | 223.279 | 2246.93 | 25.89 | 41.033 | 6.29 | 1.501 | 5.596 | 9327.09 | 2.984 | 98.2 | 78.8 | 1461 | 20.52 | 6062.6 | 3505.6 | 3470.2 | 5026.5 | 1211.4 | 0.68276 | 7.097
2024-12-09 | 22:34 | Data | 0 | 27.383 | 24.892 | 238.375 | 7.64 | 223.37 | 2249.64 | 25.89 | 41.033 | 6.29 | 1.493 | 5.604 | 9322.57 | 2.721 | 98.2 | 79 | 1462 | 20.52 | 6059.7 | 3471.5 | 3463.4 | 4997.2 | 1211.4 | 0.67968 | 7.097
2024-12-09 | 22:34 | Data | 0 | 27.565 | 24.716 | 238.601 | 7.64 | 223.505 | 2248.73 | 25.89 | 40.943 | 6.29 | 1.503 | 5.573 | 9345.18 | 2.998 | 98.2 | 78.7 | 1462 | 20.47 | 6074.4 | 3479.6 | 3480 | 5013.3 | 1211.4 | 0.67925 | 7.077
2024-12-09 | 22:34 | Data | 0 | 27.424 | 24.433 | 238.194 | 7.64 | 223.279 | 2249.64 | 25.89 | 40.943 | 6.29 | 1.515 | 5.599 | 9349.7 | 2.984 | 98.2 | 78.7 | 1463 | 20.43 | 6077.3 | 3457.9 | 3452.1 | 4978.7 | 1211.4 | 0.67777 | 7.113
2024-12-09 | 22:34 | Data | 0 | 27.302 | 24.305 | 237.923 | 7.64 | 223.189 | 2246.93 | 25.89 | 40.943 | 6.29 | 1.507 | 5.579 | 9345.18 | 2.971 | 98.2 | 78.7 | 1461 | 20.47 | 6074.4 | 3467.4 | 3499.5 | 5019 | 1211.4 | 0.67645 | 7.085
2024-12-09 | 22:34 | Data | 0 | 26.607 | 23.69 | 237.697 | 7.64 | 222.737 | 2246.93 | 25.89 | 41.123 | 6.29 | 1.506 | 5.581 | 9340.66 | 2.876 | 98.2 | 78.7 | 1461 | 20.56 | 6071.4 | 3473.4 | 3455.9 | 4992.8 | 1211.4 | 0.68088 | 7.086
2024-12-09 | 22:34 | Data | 0 | 26.924 | 23.873 | 237.606 | 7.64 | 222.782 | 2246.93 | 25.89 | 41.033 | 6.28 | 1.507 | 5.583 | 9318.05 | 2.944 | 98.2 | 78.7 | 1461 | 20.52 | 6056.7 | 3468.8 | 3448.8 | 4986.9 | 1211.4 | 0.68118 | 7.09
2024-12-09 | 22:35 | Data | 0 | 26.472 | 23.636 | 237.652 | 7.64 | 222.556 | 2241.5 | 25.89 | 41.033 | 6.29 | 1.498 | 5.584 | 9299.96 | 2.923 | 98.2 | 78.9 | 1458 | 20.52 | 6045 | 3477.5 | 3441.9 | 4984.7 | 1211.4 | 0.68269 | 7.082
2024-12-09 | 22:35 | Data | 0 | 27.451 | 24.602 | 238.42 | 7.64 | 223.37 | 2248.73 | 25.89 | 40.943 | 6.3 | 1.493 | 5.582 | 9281.87 | 2.91 | 98.2 | 78.9 | 1462 | 20.47 | 6033.2 | 3462.7 | 3435.6 | 4972.1 | 1211.4 | 0.6811 | 7.075
2024-12-09 | 22:35 | Data | 0 | 27.424 | 24.257 | 238.33 | 7.64 | 223.324 | 2249.64 | 25.89 | 41.213 | 6.29 | 1.504 | 5.62 | 9295.44 | 2.91 | 98.2 | 78.9 | 1462 | 20.61 | 6042 | 3476.4 | 3435.2 | 4978.4 | 1211.4 | 0.68394 | 7.125
2024-12-09 | 22:35 | Data | 0 | 27.775 | 24.662 | 238.466 | 7.64 | 223.46 | 2246.02 | 25.89 | 41.304 | 6.29 | 1.499 | 5.63 | 9299.96 | 2.991 | 98.2 | 79 | 1461 | 20.65 | 6045 | 3474 | 3458.8 | 4993 | 1211.5 | 0.68107 | 7.128
2024-12-09 | 22:35 | Data | 0 | 27.194 | 24.575 | 238.24 | 7.64 | 223.144 | 2247.83 | 25.89 | 41.213 | 6.3 | 1.497 | 5.611 | 9299.96 | 2.991 | 98.2 | 78.9 | 1461 | 20.61 | 6045 | 3466.9 | 3505.7 | 5023.5 | 1211.5 | 0.67432 | 7.108
2024-12-09 | 22:35 | Data | 0 | 27.37 | 24.635 | 238.33 | 7.64 | 223.324 | 2246.93 | 25.89 | 41.213 | 6.3 | 1.506 | 5.601 | 9295.44 | 2.903 | 98.2 | 78.8 | 1461 | 20.65 | 6042 | 3470.7 | 3475 | 5007.5 | 1211.5 | 0.6775 | 7.106
2024-12-09 | 22:35 | Data | 0 | 26.728 | 23.974 | 237.697 | 7.64 | 222.873 | 2247.83 | 25.89 | 41.213 | 6.29 | 1.503 | 5.606 | 9281.87 | 2.863 | 98.2 | 78.8 | 1461 | 20.61 | 6033.2 | 3466.1 | 3452 | 4987.8 | 1211.5 | 0.67956 | 7.11
2024-12-09 | 22:35 | Data | 0 | 27.397 | 24.251 | 238.24 | 7.64 | 223.234 | 2246.02 | 25.89 | 41.304 | 6.29 | 1.495 | 5.618 | 9281.87 | 2.998 | 98.2 | 79 | 1461 | 20.65 | 6033.2 | 3474.2 | 3469.3 | 5000.4 | 1211.5 | 0.68018 | 7.112
2024-12-09 | 22:35 | Data | 0 | 26.992 | 24.089 | 238.013 | 7.65 | 223.098 | 2246.93 | 25.89 | 41.213 | 6.29 | 1.487 | 5.623 | 9268.3 | 2.991 | 98.2 | 79.1 | 1461 | 20.61 | 6024.4 | 3484.3 | 3460.1 | 5004.8 | 1211.5 | 0.68188 | 7.112
2024-12-09 | 22:35 | Data | 0 | 26.533 | 23.94 | 237.878 | 7.64 | 222.827 | 2246.02 | 25.89 | 41.213 | 6.29 | 1.514 | 5.602 | 9277.35 | 2.761 | 98.2 | 78.7 | 1461 | 20.61 | 6030.3 | 3468.8 | 3426.2 | 4970 | 1211.5 | 0.68337 | 7.117
2024-12-09 | 22:35 | Data | 0 | 27.417 | 24.453 | 238.194 | 7.64 | 223.144 | 2246.93 | 25.89 | 41.213 | 6.29 | 1.511 | 5.598 | 9304.48 | 2.883 | 98.2 | 78.7 | 1461 | 20.61 | 6047.9 | 3482.7 | 3424.7 | 4985 | 1211.5 | 0.68287 | 7.11
2024-12-09 | 22:35 | Data | 0 | 26.85 | 23.954 | 237.878 | 7.64 | 222.963 | 2247.83 | 25.89 | 41.304 | 6.29 | 1.503 | 5.614 | 9295.44 | 2.984 | 98.2 | 78.9 | 1461 | 20.65 | 6042 | 3479.8 | 3452.2 | 4996.6 | 1211.5 | 0.6815 | 7.116
2024-12-09 | 22:35 | Data | 0 | 27.37 | 24.737 | 238.33 | 7.64 | 223.234 | 2246.93 | 25.89 | 41.304 | 6.29 | 1.502 | 5.586 | 9277.35 | 3.106 | 98.2 | 78.8 | 1460 | 20.65 | 6030.3 | 3465.4 | 3437.9 | 4975.9 | 1211.5 | 0.6809 | 7.088
2024-12-09 | 22:35 | Data | 0 | 26.992 | 24.149 | 238.149 | 7.64 | 223.098 | 2246.93 | 25.89 | 41.304 | 6.29 | 1.504 | 5.605 | 9268.3 | 2.977 | 98.2 | 78.8 | 1461 | 20.65 | 6024.4 | 3481.3 | 3430.4 | 4982.4 | 1211.5 | 0.68351 | 7.109
2024-12-09 | 22:35 | Data | 0 | 27.998 | 24.912 | 238.556 | 7.65 | 223.55 | 2244.22 | 25.89 | 41.304 | 6.29 | 1.496 | 5.603 | 9299.96 | 2.876 | 98.2 | 78.9 | 1457 | 20.61 | 6045 | 3469.5 | 3428.3 | 4970 | 1211.5 | 0.68275 | 7.098
2024-12-09 | 22:35 | Data | 0 | 27.019 | 23.974 | 238.013 | 7.64 | 223.189 | 2246.02 | 25.9 | 41.213 | 6.29 | 1.5 | 5.582 | 9281.87 | 2.998 | 98.2 | 78.8 | 1461 | 20.61 | 6033.2 | 3471.6 | 3430.4 | 4973.2 | 1211.5 | 0.68325 | 7.082
2024-12-09 | 22:35 | Data | 0 | 27.208 | 24.467 | 238.24 | 7.65 | 223.279 | 2246.93 | 25.89 | 41.213 | 6.29 | 1.494 | 5.583 | 9309 | 2.687 | 98.2 | 78.9 | 1461 | 20.7 | 6050.9 | 3479.4 | 3405.1 | 4967.2 | 1211.5 | 0.68604 | 7.077
2024-12-09 | 22:36 | Data | 0 | 27.552 | 24.703 | 238.375 | 7.64 | 223.505 | 2249.64 | 25.89 | 41.213 | 6.29 | 1.493 | 5.611 | 9327.09 | 2.822 | 98.2 | 79 | 1462 | 20.65 | 6062.6 | 3474.7 | 3443 | 4981.4 | 1211.5 | 0.68689 | 7.105
2024-12-09 | 22:36 | Data | 0 | 27.451 | 24.656 | 238.42 | 7.64 | 223.46 | 2250.54 | 25.89 | 41.213 | 6.3 | 1.505 | 5.606 | 9322.57 | 2.775 | 98.2 | 78.8 | 1463 | 20.65 | 6059.7 | 3470.2 | 3461.7 | 4998.6 | 1211.5 | 0.6795 | 7.11
2024-12-09 | 22:36 | Data | 0 | 28.342 | 25.378 | 238.782 | 7.64 | 223.867 | 2252.35 | 25.89 | 40.762 | 6.29 | 1.493 | 5.6 | 9322.57 | 2.93 | 98.2 | 78.9 | 1464 | 20.34 | 6059.7 | 3479.8 | 3431.1 | 4980 | 1211.5 | 0.68343 | 7.092
2024-12-09 | 22:36 | Data | 0 | 27.775 | 25.304 | 238.782 | 7.64 | 223.596 | 2252.35 | 25.89 | 41.213 | 6.29 | 1.507 | 5.633 | 9349.7 | 2.734 | 98.2 | 78.9 | 1464 | 20.65 | 6077.3 | 3475.4 | 3426.4 | 4976.1 | 1211.5 | 0.68306 | 7.14
2024-12-09 | 22:36 | Data | 0 | 27.43 | 24.46 | 238.466 | 7.65 | 223.37 | 2251.45 | 25.89 | 41.213 | 6.29 | 1.506 | 5.623 | 9349.7 | 2.923 | 98.2 | 78.9 | 1463 | 20.61 | 6077.3 | 3476.7 | 3423.6 | 4973.2 | 1211.5 | 0.68414 | 7.13
2024-12-09 | 22:36 | Data | 0 | 27.025 | 24.197 | 236.928 | 7.64 | 222.24 | 2253.25 | 25.89 | 41.304 | 6.29 | 1.494 | 5.639 | 9354.23 | 2.775 | 98.2 | 79 | 1465 | 20.61 | 6080.2 | 3482.7 | 3424.3 | 4977.4 | 1211.5 | 0.68465 | 7.134
2024-12-09 | 22:36 | Data | 0 | 27.822 | 25.452 | 225.348 | 7.64 | 211.574 | 2255.97 | 25.89 | 41.213 | 6.29 | 1.486 | 5.571 | 9349.7 | 2.545 | 98.2 | 78.9 | 1466 | 20.65 | 6077.3 | 3349 | 3302.2 | 4809.4 | 1211.5 | 0.68054 | 7.058
2024-12-09 | 22:36 | Data | 0 | 28.504 | 25.837 | 215.216 | 7.64 | 202.4 | 2254.16 | 25.89 | 41.033 | 6.29 | 1.468 | 5.323 | 9349.7 | 2.518 | 98.2 | 78.4 | 1465 | 20.47 | 6077.3 | 3246.4 | 3163.6 | 4635.4 | 1211.5 | 0.68376 | 6.793
2024-12-09 | 22:36 | Data | 0 | 28.112 | 25.797 | 207.346 | 7.64 | 195.078 | 2257.77 | 25.89 | 41.033 | 6.29 | 1.442 | 5.117 | 9327.09 | 2.437 | 98.2 | 78 | 1468 | 20.47 | 6062.6 | 3159.3 | 3049.9 | 4496.7 | 1211.5 | 0.68114 | 6.558
2024-12-09 | 22:36 | Data | 0 | 28.99 | 26.728 | 201.601 | 7.64 | 189.61 | 2257.77 | 25.89 | 41.213 | 6.3 | 1.412 | 4.985 | 9322.57 | 2.295 | 98.2 | 77.9 | 1468 | 20.65 | 6059.7 | 3079.3 | 2987.1 | 4398.3 | 1211.5 | 0.68458 | 6.397
2024-12-09 | 22:36 | Data | 0 | 29.496 | 27.491 | 196.535 | 7.64 | 185.136 | 2257.77 | 25.89 | 41.755 | 6.3 | 1.39 | 4.859 | 9327.09 | 2.16 | 98.2 | 77.7 | 1468 | 20.88 | 6062.6 | 3024.4 | 2933 | 4323.1 | 1211.5 | 0.68396 | 6.251
2024-12-09 | 22:36 | Data | 0 | 29.24 | 26.965 | 192.419 | 7.64 | 181.385 | 2255.97 | 25.89 | 42.297 | 6.31 | 1.377 | 4.724 | 9309 | 2.127 | 98.1 | 77.4 | 1466 | 21.15 | 6050.9 | 2979.8 | 2876.9 | 4274.8 | 1211.5 | 0.68316 | 6.101
2024-12-09 | 22:36 | Data | 0 | 28.227 | 26.31 | 189.117 | 7.64 | 178.221 | 2255.97 | 25.89 | 43.109 | 6.31 | 1.36 | 4.635 | 9272.83 | 1.904 | 98.1 | 77.3 | 1466 | 21.55 | 6027.3 | 2966 | 2891.4 | 4257 | 1211.5 | 0.68012 | 5.995
2024-12-09 | 22:36 | Data | 0 | 28.781 | 26.614 | 187.443 | 7.64 | 176.73 | 2255.97 | 25.9 | 43.561 | 6.33 | 1.358 | 4.56 | 9236.65 | 2.066 | 98.1 | 77.1 | 1466 | 21.78 | 6003.8 | 2938 | 2887.8 | 4234.8 | 1211.5 | 0.67698 | 5.918
2024-12-09 | 22:36 | Data | 0 | 29.004 | 26.971 | 186.267 | 7.64 | 175.51 | 2257.77 | 25.89 | 44.102 | 6.33 | 1.348 | 4.52 | 9182.38 | 2.052 | 98 | 77 | 1469 | 22.05 | 5968.5 | 2904.5 | 2860.6 | 4194.7 | 1211.5 | 0.67524 | 5.867
2024-12-09 | 22:36 | Data | 0 | 29.01 | 27.295 | 185.137 | 7.64 | 174.56 | 2258.68 | 25.89 | 44.554 | 6.34 | 1.355 | 4.502 | 9128.11 | 1.803 | 98 | 76.9 | 1468 | 22.28 | 5933.3 | 2904.1 | 2862.5 | 4198.3 | 1211.5 | 0.67448 | 5.858
2024-12-09 | 22:36 | Data | 0 | 28.632 | 26.776 | 184.141 | 7.64 | 173.702 | 2258.68 | 25.91 | 45.186 | 6.34 | 1.343 | 4.48 | 9557.73 | 1.803 | 98 | 76.9 | 1468 | 22.59 | 6212.5 | 2889.3 | 2845.8 | 4173.4 | 1211.5 | 0.67402 | 5.823
2024-12-09 | 22:36 | Data | 0 | 29.159 | 27.41 | 184.503 | 7.64 | 173.928 | 2256.87 | 25.89 | 45.637 | 6.35 | 1.341 | 4.475 | 9037.67 | 1.857 | 98 | 76.9 | 1465 | 22.82 | 5874.5 | 2886.1 | 2841.4 | 4167.5 | 1211.5 | 0.67466 | 5.818
2024-12-09 | 22:37 | Data | 0 | 29.071 | 27.106 | 184.639 | 7.64 | 174.018 | 2255.97 | 25.89 | 45.908 | 6.35 | 1.342 | 4.475 | 9024.1 | 1.843 | 98 | 76.9 | 1466 | 23 | 5865.7 | 2890.5 | 2828.7 | 4158.8 | 1211.6 | 0.67828 | 5.819
2024-12-09 | 22:37 | Data | 0 | 28.808 | 26.965 | 184.277 | 7.65 | 173.702 | 2255.97 | 25.89 | 46.54 | 6.36 | 1.341 | 4.452 | 9015.06 | 1.843 | 97.9 | 76.9 | 1465 | 23.27 | 5859.8 | 2889.8 | 2818.7 | 4153.8 | 1211.6 | 0.67809 | 5.794
2024-12-09 | 22:37 | Data | 0 | 28.841 | 27.066 | 184.277 | 7.64 | 173.792 | 2255.97 | 25.89 | 46.45 | 6.36 | 1.337 | 4.455 | 8996.97 | 1.897 | 97.9 | 76.9 | 1466 | 23.22 | 5848 | 2897.1 | 2825.6 | 4163.5 | 1211.6 | 0.67924 | 5.793
2024-12-09 | 22:37 | Data | 0 | 28.801 | 26.546 | 184.141 | 7.64 | 173.611 | 2254.16 | 25.89 | 46.811 | 6.36 | 1.337 | 4.458 | 8992.45 | 2.262 | 97.9 | 76.9 | 1465 | 23.41 | 5845.1 | 2896.3 | 2805.7 | 4150.6 | 1211.6 | 0.68078 | 5.795
2024-12-09 | 22:37 | Data | 0 | 28.578 | 27.093 | 184.187 | 7.64 | 173.611 | 2252.35 | 25.89 | 46.811 | 6.36 | 1.345 | 4.424 | 8951.75 | 1.87 | 97.9 | 76.7 | 1463 | 23.41 | 5818.6 | 2883.3 | 2832.8 | 4154.8 | 1211.6 | 0.6777 | 5.769
2024-12-09 | 22:37 | Data | 0 | 28.814 | 26.735 | 184.187 | 7.64 | 173.657 | 2247.83 | 25.89 | 47.082 | 6.37 | 1.331 | 4.469 | 8911.05 | 1.877 | 97.9 | 77 | 1461 | 23.54 | 5792.2 | 2895.5 | 2823.9 | 4162.7 | 1211.6 | 0.67822 | 5.8
2024-12-09 | 22:37 | Data | 0 | 28.808 | 27.052 | 184.277 | 7.64 | 173.611 | 2300.25 | 25.89 | 47.172 | 6.37 | 1.33 | 4.482 | 8897.48 | 1.958 | 98 | 77.1 | 1495 | 23.54 | 5783.4 | 2902.1 | 2837.7 | 4173.4 | 1211.6 | 0.67787 | 5.813
2024-12-09 | 22:37 | Data | 0 | 28.544 | 26.708 | 183.915 | 7.64 | 173.431 | 2299.35 | 25.91 | 47.082 | 6.36 | 1.335 | 4.487 | 8883.91 | 2.066 | 98 | 77.1 | 1495 | 23.54 | 5774.5 | 2888.1 | 2818.3 | 4153.1 | 1211.6 | 0.6781 | 5.821
2024-12-09 | 22:37 | Data | 0 | 28.47 | 26.674 | 183.463 | 7.64 | 173.069 | 2296.64 | 25.89 | 47.082 | 6.37 | 1.331 | 4.492 | 8883.91 | 1.87 | 97.9 | 77.1 | 1493 | 23.59 | 5774.5 | 2877 | 2815.8 | 4144.8 | 1211.6 | 0.67642 | 5.824
2024-12-09 | 22:37 | Data | 0 | 29.267 | 27.194 | 183.825 | 7.65 | 173.25 | 2299.35 | 25.89 | 47.172 | 6.37 | 1.331 | 4.465 | 8883.91 | 1.89 | 97.9 | 77 | 1495 | 23.54 | 5774.5 | 2868.6 | 2790.9 | 4120.7 | 1211.6 | 0.6801 | 5.797
2024-12-09 | 22:37 | Data | 0 | 29.044 | 27.025 | 183.689 | 7.64 | 173.295 | 2248.73 | 25.9 | 46.991 | 6.37 | 1.337 | 4.447 | 8870.35 | 1.843 | 97.9 | 76.9 | 1461 | 23.5 | 5765.7 | 2865.2 | 2788.6 | 4116.6 | 1211.6 | 0.6793 | 5.784
2024-12-09 | 22:37 | Data | 0 | 29.382 | 27.538 | 184.051 | 7.64 | 173.431 | 2244.22 | 25.91 | 47.172 | 6.37 | 1.335 | 4.447 | 8847.74 | 1.965 | 97.9 | 76.9 | 1459 | 23.59 | 5751 | 2890.3 | 2805.6 | 4138.9 | 1211.6 | 0.67702 | 5.781
2024-12-09 | 22:37 | Data | 0 | 29.726 | 27.944 | 184.368 | 7.65 | 173.792 | 2244.22 | 25.89 | 47.172 | 6.37 | 1.336 | 4.474 | 8856.78 | 2.127 | 97.9 | 77 | 1459 | 23.54 | 5756.9 | 2878.9 | 2796.1 | 4131.7 | 1211.6 | 0.6794 | 5.808
2024-12-09 | 22:37 | Data | 0 | 30.59 | 28.598 | 184.865 | 7.64 | 174.199 | 2247.83 | 25.89 | 47.172 | 6.37 | 1.331 | 4.489 | 8847.74 | 2.019 | 97.9 | 77.1 | 1461 | 23.59 | 5751 | 2882.1 | 2825.8 | 4151.8 | 1211.6 | 0.67675 | 5.82
2024-12-09 | 22:37 | Data | 0 | 30.874 | 28.646 | 184.865 | 7.64 | 174.199 | 2250.54 | 25.89 | 47.082 | 6.37 | 1.329 | 4.496 | 8825.13 | 1.911 | 97.9 | 77.2 | 1463 | 23.5 | 5736.3 | 2878.6 | 2803.7 | 4137.4 | 1211.6 | 0.67884 | 5.826
2024-12-09 | 22:37 | Data | 0 | 31.11 | 28.943 | 184.232 | 7.64 | 173.566 | 2248.73 | 25.9 | 47.082 | 6.37 | 1.347 | 4.497 | 8811.56 | 2.046 | 97.9 | 77 | 1462 | 23.63 | 5727.5 | 2876.3 | 2784.2 | 4119.8 | 1211.6 | 0.6816 | 5.843
2024-12-09 | 22:37 | Data | 0 | 31.069 | 29.321 | 183.282 | 7.64 | 172.798 | 2246.93 | 25.89 | 46.991 | 6.38 | 1.343 | 4.508 | 8807.04 | 1.843 | 97.9 | 77 | 1461 | 23.41 | 5724.6 | 2851.6 | 2802.7 | 4115.7 | 1211.6 | 0.67475 | 5.851
2024-12-09 | 22:37 | Data | 0 | 31.555 | 29.321 | 182.377 | 7.64 | 171.984 | 2246.93 | 25.89 | 46.811 | 6.37 | 1.334 | 4.479 | 8829.65 | 2.046 | 97.9 | 77.1 | 1461 | 23.36 | 5739.3 | 2848.8 | 2810.7 | 4122.2 | 1211.6 | 0.67378 | 5.813
2024-12-09 | 22:38 | Data | 0 | 31.171 | 29.071 | 182.287 | 7.64 | 171.984 | 2241.5 | 25.89 | 46.721 | 6.37 | 1.328 | 4.466 | 8856.78 | 1.782 | 97.9 | 77.1 | 1458 | 23.36 | 5756.9 | 2842.3 | 2798.9 | 4113.2 | 1211.6 | 0.67396 | 5.795
2024-12-09 | 22:38 | Data | 0 | 31.238 | 29.469 | 182.332 | 7.64 | 171.849 | 2244.22 | 25.9 | 46.54 | 6.37 | 1.336 | 4.437 | 8838.69 | 1.701 | 97.9 | 76.9 | 1459 | 23.22 | 5745.1 | 2859.3 | 2787.7 | 4112.6 | 1211.6 | 0.6777 | 5.774
2024-12-09 | 22:38 | Data | 0 | 31.063 | 29.152 | 182.196 | 7.64 | 171.758 | 2238.79 | 25.89 | 46.721 | 6.37 | 1.331 | 4.458 | 8856.78 | 1.843 | 97.9 | 77 | 1455 | 23.36 | 5756.9 | 2869.2 | 2791.2 | 4120.4 | 1211.6 | 0.67996 | 5.79
2024-12-09 | 22:38 | Data | 0 | 30.907 | 29.125 | 182.016 | 7.64 | 171.758 | 2243.31 | 25.89 | 46.811 | 6.36 | 1.329 | 4.44 | 8829.65 | 1.755 | 97.9 | 77 | 1459 | 23.36 | 5739.3 | 2843.7 | 2788.7 | 4102.2 | 1211.6 | 0.67528 | 5.769
2024-12-09 | 22:38 | Data | 0 | 30.658 | 28.855 | 181.97 | 7.65 | 171.623 | 2242.41 | 25.89 | 47.082 | 6.37 | 1.334 | 4.425 | 8856.78 | 1.857 | 97.9 | 76.8 | 1458 | 23.5 | 5756.9 | 2846.6 | 2791.1 | 4103.1 | 1211.6 | 0.6737 | 5.759
2024-12-09 | 22:38 | Data | 0 | 31.508 | 29.584 | 182.287 | 7.65 | 171.984 | 2242.41 | 25.89 | 47.082 | 6.37 | 1.329 | 4.427 | 8838.69 | 2.005 | 97.9 | 76.9 | 1457 | 23.59 | 5745.1 | 2861.8 | 2785.6 | 4112.4 | 1211.6 | 0.6791 | 5.756
2024-12-09 | 22:38 | Data | 0 | 31.339 | 29.132 | 182.513 | 7.64 | 172.075 | 2241.5 | 25.89 | 47.082 | 6.38 | 1.323 | 4.419 | 8838.69 | 1.944 | 97.9 | 77 | 1457 | 23.54 | 5745.1 | 2850 | 2766.9 | 4092.7 | 1211.6 | 0.67883 | 5.742
2024-12-09 | 22:38 | Data | 0 | 31.312 | 29.51 | 182.468 | 7.64 | 172.075 | 2242.41 | 25.88 | 47.082 | 6.37 | 1.324 | 4.428 | 8829.65 | 2.025 | 97.9 | 77 | 1457 | 23.59 | 5739.3 | 2819.7 | 2792.9 | 4090.2 | 1211.6 | 0.67231 | 5.752
2024-12-09 | 22:38 | Data | 0 | 31.603 | 29.503 | 182.558 | 7.64 | 172.21 | 2241.5 | 25.89 | 47.082 | 6.37 | 1.332 | 4.452 | 8829.65 | 1.843 | 97.9 | 77 | 1458 | 23.59 | 5739.3 | 2856.8 | 2792.8 | 4117.5 | 1211.6 | 0.67611 | 5.785
2024-12-09 | 22:38 | Data | 0 | 31.799 | 29.942 | 182.694 | 7.64 | 172.256 | 2241.5 | 25.89 | 47.172 | 6.37 | 1.328 | 4.431 | 8811.56 | 1.782 | 97.9 | 76.9 | 1457 | 23.54 | 5727.5 | 2844.8 | 2797.4 | 4110.3 | 1211.6 | 0.67452 | 5.76
2024-12-09 | 22:38 | Data | 0 | 31.799 | 29.753 | 182.739 | 7.64 | 172.301 | 2241.5 | 25.89 | 47.082 | 6.37 | 1.322 | 4.434 | 8793.47 | 1.843 | 97.9 | 77 | 1457 | 23.59 | 5715.8 | 2859.9 | 2760.1 | 4092.5 | 1211.6 | 0.68107 | 5.756
2024-12-09 | 22:38 | Data | 0 | 31.974 | 30.266 | 183.011 | 7.64 | 172.482 | 2242.41 | 25.9 | 47.172 | 6.36 | 1.325 | 4.448 | 8784.42 | 2.059 | 97.9 | 77 | 1458 | 23.59 | 5709.9 | 2867.2 | 2798.4 | 4127.6 | 1211.6 | 0.67669 | 5.774
2024-12-09 | 22:38 | Data | 0 | 31.974 | 30.185 | 183.056 | 7.64 | 172.527 | 2242.41 | 25.89 | 47.172 | 6.37 | 1.329 | 4.441 | 8788.95 | 2.012 | 97.9 | 77 | 1457 | 23.59 | 5712.8 | 2861.6 | 2782.1 | 4109.5 | 1211.6 | 0.6798 | 5.771
2024-12-09 | 22:38 | Data | 0 | 32.204 | 30.192 | 183.192 | 7.64 | 172.708 | 2242.41 | 25.89 | 47.082 | 6.36 | 1.335 | 4.438 | 8788.95 | 1.843 | 97.9 | 76.9 | 1457 | 23.54 | 5712.8 | 2827.8 | 2771.5 | 4084.7 | 1211.6 | 0.67448 | 5.773
2024-12-09 | 22:38 | Data | 0 | 32.494 | 30.556 | 183.192 | 7.64 | 172.753 | 2241.5 | 25.89 | 47.082 | 6.37 | 1.343 | 4.452 | 8784.42 | 1.992 | 97.9 | 76.8 | 1457 | 23.59 | 5709.9 | 2844 | 2798.9 | 4106.4 | 1211.6 | 0.6753 | 5.795
2024-12-09 | 22:38 | Data | 0 | 32.494 | 30.428 | 183.373 | 7.64 | 172.888 | 2236.98 | 25.89 | 46.721 | 6.38 | 1.327 | 4.454 | 8788.95 | 2.019 | 97.9 | 77.1 | 1455 | 23.36 | 5712.8 | 2848.6 | 2781.2 | 4100 | 1211.6 | 0.67759 | 5.779
2024-12-09 | 22:38 | Data | 0 | 32.278 | 30.475 | 183.327 | 7.64 | 172.798 | 2238.79 | 25.89 | 46.721 | 6.37 | 1.332 | 4.427 | 8743.73 | 1.911 | 97.9 | 76.9 | 1455 | 23.36 | 5683.4 | 2842.2 | 2801.3 | 4111.2 | 1211.6 | 0.67446 | 5.758
2024-12-09 | 22:38 | Data | 0 | 32.717 | 30.651 | 183.373 | 7.64 | 172.888 | 2241.5 | 25.89 | 46.721 | 6.37 | 1.332 | 4.426 | 8743.73 | 2.073 | 97.9 | 76.9 | 1457 | 23.36 | 5683.4 | 2879.3 | 2802.3 | 4132.5 | 1211.6 | 0.67942 | 5.757
2024-12-09 | 22:39 | Data | 0 | 32.393 | 30.651 | 183.508 | 7.64 | 172.934 | 2241.5 | 25.89 | 46.811 | 6.36 | 1.335 | 4.454 | 8757.29 | 1.681 | 97.9 | 76.9 | 1458 | 23.41 | 5692.2 | 2872 | 2809 | 4136.8 | 1211.6 | 0.67697 | 5.789
2024-12-09 | 22:39 | Data | 0 | 32.501 | 30.982 | 183.553 | 7.64 | 172.979 | 2242.41 | 25.89 | 46.721 | 6.37 | 1.339 | 4.466 | 8743.73 | 1.816 | 97.9 | 76.9 | 1457 | 23.41 | 5683.4 | 2835.9 | 2802.7 | 4111.6 | 1211.7 | 0.67253 | 5.806
2024-12-09 | 22:39 | Data | 0 | 32.723 | 30.853 | 183.508 | 7.64 | 172.934 | 2244.22 | 25.89 | 46.721 | 6.37 | 1.335 | 4.458 | 8734.68 | 1.897 | 97.9 | 77 | 1459 | 23.36 | 5677.5 | 2839.5 | 2799.1 | 4109 | 1211.7 | 0.67246 | 5.793
2024-12-09 | 22:39 | Data | 0 | 32.723 | 30.88 | 183.644 | 7.64 | 173.069 | 2246.93 | 25.89 | 46.721 | 6.37 | 1.331 | 4.471 | 8730.16 | 1.958 | 97.9 | 77.1 | 1461 | 23.32 | 5674.6 | 2870.8 | 2808 | 4137.8 | 1211.7 | 0.6765 | 5.802
2024-12-09 | 22:39 | Data | 0 | 32.339 | 30.651 | 183.553 | 7.64 | 173.069 | 2246.93 | 25.89 | 46.721 | 6.37 | 1.326 | 4.472 | 8743.73 | 1.823 | 97.9 | 77.1 | 1461 | 23.36 | 5683.4 | 2847.8 | 2787.9 | 4105.4 | 1211.7 | 0.67664 | 5.798
2024-12-09 | 22:39 | Data | 0 | 32.98 | 30.671 | 183.553 | 7.64 | 173.16 | 2246.93 | 25.89 | 46.721 | 6.37 | 1.329 | 4.482 | 8752.77 | 1.958 | 97.9 | 77.1 | 1461 | 23.36 | 5689.3 | 2841.8 | 2797.5 | 4109.3 | 1211.7 | 0.67433 | 5.811
2024-12-09 | 22:39 | Data | 0 | 32.723 | 30.867 | 183.553 | 7.64 | 173.114 | 2246.93 | 25.89 | 46.811 | 6.36 | 1.33 | 4.47 | 8757.29 | 1.897 | 97.9 | 77.1 | 1461 | 23.41 | 5692.2 | 2853.8 | 2821.6 | 4131.2 | 1211.7 | 0.6735 | 5.8
2024-12-09 | 22:39 | Data | 0 | 32.899 | 30.907 | 183.599 | 7.64 | 173.069 | 2250.54 | 25.89 | 46.811 | 6.37 | 1.335 | 4.465 | 8743.73 | 2.052 | 97.9 | 77 | 1462 | 23.41 | 5683.4 | 2842.8 | 2800.3 | 4114.1 | 1211.7 | 0.67321 | 5.799
2024-12-09 | 22:39 | Data | 0 | 32.561 | 30.766 | 183.553 | 7.64 | 173.069 | 2246.93 | 25.89 | 46.721 | 6.36 | 1.33 | 4.46 | 8757.29 | 1.735 | 97.9 | 77 | 1461 | 23.36 | 5692.2 | 2841.4 | 2788.9 | 4105.8 | 1211.7 | 0.67413 | 5.789
2024-12-09 | 22:39 | Data | 0 | 32.501 | 30.874 | 183.689 | 7.64 | 173.114 | 2249.64 | 25.89 | 46.811 | 6.37 | 1.326 | 4.449 | 8734.68 | 1.83 | 97.9 | 77 | 1462 | 23.41 | 5677.5 | 2851.3 | 2780.5 | 4106.1 | 1211.7 | 0.67656 | 5.775
2024-12-09 | 22:39 | Data | 0 | 32.73 | 30.88 | 183.599 | 7.64 | 173.114 | 2246.93 | 25.9 | 46.721 | 6.36 | 1.335 | 4.435 | 8739.2 | 1.843 | 97.9 | 76.9 | 1461 | 23.32 | 5680.5 | 2848.8 | 2789.1 | 4105.4 | 1211.7 | 0.67671 | 5.77
2024-12-09 | 22:39 | Data | 0 | 32.784 | 30.887 | 183.508 | 7.64 | 173.16 | 2243.31 | 25.89 | 46.811 | 6.36 | 1.343 | 4.457 | 8730.16 | 1.843 | 97.9 | 76.8 | 1459 | 23.41 | 5674.6 | 2851.2 | 2792.3 | 4109.3 | 1211.7 | 0.67822 | 5.8
2024-12-09 | 22:39 | Data | 0 | 32.723 | 30.84 | 183.599 | 7.64 | 172.979 | 2245.12 | 25.9 | 46.721 | 6.36 | 1.339 | 4.477 | 8725.64 | 1.931 | 97.9 | 77 | 1459 | 23.41 | 5671.7 | 2853 | 2798 | 4114.5 | 1211.7 | 0.6761 | 5.816
2024-12-09 | 22:39 | Data | 0 | 32.561 | 31.056 | 183.599 | 7.64 | 173.114 | 2245.12 | 25.89 | 46.721 | 6.37 | 1.34 | 4.481 | 8716.59 | 1.708 | 97.9 | 77 | 1459 | 23.36 | 5665.8 | 2851 | 2788.1 | 4108.4 | 1211.7 | 0.67686 | 5.82
2024-12-09 | 22:39 | Data | 0 | 32.723 | 30.705 | 183.508 | 7.64 | 172.979 | 2243.31 | 25.89 | 46.811 | 6.36 | 1.332 | 4.478 | 8716.59 | 1.965 | 97.9 | 77.1 | 1458 | 23.41 | 5665.8 | 2848.8 | 2808.6 | 4118.5 | 1211.7 | 0.67602 | 5.81
2024-12-09 | 22:39 | Data | 0 | 32.521 | 30.968 | 183.463 | 7.64 | 173.069 | 2244.22 | 25.89 | 46.63 | 6.37 | 1.338 | 4.477 | 8730.16 | 1.85 | 97.9 | 77 | 1458 | 23.41 | 5674.6 | 2846.8 | 2819.1 | 4127.4 | 1211.7 | 0.6723 | 5.815
2024-12-09 | 22:39 | Data | 0 | 32.825 | 30.88 | 183.644 | 7.64 | 173.069 | 2244.22 | 25.89 | 46.721 | 6.37 | 1.339 | 4.462 | 8734.68 | 1.951 | 97.9 | 76.9 | 1459 | 23.41 | 5677.5 | 2852.3 | 2805.3 | 4117.8 | 1211.7 | 0.67648 | 5.799
2024-12-09 | 22:40 | Data | 0 | 32.723 | 30.934 | 183.508 | 7.64 | 173.069 | 2246.93 | 25.89 | 46.721 | 6.36 | 1.335 | 4.46 | 8743.73 | 1.89 | 97.9 | 77 | 1461 | 23.36 | 5683.4 | 2854.7 | 2793.7 | 4113.8 | 1211.7 | 0.67709 | 5.796
2024-12-09 | 22:40 | Data | 0 | 33.021 | 30.887 | 183.689 | 7.64 | 173.114 | 2246.93 | 25.89 | 46.721 | 6.36 | 1.344 | 4.448 | 8743.73 | 1.884 | 97.9 | 76.8 | 1461 | 23.36 | 5683.4 | 2856.6 | 2773.3 | 4098.5 | 1211.7 | 0.67947 | 5.792
2024-12-09 | 22:40 | Data | 0 | 32.514 | 30.658 | 183.463 | 7.64 | 173.069 | 2246.93 | 25.89 | 46.811 | 6.36 | 1.336 | 4.472 | 8739.2 | 2.032 | 97.9 | 77 | 1461 | 23.41 | 5680.5 | 2861.7 | 2781.2 | 4107.5 | 1211.7 | 0.67812 | 5.808
2024-12-09 | 22:40 | Data | 0 | 33.061 | 30.901 | 183.689 | 7.64 | 173.16 | 2249.64 | 25.89 | 46.811 | 6.36 | 1.33 | 4.465 | 8743.73 | 1.951 | 97.9 | 77 | 1462 | 23.36 | 5683.4 | 2848.4 | 2789.5 | 4105.7 | 1211.7 | 0.67616 | 5.797
2024-12-09 | 22:40 | Data | 0 | 32.723 | 30.867 | 183.508 | 7.64 | 173.069 | 2248.73 | 25.89 | 46.811 | 6.37 | 1.354 | 4.481 | 8743.73 | 1.884 | 97.9 | 76.8 | 1462 | 23.36 | 5683.4 | 2859.2 | 2809.5 | 4129.5 | 1211.7 | 0.6773 | 5.835
2024-12-09 | 22:40 | Data | 0 | 32.946 | 30.84 | 183.327 | 7.64 | 172.708 | 2247.83 | 25.89 | 46.721 | 6.36 | 1.347 | 4.488 | 8730.16 | 1.998 | 97.9 | 76.9 | 1461 | 23.32 | 5674.6 | 2848.1 | 2773.2 | 4097.1 | 1211.7 | 0.67535 | 5.836
2024-12-09 | 22:40 | Data | 0 | 32.777 | 30.766 | 183.282 | 7.64 | 172.708 | 2246.93 | 25.89 | 46.721 | 6.36 | 1.343 | 4.455 | 8730.16 | 1.843 | 97.9 | 76.8 | 1460 | 23.41 | 5674.6 | 2875.5 | 2783.3 | 4119.2 | 1211.7 | 0.68075 | 5.799
2024-12-09 | 22:40 | Data | 0 | 32.696 | 30.678 | 183.192 | 7.64 | 172.708 | 2246.02 | 25.89 | 46.811 | 6.36 | 1.337 | 4.446 | 8730.16 | 1.958 | 97.9 | 76.9 | 1460 | 23.41 | 5674.6 | 2841.6 | 2771 | 4084.8 | 1211.7 | 0.67993 | 5.783
2024-12-09 | 22:40 | Data | 0 | 32.73 | 30.941 | 183.282 | 7.64 | 172.753 | 2244.22 | 25.89 | 46.721 | 6.37 | 1.326 | 4.451 | 8716.59 | 1.782 | 97.9 | 77 | 1459 | 23.36 | 5665.8 | 2832.8 | 2796.7 | 4101 | 1211.7 | 0.67302 | 5.777
2024-12-09 | 22:40 | Data | 0 | 32.723 | 30.995 | 183.373 | 7.64 | 172.798 | 2244.22 | 25.89 | 46.811 | 6.36 | 1.337 | 4.444 | 8707.55 | 1.843 | 97.9 | 76.9 | 1459 | 23.36 | 5659.9 | 2849.2 | 2796.2 | 4112.4 | 1211.7 | 0.675 | 5.78
2024-12-09 | 22:40 | Data | 0 | 32.899 | 31.096 | 183.237 | 7.64 | 172.708 | 2239.7 | 25.89 | 46.721 | 6.36 | 1.329 | 4.452 | 8662.33 | 1.857 | 97.9 | 77 | 1456 | 23.36 | 5630.5 | 2856.2 | 2788.7 | 4111.4 | 1211.7 | 0.67748 | 5.78
2024-12-09 | 22:40 | Data | 0 | 32.723 | 30.853 | 183.192 | 7.64 | 172.708 | 2244.22 | 25.89 | 46.811 | 6.36 | 1.326 | 4.474 | 8657.8 | 1.958 | 97.9 | 77.1 | 1459 | 23.41 | 5627.6 | 2835.8 | 2799.1 | 4106.5 | 1211.7 | 0.6732 | 5.8
2024-12-09 | 22:40 | Data | 0 | 32.757 | 30.685 | 183.237 | 7.64 | 172.708 | 2244.22 | 25.89 | 46.811 | 6.36 | 1.344 | 4.454 | 8662.33 | 1.843 | 97.9 | 76.8 | 1459 | 23.41 | 5630.5 | 2846.8 | 2799.9 | 4111.3 | 1211.7 | 0.67531 | 5.798
2024-12-09 | 22:40 | Data | 0 | 32.899 | 30.907 | 183.282 | 7.64 | 172.753 | 2244.22 | 25.89 | 46.721 | 6.36 | 1.331 | 4.475 | 9164.29 | 2.039 | 97.9 | 77.1 | 1459 | 23.36 | 5956.8 | 2832.7 | 2799.7 | 4110.5 | 1211.7 | 0.6746 | 5.807
2024-12-09 | 22:40 | Data | 0 | 32.825 | 30.887 | 183.192 | 7.64 | 172.662 | 2246.02 | 25.89 | 46.721 | 6.36 | 1.327 | 4.46 | 8698.5 | 2.012 | 97.9 | 77.1 | 1460 | 23.36 | 5654 | 2841.7 | 2781.7 | 4097.8 | 1211.7 | 0.67564 | 5.788
2024-12-09 | 22:40 | Data | 0 | 32.737 | 30.88 | 183.237 | 7.64 | 172.708 | 2252.35 | 25.89 | 46.811 | 6.36 | 1.339 | 4.461 | 8716.59 | 1.85 | 97.9 | 76.9 | 1464 | 23.41 | 5665.8 | 2826.6 | 2789.1 | 4093.9 | 1211.7 | 0.67256 | 5.8
2024-12-09 | 22:40 | Data | 0 | 32.764 | 30.867 | 183.282 | 7.64 | 172.753 | 2251.45 | 25.89 | 46.811 | 6.36 | 1.329 | 4.471 | 8703.03 | 1.877 | 97.9 | 77.1 | 1463 | 23.41 | 5657 | 2837.3 | 2785.3 | 4097.2 | 1211.7 | 0.6749 | 5.8
2024-12-09 | 22:40 | Data | 0 | 32.831 | 31.083 | 183.282 | 7.64 | 172.708 | 2246.93 | 25.89 | 46.811 | 6.36 | 1.325 | 4.474 | 8721.11 | 1.971 | 97.9 | 77.2 | 1461 | 23.36 | 5668.7 | 2868.2 | 2788.5 | 4115 | 1211.7 | 0.67885 | 5.799
2024-12-09 | 22:41 | Data | 0 | 33.007 | 31.11 | 183.327 | 7.64 | 172.843 | 2252.35 | 25.89 | 46.721 | 6.36 | 1.329 | 4.484 | 8716.59 | 1.674 | 97.9 | 77.1 | 1464 | 23.36 | 5665.8 | 2840.5 | 2778 | 4095.6 | 1211.7 | 0.67681 | 5.813
2024-12-09 | 22:41 | Data | 0 | 32.953 | 31.009 | 183.463 | 7.64 | 172.888 | 2249.64 | 25.89 | 46.721 | 6.36 | 1.336 | 4.476 | 8712.07 | 2.046 | 97.9 | 77 | 1463 | 23.41 | 5662.8 | 2869.4 | 2779.1 | 4113.3 | 1211.7 | 0.67957 | 5.812
2024-12-09 | 22:41 | Data | 0 | 32.723 | 31.049 | 183.146 | 7.64 | 172.753 | 2248.73 | 25.89 | 46.811 | 6.36 | 1.325 | 4.466 | 8721.11 | 1.958 | 97.9 | 77.1 | 1462 | 23.41 | 5668.7 | 2862.3 | 2784.2 | 4113.3 | 1211.7 | 0.67816 | 5.792
2024-12-09 | 22:41 | Data | 0 | 32.723 | 30.88 | 183.282 | 7.64 | 172.843 | 2249.64 | 25.89 | 46.721 | 6.36 | 1.328 | 4.451 | 8730.16 | 1.958 | 97.9 | 77 | 1462 | 23.36 | 5674.6 | 2843.5 | 2808.7 | 4113.1 | 1211.8 | 0.67381 | 5.78
2024-12-09 | 22:41 | Data | 0 | 32.75 | 30.867 | 183.237 | 7.64 | 172.708 | 2249.64 | 25.9 | 47.172 | 6.36 | 1.336 | 4.449 | 8739.2 | 1.863 | 97.9 | 76.9 | 1463 | 23.59 | 5680.5 | 2835.5 | 2785 | 4092.4 | 1211.8 | 0.67435 | 5.787
2024-12-09 | 22:41 | Data | 0 | 32.514 | 31.09 | 183.192 | 7.64 | 172.753 | 2252.35 | 25.89 | 46.811 | 6.36 | 1.335 | 4.445 | 8743.73 | 1.809 | 97.9 | 76.9 | 1464 | 23.36 | 5683.4 | 2871.2 | 2783.6 | 4116.3 | 1211.8 | 0.67821 | 5.78
2024-12-09 | 22:41 | Data | 0 | 32.71 | 30.772 | 183.282 | 7.64 | 172.708 | 2246.93 | 25.89 | 46.721 | 6.37 | 1.329 | 4.453 | 8743.73 | 2.262 | 97.9 | 77 | 1461 | 23.41 | 5683.4 | 2846.4 | 2792.8 | 4108.5 | 1211.8 | 0.67614 | 5.781
2024-12-09 | 22:41 | Data | 0 | 32.953 | 30.88 | 183.237 | 7.64 | 172.753 | 2246.93 | 25.89 | 46.721 | 6.36 | 1.344 | 4.47 | 8743.73 | 1.951 | 97.9 | 76.9 | 1461 | 23.36 | 5683.4 | 2856.1 | 2792.6 | 4117.9 | 1211.8 | 0.67496 | 5.814
2024-12-09 | 22:41 | Data | 0 | 32.831 | 30.887 | 183.192 | 7.64 | 172.753 | 2246.93 | 25.89 | 46.721 | 6.36 | 1.335 | 4.454 | 8743.73 | 1.83 | 97.9 | 76.9 | 1461 | 23.36 | 5683.4 | 2829.4 | 2793.4 | 4097.8 | 1211.8 | 0.67275 | 5.789
2024-12-09 | 22:41 | Data | 0 | 33.169 | 31.312 | 183.553 | 7.64 | 172.843 | 2249.64 | 25.89 | 46.721 | 6.36 | 1.33 | 4.466 | 8743.73 | 1.951 | 97.9 | 77.1 | 1462 | 23.36 | 5683.4 | 2829.9 | 2802.3 | 4104.3 | 1211.8 | 0.67132 | 5.798
2024-12-09 | 22:41 | Data | 0 | 32.892 | 31.15 | 183.327 | 7.64 | 172.934 | 2251.45 | 25.89 | 46.811 | 6.36 | 1.321 | 4.465 | 8752.77 | 1.911 | 97.9 | 77.1 | 1463 | 23.41 | 5689.3 | 2838.1 | 2797.9 | 4109.2 | 1211.8 | 0.6742 | 5.786
2024-12-09 | 22:41 | Data | 0 | 32.892 | 30.88 | 183.192 | 7.64 | 172.753 | 2252.35 | 25.89 | 46.811 | 6.36 | 1.329 | 4.462 | 8743.73 | 2.059 | 97.9 | 77 | 1464 | 23.41 | 5683.4 | 2849.1 | 2793.7 | 4112.1 | 1211.8 | 0.6758 | 5.79
2024-12-09 | 22:41 | Data | 0 | 33.176 | 30.961 | 183.418 | 7.64 | 172.934 | 2251.45 | 25.89 | 46.811 | 6.37 | 1.336 | 4.481 | 8743.73 | 1.85 | 97.9 | 77 | 1463 | 23.41 | 5683.4 | 2847.2 | 2781.6 | 4103.5 | 1211.8 | 0.67773 | 5.817
2024-12-09 | 22:41 | Data | 0 | 32.865 | 30.995 | 183.373 | 7.64 | 172.753 | 2252.35 | 25.89 | 46.721 | 6.37 | 1.337 | 4.457 | 8716.59 | 1.647 | 97.9 | 76.9 | 1464 | 23.36 | 5665.8 | 2839 | 2791.1 | 4098 | 1211.8 | 0.67644 | 5.793
2024-12-09 | 22:41 | Data | 0 | 32.615 | 30.988 | 183.327 | 7.64 | 172.753 | 2252.35 | 25.89 | 46.721 | 6.36 | 1.335 | 4.459 | 8703.03 | 1.931 | 97.9 | 77 | 1464 | 23.36 | 5657 | 2869.9 | 2788.4 | 4118.5 | 1211.8 | 0.68005 | 5.795
2024-12-09 | 22:41 | Data | 0 | 32.899 | 31.103 | 183.282 | 7.64 | 172.708 | 2254.16 | 25.89 | 46.811 | 6.36 | 1.341 | 4.427 | 8712.07 | 1.843 | 97.9 | 76.7 | 1466 | 23.36 | 5662.8 | 2852.3 | 2774.3 | 4098.2 | 1211.8 | 0.67924 | 5.77
2024-12-09 | 22:41 | Data | 0 | 32.568 | 31.049 | 183.282 | 7.64 | 172.798 | 2255.97 | 25.89 | 46.721 | 6.36 | 1.337 | 4.447 | 8716.59 | 1.755 | 97.9 | 76.9 | 1466 | 23.41 | 5665.8 | 2832.1 | 2786.8 | 4098.7 | 1211.8 | 0.67459 | 5.785
2024-12-09 | 22:42 | Data | 0 | 32.899 | 30.934 | 183.373 | 7.64 | 172.798 | 2250.54 | 25.89 | 46.811 | 6.36 | 1.33 | 4.429 | 8703.03 | 1.823 | 97.9 | 76.9 | 1463 | 23.41 | 5657 | 2834.9 | 2772.7 | 4085.1 | 1211.8 | 0.67554 | 5.76
2024-12-09 | 22:42 | Data | 0 | 33.095 | 30.887 | 183.373 | 7.64 | 172.888 | 2255.97 | 25.89 | 46.721 | 6.37 | 1.329 | 4.465 | 8703.03 | 1.917 | 97.9 | 77.1 | 1466 | 23.41 | 5657 | 2856 | 2805 | 4119.3 | 1211.8 | 0.67628 | 5.795
2024-12-09 | 22:42 | Data | 0 | 33.041 | 30.901 | 183.463 | 7.64 | 172.843 | 2255.97 | 25.89 | 46.721 | 6.36 | 1.329 | 4.466 | 8689.46 | 1.985 | 97.9 | 77.1 | 1466 | 23.36 | 5648.1 | 2840.9 | 2812.1 | 4119.3 | 1211.8 | 0.67327 | 5.796
2024-12-09 | 22:42 | Data | 0 | 32.717 | 30.712 | 183.237 | 7.64 | 172.708 | 2254.16 | 25.89 | 46.269 | 6.37 | 1.332 | 4.459 | 8693.98 | 1.958 | 97.9 | 77 | 1465 | 23.13 | 5651.1 | 2835.4 | 2794.8 | 4106.2 | 1211.8 | 0.67227 | 5.793
2024-12-09 | 22:42 | Data | 0 | 33.108 | 31.333 | 183.508 | 7.64 | 172.979 | 2249.64 | 25.89 | 46.721 | 6.36 | 1.334 | 4.465 | 8703.03 | 1.87 | 97.9 | 77 | 1463 | 23.36 | 5657 | 2851.5 | 2819 | 4121.2 | 1211.8 | 0.67225 | 5.799
2024-12-09 | 22:42 | Data | 0 | 32.94 | 31.056 | 183.237 | 7.64 | 172.798 | 2255.97 | 25.89 | 46.721 | 6.36 | 1.334 | 4.467 | 8716.59 | 1.951 | 97.9 | 77 | 1466 | 23.36 | 5665.8 | 2847.3 | 2795.9 | 4107.4 | 1211.8 | 0.67507 | 5.803
2024-12-09 | 22:42 | Data | 0 | 32.723 | 30.88 | 183.192 | 7.64 | 172.708 | 2255.97 | 25.89 | 46.811 | 6.36 | 1.337 | 4.446 | 8707.55 | 2.019 | 97.9 | 76.9 | 1466 | 23.36 | 5659.9 | 2834.9 | 2794.1 | 4103.1 | 1211.8 | 0.67213 | 5.784
2024-12-09 | 22:42 | Data | 0 | 32.75 | 30.887 | 183.192 | 7.64 | 172.843 | 2255.97 | 25.89 | 46.811 | 6.37 | 1.34 | 4.455 | 8716.59 | 1.836 | 97.9 | 76.9 | 1466 | 23.41 | 5665.8 | 2842.2 | 2816.2 | 4120 | 1211.8 | 0.67213 | 5.796
2024-12-09 | 22:42 | Data | 0 | 32.723 | 30.766 | 183.418 | 7.64 | 172.798 | 2255.97 | 25.89 | 46.811 | 6.36 | 1.341 | 4.46 | 8721.11 | 1.843 | 97.9 | 76.9 | 1466 | 23.41 | 5668.7 | 2825.2 | 2783.3 | 4090.7 | 1211.8 | 0.67325 | 5.801
2024-12-09 | 22:42 | Data | 0 | 32.723 | 30.88 | 183.146 | 7.64 | 172.708 | 2260.48 | 25.89 | 46.721 | 6.36 | 1.335 | 4.452 | 8739.2 | 1.843 | 97.9 | 76.9 | 1470 | 23.36 | 5680.5 | 2858.1 | 2781.7 | 4103.5 | 1211.8 | 0.67947 | 5.788
2024-12-09 | 22:42 | Data | 0 | 32.588 | 30.685 | 183.327 | 7.64 | 172.798 | 2261.39 | 25.9 | 46.721 | 6.36 | 1.338 | 4.472 | 8734.68 | 1.789 | 97.9 | 77 | 1469 | 23.41 | 5677.5 | 2827.4 | 2798.7 | 4099 | 1211.8 | 0.67186 | 5.809
2024-12-09 | 22:42 | Data | 0 | 32.872 | 30.88 | 183.327 | 7.64 | 172.798 | 2254.16 | 25.9 | 46.721 | 6.36 | 1.338 | 4.469 | 8734.68 | 1.688 | 97.9 | 77 | 1465 | 23.36 | 5677.5 | 2851.3 | 2815.5 | 4126.3 | 1211.8 | 0.67423 | 5.807
2024-12-09 | 22:42 | Data | 0 | 32.831 | 30.685 | 183.327 | 7.64 | 172.798 | 2255.97 | 25.89 | 47.172 | 6.37 | 1.341 | 4.445 | 8707.55 | 1.938 | 97.9 | 76.8 | 1466 | 23.54 | 5659.9 | 2848.5 | 2819.3 | 4127.6 | 1211.8 | 0.67212 | 5.786
2024-12-09 | 22:42 | Data | 0 | 32.906 | 30.995 | 183.282 | 7.64 | 172.798 | 2256.87 | 25.89 | 47.082 | 6.36 | 1.34 | 4.422 | 8703.03 | 2.059 | 97.9 | 76.7 | 1467 | 23.59 | 5657 | 2853.6 | 2807.3 | 4120.5 | 1211.8 | 0.67652 | 5.761
2024-12-09 | 22:42 | Data | 0 | 32.501 | 30.766 | 183.192 | 7.64 | 172.662 | 2258.68 | 25.9 | 47.082 | 6.37 | 1.342 | 4.456 | 8703.03 | 1.843 | 97.9 | 76.9 | 1468 | 23.54 | 5657 | 2833.7 | 2802.9 | 4105 | 1211.8 | 0.67238 | 5.799
2024-12-09 | 22:42 | Data | 0 | 32.615 | 30.88 | 183.237 | 7.64 | 172.798 | 2257.77 | 25.89 | 47.082 | 6.36 | 1.344 | 4.453 | 8693.98 | 1.742 | 97.9 | 76.8 | 1467 | 23.54 | 5651.1 | 2854.8 | 2820.8 | 4128.9 | 1211.8 | 0.67439 | 5.797
2024-12-09 | 22:42 | Data | 0 | 32.953 | 31.198 | 183.282 | 7.64 | 172.843 | 2252.35 | 25.89 | 47.082 | 6.36 | 1.341 | 4.446 | 8743.73 | 1.958 | 97.9 | 76.8 | 1464 | 23.59 | 5683.4 | 2836.3 | 2810.7 | 4120.5 | 1211.8 | 0.67136 | 5.787
2024-12-09 | 22:42 | Data | 0 | 32.953 | 30.887 | 183.327 | 7.63 | 172.798 | 2255.97 | 25.89 | 46.721 | 6.37 | 1.336 | 4.475 | 8748.25 | 2.046 | 97.9 | 77 | 1465 | 23.32 | 5686.4 | 2833.6 | 2832 | 4137 | 1211.8 | 0.67016 | 5.811
2024-12-09 | 22:42 | Data | 0 | 32.892 | 30.934 | 183.282 | 7.63 | 172.753 | 2252.35 | 25.9 | 46.721 | 6.36 | 1.332 | 4.462 | 8743.73 | 1.749 | 97.9 | 77 | 1463 | 23.41 | 5683.4 | 2854.2 | 2800.3 | 4119.1 | 1211.8 | 0.6758 | 5.794
2024-12-09 | 22:43 | Data | 0 | 32.845 | 31.306 | 183.463 | 7.64 | 172.843 | 2255.97 | 25.89 | 46.721 | 6.36 | 1.335 | 4.496 | 8757.29 | 1.708 | 97.9 | 77.1 | 1466 | 23.36 | 5692.2 | 2852.2 | 2792.2 | 4089.9 | 1211.8 | 0.6758 | 5.831
2024-12-09 | 22:43 | Data | 0 | 32.845 | 31.002 | 183.237 | 7.63 | 172.753 | 2251.45 | 25.89 | 46.811 | 6.37 | 1.335 | 4.455 | 8721.11 | 1.884 | 97.9 | 76.9 | 1463 | 23.41 | 5668.7 | 2841.7 | 2779.7 | 4096.9 | 1211.8 | 0.67633 | 5.789
2024-12-09 | 22:43 | Data | 0 | 32.683 | 31.056 | 183.282 | 7.64 | 172.753 | 2258.68 | 25.89 | 46.721 | 6.36 | 1.336 | 4.457 | 8712.07 | 1.695 | 97.9 | 76.9 | 1468 | 23.32 | 5662.8 | 2849.2 | 2796.7 | 4112.1 | 1211.8 | 0.67588 | 5.793
2024-12-09 | 22:43 | Data | 0 | 32.845 | 31.056 | 183.282 | 7.64 | 172.753 | 2257.77 | 25.89 | 46.721 | 6.36 | 1.331 | 4.457 | 8712.07 | 1.85 | 97.9 | 77 | 1468 | 23.41 | 5662.8 | 2847.1 | 2786.5 | 4107.2 | 1211.8 | 0.67586 | 5.789
2024-12-09 | 22:43 | Data | 0 | 32.953 | 30.907 | 183.192 | 7.64 | 172.662 | 2258.68 | 25.89 | 46.721 | 6.36 | 1.331 | 4.479 | 8730.16 | 1.958 | 97.9 | 77.1 | 1468 | 23.36 | 5674.6 | 2836.1 | 2764.6 | 4081.5 | 1211.8 | 0.67778 | 5.811
2024-12-09 | 22:43 | Data | 0 | 32.946 | 30.88 | 183.192 | 7.64 | 172.662 | 2258.68 | 25.89 | 46.721 | 6.37 | 1.34 | 4.472 | 8730.16 | 2.066 | 97.9 | 76.9 | 1468 | 23.36 | 5674.6 | 2856 | 2790.9 | 4110.4 | 1211.9 | 0.67709 | 5.811
2024-12-09 | 22:43 | Data | 0 | 32.73 | 31.056 | 183.192 | 7.64 | 172.617 | 2258.68 | 25.89 | 46.721 | 6.36 | 1.336 | 4.472 | 8734.68 | 2.005 | 97.9 | 77 | 1468 | 23.41 | 5677.5 | 2849 | 2787.7 | 4107.5 | 1211.9 | 0.6766 | 5.808
2024-12-09 | 22:43 | Data | 0 | 32.946 | 30.88 | 183.101 | 7.64 | 172.662 | 2258.68 | 25.89 | 46.811 | 6.36 | 1.337 | 4.449 | 8734.68 | 1.958 | 97.9 | 76.9 | 1468 | 23.36 | 5677.5 | 2831 | 2779.3 | 4094.6 | 1211.9 | 0.6732 | 5.787
2024-12-09 | 22:43 | Data | 0 | 32.798 | 31.056 | 183.282 | 7.64 | 172.798 | 2254.16 | 25.89 | 46.811 | 6.36 | 1.33 | 4.447 | 8721.11 | 1.843 | 97.9 | 77 | 1465 | 23.41 | 5668.7 | 2848.8 | 2770.1 | 4094.3 | 1211.9 | 0.67709 | 5.778
2024-12-09 | 22:43 | Data | 0 | 33.169 | 30.901 | 183.237 | 7.64 | 172.753 | 2254.16 | 25.89 | 46.721 | 6.37 | 1.336 | 4.434 | 8716.59 | 2.059 | 97.9 | 76.9 | 1466 | 23.36 | 5665.8 | 2840.4 | 2785.9 | 4099.9 | 1211.9 | 0.67602 | 5.771
2024-12-09 | 22:43 | Data | 0 | 32.838 | 30.88 | 183.192 | 7.63 | 172.753 | 2258.68 | 25.89 | 46.811 | 6.36 | 1.336 | 4.474 | 8712.07 | 2.019 | 97.9 | 77 | 1468 | 23.36 | 5662.8 | 2843.3 | 2780.1 | 4097.6 | 1211.9 | 0.67578 | 5.81
2024-12-09 | 22:43 | Data | 0 | 32.723 | 31.049 | 183.011 | 7.63 | 172.527 | 2257.77 | 25.9 | 46.811 | 6.36 | 1.33 | 4.47 | 8707.55 | 1.904 | 97.9 | 77.1 | 1467 | 23.41 | 5659.9 | 2833.6 | 2744.4 | 4066.6 | 1211.9 | 0.67866 | 5.799
2024-12-09 | 22:43 | Data | 0 | 32.899 | 30.988 | 183.146 | 7.63 | 172.572 | 2252.35 | 25.89 | 46.811 | 6.36 | 1.331 | 4.446 | 8707.55 | 1.863 | 97.9 | 76.9 | 1464 | 23.5 | 5659.9 | 2843.4 | 2799.4 | 4107.8 | 1211.9 | 0.67324 | 5.779
2024-12-09 | 22:43 | Data | 0 | 32.723 | 30.995 | 183.011 | 7.64 | 172.572 | 2258.68 | 25.89 | 46.721 | 6.36 | 1.322 | 4.453 | 8712.07 | 2.019 | 97.9 | 77.1 | 1468 | 23.36 | 5662.8 | 2833.8 | 2771.8 | 4084.1 | 1211.9 | 0.6767 | 5.774
2024-12-09 | 22:43 | Data | 0 | 32.953 | 30.907 | 183.011 | 7.64 | 172.572 | 2255.97 | 25.89 | 46.721 | 6.36 | 1.327 | 4.476 | 8703.03 | 1.843 | 97.9 | 77.1 | 1466 | 23.5 | 5657 | 2846.6 | 2769.9 | 4092.5 | 1211.9 | 0.6784 | 5.803
2024-12-09 | 22:43 | Data | 0 | 32.561 | 30.88 | 183.011 | 7.64 | 172.617 | 2255.97 | 25.89 | 46.721 | 6.36 | 1.332 | 4.471 | 8712.07 | 1.735 | 97.9 | 77 | 1466 | 23.41 | 5662.8 | 2830.3 | 2778.6 | 4088.4 | 1211.9 | 0.67503 | 5.805
2024-12-09 | 22:43 | Data | 0 | 32.946 | 30.934 | 183.056 | 7.64 | 172.527 | 2255.97 | 25.89 | 46.721 | 6.36 | 1.325 | 4.437 | 8707.55 | 1.965 | 97.9 | 77 | 1465 | 23.36 | 5659.9 | 2863.9 | 2783.2 | 4110.5 | 1211.9 | 0.67909 | 5.761
2024-12-09 | 22:44 | Data | 0 | 33.014 | 31.123 | 183.056 | 7.64 | 172.572 | 2258.68 | 25.9 | 46.721 | 6.36 | 1.325 | 4.442 | 8703.03 | 1.985 | 97.9 | 77 | 1468 | 23.36 | 5657 | 2842.1 | 2790 | 4095.6 | 1211.9 | 0.67633 | 5.765
2024-12-09 | 22:44 | Data | 0 | 32.838 | 31.103 | 183.056 | 7.64 | 172.527 | 2257.77 | 25.9 | 46.721 | 6.36 | 1.334 | 4.435 | 8721.11 | 1.836 | 97.9 | 76.9 | 1468 | 23.36 | 5668.7 | 2851.7 | 2776.5 | 4097 | 1211.9 | 0.67953 | 5.769
2024-12-09 | 22:44 | Data | 0 | 32.723 | 31.056 | 182.965 | 7.64 | 172.572 | 2258.68 | 25.89 | 46.721 | 6.36 | 1.337 | 4.448 | 8730.16 | 1.668 | 97.9 | 76.9 | 1468 | 23.41 | 5674.6 | 2851.1 | 2774.9 | 4100.9 | 1211.9 | 0.67686 | 5.785
2024-12-09 | 22:44 | Data | 0 | 32.967 | 31.11 | 183.282 | 7.64 | 172.662 | 2259.58 | 25.89 | 46.721 | 6.36 | 1.342 | 4.471 | 8730.16 | 1.735 | 97.9 | 76.9 | 1468 | 23.41 | 5674.6 | 2831.5 | 2803.4 | 4104.7 | 1211.9 | 0.67312 | 5.813
2024-12-09 | 22:44 | Data | 0 | 32.737 | 31.056 | 183.056 | 7.63 | 172.617 | 2256.87 | 25.89 | 46.721 | 6.36 | 1.337 | 4.486 | 8730.16 | 1.843 | 97.9 | 77 | 1467 | 23.36 | 5674.6 | 2831 | 2800.5 | 4092.9 | 1211.9 | 0.67367 | 5.823
2024-12-09 | 22:44 | Data | 0 | 32.723 | 31.076 | 183.011 | 7.63 | 172.527 | 2255.97 | 25.89 | 46.721 | 6.36 | 1.334 | 4.474 | 8757.29 | 1.857 | 97.9 | 77 | 1466 | 23.36 | 5692.2 | 2831.8 | 2780.9 | 4101.5 | 1211.9 | 0.67434 | 5.808
2024-12-09 | 22:44 | Data | 0 | 32.737 | 31.056 | 183.011 | 7.64 | 172.572 | 2254.16 | 25.89 | 46.721 | 6.37 | 1.332 | 4.432 | 8743.73 | 1.85 | 97.9 | 76.9 | 1465 | 23.36 | 5683.4 | 2852.6 | 2766.5 | 4096.5 | 1211.9 | 0.67904 | 5.764
2024-12-09 | 22:44 | Data | 0 | 32.865 | 31.204 | 183.101 | 7.63 | 172.572 | 2254.16 | 25.89 | 46.721 | 6.36 | 1.32 | 4.474 | 8739.2 | 1.998 | 97.9 | 77.2 | 1466 | 23.36 | 5680.5 | 2842.2 | 2768.5 | 4092 | 1211.9 | 0.67565 | 5.793
2024-12-09 | 22:44 | Data | 0 | 32.926 | 31.11 | 183.192 | 7.63 | 172.617 | 2255.97 | 25.89 | 46.721 | 6.36 | 1.325 | 4.454 | 8734.68 | 2.005 | 97.9 | 77.1 | 1466 | 23.36 | 5677.5 | 2841.1 | 2774.9 | 4109.8 | 1211.9 | 0.67635 | 5.779
2024-12-09 | 22:44 | Data | 0 | 32.967 | 30.887 | 183.056 | 7.63 | 172.617 | 2254.16 | 25.89 | 46.721 | 6.36 | 1.335 | 4.436 | 8730.16 | 1.85 | 97.9 | 76.9 | 1465 | 23.36 | 5674.6 | 2826.3 | 2762.8 | 4073.4 | 1211.9 | 0.67838 | 5.77
2024-12-09 | 22:44 | Data | 0 | 33.068 | 30.894 | 183.101 | 7.64 | 172.617 | 2247.83 | 25.89 | 46.721 | 6.36 | 1.341 | 4.44 | 8725.64 | 2.066 | 97.9 | 76.8 | 1461 | 23.36 | 5671.7 | 2849.5 | 2778.3 | 4098.7 | 1211.9 | 0.6791 | 5.781
2024-12-09 | 22:44 | Data | 0 | 32.723 | 31.076 | 182.785 | 7.63 | 172.527 | 2252.35 | 25.89 | 46.721 | 6.36 | 1.332 | 4.436 | 8725.64 | 1.647 | 97.9 | 76.9 | 1464 | 23.36 | 5671.7 | 2848.4 | 2789.4 | 4108.2 | 1211.9 | 0.67678 | 5.768
2024-12-09 | 22:44 | Data | 0 | 32.953 | 31.11 | 183.056 | 7.63 | 172.572 | 2255.97 | 25.89 | 46.721 | 6.36 | 1.336 | 4.437 | 8725.64 | 1.85 | 97.9 | 76.9 | 1466 | 23.36 | 5671.7 | 2845.6 | 2798.5 | 4115.3 | 1211.9 | 0.67515 | 5.771
2024-12-09 | 22:44 | Data | 0 | 32.744 | 30.779 | 183.192 | 7.64 | 172.662 | 2255.97 | 25.9 | 46.721 | 6.36 | 1.334 | 4.438 | 8938.18 | 1.944 | 97.9 | 76.9 | 1465 | 23.41 | 5809.8 | 2845.5 | 2805 | 4117.4 | 1211.9 | 0.67561 | 5.772
2024-12-09 | 22:44 | Data | 0 | 32.953 | 30.907 | 183.056 | 7.64 | 172.617 | 2254.16 | 25.89 | 46.721 | 6.36 | 1.34 | 4.452 | 8933.66 | 1.965 | 97.9 | 76.9 | 1465 | 23.36 | 5806.9 | 2835.1 | 2783.4 | 4095.3 | 1211.9 | 0.6739 | 5.792
2024-12-09 | 22:44 | Data | 0 | 32.967 | 31.312 | 183.101 | 7.64 | 172.662 | 2254.16 | 25.89 | 46.721 | 6.36 | 1.339 | 4.466 | 8938.18 | 1.843 | 97.9 | 76.9 | 1465 | 23.36 | 5809.8 | 2854.2 | 2802.5 | 4118.6 | 1211.9 | 0.67648 | 5.805
2024-12-09 | 22:44 | Data | 0 | 32.96 | 31.218 | 183.146 | 7.64 | 172.708 | 2255.97 | 25.89 | 46.721 | 6.36 | 1.334 | 4.436 | 8933.66 | 1.782 | 97.9 | 76.9 | 1466 | 23.36 | 5806.9 | 2838.7 | 2807.6 | 4111.9 | 1211.9 | 0.67386 | 5.771
2024-12-09 | 22:44 | Data | 0 | 33.176 | 31.123 | 183.237 | 7.63 | 172.662 | 2255.97 | 25.89 | 47.082 | 6.37 | 1.327 | 4.446 | 8721.11 | 1.904 | 97.9 | 77 | 1466 | 23.54 | 5668.7 | 2819.1 | 2809.4 | 4107.8 | 1211.9 | 0.66846 | 5.772
2024-12-09 | 22:45 | Data | 0 | 32.865 | 30.88 | 182.965 | 7.64 | 172.527 | 2254.16 | 25.89 | 47.082 | 6.36 | 1.329 | 4.472 | 8721.11 | 1.681 | 97.9 | 77.1 | 1465 | 23.59 | 5668.7 | 2857.5 | 2793.1 | 4114.2 | 1211.9 | 0.67752 | 5.8
2024-12-09 | 22:45 | Data | 0 | 32.737 | 31.083 | 182.558 | 7.63 | 172.075 | 2252.35 | 25.89 | 47.082 | 6.36 | 1.331 | 4.493 | 8721.11 | 1.755 | 97.9 | 77.1 | 1463 | 23.5 | 5668.7 | 2845.4 | 2785 | 4111.4 | 1211.9 | 0.67467 | 5.824
2024-12-09 | 22:45 | Data | 0 | 32.75 | 31.002 | 182.423 | 7.64 | 171.939 | 2249.64 | 25.89 | 46.721 | 6.36 | 1.331 | 4.457 | 8716.59 | 1.728 | 97.9 | 77 | 1463 | 23.36 | 5665.8 | 2838.4 | 2797.4 | 4106.3 | 1211.9 | 0.67409 | 5.789
2024-12-09 | 22:45 | Data | 0 | 32.98 | 30.894 | 182.468 | 7.64 | 172.075 | 2249.64 | 25.89 | 47.082 | 6.36 | 1.329 | 4.437 | 8739.2 | 1.843 | 97.9 | 77 | 1462 | 23.59 | 5680.5 | 2840 | 2801.6 | 4118.9 | 1211.9 | 0.67407 | 5.765
2024-12-09 | 22:45 | Data | 0 | 33.108 | 31.009 | 182.468 | 7.63 | 172.075 | 2250.54 | 25.89 | 47.172 | 6.36 | 1.341 | 4.407 | 8739.2 | 1.789 | 97.9 | 76.7 | 1463 | 23.54 | 5680.5 | 2836.5 | 2782.8 | 4096.5 | 1211.9 | 0.67543 | 5.748
2024-12-09 | 22:45 | Data | 0 | 32.629 | 31.083 | 182.377 | 7.64 | 171.984 | 2246.93 | 25.89 | 47.172 | 6.36 | 1.339 | 4.438 | 8743.73 | 1.681 | 97.9 | 76.8 | 1461 | 23.59 | 5683.4 | 2838.1 | 2773.2 | 4089.2 | 1211.9 | 0.67604 | 5.778
2024-12-09 | 22:45 | Data | 0 | 33.088 | 31.063 | 182.468 | 7.63 | 172.03 | 2246.93 | 25.89 | 47.082 | 6.36 | 1.322 | 4.444 | 8757.29 | 1.762 | 97.9 | 77.1 | 1461 | 23.54 | 5692.2 | 2834.1 | 2776.3 | 4087.3 | 1211.9 | 0.67861 | 5.766
2024-12-09 | 22:45 | Data | 0 | 33.156 | 31.009 | 182.377 | 7.64 | 171.939 | 2246.93 | 25.89 | 47.082 | 6.36 | 1.338 | 4.437 | 8784.42 | 2.019 | 97.9 | 76.8 | 1461 | 23.54 | 5709.9 | 2828.6 | 2785.6 | 4088.6 | 1212 | 0.67549 | 5.774
2024-12-09 | 22:45 | Data | 0 | 32.933 | 30.887 | 182.423 | 7.64 | 171.939 | 2246.93 | 25.89 | 47.172 | 6.36 | 1.335 | 4.444 | 8775.38 | 2.039 | 97.9 | 76.9 | 1461 | 23.59 | 5704 | 2837.3 | 2786.8 | 4095.1 | 1212 | 0.67537 | 5.779
2024-12-09 | 22:45 | Data | 0 | 32.845 | 30.894 | 182.332 | 7.64 | 171.984 | 2246.93 | 25.89 | 47.082 | 6.36 | 1.338 | 4.437 | 8775.38 | 1.836 | 97.9 | 76.8 | 1461 | 23.54 | 5704 | 2850.5 | 2782.1 | 4102.9 | 1212 | 0.6772 | 5.775
2024-12-09 | 22:45 | Data | 0 | 32.73 | 31.096 | 182.423 | 7.64 | 172.03 | 2246.93 | 25.89 | 47.172 | 6.37 | 1.334 | 4.442 | 8757.29 | 1.884 | 97.9 | 76.9 | 1460 | 23.54 | 5692.2 | 2841.3 | 2786.1 | 4098.9 | 1212 | 0.67569 | 5.776
2024-12-09 | 22:45 | Data | 0 | 33.007 | 30.914 | 182.468 | 7.63 | 171.939 | 2246.93 | 25.89 | 47.082 | 6.36 | 1.332 | 4.426 | 8761.81 | 1.843 | 97.9 | 76.9 | 1461 | 23.54 | 5695.2 | 2831.2 | 2787.2 | 4091.7 | 1212 | 0.67414 | 5.757
2024-12-09 | 22:45 | Data | 0 | 32.784 | 30.799 | 182.332 | 7.63 | 171.894 | 2250.54 | 25.89 | 47.082 | 6.35 | 1.33 | 4.446 | 8743.73 | 1.843 | 97.9 | 77 | 1463 | 23.54 | 5683.4 | 2851.2 | 2784.6 | 4106 | 1212 | 0.68048 | 5.777
2024-12-09 | 22:45 | Data | 0 | 32.629 | 30.995 | 182.377 | 7.64 | 171.894 | 2249.64 | 25.89 | 46.991 | 6.36 | 1.336 | 4.438 | 8730.16 | 1.688 | 97.9 | 76.9 | 1462 | 23.54 | 5674.6 | 2852.6 | 2780.3 | 4102.3 | 1212 | 0.67832 | 5.774
2024-12-09 | 22:45 | Data | 0 | 33.007 | 31.11 | 182.423 | 7.63 | 171.939 | 2249.64 | 25.89 | 47.082 | 6.36 | 1.332 | 4.427 | 8730.16 | 1.634 | 97.9 | 76.9 | 1462 | 23.59 | 5674.6 | 2834 | 2786.2 | 4094.2 | 1212 | 0.67431 | 5.76
2024-12-09 | 22:45 | Data | 0 | 33.007 | 31.11 | 182.377 | 7.63 | 171.984 | 2249.64 | 25.89 | 47.082 | 6.37 | 1.331 | 4.467 | 8743.73 | 1.857 | 97.9 | 77 | 1462 | 23.59 | 5683.4 | 2858 | 2827.5 | 4140.5 | 1212 | 0.67301 | 5.799
2024-12-09 | 22:45 | Data | 0 | 32.946 | 31.225 | 182.377 | 7.63 | 171.939 | 2249.64 | 25.89 | 47.082 | 6.36 | 1.335 | 4.455 | 8761.81 | 1.843 | 97.9 | 76.9 | 1462 | 23.54 | 5695.2 | 2821.9 | 2797.2 | 4099.4 | 1212 | 0.67014 | 5.79
2024-12-09 | 22:46 | Data | 0 | 33.169 | 31.11 | 182.558 | 7.63 | 172.075 | 2243.31 | 25.89 | 47.082 | 6.36 | 1.334 | 4.446 | 8757.29 | 2.052 | 97.9 | 76.9 | 1459 | 23.54 | 5692.2 | 2833.6 | 2797.1 | 4104.1 | 1212 | 0.67371 | 5.78
2024-12-09 | 22:46 | Data | 0 | 33.169 | 30.901 | 182.513 | 7.64 | 172.03 | 2249.64 | 25.9 | 47.082 | 6.36 | 1.339 | 4.44 | 8775.38 | 2.086 | 97.9 | 76.8 | 1462 | 23.54 | 5704 | 2853.5 | 2782.7 | 4103.2 | 1212 | 0.67762 | 5.779
2024-12-09 | 22:46 | Data | 0 | 32.899 | 31.103 | 182.423 | 7.64 | 171.939 | 2249.64 | 25.89 | 47.082 | 6.36 | 1.343 | 4.455 | 8761.81 | 1.843 | 97.9 | 76.8 | 1462 | 23.54 | 5695.2 | 2838.2 | 2804.1 | 4106.7 | 1212 | 0.67246 | 5.798
2024-12-09 | 22:46 | Data | 0 | 33.169 | 31.225 | 182.513 | 7.64 | 172.075 | 2248.73 | 25.89 | 47.082 | 6.36 | 1.339 | 4.46 | 8743.73 | 1.958 | 97.9 | 76.9 | 1462 | 23.54 | 5683.4 | 2846.4 | 2819.5 | 4127.2 | 1212 | 0.6717 | 5.799
2024-12-09 | 22:46 | Data | 0 | 32.953 | 31.198 | 182.423 | 7.63 | 171.984 | 2250.54 | 25.89 | 47.172 | 6.36 | 1.329 | 4.437 | 8743.73 | 1.877 | 97.9 | 77 | 1463 | 23.54 | 5683.4 | 2827.1 | 2819.5 | 4115.5 | 1212 | 0.6695 | 5.766
2024-12-09 | 22:46 | Data | 0 | 33.054 | 31.319 | 182.513 | 7.63 | 172.075 | 2251.45 | 25.9 | 47.082 | 6.36 | 1.324 | 4.439 | 8743.73 | 1.85 | 97.9 | 77 | 1463 | 23.54 | 5683.4 | 2845.9 | 2820.6 | 4130.7 | 1212 | 0.67155 | 5.764
2024-12-09 | 22:46 | Data | 0 | 32.953 | 31.096 | 182.332 | 7.63 | 171.939 | 2249.64 | 25.89 | 46.991 | 6.36 | 1.329 | 4.413 | 8707.55 | 1.87 | 97.9 | 76.8 | 1462 | 23.5 | 5659.9 | 2846.3 | 2798.8 | 4111.1 | 1212 | 0.67519 | 5.742
2024-12-09 | 22:46 | Data | 0 | 33.264 | 31.339 | 182.513 | 7.63 | 171.939 | 2250.54 | 25.89 | 47.082 | 6.36 | 1.336 | 4.44 | 8707.55 | 2.039 | 97.9 | 76.9 | 1463 | 23.59 | 5659.9 | 2838.1 | 2814.2 | 4116.8 | 1212 | 0.67227 | 5.775
2024-12-09 | 22:46 | Data | 0 | 32.737 | 30.995 | 182.332 | 7.64 | 171.939 | 2256.87 | 25.89 | 47.082 | 6.37 | 1.326 | 4.428 | 8707.55 | 1.843 | 97.9 | 77 | 1468 | 23.54 | 5659.9 | 2854.7 | 2796.7 | 4124.8 | 1212 | 0.67507 | 5.754
2024-12-09 | 22:46 | Data | 0 | 33.061 | 31.11 | 182.377 | 7.64 | 171.939 | 2258.68 | 25.9 | 47.172 | 6.37 | 1.341 | 4.421 | 8698.5 | 1.931 | 97.9 | 76.7 | 1468 | 23.54 | 5654 | 2840.6 | 2811.7 | 4116.1 | 1212 | 0.67351 | 5.763
2024-12-09 | 22:46 | Data | 0 | 33.061 | 31.069 | 182.423 | 7.63 | 171.984 | 2258.68 | 25.89 | 47.172 | 6.36 | 1.339 | 4.417 | 8712.07 | 2.019 | 97.9 | 76.7 | 1468 | 23.59 | 5662.8 | 2847.1 | 2821.2 | 4127.7 | 1212 | 0.67226 | 5.756
2024-12-09 | 22:46 | Data | 0 | 32.946 | 30.995 | 182.468 | 7.64 | 171.984 | 2257.77 | 25.89 | 47.082 | 6.36 | 1.331 | 4.436 | 8703.03 | 1.897 | 97.9 | 76.9 | 1468 | 23.54 | 5657 | 2835.3 | 2833 | 4126.8 | 1212 | 0.66978 | 5.766
2024-12-09 | 22:46 | Data | 0 | 32.946 | 31.11 | 182.332 | 7.64 | 171.894 | 2261.39 | 25.89 | 47.172 | 6.36 | 1.332 | 4.453 | 8703.03 | 1.843 | 97.9 | 77 | 1469 | 23.59 | 5657 | 2835.5 | 2811.5 | 4120.7 | 1212 | 0.67065 | 5.785
2024-12-09 | 22:46 | Data | 0 | 32.967 | 31.11 | 182.513 | 7.64 | 172.03 | 2260.48 | 25.89 | 47.082 | 6.37 | 1.33 | 4.451 | 8703.03 | 1.843 | 97.9 | 77 | 1469 | 23.54 | 5657 | 2838.9 | 2800.3 | 4113.3 | 1212 | 0.67084 | 5.779
2024-12-09 | 22:46 | Data | 0 | 32.777 | 31.056 | 182.377 | 7.63 | 171.894 | 2263.2 | 25.89 | 47.082 | 6.36 | 1.324 | 4.451 | 8703.03 | 1.728 | 97.9 | 77.1 | 1471 | 23.59 | 5657 | 2851.8 | 2814.2 | 4123 | 1212 | 0.67356 | 5.776
2024-12-09 | 22:46 | Data | 0 | 33.068 | 31.123 | 182.513 | 7.64 | 171.984 | 2263.2 | 25.89 | 47.172 | 6.36 | 1.328 | 4.444 | 8707.55 | 1.938 | 97.9 | 77 | 1471 | 23.59 | 5659.9 | 2831.5 | 2832.1 | 4122.8 | 1212 | 0.66825 | 5.771
2024-12-09 | 22:46 | Data | 0 | 33.257 | 31.535 | 182.604 | 7.63 | 172.03 | 2264.1 | 25.89 | 47.082 | 6.36 | 1.33 | 4.437 | 8703.03 | 2.046 | 97.9 | 76.9 | 1471 | 23.54 | 5657 | 2838 | 2805.5 | 4112.7 | 1212 | 0.67108 | 5.766
2024-12-09 | 22:46 | Data | 0 | 32.98 | 30.995 | 182.423 | 7.63 | 171.894 | 2265.91 | 25.89 | 47.082 | 6.36 | 1.329 | 4.421 | 8707.55 | 1.647 | 97.9 | 76.9 | 1473 | 23.59 | 5659.9 | 2816.2 | 2798 | 4092.5 | 1212 | 0.66996 | 5.75
2024-12-09 | 22:47 | Data | 0 | 32.744 | 31.11 | 182.468 | 7.64 | 172.03 | 2265.91 | 25.9 | 47.082 | 6.36 | 1.323 | 4.438 | 8689.46 | 1.62 | 97.9 | 77 | 1473 | 23.5 | 5648.1 | 2833.4 | 2822.9 | 4124.5 | 1212 | 0.67078 | 5.763
2024-12-09 | 22:47 | Data | 0 | 32.953 | 31.056 | 182.468 | 7.64 | 172.03 | 2265.91 | 25.89 | 47.082 | 6.36 | 1.329 | 4.419 | 8693.98 | 1.897 | 97.9 | 76.9 | 1473 | 23.54 | 5651.1 | 2844.6 | 2798.7 | 4120.1 | 1212 | 0.67623 | 5.749
2024-12-09 | 22:47 | Data | 0 | 32.899 | 31.123 | 182.377 | 7.63 | 171.939 | 2266.81 | 25.89 | 47.082 | 6.36 | 1.334 | 4.441 | 8693.98 | 1.951 | 97.9 | 76.9 | 1473 | 23.59 | 5651.1 | 2825.5 | 2816.2 | 4114 | 1212 | 0.66983 | 5.774
2024-12-09 | 22:47 | Data | 0 | 32.967 | 31.117 | 182.513 | 7.64 | 172.03 | 2266.81 | 25.89 | 47.082 | 6.36 | 1.334 | 4.408 | 8689.46 | 1.836 | 97.9 | 76.8 | 1473 | 23.54 | 5648.1 | 2822.7 | 2821.2 | 4112.9 | 1212 | 0.66941 | 5.742
2024-12-09 | 22:47 | Data | 0 | 32.953 | 31.272 | 182.558 | 7.64 | 172.12 | 2264.1 | 25.89 | 47.082 | 6.36 | 1.328 | 4.404 | 8707.55 | 1.776 | 97.9 | 76.8 | 1472 | 23.54 | 5659.9 | 2833.8 | 2802.4 | 4109.6 | 1212 | 0.67075 | 5.733
2024-12-09 | 22:47 | Data | 0 | 33.419 | 31.13 | 182.604 | 7.64 | 172.21 | 2265 | 25.89 | 47.082 | 6.36 | 1.33 | 4.414 | 8707.55 | 1.897 | 97.9 | 76.8 | 1472 | 23.54 | 5659.9 | 2856.2 | 2833.3 | 4142.1 | 1212 | 0.67232 | 5.745
2024-12-09 | 22:47 | Data | 0 | 32.73 | 31.096 | 182.332 | 7.63 | 172.03 | 2265 | 25.89 | 47.172 | 6.36 | 1.337 | 4.415 | 8716.59 | 1.843 | 97.9 | 76.8 | 1473 | 23.59 | 5665.8 | 2845.1 | 2797.7 | 4107.8 | 1212 | 0.67431 | 5.752
2024-12-09 | 22:47 | Data | 0 | 32.953 | 31.218 | 182.423 | 7.64 | 171.984 | 2266.81 | 25.89 | 47.082 | 6.36 | 1.327 | 4.44 | 8698.5 | 1.742 | 97.9 | 77 | 1473 | 23.54 | 5654 | 2839.6 | 2807.5 | 4115.1 | 1212 | 0.67317 | 5.769
2024-12-09 | 22:47 | Data | 0 | 32.899 | 31.11 | 182.423 | 7.63 | 171.939 | 2265.91 | 25.89 | 47.082 | 6.36 | 1.338 | 4.406 | 8707.55 | 1.823 | 97.9 | 76.7 | 1473 | 23.59 | 5659.9 | 2835.5 | 2801.8 | 4105.6 | 1212 | 0.67382 | 5.744
2024-12-09 | 22:47 | Data | 0 | 33.068 | 31.245 | 182.513 | 7.63 | 172.03 | 2265 | 25.89 | 46.721 | 6.37 | 1.34 | 4.423 | 8707.55 | 1.755 | 97.9 | 76.7 | 1472 | 23.36 | 5659.9 | 2844.5 | 2783.7 | 4103.5 | 1212.1 | 0.67651 | 5.762
2024-12-09 | 22:47 | Data | 0 | 33.007 | 31.11 | 182.423 | 7.63 | 171.984 | 2260.48 | 25.89 | 47.172 | 6.36 | 1.33 | 4.446 | 8712.07 | 1.647 | 97.9 | 77 | 1469 | 23.59 | 5662.8 | 2836.5 | 2808.9 | 4110.6 | 1212.1 | 0.67344 | 5.776
2024-12-09 | 22:47 | Data | 0 | 33.115 | 30.907 | 182.423 | 7.63 | 172.03 | 2260.48 | 25.89 | 47.082 | 6.36 | 1.328 | 4.456 | 8725.64 | 2.147 | 97.9 | 77 | 1469 | 23.59 | 5671.7 | 2821.4 | 2810.4 | 4101.2 | 1212.1 | 0.6729 | 5.785
2024-12-09 | 22:47 | Data | 0 | 32.953 | 31.225 | 182.604 | 7.64 | 171.984 | 2260.48 | 25.89 | 47.082 | 6.37 | 1.329 | 4.466 | 8716.59 | 1.843 | 97.9 | 77.1 | 1469 | 23.59 | 5665.8 | 2842.4 | 2795 | 4104.2 | 1212.1 | 0.67507 | 5.796
2024-12-09 | 22:47 | Data | 0 | 32.967 | 31.13 | 182.423 | 7.64 | 171.894 | 2260.48 | 25.9 | 47.172 | 6.36 | 1.326 | 4.443 | 8734.68 | 1.755 | 97.9 | 77 | 1469 | 23.54 | 5677.5 | 2842.4 | 2790.1 | 4107 | 1212.1 | 0.67714 | 5.769
2024-12-09 | 22:47 | Data | 0 | 32.96 | 31.204 | 182.513 | 7.64 | 172.03 | 2260.48 | 25.89 | 47.172 | 6.36 | 1.323 | 4.439 | 8743.73 | 1.89 | 97.9 | 77 | 1469 | 23.59 | 5683.4 | 2833.9 | 2802.7 | 4107.9 | 1212.1 | 0.67305 | 5.761
2024-12-09 | 22:47 | Data | 0 | 32.953 | 31.117 | 182.513 | 7.64 | 171.984 | 2261.39 | 25.89 | 46.991 | 6.36 | 1.328 | 4.454 | 8757.29 | 1.83 | 97.9 | 77 | 1470 | 23.54 | 5692.2 | 2814.3 | 2811.2 | 4095.4 | 1212.1 | 0.67225 | 5.782
2024-12-09 | 22:47 | Data | 0 | 33 | 31.009 | 182.423 | 7.63 | 171.984 | 2258.68 | 25.89 | 47.082 | 6.36 | 1.328 | 4.4 | 8757.29 | 2.046 | 97.9 | 76.8 | 1468 | 23.54 | 5692.2 | 2817.1 | 2792.7 | 4090.2 | 1212.1 | 0.67055 | 5.727
2024-12-09 | 22:47 | Data | 0 | 33.257 | 31.339 | 182.332 | 7.64 | 172.03 | 2258.68 | 25.89 | 47.082 | 6.36 | 1.328 | 4.428 | 8779.9 | 2.059 | 97.9 | 76.9 | 1468 | 23.54 | 5706.9 | 2834.6 | 2807.4 | 4111.4 | 1212.1 | 0.67164 | 5.757
2024-12-09 | 22:48 | Data | 0 | 32.98 | 31.11 | 182.468 | 7.64 | 172.075 | 2258.68 | 25.89 | 47.172 | 6.36 | 1.33 | 4.407 | 8802.51 | 1.843 | 97.9 | 76.8 | 1468 | 23.54 | 5721.6 | 2860.4 | 2831.5 | 4147.2 | 1212.1 | 0.67224 | 5.737
2024-12-09 | 22:48 | Data | 0 | 33.068 | 31.333 | 182.423 | 7.64 | 172.03 | 2257.77 | 25.89 | 47.082 | 6.36 | 1.335 | 4.408 | 8784.42 | 1.843 | 97.9 | 76.8 | 1468 | 23.54 | 5709.9 | 2827.5 | 2814.5 | 4111.6 | 1212.1 | 0.67046 | 5.742
2024-12-09 | 22:48 | Data | 0 | 32.967 | 31.11 | 182.558 | 7.64 | 172.03 | 2258.68 | 25.89 | 47.082 | 6.36 | 1.322 | 4.451 | 8775.38 | 1.728 | 97.9 | 77.1 | 1468 | 23.54 | 5704 | 2843.6 | 2803.5 | 4112.2 | 1212.1 | 0.67401 | 5.773
2024-12-09 | 22:48 | Data | 0 | 32.953 | 31.225 | 182.513 | 7.63 | 171.984 | 2257.77 | 25.89 | 47.082 | 6.36 | 1.322 | 4.462 | 8797.99 | 1.958 | 97.9 | 77.1 | 1468 | 23.54 | 5718.7 | 2839.1 | 2804.7 | 4114 | 1212.1 | 0.67084 | 5.784
2024-12-09 | 22:48 | Data | 0 | 32.98 | 31.11 | 182.649 | 7.64 | 172.21 | 2258.68 | 25.89 | 46.811 | 6.36 | 1.334 | 4.465 | 8757.29 | 1.735 | 97.9 | 77 | 1468 | 23.36 | 5692.2 | 2823.7 | 2829.2 | 4117.2 | 1212.1 | 0.66887 | 5.799
2024-12-09 | 22:48 | Data | 0 | 33.169 | 31.123 | 182.423 | 7.63 | 172.03 | 2257.77 | 25.89 | 47.172 | 6.36 | 1.332 | 4.476 | 8761.81 | 1.857 | 97.9 | 77.1 | 1468 | 23.59 | 5695.2 | 2837.7 | 2800.3 | 4110.1 | 1212.1 | 0.67423 | 5.808
2024-12-09 | 22:48 | Data | 0 | 32.953 | 30.995 | 182.377 | 7.64 | 171.984 | 2257.77 | 25.89 | 47.172 | 6.36 | 1.328 | 4.446 | 9155.25 | 2.073 | 97.9 | 77 | 1468 | 23.54 | 5950.9 | 2825.7 | 2826 | 4117.7 | 1212.1 | 0.66939 | 5.773
2024-12-09 | 22:48 | Data | 0 | 33.129 | 31.339 | 182.468 | 7.63 | 171.984 | 2258.68 | 25.9 | 47.082 | 6.36 | 1.338 | 4.423 | 8721.11 | 2.012 | 97.9 | 76.8 | 1468 | 23.54 | 5668.7 | 2838.6 | 2790.2 | 4102 | 1212.1 | 0.67475 | 5.761
2024-12-09 | 22:48 | Data | 0 | 32.953 | 30.887 | 182.423 | 7.63 | 171.939 | 2258.68 | 25.89 | 47.082 | 6.36 | 1.34 | 4.437 | 8725.64 | 2.039 | 97.9 | 76.8 | 1468 | 23.54 | 5671.7 | 2816.5 | 2786.7 | 4084.1 | 1212.1 | 0.67244 | 5.778
2024-12-09 | 22:48 | Data | 0 | 32.852 | 31.11 | 182.423 | 7.64 | 172.075 | 2257.77 | 25.89 | 47.082 | 6.36 | 1.329 | 4.446 | 8743.73 | 1.951 | 97.9 | 77 | 1468 | 23.54 | 5683.4 | 2834.8 | 2785.6 | 4095.9 | 1212.1 | 0.67499 | 5.775
2024-12-09 | 22:48 | Data | 0 | 33.061 | 31.123 | 182.423 | 7.64 | 171.984 | 2258.68 | 25.89 | 47.082 | 6.37 | 1.325 | 4.434 | 8734.68 | 1.857 | 97.9 | 77 | 1468 | 23.54 | 5677.5 | 2857.7 | 2776.2 | 4106.4 | 1212.1 | 0.67761 | 5.759
2024-12-09 | 22:48 | Data | 0 | 32.568 | 30.995 | 182.423 | 7.64 | 172.03 | 2258.68 | 25.9 | 47.082 | 6.36 | 1.336 | 4.418 | 8743.73 | 1.836 | 97.9 | 76.8 | 1468 | 23.54 | 5683.4 | 2837 | 2740.2 | 4064.1 | 1212.1 | 0.67986 | 5.754
2024-12-09 | 22:48 | Data | 0 | 33.392 | 31.292 | 182.468 | 7.64 | 172.075 | 2258.68 | 25.89 | 47.172 | 6.36 | 1.348 | 4.419 | 8734.68 | 2.019 | 97.9 | 76.6 | 1468 | 23.59 | 5677.5 | 2826.3 | 2792.2 | 4089.7 | 1212.1 | 0.67665 | 5.768
2024-12-09 | 22:48 | Data | 0 | 33.169 | 31.218 | 182.423 | 7.63 | 172.03 | 2264.1 | 25.89 | 47.082 | 6.36 | 1.339 | 4.412 | 8734.68 | 1.85 | 97.9 | 76.7 | 1471 | 23.59 | 5677.5 | 2842 | 2788.2 | 4101.5 | 1212.1 | 0.67419 | 5.751
2024-12-09 | 22:48 | Data | 0 | 33.264 | 31.366 | 182.604 | 7.63 | 172.075 | 2261.39 | 25.89 | 47.082 | 6.36 | 1.332 | 4.414 | 8730.16 | 1.89 | 97.9 | 76.8 | 1469 | 23.54 | 5674.6 | 2828.3 | 2804.3 | 4101.8 | 1212.1 | 0.67172 | 5.746
2024-12-09 | 22:48 | Data | 0 | 33.277 | 31.508 | 182.558 | 7.63 | 172.03 | 2260.48 | 25.89 | 47.082 | 6.36 | 1.329 | 4.422 | 8734.68 | 2.059 | 97.9 | 76.9 | 1470 | 23.54 | 5677.5 | 2842.3 | 2793.4 | 4102.1 | 1212.1 | 0.67573 | 5.752
2024-12-09 | 22:48 | Data | 0 | 32.98 | 31.117 | 182.468 | 7.64 | 172.075 | 2258.68 | 25.89 | 47.082 | 6.36 | 1.325 | 4.437 | 8761.81 | 1.843 | 97.9 | 77 | 1468 | 23.54 | 5695.2 | 2840.1 | 2778.5 | 4090 | 1212.1 | 0.67636 | 5.762
2024-12-09 | 22:48 | Data | 0 | 33 | 31.11 | 182.423 | 7.64 | 172.03 | 2257.77 | 25.89 | 47.172 | 6.37 | 1.324 | 4.456 | 8730.16 | 1.857 | 97.9 | 77.1 | 1468 | 23.54 | 5674.6 | 2831.7 | 2762.7 | 4080 | 1212.1 | 0.67538 | 5.78
2024-12-09 | 22:49 | Data | 0 | 32.534 | 31.083 | 182.468 | 7.64 | 171.984 | 2255.97 | 25.89 | 47.172 | 6.36 | 1.328 | 4.452 | 8739.2 | 1.701 | 97.9 | 77 | 1465 | 23.54 | 5680.5 | 2828.6 | 2782.1 | 4086.4 | 1212.1 | 0.67678 | 5.776
2024-12-09 | 22:49 | Data | 0 | 32.953 | 31.09 | 182.423 | 7.64 | 171.984 | 2258.68 | 25.89 | 47.082 | 6.37 | 1.326 | 4.449 | 8730.16 | 1.863 | 97.9 | 77.1 | 1468 | 23.54 | 5674.6 | 2854.9 | 2681.1 | 4036.8 | 1212.1 | 0.69065 | 5.774
2024-12-09 | 22:49 | Data | 0 | 32.953 | 31.279 | 182.377 | 7.63 | 171.984 | 2142.08 | 25.9 | 47.082 | 6.36 | 1.336 | 4.443 | 8734.68 | 1.735 | 97.8 | 76.9 | 1392 | 23.54 | 5677.5 | 2841.1 | 2755.4 | 4074.9 | 1212.1 | 0.68017 | 5.779
2024-12-09 | 22:49 | Data | 0 | 32.953 | 31.231 | 182.468 | 7.64 | 172.03 | 2254.16 | 25.9 | 47.082 | 6.36 | 1.325 | 4.422 | 8725.64 | 2.019 | 97.9 | 77 | 1465 | 23.54 | 5671.7 | 2826.4 | 2767.8 | 4078.6 | 1212.1 | 0.6753 | 5.746
2024-12-09 | 22:49 | Data | 0 | 33.054 | 31.549 | 182.468 | 7.64 | 172.03 | 2257.77 | 25.89 | 47.082 | 6.36 | 1.339 | 4.409 | 8725.64 | 1.803 | 97.9 | 76.7 | 1468 | 23.54 | 5671.7 | 2834.4 | 2758.1 | 4073.5 | 1212.1 | 0.6786 | 5.747
2024-12-09 | 22:49 | Data | 0 | 33.378 | 31.225 | 182.604 | 7.64 | 172.12 | 2256.87 | 25.89 | 47.172 | 6.36 | 1.343 | 4.421 | 8743.73 | 2.012 | 97.9 | 76.7 | 1467 | 23.59 | 5683.4 | 2836.5 | 2770 | 4086.1 | 1212.1 | 0.67767 | 5.763
2024-12-09 | 22:49 | Data | 0 | 33.372 | 31.123 | 182.468 | 7.63 | 172.075 | 2256.87 | 25.89 | 47.082 | 6.36 | 1.332 | 4.445 | 8730.16 | 1.951 | 97.9 | 76.9 | 1466 | 23.54 | 5674.6 | 2823 | 2770.3 | 4075.2 | 1212.1 | 0.67568 | 5.777
2024-12-09 | 22:49 | Data | 0 | 32.804 | 30.914 | 182.468 | 7.64 | 172.075 | 2251.45 | 25.89 | 47.172 | 6.36 | 1.331 | 4.422 | 8734.68 | 1.816 | 97.9 | 76.9 | 1463 | 23.59 | 5677.5 | 2843 | 2754.6 | 4078.5 | 1212.1 | 0.67897 | 5.753
2024-12-09 | 22:49 | Data | 0 | 33.156 | 31.137 | 182.604 | 7.64 | 172.075 | 2255.97 | 25.89 | 47.082 | 6.36 | 1.335 | 4.443 | 8725.64 | 1.951 | 97.9 | 76.9 | 1465 | 23.5 | 5671.7 | 2829.1 | 2749.4 | 4066.4 | 1212.1 | 0.67846 | 5.777
2024-12-09 | 22:49 | Data | 0 | 33.176 | 31.339 | 182.513 | 7.63 | 171.984 | 2257.77 | 25.89 | 47.082 | 6.37 | 1.328 | 4.448 | 8725.64 | 1.85 | 97.9 | 77 | 1468 | 23.54 | 5671.7 | 2830.6 | 2763.8 | 4076.4 | 1212.1 | 0.67707 | 5.776
2024-12-09 | 22:49 | Data | 0 | 32.953 | 31.15 | 182.468 | 7.64 | 172.03 | 2261.39 | 25.89 | 46.991 | 6.36 | 1.328 | 4.443 | 8721.11 | 1.755 | 97.9 | 77 | 1469 | 23.59 | 5668.7 | 2820.1 | 2761.6 | 4065.5 | 1212.1 | 0.67685 | 5.771
2024-12-09 | 22:49 | Data | 0 | 32.953 | 31.225 | 182.423 | 7.63 | 171.984 | 2255.97 | 25.89 | 47.082 | 6.37 | 1.337 | 4.441 | 8698.5 | 1.843 | 97.9 | 76.9 | 1465 | 23.59 | 5654 | 2824.4 | 2762.5 | 4070.1 | 1212.2 | 0.67589 | 5.778
2024-12-09 | 22:49 | Data | 0 | 33.129 | 31.326 | 182.604 | 7.64 | 172.075 | 2255.97 | 25.89 | 47.262 | 6.36 | 1.336 | 4.448 | 8684.94 | 1.857 | 97.9 | 76.9 | 1466 | 23.59 | 5645.2 | 2845.7 | 2787.4 | 4102.7 | 1212.2 | 0.67791 | 5.783
2024-12-09 | 22:49 | Data | 0 | 33.054 | 31.11 | 182.423 | 7.63 | 172.03 | 2251.45 | 25.89 | 47.172 | 6.36 | 1.322 | 4.456 | 8671.37 | 1.857 | 97.9 | 77.1 | 1464 | 23.54 | 5636.4 | 2841.3 | 2785.9 | 4095.6 | 1212.2 | 0.67753 | 5.779
2024-12-09 | 22:49 | Data | 0 | 32.953 | 31.319 | 182.468 | 7.63 | 172.075 | 2254.16 | 25.89 | 47.082 | 6.37 | 1.338 | 4.463 | 8693.98 | 1.83 | 97.9 | 76.9 | 1465 | 23.54 | 5651.1 | 2832.9 | 2751.2 | 4068.2 | 1212.2 | 0.67861 | 5.8
2024-12-09 | 22:49 | Data | 0 | 32.764 | 31.11 | 182.558 | 7.63 | 172.03 | 2249.64 | 25.89 | 46.991 | 6.37 | 1.348 | 4.439 | 8716.59 | 1.62 | 97.9 | 76.7 | 1462 | 23.54 | 5665.8 | 2855.3 | 2782.9 | 4103.6 | 1212.2 | 0.67775 | 5.787
2024-12-09 | 22:49 | Data | 0 | 33.284 | 31.339 | 182.604 | 7.63 | 172.256 | 2244.22 | 25.89 | 47.082 | 6.37 | 1.336 | 4.424 | 8721.11 | 1.89 | 97.9 | 76.8 | 1459 | 23.59 | 5668.7 | 2841.8 | 2773.2 | 4087.8 | 1212.2 | 0.67811 | 5.76
2024-12-09 | 22:50 | Data | 0 | 32.825 | 31.198 | 182.468 | 7.64 | 172.075 | 2244.22 | 25.9 | 47.082 | 6.36 | 1.324 | 4.427 | 8730.16 | 1.681 | 97.9 | 77 | 1459 | 23.54 | 5674.6 | 2839.1 | 2788.5 | 4099.6 | 1212.2 | 0.67514 | 5.751
2024-12-09 | 22:50 | Data | 0 | 32.953 | 31.225 | 182.468 | 7.63 | 171.984 | 2249.64 | 25.89 | 47.082 | 6.36 | 1.334 | 4.43 | 8743.73 | 1.843 | 97.9 | 76.9 | 1462 | 23.54 | 5683.4 | 2849.1 | 2766.4 | 4100.8 | 1212.2 | 0.67917 | 5.763
2024-12-09 | 22:50 | Data | 0 | 32.96 | 31.643 | 182.649 | 7.64 | 172.12 | 2249.64 | 25.89 | 47.172 | 6.37 | 1.33 | 4.431 | 8716.59 | 1.789 | 97.9 | 76.9 | 1462 | 23.59 | 5665.8 | 2856.4 | 2745.3 | 4083.7 | 1212.2 | 0.68157 | 5.761
2024-12-09 | 22:50 | Data | 0 | 32.953 | 31.11 | 182.423 | 7.64 | 171.984 | 2249.64 | 25.89 | 46.991 | 6.36 | 1.336 | 4.435 | 8725.64 | 1.843 | 97.9 | 76.9 | 1463 | 23.5 | 5671.7 | 2847.4 | 2754.9 | 4078.7 | 1212.2 | 0.67992 | 5.771
2024-12-09 | 22:50 | Data | 0 | 33.169 | 31.117 | 182.332 | 7.63 | 171.984 | 2252.35 | 25.89 | 47.172 | 6.36 | 1.337 | 4.452 | 8707.55 | 1.944 | 97.9 | 76.9 | 1464 | 23.59 | 5659.9 | 2846.5 | 2772.8 | 4094.1 | 1212.2 | 0.6793 | 5.789
2024-12-09 | 22:50 | Data | 0 | 32.953 | 31.096 | 182.377 | 7.64 | 172.03 | 2257.77 | 25.89 | 47.082 | 6.37 | 1.332 | 4.461 | 8716.59 | 1.897 | 97.9 | 77 | 1468 | 23.54 | 5665.8 | 2838.5 | 2767 | 4086.5 | 1212.2 | 0.67755 | 5.793
2024-12-09 | 22:50 | Data | 0 | 32.953 | 31.501 | 182.513 | 7.64 | 172.075 | 2252.35 | 25.89 | 47.172 | 6.36 | 1.34 | 4.459 | 8725.64 | 1.688 | 97.9 | 76.9 | 1464 | 23.54 | 5671.7 | 2843.7 | 2735.7 | 4071.2 | 1212.2 | 0.68011 | 5.8
2024-12-09 | 22:50 | Data | 0 | 32.798 | 30.995 | 182.558 | 7.63 | 172.21 | 2252.35 | 25.89 | 47.172 | 6.37 | 1.34 | 4.44 | 8730.16 | 1.87 | 97.9 | 76.8 | 1464 | 23.54 | 5674.6 | 2842.8 | 2762.1 | 4089.1 | 1212.2 | 0.67855 | 5.78
2024-12-09 | 22:50 | Data | 0 | 33 | 31.225 | 182.513 | 7.64 | 172.075 | 2252.35 | 25.89 | 47.082 | 6.36 | 1.328 | 4.443 | 8734.68 | 1.735 | 97.9 | 77 | 1464 | 23.54 | 5677.5 | 2849.1 | 2753.7 | 4085.7 | 1212.2 | 0.67866 | 5.771
2024-12-09 | 22:50 | Data | 0 | 33.23 | 31.353 | 182.694 | 7.63 | 172.12 | 2251.45 | 25.89 | 47.172 | 6.37 | 1.328 | 4.427 | 8721.11 | 2.12 | 97.9 | 76.9 | 1464 | 23.59 | 5668.7 | 2855.1 | 2734.4 | 4079.2 | 1212.2 | 0.68051 | 5.756
2024-12-09 | 22:50 | Data | 0 | 33.068 | 31.211 | 182.604 | 7.64 | 172.075 | 2252.35 | 25.89 | 47.082 | 6.36 | 1.334 | 4.42 | 8730.16 | 2.086 | 97.9 | 76.8 | 1464 | 23.54 | 5674.6 | 2868.9 | 2780.1 | 4123.7 | 1212.2 | 0.67831 | 5.754
2024-12-09 | 22:50 | Data | 0 | 32.73 | 31.11 | 182.558 | 7.64 | 172.21 | 2252.35 | 25.89 | 47.082 | 6.37 | 1.339 | 4.435 | 8748.25 | 1.816 | 97.9 | 76.8 | 1464 | 23.54 | 5686.4 | 2839.5 | 2785.1 | 4098.8 | 1212.2 | 0.67712 | 5.774
2024-12-09 | 22:50 | Data | 0 | 32.967 | 31.333 | 182.604 | 7.63 | 172.12 | 2252.35 | 25.9 | 47.082 | 6.37 | 1.339 | 4.451 | 8739.2 | 1.796 | 97.9 | 76.9 | 1464 | 23.54 | 5680.5 | 2855.5 | 2736.4 | 4080.5 | 1212.2 | 0.67934 | 5.789
2024-12-09 | 22:50 | Data | 0 | 32.953 | 31.11 | 182.423 | 7.63 | 171.984 | 2251.45 | 25.89 | 47.082 | 6.36 | 1.329 | 4.427 | 8730.16 | 1.843 | 97.9 | 76.9 | 1463 | 23.54 | 5674.6 | 2867.2 | 2739.6 | 4087.9 | 1212.2 | 0.68119 | 5.756
2024-12-09 | 22:50 | Data | 0 | 33.169 | 31.326 | 182.332 | 7.64 | 172.03 | 2254.16 | 25.89 | 47.082 | 6.36 | 1.337 | 4.418 | 8752.77 | 1.857 | 97.9 | 76.8 | 1465 | 23.54 | 5689.3 | 2873.7 | 2780.1 | 4120.6 | 1212.2 | 0.67955 | 5.755
2024-12-09 | 22:50 | Data | 0 | 33.041 | 31.117 | 182.377 | 7.64 | 172.12 | 2258.68 | 25.9 | 47.082 | 6.36 | 1.345 | 4.456 | 8757.29 | 2.032 | 97.9 | 76.8 | 1468 | 23.54 | 5692.2 | 2865.4 | 2774.2 | 4109.3 | 1212.2 | 0.67962 | 5.8
2024-12-09 | 22:50 | Data | 0 | 32.953 | 31.096 | 182.558 | 7.64 | 172.03 | 2258.68 | 25.89 | 47.082 | 6.36 | 1.338 | 4.472 | 8757.29 | 1.87 | 97.9 | 77 | 1469 | 23.54 | 5692.2 | 2857.4 | 2783 | 4110.1 | 1212.2 | 0.67652 | 5.808
2024-12-09 | 22:50 | Data | 0 | 33.048 | 31.495 | 182.513 | 7.64 | 171.984 | 2257.77 | 25.89 | 47.082 | 6.36 | 1.329 | 4.48 | 8757.29 | 1.843 | 97.9 | 77.1 | 1468 | 23.54 | 5692.2 | 2868.8 | 2801.4 | 4129.3 | 1212.2 | 0.67791 | 5.808
2024-12-09 | 22:51 | Data | 0 | 32.98 | 31.11 | 182.513 | 7.63 | 172.075 | 2255.97 | 25.89 | 47.082 | 6.36 | 1.334 | 4.451 | 8770.86 | 1.843 | 97.9 | 76.9 | 1466 | 23.59 | 5701.1 | 2867.4 | 2783.3 | 4116.9 | 1212.2 | 0.67974 | 5.785
2024-12-09 | 22:51 | Data | 0 | 32.967 | 31.225 | 182.513 | 7.64 | 172.12 | 2260.48 | 25.89 | 47.082 | 6.36 | 1.332 | 4.465 | 8752.77 | 1.836 | 97.9 | 77 | 1469 | 23.54 | 5689.3 | 2864.5 | 2788.9 | 4119.8 | 1212.2 | 0.6773 | 5.798
2024-12-09 | 22:51 | Data | 0 | 33.291 | 31.144 | 182.558 | 7.63 | 172.12 | 2260.48 | 25.9 | 46.991 | 6.36 | 1.34 | 4.439 | 8739.2 | 1.857 | 97.9 | 76.8 | 1470 | 23.54 | 5680.5 | 2866.6 | 2774.6 | 4114.5 | 1212.2 | 0.67905 | 5.78
2024-12-09 | 22:51 | Data | 0 | 33.297 | 31.252 | 182.558 | 7.63 | 172.12 | 2260.48 | 25.89 | 47.172 | 6.36 | 1.344 | 4.431 | 8730.16 | 1.971 | 97.9 | 76.7 | 1469 | 23.59 | 5674.6 | 2856.3 | 2804.8 | 4126.3 | 1212.2 | 0.67416 | 5.775
2024-12-09 | 22:51 | Data | 0 | 32.953 | 31.022 | 182.468 | 7.63 | 171.939 | 2261.39 | 25.89 | 47.082 | 6.36 | 1.338 | 4.458 | 8730.16 | 2.019 | 97.9 | 76.9 | 1469 | 23.59 | 5674.6 | 2854.7 | 2790.9 | 4112.1 | 1212.2 | 0.6771 | 5.795
2024-12-09 | 22:51 | Data | 0 | 32.953 | 31.103 | 182.468 | 7.63 | 172.03 | 2260.48 | 25.89 | 47.172 | 6.36 | 1.336 | 4.427 | 8734.68 | 1.85 | 97.9 | 76.8 | 1469 | 23.59 | 5677.5 | 2856.9 | 2789.8 | 4114.4 | 1212.2 | 0.67637 | 5.762
2024-12-09 | 22:51 | Data | 0 | 32.737 | 30.907 | 182.513 | 7.63 | 172.03 | 2261.39 | 25.89 | 47.082 | 6.37 | 1.324 | 4.414 | 8721.11 | 1.85 | 97.9 | 76.9 | 1469 | 23.54 | 5668.7 | 2850.3 | 2811.8 | 4126.7 | 1212.2 | 0.67255 | 5.738
2024-12-09 | 22:51 | Data | 0 | 33.183 | 31.339 | 182.558 | 7.64 | 172.12 | 2255.97 | 25.9 | 47.082 | 6.36 | 1.334 | 4.446 | 9304.48 | 1.843 | 97.9 | 76.9 | 1465 | 23.59 | 6047.9 | 2865.7 | 2822.3 | 4141.9 | 1212.2 | 0.67423 | 5.78
2024-12-09 | 22:51 | Data | 0 | 32.953 | 31.11 | 182.423 | 7.63 | 172.03 | 2255.97 | 25.89 | 47.082 | 6.36 | 1.344 | 4.451 | 8847.74 | 1.843 | 97.9 | 76.8 | 1466 | 23.59 | 5751 | 2867.9 | 2801 | 4119.4 | 1212.2 | 0.67534 | 5.796
2024-12-09 | 22:51 | Data | 0 | 33.338 | 31.177 | 182.558 | 7.64 | 172.075 | 2258.68 | 25.89 | 47.533 | 6.36 | 1.338 | 4.418 | 8703.03 | 1.992 | 97.9 | 76.8 | 1468 | 23.77 | 5657 | 2870.8 | 2801.3 | 4132.3 | 1212.2 | 0.67696 | 5.754
2024-12-09 | 22:51 | Data | 0 | 32.953 | 31.11 | 182.423 | 7.63 | 171.984 | 2253.25 | 25.89 | 47.082 | 6.37 | 1.332 | 4.435 | 8703.03 | 1.843 | 97.9 | 76.9 | 1465 | 23.54 | 5657 | 2805.6 | 2782.7 | 4069 | 1212.2 | 0.67299 | 5.769
2024-12-09 | 22:51 | Data | 0 | 32.73 | 31.164 | 182.513 | 7.64 | 172.03 | 2258.68 | 25.89 | 47.082 | 6.36 | 1.338 | 4.446 | 8703.03 | 1.762 | 97.9 | 76.9 | 1468 | 23.54 | 5657 | 2791.7 | 2787.8 | 4061.1 | 1212.2 | 0.67053 | 5.782
2024-12-09 | 22:51 | Data | 0 | 33.122 | 31.346 | 182.513 | 7.64 | 172.03 | 2256.87 | 25.89 | 47.082 | 6.37 | 1.328 | 4.405 | 8712.07 | 1.998 | 97.9 | 76.8 | 1465 | 23.54 | 5662.8 | 2793 | 2788.9 | 4062.9 | 1212.2 | 0.66903 | 5.733
2024-12-09 | 22:51 | Data | 0 | 33.156 | 31.333 | 182.513 | 7.63 | 172.03 | 2254.16 | 25.89 | 47.172 | 6.36 | 1.329 | 4.399 | 8721.11 | 1.857 | 97.9 | 76.8 | 1465 | 23.54 | 5668.7 | 2801.9 | 2786.5 | 4070.1 | 1212.3 | 0.67104 | 5.729
2024-12-09 | 22:51 | Data | 0 | 32.791 | 31.11 | 182.513 | 7.64 | 172.075 | 2254.16 | 25.89 | 46.991 | 6.36 | 1.33 | 4.426 | 8716.59 | 1.762 | 97.9 | 76.9 | 1465 | 23.5 | 5665.8 | 2791.4 | 2789.3 | 4072 | 1212.3 | 0.6681 | 5.756
2024-12-09 | 22:51 | Data | 0 | 33.156 | 31.427 | 182.468 | 7.64 | 172.03 | 2255.97 | 25.89 | 47.082 | 6.37 | 1.324 | 4.449 | 8730.16 | 1.951 | 97.9 | 77.1 | 1465 | 23.54 | 5674.6 | 2778.4 | 2806.5 | 4067.3 | 1212.3 | 0.66629 | 5.772
2024-12-09 | 22:51 | Data | 0 | 33.068 | 31.211 | 182.649 | 7.63 | 172.075 | 2255.97 | 25.89 | 47.172 | 6.36 | 1.329 | 4.455 | 8707.55 | 1.863 | 97.9 | 77 | 1466 | 23.54 | 5659.9 | 2783.4 | 2801.8 | 4065 | 1212.3 | 0.66789 | 5.784
2024-12-09 | 22:51 | Data | 0 | 32.987 | 30.995 | 182.513 | 7.64 | 172.075 | 2252.35 | 25.89 | 47.172 | 6.36 | 1.331 | 4.417 | 8703.03 | 1.85 | 97.9 | 76.8 | 1464 | 23.59 | 5657 | 2780.5 | 2761 | 4052.2 | 1212.3 | 0.67036 | 5.748
2024-12-09 | 22:52 | Data | 0 | 32.906 | 31.319 | 182.423 | 7.64 | 171.984 | 2255.97 | 25.89 | 47.172 | 6.36 | 1.332 | 4.413 | 8707.55 | 1.83 | 97.9 | 76.8 | 1465 | 23.54 | 5659.9 | 2852.7 | 2783.7 | 4111 | 1212.3 | 0.67465 | 5.745
2024-12-09 | 22:52 | Data | 0 | 33.007 | 31.11 | 182.468 | 7.63 | 171.984 | 2255.97 | 25.89 | 47.082 | 6.36 | 1.332 | 4.451 | 8707.55 | 1.843 | 97.9 | 77 | 1466 | 23.54 | 5659.9 | 2851.7 | 2758.8 | 4087.4 | 1212.3 | 0.6801 | 5.781
2024-12-09 | 22:52 | Data | 0 | 32.926 | 31.11 | 182.513 | 7.63 | 171.984 | 2251.45 | 25.9 | 47.082 | 6.36 | 1.336 | 4.44 | 8716.59 | 1.843 | 97.9 | 76.9 | 1464 | 23.59 | 5665.8 | 2848.7 | 2776.8 | 4102.2 | 1212.3 | 0.67712 | 5.777
2024-12-09 | 22:52 | Data | 0 | 33.264 | 31.164 | 182.423 | 7.63 | 172.03 | 2257.77 | 25.89 | 47.082 | 6.36 | 1.332 | 4.446 | 8716.59 | 1.857 | 97.9 | 77 | 1468 | 23.59 | 5665.8 | 2834.6 | 2786 | 4098.6 | 1212.3 | 0.67444 | 5.778
2024-12-09 | 22:52 | Data | 0 | 33.068 | 30.901 | 182.513 | 7.63 | 172.075 | 2252.35 | 25.89 | 47.172 | 6.36 | 1.33 | 4.43 | 8698.5 | 1.843 | 97.9 | 76.9 | 1464 | 23.54 | 5654 | 2849.2 | 2752.8 | 4083.2 | 1212.3 | 0.68045 | 5.76
2024-12-09 | 22:52 | Data | 0 | 33.014 | 30.941 | 182.468 | 7.63 | 172.03 | 2250.54 | 25.89 | 47.082 | 6.36 | 1.339 | 4.427 | 8693.98 | 1.681 | 97.9 | 76.8 | 1462 | 23.54 | 5651.1 | 2821.3 | 2769 | 4079.1 | 1212.3 | 0.67312 | 5.765
2024-12-09 | 22:52 | Data | 0 | 33.149 | 31.123 | 182.377 | 7.64 | 171.894 | 2249.64 | 25.89 | 47.172 | 6.36 | 1.332 | 4.451 | 8693.98 | 1.924 | 97.9 | 77 | 1462 | 23.54 | 5651.1 | 2847.2 | 2805.5 | 4117.3 | 1212.3 | 0.67337 | 5.783
2024-12-09 | 22:52 | Data | 0 | 33.338 | 31.339 | 182.513 | 7.63 | 172.075 | 2246.93 | 25.89 | 47.082 | 6.36 | 1.339 | 4.439 | 8703.03 | 1.951 | 97.9 | 76.8 | 1461 | 23.59 | 5657 | 2843.7 | 2821.6 | 4129.2 | 1212.3 | 0.67126 | 5.779
2024-12-09 | 22:52 | Data | 0 | 32.838 | 30.995 | 182.423 | 7.64 | 171.939 | 2249.64 | 25.89 | 47.172 | 6.36 | 1.345 | 4.47 | 8703.03 | 1.944 | 97.9 | 76.9 | 1462 | 23.59 | 5657 | 2860.2 | 2814.8 | 4135.8 | 1212.3 | 0.67279 | 5.815
2024-12-09 | 22:52 | Data | 0 | 32.953 | 31.279 | 182.423 | 7.63 | 172.03 | 2249.64 | 25.89 | 47.082 | 6.36 | 1.338 | 4.449 | 8712.07 | 1.843 | 97.9 | 76.9 | 1462 | 23.54 | 5662.8 | 2836 | 2805.1 | 4109.7 | 1212.3 | 0.67215 | 5.787
2024-12-09 | 22:52 | Data | 0 | 32.899 | 31.103 | 182.513 | 7.64 | 171.894 | 2249.64 | 25.89 | 47.082 | 6.37 | 1.324 | 4.422 | 8721.11 | 1.843 | 97.9 | 77 | 1462 | 23.54 | 5668.7 | 2850.5 | 2790.8 | 4109.6 | 1212.3 | 0.67576 | 5.745
2024-12-09 | 22:52 | Data | 0 | 32.98 | 31.272 | 182.332 | 7.63 | 171.984 | 2249.64 | 25.89 | 47.082 | 6.37 | 1.328 | 4.443 | 8707.55 | 1.816 | 97.9 | 77 | 1462 | 23.59 | 5659.9 | 2840.5 | 2780 | 4084.7 | 1212.3 | 0.67488 | 5.77
2024-12-09 | 22:52 | Data | 0 | 32.865 | 31.11 | 182.558 | 7.64 | 172.12 | 2252.35 | 25.89 | 47.172 | 6.37 | 1.334 | 4.431 | 8721.11 | 1.634 | 97.9 | 76.8 | 1464 | 23.59 | 5668.7 | 2842.3 | 2752.4 | 4082.7 | 1212.3 | 0.67884 | 5.766
2024-12-09 | 22:52 | Data | 0 | 32.98 | 31.11 | 182.513 | 7.63 | 171.984 | 2247.83 | 25.89 | 46.991 | 6.36 | 1.332 | 4.438 | 8703.03 | 1.674 | 97.9 | 76.9 | 1461 | 23.54 | 5657 | 2846 | 2759 | 4082.9 | 1212.3 | 0.67957 | 5.771
2024-12-09 | 22:52 | Data | 0 | 32.507 | 31.272 | 182.468 | 7.64 | 171.849 | 2246.93 | 25.89 | 47.082 | 6.36 | 1.334 | 4.447 | 8703.03 | 1.728 | 97.9 | 76.9 | 1461 | 23.54 | 5657 | 2840.2 | 2746.7 | 4078.3 | 1212.3 | 0.67875 | 5.781
2024-12-09 | 22:52 | Data | 0 | 32.899 | 30.988 | 182.332 | 7.63 | 171.894 | 2249.64 | 25.89 | 47.082 | 6.36 | 1.337 | 4.445 | 8707.55 | 1.843 | 97.9 | 76.9 | 1462 | 23.54 | 5659.9 | 2834 | 2807.9 | 4120.8 | 1212.3 | 0.67334 | 5.781
2024-12-09 | 22:52 | Data | 0 | 32.75 | 31.11 | 182.377 | 7.64 | 171.939 | 2251.45 | 25.89 | 47.082 | 6.36 | 1.33 | 4.435 | 8689.46 | 1.62 | 97.9 | 76.9 | 1464 | 23.59 | 5648.1 | 2849.8 | 2773.5 | 4098.1 | 1212.3 | 0.67733 | 5.765
2024-12-09 | 22:52 | Data | 0 | 33.291 | 31.164 | 182.513 | 7.64 | 172.03 | 2251.45 | 25.9 | 47.172 | 6.37 | 1.328 | 4.428 | 8698.5 | 1.897 | 97.9 | 76.9 | 1464 | 23.54 | 5654 | 2823.3 | 2783.5 | 4087.8 | 1212.3 | 0.67279 | 5.756
2024-12-09 | 22:53 | Data | 0 | 32.73 | 31.056 | 182.513 | 7.63 | 171.894 | 2252.35 | 25.89 | 46.991 | 6.36 | 1.334 | 4.431 | 8707.55 | 1.904 | 97.9 | 76.8 | 1464 | 23.59 | 5659.9 | 2835.8 | 2769.9 | 4084.3 | 1212.3 | 0.67604 | 5.765
2024-12-09 | 22:53 | Data | 0 | 32.838 | 30.705 | 182.287 | 7.63 | 171.804 | 2249.64 | 25.89 | 47.172 | 6.36 | 1.329 | 4.43 | 8712.07 | 1.89 | 97.9 | 76.9 | 1462 | 23.54 | 5662.8 | 2823.8 | 2797.4 | 4094.3 | 1212.3 | 0.67275 | 5.759
2024-12-09 | 22:53 | Data | 0 | 32.507 | 30.691 | 182.196 | 7.64 | 171.758 | 2249.64 | 25.89 | 47.082 | 6.36 | 1.321 | 4.417 | 8707.55 | 1.755 | 97.9 | 77 | 1462 | 23.54 | 5659.9 | 2836.7 | 2788.5 | 4094.5 | 1212.3 | 0.67456 | 5.738
2024-12-09 | 22:53 | Data | 0 | 32.696 | 30.651 | 182.151 | 7.64 | 171.668 | 2249.64 | 25.89 | 47.172 | 6.36 | 1.329 | 4.402 | 8703.03 | 2.059 | 97.9 | 76.8 | 1462 | 23.54 | 5657 | 2849 | 2795.2 | 4110.6 | 1212.3 | 0.67515 | 5.731
2024-12-09 | 22:53 | Data | 0 | 32.777 | 30.664 | 182.287 | 7.63 | 171.804 | 2246.93 | 25.89 | 47.082 | 6.37 | 1.329 | 4.426 | 8693.98 | 1.857 | 97.9 | 76.9 | 1461 | 23.54 | 5651.1 | 2820.4 | 2793.3 | 4092.6 | 1212.3 | 0.67215 | 5.757
2024-12-09 | 22:53 | Data | 0 | 32.615 | 31.049 | 182.377 | 7.63 | 171.758 | 2242.41 | 25.89 | 47.262 | 6.36 | 1.329 | 4.423 | 8689.46 | 1.823 | 97.9 | 76.9 | 1458 | 23.63 | 5648.1 | 2839.5 | 2768.7 | 4088.3 | 1212.3 | 0.67716 | 5.753
2024-12-09 | 22:53 | Data | 0 | 32.946 | 31.11 | 182.332 | 7.63 | 171.939 | 2249.64 | 25.89 | 47.353 | 6.37 | 1.33 | 4.422 | 8703.03 | 1.843 | 97.9 | 76.9 | 1462 | 23.72 | 5657 | 2823.7 | 2779.6 | 4084.2 | 1212.3 | 0.67409 | 5.752
2024-12-09 | 22:53 | Data | 0 | 32.771 | 30.88 | 182.423 | 7.63 | 172.03 | 2250.54 | 25.89 | 47.443 | 6.37 | 1.335 | 4.384 | 8707.55 | 1.85 | 97.9 | 76.7 | 1462 | 23.68 | 5659.9 | 2846.5 | 2783.1 | 4096.7 | 1212.3 | 0.67877 | 5.719
2024-12-09 | 22:53 | Data | 0 | 32.838 | 31.069 | 182.287 | 7.63 | 171.939 | 2252.35 | 25.89 | 47.353 | 6.36 | 1.329 | 4.423 | 8707.55 | 1.843 | 97.9 | 76.9 | 1463 | 23.68 | 5659.9 | 2827.8 | 2786.3 | 4088.1 | 1212.3 | 0.67608 | 5.752
2024-12-09 | 22:53 | Data | 0 | 33.007 | 30.887 | 182.377 | 7.64 | 171.939 | 2252.35 | 25.9 | 47.443 | 6.36 | 1.323 | 4.447 | 8716.59 | 1.843 | 97.9 | 77.1 | 1464 | 23.68 | 5665.8 | 2845.2 | 2801.1 | 4109.7 | 1212.3 | 0.67507 | 5.771
2024-12-09 | 22:53 | Data | 0 | 32.831 | 31.083 | 182.287 | 7.63 | 171.894 | 2256.87 | 25.89 | 47.353 | 6.36 | 1.328 | 4.442 | 8716.59 | 1.897 | 97.9 | 77 | 1467 | 23.63 | 5665.8 | 2823.6 | 2786.3 | 4086.9 | 1212.3 | 0.67318 | 5.768
2024-12-09 | 22:53 | Data | 0 | 32.946 | 30.894 | 182.377 | 7.63 | 171.894 | 2250.54 | 25.9 | 47.353 | 6.37 | 1.331 | 4.46 | 8716.59 | 1.971 | 97.9 | 77 | 1463 | 23.68 | 5665.8 | 2837.9 | 2794.1 | 4098 | 1212.3 | 0.67302 | 5.791
2024-12-09 | 22:53 | Data | 0 | 32.831 | 30.88 | 182.377 | 7.64 | 171.984 | 2253.25 | 25.89 | 47.353 | 6.36 | 1.34 | 4.428 | 8707.55 | 1.857 | 97.9 | 76.8 | 1465 | 23.68 | 5659.9 | 2817.6 | 2827.1 | 4109 | 1212.3 | 0.66827 | 5.77
2024-12-09 | 22:53 | Data | 0 | 32.899 | 31.096 | 182.332 | 7.63 | 171.984 | 2253.25 | 25.89 | 47.443 | 6.36 | 1.33 | 4.43 | 8712.07 | 1.87 | 97.9 | 76.9 | 1465 | 23.68 | 5662.8 | 2825 | 2828.7 | 4110.3 | 1212.3 | 0.6692 | 5.761
2024-12-09 | 22:53 | Data | 0 | 32.723 | 30.894 | 182.332 | 7.63 | 171.894 | 2255.97 | 25.89 | 47.353 | 6.37 | 1.331 | 4.431 | 8458.83 | 1.782 | 97.9 | 76.9 | 1466 | 23.63 | 5498.2 | 2840.1 | 2836.5 | 4134.3 | 1212.3 | 0.66898 | 5.762
2024-12-09 | 22:53 | Data | 0 | 33.183 | 31.123 | 182.468 | 7.63 | 172.075 | 2252.35 | 25.89 | 47.172 | 6.36 | 1.328 | 4.462 | 8567.36 | 1.931 | 97.9 | 77.1 | 1464 | 23.54 | 5568.8 | 2852.9 | 2854.8 | 4152.7 | 1212.4 | 0.66784 | 5.789
2024-12-09 | 22:53 | Data | 0 | 33.054 | 31.11 | 182.332 | 7.63 | 171.939 | 2257.77 | 25.89 | 46.991 | 6.36 | 1.335 | 4.466 | 8730.16 | 2.059 | 97.9 | 77 | 1468 | 23.5 | 5674.6 | 2832.6 | 2835.2 | 4123.6 | 1212.4 | 0.66603 | 5.801
2024-12-09 | 22:54 | Data | 0 | 33.061 | 31.333 | 182.513 | 7.64 | 171.984 | 2257.77 | 25.89 | 47.082 | 6.36 | 1.329 | 4.437 | 8716.59 | 1.836 | 97.9 | 76.9 | 1468 | 23.54 | 5665.8 | 2849.4 | 2798.3 | 4110 | 1212.4 | 0.67539 | 5.767
2024-12-09 | 22:54 | Data | 0 | 32.737 | 31.056 | 182.287 | 7.63 | 171.984 | 2254.16 | 25.89 | 47.353 | 6.36 | 1.331 | 4.423 | 8716.59 | 2.012 | 97.9 | 76.9 | 1465 | 23.68 | 5665.8 | 2834.2 | 2769.2 | 4096.7 | 1212.4 | 0.67709 | 5.755
2024-12-09 | 22:54 | Data | 0 | 32.838 | 31.312 | 182.468 | 7.63 | 172.075 | 2254.16 | 25.89 | 47.082 | 6.37 | 1.329 | 4.445 | 8716.59 | 1.83 | 97.9 | 77 | 1465 | 23.59 | 5665.8 | 2839.8 | 2768.2 | 4085.4 | 1212.4 | 0.6784 | 5.772
2024-12-09 | 22:54 | Data | 0 | 32.953 | 31.11 | 182.513 | 7.63 | 172.03 | 2257.77 | 25.89 | 47.082 | 6.36 | 1.327 | 4.443 | 8707.55 | 1.843 | 97.9 | 77 | 1468 | 23.54 | 5659.9 | 2851.5 | 2769.3 | 4088.1 | 1212.4 | 0.68129 | 5.77
2024-12-09 | 22:54 | Data | 0 | 32.953 | 30.995 | 182.468 | 7.63 | 172.03 | 2258.68 | 25.89 | 47.082 | 6.36 | 1.336 | 4.446 | 8707.55 | 1.843 | 97.9 | 76.9 | 1468 | 23.59 | 5659.9 | 2810.7 | 2773.1 | 4071.5 | 1212.4 | 0.67231 | 5.781
2024-12-09 | 22:54 | Data | 0 | 33.284 | 31.252 | 182.468 | 7.63 | 172.03 | 2257.77 | 25.89 | 47.353 | 6.36 | 1.339 | 4.436 | 8703.03 | 1.816 | 97.9 | 76.8 | 1468 | 23.68 | 5657 | 2831.1 | 2777.8 | 4094.4 | 1212.4 | 0.67598 | 5.776
2024-12-09 | 22:54 | Data | 0 | 33.014 | 30.914 | 182.377 | 7.64 | 171.984 | 2260.48 | 25.89 | 47.172 | 6.36 | 1.326 | 4.441 | 8703.03 | 1.897 | 97.9 | 77 | 1469 | 23.54 | 5657 | 2842.1 | 2794.9 | 4101.8 | 1212.4 | 0.67483 | 5.767
2024-12-09 | 22:54 | Data | 0 | 32.953 | 30.894 | 182.377 | 7.64 | 171.939 | 2261.39 | 25.89 | 47.082 | 6.36 | 1.319 | 4.454 | 8716.59 | 2.046 | 97.9 | 77.2 | 1469 | 23.54 | 5665.8 | 2836.5 | 2778.6 | 4094.4 | 1212.4 | 0.67536 | 5.772
2024-12-09 | 22:54 | Data | 0 | 33.054 | 31.285 | 182.332 | 7.63 | 172.03 | 2261.39 | 25.89 | 47.082 | 6.36 | 1.322 | 4.461 | 8716.59 | 1.884 | 97.9 | 77.1 | 1470 | 23.54 | 5665.8 | 2858.1 | 2802.5 | 4103.3 | 1212.4 | 0.6765 | 5.783
2024-12-09 | 22:54 | Data | 0 | 32.953 | 30.995 | 182.468 | 7.63 | 172.03 | 2260.48 | 25.89 | 47.172 | 6.37 | 1.335 | 4.43 | 8703.03 | 1.843 | 97.9 | 76.8 | 1469 | 23.54 | 5657 | 2828.7 | 2807.1 | 4103.9 | 1212.4 | 0.67226 | 5.766
2024-12-09 | 22:54 | Data | 0 | 32.838 | 30.894 | 182.377 | 7.64 | 172.03 | 2265 | 25.89 | 47.172 | 6.37 | 1.343 | 4.432 | 8707.55 | 1.83 | 97.9 | 76.8 | 1472 | 23.54 | 5659.9 | 2858.1 | 2784.8 | 4110.1 | 1212.4 | 0.67768 | 5.777
2024-12-09 | 22:54 | Data | 0 | 33.007 | 30.887 | 182.332 | 7.64 | 171.939 | 2265 | 25.89 | 47.172 | 6.37 | 1.332 | 4.461 | 8703.03 | 1.87 | 97.9 | 77 | 1472 | 23.54 | 5657 | 2826.9 | 2791 | 4096.5 | 1212.4 | 0.67408 | 5.793
2024-12-09 | 22:54 | Data | 0 | 32.953 | 30.941 | 182.558 | 7.63 | 172.03 | 2262.29 | 25.89 | 47.172 | 6.36 | 1.327 | 4.435 | 8703.03 | 1.951 | 97.9 | 77 | 1469 | 23.59 | 5657 | 2824.3 | 2785.2 | 4089.7 | 1212.4 | 0.67407 | 5.761
2024-12-09 | 22:54 | Data | 0 | 32.838 | 31.137 | 182.513 | 7.63 | 171.984 | 2261.39 | 25.89 | 47.082 | 6.37 | 1.324 | 4.429 | 8703.03 | 1.735 | 97.9 | 77 | 1470 | 23.5 | 5657 | 2822.3 | 2783.2 | 4087.5 | 1212.4 | 0.67265 | 5.755
2024-12-09 | 22:54 | Data | 0 | 32.953 | 31.157 | 182.377 | 7.64 | 172.03 | 2263.2 | 25.89 | 47.082 | 6.36 | 1.32 | 4.453 | 8689.46 | 1.809 | 97.9 | 77.1 | 1471 | 23.54 | 5648.1 | 2826 | 2768.9 | 4079.6 | 1212.4 | 0.67578 | 5.773
2024-12-09 | 22:54 | Data | 0 | 32.953 | 30.982 | 182.423 | 7.64 | 171.984 | 2264.1 | 25.89 | 47.172 | 6.37 | 1.329 | 4.436 | 8680.41 | 1.769 | 97.9 | 76.9 | 1471 | 23.54 | 5642.3 | 2825.1 | 2772.2 | 4075.2 | 1212.4 | 0.67791 | 5.765
2024-12-09 | 22:54 | Data | 0 | 32.899 | 31.319 | 182.423 | 7.64 | 171.939 | 2263.2 | 25.89 | 47.082 | 6.36 | 1.339 | 4.439 | 8689.46 | 1.863 | 97.9 | 76.8 | 1472 | 23.59 | 5648.1 | 2840.7 | 2750.6 | 4071.8 | 1212.4 | 0.67923 | 5.779
2024-12-09 | 22:55 | Data | 0 | 32.757 | 31.083 | 182.287 | 7.64 | 171.849 | 2263.2 | 25.89 | 47.082 | 6.36 | 1.33 | 4.427 | 8680.41 | 1.674 | 97.9 | 76.9 | 1472 | 23.54 | 5642.3 | 2830.7 | 2746.9 | 4066.4 | 1212.4 | 0.67908 | 5.757
2024-12-09 | 22:55 | Data | 0 | 33.061 | 31.002 | 182.468 | 7.64 | 171.984 | 2264.1 | 25.9 | 47.172 | 6.37 | 1.334 | 4.463 | 8684.94 | 1.863 | 97.9 | 77 | 1472 | 23.54 | 5645.2 | 2827.4 | 2751.5 | 4061.2 | 1212.4 | 0.68034 | 5.797
2024-12-09 | 22:55 | Data | 0 | 33.365 | 31.137 | 182.558 | 7.64 | 172.075 | 2260.48 | 25.89 | 47.172 | 6.36 | 1.339 | 4.441 | 8693.98 | 1.958 | 97.9 | 76.8 | 1469 | 23.54 | 5651.1 | 2839 | 2760.6 | 4077.3 | 1212.4 | 0.67874 | 5.78
2024-12-09 | 22:55 | Data | 0 | 32.777 | 30.894 | 182.332 | 7.63 | 171.939 | 2265.91 | 25.89 | 47.172 | 6.37 | 1.339 | 4.432 | 8693.98 | 1.823 | 97.9 | 76.8 | 1473 | 23.54 | 5651.1 | 2832 | 2758.1 | 4075.8 | 1212.4 | 0.67491 | 5.771
2024-12-09 | 22:55 | Data | 0 | 33.088 | 31.029 | 182.468 | 7.64 | 172.03 | 2260.48 | 25.89 | 47.082 | 6.36 | 1.329 | 4.455 | 8680.41 | 1.87 | 97.9 | 77 | 1469 | 23.54 | 5642.3 | 2850.5 | 2773.4 | 4095.4 | 1212.4 | 0.67884 | 5.783
2024-12-09 | 22:55 | Data | 0 | 32.845 | 30.941 | 182.332 | 7.63 | 171.984 | 2258.68 | 25.89 | 47.082 | 6.36 | 1.335 | 4.451 | 8680.41 | 1.755 | 97.9 | 76.9 | 1468 | 23.5 | 5642.3 | 2832 | 2757.9 | 4073.2 | 1212.4 | 0.67787 | 5.786
2024-12-09 | 22:55 | Data | 0 | 32.561 | 30.887 | 182.513 | 7.63 | 172.12 | 2258.68 | 25.89 | 47.082 | 6.37 | 1.325 | 4.421 | 8689.46 | 1.749 | 97.9 | 76.9 | 1468 | 23.54 | 5648.1 | 2829.1 | 2762.6 | 4077.7 | 1212.4 | 0.67661 | 5.747
2024-12-09 | 22:55 | Data | 0 | 33.176 | 31.157 | 182.513 | 7.64 | 172.12 | 2257.77 | 25.9 | 47.082 | 6.36 | 1.323 | 4.423 | 8703.03 | 1.978 | 97.9 | 77 | 1468 | 23.54 | 5657 | 2830.2 | 2768.3 | 4078.6 | 1212.4 | 0.67789 | 5.747
2024-12-09 | 22:55 | Data | 0 | 32.838 | 31.299 | 182.423 | 7.64 | 171.984 | 2255.97 | 25.9 | 46.991 | 6.36 | 1.336 | 4.447 | 8703.03 | 1.674 | 97.9 | 76.9 | 1466 | 23.5 | 5657 | 2835 | 2749.1 | 4070.7 | 1212.4 | 0.67943 | 5.783
2024-12-09 | 22:55 | Data | 0 | 33.378 | 31.393 | 182.558 | 7.63 | 172.12 | 2255.97 | 25.89 | 47.082 | 6.36 | 1.343 | 4.432 | 8721.11 | 1.789 | 97.9 | 76.7 | 1466 | 23.54 | 5668.7 | 2828.4 | 2754.5 | 4069.4 | 1212.4 | 0.67789 | 5.775
2024-12-09 | 22:55 | Data | 0 | 32.899 | 31.09 | 182.377 | 7.63 | 172.03 | 2255.97 | 25.89 | 47.082 | 6.36 | 1.325 | 4.418 | 8703.03 | 1.924 | 97.9 | 76.9 | 1465 | 23.59 | 5657 | 2834.7 | 2756.7 | 4077.6 | 1212.4 | 0.67773 | 5.743
2024-12-09 | 22:55 | Data | 0 | 32.791 | 31.11 | 182.513 | 7.64 | 172.03 | 2254.16 | 25.89 | 47.172 | 6.36 | 1.326 | 4.401 | 8707.55 | 1.634 | 97.9 | 76.8 | 1465 | 23.54 | 5659.9 | 2831.4 | 2752.6 | 4072.9 | 1212.4 | 0.67773 | 5.727
2024-12-09 | 22:55 | Data | 0 | 32.96 | 31.11 | 182.513 | 7.63 | 172.12 | 2252.35 | 25.89 | 47.172 | 6.37 | 1.331 | 4.41 | 8712.07 | 1.843 | 97.9 | 76.8 | 1464 | 23.54 | 5662.8 | 2835 | 2746.5 | 4069.4 | 1212.4 | 0.67964 | 5.742
2024-12-09 | 22:55 | Data | 0 | 32.94 | 31.11 | 182.423 | 7.63 | 171.984 | 2248.73 | 25.89 | 47.082 | 6.36 | 1.339 | 4.455 | 8721.11 | 1.958 | 97.9 | 76.9 | 1462 | 23.54 | 5668.7 | 2812 | 2745 | 4051.3 | 1212.4 | 0.67616 | 5.793
2024-12-09 | 22:55 | Data | 0 | 33.183 | 31.002 | 182.377 | 7.63 | 171.984 | 2248.73 | 25.89 | 47.082 | 6.37 | 1.334 | 4.47 | 8721.11 | 1.931 | 97.9 | 77 | 1462 | 23.59 | 5668.7 | 2827.9 | 2757.6 | 4065.5 | 1212.4 | 0.67878 | 5.805
2024-12-09 | 22:55 | Data | 0 | 32.73 | 31.103 | 182.513 | 7.63 | 172.03 | 2248.73 | 25.89 | 46.991 | 6.37 | 1.33 | 4.459 | 8707.55 | 1.627 | 97.9 | 77 | 1462 | 23.54 | 5659.9 | 2827.7 | 2757.1 | 4074.1 | 1212.4 | 0.67707 | 5.789
2024-12-09 | 22:55 | Data | 0 | 32.838 | 31.103 | 182.423 | 7.63 | 172.03 | 2252.35 | 25.89 | 47.082 | 6.36 | 1.329 | 4.451 | 8734.68 | 1.634 | 97.9 | 77 | 1464 | 23.54 | 5677.5 | 2825.2 | 2764.5 | 4070.3 | 1212.4 | 0.67733 | 5.78
2024-12-09 | 22:56 | Data | 0 | 32.946 | 30.934 | 182.377 | 7.63 | 172.03 | 2252.35 | 25.89 | 47.082 | 6.36 | 1.33 | 4.432 | 8743.73 | 1.958 | 97.9 | 76.9 | 1464 | 23.54 | 5683.4 | 2841 | 2753 | 4078.5 | 1212.5 | 0.67977 | 5.762
2024-12-09 | 22:56 | Data | 0 | 33.27 | 31.346 | 182.423 | 7.63 | 171.939 | 2247.83 | 25.89 | 47.082 | 6.37 | 1.332 | 4.412 | 8730.16 | 1.951 | 97.9 | 76.8 | 1461 | 23.54 | 5674.6 | 2832.5 | 2767.3 | 4079.3 | 1212.5 | 0.67772 | 5.744
2024-12-09 | 22:56 | Data | 0 | 32.94 | 31.11 | 182.377 | 7.63 | 172.03 | 2246.02 | 25.89 | 47.172 | 6.36 | 1.328 | 4.424 | 8716.59 | 2.039 | 97.9 | 76.9 | 1461 | 23.54 | 5665.8 | 2832.1 | 2771.4 | 4080.9 | 1212.5 | 0.67775 | 5.751
2024-12-09 | 22:56 | Data | 0 | 33.183 | 31.339 | 182.513 | 7.63 | 172.03 | 2246.93 | 25.89 | 47.172 | 6.37 | 1.332 | 4.441 | 8716.59 | 1.843 | 97.9 | 76.9 | 1461 | 23.59 | 5665.8 | 2824.3 | 2741.4 | 4061.4 | 1212.5 | 0.67848 | 5.773
2024-12-09 | 22:56 | Data | 0 | 33.196 | 31.117 | 182.604 | 7.63 | 172.256 | 2250.54 | 25.89 | 47.082 | 6.36 | 1.342 | 4.445 | 8703.03 | 1.938 | 97.9 | 76.8 | 1462 | 23.54 | 5657 | 2828.3 | 2743.3 | 4062.5 | 1212.5 | 0.67904 | 5.787
2024-12-09 | 22:56 | Data | 0 | 32.798 | 31.096 | 182.468 | 7.63 | 171.939 | 2254.16 | 25.89 | 47.172 | 6.37 | 1.334 | 4.391 | 8707.55 | 2.032 | 97.9 | 76.7 | 1466 | 23.59 | 5659.9 | 2837.6 | 2746.6 | 4069.5 | 1212.5 | 0.67976 | 5.724
2024-12-09 | 22:56 | Data | 0 | 33.156 | 31.123 | 182.468 | 7.64 | 172.03 | 2258.68 | 25.89 | 47.082 | 6.37 | 1.344 | 4.409 | 8716.59 | 1.958 | 97.9 | 76.6 | 1468 | 23.59 | 5665.8 | 2817.9 | 2747.4 | 4052.7 | 1212.5 | 0.67955 | 5.751
2024-12-09 | 22:56 | Data | 0 | 33.23 | 30.901 | 182.649 | 7.64 | 172.12 | 2260.48 | 25.89 | 47.082 | 6.37 | 1.339 | 4.43 | 8707.55 | 1.904 | 97.9 | 76.8 | 1470 | 23.59 | 5659.9 | 2826.7 | 2750.2 | 4065.9 | 1212.5 | 0.67792 | 5.771
2024-12-09 | 22:56 | Data | 0 | 32.953 | 31.11 | 182.423 | 7.63 | 171.984 | 2261.39 | 25.89 | 47.082 | 6.36 | 1.328 | 4.437 | 8703.03 | 1.85 | 97.9 | 77 | 1469 | 23.54 | 5657 | 2844.8 | 2749.8 | 4072.8 | 1212.5 | 0.68206 | 5.763
2024-12-09 | 22:56 | Data | 0 | 32.798 | 31.002 | 182.513 | 7.63 | 172.03 | 2258.68 | 25.89 | 47.082 | 6.37 | 1.329 | 4.427 | 8712.07 | 1.836 | 97.9 | 76.9 | 1468 | 23.54 | 5662.8 | 2827.8 | 2735.7 | 4058.9 | 1212.5 | 0.6792 | 5.756
2024-12-09 | 22:56 | Data | 0 | 32.953 | 31.285 | 182.468 | 7.64 | 172.03 | 2260.48 | 25.89 | 47.172 | 6.37 | 1.32 | 4.425 | 8703.03 | 1.843 | 97.9 | 77 | 1469 | 23.59 | 5657 | 2832 | 2758.4 | 4075.2 | 1212.5 | 0.67606 | 5.745
2024-12-09 | 22:56 | Data | 0 | 33.014 | 30.941 | 182.513 | 7.63 | 172.03 | 2261.39 | 25.9 | 47.082 | 6.37 | 1.322 | 4.423 | 8707.55 | 1.796 | 97.9 | 77 | 1470 | 23.54 | 5659.9 | 2835.4 | 2777.2 | 4091.7 | 1212.5 | 0.67499 | 5.746
2024-12-09 | 22:56 | Data | 0 | 32.946 | 31.123 | 182.468 | 7.64 | 171.984 | 2261.39 | 25.89 | 47.082 | 6.37 | 1.339 | 4.471 | 8703.03 | 1.816 | 97.9 | 76.9 | 1470 | 23.59 | 5657 | 2812.7 | 2767.6 | 4065.8 | 1212.5 | 0.67529 | 5.81
2024-12-09 | 22:56 | Data | 0 | 32.75 | 30.907 | 182.377 | 7.64 | 171.984 | 2265 | 25.89 | 47.082 | 6.36 | 1.341 | 4.475 | 8716.59 | 1.742 | 97.9 | 76.9 | 1472 | 23.54 | 5665.8 | 2853.6 | 2757.6 | 4087.3 | 1212.5 | 0.68131 | 5.817
2024-12-09 | 22:56 | Data | 0 | 32.757 | 30.88 | 182.377 | 7.64 | 172.075 | 2261.39 | 25.89 | 47.082 | 6.36 | 1.332 | 4.437 | 8721.11 | 1.85 | 97.9 | 76.9 | 1469 | 23.5 | 5668.7 | 2828.5 | 2751.7 | 4068.3 | 1212.5 | 0.67782 | 5.768
2024-12-09 | 22:56 | Data | 0 | 32.98 | 31.11 | 182.423 | 7.64 | 172.03 | 2260.48 | 25.89 | 47.172 | 6.37 | 1.336 | 4.439 | 8703.03 | 1.85 | 97.9 | 76.9 | 1469 | 23.54 | 5657 | 2831.8 | 2767.2 | 4077.9 | 1212.5 | 0.67834 | 5.775
2024-12-09 | 22:57 | Data | 0 | 32.953 | 31.11 | 182.423 | 7.64 | 172.075 | 2261.39 | 25.89 | 47.082 | 6.37 | 1.334 | 4.438 | 8712.07 | 1.843 | 97.9 | 76.9 | 1469 | 23.54 | 5662.8 | 2834 | 2763.7 | 4078.8 | 1212.5 | 0.67763 | 5.772
2024-12-09 | 22:57 | Data | 0 | 33.183 | 31.164 | 182.468 | 7.63 | 172.03 | 2260.48 | 25.89 | 47.172 | 6.37 | 1.332 | 4.455 | 8748.25 | 1.958 | 97.9 | 77 | 1470 | 23.54 | 5686.4 | 2842.5 | 2771.2 | 4082 | 1212.5 | 0.67857 | 5.788
2024-12-09 | 22:57 | Data | 0 | 32.953 | 30.907 | 182.604 | 7.63 | 172.12 | 2260.48 | 25.89 | 47.172 | 6.37 | 1.326 | 4.454 | 8730.16 | 1.951 | 97.9 | 77.1 | 1470 | 23.59 | 5674.6 | 2816.7 | 2764.7 | 4064.7 | 1212.5 | 0.6773 | 5.779
2024-12-09 | 22:57 | Data | 0 | 33.068 | 31.326 | 182.332 | 7.63 | 171.984 | 2260.48 | 25.89 | 47.172 | 6.37 | 1.332 | 4.426 | 8730.16 | 1.857 | 97.9 | 76.9 | 1470 | 23.54 | 5674.6 | 2820.2 | 2762.1 | 4068 | 1212.5 | 0.67574 | 5.758
2024-12-09 | 22:57 | Data | 0 | 33.007 | 31.11 | 182.468 | 7.63 | 171.939 | 2260.48 | 25.89 | 47.082 | 6.36 | 1.339 | 4.443 | 8739.2 | 1.857 | 97.9 | 76.8 | 1469 | 23.59 | 5680.5 | 2824.8 | 2733.2 | 4046 | 1212.5 | 0.68116 | 5.78
2024-12-09 | 22:57 | Data | 0 | 32.899 | 31.11 | 182.604 | 7.64 | 172.075 | 2260.48 | 25.9 | 47.082 | 6.37 | 1.324 | 4.445 | 8721.11 | 1.816 | 97.9 | 77 | 1470 | 23.54 | 5668.7 | 2800.8 | 2756.7 | 4050.5 | 1212.5 | 0.67495 | 5.769
2024-12-09 | 22:57 | Data | 0 | 32.75 | 31.096 | 182.423 | 7.63 | 172.03 | 2263.2 | 25.89 | 47.172 | 6.37 | 1.323 | 4.446 | 8730.16 | 1.641 | 97.9 | 77.1 | 1471 | 23.54 | 5674.6 | 2826.9 | 2760.9 | 4060.2 | 1212.5 | 0.67672 | 5.771
2024-12-09 | 22:57 | Data | 0 | 33.183 | 31.137 | 182.513 | 7.63 | 172.21 | 2258.68 | 25.89 | 47.082 | 6.37 | 1.326 | 4.397 | 8721.11 | 1.843 | 97.9 | 76.8 | 1468 | 23.54 | 5668.7 | 2837 | 2778.5 | 4083.6 | 1212.5 | 0.67671 | 5.723
2024-12-09 | 22:57 | Data | 0 | 32.845 | 31.15 | 182.604 | 7.64 | 172.075 | 2258.68 | 25.89 | 47.082 | 6.36 | 1.328 | 4.412 | 8739.2 | 1.917 | 97.9 | 76.9 | 1469 | 23.54 | 5680.5 | 2842.9 | 2747 | 4073.7 | 1212.5 | 0.67938 | 5.739
2024-12-09 | 22:57 | Data | 0 | 32.98 | 31.11 | 182.423 | 7.63 | 172.03 | 2258.68 | 25.89 | 47.172 | 6.37 | 1.323 | 4.427 | 8739.2 | 1.857 | 97.9 | 77 | 1468 | 23.54 | 5680.5 | 2837.8 | 2743.9 | 4069 | 1212.5 | 0.68105 | 5.75
2024-12-09 | 22:57 | Data | 0 | 32.953 | 31.11 | 182.423 | 7.63 | 172.075 | 2253.25 | 25.89 | 47.082 | 6.37 | 1.327 | 4.435 | 8730.16 | 1.843 | 97.9 | 77 | 1465 | 23.54 | 5674.6 | 2839.5 | 2747.1 | 4056.6 | 1212.5 | 0.68115 | 5.761
2024-12-09 | 22:57 | Data | 0 | 33.257 | 31.542 | 182.604 | 7.64 | 172.075 | 2248.73 | 25.89 | 46.811 | 6.37 | 1.33 | 4.437 | 8734.68 | 1.884 | 97.9 | 77 | 1462 | 23.36 | 5677.5 | 2827.1 | 2765.3 | 4077.3 | 1212.5 | 0.67584 | 5.768
2024-12-09 | 22:57 | Data | 0 | 32.764 | 31.326 | 182.468 | 7.63 | 172.075 | 2249.64 | 25.89 | 46.721 | 6.36 | 1.33 | 4.442 | 8734.68 | 1.614 | 97.9 | 77 | 1462 | 23.36 | 5677.5 | 2834 | 2750.6 | 4069.4 | 1212.5 | 0.67598 | 5.771
2024-12-09 | 22:57 | Data | 0 | 33.203 | 30.914 | 182.558 | 7.63 | 172.075 | 2249.64 | 25.89 | 46.721 | 6.36 | 1.339 | 4.443 | 8721.11 | 1.917 | 97.9 | 76.8 | 1462 | 23.41 | 5668.7 | 2847.7 | 2755.7 | 4082.6 | 1212.5 | 0.68042 | 5.782
2024-12-09 | 22:57 | Data | 0 | 33.156 | 31.123 | 182.423 | 7.63 | 172.03 | 2246.93 | 25.89 | 46.721 | 6.37 | 1.34 | 4.418 | 8716.59 | 2.039 | 97.9 | 76.7 | 1461 | 23.36 | 5665.8 | 2840.6 | 2757.4 | 4079.2 | 1212.5 | 0.67926 | 5.757
2024-12-09 | 22:57 | Data | 0 | 33.007 | 31.326 | 182.513 | 7.63 | 172.075 | 2246.93 | 25.89 | 46.811 | 6.36 | 1.329 | 4.432 | 8712.07 | 1.735 | 97.9 | 76.9 | 1460 | 23.41 | 5662.8 | 2842.9 | 2783.3 | 4095.3 | 1212.5 | 0.67753 | 5.761
2024-12-09 | 22:57 | Data | 0 | 32.899 | 31.333 | 182.513 | 7.64 | 171.984 | 2247.83 | 25.89 | 46.811 | 6.37 | 1.325 | 4.41 | 8721.11 | 1.809 | 97.9 | 76.9 | 1461 | 23.41 | 5668.7 | 2801.4 | 2790.1 | 4075.8 | 1212.5 | 0.67054 | 5.737
2024-12-09 | 22:57 | Data | 0 | 33.081 | 31.144 | 182.513 | 7.63 | 172.03 | 2244.22 | 25.89 | 46.721 | 6.37 | 1.33 | 4.436 | 8721.11 | 1.722 | 97.9 | 76.9 | 1459 | 23.41 | 5668.7 | 2829.8 | 2782.6 | 4089.3 | 1212.5 | 0.67618 | 5.767
2024-12-09 | 22:58 | Data | 0 | 33.196 | 31.272 | 182.558 | 7.63 | 172.075 | 2245.12 | 25.9 | 46.991 | 6.37 | 1.344 | 4.457 | 8743.73 | 1.911 | 97.9 | 76.8 | 1459 | 23.5 | 5683.4 | 2858.4 | 2786.9 | 4104.2 | 1212.5 | 0.67999 | 5.801
2024-12-09 | 22:58 | Data | 0 | 32.953 | 31.11 | 182.558 | 7.63 | 172.075 | 2235.18 | 25.9 | 46.721 | 6.36 | 1.329 | 4.453 | 8743.73 | 1.843 | 97.9 | 77 | 1453 | 23.41 | 5683.4 | 2822.4 | 2738.8 | 4051.1 | 1212.5 | 0.67907 | 5.782
2024-12-09 | 22:58 | Data | 0 | 32.98 | 30.894 | 182.423 | 7.63 | 171.939 | 2242.41 | 25.89 | 46.721 | 6.37 | 1.338 | 4.448 | 8743.73 | 1.796 | 97.9 | 76.9 | 1457 | 23.36 | 5683.4 | 2822.5 | 2738.7 | 4058.6 | 1212.6 | 0.67897 | 5.787
2024-12-09 | 22:58 | Data | 0 | 33.291 | 31.177 | 182.468 | 7.63 | 172.075 | 2241.5 | 25.89 | 46.811 | 6.36 | 1.335 | 4.432 | 8721.11 | 1.87 | 97.9 | 76.9 | 1457 | 23.41 | 5668.7 | 2835.2 | 2741.7 | 4062.1 | 1212.6 | 0.68029 | 5.767
2024-12-09 | 22:58 | Data | 0 | 33.27 | 31.339 | 182.558 | 7.64 | 172.075 | 2244.22 | 25.89 | 46.63 | 6.37 | 1.324 | 4.41 | 8707.55 | 1.89 | 97.9 | 76.9 | 1459 | 23.36 | 5659.9 | 2832 | 2729.3 | 4057.7 | 1212.6 | 0.6798 | 5.735
2024-12-09 | 22:58 | Data | 0 | 32.94 | 31.11 | 182.423 | 7.63 | 172.03 | 2243.31 | 25.89 | 46.811 | 6.37 | 1.335 | 4.437 | 8721.11 | 1.85 | 97.9 | 76.9 | 1459 | 23.36 | 5668.7 | 2835.3 | 2753.7 | 4075 | 1212.6 | 0.67819 | 5.772
2024-12-09 | 22:58 | Data | 0 | 33.014 | 30.948 | 182.513 | 7.63 | 172.075 | 2245.12 | 25.9 | 46.811 | 6.37 | 1.339 | 4.441 | 8716.59 | 1.843 | 97.9 | 76.8 | 1459 | 23.36 | 5665.8 | 2836.6 | 2754.4 | 4073 | 1212.6 | 0.67877 | 5.78
2024-12-09 | 22:58 | Data | 0 | 33.007 | 30.894 | 182.558 | 7.64 | 172.12 | 2244.22 | 25.89 | 46.811 | 6.37 | 1.338 | 4.457 | 8721.11 | 1.951 | 97.9 | 76.9 | 1459 | 23.41 | 5668.7 | 2833.2 | 2761.3 | 4078.7 | 1212.6 | 0.6786 | 5.795
2024-12-09 | 22:58 | Data | 0 | 32.946 | 31.11 | 182.377 | 7.63 | 172.03 | 2244.22 | 25.89 | 46.721 | 6.37 | 1.339 | 4.444 | 8757.29 | 1.843 | 97.9 | 76.8 | 1459 | 23.41 | 5692.2 | 2837.8 | 2753.6 | 4074.9 | 1212.6 | 0.6784 | 5.783
2024-12-09 | 22:58 | Data | 0 | 33.176 | 31.333 | 182.468 | 7.64 | 172.03 | 2246.93 | 25.89 | 46.811 | 6.37 | 1.337 | 4.437 | 8748.25 | 1.85 | 97.9 | 76.8 | 1461 | 23.41 | 5686.4 | 2826.7 | 2737 | 4053.9 | 1212.6 | 0.6796 | 5.774
2024-12-09 | 22:58 | Data | 0 | 32.953 | 31.333 | 182.423 | 7.63 | 172.03 | 2246.93 | 25.89 | 46.811 | 6.37 | 1.331 | 4.463 | 8757.29 | 1.755 | 97.9 | 77 | 1461 | 23.36 | 5692.2 | 2821 | 2747 | 4064 | 1212.6 | 0.6762 | 5.795
2024-12-09 | 22:58 | Data | 0 | 32.845 | 31.177 | 182.513 | 7.63 | 172.075 | 2246.93 | 25.89 | 46.811 | 6.37 | 1.335 | 4.43 | 8743.73 | 1.938 | 97.9 | 76.9 | 1461 | 23.41 | 5683.4 | 2837.7 | 2765.2 | 4086.6 | 1212.6 | 0.67713 | 5.764
2024-12-09 | 22:58 | Data | 0 | 33.068 | 31.441 | 182.558 | 7.63 | 172.075 | 2246.93 | 25.89 | 46.721 | 6.37 | 1.342 | 4.44 | 8730.16 | 1.843 | 97.9 | 76.8 | 1461 | 23.36 | 5674.6 | 2815.6 | 2758 | 4061.5 | 1212.6 | 0.67685 | 5.781
2024-12-09 | 22:58 | Data | 0 | 32.784 | 30.887 | 182.377 | 7.64 | 171.894 | 2248.73 | 25.89 | 46.721 | 6.36 | 1.335 | 4.441 | 8716.59 | 2.012 | 97.9 | 76.9 | 1462 | 23.41 | 5665.8 | 2834 | 2749.8 | 4067 | 1212.6 | 0.68028 | 5.775
2024-12-09 | 22:58 | Data | 0 | 32.953 | 31.11 | 182.377 | 7.63 | 171.984 | 2249.64 | 25.9 | 46.811 | 6.37 | 1.335 | 4.43 | 8734.68 | 2.046 | 97.9 | 76.9 | 1462 | 23.41 | 5677.5 | 2839.6 | 2748.2 | 4071.1 | 1212.6 | 0.67987 | 5.764
2024-12-09 | 22:58 | Data | 0 | 33.007 | 31.11 | 182.423 | 7.64 | 171.984 | 2245.12 | 25.9 | 46.811 | 6.37 | 1.335 | 4.439 | 8730.16 | 1.85 | 97.9 | 76.9 | 1459 | 23.41 | 5674.6 | 2823 | 2760.3 | 4066.5 | 1212.6 | 0.68022 | 5.774
2024-12-09 | 22:58 | Data | 0 | 33.176 | 31.164 | 182.468 | 7.63 | 172.075 | 2250.54 | 25.89 | 47.082 | 6.37 | 1.326 | 4.427 | 8743.73 | 1.843 | 97.9 | 77 | 1463 | 23.59 | 5683.4 | 2822.3 | 2749.9 | 4072.7 | 1212.6 | 0.6808 | 5.752
2024-12-09 | 22:58 | Data | 0 | 32.98 | 31.11 | 182.513 | 7.64 | 171.984 | 2253.25 | 25.89 | 47.172 | 6.37 | 1.334 | 4.422 | 8743.73 | 1.843 | 97.9 | 76.8 | 1465 | 23.54 | 5683.4 | 2830.6 | 2750.8 | 4066.9 | 1212.6 | 0.67907 | 5.756
2024-12-09 | 22:59 | Data | 0 | 32.737 | 31.211 | 182.468 | 7.64 | 172.03 | 2250.54 | 25.89 | 47.082 | 6.37 | 1.328 | 4.427 | 8748.25 | 1.688 | 97.9 | 76.9 | 1462 | 23.54 | 5686.4 | 2843.5 | 2759.1 | 4082.9 | 1212.6 | 0.6802 | 5.755
2024-12-09 | 22:59 | Data | 0 | 33.237 | 31.002 | 182.604 | 7.63 | 172.12 | 2248.73 | 25.89 | 47.082 | 6.37 | 1.327 | 4.427 | 8734.68 | 1.83 | 97.9 | 77 | 1462 | 23.54 | 5677.5 | 2826.6 | 2751.3 | 4064.2 | 1212.6 | 0.6781 | 5.754
2024-12-09 | 22:59 | Data | 0 | 32.994 | 31.002 | 182.513 | 7.64 | 172.03 | 2248.73 | 25.89 | 47.172 | 6.36 | 1.329 | 4.455 | 8693.98 | 1.877 | 97.9 | 77 | 1462 | 23.54 | 5651.1 | 2828.5 | 2765.7 | 4081.3 | 1212.6 | 0.67484 | 5.784
2024-12-09 | 22:59 | Data | 0 | 32.967 | 31.11 | 182.468 | 7.63 | 172.075 | 2252.35 | 25.89 | 47.082 | 6.37 | 1.325 | 4.44 | 8703.03 | 1.728 | 97.9 | 77 | 1464 | 23.54 | 5657 | 2830.5 | 2766 | 4074.8 | 1212.6 | 0.67844 | 5.764
2024-12-09 | 22:59 | Data | 0 | 32.852 | 31.056 | 182.423 | 7.63 | 172.03 | 2253.25 | 25.89 | 47.082 | 6.37 | 1.33 | 4.427 | 8703.03 | 1.755 | 97.9 | 76.9 | 1464 | 23.59 | 5657 | 2828.5 | 2735.5 | 4055.9 | 1212.6 | 0.68126 | 5.758
2024-12-09 | 22:59 | Data | 0 | 33.108 | 31.495 | 182.558 | 7.63 | 171.984 | 2252.35 | 25.89 | 47.172 | 6.38 | 1.339 | 4.437 | 8716.59 | 1.884 | 97.9 | 76.8 | 1464 | 23.59 | 5665.8 | 2811.2 | 2749.3 | 4052.6 | 1212.6 | 0.67697 | 5.777
2024-12-09 | 22:59 | Data | 0 | 32.98 | 31.15 | 182.558 | 7.64 | 172.075 | 2252.35 | 25.89 | 47.082 | 6.37 | 1.343 | 4.437 | 8748.25 | 1.762 | 97.9 | 76.8 | 1464 | 23.59 | 5686.4 | 2821.3 | 2756 | 4065.4 | 1212.6 | 0.67735 | 5.78
2024-12-09 | 22:59 | Data | 0 | 32.953 | 31.022 | 182.332 | 7.63 | 171.939 | 2255.97 | 25.89 | 47.082 | 6.37 | 1.342 | 4.446 | 8748.25 | 1.951 | 97.9 | 76.8 | 1466 | 23.54 | 5686.4 | 2830.6 | 2745.8 | 4070.8 | 1212.6 | 0.67647 | 5.788
2024-12-09 | 22:59 | Data | 0 | 32.96 | 31.11 | 182.468 | 7.63 | 172.21 | 2252.35 | 25.89 | 47.172 | 6.37 | 1.329 | 4.447 | 8743.73 | 1.843 | 97.9 | 77 | 1464 | 23.54 | 5683.4 | 2833.5 | 2746.9 | 4077 | 1212.6 | 0.68019 | 5.777
2024-12-09 | 22:59 | Data | 0 | 33.183 | 31.312 | 182.558 | 7.63 | 172.12 | 2246.02 | 25.89 | 47.082 | 6.37 | 1.331 | 4.438 | 8757.29 | 1.958 | 97.9 | 76.9 | 1461 | 23.59 | 5692.2 | 2822.7 | 2760.8 | 4069.9 | 1212.6 | 0.67639 | 5.771
2024-12-09 | 22:59 | Data | 0 | 32.737 | 31.11 | 182.468 | 7.63 | 172.075 | 2251.45 | 25.89 | 47.082 | 6.37 | 1.329 | 4.445 | 9182.38 | 1.789 | 97.9 | 77 | 1463 | 23.54 | 5968.5 | 2823.3 | 2779 | 4080 | 1212.6 | 0.67521 | 5.774
2024-12-09 | 22:59 | Data | 0 | 32.994 | 31.11 | 182.513 | 7.63 | 172.03 | 2252.35 | 25.89 | 47.082 | 6.37 | 1.33 | 4.417 | 8734.68 | 1.843 | 97.9 | 76.9 | 1464 | 23.59 | 5677.5 | 2814.3 | 2781.6 | 4076.4 | 1212.6 | 0.67397 | 5.746
2024-12-09 | 22:59 | Data | 0 | 33.007 | 31.285 | 182.604 | 7.63 | 172.12 | 2252.35 | 25.9 | 47.172 | 6.37 | 1.336 | 4.453 | 8716.59 | 1.742 | 97.9 | 76.9 | 1464 | 23.54 | 5665.8 | 2845.7 | 2794.6 | 4108.6 | 1212.6 | 0.67489 | 5.789
2024-12-09 | 22:59 | Data | 0 | 33.007 | 31.326 | 182.604 | 7.63 | 172.075 | 2251.45 | 25.89 | 47.082 | 6.37 | 1.337 | 4.447 | 8734.68 | 1.634 | 97.9 | 76.9 | 1464 | 23.54 | 5677.5 | 2845.8 | 2785.2 | 4100.2 | 1212.6 | 0.67569 | 5.784
2024-12-09 | 22:59 | Data | 0 | 33.169 | 31.144 | 182.513 | 7.63 | 172.075 | 2252.35 | 25.89 | 47.082 | 6.36 | 1.33 | 4.435 | 8716.59 | 1.998 | 97.9 | 76.9 | 1463 | 23.54 | 5665.8 | 2840.3 | 2789.9 | 4098.5 | 1212.6 | 0.67599 | 5.765
2024-12-09 | 22:59 | Data | 0 | 32.967 | 31.096 | 182.558 | 7.63 | 172.21 | 2252.35 | 25.89 | 47.082 | 6.37 | 1.336 | 4.444 | 8716.59 | 1.87 | 97.9 | 76.9 | 1464 | 23.54 | 5665.8 | 2821.6 | 2765.6 | 4071.9 | 1212.6 | 0.67645 | 5.78
2024-12-09 | 22:59 | Data | 0 | 32.98 | 31.211 | 182.513 | 7.63 | 172.12 | 2252.35 | 25.89 | 47.082 | 6.37 | 1.344 | 4.441 | 8703.03 | 1.681 | 97.9 | 76.8 | 1464 | 23.59 | 5657 | 2824.4 | 2745.5 | 4059.6 | 1212.6 | 0.67836 | 5.784
2024-12-09 | 23:00 | Data | 0 | 33.095 | 31.137 | 182.513 | 7.63 | 172.12 | 2252.35 | 25.89 | 47.172 | 6.37 | 1.337 | 4.428 | 8721.11 | 2.005 | 97.9 | 76.8 | 1464 | 23.54 | 5668.7 | 2838.8 | 2754.3 | 4072.8 | 1212.6 | 0.67982 | 5.764
2024-12-09 | 23:00 | Data | 0 | 32.953 | 31.157 | 182.468 | 7.63 | 172.075 | 2252.35 | 25.89 | 47.172 | 6.37 | 1.327 | 4.453 | 8730.16 | 1.749 | 97.9 | 77 | 1464 | 23.59 | 5674.6 | 2817.3 | 2726.6 | 4041.8 | 1212.6 | 0.6807 | 5.78
2024-12-09 | 23:00 | Data | 0 | 32.953 | 31.535 | 182.558 | 7.63 | 172.21 | 2251.45 | 25.89 | 47.172 | 6.37 | 1.327 | 4.426 | 8721.11 | 1.843 | 97.9 | 76.9 | 1464 | 23.59 | 5668.7 | 2842.1 | 2751.8 | 4071.7 | 1212.6 | 0.6814 | 5.753
2024-12-09 | 23:00 | Data | 0 | 33.378 | 31.252 | 182.604 | 7.63 | 172.256 | 2252.35 | 25.89 | 47.082 | 6.36 | 1.332 | 4.412 | 8721.11 | 1.897 | 97.9 | 76.8 | 1463 | 23.54 | 5668.7 | 2831.4 | 2752 | 4068 | 1212.6 | 0.67866 | 5.742
2024-12-09 | 23:00 | Data | 0 | 32.967 | 31.11 | 182.558 | 7.63 | 172.075 | 2255.97 | 25.9 | 47.172 | 6.37 | 1.338 | 4.446 | 8721.11 | 1.843 | 97.9 | 76.9 | 1466 | 23.59 | 5668.7 | 2860 | 2746.6 | 4078.7 | 1212.7 | 0.68519 | 5.784
2024-12-09 | 23:00 | Data | 0 | 33.405 | 31.238 | 182.604 | 7.63 | 172.21 | 2255.97 | 25.89 | 47.082 | 6.36 | 1.328 | 4.447 | 8712.07 | 1.87 | 97.9 | 77 | 1465 | 23.54 | 5662.8 | 2842.3 | 2753.2 | 4078 | 1212.7 | 0.67926 | 5.775
2024-12-09 | 23:00 | Data | 0 | 33.405 | 31.144 | 182.604 | 7.63 | 172.256 | 2255.97 | 25.89 | 47.082 | 6.37 | 1.331 | 4.445 | 8698.5 | 2.039 | 97.9 | 77 | 1465 | 23.54 | 5654 | 2844.1 | 2777.5 | 4097.6 | 1212.7 | 0.67648 | 5.777
2024-12-09 | 23:00 | Data | 0 | 32.953 | 31.15 | 182.513 | 7.63 | 172.12 | 2255.97 | 25.89 | 47.172 | 6.37 | 1.339 | 4.465 | 8703.03 | 1.87 | 97.9 | 76.9 | 1466 | 23.59 | 5657 | 2829.6 | 2734.2 | 4058.1 | 1212.7 | 0.6788 | 5.805
2024-12-09 | 23:00 | Data | 0 | 33.284 | 31.542 | 182.558 | 7.63 | 172.075 | 2256.87 | 25.89 | 47.082 | 6.37 | 1.33 | 4.46 | 8703.03 | 1.89 | 97.9 | 77 | 1466 | 23.54 | 5657 | 2825.1 | 2737 | 4055.8 | 1212.7 | 0.67924 | 5.79
2024-12-09 | 23:00 | Data | 0 | 32.926 | 31.11 | 182.468 | 7.64 | 172.03 | 2252.35 | 25.9 | 47.082 | 6.37 | 1.326 | 4.453 | 8703.03 | 1.836 | 97.9 | 77.1 | 1463 | 23.54 | 5657 | 2820.3 | 2736.1 | 4051.7 | 1212.7 | 0.67892 | 5.78
2024-12-09 | 23:00 | Data | 0 | 32.953 | 31.11 | 182.649 | 7.64 | 172.075 | 2252.35 | 25.89 | 47.082 | 6.37 | 1.328 | 4.444 | 8730.16 | 1.958 | 97.9 | 77 | 1464 | 23.54 | 5674.6 | 2834.1 | 2736.3 | 4072.5 | 1212.7 | 0.68102 | 5.771
2024-12-09 | 23:00 | Data | 0 | 33.034 | 31.225 | 182.468 | 7.63 | 172.12 | 2248.73 | 25.89 | 47.172 | 6.37 | 1.33 | 4.461 | 8734.68 | 1.857 | 97.9 | 77 | 1462 | 23.59 | 5677.5 | 2829.9 | 2736.4 | 4057.2 | 1212.7 | 0.68088 | 5.79
2024-12-09 | 23:00 | Data | 0 | 32.953 | 31.427 | 182.468 | 7.64 | 172.075 | 2249.64 | 25.89 | 47.082 | 6.37 | 1.331 | 4.43 | 8730.16 | 1.843 | 97.9 | 76.9 | 1462 | 23.54 | 5674.6 | 2838 | 2749.5 | 4070 | 1212.7 | 0.68074 | 5.762
2024-12-09 | 23:00 | Data | 0 | 33.129 | 31.333 | 182.558 | 7.63 | 172.075 | 2252.35 | 25.89 | 47.082 | 6.37 | 1.329 | 4.445 | 8730.16 | 1.904 | 97.9 | 77 | 1464 | 23.54 | 5674.6 | 2831.5 | 2747.6 | 4065.2 | 1212.7 | 0.6797 | 5.773
2024-12-09 | 23:00 | Data | 0 | 32.953 | 31.42 | 182.468 | 7.63 | 172.03 | 2251.45 | 25.89 | 47.172 | 6.37 | 1.342 | 4.461 | 8743.73 | 1.857 | 97.9 | 76.9 | 1463 | 23.59 | 5683.4 | 2824.7 | 2746.2 | 4062.1 | 1212.7 | 0.67847 | 5.804
2024-12-09 | 23:00 | Data | 0 | 32.96 | 31.11 | 182.513 | 7.63 | 172.12 | 2249.64 | 25.89 | 47.082 | 6.37 | 1.338 | 4.427 | 8748.25 | 1.843 | 97.9 | 76.8 | 1462 | 23.54 | 5686.4 | 2827.1 | 2754.2 | 4065.3 | 1212.7 | 0.67921 | 5.765
2024-12-09 | 23:00 | Data | 0 | 32.967 | 31.11 | 182.513 | 7.63 | 172.075 | 2249.64 | 25.89 | 47.172 | 6.37 | 1.337 | 4.422 | 8730.16 | 1.843 | 97.9 | 76.8 | 1462 | 23.54 | 5674.6 | 2832.7 | 2771.9 | 4081.6 | 1212.7 | 0.67807 | 5.759
2024-12-09 | 23:00 | Data | 0 | 33.183 | 31.245 | 182.604 | 7.64 | 172.075 | 2249.64 | 25.89 | 47.082 | 6.37 | 1.334 | 4.447 | 8743.73 | 1.769 | 97.9 | 76.9 | 1462 | 23.59 | 5683.4 | 2849.3 | 2766.5 | 4088.6 | 1212.7 | 0.67982 | 5.781
2024-12-09 | 23:01 | Data | 0 | 33.108 | 31.326 | 182.694 | 7.63 | 172.21 | 2248.73 | 25.89 | 47.172 | 6.37 | 1.332 | 4.443 | 8757.29 | 2.019 | 97.9 | 76.9 | 1462 | 23.54 | 5692.2 | 2834.8 | 2760.3 | 4080.7 | 1212.7 | 0.67704 | 5.777
2024-12-09 | 23:01 | Data | 0 | 33.169 | 31.339 | 182.513 | 7.64 | 172.12 | 2247.83 | 25.89 | 47.082 | 6.37 | 1.335 | 4.451 | 8752.77 | 1.85 | 97.9 | 76.9 | 1462 | 23.59 | 5689.3 | 2834.1 | 2772.6 | 4083.9 | 1212.7 | 0.67794 | 5.786
2024-12-09 | 23:01 | Data | 0 | 33.068 | 31.11 | 182.694 | 7.64 | 172.21 | 2249.64 | 25.89 | 47.082 | 6.37 | 1.338 | 4.46 | 8748.25 | 1.857 | 97.9 | 76.9 | 1462 | 23.54 | 5686.4 | 2837.7 | 2745.5 | 4069.9 | 1212.7 | 0.68096 | 5.798
2024-12-09 | 23:01 | Data | 0 | 33.115 | 31.123 | 182.513 | 7.64 | 172.03 | 2249.64 | 25.89 | 47.082 | 6.37 | 1.343 | 4.46 | 8757.29 | 2.039 | 97.9 | 76.8 | 1462 | 23.54 | 5692.2 | 2843.5 | 2772.1 | 4092.3 | 1212.7 | 0.67692 | 5.805
2024-12-09 | 23:01 | Data | 0 | 32.987 | 31.333 | 182.649 | 7.63 | 172.21 | 2246.93 | 25.89 | 47.172 | 6.37 | 1.337 | 4.467 | 8757.29 | 1.749 | 97.9 | 77 | 1461 | 23.54 | 5692.2 | 2839.9 | 2765.9 | 4084.6 | 1212.7 | 0.67893 | 5.806
2024-12-09 | 23:01 | Data | 0 | 32.98 | 31.117 | 182.604 | 7.63 | 172.12 | 2249.64 | 25.89 | 47.082 | 6.37 | 1.339 | 4.446 | 8757.29 | 2.012 | 97.9 | 76.9 | 1462 | 23.54 | 5692.2 | 2843.2 | 2758.5 | 4082.3 | 1212.7 | 0.67938 | 5.786
2024-12-09 | 23:01 | Data | 0 | 32.953 | 31.285 | 182.468 | 7.63 | 172.12 | 2248.73 | 25.89 | 47.172 | 6.37 | 1.342 | 4.473 | 8743.73 | 1.728 | 97.9 | 76.9 | 1462 | 23.59 | 5683.4 | 2836.2 | 2768.9 | 4083.5 | 1212.7 | 0.67682 | 5.814
2024-12-09 | 23:01 | Data | 0 | 33.318 | 31.339 | 182.785 | 7.63 | 172.21 | 2250.54 | 25.89 | 47.082 | 6.37 | 1.335 | 4.449 | 8757.29 | 1.647 | 97.9 | 76.9 | 1463 | 23.54 | 5692.2 | 2829.1 | 2756.7 | 4089.7 | 1212.7 | 0.67787 | 5.784
2024-12-09 | 23:01 | Data | 0 | 33.237 | 31.252 | 182.694 | 7.63 | 172.21 | 2248.73 | 25.89 | 47.082 | 6.37 | 1.327 | 4.439 | 8743.73 | 1.958 | 97.9 | 77 | 1462 | 23.54 | 5683.4 | 2827.3 | 2759.6 | 4069.3 | 1212.7 | 0.67873 | 5.766
2024-12-09 | 23:01 | Data | 0 | 32.973 | 31.501 | 182.604 | 7.63 | 172.075 | 2249.64 | 25.89 | 47.082 | 6.37 | 1.323 | 4.408 | 8748.25 | 1.674 | 97.9 | 76.9 | 1462 | 23.54 | 5686.4 | 2841.2 | 2773.5 | 4088.7 | 1212.7 | 0.67887 | 5.731
2024-12-09 | 23:01 | Data | 0 | 33.162 | 31.11 | 182.468 | 7.63 | 172.075 | 2252.35 | 25.89 | 47.172 | 6.36 | 1.335 | 4.396 | 8730.16 | 1.87 | 97.9 | 76.7 | 1464 | 23.59 | 5674.6 | 2836.5 | 2769.7 | 4085.6 | 1212.7 | 0.67672 | 5.732
2024-12-09 | 23:01 | Data | 0 | 32.953 | 31.11 | 182.423 | 7.63 | 172.03 | 2252.35 | 25.89 | 47.082 | 6.37 | 1.341 | 4.446 | 8730.16 | 1.843 | 97.9 | 76.8 | 1464 | 23.54 | 5674.6 | 2836.9 | 2744.1 | 4067.1 | 1212.7 | 0.68005 | 5.788
2024-12-09 | 23:01 | Data | 0 | 33.223 | 31.164 | 182.558 | 7.63 | 172.075 | 2252.35 | 25.89 | 47.082 | 6.37 | 1.341 | 4.459 | 8743.73 | 1.863 | 97.9 | 76.9 | 1463 | 23.59 | 5683.4 | 2835.6 | 2769.9 | 4086.2 | 1212.7 | 0.67717 | 5.799
2024-12-09 | 23:01 | Data | 0 | 33.075 | 31.123 | 182.694 | 7.63 | 172.12 | 2252.35 | 25.9 | 47.082 | 6.37 | 1.328 | 4.455 | 8730.16 | 1.87 | 97.9 | 77 | 1463 | 23.59 | 5674.6 | 2845 | 2779.8 | 4098.6 | 1212.7 | 0.67812 | 5.783
2024-12-09 | 23:01 | Data | 0 | 33.014 | 31.11 | 182.423 | 7.63 | 172.075 | 2249.64 | 25.89 | 47.082 | 6.37 | 1.329 | 4.481 | 8730.16 | 1.742 | 97.9 | 77.1 | 1462 | 23.54 | 5674.6 | 2832 | 2770.9 | 4081.5 | 1212.7 | 0.67735 | 5.809
2024-12-09 | 23:01 | Data | 0 | 33.014 | 31.11 | 182.558 | 7.63 | 172.21 | 2248.73 | 25.89 | 46.721 | 6.37 | 1.337 | 4.481 | 8743.73 | 1.85 | 97.9 | 77 | 1462 | 23.36 | 5683.4 | 2847.9 | 2758 | 4080.5 | 1212.7 | 0.67881 | 5.818
2024-12-09 | 23:01 | Data | 0 | 33.068 | 31.508 | 182.694 | 7.63 | 172.256 | 2250.54 | 25.89 | 47.082 | 6.37 | 1.328 | 4.451 | 8734.68 | 1.816 | 97.9 | 77 | 1463 | 23.59 | 5677.5 | 2837.1 | 2765.5 | 4081.9 | 1212.7 | 0.67839 | 5.779
2024-12-09 | 23:01 | Data | 0 | 33.405 | 31.144 | 182.604 | 7.63 | 172.256 | 2249.64 | 25.89 | 47.082 | 6.37 | 1.329 | 4.454 | 8734.68 | 2.059 | 97.9 | 77 | 1463 | 23.54 | 5677.5 | 2822 | 2766.5 | 4073 | 1212.7 | 0.67534 | 5.782
2024-12-09 | 23:02 | Data | 0 | 32.926 | 31.11 | 182.558 | 7.63 | 172.256 | 2252.35 | 25.89 | 46.811 | 6.37 | 1.329 | 4.44 | 8725.64 | 1.634 | 97.9 | 77 | 1464 | 23.36 | 5671.7 | 2823.2 | 2765.5 | 4071.7 | 1212.7 | 0.67595 | 5.768
2024-12-09 | 23:02 | Data | 0 | 33.169 | 31.319 | 182.468 | 7.63 | 172.03 | 2253.25 | 25.89 | 46.721 | 6.37 | 1.329 | 4.449 | 8725.64 | 1.863 | 97.9 | 77 | 1465 | 23.36 | 5671.7 | 2823.8 | 2786.2 | 4084.5 | 1212.7 | 0.67515 | 5.779
2024-12-09 | 23:02 | Data | 0 | 33.297 | 31.238 | 182.649 | 7.63 | 172.256 | 2252.35 | 25.89 | 46.811 | 6.37 | 1.338 | 4.438 | 8712.07 | 1.877 | 97.9 | 76.8 | 1463 | 23.41 | 5662.8 | 2830.5 | 2769.3 | 4085.5 | 1212.7 | 0.67428 | 5.777
2024-12-09 | 23:02 | Data | 0 | 33.108 | 31.333 | 182.604 | 7.63 | 172.12 | 2261.39 | 25.89 | 46.721 | 6.37 | 1.338 | 4.447 | 8716.59 | 1.85 | 97.9 | 76.9 | 1469 | 23.36 | 5665.8 | 2850.3 | 2777.9 | 4102.2 | 1212.7 | 0.67847 | 5.784
2024-12-09 | 23:02 | Data | 0 | 33.068 | 31.495 | 182.604 | 7.63 | 172.075 | 2257.77 | 25.89 | 46.811 | 6.37 | 1.331 | 4.449 | 8730.16 | 1.735 | 97.9 | 77 | 1468 | 23.41 | 5674.6 | 2830.5 | 2777 | 4088.4 | 1212.7 | 0.67537 | 5.78
2024-12-09 | 23:02 | Data | 0 | 32.987 | 31.312 | 182.604 | 7.63 | 172.256 | 2255.97 | 25.89 | 46.811 | 6.37 | 1.329 | 4.431 | 8734.68 | 1.735 | 97.9 | 76.9 | 1466 | 23.41 | 5677.5 | 2839.8 | 2804.5 | 4111.5 | 1212.7 | 0.67292 | 5.759
2024-12-09 | 23:02 | Data | 0 | 33.129 | 31.535 | 182.513 | 7.63 | 172.12 | 2255.97 | 25.89 | 46.721 | 6.37 | 1.334 | 4.434 | 8716.59 | 1.83 | 97.9 | 76.9 | 1466 | 23.41 | 5665.8 | 2853.6 | 2764.6 | 4094.3 | 1212.8 | 0.67997 | 5.768
2024-12-09 | 23:02 | Data | 0 | 33.264 | 31.117 | 182.604 | 7.63 | 172.12 | 2254.16 | 25.89 | 46.811 | 6.37 | 1.336 | 4.436 | 8712.07 | 1.863 | 97.9 | 76.9 | 1466 | 23.36 | 5662.8 | 2837.5 | 2771.2 | 4088 | 1212.8 | 0.67798 | 5.771
2024-12-09 | 23:02 | Data | 0 | 32.994 | 31.123 | 182.649 | 7.63 | 172.301 | 2258.68 | 25.9 | 46.721 | 6.37 | 1.332 | 4.43 | 8716.59 | 1.803 | 97.9 | 76.9 | 1468 | 23.32 | 5665.8 | 2813.2 | 2749.6 | 4057.4 | 1212.8 | 0.67566 | 5.762
2024-12-09 | 23:02 | Data | 0 | 33.405 | 31.036 | 182.513 | 7.63 | 172.21 | 2257.77 | 25.89 | 46.721 | 6.37 | 1.339 | 4.42 | 8703.03 | 1.944 | 97.9 | 76.8 | 1468 | 23.32 | 5657 | 2825.4 | 2746.6 | 4063.1 | 1212.8 | 0.67915 | 5.759
2024-12-09 | 23:02 | Data | 0 | 32.987 | 31.117 | 182.558 | 7.64 | 172.12 | 2258.68 | 25.89 | 46.811 | 6.37 | 1.334 | 4.436 | 8716.59 | 1.836 | 97.9 | 76.9 | 1468 | 23.41 | 5665.8 | 2826 | 2754.4 | 4068.1 | 1212.8 | 0.67804 | 5.77
2024-12-09 | 23:02 | Data | 0 | 33.183 | 31.137 | 182.513 | 7.63 | 172.03 | 2258.68 | 25.89 | 46.721 | 6.37 | 1.334 | 4.444 | 8730.16 | 2.025 | 97.9 | 76.9 | 1468 | 23.36 | 5674.6 | 2833.9 | 2751.5 | 4068.8 | 1212.8 | 0.6792 | 5.778
2024-12-09 | 23:02 | Data | 0 | 33.399 | 31.252 | 182.558 | 7.63 | 172.21 | 2257.77 | 25.89 | 47.172 | 6.37 | 1.329 | 4.432 | 8730.16 | 1.688 | 97.9 | 76.9 | 1468 | 23.54 | 5674.6 | 2823.3 | 2759.2 | 4066.4 | 1212.8 | 0.67856 | 5.762
2024-12-09 | 23:02 | Data | 0 | 32.967 | 31.11 | 182.513 | 7.63 | 172.03 | 2258.68 | 25.89 | 46.721 | 6.37 | 1.329 | 4.442 | 8743.73 | 1.843 | 97.9 | 77 | 1468 | 23.36 | 5683.4 | 2820.3 | 2747.1 | 4060.3 | 1212.8 | 0.67632 | 5.771
2024-12-09 | 23:02 | Data | 0 | 32.953 | 31.11 | 182.649 | 7.63 | 172.21 | 2255.97 | 25.89 | 46.721 | 6.37 | 1.334 | 4.46 | 8739.2 | 1.843 | 97.9 | 77 | 1467 | 23.36 | 5680.5 | 2846 | 2750.8 | 4073.9 | 1212.8 | 0.68195 | 5.794
2024-12-09 | 23:02 | Data | 0 | 33.081 | 31.164 | 182.649 | 7.63 | 172.12 | 2254.16 | 25.89 | 46.721 | 6.37 | 1.332 | 4.446 | 9186.9 | 1.83 | 97.9 | 76.9 | 1466 | 23.32 | 5971.5 | 2835.9 | 2743.2 | 4064.6 | 1212.8 | 0.68097 | 5.777
2024-12-09 | 23:02 | Data | 0 | 33.156 | 31.542 | 182.739 | 7.63 | 172.256 | 2255.97 | 25.89 | 46.811 | 6.37 | 1.336 | 4.448 | 8730.16 | 1.755 | 97.9 | 76.9 | 1466 | 23.36 | 5674.6 | 2812.2 | 2756.8 | 4067.8 | 1212.8 | 0.67625 | 5.784
2024-12-09 | 23:02 | Data | 0 | 33.021 | 31.117 | 182.694 | 7.63 | 172.301 | 2253.25 | 25.89 | 46.811 | 6.37 | 1.33 | 4.438 | 8721.11 | 1.857 | 97.9 | 76.9 | 1465 | 23.41 | 5668.7 | 2836.8 | 2777.9 | 4092.7 | 1212.8 | 0.67584 | 5.771
2024-12-09 | 23:03 | Data | 0 | 32.96 | 31.11 | 182.604 | 7.63 | 172.075 | 2255.97 | 25.89 | 46.811 | 6.37 | 1.33 | 4.44 | 8721.11 | 1.843 | 97.9 | 76.9 | 1466 | 23.41 | 5668.7 | 2860 | 2786.2 | 4106.2 | 1212.8 | 0.6792 | 5.771
2024-12-09 | 23:03 | Data | 0 | 33.183 | 31.285 | 182.604 | 7.63 | 172.075 | 2254.16 | 25.89 | 46.811 | 6.37 | 1.32 | 4.431 | 8721.11 | 1.89 | 97.9 | 77 | 1465 | 23.41 | 5668.7 | 2827.7 | 2767.5 | 4081 | 1212.8 | 0.67485 | 5.752
2024-12-09 | 23:03 | Data | 0 | 32.96 | 31.218 | 182.558 | 7.63 | 172.12 | 2255.97 | 25.9 | 46.721 | 6.37 | 1.322 | 4.459 | 8716.59 | 1.958 | 97.9 | 77.1 | 1466 | 23.36 | 5665.8 | 2849.9 | 2761 | 4088.9 | 1212.8 | 0.67986 | 5.782
2024-12-09 | 23:03 | Data | 0 | 33.223 | 31.123 | 182.694 | 7.63 | 172.301 | 2255.97 | 25.9 | 47.353 | 6.37 | 1.335 | 4.451 | 8721.11 | 1.89 | 97.9 | 76.9 | 1465 | 23.63 | 5668.7 | 2844.1 | 2784.9 | 4102 | 1212.8 | 0.67616 | 5.785
2024-12-09 | 23:03 | Data | 0 | 33.169 | 31.312 | 182.604 | 7.63 | 172.12 | 2254.16 | 25.89 | 46.811 | 6.37 | 1.331 | 4.437 | 8725.64 | 1.897 | 97.9 | 76.9 | 1466 | 23.41 | 5671.7 | 2824.3 | 2769.8 | 4079.3 | 1212.8 | 0.67515 | 5.768
2024-12-09 | 23:03 | Data | 0 | 33.129 | 31.508 | 182.604 | 7.63 | 172.256 | 2255.97 | 25.89 | 46.811 | 6.37 | 1.327 | 4.435 | 8703.03 | 1.722 | 97.9 | 77 | 1467 | 23.41 | 5657 | 2820.6 | 2771.7 | 4077.7 | 1212.8 | 0.67579 | 5.761
2024-12-09 | 23:03 | Data | 0 | 33.189 | 31.225 | 182.558 | 7.63 | 172.256 | 2249.64 | 25.89 | 46.721 | 6.37 | 1.335 | 4.446 | 8707.55 | 1.843 | 97.9 | 76.9 | 1462 | 23.41 | 5659.9 | 2816.3 | 2745.7 | 4061 | 1212.8 | 0.67582 | 5.781
2024-12-09 | 23:03 | Data | 0 | 33.183 | 31.123 | 182.604 | 7.63 | 172.256 | 2249.64 | 25.89 | 46.721 | 6.37 | 1.334 | 4.44 | 8703.03 | 2.059 | 97.9 | 76.9 | 1462 | 23.36 | 5657 | 2807.6 | 2763.6 | 4062.1 | 1212.8 | 0.67584 | 5.772
2024-12-09 | 23:03 | Data | 0 | 32.953 | 31.069 | 182.468 | 7.63 | 172.075 | 2251.45 | 25.89 | 46.721 | 6.37 | 1.34 | 4.446 | 8716.59 | 1.998 | 97.9 | 76.8 | 1464 | 23.41 | 5665.8 | 2831 | 2761.4 | 4077.4 | 1212.8 | 0.67652 | 5.786
2024-12-09 | 23:03 | Data | 0 | 33.129 | 31.333 | 182.649 | 7.63 | 172.075 | 2252.35 | 25.89 | 46.811 | 6.37 | 1.329 | 4.441 | 8707.55 | 1.836 | 97.9 | 77 | 1464 | 23.41 | 5659.9 | 2851.3 | 2790.7 | 4109.3 | 1212.8 | 0.67657 | 5.77
2024-12-09 | 23:03 | Data | 0 | 32.953 | 31.123 | 182.739 | 7.63 | 172.301 | 2252.35 | 25.89 | 46.721 | 6.37 | 1.329 | 4.419 | 8689.46 | 2.005 | 97.9 | 76.9 | 1464 | 23.41 | 5648.1 | 2818.6 | 2765 | 4070.2 | 1212.8 | 0.67413 | 5.748
2024-12-09 | 23:03 | Data | 0 | 33.345 | 31.4 | 182.558 | 7.63 | 172.12 | 2248.73 | 25.89 | 46.721 | 6.37 | 1.321 | 4.429 | 8693.98 | 1.944 | 97.9 | 77 | 1462 | 23.36 | 5651.1 | 2825.6 | 2762.7 | 4059.8 | 1212.8 | 0.6759 | 5.751
2024-12-09 | 23:03 | Data | 0 | 32.96 | 31.285 | 182.785 | 7.63 | 172.256 | 2249.64 | 25.89 | 46.721 | 6.37 | 1.33 | 4.48 | 8693.98 | 1.951 | 97.9 | 77.1 | 1463 | 23.36 | 5651.1 | 2831.2 | 2762.5 | 4077.5 | 1212.8 | 0.67669 | 5.81
2024-12-09 | 23:03 | Data | 0 | 33.183 | 31.454 | 182.694 | 7.63 | 172.301 | 2249.64 | 25.89 | 46.811 | 6.37 | 1.334 | 4.471 | 8517.61 | 1.843 | 97.9 | 77 | 1462 | 23.36 | 5536.4 | 2834.3 | 2751.7 | 4072.2 | 1212.8 | 0.67891 | 5.804
2024-12-09 | 23:03 | Data | 0 | 32.973 | 31.157 | 182.604 | 7.63 | 172.21 | 2249.64 | 25.89 | 46.721 | 6.37 | 1.328 | 4.455 | 8495 | 1.641 | 97.9 | 77 | 1462 | 23.36 | 5521.8 | 2827 | 2774.4 | 4080.6 | 1212.8 | 0.6748 | 5.783
2024-12-09 | 23:03 | Data | 0 | 33.068 | 31.117 | 182.694 | 7.63 | 172.256 | 2249.64 | 25.89 | 46.721 | 6.37 | 1.34 | 4.436 | 8476.91 | 1.843 | 97.9 | 76.8 | 1462 | 23.36 | 5510 | 2834.3 | 2760.5 | 4080.4 | 1212.8 | 0.67787 | 5.776
2024-12-09 | 23:03 | Data | 0 | 33.129 | 31.427 | 182.558 | 7.63 | 172.21 | 2249.64 | 25.9 | 46.721 | 6.37 | 1.329 | 4.46 | 8463.35 | 1.89 | 97.9 | 77 | 1462 | 23.36 | 5501.2 | 2840.5 | 2748.7 | 4072.2 | 1212.8 | 0.67951 | 5.789
2024-12-09 | 23:04 | Data | 0 | 33.27 | 31.177 | 182.558 | 7.63 | 172.12 | 2252.35 | 25.89 | 47.172 | 6.37 | 1.332 | 4.427 | 8648.76 | 2.059 | 97.9 | 76.9 | 1463 | 23.54 | 5621.7 | 2812 | 2752.9 | 4068.8 | 1212.8 | 0.67595 | 5.758
2024-12-09 | 23:04 | Data | 0 | 33.183 | 31.339 | 182.649 | 7.63 | 172.21 | 2255.97 | 25.89 | 47.082 | 6.37 | 1.33 | 4.436 | 8680.41 | 1.843 | 97.9 | 76.9 | 1465 | 23.54 | 5642.3 | 2821.6 | 2780.3 | 4081.9 | 1212.8 | 0.67315 | 5.766
2024-12-09 | 23:04 | Data | 0 | 32.967 | 31.312 | 182.468 | 7.63 | 172.12 | 2255.97 | 25.89 | 46.721 | 6.37 | 1.329 | 4.44 | 8680.41 | 1.735 | 97.9 | 77 | 1465 | 23.41 | 5642.3 | 2023.1 | 2611.9 | 3322.2 | 1212.8 | 0.61602 | 5.77
2024-12-09 | 23:04 | Data | 0 | 32.987 | 31.231 | 182.513 | 7.63 | 172.12 | 2258.68 | 25.89 | 47.172 | 6.37 | 1.335 | 4.462 | 8693.98 | 1.843 | 97.9 | 77 | 1467 | 23.59 | 5651.1 | 1729.5 | 2193.7 | 2806.4 | 1212.8 | 0.61405 | 5.797
2024-12-09 | 23:04 | Data | 0 | 33.297 | 31.346 | 182.83 | 7.63 | 172.301 | 2255.97 | 25.89 | 47.082 | 6.37 | 1.329 | 4.458 | 8693.98 | 1.87 | 97.9 | 77 | 1466 | 23.59 | 5651.1 | 1754.4 | 2186.4 | 2825.4 | 1212.8 | 0.61977 | 5.788
2024-12-09 | 23:04 | Data | 0 | 33.007 | 31.117 | 182.423 | 7.63 | 172.075 | 2255.97 | 25.89 | 46.721 | 6.37 | 1.337 | 4.465 | 8698.5 | 1.843 | 97.9 | 77 | 1466 | 23.36 | 5654 | 1753.6 | 2191.9 | 2820.8 | 1212.8 | 0.62 | 5.8
2024-12-09 | 23:04 | Data | 0 | 32.967 | 31.501 | 182.739 | 7.63 | 172.301 | 2252.35 | 25.89 | 46.63 | 6.37 | 1.331 | 4.425 | 8689.46 | 1.843 | 97.9 | 76.9 | 1464 | 23.36 | 5648.1 | 1744.9 | 2183.4 | 2807 | 1212.8 | 0.61858 | 5.756
2024-12-09 | 23:04 | Data | 0 | 33.297 | 31.144 | 182.649 | 7.64 | 172.256 | 2258.68 | 25.89 | 46.991 | 6.37 | 1.337 | 4.406 | 8698.5 | 1.877 | 97.9 | 76.7 | 1468 | 23.54 | 5654 | 1755.5 | 2195.4 | 2824.1 | 1212.8 | 0.6187 | 5.742
2024-12-09 | 23:04 | Data | 0 | 33.264 | 31.137 | 182.604 | 7.63 | 172.12 | 2258.68 | 25.88 | 46.811 | 6.37 | 1.328 | 4.437 | 8698.5 | 2.208 | 97.9 | 77 | 1468 | 23.41 | 5654 | 1746.3 | 2190.9 | 2813.8 | 1212.8 | 0.61818 | 5.764
2024-12-09 | 23:04 | Data | 0 | 33.237 | 31.225 | 182.694 | 7.63 | 172.256 | 2253.25 | 25.89 | 47.172 | 6.36 | 1.331 | 4.434 | 8721.11 | 1.728 | 97.9 | 76.9 | 1465 | 23.54 | 5668.7 | 1752.8 | 2215.2 | 2836.9 | 1212.8 | 0.61759 | 5.765
2024-12-09 | 23:04 | Data | 0 | 33.189 | 31.339 | 182.649 | 7.63 | 172.12 | 2252.35 | 25.88 | 46.721 | 6.37 | 1.326 | 4.413 | 8712.07 | 1.85 | 97.9 | 76.9 | 1464 | 23.36 | 5662.8 | 1743.5 | 2217.2 | 2844.9 | 1212.8 | 0.61418 | 5.739
2024-12-09 | 23:04 | Data | 0 | 33.176 | 31.137 | 182.513 | 7.63 | 172.12 | 2252.35 | 25.88 | 46.811 | 6.37 | 1.33 | 4.426 | 8703.03 | 1.87 | 97.9 | 76.9 | 1464 | 23.41 | 5657 | 1743.7 | 2200.9 | 2817.8 | 1212.8 | 0.61654 | 5.755
2024-12-09 | 23:04 | Data | 0 | 32.994 | 31.285 | 182.649 | 7.63 | 172.256 | 2252.35 | 25.89 | 47.082 | 6.37 | 1.332 | 4.422 | 8734.68 | 1.971 | 97.9 | 76.8 | 1464 | 23.5 | 5677.5 | 1726.3 | 2190.8 | 2801.6 | 1212.9 | 0.61343 | 5.757
2024-12-09 | 23:04 | Data | 0 | 33.021 | 31.326 | 182.558 | 7.63 | 172.256 | 2205.35 | 25.88 | 47.082 | 6.37 | 1.329 | 4.44 | 8703.03 | 1.634 | 97.9 | 77 | 1432 | 23.59 | 5657 | 1737.7 | 2222.1 | 2833.8 | 1212.9 | 0.61099 | 5.767
2024-12-09 | 23:04 | Data | 0 | 32.94 | 31.285 | 182.513 | 7.63 | 172.03 | 2197.22 | 25.89 | 47.172 | 6.37 | 1.32 | 4.439 | 8716.59 | 2.012 | 97.9 | 77.1 | 1428 | 23.54 | 5665.8 | 1756.6 | 2195.1 | 2824.3 | 1212.9 | 0.61791 | 5.76
2024-12-09 | 23:04 | Data | 0 | 33.439 | 31.366 | 182.649 | 7.63 | 172.301 | 2197.22 | 25.88 | 47.082 | 6.37 | 1.329 | 4.437 | 8716.59 | 1.85 | 97.9 | 77 | 1428 | 23.59 | 5665.8 | 1761.9 | 2212.9 | 2840.8 | 1212.9 | 0.61511 | 5.766
2024-12-09 | 23:04 | Data | 0 | 33.459 | 31.184 | 182.649 | 7.63 | 172.301 | 2194.5 | 25.88 | 47.082 | 6.37 | 1.332 | 4.429 | 8721.11 | 1.931 | 97.9 | 76.9 | 1426 | 23.54 | 5668.7 | 1753.1 | 2211.3 | 2833.9 | 1212.9 | 0.61585 | 5.762
2024-12-09 | 23:05 | Data | 0 | 33.183 | 31.387 | 182.649 | 7.63 | 172.256 | 2249.64 | 25.88 | 47.082 | 6.37 | 1.335 | 4.423 | 8712.07 | 1.917 | 97.9 | 76.8 | 1462 | 23.54 | 5662.8 | 1732.7 | 2179.2 | 2797.5 | 1212.9 | 0.6166 | 5.757
2024-12-09 | 23:05 | Data | 0 | 32.967 | 31.11 | 182.558 | 7.63 | 172.075 | 2249.64 | 25.88 | 47.082 | 6.37 | 1.328 | 4.461 | 8730.16 | 1.843 | 97.9 | 77.1 | 1462 | 23.54 | 5674.6 | 1761.8 | 2196.9 | 2823 | 1212.9 | 0.62355 | 5.789
2024-12-09 | 23:05 | Data | 0 | 33.068 | 31.069 | 182.558 | 7.63 | 172.21 | 2249.64 | 25.89 | 47.172 | 6.38 | 1.334 | 4.445 | 8734.68 | 1.769 | 97.9 | 76.9 | 1462 | 23.59 | 5677.5 | 1740.3 | 2183.2 | 2805.8 | 1212.9 | 0.61825 | 5.779
2024-12-09 | 23:05 | Data | 0 | 33.446 | 31.366 | 182.649 | 7.64 | 172.256 | 2249.64 | 25.89 | 47.082 | 6.37 | 1.346 | 4.425 | 8730.16 | 1.958 | 97.9 | 76.7 | 1462 | 23.54 | 5674.6 | 1743.2 | 2175.9 | 2800 | 1212.9 | 0.61765 | 5.771
2024-12-09 | 23:05 | Data | 0 | 33.129 | 31.225 | 182.468 | 7.63 | 172.12 | 2247.83 | 25.89 | 47.172 | 6.38 | 1.329 | 4.447 | 8734.68 | 1.83 | 97.9 | 77 | 1461 | 23.54 | 5677.5 | 1756.8 | 2176.9 | 2810.5 | 1212.9 | 0.62173 | 5.777
2024-12-09 | 23:05 | Data | 0 | 32.953 | 31.285 | 182.604 | 7.63 | 172.21 | 2249.64 | 25.88 | 47.082 | 6.37 | 1.33 | 4.458 | 8725.64 | 1.843 | 97.9 | 77 | 1462 | 23.54 | 5671.7 | 1748 | 2184.7 | 2811.4 | 1212.9 | 0.61649 | 5.789
2024-12-09 | 23:05 | Data | 0 | 33.392 | 31.393 | 182.785 | 7.63 | 172.256 | 2249.64 | 25.89 | 47.172 | 6.37 | 1.329 | 4.409 | 8721.11 | 1.85 | 97.9 | 76.8 | 1462 | 23.59 | 5668.7 | 1752.9 | 2188.7 | 2812.7 | 1212.9 | 0.6191 | 5.74
2024-12-09 | 23:05 | Data | 0 | 33.081 | 31.117 | 182.513 | 7.63 | 172.21 | 2248.73 | 25.89 | 47.082 | 6.37 | 1.335 | 4.422 | 8716.59 | 1.87 | 97.9 | 76.8 | 1462 | 23.54 | 5665.8 | 1751.6 | 2204.2 | 2826.4 | 1212.9 | 0.61792 | 5.759
2024-12-09 | 23:05 | Data | 0 | 33.196 | 31.123 | 182.558 | 7.63 | 172.21 | 2249.64 | 25.89 | 47.082 | 6.37 | 1.334 | 4.461 | 8712.07 | 1.87 | 97.9 | 77 | 1463 | 23.54 | 5662.8 | 1744.3 | 2177 | 2804.5 | 1212.9 | 0.61907 | 5.795
2024-12-09 | 23:05 | Data | 0 | 32.784 | 31.103 | 182.513 | 7.63 | 172.256 | 2248.73 | 25.88 | 47.172 | 6.37 | 1.331 | 4.465 | 8716.59 | 1.668 | 97.9 | 77 | 1462 | 23.59 | 5665.8 | 1752.6 | 2195.2 | 2822.3 | 1212.9 | 0.61801 | 5.797
2024-12-09 | 23:05 | Data | 0 | 33.156 | 31.326 | 182.513 | 7.63 | 172.03 | 2249.64 | 25.88 | 47.082 | 6.37 | 1.327 | 4.429 | 8721.11 | 1.85 | 97.9 | 77 | 1462 | 23.54 | 5668.7 | 1750.6 | 2183.6 | 2812 | 1212.9 | 0.61787 | 5.756
2024-12-09 | 23:05 | Data | 0 | 33.183 | 31.164 | 182.694 | 7.63 | 172.301 | 2249.64 | 25.88 | 47.082 | 6.37 | 1.329 | 4.421 | 8730.16 | 1.85 | 97.9 | 76.9 | 1462 | 23.54 | 5674.6 | 1755.3 | 2187.1 | 2818.7 | 1212.9 | 0.61788 | 5.748
2024-12-09 | 23:05 | Data | 0 | 32.953 | 31.441 | 182.604 | 7.63 | 172.075 | 2249.64 | 25.89 | 47.172 | 6.37 | 1.339 | 4.444 | 8721.11 | 1.816 | 97.9 | 76.8 | 1462 | 23.54 | 5668.7 | 1762.2 | 2200.5 | 2829.5 | 1212.9 | 0.62063 | 5.781
2024-12-09 | 23:05 | Data | 0 | 32.926 | 31.393 | 182.513 | 7.63 | 172.03 | 2248.73 | 25.89 | 47.082 | 6.37 | 1.334 | 4.446 | 8743.73 | 1.897 | 97.9 | 76.9 | 1462 | 23.54 | 5683.4 | 1777.4 | 2209.6 | 2845.6 | 1212.9 | 0.62254 | 5.78
2024-12-09 | 23:05 | Data | 0 | 33.156 | 31.339 | 182.739 | 7.63 | 172.21 | 2249.64 | 25.88 | 46.811 | 6.37 | 1.325 | 4.408 | 8725.64 | 1.836 | 97.9 | 76.9 | 1462 | 23.36 | 5671.7 | 1751.5 | 2174.5 | 2803.5 | 1212.9 | 0.61949 | 5.733
2024-12-09 | 23:05 | Data | 0 | 33.068 | 31.535 | 182.558 | 7.63 | 172.12 | 2248.73 | 25.89 | 46.721 | 6.37 | 1.314 | 4.418 | 8707.55 | 1.843 | 97.9 | 77.1 | 1462 | 23.32 | 5659.9 | 1758.1 | 2192.7 | 2823.6 | 1212.9 | 0.62036 | 5.731
2024-12-09 | 23:05 | Data | 0 | 33.25 | 31.144 | 182.558 | 7.63 | 172.21 | 2249.64 | 25.88 | 47.082 | 6.37 | 1.322 | 4.455 | 8721.11 | 1.85 | 97.9 | 77.1 | 1462 | 23.54 | 5668.7 | 1739.2 | 2162.5 | 2788.3 | 1212.9 | 0.62183 | 5.777
2024-12-09 | 23:06 | Data | 0 | 32.953 | 31.11 | 182.604 | 7.63 | 172.12 | 2245.12 | 25.88 | 47.172 | 6.37 | 1.334 | 4.456 | 8721.11 | 1.843 | 97.9 | 77 | 1459 | 23.54 | 5668.7 | 1755.4 | 2176.5 | 2808.3 | 1212.9 | 0.62229 | 5.791
2024-12-09 | 23:06 | Data | 0 | 33.156 | 31.312 | 182.694 | 7.63 | 172.12 | 2252.35 | 25.88 | 47.082 | 6.37 | 1.33 | 4.429 | 8703.03 | 1.654 | 97.9 | 76.9 | 1464 | 23.54 | 5657 | 1742.2 | 2184.6 | 2807.3 | 1212.9 | 0.61786 | 5.761
2024-12-09 | 23:06 | Data | 0 | 33.183 | 31.339 | 182.558 | 7.63 | 172.256 | 2252.35 | 25.89 | 46.721 | 6.37 | 1.336 | 4.425 | 8730.16 | 1.843 | 97.9 | 76.8 | 1463 | 23.41 | 5674.6 | 1741.7 | 2175.1 | 2827 | 1212.9 | 0.61746 | 5.761
2024-12-09 | 23:06 | Data | 0 | 33.156 | 31.137 | 182.513 | 7.63 | 172.12 | 2255.97 | 25.89 | 46.721 | 6.37 | 1.327 | 4.453 | 8716.59 | 1.958 | 97.9 | 77 | 1466 | 23.36 | 5665.8 | 1739 | 2206.5 | 2822.5 | 1212.9 | 0.61352 | 5.78
2024-12-09 | 23:06 | Data | 0 | 33.196 | 31.117 | 182.649 | 7.63 | 172.256 | 2255.97 | 25.88 | 47.082 | 6.37 | 1.328 | 4.454 | 8716.59 | 1.843 | 97.9 | 77 | 1465 | 23.54 | 5665.8 | 1732.5 | 2192.5 | 2807 | 1212.9 | 0.61429 | 5.78
2024-12-09 | 23:06 | Data | 0 | 32.98 | 31.13 | 182.558 | 7.63 | 172.03 | 2255.97 | 25.89 | 46.721 | 6.37 | 1.329 | 4.46 | 8712.07 | 1.762 | 97.9 | 77 | 1466 | 23.36 | 5662.8 | 1740.5 | 2186 | 2813.5 | 1212.9 | 0.61883 | 5.789
2024-12-09 | 23:06 | Data | 0 | 32.75 | 31.103 | 182.604 | 7.63 | 172.12 | 2254.16 | 25.88 | 47.082 | 6.37 | 1.342 | 4.441 | 8716.59 | 1.647 | 97.9 | 76.8 | 1466 | 23.59 | 5665.8 | 1770.1 | 2200.8 | 2834.8 | 1212.9 | 0.62233 | 5.784
2024-12-09 | 23:06 | Data | 0 | 32.953 | 31.11 | 182.513 | 7.63 | 172.075 | 2255.97 | 25.89 | 47.082 | 6.37 | 1.335 | 4.432 | 8707.55 | 1.843 | 97.9 | 76.9 | 1466 | 23.59 | 5659.9 | 1746 | 2181.6 | 2807.9 | 1212.9 | 0.619 | 5.767
2024-12-09 | 23:06 | Data | 0 | 32.98 | 31.279 | 182.558 | 7.63 | 172.075 | 2254.16 | 25.88 | 47.443 | 6.37 | 1.326 | 4.447 | 8703.03 | 1.674 | 97.9 | 77 | 1465 | 23.68 | 5657 | 1759.3 | 2170.2 | 2805 | 1212.9 | 0.62446 | 5.774
2024-12-09 | 23:06 | Data | 0 | 32.838 | 30.934 | 182.513 | 7.63 | 172.075 | 2252.35 | 25.88 | 47.082 | 6.37 | 1.33 | 4.455 | 8703.03 | 1.985 | 97.9 | 77 | 1464 | 23.59 | 5657 | 1758.3 | 2192 | 2814.1 | 1212.9 | 0.6171 | 5.786
2024-12-09 | 23:06 | Data | 0 | 32.845 | 31.083 | 182.468 | 7.63 | 172.12 | 2248.73 | 25.89 | 47.172 | 6.37 | 1.331 | 4.434 | 8739.2 | 1.742 | 97.9 | 76.9 | 1462 | 23.54 | 5680.5 | 1746.6 | 2181.1 | 2801.1 | 1212.9 | 0.61732 | 5.765
2024-12-09 | 23:06 | Data | 0 | 32.852 | 31.11 | 182.513 | 7.63 | 172.21 | 2250.54 | 25.89 | 47.172 | 6.37 | 1.332 | 4.436 | 8743.73 | 1.647 | 97.9 | 76.9 | 1462 | 23.54 | 5683.4 | 1745.4 | 2197.6 | 2819.4 | 1212.9 | 0.61609 | 5.768
2024-12-09 | 23:06 | Data | 0 | 32.784 | 30.894 | 182.468 | 7.63 | 172.075 | 2249.64 | 25.88 | 47.172 | 6.37 | 1.328 | 4.428 | 8748.25 | 1.823 | 97.9 | 76.9 | 1462 | 23.59 | 5686.4 | 1763.4 | 2209.3 | 2839.6 | 1212.9 | 0.61894 | 5.756
2024-12-09 | 23:06 | Data | 0 | 33.156 | 31.117 | 182.468 | 7.63 | 172.03 | 2255.97 | 25.88 | 47.172 | 6.37 | 1.334 | 4.456 | 8734.68 | 2.046 | 97.9 | 77 | 1465 | 23.59 | 5677.5 | 1759.3 | 2205.2 | 2833.9 | 1212.9 | 0.61854 | 5.789
2024-12-09 | 23:06 | Data | 0 | 33.122 | 31.319 | 182.513 | 7.63 | 172.03 | 2249.64 | 25.88 | 47.172 | 6.37 | 1.329 | 4.452 | 8716.59 | 1.904 | 97.9 | 77 | 1462 | 23.54 | 5665.8 | 1757 | 2175.7 | 2807.9 | 1212.9 | 0.62365 | 5.781
2024-12-09 | 23:06 | Data | 0 | 32.967 | 31.056 | 182.513 | 7.63 | 172.075 | 2249.64 | 25.89 | 47.082 | 6.37 | 1.339 | 4.437 | 8707.55 | 1.843 | 97.9 | 76.8 | 1462 | 23.54 | 5659.9 | 1761.7 | 2183.3 | 2819.6 | 1212.9 | 0.62265 | 5.778
2024-12-09 | 23:06 | Data | 0 | 32.953 | 31.312 | 182.558 | 7.63 | 172.03 | 2249.64 | 25.88 | 47.172 | 6.37 | 1.329 | 4.446 | 8716.59 | 1.843 | 97.9 | 77 | 1462 | 23.59 | 5665.8 | 1754.3 | 2178.7 | 2808.6 | 1212.9 | 0.62218 | 5.775
2024-12-09 | 23:06 | Data | 0 | 32.98 | 31.225 | 182.558 | 7.63 | 172.12 | 2249.64 | 25.88 | 47.172 | 6.37 | 1.337 | 4.434 | 8689.46 | 1.85 | 97.9 | 76.8 | 1462 | 23.59 | 5648.1 | 1768.8 | 2183.9 | 2822.5 | 1212.9 | 0.62431 | 5.771
2024-12-09 | 23:07 | Data | 0 | 33.169 | 31.225 | 182.513 | 7.63 | 172.03 | 2249.64 | 25.88 | 47.082 | 6.37 | 1.335 | 4.407 | 8707.55 | 1.857 | 97.9 | 76.8 | 1463 | 23.54 | 5659.9 | 1748.9 | 2162.2 | 2794.8 | 1212.9 | 0.62331 | 5.742
2024-12-09 | 23:07 | Data | 0 | 32.953 | 31.177 | 182.513 | 7.63 | 172.075 | 2252.35 | 25.88 | 47.082 | 6.37 | 1.329 | 4.421 | 8703.03 | 2.046 | 97.9 | 76.9 | 1463 | 23.54 | 5657 | 3035.7 | 3365.1 | 4652.1 | 1212.9 | 0.63352 | 5.751
2024-12-09 | 23:07 | Data | 0 | 32.953 | 31.11 | 182.604 | 7.63 | 172.21 | 2257.77 | 25.88 | 47.082 | 6.37 | 1.332 | 4.437 | 8680.41 | 1.668 | 97.9 | 76.9 | 1468 | 23.54 | 5642.3 | 2837.7 | 2771.3 | 4088.1 | 1212.9 | 0.67881 | 5.768
2024-12-09 | 23:07 | Data | 0 | 32.879 | 30.941 | 182.558 | 7.63 | 172.12 | 2252.35 | 25.88 | 47.082 | 6.37 | 1.339 | 4.458 | 8671.37 | 1.803 | 97.9 | 76.9 | 1463 | 23.54 | 5636.4 | 2833.1 | 2778.7 | 4093.8 | 1212.9 | 0.67562 | 5.799
2024-12-09 | 23:07 | Data | 0 | 32.953 | 31.11 | 182.558 | 7.63 | 172.12 | 2252.35 | 25.88 | 47.082 | 6.37 | 1.329 | 4.465 | 8671.37 | 1.843 | 97.9 | 77.1 | 1464 | 23.59 | 5636.4 | 2816.9 | 2759.5 | 4067.2 | 1212.9 | 0.67588 | 5.794
2024-12-09 | 23:07 | Data | 0 | 33.183 | 31.11 | 182.558 | 7.63 | 172.21 | 2246.93 | 25.88 | 47.082 | 6.37 | 1.321 | 4.448 | 8680.41 | 1.951 | 97.9 | 77.1 | 1461 | 23.54 | 5642.3 | 2815.9 | 2772.2 | 4080 | 1212.9 | 0.67493 | 5.769
2024-12-09 | 23:07 | Data | 0 | 32.953 | 31.123 | 182.468 | 7.63 | 171.984 | 2249.64 | 25.88 | 47.082 | 6.37 | 1.32 | 4.446 | 8680.41 | 1.796 | 97.9 | 77.1 | 1462 | 23.54 | 5642.3 | 2834.4 | 2760.6 | 4078.5 | 1212.9 | 0.67704 | 5.764
2024-12-09 | 23:07 | Data | 0 | 32.838 | 31.211 | 182.468 | 7.63 | 172.075 | 2249.64 | 25.88 | 47.353 | 6.37 | 1.339 | 4.448 | 8693.98 | 1.911 | 97.9 | 76.9 | 1462 | 23.68 | 5651.1 | 2823.8 | 2766.9 | 4077.1 | 1212.9 | 0.67589 | 5.788
2024-12-09 | 23:07 | Data | 0 | 32.953 | 31.441 | 182.558 | 7.63 | 172.21 | 2244.22 | 25.86 | 47.172 | 6.37 | 1.342 | 4.439 | 8684.94 | 1.843 | 97.9 | 76.8 | 1459 | 23.59 | 5645.2 | 2810.8 | 2747.4 | 4053.3 | 1212.9 | 0.6773 | 5.78
2024-12-09 | 23:07 | Data | 0 | 32.953 | 31.333 | 182.513 | 7.63 | 172.075 | 2249.64 | 25.88 | 47.082 | 6.37 | 1.349 | 4.428 | 8689.46 | 1.742 | 97.9 | 76.6 | 1462 | 23.54 | 5648.1 | 2835.6 | 2769.1 | 4085.2 | 1212.9 | 0.67647 | 5.778
2024-12-09 | 23:07 | Data | 0 | 33.027 | 31.117 | 182.513 | 7.63 | 172.12 | 2249.64 | 25.89 | 46.721 | 6.37 | 1.336 | 4.44 | 8693.98 | 1.674 | 97.9 | 76.9 | 1462 | 23.36 | 5651.1 | 2830.8 | 2788.4 | 4093 | 1212.9 | 0.67712 | 5.777
2024-12-09 | 23:07 | Data | 0 | 32.777 | 31.056 | 182.423 | 7.63 | 172.075 | 2246.02 | 25.89 | 46.63 | 6.37 | 1.326 | 4.412 | 8693.98 | 1.735 | 97.9 | 76.9 | 1460 | 23.32 | 5651.1 | 2843 | 2759.3 | 4077.4 | 1212.9 | 0.67996 | 5.738
2024-12-09 | 23:07 | Data | 0 | 32.953 | 31.09 | 182.377 | 7.63 | 171.984 | 2255.97 | 25.88 | 46.721 | 6.37 | 1.324 | 4.432 | 8693.98 | 1.931 | 97.9 | 77 | 1466 | 23.36 | 5651.1 | 2833.6 | 2771.1 | 4086.1 | 1213 | 0.67648 | 5.756
2024-12-09 | 23:07 | Data | 0 | 32.967 | 31.056 | 182.423 | 7.63 | 172.075 | 2254.16 | 25.85 | 46.721 | 6.37 | 1.327 | 4.453 | 8703.03 | 2.059 | 97.9 | 77 | 1465 | 23.36 | 5657 | 2837.4 | 2747.8 | 4068.6 | 1213 | 0.68133 | 5.781
2024-12-09 | 23:07 | Data | 0 | 32.96 | 31.164 | 182.468 | 7.63 | 172.075 | 2259.58 | 25.86 | 46.721 | 6.37 | 1.329 | 4.455 | 8707.55 | 1.789 | 97.9 | 77 | 1468 | 23.41 | 5659.9 | 2838.2 | 2767.5 | 4086.1 | 1213 | 0.67517 | 5.783
2024-12-09 | 23:07 | Data | 0 | 32.953 | 31.211 | 182.604 | 7.63 | 172.21 | 2257.77 | 25.85 | 46.811 | 6.37 | 1.331 | 4.446 | 8703.03 | 1.924 | 97.9 | 77 | 1468 | 23.41 | 5657 | 2812.3 | 2755.1 | 4064 | 1213 | 0.67501 | 5.778
2024-12-09 | 23:07 | Data | 0 | 33.156 | 31.339 | 182.558 | 7.63 | 172.075 | 2257.77 | 25.85 | 46.721 | 6.37 | 1.335 | 4.424 | 8689.46 | 2.032 | 97.9 | 76.8 | 1468 | 23.41 | 5648.1 | 2826.7 | 2768.9 | 4080 | 1213 | 0.67553 | 5.759
2024-12-09 | 23:08 | Data | 0 | 33.196 | 31.117 | 182.513 | 7.63 | 172.12 | 2255.97 | 25.86 | 46.721 | 6.37 | 1.332 | 4.452 | 8657.8 | 1.863 | 97.9 | 77 | 1466 | 23.36 | 5627.6 | 2819.5 | 2755.9 | 4069.7 | 1213 | 0.67613 | 5.783
2024-12-09 | 23:08 | Data | 0 | 32.757 | 31.225 | 182.423 | 7.64 | 172.03 | 2255.97 | 25.86 | 46.721 | 6.37 | 1.332 | 4.429 | 8680.41 | 1.789 | 97.9 | 76.9 | 1465 | 23.36 | 5642.3 | 2819.4 | 2762 | 4072.8 | 1213 | 0.67473 | 5.762
2024-12-09 | 23:08 | Data | 0 | 32.96 | 31.333 | 182.558 | 7.63 | 172.075 | 2255.97 | 25.86 | 46.63 | 6.37 | 1.335 | 4.41 | 8680.41 | 1.627 | 97.9 | 76.8 | 1466 | 23.32 | 5642.3 | 2841 | 2760.8 | 4085 | 1213 | 0.67897 | 5.744
2024-12-09 | 23:08 | Data | 0 | 32.953 | 31.11 | 182.423 | 7.63 | 172.03 | 2253.25 | 25.86 | 46.811 | 6.37 | 1.331 | 4.417 | 8684.94 | 1.843 | 97.9 | 76.8 | 1465 | 23.41 | 5645.2 | 2819.6 | 2759.2 | 4063.8 | 1213 | 0.67798 | 5.748
2024-12-09 | 23:08 | Data | 0 | 33.183 | 31.312 | 182.604 | 7.63 | 172.21 | 2252.35 | 25.86 | 46.811 | 6.37 | 1.324 | 4.409 | 8716.59 | 1.87 | 97.9 | 76.9 | 1464 | 23.41 | 5665.8 | 2840.9 | 2774.5 | 4090.6 | 1213 | 0.67652 | 5.733
2024-12-09 | 23:08 | Data | 0 | 33.129 | 30.914 | 182.558 | 7.63 | 172.075 | 2252.35 | 25.85 | 46.811 | 6.37 | 1.322 | 4.422 | 8703.03 | 1.965 | 97.9 | 77 | 1464 | 23.41 | 5657 | 2838.2 | 2779 | 4091.5 | 1213 | 0.67742 | 5.743
2024-12-09 | 23:08 | Data | 0 | 32.98 | 30.995 | 182.604 | 7.63 | 172.21 | 2249.64 | 25.86 | 46.811 | 6.37 | 1.336 | 4.428 | 8721.11 | 1.958 | 97.9 | 76.8 | 1462 | 23.41 | 5668.7 | 2823.4 | 2765.5 | 4077.3 | 1213 | 0.67407 | 5.763
2024-12-09 | 23:08 | Data | 0 | 32.926 | 31.063 | 182.423 | 7.64 | 172.03 | 2249.64 | 25.86 | 46.811 | 6.37 | 1.338 | 4.445 | 8730.16 | 2.032 | 97.9 | 76.9 | 1462 | 23.36 | 5674.6 | 2832.7 | 2780.7 | 4089 | 1213 | 0.67613 | 5.782
2024-12-09 | 23:08 | Data | 0 | 32.899 | 31.211 | 182.513 | 7.63 | 172.12 | 2248.73 | 25.89 | 46.721 | 6.37 | 1.336 | 4.426 | 8725.64 | 1.863 | 97.9 | 76.8 | 1462 | 23.36 | 5671.7 | 2822.1 | 2761.3 | 4072.4 | 1213 | 0.67525 | 5.761
2024-12-09 | 23:08 | Data | 0 | 33.176 | 30.995 | 182.558 | 7.63 | 172.12 | 2248.73 | 25.88 | 46.721 | 6.37 | 1.338 | 4.443 | 8734.68 | 1.857 | 97.9 | 76.9 | 1461 | 23.36 | 5677.5 | 2827.8 | 2760.6 | 4076.3 | 1213 | 0.67757 | 5.78
2024-12-09 | 23:08 | Data | 0 | 33.176 | 31.218 | 182.513 | 7.63 | 172.075 | 2247.83 | 25.86 | 46.721 | 6.37 | 1.329 | 4.432 | 8734.68 | 1.735 | 97.9 | 76.9 | 1461 | 23.41 | 5677.5 | 2854 | 2786.2 | 4108.9 | 1213 | 0.67862 | 5.761
2024-12-09 | 23:08 | Data | 0 | 32.953 | 31.11 | 182.513 | 7.63 | 172.03 | 2249.64 | 25.89 | 46.721 | 6.37 | 1.32 | 4.404 | 8730.16 | 1.843 | 97.9 | 76.9 | 1462 | 23.36 | 5674.6 | 2828.4 | 2766.8 | 4078.1 | 1213 | 0.67642 | 5.725
2024-12-09 | 23:08 | Data | 0 | 33.108 | 31.171 | 182.513 | 7.64 | 172.12 | 2250.54 | 25.89 | 46.721 | 6.37 | 1.33 | 4.399 | 8748.25 | 1.857 | 97.9 | 76.8 | 1463 | 23.36 | 5686.4 | 2848.3 | 2772.6 | 4096.7 | 1213 | 0.67774 | 5.731
2024-12-09 | 23:08 | Data | 0 | 32.953 | 31.285 | 182.558 | 7.63 | 172.21 | 2248.73 | 25.89 | 46.811 | 6.37 | 1.331 | 4.443 | 8761.81 | 1.958 | 97.9 | 76.9 | 1462 | 23.41 | 5695.2 | 2817.6 | 2770 | 4074.6 | 1213 | 0.67327 | 5.775
2024-12-09 | 23:08 | Data | 0 | 33.183 | 31.117 | 182.558 | 7.63 | 172.21 | 2246.93 | 25.88 | 46.721 | 6.37 | 1.337 | 4.444 | 8743.73 | 1.843 | 97.9 | 76.9 | 1461 | 23.36 | 5683.4 | 2839.3 | 2772.3 | 4094 | 1213 | 0.67583 | 5.78
2024-12-09 | 23:08 | Data | 0 | 33.176 | 31.11 | 182.604 | 7.63 | 172.12 | 2246.93 | 25.88 | 46.721 | 6.37 | 1.335 | 4.427 | 8743.73 | 1.958 | 97.9 | 76.8 | 1461 | 23.36 | 5683.4 | 2823.2 | 2771.9 | 4077.3 | 1213 | 0.67731 | 5.761
2024-12-09 | 23:08 | Data | 0 | 32.737 | 31.009 | 182.423 | 7.63 | 172.03 | 2246.93 | 25.88 | 46.811 | 6.37 | 1.334 | 4.448 | 8716.59 | 1.816 | 97.9 | 76.9 | 1461 | 23.41 | 5665.8 | 2862.1 | 2754 | 4090.8 | 1213 | 0.68225 | 5.783
2024-12-09 | 23:08 | Data | 0 | 32.791 | 30.988 | 182.513 | 7.63 | 172.256 | 2246.93 | 25.88 | 46.811 | 6.37 | 1.334 | 4.436 | 8721.11 | 1.634 | 97.9 | 76.9 | 1461 | 23.36 | 5668.7 | 2836.9 | 2757.7 | 4072.8 | 1213 | 0.67878 | 5.77
2024-12-09 | 23:09 | Data | 0 | 33.176 | 31.333 | 182.558 | 7.63 | 172.12 | 2246.02 | 25.88 | 46.721 | 6.37 | 1.332 | 4.417 | 8757.29 | 1.857 | 97.9 | 76.8 | 1459 | 23.41 | 5692.2 | 2839 | 2771.4 | 4087.8 | 1213 | 0.6766 | 5.748
2024-12-09 | 23:09 | Data | 0 | 33.068 | 31.15 | 182.558 | 7.63 | 172.12 | 2246.93 | 25.89 | 46.721 | 6.37 | 1.331 | 4.437 | 8730.16 | 1.843 | 97.9 | 76.9 | 1461 | 23.36 | 5674.6 | 2840.2 | 2770.5 | 4090 | 1213 | 0.67682 | 5.769
2024-12-09 | 23:09 | Data | 0 | 32.73 | 31.11 | 182.513 | 7.63 | 172.075 | 2246.93 | 25.88 | 46.721 | 6.37 | 1.339 | 4.431 | 8730.16 | 1.803 | 97.9 | 76.8 | 1461 | 23.36 | 5674.6 | 2844.2 | 2772.5 | 4092.5 | 1213 | 0.67804 | 5.77
2024-12-09 | 23:09 | Data | 0 | 33.183 | 31.225 | 182.604 | 7.63 | 172.21 | 2244.22 | 25.89 | 46.721 | 6.38 | 1.318 | 4.437 | 8734.68 | 1.843 | 97.9 | 77.1 | 1459 | 23.41 | 5677.5 | 2823.8 | 2768.4 | 4075.8 | 1213 | 0.67391 | 5.753
2024-12-09 | 23:09 | Data | 0 | 32.98 | 31.333 | 182.604 | 7.63 | 172.075 | 2244.22 | 25.88 | 46.721 | 6.37 | 1.329 | 4.447 | 8743.73 | 1.803 | 97.9 | 77 | 1459 | 23.36 | 5683.4 | 2824.2 | 2768 | 4075.5 | 1213 | 0.67635 | 5.776
2024-12-09 | 23:09 | Data | 0 | 32.96 | 31.353 | 182.649 | 7.63 | 172.256 | 2244.22 | 25.86 | 46.721 | 6.37 | 1.339 | 4.428 | 8730.16 | 1.884 | 97.9 | 76.8 | 1459 | 23.36 | 5674.6 | 2812.9 | 2775.3 | 4070.2 | 1213 | 0.67397 | 5.767
2024-12-09 | 23:09 | Data | 0 | 33.183 | 31.022 | 182.513 | 7.63 | 172.075 | 2246.93 | 25.88 | 47.082 | 6.37 | 1.337 | 4.417 | 8730.16 | 1.904 | 97.9 | 76.8 | 1461 | 23.54 | 5674.6 | 2820.2 | 2770.8 | 4077.7 | 1213 | 0.67447 | 5.754
2024-12-09 | 23:09 | Data | 0 | 32.94 | 31.11 | 182.468 | 7.63 | 172.075 | 2247.83 | 25.88 | 47.082 | 6.37 | 1.329 | 4.408 | 8730.16 | 2.012 | 97.9 | 76.8 | 1462 | 23.54 | 5674.6 | 2821 | 2777.7 | 4078.1 | 1213 | 0.67485 | 5.737
2024-12-09 | 23:09 | Data | 0 | 32.845 | 31.11 | 182.423 | 7.63 | 172.075 | 2247.83 | 25.88 | 47.172 | 6.37 | 1.327 | 4.419 | 8730.16 | 1.674 | 97.9 | 76.9 | 1461 | 23.54 | 5674.6 | 2822.2 | 2790.2 | 4089.1 | 1213 | 0.67334 | 5.746
2024-12-09 | 23:09 | Data | 0 | 33.007 | 31.117 | 182.604 | 7.63 | 172.12 | 2251.45 | 25.88 | 47.082 | 6.37 | 1.339 | 4.425 | 8734.68 | 1.843 | 97.9 | 76.8 | 1463 | 23.54 | 5677.5 | 2834.8 | 2804 | 4106.9 | 1213 | 0.67371 | 5.763
2024-12-09 | 23:09 | Data | 0 | 33.169 | 31.225 | 182.604 | 7.63 | 172.075 | 2251.45 | 25.89 | 47.082 | 6.37 | 1.338 | 4.417 | 8721.11 | 1.843 | 97.9 | 76.8 | 1464 | 23.54 | 5668.7 | 2836.3 | 2786.4 | 4095.6 | 1213 | 0.67576 | 5.754
2024-12-09 | 23:09 | Data | 0 | 33.061 | 31.225 | 182.513 | 7.63 | 172.12 | 2252.35 | 25.88 | 46.721 | 6.37 | 1.337 | 4.437 | 8707.55 | 2.059 | 97.9 | 76.9 | 1464 | 23.27 | 5659.9 | 2850.4 | 2795 | 4111.8 | 1213 | 0.67538 | 5.771
2024-12-09 | 23:09 | Data | 0 | 33.284 | 31.339 | 182.604 | 7.63 | 172.256 | 2251.45 | 25.88 | 47.082 | 6.37 | 1.336 | 4.455 | 8698.5 | 1.944 | 97.9 | 76.9 | 1463 | 23.54 | 5654 | 2812.6 | 2788.8 | 4080.7 | 1213 | 0.67311 | 5.79
2024-12-09 | 23:09 | Data | 0 | 33.399 | 31.225 | 182.694 | 7.63 | 172.12 | 2252.35 | 25.88 | 47.082 | 6.38 | 1.332 | 4.42 | 8693.98 | 1.944 | 97.9 | 76.8 | 1464 | 23.54 | 5651.1 | 2820.3 | 2803.3 | 4098.4 | 1213 | 0.67045 | 5.753
2024-12-09 | 23:09 | Data | 0 | 32.744 | 31.11 | 182.468 | 7.64 | 172.12 | 2252.35 | 25.88 | 47.082 | 6.37 | 1.335 | 4.407 | 8689.46 | 1.789 | 97.9 | 76.8 | 1464 | 23.54 | 5648.1 | 2856.6 | 2793.7 | 4111.5 | 1213.1 | 0.67778 | 5.742
2024-12-09 | 23:09 | Data | 0 | 33.237 | 31.13 | 182.558 | 7.63 | 172.301 | 2252.35 | 25.89 | 47.172 | 6.38 | 1.34 | 4.41 | 8693.98 | 2.032 | 97.9 | 76.7 | 1464 | 23.54 | 5651.1 | 2845.5 | 2791 | 4104.5 | 1213.1 | 0.67618 | 5.751
2024-12-09 | 23:09 | Data | 0 | 33.453 | 31.238 | 182.694 | 7.63 | 172.256 | 2254.16 | 25.88 | 47.082 | 6.37 | 1.328 | 4.438 | 8693.98 | 1.877 | 97.9 | 77 | 1466 | 23.59 | 5651.1 | 2840.7 | 2787.6 | 4101.5 | 1213.1 | 0.67401 | 5.766
2024-12-09 | 23:09 | Data | 0 | 32.987 | 31.285 | 182.649 | 7.63 | 172.21 | 2251.45 | 25.89 | 47.082 | 6.37 | 1.337 | 4.459 | 8689.46 | 1.857 | 97.9 | 76.9 | 1463 | 23.54 | 5648.1 | 2847.7 | 2771.6 | 4097.6 | 1213.1 | 0.67777 | 5.795
2024-12-09 | 23:10 | Data | 0 | 32.953 | 31.11 | 182.468 | 7.63 | 172.03 | 2253.25 | 25.89 | 47.172 | 6.37 | 1.335 | 4.437 | 8693.98 | 1.843 | 97.9 | 76.9 | 1465 | 23.54 | 5651.1 | 2836 | 2783 | 4091.3 | 1213.1 | 0.67443 | 5.772
2024-12-09 | 23:10 | Data | 0 | 33.068 | 31.333 | 182.513 | 7.63 | 172.12 | 2246.93 | 25.89 | 47.082 | 6.37 | 1.33 | 4.446 | 8707.55 | 1.83 | 97.9 | 77 | 1460 | 23.59 | 5659.9 | 2827.1 | 2776 | 4085.3 | 1213.1 | 0.67417 | 5.776
2024-12-09 | 23:10 | Data | 0 | 33.183 | 31.117 | 182.649 | 7.63 | 172.256 | 2252.35 | 25.89 | 47.082 | 6.37 | 1.336 | 4.455 | 8693.98 | 1.938 | 97.9 | 76.9 | 1463 | 23.54 | 5651.1 | 2851.1 | 2795.7 | 4112.8 | 1213.1 | 0.67619 | 5.79
2024-12-09 | 23:10 | Data | 0 | 32.953 | 31.11 | 182.604 | 7.63 | 172.21 | 2249.64 | 25.88 | 47.172 | 6.37 | 1.335 | 4.447 | 8689.46 | 1.843 | 97.9 | 76.9 | 1462 | 23.59 | 5648.1 | 2815.2 | 2800.9 | 4098.1 | 1213.1 | 0.66939 | 5.783
2024-12-09 | 23:10 | Data | 0 | 32.899 | 31.157 | 182.513 | 7.63 | 172.03 | 2249.64 | 25.89 | 47.082 | 6.37 | 1.337 | 4.413 | 8689.46 | 1.843 | 97.9 | 76.8 | 1462 | 23.54 | 5648.1 | 2831.5 | 2802.7 | 4104.6 | 1213.1 | 0.67283 | 5.751
2024-12-09 | 23:10 | Data | 0 | 32.98 | 31.225 | 182.604 | 7.63 | 172.12 | 2244.22 | 25.89 | 47.082 | 6.38 | 1.341 | 4.43 | 8716.59 | 1.735 | 97.9 | 76.8 | 1459 | 23.54 | 5665.8 | 2841.5 | 2791.8 | 4105.7 | 1213.1 | 0.67425 | 5.771
2024-12-09 | 23:10 | Data | 0 | 32.967 | 31.198 | 182.558 | 7.63 | 172.12 | 2248.73 | 25.89 | 47.172 | 6.37 | 1.337 | 4.418 | 8689.46 | 1.668 | 97.9 | 76.8 | 1462 | 23.59 | 5648.1 | 2822.5 | 2751.3 | 4064.4 | 1213.1 | 0.67699 | 5.755
2024-12-09 | 23:10 | Data | 0 | 33.068 | 31.198 | 182.558 | 7.63 | 172.12 | 2248.73 | 25.88 | 46.721 | 6.37 | 1.339 | 4.425 | 8721.11 | 1.749 | 97.9 | 76.8 | 1462 | 23.32 | 5668.7 | 2823.7 | 2764.8 | 4072.9 | 1213.1 | 0.67578 | 5.765
2024-12-09 | 23:10 | Data | 0 | 33.176 | 31.447 | 182.649 | 7.63 | 172.21 | 2249.64 | 25.88 | 46.721 | 6.38 | 1.334 | 4.408 | 8716.59 | 1.863 | 97.9 | 76.8 | 1462 | 23.36 | 5665.8 | 2834 | 2762.1 | 4079 | 1213.1 | 0.67711 | 5.743
2024-12-09 | 23:10 | Data | 0 | 33.135 | 31.326 | 182.604 | 7.63 | 172.256 | 2251.45 | 25.88 | 46.811 | 6.37 | 1.326 | 4.409 | 8716.59 | 1.978 | 97.9 | 76.9 | 1463 | 23.36 | 5665.8 | 2858.6 | 2786 | 4111.6 | 1213.1 | 0.6774 | 5.733
2024-12-09 | 23:10 | Data | 0 | 33.007 | 31.285 | 182.604 | 7.64 | 172.21 | 2248.73 | 25.89 | 46.721 | 6.37 | 1.323 | 4.432 | 8716.59 | 1.674 | 97.9 | 77 | 1461 | 23.36 | 5665.8 | 2850.9 | 2761.7 | 4088.1 | 1213.1 | 0.68104 | 5.755
2024-12-09 | 23:10 | Data | 0 | 32.953 | 31.11 | 182.694 | 7.63 | 172.12 | 2247.83 | 25.89 | 46.811 | 6.38 | 1.324 | 4.453 | 8721.11 | 2.046 | 97.9 | 77.1 | 1462 | 23.41 | 5668.7 | 2808.9 | 2764.3 | 4062.7 | 1213.1 | 0.6747 | 5.777
2024-12-09 | 23:10 | Data | 0 | 33.068 | 31.339 | 182.558 | 7.63 | 172.256 | 2249.64 | 25.89 | 46.721 | 6.37 | 1.33 | 4.426 | 8707.55 | 1.944 | 97.9 | 76.9 | 1462 | 23.36 | 5659.9 | 2838.7 | 2744.8 | 4066.6 | 1213.1 | 0.68118 | 5.756
2024-12-09 | 23:10 | Data | 0 | 33.291 | 31.225 | 182.558 | 7.63 | 172.21 | 2249.64 | 25.88 | 46.811 | 6.37 | 1.332 | 4.443 | 8698.5 | 1.863 | 97.9 | 76.9 | 1463 | 23.36 | 5654 | 2822.1 | 2720.1 | 4051.6 | 1213.1 | 0.68684 | 5.775
2024-12-09 | 23:10 | Data | 0 | 32.953 | 31.204 | 182.558 | 7.63 | 172.12 | 2249.64 | 25.89 | 46.721 | 6.37 | 1.339 | 4.441 | 8712.07 | 1.884 | 97.9 | 76.8 | 1462 | 23.41 | 5662.8 | 2844.3 | 2744.2 | 4068.7 | 1213.1 | 0.68299 | 5.78
2024-12-09 | 23:10 | Data | 0 | 32.858 | 31.11 | 182.649 | 7.63 | 172.075 | 2248.73 | 25.88 | 46.721 | 6.37 | 1.342 | 4.425 | 8703.03 | 1.823 | 97.9 | 76.7 | 1462 | 23.41 | 5657 | 2816.4 | 2755.1 | 4061.1 | 1213.1 | 0.67586 | 5.767
2024-12-09 | 23:10 | Data | 0 | 33.264 | 31.366 | 182.604 | 7.63 | 172.12 | 2248.73 | 25.88 | 46.811 | 6.37 | 1.324 | 4.418 | 8721.11 | 1.911 | 97.9 | 76.9 | 1462 | 23.41 | 5668.7 | 2834.4 | 2754.1 | 4074.5 | 1213.1 | 0.6783 | 5.742
2024-12-09 | 23:10 | Data | 0 | 32.953 | 31.11 | 182.875 | 7.63 | 172.256 | 2249.64 | 25.88 | 46.721 | 6.37 | 1.33 | 4.449 | 8693.98 | 1.843 | 97.9 | 77 | 1462 | 23.36 | 5651.1 | 2841.3 | 2776.9 | 4094.8 | 1213.1 | 0.67662 | 5.78
2024-12-09 | 23:11 | Data | 0 | 32.953 | 31.002 | 182.423 | 7.63 | 172.075 | 2249.64 | 25.88 | 46.811 | 6.37 | 1.338 | 4.423 | 8703.03 | 1.951 | 97.9 | 76.8 | 1462 | 23.36 | 5657 | 2834 | 2765.5 | 4079.2 | 1213.1 | 0.67813 | 5.761
2024-12-09 | 23:11 | Data | 0 | 32.96 | 31.11 | 182.694 | 7.63 | 172.21 | 2251.45 | 25.89 | 46.811 | 6.37 | 1.325 | 4.414 | 8693.98 | 1.843 | 97.9 | 76.9 | 1464 | 23.41 | 5651.1 | 2824 | 2741.1 | 4057.6 | 1213.1 | 0.67909 | 5.74
2024-12-09 | 23:11 | Data | 0 | 32.98 | 31.11 | 182.604 | 7.63 | 172.12 | 2246.93 | 25.88 | 46.811 | 6.37 | 1.335 | 4.423 | 8689.46 | 1.843 | 97.9 | 76.8 | 1461 | 23.41 | 5648.1 | 2814.3 | 2756.3 | 4061.8 | 1213.1 | 0.67335 | 5.756
2024-12-09 | 23:11 | Data | 0 | 33.081 | 31.123 | 182.694 | 7.63 | 172.256 | 2247.83 | 25.88 | 46.721 | 6.37 | 1.339 | 4.423 | 8703.03 | 1.83 | 97.9 | 76.8 | 1461 | 23.36 | 5657 | 2842.8 | 2754.7 | 4078.3 | 1213.1 | 0.67977 | 5.762
2024-12-09 | 23:11 | Data | 0 | 33.122 | 31.11 | 182.468 | 7.63 | 172.03 | 2249.64 | 25.88 | 46.721 | 6.37 | 1.327 | 4.414 | 8703.03 | 2.059 | 97.9 | 76.9 | 1462 | 23.36 | 5657 | 2812.7 | 2742.9 | 4053.6 | 1213.1 | 0.67621 | 5.742
2024-12-09 | 23:11 | Data | 0 | 33.351 | 31.562 | 182.739 | 7.63 | 172.21 | 2254.16 | 25.89 | 46.811 | 6.37 | 1.323 | 4.427 | 8703.03 | 1.843 | 97.9 | 77 | 1466 | 23.36 | 5657 | 2831.3 | 2742.9 | 4063.5 | 1213.1 | 0.6795 | 5.75
2024-12-09 | 23:11 | Data | 0 | 33.183 | 31.171 | 182.694 | 7.63 | 172.21 | 2252.35 | 25.88 | 46.721 | 6.37 | 1.326 | 4.452 | 8707.55 | 1.944 | 97.9 | 77 | 1464 | 23.36 | 5659.9 | 2835.6 | 2759.1 | 4076.6 | 1213.1 | 0.67796 | 5.777
2024-12-09 | 23:11 | Data | 0 | 33.304 | 31.339 | 182.694 | 7.63 | 172.256 | 2252.35 | 25.88 | 46.54 | 6.37 | 1.326 | 4.455 | 8721.11 | 1.688 | 97.9 | 77.1 | 1464 | 23.27 | 5668.7 | 2833.4 | 2761 | 4078.4 | 1213.1 | 0.67671 | 5.78
2024-12-09 | 23:11 | Data | 0 | 33.021 | 31.002 | 182.558 | 7.63 | 172.12 | 2252.35 | 25.89 | 46.54 | 6.37 | 1.337 | 4.441 | 8707.55 | 1.674 | 97.9 | 76.9 | 1464 | 23.22 | 5659.9 | 2820.6 | 2778.2 | 4080.3 | 1213.1 | 0.67256 | 5.778
2024-12-09 | 23:11 | Data | 0 | 33.156 | 31.562 | 182.558 | 7.63 | 172.21 | 2252.35 | 25.88 | 46.45 | 6.37 | 1.337 | 4.431 | 8693.98 | 1.83 | 97.9 | 76.8 | 1464 | 23.22 | 5651.1 | 2844.7 | 2785.3 | 4100.7 | 1213.1 | 0.67668 | 5.768
2024-12-09 | 23:11 | Data | 0 | 33.372 | 31.339 | 182.558 | 7.63 | 172.12 | 2252.35 | 25.88 | 46.63 | 6.38 | 1.334 | 4.43 | 8693.98 | 1.958 | 97.9 | 76.9 | 1464 | 23.27 | 5651.1 | 2837.5 | 2775.4 | 4090.8 | 1213.1 | 0.67716 | 5.764
2024-12-09 | 23:11 | Data | 0 | 32.96 | 31.117 | 182.649 | 7.63 | 172.21 | 2253.25 | 25.88 | 46.54 | 6.37 | 1.337 | 4.417 | 8703.03 | 1.816 | 97.9 | 76.8 | 1464 | 23.22 | 5657 | 2827.7 | 2764.4 | 4074.3 | 1213.1 | 0.67765 | 5.752
2024-12-09 | 23:11 | Data | 0 | 32.953 | 31.339 | 182.694 | 7.63 | 172.256 | 2252.35 | 25.88 | 46.45 | 6.38 | 1.331 | 4.428 | 8707.55 | 1.998 | 97.9 | 76.9 | 1464 | 23.22 | 5659.9 | 2841.8 | 2761.3 | 4082.4 | 1213.1 | 0.67882 | 5.76
2024-12-09 | 23:11 | Data | 0 | 32.96 | 31.339 | 182.604 | 7.63 | 172.256 | 2255.97 | 25.89 | 46.45 | 6.37 | 1.334 | 4.451 | 8707.55 | 1.782 | 97.9 | 76.9 | 1466 | 23.22 | 5659.9 | 2827.3 | 2767.4 | 4079.7 | 1213.1 | 0.67427 | 5.783
2024-12-09 | 23:11 | Data | 0 | 33.068 | 31.333 | 182.513 | 7.63 | 172.256 | 2252.35 | 25.88 | 46.45 | 6.37 | 1.338 | 4.46 | 8707.55 | 1.836 | 97.9 | 76.9 | 1464 | 23.27 | 5659.9 | 2834 | 2764.1 | 4079.3 | 1213.1 | 0.6764 | 5.798
2024-12-09 | 23:11 | Data | 0 | 32.953 | 31.326 | 182.558 | 7.64 | 172.256 | 2251.45 | 25.88 | 46.54 | 6.37 | 1.332 | 4.463 | 8721.11 | 1.728 | 97.9 | 77 | 1464 | 23.27 | 5668.7 | 2816.4 | 2757 | 4065.5 | 1213.1 | 0.67759 | 5.795
2024-12-09 | 23:11 | Data | 0 | 33.169 | 31.292 | 182.558 | 7.64 | 172.12 | 2252.35 | 25.88 | 46.45 | 6.37 | 1.331 | 4.449 | 8689.46 | 2.019 | 97.9 | 77 | 1464 | 23.27 | 5648.1 | 2820.5 | 2762.2 | 4070.5 | 1213.2 | 0.6751 | 5.78
2024-12-09 | 23:12 | Data | 0 | 32.96 | 31.11 | 182.649 | 7.63 | 172.12 | 2252.35 | 25.89 | 46.45 | 6.37 | 1.33 | 4.437 | 8680.41 | 1.843 | 97.9 | 76.9 | 1464 | 23.27 | 5642.3 | 2828 | 2764.3 | 4074.7 | 1213.2 | 0.67828 | 5.768
2024-12-09 | 23:12 | Data | 0 | 33.027 | 31.009 | 182.649 | 7.63 | 172.21 | 2252.35 | 25.89 | 46.54 | 6.37 | 1.329 | 4.444 | 8666.85 | 1.573 | 97.9 | 77 | 1463 | 23.27 | 5633.5 | 2828.3 | 2780.8 | 4080.8 | 1213.2 | 0.67599 | 5.774
2024-12-09 | 23:12 | Data | 0 | 32.96 | 31.285 | 182.649 | 7.63 | 172.075 | 2246.93 | 25.88 | 46.54 | 6.37 | 1.338 | 4.429 | 8653.28 | 1.782 | 97.9 | 76.8 | 1461 | 23.27 | 5624.6 | 2844.6 | 2772.6 | 4090.5 | 1213.2 | 0.67846 | 5.767
2024-12-09 | 23:12 | Data | 0 | 33.291 | 31.137 | 182.604 | 7.63 | 172.12 | 2246.93 | 25.88 | 46.45 | 6.38 | 1.337 | 4.458 | 8689.46 | 1.857 | 97.9 | 76.9 | 1461 | 23.27 | 5648.1 | 2840.5 | 2802.8 | 4111.4 | 1213.2 | 0.67304 | 5.795
2024-12-09 | 23:12 | Data | 0 | 33.183 | 31.137 | 182.558 | 7.64 | 172.21 | 2249.64 | 25.88 | 46.54 | 6.37 | 1.329 | 4.442 | 8689.46 | 2.019 | 97.9 | 77 | 1462 | 23.22 | 5648.1 | 2829 | 2793.7 | 4097.9 | 1213.2 | 0.6727 | 5.772
2024-12-09 | 23:12 | Data | 0 | 32.973 | 31.339 | 182.649 | 7.63 | 172.21 | 2248.73 | 25.88 | 46.45 | 6.38 | 1.331 | 4.431 | 8716.59 | 1.62 | 97.9 | 76.9 | 1462 | 23.27 | 5665.8 | 2832.6 | 2805 | 4104.7 | 1213.2 | 0.67301 | 5.762
2024-12-09 | 23:12 | Data | 0 | 32.967 | 31.339 | 182.604 | 7.63 | 172.21 | 2247.83 | 25.88 | 46.269 | 6.37 | 1.335 | 4.439 | 8716.59 | 1.62 | 97.9 | 76.9 | 1461 | 23.13 | 5665.8 | 2825 | 2811.2 | 4101.4 | 1213.2 | 0.67347 | 5.773
2024-12-09 | 23:12 | Data | 0 | 33.183 | 31.123 | 182.604 | 7.63 | 172.256 | 2251.45 | 25.88 | 46.45 | 6.37 | 1.336 | 4.437 | 8707.55 | 1.904 | 97.9 | 76.9 | 1463 | 23.27 | 5659.9 | 2824.9 | 2786.6 | 4088.5 | 1213.2 | 0.6731 | 5.774
2024-12-09 | 23:12 | Data | 0 | 32.96 | 31.312 | 182.649 | 7.63 | 172.256 | 2251.45 | 25.88 | 46.45 | 6.37 | 1.326 | 4.446 | 8707.55 | 2.052 | 97.9 | 77 | 1463 | 23.22 | 5659.9 | 2829.7 | 2747.8 | 4067.7 | 1213.2 | 0.67825 | 5.771
2024-12-09 | 23:12 | Data | 0 | 32.926 | 31.11 | 182.604 | 7.63 | 172.256 | 2252.35 | 25.89 | 46.359 | 6.37 | 1.331 | 4.436 | 8689.46 | 2.059 | 97.9 | 76.9 | 1464 | 23.18 | 5648.1 | 2826.2 | 2767.3 | 4072.3 | 1213.2 | 0.67794 | 5.768
2024-12-09 | 23:12 | Data | 0 | 33.156 | 31.225 | 182.604 | 7.63 | 172.301 | 2250.54 | 25.89 | 46.45 | 6.37 | 1.34 | 4.421 | 8671.37 | 2.066 | 97.9 | 76.7 | 1463 | 23.27 | 5636.4 | 2823.9 | 2771.1 | 4075.5 | 1213.2 | 0.6776 | 5.761
2024-12-09 | 23:12 | Data | 0 | 32.926 | 31.225 | 182.785 | 7.63 | 172.12 | 2252.35 | 25.89 | 46.45 | 6.37 | 1.337 | 4.44 | 8703.03 | 1.83 | 97.9 | 76.9 | 1464 | 23.22 | 5657 | 2837.1 | 2772.2 | 4085.6 | 1213.2 | 0.67733 | 5.777
2024-12-09 | 23:12 | Data | 0 | 32.967 | 31.312 | 182.649 | 7.64 | 172.12 | 2255.97 | 25.88 | 46.811 | 6.37 | 1.335 | 4.43 | 8707.55 | 1.836 | 97.9 | 76.8 | 1466 | 23.41 | 5659.9 | 2861.5 | 2765.2 | 4095.2 | 1213.2 | 0.68069 | 5.765
2024-12-09 | 23:12 | Data | 0 | 33.176 | 31.333 | 182.694 | 7.63 | 172.12 | 2255.97 | 25.88 | 46.811 | 6.37 | 1.331 | 4.446 | 8707.55 | 1.85 | 97.9 | 77 | 1465 | 23.36 | 5659.9 | 2825.6 | 2782.7 | 4086.8 | 1213.2 | 0.67398 | 5.777
2024-12-09 | 23:12 | Data | 0 | 33.412 | 31.339 | 182.785 | 7.63 | 172.256 | 2255.97 | 25.88 | 46.721 | 6.37 | 1.335 | 4.459 | 8703.03 | 1.89 | 97.9 | 76.9 | 1466 | 23.41 | 5657 | 2822.7 | 2768.7 | 4074.2 | 1213.2 | 0.67506 | 5.795
2024-12-09 | 23:12 | Data | 0 | 33.601 | 31.393 | 182.739 | 7.63 | 172.346 | 2254.16 | 25.89 | 46.721 | 6.38 | 1.335 | 4.442 | 8680.41 | 1.944 | 97.9 | 76.9 | 1465 | 23.41 | 5642.3 | 2846.2 | 2784.5 | 4104.8 | 1213.2 | 0.67673 | 5.778
2024-12-09 | 23:12 | Data | 0 | 33.183 | 31.508 | 182.558 | 7.63 | 172.256 | 2255.97 | 25.88 | 46.721 | 6.37 | 1.331 | 4.418 | 8680.41 | 1.85 | 97.9 | 76.9 | 1466 | 23.36 | 5642.3 | 2821.7 | 2762.9 | 4071 | 1213.2 | 0.67535 | 5.749
2024-12-09 | 23:12 | Data | 0 | 32.96 | 31.333 | 182.513 | 7.63 | 172.075 | 2255.97 | 25.88 | 46.721 | 6.37 | 1.324 | 4.439 | 8680.41 | 1.816 | 97.9 | 77 | 1466 | 23.41 | 5642.3 | 2831.2 | 2795.8 | 4101 | 1213.2 | 0.67378 | 5.763
2024-12-09 | 23:13 | Data | 0 | 32.987 | 31.312 | 182.649 | 7.63 | 172.256 | 2252.35 | 25.89 | 46.811 | 6.38 | 1.334 | 4.412 | 8662.33 | 1.857 | 97.9 | 76.8 | 1464 | 23.41 | 5630.5 | 2842.1 | 2773.2 | 4092.6 | 1213.2 | 0.67591 | 5.748
2024-12-09 | 23:13 | Data | 0 | 33.169 | 31.333 | 182.604 | 7.63 | 172.21 | 2251.45 | 25.88 | 46.721 | 6.37 | 1.339 | 4.405 | 8689.46 | 1.742 | 97.9 | 76.7 | 1464 | 23.41 | 5648.1 | 2863.8 | 2787.5 | 4116.9 | 1213.2 | 0.67674 | 5.744
2024-12-09 | 23:13 | Data | 0 | 33.183 | 31.339 | 182.604 | 7.63 | 172.21 | 2251.45 | 25.89 | 46.811 | 6.38 | 1.337 | 4.435 | 8707.55 | 1.843 | 97.9 | 76.8 | 1463 | 23.41 | 5659.9 | 2872.6 | 2773.8 | 4116.1 | 1213.2 | 0.68007 | 5.771
2024-12-09 | 23:13 | Data | 0 | 33.176 | 31.123 | 182.468 | 7.63 | 172.256 | 2251.45 | 25.89 | 46.63 | 6.37 | 1.326 | 4.422 | 8707.55 | 1.904 | 97.9 | 76.9 | 1464 | 23.32 | 5659.9 | 2851.8 | 2792.9 | 4113.3 | 1213.2 | 0.67573 | 5.748
2024-12-09 | 23:13 | Data | 0 | 33.068 | 31.495 | 182.649 | 7.63 | 172.256 | 2247.83 | 25.89 | 46.721 | 6.38 | 1.318 | 4.428 | 9150.73 | 1.728 | 97.9 | 77.1 | 1461 | 23.41 | 5948 | 2852.3 | 2779.9 | 4105.4 | 1213.2 | 0.67763 | 5.747
2024-12-09 | 23:13 | Data | 0 | 33.237 | 31.117 | 182.739 | 7.64 | 172.21 | 2260.48 | 25.88 | 46.721 | 6.37 | 1.338 | 4.432 | 8707.55 | 1.857 | 97.9 | 76.8 | 1469 | 23.41 | 5659.9 | 2853.6 | 2767.6 | 4097.4 | 1213.2 | 0.67988 | 5.77
2024-12-09 | 23:13 | Data | 0 | 33.162 | 31.441 | 182.649 | 7.63 | 172.256 | 2258.68 | 25.88 | 46.991 | 6.38 | 1.329 | 4.445 | 8671.37 | 1.755 | 97.9 | 77 | 1468 | 23.41 | 5636.4 | 2853.2 | 2765.5 | 4097.4 | 1213.2 | 0.67862 | 5.773
2024-12-09 | 23:13 | Data | 0 | 32.98 | 31.528 | 182.694 | 7.63 | 172.21 | 2257.77 | 25.88 | 46.811 | 6.38 | 1.336 | 4.429 | 8707.55 | 1.668 | 97.9 | 76.8 | 1468 | 23.41 | 5659.9 | 2840.6 | 2759.8 | 4087.6 | 1213.2 | 0.6776 | 5.765
2024-12-09 | 23:13 | Data | 0 | 33.297 | 31.184 | 182.739 | 7.63 | 172.301 | 2257.77 | 25.88 | 46.721 | 6.37 | 1.34 | 4.453 | 8671.37 | 1.843 | 97.9 | 76.9 | 1468 | 23.32 | 5636.4 | 2829.1 | 2779 | 4088 | 1213.2 | 0.67486 | 5.793
2024-12-09 | 23:13 | Data | 0 | 33.027 | 31.339 | 182.513 | 7.63 | 172.256 | 2261.39 | 25.89 | 46.811 | 6.37 | 1.342 | 4.452 | 8684.94 | 1.647 | 97.9 | 76.8 | 1469 | 23.36 | 5645.2 | 2892.4 | 2773.8 | 4137.8 | 1213.2 | 0.68016 | 5.793
2024-12-09 | 23:13 | Data | 0 | 33.176 | 31.225 | 182.558 | 7.63 | 172.12 | 2257.77 | 25.89 | 46.811 | 6.37 | 1.34 | 4.454 | 8680.41 | 1.944 | 97.9 | 76.9 | 1468 | 23.32 | 5642.3 | 2848.7 | 2782 | 4107.5 | 1213.2 | 0.67569 | 5.795
2024-12-09 | 23:13 | Data | 0 | 33.176 | 31.339 | 182.694 | 7.63 | 172.21 | 2258.68 | 25.88 | 46.721 | 6.37 | 1.337 | 4.42 | 8693.98 | 1.836 | 97.9 | 76.8 | 1468 | 23.41 | 5651.1 | 2863 | 2782.8 | 4116.6 | 1213.2 | 0.67702 | 5.757
2024-12-09 | 23:13 | Data | 0 | 33.054 | 31.11 | 182.468 | 7.63 | 172.12 | 2257.77 | 25.88 | 46.721 | 6.37 | 1.34 | 4.429 | 8689.46 | 1.857 | 97.9 | 76.8 | 1468 | 23.36 | 5648.1 | 2850.3 | 2779.6 | 4104.9 | 1213.2 | 0.67745 | 5.77
2024-12-09 | 23:13 | Data | 0 | 33.405 | 31.339 | 182.785 | 7.64 | 172.301 | 2258.68 | 25.89 | 46.721 | 6.37 | 1.342 | 4.461 | 8689.46 | 1.681 | 97.9 | 76.9 | 1468 | 23.32 | 5648.1 | 2867.5 | 2782.2 | 4120.6 | 1213.2 | 0.67773 | 5.803
2024-12-09 | 23:13 | Data | 0 | 33.183 | 31.171 | 182.513 | 7.63 | 172.21 | 2254.16 | 25.88 | 46.811 | 6.38 | 1.336 | 4.458 | 8680.41 | 1.897 | 97.9 | 76.9 | 1465 | 23.36 | 5642.3 | 2864.5 | 2787.8 | 4120.9 | 1213.2 | 0.67845 | 5.795
2024-12-09 | 23:13 | Data | 0 | 33.068 | 31.238 | 182.513 | 7.63 | 172.21 | 2255.97 | 25.88 | 46.721 | 6.37 | 1.344 | 4.455 | 8671.37 | 1.911 | 97.9 | 76.8 | 1466 | 23.36 | 5636.4 | 2878.7 | 2773.4 | 4119.7 | 1213.2 | 0.68118 | 5.8
2024-12-09 | 23:13 | Data | 0 | 33.297 | 31.015 | 182.785 | 7.63 | 172.346 | 2255.97 | 25.88 | 46.721 | 6.37 | 1.335 | 4.445 | 8693.98 | 1.965 | 97.9 | 76.9 | 1466 | 23.36 | 5651.1 | 2864.1 | 2785.1 | 4116.8 | 1213.2 | 0.67892 | 5.781
2024-12-09 | 23:14 | Data | 0 | 32.906 | 31.326 | 182.604 | 7.63 | 172.21 | 2254.16 | 25.88 | 46.721 | 6.37 | 1.323 | 4.439 | 8689.46 | 1.836 | 97.9 | 77 | 1466 | 23.41 | 5648.1 | 2856.7 | 2765.5 | 4098.4 | 1213.2 | 0.68023 | 5.763
2024-12-09 | 23:14 | Data | 0 | 32.791 | 31.11 | 182.694 | 7.63 | 172.301 | 2252.35 | 25.86 | 46.811 | 6.38 | 1.329 | 4.46 | 8693.98 | 1.755 | 97.9 | 77 | 1464 | 23.41 | 5651.1 | 2845.1 | 2785.3 | 4106.9 | 1213.2 | 0.67479 | 5.79
2024-12-09 | 23:14 | Data | 0 | 33.264 | 31.312 | 182.649 | 7.63 | 172.21 | 2251.45 | 25.89 | 46.721 | 6.38 | 1.332 | 4.455 | 8698.5 | 1.89 | 97.9 | 77 | 1463 | 23.41 | 5654 | 2849.3 | 2774.3 | 4103.1 | 1213.3 | 0.67737 | 5.787
2024-12-09 | 23:14 | Data | 0 | 32.926 | 31.285 | 182.423 | 7.64 | 172.12 | 2252.35 | 25.88 | 46.721 | 6.37 | 1.337 | 4.446 | 8689.46 | 1.951 | 97.9 | 76.9 | 1464 | 23.36 | 5648.1 | 2848.2 | 2765.3 | 4094.1 | 1213.3 | 0.67659 | 5.782
2024-12-09 | 23:14 | Data | 0 | 33.068 | 31.117 | 182.558 | 7.63 | 172.21 | 2251.45 | 25.88 | 46.721 | 6.37 | 1.332 | 4.442 | 8693.98 | 1.877 | 97.9 | 76.9 | 1463 | 23.36 | 5651.1 | 2854.2 | 2779.9 | 4110.9 | 1213.3 | 0.67554 | 5.773
2024-12-09 | 23:14 | Data | 0 | 33.196 | 31.339 | 182.604 | 7.63 | 172.301 | 2252.35 | 25.89 | 46.811 | 6.38 | 1.339 | 4.444 | 8680.41 | 1.836 | 97.9 | 76.9 | 1464 | 23.36 | 5642.3 | 2858.3 | 2805.1 | 4125 | 1213.3 | 0.67541 | 5.782
2024-12-09 | 23:14 | Data | 0 | 32.845 | 31.11 | 182.513 | 7.63 | 172.21 | 2249.64 | 25.88 | 46.721 | 6.38 | 1.335 | 4.444 | 8680.41 | 1.816 | 97.9 | 76.9 | 1462 | 23.41 | 5642.3 | 2875.5 | 2799.3 | 4142.9 | 1213.3 | 0.6778 | 5.779
2024-12-09 | 23:14 | Data | 0 | 33.176 | 31.117 | 182.513 | 7.63 | 172.12 | 2249.64 | 25.88 | 46.721 | 6.38 | 1.328 | 4.41 | 8662.33 | 1.863 | 97.9 | 76.9 | 1462 | 23.36 | 5630.5 | 2870.4 | 2806 | 4134.2 | 1213.3 | 0.6765 | 5.738
2024-12-09 | 23:14 | Data | 0 | 33.041 | 31.549 | 182.649 | 7.63 | 172.256 | 2248.73 | 25.88 | 46.721 | 6.38 | 1.329 | 4.44 | 8671.37 | 1.938 | 97.9 | 77 | 1462 | 23.41 | 5636.4 | 2877.5 | 2813.3 | 4142.1 | 1213.3 | 0.674 | 5.769
2024-12-09 | 23:14 | Data | 0 | 33.5 | 31.569 | 182.785 | 7.63 | 172.346 | 2246.93 | 25.89 | 46.721 | 6.38 | 1.335 | 4.438 | 8657.8 | 1.884 | 97.9 | 76.9 | 1460 | 23.36 | 5627.6 | 2860.3 | 2803.5 | 4129 | 1213.3 | 0.67461 | 5.773
2024-12-09 | 23:14 | Data | 0 | 33.156 | 31.339 | 182.649 | 7.63 | 172.12 | 2244.22 | 25.89 | 46.811 | 6.37 | 1.338 | 4.435 | 8648.76 | 1.843 | 97.9 | 76.8 | 1459 | 23.36 | 5621.7 | 2800.1 | 2757.3 | 4047.5 | 1213.3 | 0.67271 | 5.772
2024-12-09 | 23:14 | Data | 0 | 33.048 | 31.441 | 182.649 | 7.63 | 172.301 | 2246.02 | 25.88 | 46.721 | 6.38 | 1.337 | 4.423 | 8662.33 | 1.944 | 97.9 | 76.8 | 1459 | 23.36 | 5630.5 | 2769.1 | 2760 | 4030.9 | 1213.3 | 0.66991 | 5.759
2024-12-09 | 23:14 | Data | 0 | 32.98 | 31.11 | 182.694 | 7.63 | 172.256 | 2247.83 | 25.89 | 46.721 | 6.38 | 1.33 | 4.418 | 8648.76 | 1.843 | 97.9 | 76.9 | 1461 | 23.41 | 5621.7 | 2795.6 | 2755.1 | 4042.8 | 1213.3 | 0.67414 | 5.747
2024-12-09 | 23:14 | Data | 0 | 32.953 | 31.11 | 182.513 | 7.63 | 172.21 | 2246.93 | 25.88 | 46.721 | 6.38 | 1.329 | 4.453 | 8648.76 | 1.843 | 97.9 | 77 | 1461 | 23.36 | 5621.7 | 2795.4 | 2764.5 | 4051.3 | 1213.3 | 0.67301 | 5.782
2024-12-09 | 23:14 | Data | 0 | 33.284 | 31.454 | 182.694 | 7.63 | 172.346 | 2246.93 | 25.88 | 46.811 | 6.38 | 1.327 | 4.451 | 8662.33 | 1.843 | 97.9 | 77 | 1461 | 23.36 | 5630.5 | 2795.2 | 2766.8 | 4054.5 | 1213.3 | 0.67143 | 5.778
2024-12-09 | 23:14 | Data | 0 | 33.399 | 31.339 | 182.604 | 7.63 | 172.21 | 2246.93 | 25.89 | 46.721 | 6.38 | 1.323 | 4.455 | 8653.28 | 1.897 | 97.9 | 77.1 | 1461 | 23.36 | 5624.6 | 2786.6 | 2785.9 | 4056.9 | 1213.3 | 0.67058 | 5.779
2024-12-09 | 23:14 | Data | 0 | 33.291 | 31.144 | 182.649 | 7.63 | 172.301 | 2244.22 | 25.88 | 46.721 | 6.38 | 1.322 | 4.453 | 8662.33 | 1.938 | 97.9 | 77.1 | 1459 | 23.41 | 5630.5 | 2776 | 2810.3 | 4070.9 | 1213.3 | 0.66329 | 5.774
2024-12-09 | 23:14 | Data | 0 | 33.075 | 31.123 | 182.649 | 7.63 | 172.12 | 2244.22 | 25.88 | 46.811 | 6.38 | 1.329 | 4.461 | 8689.46 | 2.154 | 97.9 | 77.1 | 1459 | 23.36 | 5648.1 | 2780 | 2809.1 | 4068.2 | 1213.3 | 0.66637 | 5.79
2024-12-09 | 23:14 | Data | 0 | 32.953 | 31.11 | 182.558 | 7.63 | 172.21 | 2244.22 | 25.89 | 46.811 | 6.38 | 1.327 | 4.458 | 8689.46 | 1.843 | 97.9 | 77.1 | 1459 | 23.41 | 5648.1 | 2777.9 | 2812.7 | 4071.6 | 1213.3 | 0.66459 | 5.785
2024-12-09 | 23:15 | Data | 0 | 33.156 | 31.137 | 182.604 | 7.63 | 172.12 | 2243.31 | 25.85 | 46.811 | 6.38 | 1.322 | 4.434 | 8698.5 | 1.951 | 97.9 | 77 | 1459 | 23.41 | 5654 | 2853.6 | 2817.9 | 4131.6 | 1213.3 | 0.66981 | 5.757
2024-12-09 | 23:15 | Data | 0 | 32.953 | 31.333 | 182.694 | 7.64 | 172.12 | 2244.22 | 25.88 | 46.721 | 6.38 | 1.326 | 4.422 | 8671.37 | 1.965 | 97.9 | 76.9 | 1459 | 23.36 | 5636.4 | 2843.7 | 2794 | 4109.2 | 1213.3 | 0.67345 | 5.748
2024-12-09 | 23:15 | Data | 0 | 32.737 | 31.083 | 182.649 | 7.63 | 172.21 | 2244.22 | 25.89 | 46.721 | 6.38 | 1.332 | 4.432 | 8689.46 | 1.897 | 97.9 | 76.9 | 1459 | 23.36 | 5648.1 | 2849.4 | 2792.2 | 4113.4 | 1213.3 | 0.67525 | 5.766
2024-12-09 | 23:15 | Data | 0 | 32.899 | 31.326 | 182.649 | 7.63 | 172.12 | 2244.22 | 25.86 | 46.721 | 6.37 | 1.34 | 4.451 | 8707.55 | 1.803 | 97.9 | 76.8 | 1459 | 23.36 | 5659.9 | 2854.6 | 2768.8 | 4083.8 | 1213.3 | 0.67868 | 5.792
2024-12-09 | 23:15 | Data | 0 | 32.899 | 31.198 | 182.604 | 7.63 | 172.12 | 2245.12 | 25.88 | 46.721 | 6.38 | 1.33 | 4.436 | 8703.03 | 1.897 | 97.9 | 76.9 | 1459 | 23.36 | 5657 | 2843 | 2786.5 | 4102.1 | 1213.3 | 0.67474 | 5.767
2024-12-09 | 23:15 | Data | 0 | 32.953 | 31.225 | 182.558 | 7.63 | 172.21 | 2244.22 | 25.85 | 46.721 | 6.38 | 1.339 | 4.445 | 8707.55 | 1.843 | 97.9 | 76.9 | 1459 | 23.41 | 5659.9 | 2835.6 | 2782.7 | 4099.3 | 1213.3 | 0.67731 | 5.782
2024-12-09 | 23:15 | Data | 0 | 32.953 | 31.326 | 182.604 | 7.63 | 172.075 | 2245.12 | 25.86 | 46.721 | 6.38 | 1.338 | 4.434 | 8707.55 | 1.85 | 97.9 | 76.8 | 1459 | 23.36 | 5659.9 | 2833.3 | 2805.4 | 4121.4 | 1213.3 | 0.67221 | 5.772
2024-12-09 | 23:15 | Data | 0 | 32.953 | 31.11 | 182.558 | 7.63 | 172.075 | 2241.5 | 25.86 | 46.811 | 6.38 | 1.326 | 4.427 | 8703.03 | 1.843 | 97.9 | 77 | 1457 | 23.36 | 5657 | 2834.9 | 2817.1 | 4117.8 | 1213.3 | 0.6708 | 5.753
2024-12-09 | 23:15 | Data | 0 | 33.007 | 31.171 | 182.468 | 7.63 | 172.075 | 2244.22 | 25.86 | 46.721 | 6.38 | 1.329 | 4.443 | 8703.03 | 1.87 | 97.9 | 77 | 1459 | 23.36 | 5657 | 2825.7 | 2826.3 | 4120.2 | 1213.3 | 0.66774 | 5.772
2024-12-09 | 23:15 | Data | 0 | 33.156 | 31.535 | 182.649 | 7.63 | 172.21 | 2244.22 | 25.85 | 46.63 | 6.37 | 1.331 | 4.418 | 8707.55 | 1.735 | 97.9 | 76.9 | 1459 | 23.36 | 5659.9 | 2845.1 | 2839.5 | 4142 | 1213.3 | 0.66832 | 5.749
2024-12-09 | 23:15 | Data | 0 | 32.96 | 31.063 | 182.513 | 7.63 | 172.12 | 2245.12 | 25.85 | 46.811 | 6.38 | 1.335 | 4.424 | 8693.98 | 1.944 | 97.9 | 76.8 | 1459 | 23.41 | 5651.1 | 2839.8 | 2849.4 | 4144.5 | 1213.3 | 0.66721 | 5.759
2024-12-09 | 23:15 | Data | 0 | 32.96 | 31.225 | 182.604 | 7.63 | 172.21 | 2246.93 | 25.85 | 46.63 | 6.38 | 1.339 | 4.43 | 8689.46 | 1.742 | 97.9 | 76.8 | 1461 | 23.36 | 5648.1 | 2848.3 | 2841.9 | 4135.2 | 1213.3 | 0.6694 | 5.77
2024-12-09 | 23:15 | Data | 0 | 32.953 | 31.002 | 182.468 | 7.63 | 172.21 | 2246.02 | 25.86 | 46.811 | 6.38 | 1.332 | 4.413 | 8703.03 | 1.884 | 97.9 | 76.8 | 1460 | 23.41 | 5657 | 2844.7 | 2824.6 | 4118.3 | 1213.3 | 0.66988 | 5.745
2024-12-09 | 23:15 | Data | 0 | 32.73 | 31.11 | 182.604 | 7.63 | 172.21 | 2246.93 | 25.86 | 46.721 | 6.38 | 1.325 | 4.439 | 8707.55 | 1.789 | 97.9 | 77 | 1460 | 23.32 | 5659.9 | 2853.3 | 2800.9 | 4125.4 | 1213.3 | 0.67339 | 5.762
2024-12-09 | 23:15 | Data | 0 | 32.96 | 31.11 | 182.468 | 7.63 | 172.075 | 2246.02 | 25.85 | 46.54 | 6.38 | 1.335 | 4.449 | 8680.41 | 1.843 | 97.9 | 76.9 | 1460 | 23.27 | 5642.3 | 2856.5 | 2813.7 | 4133.3 | 1213.3 | 0.67243 | 5.786
2024-12-09 | 23:15 | Data | 0 | 32.953 | 31.333 | 182.558 | 7.63 | 172.21 | 2246.93 | 25.85 | 46.54 | 6.37 | 1.339 | 4.427 | 8716.59 | 1.836 | 97.9 | 76.8 | 1461 | 23.27 | 5665.8 | 2850.7 | 2772.9 | 4099.6 | 1213.3 | 0.67761 | 5.767
2024-12-09 | 23:15 | Data | 0 | 33.007 | 31.11 | 182.558 | 7.64 | 172.075 | 2247.83 | 25.85 | 46.45 | 6.38 | 1.32 | 4.444 | 8730.16 | 1.85 | 97.9 | 77.1 | 1461 | 23.27 | 5674.6 | 2836 | 2790.6 | 4101.8 | 1213.3 | 0.67384 | 5.763
2024-12-09 | 23:16 | Data | 0 | 32.953 | 31.137 | 182.649 | 7.63 | 172.21 | 2249.64 | 25.86 | 46.54 | 6.38 | 1.324 | 4.44 | 8703.03 | 2.012 | 97.9 | 77 | 1462 | 23.27 | 5657 | 2839 | 2789.2 | 4103.7 | 1213.3 | 0.67379 | 5.763
2024-12-09 | 23:16 | Data | 0 | 32.872 | 31.204 | 182.513 | 7.63 | 172.21 | 2249.64 | 25.85 | 46.54 | 6.38 | 1.323 | 4.441 | 8703.03 | 1.641 | 97.9 | 77 | 1462 | 23.22 | 5657 | 2826 | 2776.8 | 4085.7 | 1213.3 | 0.67721 | 5.764
2024-12-09 | 23:16 | Data | 0 | 32.609 | 30.88 | 182.287 | 7.63 | 171.894 | 2249.64 | 25.85 | 46.54 | 6.38 | 1.338 | 4.465 | 8671.37 | 1.641 | 97.9 | 76.9 | 1462 | 23.27 | 5636.4 | 2828.1 | 2785.5 | 4093.1 | 1213.3 | 0.6739 | 5.803
2024-12-09 | 23:16 | Data | 0 | 32.622 | 30.995 | 182.377 | 7.63 | 171.939 | 2248.73 | 25.85 | 46.45 | 6.38 | 1.336 | 4.465 | 8693.98 | 1.803 | 97.9 | 77 | 1462 | 23.22 | 5651.1 | 2844.3 | 2812.4 | 4115.1 | 1213.4 | 0.67434 | 5.799
2024-12-09 | 23:16 | Data | 0 | 32.744 | 31.056 | 182.468 | 7.63 | 172.075 | 2249.64 | 25.86 | 46.54 | 6.38 | 1.322 | 4.447 | 8693.98 | 2.052 | 97.9 | 77.1 | 1463 | 23.22 | 5651.1 | 2832.7 | 2837.3 | 4125.8 | 1213.4 | 0.67064 | 5.769
2024-12-09 | 23:16 | Data | 0 | 32.946 | 31.056 | 182.513 | 7.63 | 172.03 | 2250.54 | 25.89 | 46.54 | 6.38 | 1.323 | 4.419 | 8689.46 | 1.951 | 97.9 | 77 | 1463 | 23.32 | 5648.1 | 2822.6 | 2819.9 | 4110.9 | 1213.4 | 0.66875 | 5.742
2024-12-09 | 23:16 | Data | 0 | 32.953 | 31.11 | 182.558 | 7.63 | 172.075 | 2252.35 | 25.88 | 46.811 | 6.38 | 1.331 | 4.435 | 8693.98 | 1.843 | 97.9 | 76.9 | 1464 | 23.36 | 5651.1 | 2841.6 | 2827 | 4123.7 | 1213.4 | 0.67144 | 5.765
2024-12-09 | 23:16 | Data | 0 | 33.21 | 30.955 | 182.649 | 7.63 | 172.21 | 2251.45 | 25.88 | 46.54 | 6.38 | 1.331 | 4.443 | 8693.98 | 2.052 | 97.9 | 76.9 | 1463 | 23.27 | 5651.1 | 2844 | 2827.8 | 4126.9 | 1213.4 | 0.67141 | 5.774
2024-12-09 | 23:16 | Data | 0 | 33.169 | 31.312 | 182.604 | 7.63 | 172.12 | 2252.35 | 25.89 | 46.45 | 6.38 | 1.335 | 4.436 | 8693.98 | 2.066 | 97.9 | 76.9 | 1464 | 23.27 | 5651.1 | 2830.2 | 2799.3 | 4103.8 | 1213.4 | 0.67262 | 5.771
2024-12-09 | 23:16 | Data | 0 | 33.014 | 31.11 | 182.558 | 7.63 | 172.075 | 2252.35 | 25.88 | 46.54 | 6.37 | 1.339 | 4.446 | 8680.41 | 1.647 | 97.9 | 76.9 | 1463 | 23.22 | 5642.3 | 2833.3 | 2795.3 | 4100 | 1213.4 | 0.6739 | 5.785
2024-12-09 | 23:16 | Data | 0 | 33.068 | 31.38 | 182.558 | 7.63 | 172.12 | 2251.45 | 25.88 | 46.54 | 6.38 | 1.336 | 4.456 | 8698.5 | 1.836 | 97.9 | 77 | 1464 | 23.27 | 5654 | 2821.7 | 2770.7 | 4074.9 | 1213.4 | 0.67467 | 5.792
2024-12-09 | 23:16 | Data | 0 | 32.953 | 30.907 | 182.423 | 7.63 | 172.03 | 2252.35 | 25.88 | 46.45 | 6.38 | 1.332 | 4.444 | 8698.5 | 1.897 | 97.9 | 76.9 | 1464 | 23.22 | 5654 | 2829.5 | 2769.8 | 4081.6 | 1213.4 | 0.67572 | 5.775
2024-12-09 | 23:16 | Data | 0 | 33.129 | 31.117 | 182.694 | 7.63 | 172.256 | 2249.64 | 25.89 | 46.811 | 6.38 | 1.334 | 4.436 | 8693.98 | 1.863 | 97.9 | 76.9 | 1462 | 23.41 | 5651.1 | 2820.8 | 2771.7 | 4075.2 | 1213.4 | 0.6737 | 5.769
2024-12-09 | 23:16 | Data | 0 | 32.771 | 31.218 | 182.513 | 7.64 | 172.075 | 2252.35 | 25.88 | 46.811 | 6.38 | 1.34 | 4.439 | 8703.03 | 1.634 | 97.9 | 76.8 | 1464 | 23.36 | 5657 | 2834.1 | 2782.8 | 4088.8 | 1213.4 | 0.67733 | 5.78
2024-12-09 | 23:16 | Data | 0 | 32.913 | 31.225 | 182.694 | 7.63 | 172.075 | 2249.64 | 25.88 | 46.721 | 6.38 | 1.332 | 4.406 | 8689.46 | 1.83 | 97.9 | 76.8 | 1462 | 23.36 | 5648.1 | 2835.8 | 2798.2 | 4106.7 | 1213.4 | 0.67199 | 5.738
2024-12-09 | 23:16 | Data | 0 | 33.338 | 31.38 | 182.649 | 7.63 | 172.21 | 2252.35 | 25.89 | 46.811 | 6.38 | 1.332 | 4.395 | 9132.64 | 1.938 | 97.9 | 76.8 | 1464 | 23.41 | 5936.2 | 2855.4 | 2820.3 | 4131.6 | 1213.4 | 0.67309 | 5.726
2024-12-09 | 23:16 | Data | 0 | 32.953 | 31.117 | 182.513 | 7.63 | 172.075 | 2252.35 | 25.88 | 46.721 | 6.38 | 1.339 | 4.391 | 8684.94 | 1.83 | 97.9 | 76.6 | 1464 | 23.36 | 5645.2 | 2816.7 | 2828.5 | 4112.8 | 1213.4 | 0.66771 | 5.73
2024-12-09 | 23:16 | Data | 0 | 32.838 | 31.285 | 182.513 | 7.63 | 172.256 | 2251.45 | 25.88 | 46.721 | 6.38 | 1.332 | 4.421 | 8689.46 | 1.884 | 97.9 | 76.8 | 1463 | 23.36 | 5648.1 | 2844.1 | 2836.9 | 4133.4 | 1213.4 | 0.67022 | 5.753
2024-12-09 | 23:17 | Data | 0 | 33.345 | 31.508 | 182.604 | 7.63 | 172.21 | 2252.35 | 25.89 | 46.721 | 6.38 | 1.342 | 4.406 | 8693.98 | 1.951 | 97.9 | 76.6 | 1463 | 23.36 | 5651.1 | 2811.2 | 2838.8 | 4115.1 | 1213.4 | 0.66775 | 5.748
2024-12-09 | 23:17 | Data | 0 | 33.068 | 31.11 | 182.513 | 7.63 | 172.12 | 2249.64 | 25.86 | 46.811 | 6.38 | 1.341 | 4.467 | 8707.55 | 1.857 | 97.9 | 76.9 | 1462 | 23.41 | 5659.9 | 2828.8 | 2788.3 | 4088.5 | 1213.4 | 0.67203 | 5.808
2024-12-09 | 23:17 | Data | 0 | 32.865 | 31.103 | 182.604 | 7.63 | 172.21 | 2249.64 | 25.88 | 46.811 | 6.38 | 1.337 | 4.463 | 8716.59 | 1.641 | 97.9 | 77 | 1462 | 23.41 | 5665.8 | 2848 | 2806.4 | 4120.4 | 1213.4 | 0.67334 | 5.799
2024-12-09 | 23:17 | Data | 0 | 32.899 | 30.887 | 182.332 | 7.63 | 172.075 | 2249.64 | 25.88 | 46.811 | 6.38 | 1.335 | 4.459 | 8707.55 | 2.019 | 97.9 | 77 | 1462 | 23.36 | 5659.9 | 2837.9 | 2789.4 | 4099.5 | 1213.4 | 0.67612 | 5.793
2024-12-09 | 23:17 | Data | 0 | 32.744 | 31.164 | 182.649 | 7.63 | 172.12 | 2245.12 | 25.88 | 46.721 | 6.38 | 1.323 | 4.44 | 8680.41 | 1.688 | 97.9 | 77 | 1459 | 23.36 | 5642.3 | 2826.7 | 2774.9 | 4090.5 | 1213.4 | 0.6748 | 5.763
2024-12-09 | 23:17 | Data | 0 | 32.852 | 31.096 | 182.513 | 7.63 | 172.03 | 2253.25 | 25.88 | 46.721 | 6.38 | 1.32 | 4.449 | 8684.94 | 1.668 | 97.9 | 77.1 | 1465 | 23.41 | 5645.2 | 2835.9 | 2786.6 | 4101.3 | 1213.4 | 0.67458 | 5.769
2024-12-09 | 23:17 | Data | 0 | 32.777 | 31.096 | 182.423 | 7.63 | 172.03 | 2251.45 | 25.89 | 46.811 | 6.38 | 1.323 | 4.459 | 8703.03 | 1.843 | 97.9 | 77.1 | 1463 | 23.41 | 5657 | 2830.2 | 2816.3 | 4109.5 | 1213.4 | 0.6712 | 5.783
2024-12-09 | 23:17 | Data | 0 | 32.899 | 31.11 | 182.513 | 7.63 | 172.12 | 2254.16 | 25.88 | 46.721 | 6.38 | 1.328 | 4.437 | 8689.46 | 1.809 | 97.9 | 77 | 1465 | 23.36 | 5648.1 | 2826.8 | 2800.2 | 4101.4 | 1213.4 | 0.67204 | 5.765
2024-12-09 | 23:17 | Data | 0 | 32.757 | 31.096 | 182.423 | 7.63 | 172.075 | 2248.73 | 25.88 | 46.721 | 6.38 | 1.334 | 4.431 | 8671.37 | 1.83 | 97.9 | 76.9 | 1462 | 23.41 | 5636.4 | 2842.1 | 2800.4 | 4107.9 | 1213.4 | 0.67299 | 5.765
2024-12-09 | 23:17 | Data | 0 | 33.156 | 31.279 | 182.558 | 7.63 | 172.12 | 2249.64 | 25.88 | 46.721 | 6.38 | 1.334 | 4.453 | 8689.46 | 1.897 | 97.9 | 76.9 | 1462 | 23.36 | 5648.1 | 2836.1 | 2828.2 | 4112.7 | 1213.4 | 0.66686 | 5.788
2024-12-09 | 23:17 | Data | 0 | 32.987 | 30.941 | 182.649 | 7.63 | 172.256 | 2249.64 | 25.89 | 46.721 | 6.37 | 1.33 | 4.46 | 8693.98 | 1.836 | 97.9 | 77 | 1462 | 23.41 | 5651.1 | 2852.2 | 2831.6 | 4141.7 | 1213.4 | 0.67101 | 5.79
2024-12-09 | 23:17 | Data | 0 | 32.953 | 31.211 | 182.649 | 7.63 | 172.256 | 2249.64 | 25.88 | 46.721 | 6.37 | 1.331 | 4.426 | 8693.98 | 1.755 | 97.9 | 76.9 | 1462 | 23.36 | 5651.1 | 2819.6 | 2808.8 | 4102.4 | 1213.4 | 0.66901 | 5.757
2024-12-09 | 23:17 | Data | 0 | 32.744 | 31.096 | 182.649 | 7.63 | 172.21 | 2249.64 | 25.88 | 46.721 | 6.38 | 1.33 | 4.454 | 8703.03 | 1.755 | 97.9 | 77 | 1462 | 23.36 | 5657 | 2828.4 | 2811.3 | 4111.5 | 1213.4 | 0.6697 | 5.783
2024-12-09 | 23:17 | Data | 0 | 33.284 | 31.225 | 182.649 | 7.63 | 172.256 | 2252.35 | 25.88 | 46.811 | 6.38 | 1.338 | 4.454 | 8716.59 | 2.012 | 97.9 | 76.9 | 1464 | 23.41 | 5665.8 | 2823 | 2809.7 | 4103.8 | 1213.4 | 0.6714 | 5.792
2024-12-09 | 23:17 | Data | 0 | 32.98 | 31.11 | 182.513 | 7.63 | 172.075 | 2251.45 | 25.88 | 46.811 | 6.38 | 1.327 | 4.417 | 8716.59 | 1.728 | 97.9 | 76.9 | 1464 | 23.41 | 5665.8 | 2844.1 | 2839.3 | 4121.6 | 1213.4 | 0.6687 | 5.743
2024-12-09 | 23:17 | Data | 0 | 33.291 | 31.339 | 182.694 | 7.63 | 172.256 | 2252.35 | 25.88 | 46.721 | 6.38 | 1.319 | 4.436 | 8730.16 | 1.742 | 97.9 | 77.1 | 1464 | 23.41 | 5674.6 | 2841.3 | 2812.8 | 4116.3 | 1213.4 | 0.67249 | 5.754
2024-12-09 | 23:17 | Data | 0 | 33.054 | 31.123 | 182.694 | 7.63 | 172.12 | 2250.54 | 25.89 | 46.811 | 6.38 | 1.33 | 4.454 | 8730.16 | 1.836 | 97.9 | 77 | 1463 | 23.41 | 5674.6 | 2828.5 | 2830.9 | 4120.5 | 1213.4 | 0.66829 | 5.784
2024-12-09 | 23:18 | Data | 0 | 33.156 | 31.326 | 182.604 | 7.63 | 172.12 | 2252.35 | 25.89 | 46.721 | 6.38 | 1.331 | 4.411 | 8730.16 | 1.884 | 97.9 | 76.8 | 1464 | 23.32 | 5674.6 | 2849.9 | 2800.9 | 4117.5 | 1213.4 | 0.67298 | 5.742
2024-12-09 | 23:18 | Data | 0 | 32.98 | 31.312 | 182.468 | 7.63 | 172.12 | 2251.45 | 25.88 | 46.811 | 6.38 | 1.324 | 4.406 | 8730.16 | 1.674 | 97.9 | 76.9 | 1463 | 23.41 | 5674.6 | 2842.4 | 2811 | 4115.4 | 1213.4 | 0.67352 | 5.73
2024-12-09 | 23:18 | Data | 0 | 33.068 | 31.117 | 182.649 | 7.63 | 172.21 | 2252.35 | 25.88 | 46.721 | 6.38 | 1.334 | 4.413 | 8730.16 | 1.85 | 97.9 | 76.8 | 1465 | 23.36 | 5674.6 | 2852.3 | 2798 | 4114.4 | 1213.4 | 0.6758 | 5.747
2024-12-09 | 23:18 | Data | 0 | 33.277 | 31.029 | 182.468 | 7.63 | 172.12 | 2252.35 | 25.88 | 46.54 | 6.38 | 1.336 | 4.421 | 8730.16 | 1.924 | 97.9 | 76.8 | 1465 | 23.27 | 5674.6 | 2819.1 | 2807.8 | 4101.8 | 1213.4 | 0.67001 | 5.759
2024-12-09 | 23:18 | Data | 0 | 33.169 | 31.535 | 182.604 | 7.63 | 172.301 | 2252.35 | 25.89 | 46.721 | 6.38 | 1.335 | 4.408 | 8716.59 | 1.897 | 97.9 | 76.8 | 1464 | 23.41 | 5665.8 | 2845 | 2787 | 4096.4 | 1213.4 | 0.67507 | 5.742
2024-12-09 | 23:18 | Data | 0 | 33.156 | 31.11 | 182.513 | 7.63 | 172.12 | 2252.35 | 25.89 | 46.721 | 6.38 | 1.338 | 4.443 | 8725.64 | 1.87 | 97.9 | 76.9 | 1463 | 23.36 | 5671.7 | 2824.6 | 2796 | 4096.7 | 1213.4 | 0.67192 | 5.78
2024-12-09 | 23:18 | Data | 0 | 33.338 | 31.252 | 182.604 | 7.63 | 172.256 | 2252.35 | 25.88 | 46.45 | 6.38 | 1.329 | 4.446 | 8716.59 | 1.89 | 97.9 | 77 | 1463 | 23.22 | 5665.8 | 2838.4 | 2813.4 | 4115.9 | 1213.5 | 0.67093 | 5.775
2024-12-09 | 23:18 | Data | 0 | 32.953 | 31.306 | 182.739 | 7.64 | 172.21 | 2252.35 | 25.89 | 46.54 | 6.37 | 1.321 | 4.453 | 8721.11 | 1.857 | 97.9 | 77.1 | 1464 | 23.22 | 5668.7 | 2840.1 | 2836.3 | 4134.4 | 1213.5 | 0.66924 | 5.774
2024-12-09 | 23:18 | Data | 0 | 33.014 | 31.117 | 182.694 | 7.63 | 172.346 | 2253.25 | 25.88 | 46.45 | 6.38 | 1.321 | 4.446 | 8689.46 | 1.85 | 97.9 | 77.1 | 1464 | 23.22 | 5648.1 | 2834.6 | 2829.4 | 4125.4 | 1213.5 | 0.66917 | 5.767
2024-12-09 | 23:18 | Data | 0 | 32.96 | 31.333 | 182.558 | 7.63 | 172.21 | 2251.45 | 25.89 | 46.54 | 6.38 | 1.329 | 4.46 | 8689.46 | 1.796 | 97.9 | 77 | 1464 | 23.27 | 5648.1 | 2832.4 | 2823.9 | 4119 | 1213.5 | 0.66944 | 5.789
2024-12-09 | 23:18 | Data | 0 | 32.73 | 31.333 | 182.649 | 7.63 | 172.12 | 2255.97 | 25.88 | 46.45 | 6.38 | 1.326 | 4.437 | 8693.98 | 1.735 | 97.9 | 77 | 1466 | 23.27 | 5651.1 | 2802.8 | 2805.5 | 4087.5 | 1213.5 | 0.6672 | 5.763
2024-12-09 | 23:18 | Data | 0 | 32.953 | 31.11 | 182.558 | 7.63 | 172.075 | 2246.93 | 25.88 | 46.811 | 6.38 | 1.325 | 4.415 | 8689.46 | 1.958 | 97.9 | 76.9 | 1461 | 23.41 | 5648.1 | 2837 | 2791.1 | 4097.1 | 1213.5 | 0.67453 | 5.74
2024-12-09 | 23:18 | Data | 0 | 33.095 | 31.117 | 182.694 | 7.63 | 172.346 | 2252.35 | 25.88 | 46.811 | 6.38 | 1.331 | 4.392 | 8721.11 | 1.749 | 97.9 | 76.7 | 1464 | 23.36 | 5668.7 | 2842 | 2777.2 | 4092.8 | 1213.5 | 0.67625 | 5.723
2024-12-09 | 23:18 | Data | 0 | 32.953 | 31.117 | 182.513 | 7.63 | 172.075 | 2252.35 | 25.88 | 46.721 | 6.38 | 1.338 | 4.435 | 8707.55 | 1.951 | 97.9 | 76.8 | 1464 | 23.36 | 5659.9 | 2839 | 2739.9 | 4064.6 | 1213.5 | 0.67987 | 5.771
2024-12-09 | 23:18 | Data | 0 | 33.561 | 31.177 | 182.785 | 7.63 | 172.256 | 2252.35 | 25.88 | 46.721 | 6.38 | 1.343 | 4.442 | 8716.59 | 2.093 | 97.9 | 76.8 | 1464 | 23.36 | 5665.8 | 2834.1 | 2743.5 | 4062.5 | 1213.5 | 0.67951 | 5.784
2024-12-09 | 23:18 | Data | 0 | 32.953 | 31.312 | 182.513 | 7.63 | 172.21 | 2248.73 | 25.88 | 46.811 | 6.38 | 1.339 | 4.455 | 8730.16 | 1.816 | 97.9 | 76.9 | 1462 | 23.41 | 5674.6 | 2828.3 | 2771.5 | 4081.3 | 1213.5 | 0.67578 | 5.793
2024-12-09 | 23:18 | Data | 0 | 33.149 | 31.353 | 182.649 | 7.63 | 172.12 | 2249.64 | 25.88 | 46.811 | 6.38 | 1.329 | 4.434 | 8707.55 | 1.83 | 97.9 | 76.9 | 1462 | 23.41 | 5659.9 | 2826.2 | 2815.8 | 4111.1 | 1213.5 | 0.67048 | 5.762
2024-12-09 | 23:18 | Data | 0 | 32.723 | 31.083 | 182.513 | 7.63 | 172.12 | 2246.93 | 25.89 | 46.721 | 6.39 | 1.332 | 4.432 | 8693.98 | 1.843 | 97.9 | 76.9 | 1461 | 23.36 | 5651.1 | 2826.5 | 2830.5 | 4122.1 | 1213.5 | 0.66837 | 5.763
2024-12-09 | 23:19 | Data | 0 | 33.392 | 31.231 | 182.558 | 7.64 | 172.301 | 2246.02 | 25.88 | 46.721 | 6.38 | 1.331 | 4.44 | 8693.98 | 1.931 | 97.9 | 76.9 | 1460 | 23.41 | 5651.1 | 2840 | 2843.3 | 4134.8 | 1213.5 | 0.66908 | 5.771
2024-12-09 | 23:19 | Data | 0 | 32.953 | 31.326 | 182.649 | 7.63 | 172.21 | 2246.02 | 25.89 | 46.721 | 6.38 | 1.331 | 4.452 | 8680.41 | 1.843 | 97.9 | 77 | 1461 | 23.36 | 5642.3 | 2838.9 | 2830.1 | 4123.4 | 1213.5 | 0.66844 | 5.783
2024-12-09 | 23:19 | Data | 0 | 32.852 | 31.11 | 182.513 | 7.64 | 171.984 | 2246.93 | 25.88 | 46.721 | 6.38 | 1.338 | 4.449 | 8684.94 | 1.816 | 97.9 | 76.9 | 1461 | 23.36 | 5645.2 | 2837.1 | 2826.9 | 4126.1 | 1213.5 | 0.66805 | 5.787
2024-12-09 | 23:19 | Data | 0 | 33.027 | 31.123 | 182.694 | 7.63 | 172.21 | 2246.93 | 25.88 | 46.721 | 6.38 | 1.338 | 4.427 | 8689.46 | 1.674 | 97.9 | 76.8 | 1461 | 23.36 | 5648.1 | 2834 | 2815.3 | 4115.1 | 1213.5 | 0.67048 | 5.765
2024-12-09 | 23:19 | Data | 0 | 33.156 | 31.292 | 182.604 | 7.63 | 172.075 | 2244.22 | 25.88 | 46.811 | 6.39 | 1.334 | 4.423 | 8689.46 | 2.005 | 97.9 | 76.8 | 1459 | 23.41 | 5648.1 | 2841.3 | 2823.5 | 4118.9 | 1213.5 | 0.67057 | 5.757
2024-12-09 | 23:19 | Data | 0 | 33.183 | 31.123 | 182.468 | 7.63 | 172.03 | 2244.22 | 25.88 | 46.811 | 6.38 | 1.324 | 4.454 | 8680.41 | 1.857 | 97.9 | 77.1 | 1459 | 23.41 | 5642.3 | 2844 | 2776.3 | 4093.5 | 1213.5 | 0.67729 | 5.778
2024-12-09 | 23:19 | Data | 0 | 32.973 | 31.198 | 182.604 | 7.63 | 172.12 | 2244.22 | 25.88 | 46.721 | 6.38 | 1.328 | 4.477 | 8680.41 | 1.89 | 97.9 | 77.1 | 1458 | 23.36 | 5642.3 | 2828.9 | 2790.2 | 4095.9 | 1213.5 | 0.67286 | 5.806
2024-12-09 | 23:19 | Data | 0 | 32.804 | 31.002 | 182.558 | 7.63 | 172.21 | 2246.02 | 25.88 | 46.811 | 6.38 | 1.329 | 4.434 | 8680.41 | 1.843 | 97.9 | 76.9 | 1460 | 23.36 | 5642.3 | 2823.6 | 2783.9 | 4103.6 | 1213.5 | 0.66935 | 5.763
2024-12-09 | 23:19 | Data | 0 | 32.798 | 31.387 | 182.604 | 7.63 | 172.12 | 2244.22 | 25.89 | 46.721 | 6.38 | 1.336 | 4.404 | 8693.98 | 1.843 | 97.9 | 76.7 | 1459 | 23.41 | 5651.1 | 2829.1 | 2799.2 | 4108.2 | 1213.5 | 0.67241 | 5.74
2024-12-09 | 23:19 | Data | 0 | 32.96 | 31.285 | 182.694 | 7.63 | 172.256 | 2244.22 | 25.89 | 46.721 | 6.38 | 1.329 | 4.42 | 8671.37 | 1.843 | 97.9 | 76.9 | 1459 | 23.36 | 5636.4 | 2823.3 | 2803.3 | 4103.8 | 1213.5 | 0.66961 | 5.749
2024-12-09 | 23:19 | Data | 0 | 32.96 | 31.123 | 182.558 | 7.63 | 172.12 | 2243.31 | 25.88 | 46.721 | 6.38 | 1.327 | 4.427 | 8693.98 | 1.816 | 97.9 | 76.9 | 1459 | 23.36 | 5651.1 | 2831.2 | 2825.3 | 4122.3 | 1213.5 | 0.66856 | 5.753
2024-12-09 | 23:19 | Data | 0 | 33.237 | 31.339 | 182.694 | 7.63 | 172.21 | 2245.12 | 25.89 | 46.721 | 6.38 | 1.324 | 4.431 | 8666.85 | 1.863 | 97.9 | 77 | 1459 | 23.36 | 5633.5 | 2840.7 | 2800.5 | 4106.7 | 1213.5 | 0.67234 | 5.755
2024-12-09 | 23:19 | Data | 0 | 32.953 | 31.312 | 182.604 | 7.63 | 172.12 | 2242.41 | 25.89 | 46.811 | 6.38 | 1.328 | 4.439 | 8662.33 | 1.735 | 97.9 | 77 | 1457 | 23.36 | 5630.5 | 2833.3 | 2826.8 | 4112.5 | 1213.5 | 0.67087 | 5.767
2024-12-09 | 23:19 | Data | 0 | 33.129 | 31.231 | 182.649 | 7.63 | 172.256 | 2241.5 | 25.88 | 46.721 | 6.38 | 1.325 | 4.464 | 8680.41 | 1.992 | 97.9 | 77.1 | 1457 | 23.41 | 5642.3 | 2842 | 2834.1 | 4129.7 | 1213.5 | 0.66993 | 5.789
2024-12-09 | 23:19 | Data | 0 | 33.014 | 31.312 | 182.558 | 7.64 | 172.12 | 2241.5 | 25.88 | 46.811 | 6.38 | 1.329 | 4.441 | 8666.85 | 1.674 | 97.9 | 77 | 1457 | 23.41 | 5633.5 | 2825.2 | 2800.5 | 4098.8 | 1213.5 | 0.67179 | 5.77
2024-12-09 | 23:19 | Data | 0 | 33.014 | 31.123 | 182.694 | 7.63 | 172.301 | 2241.5 | 25.89 | 46.811 | 6.38 | 1.341 | 4.426 | 8662.33 | 1.83 | 97.9 | 76.7 | 1457 | 23.36 | 5630.5 | 2819.6 | 2810.6 | 4104.6 | 1213.5 | 0.66829 | 5.767
2024-12-09 | 23:19 | Data | 0 | 32.926 | 31.198 | 182.468 | 7.63 | 172.075 | 2241.5 | 25.88 | 46.721 | 6.38 | 1.348 | 4.446 | 8648.76 | 2.005 | 97.9 | 76.7 | 1457 | 23.32 | 5621.7 | 2825.5 | 2822.3 | 4111.8 | 1213.5 | 0.67016 | 5.794
2024-12-09 | 23:19 | Data | 0 | 33.399 | 31.177 | 182.604 | 7.64 | 172.256 | 2244.22 | 25.89 | 46.811 | 6.38 | 1.342 | 4.455 | 8662.33 | 2.032 | 97.9 | 76.8 | 1459 | 23.41 | 5630.5 | 2842.2 | 2778.4 | 4100.5 | 1213.5 | 0.67707 | 5.797
2024-12-09 | 23:20 | Data | 0 | 33.156 | 31.339 | 182.694 | 7.63 | 172.21 | 2244.22 | 25.88 | 46.811 | 6.38 | 1.342 | 4.43 | 8657.8 | 1.843 | 97.9 | 76.7 | 1459 | 23.41 | 5627.6 | 2827.9 | 2806.3 | 4103 | 1213.5 | 0.6718 | 5.773
2024-12-09 | 23:20 | Data | 0 | 33.135 | 31.508 | 182.649 | 7.63 | 172.256 | 2246.93 | 25.86 | 46.721 | 6.38 | 1.339 | 4.431 | 8698.5 | 1.911 | 97.9 | 76.8 | 1461 | 23.36 | 5654 | 2820.4 | 2792.3 | 4087.7 | 1213.5 | 0.67481 | 5.77
2024-12-09 | 23:20 | Data | 0 | 33.068 | 31.123 | 182.649 | 7.63 | 172.256 | 2252.35 | 25.88 | 47.082 | 6.38 | 1.331 | 4.427 | 8707.55 | 1.904 | 97.9 | 76.9 | 1464 | 23.54 | 5659.9 | 2823 | 2768 | 4077.5 | 1213.5 | 0.67372 | 5.758
2024-12-09 | 23:20 | Data | 0 | 33.392 | 31.164 | 182.558 | 7.63 | 172.12 | 2242.41 | 25.89 | 46.721 | 6.38 | 1.336 | 4.443 | 8847.74 | 1.789 | 97.9 | 76.9 | 1458 | 23.36 | 5751 | 2829.5 | 2796.3 | 4099.3 | 1213.5 | 0.67205 | 5.78
2024-12-09 | 23:20 | Data | 0 | 33.196 | 31.339 | 182.604 | 7.63 | 172.21 | 2244.22 | 25.88 | 46.721 | 6.38 | 1.329 | 4.447 | 8969.84 | 1.762 | 97.9 | 77 | 1458 | 23.41 | 5830.4 | 2832.7 | 2813.8 | 4110.7 | 1213.5 | 0.67064 | 5.775
2024-12-09 | 23:20 | Data | 0 | 33.183 | 31.339 | 182.649 | 7.63 | 172.256 | 2244.22 | 25.88 | 46.721 | 6.38 | 1.319 | 4.453 | 8689.46 | 1.843 | 97.9 | 77.2 | 1459 | 23.36 | 5648.1 | 2830.9 | 2830.4 | 4124 | 1213.5 | 0.66813 | 5.771
2024-12-09 | 23:20 | Data | 0 | 32.744 | 31.022 | 182.558 | 7.63 | 172.21 | 2246.93 | 25.88 | 46.811 | 6.38 | 1.324 | 4.412 | 8703.03 | 1.843 | 97.9 | 76.9 | 1461 | 23.36 | 5657 | 2830.8 | 2821.9 | 4115.1 | 1213.5 | 0.66933 | 5.735
2024-12-09 | 23:20 | Data | 0 | 33.183 | 31.441 | 182.694 | 7.63 | 172.256 | 2246.93 | 25.89 | 46.811 | 6.38 | 1.322 | 4.415 | 8707.55 | 1.809 | 97.9 | 77 | 1461 | 23.36 | 5659.9 | 2838.4 | 2814.6 | 4114.9 | 1213.6 | 0.67118 | 5.739
2024-12-09 | 23:20 | Data | 0 | 32.757 | 31.225 | 182.558 | 7.64 | 172.256 | 2247.83 | 25.88 | 46.811 | 6.38 | 1.32 | 4.442 | 8693.98 | 1.735 | 97.9 | 77.1 | 1461 | 23.36 | 5651.1 | 2823.5 | 2788.2 | 4086.7 | 1213.6 | 0.67335 | 5.761
2024-12-09 | 23:20 | Data | 0 | 33.27 | 31.137 | 182.604 | 7.63 | 172.12 | 2245.12 | 25.88 | 46.721 | 6.38 | 1.313 | 4.446 | 8707.55 | 2.12 | 97.9 | 77.2 | 1459 | 23.41 | 5659.9 | 2834.3 | 2792.9 | 4096.8 | 1213.6 | 0.67078 | 5.759
2024-12-09 | 23:20 | Data | 0 | 33.318 | 31.144 | 182.694 | 7.63 | 172.256 | 2244.22 | 25.88 | 46.359 | 6.38 | 1.324 | 4.44 | 8703.03 | 1.897 | 97.9 | 77 | 1459 | 23.22 | 5657 | 2861.4 | 2792 | 4116.8 | 1213.6 | 0.67732 | 5.764
2024-12-09 | 23:20 | Data | 0 | 32.98 | 31.285 | 182.785 | 7.63 | 172.256 | 2247.83 | 25.88 | 46.45 | 6.38 | 1.341 | 4.446 | 8693.98 | 1.735 | 97.9 | 76.8 | 1461 | 23.27 | 5651.1 | 2829.6 | 2775.5 | 4082.4 | 1213.6 | 0.67691 | 5.787
2024-12-09 | 23:20 | Data | 0 | 32.953 | 31.11 | 182.649 | 7.63 | 172.12 | 2244.22 | 25.89 | 46.54 | 6.38 | 1.331 | 4.449 | 8693.98 | 1.843 | 97.9 | 77 | 1459 | 23.27 | 5651.1 | 2821.1 | 2787.9 | 4087.1 | 1213.6 | 0.6742 | 5.78
2024-12-09 | 23:20 | Data | 0 | 33.237 | 31.123 | 182.604 | 7.63 | 172.301 | 2240.6 | 25.88 | 46.54 | 6.38 | 1.325 | 4.41 | 8662.33 | 1.85 | 97.9 | 76.9 | 1456 | 23.27 | 5630.5 | 2835.6 | 2806.5 | 4109.3 | 1213.6 | 0.67241 | 5.734
2024-12-09 | 23:20 | Data | 0 | 33.183 | 31.447 | 182.649 | 7.63 | 172.301 | 2241.5 | 25.88 | 46.54 | 6.38 | 1.32 | 4.428 | 8671.37 | 1.789 | 97.9 | 77 | 1457 | 23.27 | 5636.4 | 2825.8 | 2782 | 4085 | 1213.6 | 0.67488 | 5.749
2024-12-09 | 23:20 | Data | 0 | 32.953 | 31.326 | 182.649 | 7.63 | 172.21 | 2241.5 | 25.89 | 46.45 | 6.38 | 1.323 | 4.454 | 8662.33 | 1.843 | 97.9 | 77.1 | 1457 | 23.22 | 5630.5 | 2828.9 | 2796.3 | 4094.1 | 1213.6 | 0.67356 | 5.776
2024-12-09 | 23:20 | Data | 0 | 33.351 | 31.366 | 182.558 | 7.63 | 172.21 | 2241.5 | 25.89 | 46.54 | 6.37 | 1.329 | 4.428 | 8662.33 | 1.863 | 97.9 | 76.9 | 1457 | 23.27 | 5630.5 | 2840.6 | 2811 | 4112.4 | 1213.6 | 0.67289 | 5.758
2024-12-09 | 23:20 | Data | 0 | 33.176 | 31.117 | 182.649 | 7.63 | 172.12 | 2241.5 | 25.88 | 46.54 | 6.38 | 1.329 | 4.446 | 8680.41 | 1.89 | 97.9 | 77 | 1457 | 23.27 | 5642.3 | 2835.8 | 2796.6 | 4103.1 | 1213.6 | 0.67329 | 5.773
2024-12-09 | 23:21 | Data | 0 | 32.953 | 31.225 | 182.513 | 7.63 | 172.12 | 2242.41 | 25.88 | 46.45 | 6.38 | 1.322 | 4.446 | 8689.46 | 2.019 | 97.9 | 77.1 | 1458 | 23.22 | 5648.1 | 2822.7 | 2811.1 | 4101.6 | 1213.6 | 0.67119 | 5.769
2024-12-09 | 23:21 | Data | 0 | 33.378 | 31.123 | 182.604 | 7.63 | 172.21 | 2242.41 | 25.88 | 47.082 | 6.38 | 1.331 | 4.437 | 8680.41 | 2.046 | 97.9 | 76.9 | 1458 | 23.54 | 5642.3 | 2832 | 2818.4 | 4108.9 | 1213.6 | 0.67085 | 5.768
2024-12-09 | 23:21 | Data | 0 | 32.953 | 31.11 | 182.558 | 7.63 | 172.075 | 2242.41 | 25.88 | 46.45 | 6.38 | 1.329 | 4.415 | 8680.41 | 1.843 | 97.9 | 76.9 | 1457 | 23.27 | 5642.3 | 2839.4 | 2794.2 | 4103.5 | 1213.6 | 0.67485 | 5.746
2024-12-09 | 23:21 | Data | 0 | 33.284 | 31.387 | 182.649 | 7.63 | 172.301 | 2240.6 | 25.89 | 46.45 | 6.38 | 1.334 | 4.427 | 8703.03 | 1.843 | 97.9 | 76.8 | 1457 | 23.22 | 5657 | 2837.5 | 2783.8 | 4091.5 | 1213.6 | 0.67642 | 5.761
2024-12-09 | 23:21 | Data | 0 | 32.96 | 31.285 | 182.604 | 7.63 | 172.21 | 2241.5 | 25.88 | 46.45 | 6.38 | 1.329 | 4.419 | 8693.98 | 1.843 | 97.9 | 76.9 | 1457 | 23.22 | 5651.1 | 2826.2 | 2799.9 | 4095.5 | 1213.6 | 0.67286 | 5.748
2024-12-09 | 23:21 | Data | 0 | 33.176 | 31.117 | 182.604 | 7.63 | 172.03 | 2241.5 | 25.88 | 46.54 | 6.38 | 1.321 | 4.441 | 8693.98 | 1.843 | 97.9 | 77.1 | 1457 | 23.27 | 5651.1 | 2824.4 | 2800.2 | 4098.2 | 1213.6 | 0.67105 | 5.763
2024-12-09 | 23:21 | Data | 0 | 32.953 | 31.312 | 182.468 | 7.63 | 172.12 | 2241.5 | 25.88 | 46.45 | 6.38 | 1.335 | 4.436 | 8703.03 | 1.728 | 97.9 | 76.9 | 1457 | 23.22 | 5657 | 2813.4 | 2809.5 | 4098.1 | 1213.6 | 0.66774 | 5.771
2024-12-09 | 23:21 | Data | 0 | 33.338 | 31.454 | 182.649 | 7.63 | 172.12 | 2244.22 | 25.88 | 46.45 | 6.38 | 1.339 | 4.42 | 8698.5 | 2.039 | 97.9 | 76.8 | 1459 | 23.27 | 5654 | 2828.7 | 2788.7 | 4093.1 | 1213.6 | 0.67254 | 5.759
2024-12-09 | 23:21 | Data | 0 | 33.068 | 31.535 | 182.785 | 7.63 | 172.256 | 2244.22 | 25.88 | 46.54 | 6.38 | 1.332 | 4.43 | 8684.94 | 1.769 | 97.9 | 76.9 | 1459 | 23.27 | 5645.2 | 2823 | 2798.4 | 4095.8 | 1213.6 | 0.67055 | 5.762
2024-12-09 | 23:21 | Data | 0 | 32.953 | 31.11 | 182.604 | 7.63 | 172.075 | 2244.22 | 25.89 | 46.45 | 6.38 | 1.334 | 4.44 | 8693.98 | 1.958 | 97.9 | 76.9 | 1459 | 23.22 | 5651.1 | 2828.5 | 2836.7 | 4126.9 | 1213.6 | 0.66675 | 5.773
2024-12-09 | 23:21 | Data | 0 | 33.068 | 31.441 | 182.558 | 7.63 | 172.075 | 2243.31 | 25.89 | 46.45 | 6.38 | 1.332 | 4.467 | 8689.46 | 1.715 | 97.9 | 77 | 1459 | 23.22 | 5648.1 | 2821.6 | 2816.2 | 4102.4 | 1213.6 | 0.67097 | 5.799
2024-12-09 | 23:21 | Data | 0 | 33.392 | 31.171 | 182.649 | 7.63 | 172.256 | 2243.31 | 25.89 | 46.54 | 6.38 | 1.322 | 4.438 | 8693.98 | 2.052 | 97.9 | 77.1 | 1459 | 23.27 | 5651.1 | 2817.8 | 2774.6 | 4075.9 | 1213.6 | 0.67288 | 5.761
2024-12-09 | 23:21 | Data | 0 | 33.068 | 31.117 | 182.604 | 7.63 | 172.256 | 2245.12 | 25.88 | 46.45 | 6.38 | 1.323 | 4.442 | 8689.46 | 1.85 | 97.9 | 77 | 1459 | 23.27 | 5648.1 | 2838.5 | 2794.6 | 4101.6 | 1213.6 | 0.6737 | 5.765
2024-12-09 | 23:21 | Data | 0 | 33.068 | 31.312 | 182.649 | 7.63 | 172.12 | 2238.79 | 25.88 | 46.45 | 6.38 | 1.314 | 4.455 | 8680.41 | 1.884 | 97.9 | 77.2 | 1455 | 23.27 | 5642.3 | 2839 | 2792.6 | 4100.7 | 1213.6 | 0.675 | 5.769
2024-12-09 | 23:21 | Data | 0 | 33.237 | 31.123 | 182.604 | 7.63 | 172.256 | 2245.12 | 25.88 | 46.63 | 6.38 | 1.329 | 4.454 | 8671.37 | 1.877 | 97.9 | 77 | 1459 | 23.32 | 5636.4 | 2832.1 | 2766.9 | 4100.9 | 1213.6 | 0.67526 | 5.784
2024-12-09 | 23:21 | Data | 0 | 33.183 | 31.346 | 182.694 | 7.63 | 172.346 | 2249.64 | 25.88 | 46.721 | 6.38 | 1.343 | 4.425 | 8671.37 | 1.83 | 97.9 | 76.7 | 1462 | 23.41 | 5636.4 | 2839.9 | 2828 | 4129 | 1213.6 | 0.6715 | 5.768
2024-12-09 | 23:21 | Data | 0 | 33.338 | 31.441 | 182.649 | 7.64 | 172.21 | 2248.73 | 25.88 | 46.45 | 6.38 | 1.341 | 4.437 | 8657.8 | 1.85 | 97.9 | 76.8 | 1462 | 23.27 | 5627.6 | 2841.4 | 2795.4 | 4109.1 | 1213.6 | 0.67362 | 5.777
2024-12-09 | 23:22 | Data | 0 | 32.953 | 31.312 | 182.604 | 7.63 | 172.075 | 2249.64 | 25.88 | 46.45 | 6.38 | 1.328 | 4.449 | 8680.41 | 1.843 | 97.9 | 77 | 1462 | 23.22 | 5642.3 | 2836.4 | 2833.1 | 4130.4 | 1213.6 | 0.66866 | 5.777
2024-12-09 | 23:22 | Data | 0 | 33.183 | 31.333 | 182.649 | 7.64 | 172.301 | 2249.64 | 25.89 | 46.721 | 6.38 | 1.33 | 4.427 | 8680.41 | 1.742 | 97.9 | 76.9 | 1462 | 23.36 | 5642.3 | 2841.1 | 2796.4 | 4109.7 | 1213.6 | 0.67357 | 5.756
2024-12-09 | 23:22 | Data | 0 | 33.21 | 31.117 | 182.694 | 7.63 | 172.21 | 2249.64 | 25.88 | 46.45 | 6.38 | 1.334 | 4.434 | 8671.37 | 1.944 | 97.9 | 76.9 | 1462 | 23.22 | 5636.4 | 2825.3 | 2808.1 | 4103.3 | 1213.6 | 0.6696 | 5.768
2024-12-09 | 23:22 | Data | 0 | 32.98 | 31.009 | 182.558 | 7.64 | 172.301 | 2249.64 | 25.88 | 46.54 | 6.38 | 1.326 | 4.443 | 8689.46 | 2.046 | 97.9 | 77 | 1462 | 23.27 | 5648.1 | 2837 | 2800.6 | 4099.4 | 1213.6 | 0.67243 | 5.769
2024-12-09 | 23:22 | Data | 0 | 33.068 | 31.312 | 182.604 | 7.63 | 172.21 | 2249.64 | 25.88 | 46.54 | 6.38 | 1.329 | 4.446 | 8689.46 | 1.931 | 97.9 | 77 | 1462 | 23.22 | 5648.1 | 2838.4 | 2772.4 | 4088.2 | 1213.6 | 0.67567 | 5.774
2024-12-09 | 23:22 | Data | 0 | 33.291 | 31.123 | 182.785 | 7.63 | 172.301 | 2248.73 | 25.88 | 46.45 | 6.38 | 1.325 | 4.448 | 8680.41 | 1.911 | 97.9 | 77.1 | 1462 | 23.27 | 5642.3 | 2828.2 | 2767.1 | 4072.7 | 1213.6 | 0.67686 | 5.773
2024-12-09 | 23:22 | Data | 0 | 32.96 | 31.083 | 182.604 | 7.63 | 172.256 | 2247.83 | 25.88 | 46.721 | 6.39 | 1.325 | 4.445 | 8693.98 | 1.87 | 97.9 | 77 | 1461 | 23.36 | 5651.1 | 2816.9 | 2784.9 | 4080.6 | 1213.6 | 0.67489 | 5.77
2024-12-09 | 23:22 | Data | 0 | 33.156 | 31.225 | 182.694 | 7.63 | 172.256 | 2249.64 | 25.88 | 46.54 | 6.38 | 1.339 | 4.43 | 8671.37 | 2.059 | 97.9 | 76.8 | 1462 | 23.22 | 5636.4 | 2832.5 | 2757 | 4071.3 | 1213.6 | 0.67434 | 5.769
2024-12-09 | 23:22 | Data | 0 | 33.068 | 31.427 | 182.649 | 7.63 | 172.256 | 2248.73 | 25.88 | 46.54 | 6.38 | 1.348 | 4.427 | 8693.98 | 1.924 | 97.9 | 76.6 | 1462 | 23.27 | 5651.1 | 2824.4 | 2796.9 | 4096.3 | 1213.6 | 0.67151 | 5.777
2024-12-09 | 23:22 | Data | 0 | 33.378 | 31.225 | 182.649 | 7.63 | 172.301 | 2249.64 | 25.88 | 46.45 | 6.38 | 1.331 | 4.453 | 8680.41 | 1.897 | 97.9 | 77 | 1462 | 23.22 | 5642.3 | 2838.9 | 2786.7 | 4099.9 | 1213.7 | 0.67507 | 5.784
2024-12-09 | 23:22 | Data | 0 | 33.405 | 31.393 | 182.739 | 7.63 | 172.301 | 2249.64 | 25.88 | 46.721 | 6.39 | 1.33 | 4.447 | 8698.5 | 2.019 | 97.9 | 77 | 1462 | 23.36 | 5654 | 2827.9 | 2784.3 | 4090.2 | 1213.7 | 0.67357 | 5.777
2024-12-09 | 23:22 | Data | 0 | 32.967 | 31.252 | 182.739 | 7.63 | 172.21 | 2248.73 | 25.88 | 46.54 | 6.38 | 1.331 | 4.432 | 8693.98 | 1.62 | 97.9 | 76.9 | 1461 | 23.27 | 5651.1 | 2833.5 | 2783.4 | 4087.3 | 1213.7 | 0.67502 | 5.763
2024-12-09 | 23:22 | Data | 0 | 33.088 | 31.528 | 182.558 | 7.63 | 172.21 | 2247.83 | 25.88 | 46.54 | 6.38 | 1.329 | 4.431 | 8680.41 | 1.735 | 97.9 | 76.9 | 1461 | 23.22 | 5642.3 | 2823.4 | 2772.1 | 4078.2 | 1213.7 | 0.6736 | 5.761
2024-12-09 | 23:22 | Data | 0 | 33.129 | 31.65 | 182.604 | 7.63 | 172.256 | 2246.02 | 25.89 | 46.54 | 6.38 | 1.322 | 4.441 | 8666.85 | 1.85 | 97.9 | 77.1 | 1460 | 23.27 | 5633.5 | 2830.3 | 2769.2 | 4079.8 | 1213.7 | 0.67612 | 5.763
2024-12-09 | 23:22 | Data | 0 | 33.183 | 31.285 | 182.649 | 7.63 | 172.21 | 2246.93 | 25.88 | 46.45 | 6.38 | 1.335 | 4.452 | 8662.33 | 1.85 | 97.9 | 76.9 | 1461 | 23.22 | 5630.5 | 2830.5 | 2797.3 | 4098.1 | 1213.7 | 0.67344 | 5.789
2024-12-09 | 23:22 | Data | 0 | 33.399 | 31.339 | 182.604 | 7.63 | 172.301 | 2249.64 | 25.88 | 46.54 | 6.38 | 1.344 | 4.449 | 8662.33 | 2.066 | 97.9 | 76.8 | 1462 | 23.27 | 5630.5 | 2824.3 | 2790.1 | 4088.5 | 1213.7 | 0.67341 | 5.792
2024-12-09 | 23:22 | Data | 0 | 32.96 | 31.339 | 182.694 | 7.63 | 172.301 | 2244.22 | 25.88 | 46.45 | 6.38 | 1.32 | 4.446 | 8662.33 | 1.735 | 97.9 | 77.1 | 1459 | 23.22 | 5630.5 | 2844.3 | 2811.9 | 4117.8 | 1213.7 | 0.67297 | 5.767
2024-12-09 | 23:22 | Data | 0 | 33.169 | 31.542 | 182.694 | 7.63 | 172.21 | 2244.22 | 25.86 | 46.54 | 6.38 | 1.321 | 4.403 | 8680.41 | 1.836 | 97.9 | 76.9 | 1459 | 23.27 | 5642.3 | 2821.5 | 2808.8 | 4098.6 | 1213.7 | 0.66936 | 5.724
2024-12-09 | 23:23 | Data | 0 | 33.183 | 31.508 | 182.558 | 7.63 | 172.346 | 2244.22 | 25.88 | 46.54 | 6.38 | 1.329 | 4.409 | 8671.37 | 1.735 | 97.9 | 76.8 | 1459 | 23.32 | 5636.4 | 2836 | 2810.9 | 4114.8 | 1213.7 | 0.67018 | 5.739
2024-12-09 | 23:23 | Data | 0 | 33.405 | 31.252 | 182.739 | 7.63 | 172.391 | 2242.41 | 25.88 | 46.721 | 6.38 | 1.328 | 4.419 | 8680.41 | 2.046 | 97.9 | 76.9 | 1457 | 23.41 | 5642.3 | 2832.7 | 2813.7 | 4113.4 | 1213.7 | 0.66977 | 5.747
2024-12-09 | 23:23 | Data | 0 | 33.169 | 31.225 | 182.649 | 7.63 | 172.21 | 2241.5 | 25.89 | 46.54 | 6.38 | 1.33 | 4.439 | 8662.33 | 2.052 | 97.9 | 76.9 | 1457 | 23.27 | 5630.5 | 2819.6 | 2796 | 4097.3 | 1213.7 | 0.66955 | 5.77
2024-12-09 | 23:23 | Data | 0 | 32.967 | 31.117 | 182.649 | 7.63 | 172.256 | 2240.6 | 25.89 | 46.54 | 6.38 | 1.329 | 4.453 | 8666.85 | 2.012 | 97.9 | 77 | 1457 | 23.22 | 5633.5 | 2838 | 2776.9 | 4087.4 | 1213.7 | 0.67807 | 5.782
2024-12-09 | 23:23 | Data | 0 | 33.176 | 31.319 | 182.604 | 7.63 | 172.12 | 2241.5 | 25.88 | 46.721 | 6.38 | 1.327 | 4.456 | 8666.85 | 1.89 | 97.9 | 77.1 | 1457 | 23.36 | 5633.5 | 2830 | 2759.2 | 4072.3 | 1213.7 | 0.67761 | 5.782
2024-12-09 | 23:23 | Data | 0 | 32.973 | 31.319 | 182.785 | 7.63 | 172.21 | 2244.22 | 25.89 | 46.54 | 6.38 | 1.325 | 4.437 | 8680.41 | 1.769 | 97.9 | 77 | 1459 | 23.22 | 5642.3 | 2802.8 | 2756.1 | 4056 | 1213.7 | 0.6743 | 5.761
2024-12-09 | 23:23 | Data | 0 | 33.608 | 31.366 | 182.739 | 7.63 | 172.346 | 2241.5 | 25.88 | 46.54 | 6.38 | 1.337 | 4.427 | 8680.41 | 2.052 | 97.9 | 76.8 | 1458 | 23.22 | 5642.3 | 2844.3 | 2780.9 | 4097.5 | 1213.7 | 0.67684 | 5.764
2024-12-09 | 23:23 | Data | 0 | 32.96 | 31.117 | 182.739 | 7.64 | 172.391 | 2240.6 | 25.89 | 46.54 | 6.38 | 1.331 | 4.417 | 8680.41 | 1.836 | 97.9 | 76.8 | 1457 | 23.22 | 5642.3 | 2833.6 | 2786.1 | 4092.3 | 1213.7 | 0.67456 | 5.746
2024-12-09 | 23:23 | Data | 0 | 33.608 | 31.4 | 182.694 | 7.63 | 172.346 | 2242.41 | 25.89 | 46.45 | 6.38 | 1.329 | 4.428 | 8680.41 | 1.85 | 97.9 | 76.9 | 1457 | 23.22 | 5642.3 | 2852.3 | 2793.1 | 4113.9 | 1213.7 | 0.67555 | 5.758
2024-12-09 | 23:23 | Data | 0 | 33.183 | 31.137 | 182.604 | 7.63 | 172.256 | 2241.5 | 25.88 | 46.54 | 6.38 | 1.323 | 4.44 | 8671.37 | 2.046 | 97.9 | 77 | 1457 | 23.27 | 5636.4 | 2826.3 | 2810.4 | 4108.1 | 1213.7 | 0.66943 | 5.764
2024-12-09 | 23:23 | Data | 0 | 32.96 | 31.117 | 182.604 | 7.63 | 172.256 | 2241.5 | 25.88 | 46.45 | 6.38 | 1.332 | 4.427 | 8662.33 | 1.836 | 97.9 | 76.9 | 1457 | 23.22 | 5630.5 | 2826.2 | 2796 | 4095.8 | 1213.7 | 0.67141 | 5.76
2024-12-09 | 23:23 | Data | 0 | 33.007 | 31.326 | 182.694 | 7.63 | 172.21 | 2242.41 | 25.88 | 46.54 | 6.38 | 1.343 | 4.427 | 8680.41 | 1.755 | 97.9 | 76.7 | 1458 | 23.27 | 5642.3 | 2823.2 | 2803.5 | 4105.6 | 1213.7 | 0.6701 | 5.769
2024-12-09 | 23:23 | Data | 0 | 33.412 | 31.339 | 182.694 | 7.63 | 172.436 | 2242.41 | 25.88 | 46.54 | 6.38 | 1.336 | 4.445 | 8671.37 | 1.857 | 97.9 | 76.9 | 1457 | 23.27 | 5636.4 | 2829.8 | 2814.6 | 4110.1 | 1213.7 | 0.66791 | 5.78
2024-12-09 | 23:23 | Data | 0 | 33.561 | 31.366 | 182.785 | 7.63 | 172.301 | 2241.5 | 25.88 | 46.45 | 6.38 | 1.339 | 4.448 | 8693.98 | 1.944 | 97.9 | 76.9 | 1458 | 23.27 | 5651.1 | 2835.5 | 2795 | 4103.7 | 1213.7 | 0.67317 | 5.787
2024-12-09 | 23:23 | Data | 0 | 33.075 | 31.549 | 182.739 | 7.63 | 172.301 | 2243.31 | 25.89 | 46.45 | 6.38 | 1.336 | 4.438 | 8680.41 | 1.735 | 97.9 | 76.9 | 1459 | 23.27 | 5642.3 | 2841.2 | 2775 | 4096 | 1213.7 | 0.67511 | 5.774
2024-12-09 | 23:23 | Data | 0 | 33.412 | 31.454 | 182.785 | 7.63 | 172.346 | 2244.22 | 25.89 | 46.45 | 6.38 | 1.336 | 4.447 | 8680.41 | 1.85 | 97.9 | 76.9 | 1459 | 23.27 | 5642.3 | 2839.5 | 2769 | 4089.9 | 1213.7 | 0.67803 | 5.783
2024-12-09 | 23:23 | Data | 0 | 33.21 | 31.312 | 182.649 | 7.63 | 172.256 | 2244.22 | 25.88 | 46.45 | 6.38 | 1.33 | 4.455 | 8703.03 | 1.735 | 97.9 | 77 | 1459 | 23.22 | 5657 | 2825 | 2788 | 4084.2 | 1213.7 | 0.67363 | 5.786
2024-12-09 | 23:23 | Data | 0 | 33.385 | 31.441 | 182.739 | 7.63 | 172.301 | 2244.22 | 25.88 | 46.54 | 6.38 | 1.337 | 4.445 | 9141.68 | 1.951 | 97.9 | 76.9 | 1459 | 23.22 | 5942.1 | 2835.9 | 2791 | 4097.7 | 1213.7 | 0.6751 | 5.781
2024-12-09 | 23:24 | Data | 0 | 33.162 | 31.535 | 182.649 | 7.63 | 172.301 | 2245.12 | 25.88 | 46.45 | 6.38 | 1.334 | 4.438 | 8707.55 | 1.816 | 97.9 | 76.9 | 1460 | 23.22 | 5659.9 | 2833.5 | 2777.9 | 4090.4 | 1213.7 | 0.67465 | 5.771
2024-12-09 | 23:24 | Data | 0 | 33.297 | 31.555 | 182.649 | 7.64 | 172.256 | 2245.12 | 25.88 | 46.45 | 6.38 | 1.329 | 4.447 | 8703.03 | 1.85 | 97.9 | 77 | 1458 | 23.27 | 5657 | 2832.2 | 2772.7 | 4084.1 | 1213.7 | 0.67683 | 5.776
2024-12-09 | 23:24 | Data | 0 | 32.798 | 31.231 | 182.694 | 7.63 | 172.256 | 2243.31 | 25.89 | 46.991 | 6.38 | 1.332 | 4.447 | 8680.41 | 1.816 | 97.9 | 76.9 | 1459 | 23.54 | 5642.3 | 2821.6 | 2769 | 4078 | 1213.7 | 0.67431 | 5.78
2024-12-09 | 23:24 | Data | 0 | 33.095 | 31.238 | 182.83 | 7.63 | 172.391 | 2246.93 | 25.88 | 46.54 | 6.38 | 1.338 | 4.44 | 8693.98 | 1.857 | 97.9 | 76.9 | 1461 | 23.27 | 5651.1 | 1752.1 | 2223.8 | 2843.6 | 1213.7 | 0.61377 | 5.779
2024-12-09 | 23:24 | Data | 0 | 32.953 | 31.225 | 182.83 | 7.63 | 172.346 | 2246.93 | 25.88 | 46.721 | 6.38 | 1.33 | 4.441 | 8689.46 | 1.904 | 97.9 | 76.9 | 1461 | 23.36 | 5648.1 | 1750.6 | 2223.1 | 2841.7 | 1213.7 | 0.6136 | 5.771
2024-12-09 | 23:24 | Data | 0 | 32.953 | 31.225 | 182.513 | 7.64 | 172.12 | 2246.93 | 25.88 | 46.721 | 6.38 | 1.339 | 4.438 | 8703.03 | 1.958 | 97.9 | 76.8 | 1461 | 23.32 | 5657 | 1770.8 | 2261.4 | 2884.9 | 1213.7 | 0.61133 | 5.778
2024-12-09 | 23:24 | Data | 0 | 33.493 | 31.569 | 182.739 | 7.63 | 172.301 | 2246.93 | 25.89 | 46.991 | 6.38 | 1.335 | 4.465 | 8730.16 | 2.046 | 97.9 | 77 | 1460 | 23.41 | 5674.6 | 1764.3 | 2226.8 | 2853.7 | 1213.7 | 0.61512 | 5.8
2024-12-09 | 23:24 | Data | 0 | 32.96 | 31.225 | 182.604 | 7.63 | 172.256 | 2244.22 | 25.88 | 46.811 | 6.38 | 1.335 | 4.417 | 8712.07 | 1.843 | 97.9 | 76.8 | 1459 | 23.36 | 5662.8 | 1765.4 | 2219.6 | 2847.2 | 1213.7 | 0.61759 | 5.752
2024-12-09 | 23:24 | Data | 0 | 33.378 | 31.569 | 182.694 | 7.63 | 172.346 | 2246.02 | 25.88 | 46.811 | 6.38 | 1.341 | 4.412 | 8716.59 | 1.924 | 97.9 | 76.7 | 1460 | 23.36 | 5665.8 | 1738 | 2222.9 | 2834.3 | 1213.7 | 0.61013 | 5.753
2024-12-09 | 23:24 | Data | 0 | 33.297 | 31.339 | 182.739 | 7.63 | 172.391 | 2246.93 | 25.89 | 46.721 | 6.38 | 1.332 | 4.425 | 8721.11 | 1.857 | 97.9 | 76.8 | 1461 | 23.41 | 5668.7 | 1747.4 | 2213 | 2830.9 | 1213.7 | 0.61473 | 5.759
2024-12-09 | 23:24 | Data | 0 | 33.129 | 31.312 | 182.604 | 7.63 | 172.256 | 2246.93 | 25.88 | 46.811 | 6.38 | 1.325 | 4.463 | 8716.59 | 1.938 | 97.9 | 77.1 | 1461 | 23.41 | 5665.8 | 1745.8 | 2234.5 | 2847.2 | 1213.7 | 0.61078 | 5.789
2024-12-09 | 23:24 | Data | 0 | 33.399 | 31.279 | 182.83 | 7.64 | 172.301 | 2246.93 | 25.89 | 46.721 | 6.38 | 1.329 | 4.454 | 8698.5 | 1.958 | 97.9 | 77 | 1461 | 23.36 | 5654 | 1766.4 | 2216.3 | 2846.3 | 1213.7 | 0.61829 | 5.782
2024-12-09 | 23:24 | Data | 0 | 32.96 | 31.441 | 182.83 | 7.64 | 172.346 | 2248.73 | 25.88 | 46.63 | 6.39 | 1.332 | 4.427 | 8689.46 | 1.931 | 97.9 | 76.9 | 1462 | 23.27 | 5648.1 | 1769.7 | 2226 | 2856.6 | 1213.7 | 0.61728 | 5.758
2024-12-09 | 23:24 | Data | 0 | 33.183 | 31.454 | 182.694 | 7.63 | 172.301 | 2246.93 | 25.88 | 46.54 | 6.38 | 1.324 | 4.446 | 8693.98 | 2.012 | 97.9 | 77.1 | 1461 | 23.22 | 5651.1 | 1755.3 | 2196.4 | 2825.3 | 1213.7 | 0.61865 | 5.771
2024-12-09 | 23:24 | Data | 0 | 33.237 | 31.184 | 182.558 | 7.63 | 172.301 | 2246.02 | 25.89 | 46.45 | 6.38 | 1.33 | 4.455 | 8703.03 | 1.816 | 97.9 | 77 | 1459 | 23.22 | 5657 | 1770.3 | 2229 | 2858.9 | 1213.7 | 0.61676 | 5.786
2024-12-09 | 23:24 | Data | 0 | 33.399 | 31.562 | 182.694 | 7.63 | 172.346 | 2244.22 | 25.88 | 46.45 | 6.38 | 1.327 | 4.455 | 8721.11 | 1.857 | 97.9 | 77.1 | 1458 | 23.22 | 5668.7 | 1741.2 | 2207.6 | 2823.2 | 1213.7 | 0.6142 | 5.781
2024-12-09 | 23:24 | Data | 0 | 32.953 | 31.285 | 182.604 | 7.63 | 172.301 | 2249.64 | 25.88 | 46.54 | 6.39 | 1.323 | 4.419 | 8748.25 | 1.931 | 97.9 | 77 | 1462 | 23.27 | 5686.4 | 1768.3 | 2248 | 2873.2 | 1213.8 | 0.61278 | 5.742
2024-12-09 | 23:24 | Data | 0 | 33.183 | 31.252 | 182.785 | 7.63 | 172.346 | 2242.41 | 25.88 | 46.54 | 6.38 | 1.324 | 4.408 | 8743.73 | 1.884 | 97.9 | 76.9 | 1458 | 23.27 | 5683.4 | 1754.5 | 2250.4 | 2864.2 | 1213.8 | 0.61019 | 5.733
2024-12-09 | 23:25 | Data | 0 | 32.953 | 31.312 | 182.468 | 7.63 | 172.12 | 2241.5 | 25.88 | 46.54 | 6.38 | 1.337 | 4.429 | 8743.73 | 1.782 | 97.9 | 76.8 | 1457 | 23.27 | 5683.4 | 1758.8 | 2240.5 | 2860.8 | 1213.8 | 0.61075 | 5.765
2024-12-09 | 23:25 | Data | 0 | 33.399 | 31.252 | 182.83 | 7.63 | 172.482 | 2244.22 | 25.89 | 46.45 | 6.39 | 1.329 | 4.426 | 8716.59 | 1.857 | 97.9 | 76.9 | 1459 | 23.22 | 5665.8 | 1743.5 | 2255.9 | 2862.9 | 1213.8 | 0.60651 | 5.753
2024-12-09 | 23:25 | Data | 0 | 33.075 | 31.312 | 182.649 | 7.63 | 172.12 | 2243.31 | 25.88 | 46.54 | 6.38 | 1.331 | 4.436 | 8716.59 | 1.904 | 97.9 | 76.9 | 1459 | 23.27 | 5665.8 | 1780.2 | 2243.8 | 2876.2 | 1213.8 | 0.61669 | 5.768
2024-12-09 | 23:25 | Data | 0 | 32.96 | 31.285 | 182.513 | 7.63 | 172.256 | 2246.93 | 25.88 | 46.54 | 6.38 | 1.342 | 4.44 | 8716.59 | 1.728 | 97.9 | 76.8 | 1461 | 23.22 | 5665.8 | 1751.8 | 2242.2 | 2856.9 | 1213.8 | 0.61103 | 5.784
2024-12-09 | 23:25 | Data | 0 | 33.399 | 31.454 | 182.785 | 7.63 | 172.256 | 2246.93 | 25.88 | 46.45 | 6.38 | 1.349 | 4.471 | 8734.68 | 1.843 | 97.9 | 76.8 | 1461 | 23.27 | 5677.5 | 1754.6 | 2241 | 2856.8 | 1213.8 | 0.61124 | 5.819
2024-12-09 | 23:25 | Data | 0 | 33.081 | 31.171 | 182.649 | 7.63 | 172.346 | 2246.93 | 25.89 | 46.54 | 6.38 | 1.337 | 4.457 | 8743.73 | 1.762 | 97.9 | 76.9 | 1461 | 23.27 | 5683.4 | 1748.3 | 2214.2 | 2830.7 | 1213.8 | 0.61578 | 5.793
2024-12-09 | 23:25 | Data | 0 | 32.96 | 31.11 | 182.513 | 7.63 | 172.075 | 2244.22 | 25.88 | 46.54 | 6.38 | 1.334 | 4.426 | 8743.73 | 1.843 | 97.9 | 76.8 | 1459 | 23.22 | 5683.4 | 1749 | 2208.1 | 2834.9 | 1213.8 | 0.61598 | 5.76
2024-12-09 | 23:25 | Data | 0 | 32.953 | 31.495 | 182.694 | 7.63 | 172.256 | 2240.6 | 25.86 | 46.54 | 6.38 | 1.33 | 4.438 | 8743.73 | 1.843 | 97.9 | 77 | 1457 | 23.27 | 5683.4 | 1761.8 | 2203.9 | 2834.3 | 1213.8 | 0.61888 | 5.769
2024-12-09 | 23:25 | Data | 0 | 33.068 | 31.285 | 182.604 | 7.63 | 172.21 | 2241.5 | 25.89 | 46.45 | 6.39 | 1.322 | 4.421 | 8721.11 | 1.897 | 97.9 | 77 | 1457 | 23.27 | 5668.7 | 1738 | 2194.2 | 2812.9 | 1213.8 | 0.6145 | 5.743
2024-12-09 | 23:25 | Data | 0 | 33.304 | 31.231 | 182.694 | 7.63 | 172.256 | 2242.41 | 25.88 | 46.45 | 6.39 | 1.325 | 4.402 | 8730.16 | 1.796 | 97.9 | 76.9 | 1458 | 23.22 | 5674.6 | 1751.5 | 2182.1 | 2810.9 | 1213.8 | 0.61887 | 5.726
2024-12-09 | 23:25 | Data | 0 | 32.967 | 31.326 | 182.558 | 7.64 | 172.21 | 2242.41 | 25.89 | 46.54 | 6.38 | 1.334 | 4.431 | 8712.07 | 1.728 | 97.9 | 76.9 | 1457 | 23.22 | 5662.8 | 1764.4 | 2222.6 | 2847.3 | 1213.8 | 0.61693 | 5.763
2024-12-09 | 23:25 | Data | 0 | 33.183 | 31.427 | 182.649 | 7.63 | 172.301 | 2240.6 | 25.86 | 46.45 | 6.38 | 1.337 | 4.435 | 8716.59 | 1.728 | 97.9 | 76.8 | 1457 | 23.22 | 5665.8 | 1742.4 | 2209.2 | 2825.7 | 1213.8 | 0.61485 | 5.772
2024-12-09 | 23:25 | Data | 0 | 33.176 | 31.339 | 182.604 | 7.63 | 172.256 | 2240.6 | 25.88 | 46.63 | 6.38 | 1.32 | 4.427 | 8721.11 | 1.843 | 97.9 | 77 | 1456 | 23.27 | 5668.7 | 1758.9 | 2200.1 | 2826.6 | 1213.8 | 0.6199 | 5.746
2024-12-09 | 23:25 | Data | 0 | 33.453 | 31.144 | 182.739 | 7.63 | 172.256 | 2139.37 | 25.88 | 46.54 | 6.38 | 1.328 | 4.422 | 8716.59 | 1.877 | 97.8 | 76.9 | 1391 | 23.22 | 5665.8 | 1767 | 2204.6 | 2839 | 1213.8 | 0.61936 | 5.749
2024-12-09 | 23:25 | Data | 0 | 32.967 | 31.11 | 182.649 | 7.63 | 172.256 | 2246.93 | 25.85 | 46.45 | 6.38 | 1.339 | 4.41 | 8707.55 | 1.843 | 97.9 | 76.7 | 1461 | 23.22 | 5659.9 | 1759.8 | 2215.8 | 2841 | 1213.8 | 0.61722 | 5.748
2024-12-09 | 23:25 | Data | 0 | 33.176 | 31.339 | 182.604 | 7.63 | 172.256 | 2246.93 | 25.88 | 46.54 | 6.38 | 1.347 | 4.444 | 8703.03 | 1.843 | 97.9 | 76.7 | 1461 | 23.22 | 5657 | 1735.4 | 2184.6 | 2802 | 1213.8 | 0.61697 | 5.79
2024-12-09 | 23:25 | Data | 0 | 33.129 | 31.535 | 182.694 | 7.63 | 172.256 | 2246.93 | 25.88 | 46.54 | 6.39 | 1.338 | 4.443 | 8707.55 | 1.85 | 97.9 | 76.9 | 1461 | 23.27 | 5659.9 | 1732.1 | 2204.8 | 2814.7 | 1213.8 | 0.61247 | 5.78
2024-12-09 | 23:26 | Data | 0 | 33.392 | 31.258 | 182.785 | 7.63 | 172.391 | 2246.02 | 25.89 | 46.54 | 6.38 | 1.331 | 4.427 | 8703.03 | 2.005 | 97.9 | 76.9 | 1461 | 23.27 | 5657 | 1740.1 | 2196.9 | 2813.1 | 1213.8 | 0.61745 | 5.76
2024-12-09 | 23:26 | Data | 0 | 33.068 | 31.535 | 182.694 | 7.63 | 172.346 | 2246.93 | 25.88 | 46.45 | 6.39 | 1.331 | 4.419 | 8703.03 | 1.863 | 97.9 | 76.8 | 1461 | 23.22 | 5657 | 1757.4 | 2194.1 | 2822 | 1213.8 | 0.61974 | 5.751
2024-12-09 | 23:26 | Data | 0 | 33.061 | 31.11 | 182.604 | 7.63 | 172.256 | 2251.45 | 25.88 | 46.54 | 6.38 | 1.329 | 4.43 | 8707.55 | 1.89 | 97.9 | 76.9 | 1463 | 23.27 | 5659.9 | 1750 | 2208.1 | 2828.8 | 1213.8 | 0.61654 | 5.761
2024-12-09 | 23:26 | Data | 0 | 32.791 | 31.09 | 182.785 | 7.63 | 172.21 | 2246.93 | 25.88 | 46.45 | 6.38 | 1.339 | 4.434 | 8707.55 | 1.843 | 97.9 | 76.8 | 1460 | 23.22 | 5659.9 | 1744.7 | 2173.7 | 2799.3 | 1213.8 | 0.62127 | 5.774
2024-12-09 | 23:26 | Data | 0 | 33.21 | 31.326 | 182.649 | 7.63 | 172.256 | 2247.83 | 25.86 | 46.45 | 6.39 | 1.337 | 4.437 | 8698.5 | 1.695 | 97.9 | 76.8 | 1461 | 23.22 | 5654 | 1738.8 | 2165.1 | 2801.7 | 1213.8 | 0.61992 | 5.773
2024-12-09 | 23:26 | Data | 0 | 32.98 | 31.285 | 182.649 | 7.63 | 172.256 | 2246.93 | 25.88 | 46.54 | 6.38 | 1.331 | 4.44 | 8707.55 | 1.735 | 97.9 | 76.9 | 1461 | 23.27 | 5659.9 | 1740.7 | 2191.7 | 2811.2 | 1213.8 | 0.6163 | 5.771
2024-12-09 | 23:26 | Data | 0 | 33.129 | 31.333 | 182.558 | 7.63 | 172.256 | 2246.93 | 25.88 | 46.45 | 6.38 | 1.326 | 4.447 | 8707.55 | 1.85 | 97.9 | 77 | 1461 | 23.22 | 5659.9 | 1747.1 | 2215.9 | 2834.6 | 1213.8 | 0.61312 | 5.775
2024-12-09 | 23:26 | Data | 0 | 33.392 | 31.252 | 182.649 | 7.64 | 172.256 | 2252.35 | 25.88 | 46.54 | 6.38 | 1.337 | 4.445 | 8716.59 | 1.85 | 97.9 | 76.9 | 1463 | 23.27 | 5665.8 | 1740 | 2188.8 | 2831.9 | 1213.8 | 0.6182 | 5.781
2024-12-09 | 23:26 | Data | 0 | 33.007 | 31.312 | 182.558 | 7.64 | 172.12 | 2246.93 | 25.86 | 46.45 | 6.38 | 1.338 | 4.429 | 8689.46 | 1.755 | 97.9 | 76.8 | 1460 | 23.27 | 5648.1 | 1742.4 | 2201.7 | 2818.7 | 1213.8 | 0.61691 | 5.767
2024-12-09 | 23:26 | Data | 0 | 32.96 | 31.225 | 182.739 | 7.63 | 172.301 | 2243.31 | 25.86 | 46.45 | 6.38 | 1.326 | 4.455 | 8693.98 | 1.728 | 97.9 | 77.1 | 1458 | 23.22 | 5651.1 | 1760.8 | 2200.6 | 2829.9 | 1213.8 | 0.61963 | 5.781
2024-12-09 | 23:26 | Data | 0 | 33.176 | 31.117 | 182.649 | 7.63 | 172.12 | 2246.02 | 25.88 | 46.45 | 6.39 | 1.332 | 4.421 | 8689.46 | 2.039 | 97.9 | 76.8 | 1460 | 23.18 | 5648.1 | 1746 | 2219.6 | 2835.9 | 1213.8 | 0.61679 | 5.753
2024-12-09 | 23:26 | Data | 0 | 32.764 | 30.894 | 182.558 | 7.63 | 172.12 | 2249.64 | 25.88 | 46.54 | 6.39 | 1.339 | 4.46 | 8680.41 | 1.735 | 97.9 | 76.9 | 1463 | 23.27 | 5642.3 | 1749.5 | 2199 | 2820.9 | 1213.8 | 0.61735 | 5.798
2024-12-09 | 23:26 | Data | 0 | 33.122 | 31.157 | 182.649 | 7.63 | 172.075 | 2246.02 | 25.86 | 46.54 | 6.38 | 1.338 | 4.456 | 8680.41 | 2.019 | 97.9 | 76.9 | 1461 | 23.27 | 5642.3 | 1752.7 | 2240 | 2855.2 | 1213.8 | 0.61153 | 5.794
2024-12-09 | 23:26 | Data | 0 | 33.068 | 31.61 | 182.83 | 7.63 | 172.301 | 2249.64 | 25.86 | 46.45 | 6.38 | 1.336 | 4.447 | 8693.98 | 1.843 | 97.9 | 76.9 | 1462 | 23.22 | 5651.1 | 1763.5 | 2214.9 | 2842.6 | 1213.8 | 0.61766 | 5.784
2024-12-09 | 23:26 | Data | 0 | 32.967 | 31.069 | 182.604 | 7.63 | 172.256 | 2249.64 | 25.85 | 46.45 | 6.38 | 1.338 | 4.442 | 8680.41 | 1.944 | 97.9 | 76.9 | 1462 | 23.27 | 5642.3 | 1740.2 | 2205.3 | 2821 | 1213.8 | 0.61418 | 5.78
2024-12-09 | 23:26 | Data | 0 | 32.96 | 31.285 | 182.649 | 7.63 | 172.256 | 2240.6 | 25.88 | 46.54 | 6.38 | 1.334 | 4.453 | 8680.41 | 1.85 | 97.9 | 76.9 | 1457 | 23.27 | 5642.3 | 1744.9 | 2210.5 | 2826.8 | 1213.8 | 0.61504 | 5.787
2024-12-09 | 23:26 | Data | 0 | 33.284 | 31.123 | 182.604 | 7.64 | 172.301 | 2246.93 | 25.88 | 46.45 | 6.38 | 1.329 | 4.442 | 8671.37 | 1.85 | 97.9 | 77 | 1461 | 23.27 | 5636.4 | 1749.2 | 2218.3 | 2837.6 | 1213.8 | 0.61588 | 5.771
2024-12-09 | 23:26 | Data | 0 | 32.946 | 31.11 | 182.604 | 7.63 | 172.12 | 2246.93 | 25.86 | 46.54 | 6.38 | 1.322 | 4.44 | 8680.41 | 1.85 | 97.9 | 77.1 | 1461 | 23.27 | 5642.3 | 1753.1 | 2219.4 | 2840.1 | 1213.8 | 0.61507 | 5.762
2024-12-09 | 23:27 | Data | 0 | 32.967 | 31.225 | 182.468 | 7.63 | 172.21 | 2246.93 | 25.88 | 46.45 | 6.38 | 1.327 | 4.394 | 8680.41 | 1.843 | 97.9 | 76.8 | 1461 | 23.22 | 5642.3 | 1745.1 | 2216.2 | 2832.5 | 1213.8 | 0.61355 | 5.721
2024-12-09 | 23:27 | Data | 0 | 33.284 | 31.339 | 182.694 | 7.63 | 172.256 | 2248.73 | 25.86 | 46.54 | 6.38 | 1.329 | 4.437 | 8662.33 | 1.742 | 97.9 | 77 | 1462 | 23.27 | 5630.5 | 1749.6 | 2228.3 | 2845.6 | 1213.8 | 0.61183 | 5.765
2024-12-09 | 23:27 | Data | 0 | 32.798 | 31.056 | 182.649 | 7.63 | 172.301 | 2249.64 | 25.89 | 46.45 | 6.38 | 1.338 | 4.444 | 8648.76 | 1.843 | 97.9 | 76.9 | 1462 | 23.22 | 5621.7 | 2853.5 | 3672.5 | 4695.1 | 1213.8 | 0.60934 | 5.781
2024-12-09 | 23:27 | Data | 0 | 33.183 | 31.393 | 182.649 | 7.63 | 172.21 | 2254.16 | 25.86 | 46.45 | 6.38 | 1.337 | 4.418 | 8662.33 | 1.735 | 97.9 | 76.8 | 1465 | 23.22 | 5630.5 | 2817.7 | 2828.3 | 4112.9 | 1213.8 | 0.66812 | 5.754
2024-12-09 | 23:27 | Data | 0 | 33.007 | 30.894 | 182.377 | 7.63 | 172.075 | 2245.12 | 25.86 | 46.54 | 6.38 | 1.323 | 4.437 | 8662.33 | 1.89 | 97.9 | 77 | 1460 | 23.22 | 5630.5 | 2831 | 2814.1 | 4114.3 | 1213.8 | 0.67081 | 5.76
2024-12-09 | 23:27 | Data | 0 | 33.068 | 31.393 | 182.694 | 7.63 | 172.21 | 2246.93 | 25.88 | 46.45 | 6.38 | 1.33 | 4.439 | 8666.85 | 1.836 | 97.9 | 77 | 1461 | 23.22 | 5633.5 | 2820.2 | 2775.5 | 4081.7 | 1213.8 | 0.67482 | 5.769
2024-12-09 | 23:27 | Data | 0 | 32.953 | 31.333 | 182.604 | 7.63 | 172.12 | 2246.93 | 25.88 | 46.54 | 6.38 | 1.326 | 4.453 | 8662.33 | 1.823 | 97.9 | 77.1 | 1461 | 23.22 | 5630.5 | 2840.8 | 2774.7 | 4089.4 | 1213.8 | 0.67665 | 5.778
2024-12-09 | 23:27 | Data | 0 | 33.041 | 31.333 | 182.649 | 7.63 | 172.12 | 2246.93 | 25.85 | 46.54 | 6.38 | 1.332 | 4.464 | 8644.24 | 2.019 | 97.9 | 77 | 1461 | 23.27 | 5618.8 | 2830.9 | 2783.7 | 4093.4 | 1213.8 | 0.67542 | 5.797
2024-12-09 | 23:27 | Data | 0 | 32.899 | 31.11 | 182.649 | 7.63 | 172.21 | 2247.83 | 25.85 | 46.45 | 6.38 | 1.339 | 4.427 | 8635.19 | 1.83 | 97.9 | 76.8 | 1461 | 23.22 | 5612.9 | 2838.9 | 2764.2 | 4084.4 | 1213.8 | 0.67718 | 5.766
2024-12-09 | 23:27 | Data | 0 | 32.96 | 31.11 | 182.513 | 7.63 | 172.075 | 2246.93 | 25.86 | 46.54 | 6.39 | 1.33 | 4.385 | 8635.19 | 1.843 | 97.9 | 76.7 | 1461 | 23.32 | 5612.9 | 2814.3 | 2775.6 | 4074.7 | 1213.8 | 0.67329 | 5.714
2024-12-09 | 23:27 | Data | 0 | 33.351 | 31.238 | 182.649 | 7.63 | 172.075 | 2246.93 | 25.85 | 46.45 | 6.39 | 1.329 | 4.439 | 8644.24 | 1.965 | 97.9 | 77 | 1461 | 23.22 | 5618.8 | 2840.8 | 2796.5 | 4105.2 | 1213.8 | 0.67486 | 5.768
2024-12-09 | 23:27 | Data | 0 | 32.953 | 30.995 | 182.468 | 7.63 | 172.03 | 2246.93 | 25.84 | 46.54 | 6.38 | 1.337 | 4.444 | 8626.15 | 2.059 | 97.9 | 76.9 | 1461 | 23.27 | 5607 | 2846.4 | 2792.3 | 4108.8 | 1213.8 | 0.67467 | 5.78
2024-12-09 | 23:27 | Data | 0 | 33.034 | 31.11 | 182.468 | 7.63 | 172.075 | 2246.93 | 25.84 | 46.54 | 6.39 | 1.334 | 4.44 | 8639.71 | 1.89 | 97.9 | 76.9 | 1461 | 23.32 | 5615.8 | 2837.5 | 2783.2 | 4096.2 | 1213.8 | 0.67367 | 5.774
2024-12-09 | 23:27 | Data | 0 | 33.007 | 31.022 | 182.604 | 7.63 | 172.075 | 2247.83 | 25.83 | 46.45 | 6.38 | 1.341 | 4.427 | 8621.63 | 1.931 | 97.9 | 76.8 | 1461 | 23.27 | 5604.1 | 2821.5 | 2801.6 | 4096.2 | 1213.8 | 0.67019 | 5.767
2024-12-09 | 23:27 | Data | 0 | 33.169 | 31.11 | 182.558 | 7.63 | 172.21 | 2246.93 | 25.84 | 46.54 | 6.38 | 1.336 | 4.437 | 8626.15 | 1.897 | 97.9 | 76.9 | 1461 | 23.22 | 5607 | 2816.2 | 2800 | 4089.4 | 1213.8 | 0.67199 | 5.771
2024-12-09 | 23:27 | Data | 0 | 32.73 | 31.11 | 182.604 | 7.63 | 172.21 | 2246.93 | 25.84 | 46.45 | 6.38 | 1.331 | 4.437 | 8644.24 | 1.789 | 97.9 | 76.9 | 1461 | 23.22 | 5618.8 | 2830.9 | 2811.7 | 4108.7 | 1213.8 | 0.67229 | 5.77
2024-12-09 | 23:27 | Data | 0 | 32.73 | 31.306 | 182.604 | 7.63 | 172.03 | 2246.02 | 25.84 | 46.45 | 6.38 | 1.336 | 4.436 | 8666.85 | 1.634 | 97.9 | 76.9 | 1461 | 23.27 | 5633.5 | 2834.6 | 2783.5 | 4100.3 | 1213.9 | 0.67243 | 5.771
2024-12-09 | 23:27 | Data | 0 | 33.169 | 31.11 | 182.513 | 7.63 | 172.075 | 2246.93 | 25.84 | 46.359 | 6.38 | 1.331 | 4.457 | 8689.46 | 1.89 | 97.9 | 77 | 1460 | 23.22 | 5648.1 | 2829.8 | 2765.7 | 4077.4 | 1213.9 | 0.6766 | 5.788
2024-12-09 | 23:28 | Data | 0 | 33.014 | 31.11 | 182.558 | 7.63 | 172.21 | 2244.22 | 25.83 | 46.54 | 6.39 | 1.331 | 4.4 | 8689.46 | 1.647 | 97.9 | 76.8 | 1459 | 23.22 | 5648.1 | 2839.1 | 2771.1 | 4088.5 | 1213.9 | 0.6778 | 5.733
2024-12-09 | 23:28 | Data | 0 | 32.798 | 31.285 | 182.513 | 7.63 | 172.21 | 2244.22 | 25.84 | 46.54 | 6.38 | 1.337 | 4.418 | 8680.41 | 1.614 | 97.9 | 76.8 | 1459 | 23.27 | 5642.3 | 2828.8 | 2763.8 | 4074.4 | 1213.9 | 0.6775 | 5.753
2024-12-09 | 23:28 | Data | 0 | 33.385 | 31.191 | 182.694 | 7.63 | 172.301 | 2244.22 | 25.84 | 46.721 | 6.39 | 1.338 | 4.442 | 8680.41 | 1.958 | 97.9 | 76.9 | 1459 | 23.36 | 5642.3 | 2830.7 | 2762.6 | 4077.7 | 1213.9 | 0.67695 | 5.779
2024-12-09 | 23:28 | Data | 0 | 32.953 | 31.11 | 182.694 | 7.63 | 172.21 | 2242.41 | 25.83 | 46.721 | 6.38 | 1.327 | 4.443 | 8680.41 | 1.843 | 97.9 | 77 | 1457 | 23.36 | 5642.3 | 2838.3 | 2772.5 | 4091.4 | 1213.9 | 0.67611 | 5.769
2024-12-09 | 23:28 | Data | 0 | 33.169 | 31.319 | 182.649 | 7.63 | 172.21 | 2245.12 | 25.84 | 46.45 | 6.38 | 1.327 | 4.446 | 8671.37 | 1.924 | 97.9 | 77 | 1459 | 23.22 | 5636.4 | 2855 | 2788.2 | 4109.5 | 1213.9 | 0.6777 | 5.773
2024-12-09 | 23:28 | Data | 0 | 32.96 | 31.333 | 182.513 | 7.63 | 172.075 | 2248.73 | 25.84 | 46.54 | 6.38 | 1.32 | 4.435 | 8680.41 | 1.803 | 97.9 | 77.1 | 1462 | 23.27 | 5642.3 | 2844.9 | 2780.2 | 4096.8 | 1213.9 | 0.67584 | 5.756
2024-12-09 | 23:28 | Data | 0 | 33.183 | 31.339 | 182.649 | 7.63 | 172.21 | 2249.64 | 25.84 | 46.45 | 6.38 | 1.327 | 4.417 | 8644.24 | 1.843 | 97.9 | 76.9 | 1462 | 23.27 | 5618.8 | 2831.2 | 2767.1 | 4081 | 1213.9 | 0.67671 | 5.743
2024-12-09 | 23:28 | Data | 0 | 32.94 | 31.11 | 182.558 | 7.63 | 172.256 | 2249.64 | 25.83 | 46.54 | 6.38 | 1.329 | 4.436 | 8648.76 | 2.012 | 97.9 | 77 | 1462 | 23.27 | 5621.7 | 2847.3 | 2775.1 | 4095.2 | 1213.9 | 0.67776 | 5.764
2024-12-09 | 23:28 | Data | 0 | 32.96 | 31.11 | 182.558 | 7.63 | 172.075 | 2254.16 | 25.84 | 46.54 | 6.38 | 1.332 | 4.44 | 8648.76 | 1.843 | 97.9 | 76.9 | 1464 | 23.22 | 5621.7 | 2813.5 | 2754.4 | 4058 | 1213.9 | 0.67761 | 5.773
2024-12-09 | 23:28 | Data | 0 | 33.007 | 30.901 | 182.604 | 7.63 | 172.21 | 2249.64 | 25.84 | 46.721 | 6.38 | 1.337 | 4.465 | 8644.24 | 1.863 | 97.9 | 77 | 1463 | 23.36 | 5618.8 | 2839.6 | 2772.6 | 4089.1 | 1213.9 | 0.67406 | 5.801
2024-12-09 | 23:28 | Data | 0 | 32.946 | 30.948 | 182.694 | 7.63 | 172.256 | 2249.64 | 25.84 | 46.811 | 6.38 | 1.332 | 4.44 | 8639.71 | 2.093 | 97.9 | 76.9 | 1462 | 23.36 | 5615.8 | 2824.4 | 2756.4 | 4064.2 | 1213.9 | 0.6774 | 5.772
2024-12-09 | 23:28 | Data | 0 | 33.068 | 31.481 | 182.649 | 7.63 | 172.12 | 2249.64 | 25.84 | 46.721 | 6.38 | 1.329 | 4.436 | 8644.24 | 1.884 | 97.9 | 76.9 | 1462 | 23.36 | 5618.8 | 2833 | 2770.4 | 4088.2 | 1213.9 | 0.677 | 5.765
2024-12-09 | 23:28 | Data | 0 | 33.183 | 31.225 | 182.649 | 7.63 | 172.256 | 2248.73 | 25.83 | 46.721 | 6.38 | 1.326 | 4.437 | 8635.19 | 1.958 | 97.9 | 77 | 1462 | 23.36 | 5612.9 | 2824.5 | 2751.1 | 4071.6 | 1213.9 | 0.67668 | 5.763
2024-12-09 | 23:28 | Data | 0 | 33.129 | 31.164 | 182.694 | 7.64 | 172.301 | 2249.64 | 25.84 | 46.811 | 6.39 | 1.336 | 4.438 | 8635.19 | 1.958 | 97.9 | 76.9 | 1462 | 23.41 | 5612.9 | 2840 | 2783 | 4098.6 | 1213.9 | 0.67515 | 5.773
2024-12-09 | 23:28 | Data | 0 | 33.345 | 31.495 | 182.694 | 7.63 | 172.256 | 2249.64 | 25.84 | 46.811 | 6.38 | 1.329 | 4.425 | 8666.85 | 1.971 | 97.9 | 76.9 | 1462 | 23.36 | 5633.5 | 2808.3 | 2767.2 | 4076.3 | 1213.9 | 0.67273 | 5.754
2024-12-09 | 23:28 | Data | 0 | 32.98 | 31.11 | 182.649 | 7.63 | 172.21 | 2249.64 | 25.83 | 46.811 | 6.38 | 1.343 | 4.424 | 8648.76 | 1.85 | 97.9 | 76.7 | 1462 | 23.41 | 5621.7 | 2836 | 2753.8 | 4074 | 1213.9 | 0.6795 | 5.767
2024-12-09 | 23:28 | Data | 0 | 32.973 | 31.11 | 182.694 | 7.63 | 172.256 | 2246.93 | 25.84 | 46.721 | 6.38 | 1.329 | 4.438 | 8662.33 | 1.85 | 97.9 | 77 | 1461 | 23.36 | 5630.5 | 2813.5 | 2745.3 | 4057.8 | 1213.9 | 0.67606 | 5.767
2024-12-09 | 23:28 | Data | 0 | 32.953 | 31.225 | 182.694 | 7.63 | 172.12 | 2241.5 | 25.84 | 46.45 | 6.38 | 1.324 | 4.448 | 8680.41 | 1.958 | 97.9 | 77.1 | 1458 | 23.22 | 5642.3 | 2816.9 | 2761 | 4072.8 | 1213.9 | 0.67466 | 5.772
2024-12-09 | 23:29 | Data | 0 | 33.135 | 31.117 | 182.694 | 7.63 | 172.346 | 2247.83 | 25.84 | 46.54 | 6.38 | 1.334 | 4.437 | 8671.37 | 1.755 | 97.9 | 76.9 | 1461 | 23.27 | 5636.4 | 2838.6 | 2729.7 | 4060.3 | 1213.9 | 0.68244 | 5.771
2024-12-09 | 23:29 | Data | 0 | 33.176 | 31.285 | 182.604 | 7.64 | 172.21 | 2245.12 | 25.84 | 46.54 | 6.38 | 1.337 | 4.446 | 8684.94 | 1.884 | 97.9 | 76.9 | 1459 | 23.22 | 5645.2 | 2823.1 | 2757.8 | 4067.4 | 1213.9 | 0.67834 | 5.782
2024-12-09 | 23:29 | Data | 0 | 33.345 | 31.238 | 182.739 | 7.63 | 172.391 | 2243.31 | 25.84 | 46.54 | 6.38 | 1.331 | 4.43 | 8693.98 | 1.668 | 97.9 | 76.9 | 1458 | 23.27 | 5651.1 | 2843.2 | 2752.3 | 4073.2 | 1213.9 | 0.68058 | 5.763
2024-12-09 | 23:29 | Data | 0 | 32.953 | 31.11 | 182.468 | 7.63 | 172.075 | 2245.12 | 25.84 | 46.45 | 6.39 | 1.337 | 4.441 | 8693.98 | 1.843 | 97.9 | 76.9 | 1459 | 23.18 | 5651.1 | 2819.4 | 2760.4 | 4072.3 | 1213.9 | 0.67531 | 5.777
2024-12-09 | 23:29 | Data | 0 | 32.784 | 31.096 | 182.558 | 7.63 | 172.075 | 2244.22 | 25.83 | 46.45 | 6.38 | 1.324 | 4.426 | 8689.46 | 1.728 | 97.9 | 77 | 1459 | 23.22 | 5648.1 | 2848.5 | 2759.9 | 4082.1 | 1213.9 | 0.68063 | 5.75
2024-12-09 | 23:29 | Data | 0 | 33.075 | 30.941 | 182.694 | 7.63 | 172.346 | 2244.22 | 25.84 | 46.54 | 6.39 | 1.328 | 4.429 | 8703.03 | 1.85 | 97.9 | 76.9 | 1459 | 23.22 | 5657 | 2838.9 | 2756.7 | 4077.3 | 1213.9 | 0.67846 | 5.757
2024-12-09 | 23:29 | Data | 0 | 32.96 | 31.117 | 182.558 | 7.64 | 172.075 | 2244.22 | 25.84 | 46.54 | 6.38 | 1.33 | 4.417 | 8703.03 | 1.836 | 97.9 | 76.8 | 1458 | 23.22 | 5657 | 2819.9 | 2748.2 | 4061 | 1213.9 | 0.67687 | 5.745
2024-12-09 | 23:29 | Data | 0 | 33.183 | 31.583 | 182.649 | 7.63 | 172.12 | 2244.22 | 25.83 | 46.54 | 6.38 | 1.34 | 4.44 | 8707.55 | 1.762 | 97.9 | 76.8 | 1459 | 23.22 | 5659.9 | 2828.4 | 2737.7 | 4057.9 | 1213.9 | 0.67902 | 5.781
2024-12-09 | 23:29 | Data | 0 | 33.156 | 31.279 | 182.604 | 7.63 | 172.12 | 2242.41 | 25.84 | 46.45 | 6.38 | 1.331 | 4.442 | 8716.59 | 1.836 | 97.9 | 77 | 1458 | 23.27 | 5665.8 | 2840.8 | 2756.3 | 4081.4 | 1213.9 | 0.67754 | 5.773
2024-12-09 | 23:29 | Data | 0 | 33.345 | 31.346 | 182.558 | 7.64 | 172.075 | 2241.5 | 25.84 | 46.54 | 6.38 | 1.339 | 4.415 | 8716.59 | 2.005 | 97.9 | 76.7 | 1457 | 23.22 | 5665.8 | 2832.6 | 2741.8 | 4062.5 | 1213.9 | 0.67842 | 5.752
2024-12-09 | 23:29 | Data | 0 | 32.798 | 31.312 | 182.694 | 7.63 | 172.346 | 2241.5 | 25.84 | 46.721 | 6.38 | 1.335 | 4.434 | 8730.16 | 1.627 | 97.9 | 76.9 | 1457 | 23.41 | 5674.6 | 2827.6 | 2749.2 | 4061.4 | 1213.9 | 0.6781 | 5.769
2024-12-09 | 23:29 | Data | 0 | 32.953 | 31.501 | 182.649 | 7.63 | 172.12 | 2242.41 | 25.83 | 46.54 | 6.38 | 1.32 | 4.437 | 8730.16 | 1.755 | 97.9 | 77.1 | 1457 | 23.27 | 5674.6 | 2838.3 | 2777.8 | 4084.4 | 1213.9 | 0.67375 | 5.758
2024-12-09 | 23:29 | Data | 0 | 33.156 | 31.508 | 182.739 | 7.63 | 172.301 | 2233.37 | 25.84 | 46.54 | 6.38 | 1.331 | 4.428 | 8716.59 | 2.005 | 97.9 | 76.9 | 1452 | 23.27 | 5665.8 | 2847.1 | 2770.9 | 4087.6 | 1213.9 | 0.67771 | 5.76
2024-12-09 | 23:29 | Data | 0 | 32.953 | 31.11 | 182.604 | 7.63 | 172.21 | 2236.08 | 25.85 | 46.54 | 6.38 | 1.332 | 4.446 | 8721.11 | 2.046 | 97.9 | 76.9 | 1453 | 23.22 | 5668.7 | 2842.3 | 2774.2 | 4094 | 1213.9 | 0.67699 | 5.779
2024-12-09 | 23:29 | Data | 0 | 32.98 | 31.123 | 182.649 | 7.63 | 172.256 | 2238.79 | 25.84 | 46.54 | 6.38 | 1.329 | 4.437 | 8703.03 | 1.83 | 97.9 | 77 | 1455 | 23.27 | 5657 | 2842.5 | 2766.2 | 4090.1 | 1213.9 | 0.67776 | 5.765
2024-12-09 | 23:29 | Data | 0 | 33.156 | 31.387 | 182.604 | 7.63 | 172.21 | 2239.7 | 25.84 | 46.45 | 6.38 | 1.329 | 4.446 | 8707.55 | 1.944 | 97.9 | 77 | 1456 | 23.22 | 5659.9 | 2846.8 | 2800.7 | 4111.2 | 1213.9 | 0.67496 | 5.776
2024-12-09 | 23:29 | Data | 0 | 33.169 | 31.218 | 182.694 | 7.63 | 172.12 | 2238.79 | 25.83 | 46.54 | 6.39 | 1.329 | 4.428 | 8716.59 | 1.863 | 97.9 | 76.9 | 1456 | 23.27 | 5665.8 | 2847.6 | 2786.8 | 4101.6 | 1213.9 | 0.67555 | 5.756
2024-12-09 | 23:30 | Data | 0 | 32.933 | 31.333 | 182.694 | 7.63 | 172.12 | 2241.5 | 25.84 | 46.45 | 6.39 | 1.327 | 4.418 | 8734.68 | 1.931 | 97.9 | 76.9 | 1457 | 23.27 | 5677.5 | 2847.2 | 2764.2 | 4089 | 1214 | 0.67898 | 5.744
2024-12-09 | 23:30 | Data | 0 | 33.183 | 31.211 | 182.604 | 7.63 | 172.12 | 2244.22 | 25.83 | 46.54 | 6.39 | 1.336 | 4.427 | 8712.07 | 1.722 | 97.9 | 76.8 | 1459 | 23.27 | 5662.8 | 2842.9 | 2777.6 | 4096.4 | 1214 | 0.67774 | 5.761
2024-12-09 | 23:30 | Data | 0 | 33.115 | 31.501 | 182.604 | 7.63 | 172.21 | 2248.73 | 25.84 | 46.45 | 6.38 | 1.326 | 4.456 | 8707.55 | 1.985 | 97.9 | 77.1 | 1462 | 23.27 | 5659.9 | 2837.9 | 2759.5 | 4077.7 | 1214 | 0.67965 | 5.782
2024-12-09 | 23:30 | Data | 0 | 33.378 | 31.177 | 182.604 | 7.63 | 172.256 | 2241.5 | 25.84 | 46.45 | 6.38 | 1.329 | 4.446 | 8707.55 | 1.897 | 97.9 | 77 | 1457 | 23.22 | 5659.9 | 2840 | 2767.6 | 4089.3 | 1214 | 0.67716 | 5.775
2024-12-09 | 23:30 | Data | 0 | 33.378 | 31.508 | 182.83 | 7.64 | 172.301 | 2243.31 | 25.84 | 46.45 | 6.38 | 1.338 | 4.454 | 8693.98 | 1.951 | 97.9 | 76.9 | 1459 | 23.22 | 5651.1 | 2831.3 | 2774.7 | 4071.4 | 1214 | 0.6776 | 5.792
2024-12-09 | 23:30 | Data | 0 | 33.068 | 31.117 | 182.694 | 7.64 | 172.301 | 2244.22 | 25.84 | 46.45 | 6.39 | 1.339 | 4.456 | 8684.94 | 1.87 | 97.9 | 76.9 | 1459 | 23.22 | 5645.2 | 2849.4 | 2764.5 | 4072.6 | 1214 | 0.67914 | 5.795
2024-12-09 | 23:30 | Data | 0 | 32.744 | 31.11 | 182.604 | 7.63 | 172.21 | 2245.12 | 25.85 | 46.54 | 6.39 | 1.329 | 4.46 | 8689.46 | 1.62 | 97.9 | 77.1 | 1459 | 23.27 | 5648.1 | 2836.6 | 2770.4 | 4088.4 | 1214 | 0.67759 | 5.789
2024-12-09 | 23:30 | Data | 0 | 33.068 | 31.333 | 182.604 | 7.63 | 172.21 | 2244.22 | 25.84 | 46.54 | 6.38 | 1.339 | 4.442 | 8703.03 | 1.897 | 97.9 | 76.8 | 1459 | 23.32 | 5657 | 2848 | 2799.7 | 4109.7 | 1214 | 0.67662 | 5.78
2024-12-09 | 23:30 | Data | 0 | 33.135 | 31.366 | 182.558 | 7.64 | 172.256 | 2244.22 | 25.83 | 46.45 | 6.39 | 1.339 | 4.448 | 8721.11 | 1.924 | 97.9 | 76.8 | 1459 | 23.22 | 5668.7 | 2843 | 2800.4 | 4108.9 | 1214 | 0.67365 | 5.789
2024-12-09 | 23:30 | Data | 0 | 32.953 | 31.326 | 182.513 | 7.63 | 172.21 | 2245.12 | 25.85 | 46.54 | 6.38 | 1.331 | 4.436 | 8716.59 | 1.668 | 97.9 | 76.9 | 1459 | 23.22 | 5665.8 | 2843.6 | 2789.4 | 4106.1 | 1214 | 0.6751 | 5.767
2024-12-09 | 23:30 | Data | 0 | 32.98 | 31.339 | 182.694 | 7.64 | 172.346 | 2246.02 | 25.85 | 46.45 | 6.39 | 1.329 | 4.42 | 8716.59 | 1.634 | 97.9 | 76.9 | 1461 | 23.22 | 5665.8 | 2856.3 | 2800.3 | 4120 | 1214 | 0.67589 | 5.75
2024-12-09 | 23:30 | Data | 0 | 32.98 | 31.272 | 182.558 | 7.63 | 172.301 | 2246.93 | 25.83 | 46.54 | 6.38 | 1.328 | 4.436 | 8716.59 | 1.89 | 97.9 | 77 | 1461 | 23.22 | 5665.8 | 2842.4 | 2791.9 | 4106.7 | 1214 | 0.67424 | 5.761
2024-12-09 | 23:30 | Data | 0 | 32.845 | 31.11 | 182.468 | 7.64 | 172.03 | 2239.7 | 25.84 | 46.45 | 6.38 | 1.32 | 4.418 | 8721.11 | 1.83 | 97.9 | 77 | 1456 | 23.27 | 5668.7 | 2829.6 | 2749.9 | 4063.1 | 1214 | 0.67935 | 5.737
2024-12-09 | 23:30 | Data | 0 | 33.405 | 31.15 | 182.649 | 7.63 | 172.21 | 2247.83 | 25.83 | 46.359 | 6.38 | 1.323 | 4.412 | 8734.68 | 2.086 | 97.9 | 76.9 | 1461 | 23.18 | 5677.5 | 2836 | 2772.4 | 4085.5 | 1214 | 0.6757 | 5.735
2024-12-09 | 23:30 | Data | 0 | 32.987 | 30.955 | 182.558 | 7.63 | 172.256 | 2246.02 | 25.84 | 46.269 | 6.38 | 1.332 | 4.423 | 8716.59 | 1.803 | 97.9 | 76.9 | 1461 | 23.13 | 5665.8 | 2824.6 | 2770.5 | 4081.1 | 1214 | 0.67483 | 5.754
2024-12-09 | 23:30 | Data | 0 | 33.405 | 31.171 | 182.604 | 7.63 | 172.301 | 2246.93 | 25.84 | 46.45 | 6.38 | 1.332 | 4.445 | 8707.55 | 1.884 | 97.9 | 76.9 | 1461 | 23.22 | 5659.9 | 2822.6 | 2774.5 | 4081.4 | 1214 | 0.67754 | 5.777
2024-12-09 | 23:30 | Data | 0 | 33.129 | 31.454 | 182.694 | 7.63 | 172.21 | 2246.93 | 25.85 | 46.45 | 6.39 | 1.338 | 4.46 | 9123.59 | 1.836 | 97.9 | 76.9 | 1461 | 23.27 | 5930.3 | 2838.1 | 2777.3 | 4096.3 | 1214 | 0.67522 | 5.799
2024-12-09 | 23:30 | Data | 0 | 32.96 | 31.312 | 182.694 | 7.63 | 172.21 | 2246.93 | 25.84 | 46.45 | 6.38 | 1.337 | 4.434 | 8680.41 | 1.728 | 97.9 | 76.8 | 1461 | 23.22 | 5642.3 | 2823.6 | 2766.6 | 4076.7 | 1214 | 0.6746 | 5.769
2024-12-09 | 23:31 | Data | 0 | 33.385 | 31.387 | 182.739 | 7.63 | 172.301 | 2239.7 | 25.84 | 46.45 | 6.38 | 1.329 | 4.403 | 8680.41 | 1.965 | 97.9 | 76.8 | 1455 | 23.22 | 5642.3 | 2855.7 | 2766.9 | 4097.8 | 1214 | 0.67882 | 5.733
2024-12-09 | 23:31 | Data | 0 | 33.183 | 31.312 | 182.649 | 7.63 | 172.256 | 2244.22 | 25.84 | 46.54 | 6.38 | 1.334 | 4.437 | 8680.41 | 1.951 | 97.9 | 76.9 | 1459 | 23.27 | 5642.3 | 2836.7 | 2766.5 | 4082.6 | 1214 | 0.67792 | 5.772
2024-12-09 | 23:31 | Data | 0 | 33.129 | 31.333 | 182.739 | 7.64 | 172.301 | 2244.22 | 25.84 | 46.269 | 6.38 | 1.332 | 4.449 | 8680.41 | 1.843 | 97.9 | 77 | 1459 | 23.13 | 5642.3 | 2828.9 | 2757.9 | 4076.9 | 1214 | 0.67452 | 5.783
2024-12-09 | 23:31 | Data | 0 | 33.156 | 31.339 | 182.558 | 7.63 | 172.12 | 2244.22 | 25.84 | 46.269 | 6.38 | 1.337 | 4.46 | 8680.41 | 1.843 | 97.9 | 76.9 | 1459 | 23.09 | 5642.3 | 2851.1 | 2769.8 | 4091.6 | 1214 | 0.67684 | 5.797
2024-12-09 | 23:31 | Data | 0 | 33.378 | 31.272 | 182.739 | 7.64 | 172.301 | 2243.31 | 25.85 | 46.269 | 6.38 | 1.337 | 4.425 | 8671.37 | 1.965 | 97.9 | 76.8 | 1458 | 23.13 | 5636.4 | 2816.2 | 2797.1 | 4107.5 | 1214 | 0.6745 | 5.762
2024-12-09 | 23:31 | Data | 0 | 32.798 | 31.312 | 182.785 | 7.64 | 172.301 | 2244.22 | 25.84 | 46.179 | 6.39 | 1.336 | 4.43 | 8680.41 | 1.62 | 97.9 | 76.8 | 1459 | 23.09 | 5642.3 | 2832.3 | 2785.2 | 4093.4 | 1214 | 0.67376 | 5.766
2024-12-09 | 23:31 | Data | 0 | 33.297 | 31.751 | 182.83 | 7.63 | 172.256 | 2244.22 | 25.84 | 46.179 | 6.38 | 1.339 | 4.454 | 8671.37 | 1.742 | 97.9 | 76.9 | 1459 | 23.13 | 5636.4 | 2839.8 | 2772.4 | 4091.3 | 1214 | 0.67715 | 5.793
2024-12-09 | 23:31 | Data | 0 | 33.068 | 31.123 | 182.604 | 7.64 | 172.12 | 2245.12 | 25.84 | 46.269 | 6.39 | 1.342 | 4.434 | 8693.98 | 1.816 | 97.9 | 76.8 | 1459 | 23.18 | 5651.1 | 2842 | 2796.1 | 4109 | 1214 | 0.67439 | 5.775
2024-12-09 | 23:31 | Data | 0 | 33.358 | 31.144 | 182.739 | 7.64 | 172.256 | 2246.93 | 25.84 | 46.359 | 6.38 | 1.34 | 4.403 | 8671.37 | 2.032 | 97.9 | 76.7 | 1461 | 23.22 | 5636.4 | 2820 | 2767.6 | 4074.4 | 1214 | 0.67594 | 5.743
2024-12-09 | 23:31 | Data | 0 | 32.73 | 31.11 | 182.604 | 7.63 | 172.12 | 2247.83 | 25.84 | 46.45 | 6.39 | 1.327 | 4.419 | 8689.46 | 1.789 | 97.9 | 76.9 | 1461 | 23.22 | 5648.1 | 2841.7 | 2746.7 | 4074.7 | 1214 | 0.68177 | 5.747
2024-12-09 | 23:31 | Data | 0 | 33.284 | 31.339 | 182.558 | 7.63 | 172.12 | 2246.93 | 25.84 | 46.45 | 6.38 | 1.331 | 4.424 | 8662.33 | 2.012 | 97.9 | 76.9 | 1461 | 23.22 | 5630.5 | 2851.3 | 2759.7 | 4088.5 | 1214 | 0.68195 | 5.755
2024-12-09 | 23:31 | Data | 0 | 33.075 | 31.447 | 182.739 | 7.63 | 172.301 | 2246.93 | 25.84 | 46.45 | 6.39 | 1.343 | 4.432 | 8662.33 | 1.83 | 97.9 | 76.7 | 1460 | 23.27 | 5630.5 | 2843.4 | 2753.2 | 4080 | 1214 | 0.681 | 5.774
2024-12-09 | 23:31 | Data | 0 | 33.068 | 31.38 | 182.649 | 7.63 | 172.256 | 2244.22 | 25.84 | 46.45 | 6.39 | 1.34 | 4.441 | 8666.85 | 1.951 | 97.9 | 76.8 | 1459 | 23.27 | 5633.5 | 2838.5 | 2779 | 4094 | 1214 | 0.67659 | 5.781
2024-12-09 | 23:31 | Data | 0 | 33.122 | 31.333 | 182.558 | 7.63 | 172.12 | 2244.22 | 25.84 | 46.54 | 6.38 | 1.331 | 4.432 | 8644.24 | 1.85 | 97.9 | 76.9 | 1459 | 23.22 | 5618.8 | 2828.2 | 2782.1 | 4088.8 | 1214 | 0.67415 | 5.763
2024-12-09 | 23:31 | Data | 0 | 33.412 | 31.353 | 182.694 | 7.63 | 172.256 | 2245.12 | 25.84 | 46.63 | 6.39 | 1.33 | 4.43 | 8689.46 | 1.87 | 97.9 | 76.9 | 1459 | 23.27 | 5648.1 | 2824.8 | 2818.9 | 4111.8 | 1214 | 0.6698 | 5.761
2024-12-09 | 23:31 | Data | 0 | 32.96 | 31.09 | 182.649 | 7.64 | 172.21 | 2244.22 | 25.84 | 46.179 | 6.39 | 1.332 | 4.457 | 8693.98 | 1.863 | 97.9 | 77 | 1459 | 23.13 | 5651.1 | 2837.3 | 2812.4 | 4133 | 1214 | 0.67258 | 5.789
2024-12-09 | 23:31 | Data | 0 | 33.007 | 31.326 | 182.604 | 7.64 | 172.256 | 2246.93 | 25.83 | 46.179 | 6.38 | 1.341 | 4.427 | 8703.03 | 1.735 | 97.9 | 76.7 | 1460 | 23.13 | 5657 | 2828.9 | 2822 | 4115.8 | 1214 | 0.6698 | 5.769
2024-12-09 | 23:31 | Data | 0 | 33.399 | 31.555 | 182.739 | 7.63 | 172.21 | 2246.93 | 25.84 | 46.179 | 6.39 | 1.343 | 4.409 | 8707.55 | 1.735 | 97.9 | 76.7 | 1461 | 23.09 | 5659.9 | 2827.5 | 2791.9 | 4095.5 | 1214 | 0.67344 | 5.752
2024-12-09 | 23:32 | Data | 0 | 33.277 | 31.164 | 182.83 | 7.64 | 172.346 | 2246.02 | 25.84 | 46.269 | 6.39 | 1.328 | 4.448 | 8703.03 | 1.89 | 97.9 | 77 | 1460 | 23.09 | 5657 | 2844.4 | 2774.5 | 4097.3 | 1214 | 0.67628 | 5.775
2024-12-09 | 23:32 | Data | 0 | 33.21 | 31.198 | 182.785 | 7.63 | 172.346 | 2246.93 | 25.84 | 46.179 | 6.39 | 1.33 | 4.448 | 8721.11 | 1.728 | 97.9 | 77 | 1460 | 23.13 | 5668.7 | 2842.3 | 2778 | 4094.6 | 1214 | 0.67645 | 5.78
2024-12-09 | 23:32 | Data | 0 | 32.953 | 31.312 | 182.649 | 7.64 | 172.256 | 2246.93 | 25.85 | 46.269 | 6.38 | 1.337 | 4.437 | 8703.03 | 1.782 | 97.9 | 76.8 | 1461 | 23.13 | 5657 | 2845.3 | 2769.9 | 4093.8 | 1214.1 | 0.67832 | 5.774
2024-12-09 | 23:32 | Data | 0 | 32.98 | 31.231 | 182.558 | 7.64 | 172.12 | 2246.93 | 25.85 | 46.269 | 6.38 | 1.335 | 4.438 | 8703.03 | 1.728 | 97.9 | 76.9 | 1461 | 23.13 | 5657 | 2835.7 | 2768.8 | 4077.6 | 1214.1 | 0.67693 | 5.773
2024-12-09 | 23:32 | Data | 0 | 33.291 | 31.711 | 182.739 | 7.63 | 172.346 | 2240.6 | 25.84 | 46.179 | 6.39 | 1.33 | 4.456 | 8693.98 | 1.782 | 97.9 | 77 | 1456 | 23.09 | 5651.1 | 2839.2 | 2787.9 | 4100.7 | 1214.1 | 0.67715 | 5.786
2024-12-09 | 23:32 | Data | 0 | 32.946 | 31.11 | 182.468 | 7.64 | 172.075 | 2244.22 | 25.84 | 46.359 | 6.38 | 1.342 | 4.452 | 8693.98 | 1.843 | 97.9 | 76.8 | 1459 | 23.22 | 5651.1 | 2846.2 | 2773.6 | 4095.4 | 1214.1 | 0.67616 | 5.795
2024-12-09 | 23:32 | Data | 0 | 33.156 | 31.11 | 182.558 | 7.63 | 172.12 | 2242.41 | 25.84 | 46.45 | 6.38 | 1.332 | 4.457 | 8684.94 | 2.059 | 97.9 | 77 | 1458 | 23.22 | 5645.2 | 2838.6 | 2771.6 | 4088.9 | 1214.1 | 0.67658 | 5.79
2024-12-09 | 23:32 | Data | 0 | 33.129 | 31.333 | 182.604 | 7.63 | 172.21 | 2246.93 | 25.84 | 46.359 | 6.39 | 1.335 | 4.447 | 8671.37 | 1.843 | 97.9 | 76.9 | 1460 | 23.18 | 5636.4 | 2857.5 | 2793.2 | 4117.1 | 1214.1 | 0.67531 | 5.781
2024-12-09 | 23:32 | Data | 0 | 33.156 | 31.137 | 182.739 | 7.63 | 172.256 | 2246.93 | 25.84 | 46.54 | 6.39 | 1.329 | 4.44 | 8680.41 | 2.019 | 97.9 | 77 | 1461 | 23.22 | 5642.3 | 2839.8 | 2789 | 4103.6 | 1214.1 | 0.67434 | 5.77
2024-12-09 | 23:32 | Data | 0 | 32.804 | 31.11 | 182.604 | 7.63 | 172.256 | 2246.93 | 25.83 | 46.269 | 6.39 | 1.326 | 4.454 | 8693.98 | 1.742 | 97.9 | 77 | 1461 | 23.18 | 5651.1 | 2849.4 | 2782.5 | 4103.4 | 1214.1 | 0.67669 | 5.78
2024-12-09 | 23:32 | Data | 0 | 33.27 | 31.346 | 182.83 | 7.63 | 172.346 | 2246.93 | 25.86 | 46.269 | 6.39 | 1.323 | 4.427 | 8693.98 | 1.924 | 97.9 | 77 | 1461 | 23.13 | 5651.1 | 2841.5 | 2782 | 4100.9 | 1214.1 | 0.67843 | 5.749
2024-12-09 | 23:32 | Data | 0 | 33.169 | 31.508 | 182.694 | 7.63 | 172.256 | 2244.22 | 25.85 | 46.179 | 6.38 | 1.334 | 4.445 | 8689.46 | 1.877 | 97.9 | 76.9 | 1459 | 23.09 | 5648.1 | 2828.4 | 2777.1 | 4088.7 | 1214.1 | 0.67764 | 5.777
2024-12-09 | 23:32 | Data | 0 | 33.156 | 31.231 | 182.694 | 7.63 | 172.21 | 2244.22 | 25.84 | 46.269 | 6.38 | 1.327 | 4.437 | 8703.03 | 2.059 | 97.9 | 77 | 1459 | 23.09 | 5657 | 2833.5 | 2773.1 | 4085.2 | 1214.1 | 0.676 | 5.765
2024-12-09 | 23:32 | Data | 0 | 33.048 | 31.312 | 182.649 | 7.63 | 172.301 | 2244.22 | 25.85 | 46.179 | 6.38 | 1.334 | 4.453 | 8689.46 | 1.614 | 97.9 | 76.9 | 1458 | 23.09 | 5648.1 | 2847.5 | 2800 | 4114.2 | 1214.1 | 0.67533 | 5.788
2024-12-09 | 23:32 | Data | 0 | 32.96 | 31.339 | 182.649 | 7.63 | 172.12 | 2244.22 | 25.83 | 46.179 | 6.38 | 1.329 | 4.461 | 8707.55 | 1.796 | 97.9 | 77 | 1459 | 23.13 | 5659.9 | 2850 | 2793.8 | 4111.2 | 1214.1 | 0.67687 | 5.791
2024-12-09 | 23:32 | Data | 0 | 33.189 | 31.312 | 182.694 | 7.64 | 172.12 | 2246.93 | 25.84 | 46.269 | 6.38 | 1.329 | 4.442 | 8707.55 | 1.944 | 97.9 | 77 | 1461 | 23.13 | 5659.9 | 2834.2 | 2797.8 | 4106.3 | 1214.1 | 0.67162 | 5.771
2024-12-09 | 23:32 | Data | 0 | 33.405 | 31.353 | 182.785 | 7.63 | 172.346 | 2239.7 | 25.84 | 46.179 | 6.39 | 1.323 | 4.446 | 8693.98 | 1.742 | 97.9 | 77.1 | 1456 | 23.09 | 5651.1 | 2839.9 | 2796.5 | 4101.5 | 1214.1 | 0.67497 | 5.77
2024-12-09 | 23:32 | Data | 0 | 33.574 | 31.454 | 182.83 | 7.63 | 172.436 | 2246.02 | 25.84 | 46.269 | 6.38 | 1.325 | 4.47 | 8693.98 | 1.978 | 97.9 | 77.1 | 1460 | 23.13 | 5651.1 | 2838.5 | 2801.4 | 4110.2 | 1214.1 | 0.67275 | 5.795
2024-12-09 | 23:33 | Data | 0 | 33.25 | 31.123 | 182.694 | 7.64 | 172.256 | 2244.22 | 25.84 | 46.269 | 6.38 | 1.334 | 4.431 | 8693.98 | 1.857 | 97.9 | 76.9 | 1459 | 23.13 | 5651.1 | 2838.8 | 2784.9 | 4097.5 | 1214.1 | 0.6755 | 5.765
2024-12-09 | 23:33 | Data | 0 | 33.075 | 31.117 | 182.649 | 7.63 | 172.346 | 2247.83 | 25.84 | 46.269 | 6.38 | 1.322 | 4.422 | 8689.46 | 1.843 | 97.9 | 77 | 1461 | 23.13 | 5648.1 | 2832.6 | 2783.6 | 4093.2 | 1214.1 | 0.67559 | 5.745
2024-12-09 | 23:33 | Data | 0 | 32.967 | 31.11 | 182.649 | 7.64 | 172.12 | 2246.93 | 25.84 | 46.269 | 6.38 | 1.331 | 4.452 | 8689.46 | 1.843 | 97.9 | 77 | 1461 | 23.09 | 5648.1 | 2827.6 | 2757.9 | 4074.6 | 1214.1 | 0.67748 | 5.782
2024-12-09 | 23:33 | Data | 0 | 33.237 | 31.184 | 182.694 | 7.63 | 172.256 | 2246.93 | 25.84 | 46.269 | 6.38 | 1.332 | 4.458 | 8698.5 | 1.843 | 97.9 | 77 | 1461 | 23.09 | 5654 | 2832.7 | 2777.4 | 4091.6 | 1214.1 | 0.67574 | 5.79
2024-12-09 | 23:33 | Data | 0 | 33.048 | 31.454 | 182.739 | 7.63 | 172.346 | 2241.5 | 25.85 | 46.269 | 6.39 | 1.33 | 4.455 | 8703.03 | 1.904 | 97.9 | 77 | 1456 | 23.13 | 5657 | 2829.2 | 2782.2 | 4088.5 | 1214.1 | 0.6746 | 5.786
2024-12-09 | 23:33 | Data | 0 | 33.183 | 31.339 | 182.649 | 7.64 | 172.256 | 2246.02 | 25.85 | 46.179 | 6.38 | 1.322 | 4.445 | 8684.94 | 1.843 | 97.9 | 77.1 | 1459 | 23.09 | 5645.2 | 2845.3 | 2784.6 | 4103.3 | 1214.1 | 0.67629 | 5.766
2024-12-09 | 23:33 | Data | 0 | 33 | 31.117 | 182.649 | 7.63 | 172.346 | 2244.22 | 25.85 | 46.269 | 6.39 | 1.321 | 4.428 | 8693.98 | 1.641 | 97.9 | 77 | 1459 | 23.09 | 5651.1 | 2830.7 | 2775 | 4088.7 | 1214.1 | 0.67505 | 5.75
2024-12-09 | 23:33 | Data | 0 | 33.264 | 31.441 | 182.649 | 7.63 | 172.346 | 2244.22 | 25.84 | 46.269 | 6.38 | 1.324 | 4.442 | 8689.46 | 1.87 | 97.9 | 77 | 1459 | 23.13 | 5648.1 | 2834.8 | 2777.6 | 4087.8 | 1214.1 | 0.67643 | 5.766
2024-12-09 | 23:33 | Data | 0 | 33.169 | 31.562 | 182.785 | 7.63 | 172.301 | 2244.22 | 25.84 | 46.269 | 6.38 | 1.336 | 4.452 | 8693.98 | 1.823 | 97.9 | 76.9 | 1459 | 23.13 | 5651.1 | 2847.9 | 2780.2 | 4102.6 | 1214.1 | 0.67757 | 5.788
2024-12-09 | 23:33 | Data | 0 | 33.176 | 31.117 | 182.649 | 7.63 | 172.256 | 2244.22 | 25.84 | 46.269 | 6.39 | 1.329 | 4.439 | 8693.98 | 2.046 | 97.9 | 77 | 1459 | 23.09 | 5651.1 | 2837 | 2764.4 | 4077.7 | 1214.1 | 0.67875 | 5.768
2024-12-09 | 23:33 | Data | 0 | 32.98 | 31.285 | 182.649 | 7.63 | 172.256 | 2244.22 | 25.85 | 46.179 | 6.38 | 1.33 | 4.424 | 8689.46 | 1.735 | 97.9 | 76.9 | 1459 | 23.09 | 5648.1 | 2827.4 | 2755.8 | 4070.9 | 1214.1 | 0.67674 | 5.754
2024-12-09 | 23:33 | Data | 0 | 33.183 | 31.339 | 182.694 | 7.64 | 172.256 | 2244.22 | 25.84 | 46.269 | 6.38 | 1.334 | 4.437 | 8693.98 | 1.85 | 97.9 | 76.9 | 1459 | 23.13 | 5651.1 | 2818.6 | 2783.8 | 4083.2 | 1214.1 | 0.67365 | 5.771
2024-12-09 | 23:33 | Data | 0 | 32.953 | 31.447 | 182.694 | 7.64 | 172.346 | 2244.22 | 25.84 | 46.179 | 6.38 | 1.334 | 4.417 | 8707.55 | 1.958 | 97.9 | 76.8 | 1459 | 23.13 | 5659.9 | 2827.4 | 2761.6 | 4074.8 | 1214.1 | 0.67601 | 5.751
2024-12-09 | 23:33 | Data | 0 | 33.27 | 31.724 | 182.649 | 7.63 | 172.21 | 2244.22 | 25.83 | 46.269 | 6.38 | 1.347 | 4.427 | 8693.98 | 1.843 | 97.9 | 76.7 | 1459 | 23.09 | 5651.1 | 2847.3 | 2786 | 4103.2 | 1214.1 | 0.67635 | 5.772
2024-12-09 | 23:33 | Data | 0 | 32.96 | 31.137 | 182.739 | 7.63 | 172.301 | 2244.22 | 25.84 | 46.269 | 6.38 | 1.334 | 4.43 | 8671.37 | 1.735 | 97.9 | 76.9 | 1459 | 23.13 | 5636.4 | 2834.4 | 2777.1 | 4090.9 | 1214.1 | 0.67492 | 5.763
2024-12-09 | 23:33 | Data | 0 | 33.183 | 31.225 | 182.604 | 7.63 | 172.256 | 2244.22 | 25.85 | 46.089 | 6.38 | 1.339 | 4.443 | 8693.98 | 1.87 | 97.9 | 76.8 | 1459 | 23.04 | 5651.1 | 2824.3 | 2783.3 | 4087.8 | 1214.1 | 0.67399 | 5.78
2024-12-09 | 23:33 | Data | 0 | 33 | 31.312 | 182.694 | 7.63 | 172.391 | 2244.22 | 25.84 | 46.269 | 6.38 | 1.331 | 4.447 | 8707.55 | 1.681 | 97.9 | 77 | 1458 | 23.13 | 5659.9 | 2848.5 | 2793.8 | 4112.1 | 1214.1 | 0.67699 | 5.778
2024-12-09 | 23:34 | Data | 0 | 33.176 | 31.137 | 182.694 | 7.63 | 172.256 | 2245.12 | 25.86 | 46.179 | 6.39 | 1.332 | 4.446 | 8707.55 | 1.843 | 97.9 | 76.9 | 1459 | 23.13 | 5659.9 | 2838.3 | 2777.4 | 4088.3 | 1214.1 | 0.67675 | 5.778
2024-12-09 | 23:34 | Data | 0 | 33.027 | 31.312 | 182.694 | 7.63 | 172.346 | 2242.41 | 25.85 | 46.269 | 6.38 | 1.325 | 4.448 | 8689.46 | 1.647 | 97.9 | 77 | 1458 | 23.13 | 5648.1 | 2832.5 | 2802 | 4105 | 1214.1 | 0.67276 | 5.774
2024-12-09 | 23:34 | Data | 0 | 33.183 | 31.454 | 182.785 | 7.63 | 172.256 | 2242.41 | 25.84 | 46.269 | 6.38 | 1.329 | 4.429 | 8703.03 | 1.796 | 97.9 | 76.9 | 1457 | 23.13 | 5657 | 2820.1 | 2798.3 | 4089 | 1214.1 | 0.6727 | 5.758
2024-12-09 | 23:34 | Data | 0 | 33.021 | 31.231 | 182.649 | 7.63 | 172.301 | 2241.5 | 25.84 | 46.179 | 6.38 | 1.332 | 4.422 | 8693.98 | 1.83 | 97.9 | 76.8 | 1458 | 23.13 | 5651.1 | 2831 | 2798.9 | 4104.7 | 1214.1 | 0.6723 | 5.754
2024-12-09 | 23:34 | Data | 0 | 33.129 | 31.454 | 182.649 | 7.63 | 172.301 | 2241.5 | 25.84 | 46.179 | 6.39 | 1.329 | 4.431 | 8698.5 | 2.019 | 97.9 | 76.9 | 1457 | 23.09 | 5654 | 2836.7 | 2780.2 | 4093.1 | 1214.2 | 0.6751 | 5.759
2024-12-09 | 23:34 | Data | 0 | 32.953 | 31.333 | 182.694 | 7.63 | 172.256 | 2242.41 | 25.84 | 46.45 | 6.38 | 1.339 | 4.447 | 8707.55 | 1.776 | 97.9 | 76.9 | 1457 | 23.22 | 5659.9 | 2821.3 | 2779.2 | 4085.4 | 1214.2 | 0.6736 | 5.787
2024-12-09 | 23:34 | Data | 0 | 33.183 | 31.339 | 182.83 | 7.63 | 172.256 | 2241.5 | 25.84 | 46.269 | 6.38 | 1.336 | 4.439 | 8721.11 | 1.843 | 97.9 | 76.9 | 1457 | 23.09 | 5668.7 | 2822.6 | 2769.1 | 4077.2 | 1214.2 | 0.67493 | 5.775
2024-12-09 | 23:34 | Data | 0 | 33.068 | 31.326 | 182.604 | 7.64 | 172.21 | 2238.79 | 25.84 | 46.179 | 6.39 | 1.33 | 4.46 | 8743.73 | 1.843 | 97.9 | 77 | 1456 | 23.09 | 5683.4 | 2834.7 | 2759.5 | 4077.1 | 1214.2 | 0.67862 | 5.79
2024-12-09 | 23:34 | Data | 0 | 33.183 | 31.11 | 182.649 | 7.63 | 172.256 | 2239.7 | 25.86 | 46.63 | 6.38 | 1.334 | 4.432 | 8748.25 | 1.951 | 97.9 | 76.9 | 1456 | 23.27 | 5686.4 | 2835.6 | 2773.9 | 4087.6 | 1214.2 | 0.67652 | 5.766
2024-12-09 | 23:34 | Data | 0 | 33.405 | 31.346 | 182.875 | 7.64 | 172.436 | 2238.79 | 25.84 | 46.269 | 6.38 | 1.339 | 4.454 | 8739.2 | 1.749 | 97.9 | 76.9 | 1455 | 23.18 | 5680.5 | 2833.3 | 2771.5 | 4085.7 | 1214.2 | 0.67619 | 5.792
2024-12-09 | 23:34 | Data | 0 | 32.96 | 31.326 | 182.558 | 7.64 | 172.301 | 2239.7 | 25.84 | 46.359 | 6.38 | 1.329 | 4.437 | 8734.68 | 1.668 | 97.9 | 76.9 | 1456 | 23.22 | 5677.5 | 2848.1 | 2768 | 4093.2 | 1214.2 | 0.67844 | 5.767
2024-12-09 | 23:34 | Data | 0 | 33.21 | 31.198 | 182.785 | 7.63 | 172.391 | 2238.79 | 25.83 | 46.45 | 6.38 | 1.328 | 4.423 | 8730.16 | 1.911 | 97.9 | 76.9 | 1455 | 23.22 | 5674.6 | 2824.7 | 2777.9 | 4083.5 | 1214.2 | 0.67356 | 5.752
2024-12-09 | 23:34 | Data | 0 | 33.345 | 31.346 | 182.875 | 7.64 | 172.391 | 2236.08 | 25.86 | 46.45 | 6.38 | 1.337 | 4.432 | 8734.68 | 2.039 | 97.9 | 76.8 | 1453 | 23.22 | 5677.5 | 2822.6 | 2787.1 | 4089.1 | 1214.2 | 0.67287 | 5.768
2024-12-09 | 23:34 | Data | 0 | 33.243 | 31.144 | 182.649 | 7.63 | 172.346 | 2232.47 | 25.84 | 46.54 | 6.39 | 1.329 | 4.438 | 8725.64 | 1.958 | 97.9 | 76.9 | 1452 | 23.27 | 5671.7 | 2839.4 | 2771.8 | 4085.7 | 1214.2 | 0.67832 | 5.767
2024-12-09 | 23:34 | Data | 0 | 33.183 | 31.11 | 182.649 | 7.63 | 172.256 | 2233.37 | 25.84 | 46.45 | 6.39 | 1.326 | 4.439 | 8721.11 | 1.863 | 97.9 | 77 | 1452 | 23.27 | 5668.7 | 2842.8 | 2768.5 | 4094.2 | 1214.2 | 0.67724 | 5.765
2024-12-09 | 23:34 | Data | 0 | 33.068 | 31.326 | 182.558 | 7.63 | 172.256 | 2233.37 | 25.85 | 46.45 | 6.38 | 1.33 | 4.419 | 8716.59 | 1.958 | 97.9 | 76.9 | 1452 | 23.22 | 5665.8 | 2828.4 | 2768.4 | 4077.2 | 1214.2 | 0.67709 | 5.75
2024-12-09 | 23:34 | Data | 0 | 32.953 | 31.285 | 182.468 | 7.64 | 172.075 | 2232.47 | 25.86 | 46.54 | 6.38 | 1.325 | 4.439 | 8716.59 | 1.87 | 97.9 | 77 | 1451 | 23.27 | 5665.8 | 2827.9 | 2763.6 | 4073.2 | 1214.2 | 0.67818 | 5.765
2024-12-09 | 23:34 | Data | 0 | 33.176 | 31.339 | 182.649 | 7.64 | 172.256 | 2235.18 | 25.85 | 46.54 | 6.38 | 1.33 | 4.455 | 8716.59 | 1.843 | 97.9 | 77 | 1453 | 23.22 | 5665.8 | 2835.9 | 2777.7 | 4090.4 | 1214.2 | 0.67705 | 5.785
2024-12-09 | 23:35 | Data | 0 | 33.176 | 31.292 | 182.694 | 7.63 | 172.301 | 2235.18 | 25.83 | 46.54 | 6.39 | 1.332 | 4.459 | 8703.03 | 1.931 | 97.9 | 77 | 1453 | 23.27 | 5657 | 2830.8 | 2759.8 | 4074.8 | 1214.2 | 0.67804 | 5.794
2024-12-09 | 23:35 | Data | 0 | 32.967 | 31.117 | 182.694 | 7.63 | 172.301 | 2236.08 | 25.84 | 46.45 | 6.39 | 1.34 | 4.441 | 8703.03 | 1.83 | 97.9 | 76.8 | 1453 | 23.22 | 5657 | 2841.1 | 2782.9 | 4095.8 | 1214.2 | 0.67785 | 5.782
2024-12-09 | 23:35 | Data | 0 | 33.196 | 31.225 | 182.739 | 7.64 | 172.391 | 2234.27 | 25.83 | 46.45 | 6.39 | 1.341 | 4.464 | 8703.03 | 1.836 | 97.9 | 76.9 | 1452 | 23.22 | 5657 | 2819.5 | 2766.3 | 4074 | 1214.2 | 0.67448 | 5.806
2024-12-09 | 23:35 | Data | 0 | 33.351 | 31.447 | 182.785 | 7.63 | 172.256 | 2235.18 | 25.84 | 46.54 | 6.39 | 1.329 | 4.456 | 8707.55 | 1.83 | 97.9 | 77 | 1453 | 23.22 | 5659.9 | 2823.8 | 2758.7 | 4071.1 | 1214.2 | 0.67676 | 5.784
2024-12-09 | 23:35 | Data | 0 | 33.412 | 31.225 | 182.83 | 7.63 | 172.301 | 2236.08 | 25.85 | 46.54 | 6.38 | 1.334 | 4.426 | 8721.11 | 1.749 | 97.9 | 76.8 | 1453 | 23.27 | 5668.7 | 2832.9 | 2746.3 | 4065.6 | 1214.2 | 0.6789 | 5.76
2024-12-09 | 23:35 | Data | 0 | 33.264 | 31.339 | 182.694 | 7.63 | 172.301 | 2238.79 | 25.84 | 46.45 | 6.39 | 1.338 | 4.436 | 8716.59 | 1.884 | 97.9 | 76.8 | 1455 | 23.22 | 5665.8 | 2837.7 | 2761.2 | 4080.1 | 1214.2 | 0.67795 | 5.772
2024-12-09 | 23:35 | Data | 0 | 33.183 | 31.339 | 182.785 | 7.63 | 172.346 | 2236.08 | 25.86 | 46.45 | 6.39 | 1.334 | 4.437 | 8734.68 | 1.843 | 97.9 | 76.9 | 1453 | 23.22 | 5677.5 | 2825.2 | 2768.6 | 4076.1 | 1214.2 | 0.67604 | 5.772
2024-12-09 | 23:35 | Data | 0 | 33.129 | 31.339 | 182.739 | 7.63 | 172.346 | 2186.37 | 25.83 | 46.54 | 6.39 | 1.33 | 4.432 | 8716.59 | 1.836 | 97.9 | 76.9 | 1420 | 23.27 | 5665.8 | 1768.6 | 2210.6 | 2837 | 1214.2 | 0.61686 | 5.761
2024-12-09 | 23:35 | Data | 0 | 32.96 | 31.123 | 182.694 | 7.63 | 172.346 | 2178.24 | 25.85 | 46.54 | 6.39 | 1.327 | 4.429 | 8693.98 | 2.019 | 97.9 | 76.9 | 1416 | 23.27 | 5651.1 | 1742.4 | 2200.2 | 2819 | 1214.2 | 0.61546 | 5.757
2024-12-09 | 23:35 | Data | 0 | 32.967 | 31.454 | 182.785 | 7.63 | 172.346 | 2178.24 | 25.85 | 46.45 | 6.39 | 1.334 | 4.432 | 8671.37 | 1.816 | 97.9 | 76.9 | 1416 | 23.22 | 5636.4 | 1734.1 | 2206.8 | 2819.3 | 1214.2 | 0.61264 | 5.765
2024-12-09 | 23:35 | Data | 0 | 33.183 | 31.454 | 182.785 | 7.63 | 172.21 | 2177.33 | 25.84 | 46.54 | 6.38 | 1.33 | 4.446 | 8684.94 | 1.728 | 97.9 | 77 | 1415 | 23.27 | 5645.2 | 1754.3 | 2190.3 | 2808.8 | 1214.2 | 0.61793 | 5.777
2024-12-09 | 23:35 | Data | 0 | 32.98 | 31.11 | 182.558 | 7.64 | 172.256 | 2227.04 | 25.85 | 46.45 | 6.39 | 1.326 | 4.442 | 8671.37 | 1.843 | 97.9 | 77 | 1447 | 23.22 | 5636.4 | 1756.1 | 2207.5 | 2832.6 | 1214.2 | 0.61748 | 5.768
2024-12-09 | 23:35 | Data | 0 | 33.345 | 31.596 | 182.694 | 7.63 | 172.301 | 2238.79 | 25.84 | 46.54 | 6.39 | 1.325 | 4.427 | 8680.41 | 1.735 | 97.9 | 77 | 1455 | 23.27 | 5642.3 | 1760.4 | 2213.5 | 2838.3 | 1214.2 | 0.61562 | 5.751
2024-12-09 | 23:35 | Data | 0 | 33.284 | 31.366 | 182.694 | 7.63 | 172.346 | 2236.08 | 25.84 | 46.54 | 6.39 | 1.335 | 4.425 | 8693.98 | 1.985 | 97.9 | 76.8 | 1453 | 23.22 | 5651.1 | 1755.1 | 2212.2 | 2835.6 | 1214.2 | 0.61632 | 5.761
2024-12-09 | 23:35 | Data | 0 | 32.96 | 31.414 | 182.83 | 7.64 | 172.391 | 2238.79 | 25.83 | 46.54 | 6.39 | 1.334 | 4.422 | 8693.98 | 1.789 | 97.9 | 76.8 | 1455 | 23.22 | 5651.1 | 1751.1 | 2216.5 | 2838.3 | 1214.2 | 0.61409 | 5.756
2024-12-09 | 23:35 | Data | 0 | 33.021 | 31.171 | 182.694 | 7.63 | 172.301 | 2244.22 | 25.84 | 46.45 | 6.39 | 1.341 | 4.414 | 8689.46 | 1.647 | 97.9 | 76.7 | 1459 | 23.22 | 5648.1 | 1769.4 | 2212.8 | 2845.4 | 1214.2 | 0.61882 | 5.754
2024-12-09 | 23:35 | Data | 0 | 33.237 | 31.123 | 182.785 | 7.64 | 172.436 | 2241.5 | 25.84 | 46.45 | 6.39 | 1.337 | 4.44 | 8689.46 | 1.863 | 97.9 | 76.9 | 1458 | 23.22 | 5648.1 | 1751.8 | 2217.9 | 2836.7 | 1214.2 | 0.61483 | 5.777
2024-12-09 | 23:35 | Data | 0 | 33.183 | 31.123 | 182.649 | 7.64 | 172.346 | 2238.79 | 25.83 | 46.54 | 6.39 | 1.335 | 4.412 | 8680.41 | 2.046 | 97.9 | 76.8 | 1456 | 23.22 | 5642.3 | 1756.3 | 2216.5 | 2838.4 | 1214.2 | 0.61682 | 5.747
2024-12-09 | 23:36 | Data | 0 | 33.399 | 31.596 | 182.694 | 7.63 | 172.436 | 2238.79 | 25.83 | 46.359 | 6.39 | 1.332 | 4.426 | 8680.41 | 1.735 | 97.9 | 76.9 | 1456 | 23.13 | 5642.3 | 1753.3 | 2184.8 | 2815.3 | 1214.2 | 0.61733 | 5.758
2024-12-09 | 23:36 | Data | 0 | 33.459 | 31.36 | 182.694 | 7.64 | 172.346 | 2234.27 | 25.83 | 46.359 | 6.39 | 1.327 | 4.429 | 8693.98 | 1.938 | 97.9 | 77 | 1452 | 23.22 | 5651.1 | 1766.8 | 2198.1 | 2810.8 | 1214.2 | 0.61904 | 5.756
2024-12-09 | 23:36 | Data | 0 | 33.054 | 31.326 | 182.649 | 7.64 | 172.21 | 2233.37 | 25.84 | 46.45 | 6.39 | 1.327 | 4.406 | 8703.03 | 1.863 | 97.9 | 76.9 | 1451 | 23.22 | 5657 | 1768.4 | 2178 | 2818.8 | 1214.2 | 0.62427 | 5.733
2024-12-09 | 23:36 | Data | 0 | 33.007 | 31.164 | 182.739 | 7.63 | 172.301 | 2228.85 | 25.84 | 46.269 | 6.39 | 1.339 | 4.419 | 8689.46 | 1.789 | 97.9 | 76.7 | 1449 | 23.13 | 5648.1 | 1757.7 | 2193.8 | 2827 | 1214.2 | 0.61847 | 5.759
2024-12-09 | 23:36 | Data | 0 | 33.183 | 31.555 | 182.649 | 7.63 | 172.301 | 2233.37 | 25.83 | 46.269 | 6.39 | 1.332 | 4.421 | 8693.98 | 1.843 | 97.9 | 76.9 | 1451 | 23.13 | 5651.1 | 1758.5 | 2180.5 | 2814.1 | 1214.2 | 0.62309 | 5.752
2024-12-09 | 23:36 | Data | 0 | 33.351 | 31.407 | 181.789 | 7.63 | 171.352 | 2233.37 | 25.84 | 46.179 | 6.39 | 1.339 | 4.417 | 8689.46 | 2.019 | 97.9 | 76.7 | 1452 | 23.13 | 5648.1 | 1729.6 | 2165.2 | 2785.4 | 1214.2 | 0.61809 | 5.756
2024-12-09 | 23:36 | Data | 0 | 33.723 | 31.697 | 178.804 | 7.64 | 168.685 | 2232.47 | 25.83 | 46.179 | 6.39 | 1.322 | 4.403 | 8693.98 | 1.836 | 97.9 | 76.9 | 1452 | 23.09 | 5651.1 | 1729.8 | 2174.6 | 2793.1 | 1214.2 | 0.61614 | 5.725
2024-12-09 | 23:36 | Data | 0 | 33.237 | 31.522 | 175.864 | 7.63 | 166.154 | 2232.47 | 25.85 | 46.269 | 6.39 | 1.317 | 4.355 | 8689.46 | 1.722 | 97.9 | 76.8 | 1452 | 23.13 | 5648.1 | 1707.4 | 2148.4 | 2756.4 | 1214.2 | 0.61668 | 5.672
2024-12-09 | 23:36 | Data | 0 | 33.54 | 31.967 | 173.783 | 7.63 | 164.076 | 2232.47 | 25.84 | 46.179 | 6.39 | 1.319 | 4.272 | 8693.98 | 1.661 | 97.9 | 76.4 | 1451 | 23.04 | 5651.1 | 1684.7 | 2124.3 | 2725.5 | 1214.2 | 0.61564 | 5.591
2024-12-09 | 23:36 | Data | 0 | 33.588 | 32.021 | 172.2 | 7.63 | 162.629 | 2244.22 | 25.84 | 46.179 | 6.39 | 1.299 | 4.228 | 8680.41 | 1.789 | 97.9 | 76.5 | 1458 | 23.09 | 5642.3 | 1676.7 | 2116.7 | 2715.2 | 1214.2 | 0.6144 | 5.529
2024-12-09 | 23:36 | Data | 0 | 33.81 | 32.035 | 170.843 | 7.64 | 161.409 | 2239.7 | 25.84 | 46.45 | 6.39 | 1.287 | 4.213 | 8662.33 | 1.809 | 97.9 | 76.6 | 1456 | 23.27 | 5630.5 | 1678.6 | 2091.5 | 2695.1 | 1214.2 | 0.62064 | 5.5
2024-12-09 | 23:36 | Data | 0 | 33.561 | 32.021 | 169.712 | 7.64 | 160.46 | 2230.66 | 25.84 | 46.811 | 6.39 | 1.283 | 4.18 | 8662.33 | 1.33 | 97.9 | 76.5 | 1450 | 23.41 | 5630.5 | 1651.2 | 2075.9 | 2661.2 | 1214.2 | 0.61338 | 5.464
2024-12-09 | 23:36 | Data | 0 | 33.696 | 32.028 | 168.943 | 7.63 | 159.556 | 2235.18 | 25.84 | 47.082 | 6.39 | 1.276 | 4.162 | 8662.33 | 1.62 | 97.9 | 76.5 | 1453 | 23.54 | 5630.5 | 1624.2 | 2070 | 2647.6 | 1214.2 | 0.61008 | 5.438
2024-12-09 | 23:36 | Data | 0 | 33.655 | 31.826 | 168.627 | 7.63 | 159.33 | 2232.47 | 25.84 | 47.353 | 6.4 | 1.289 | 4.12 | 8635.19 | 1.728 | 97.9 | 76.2 | 1452 | 23.63 | 5612.9 | 1657.6 | 2091.9 | 2683.2 | 1214.2 | 0.61476 | 5.41
2024-12-09 | 23:36 | Data | 0 | 33.581 | 32.028 | 168.627 | 7.63 | 159.375 | 2232.47 | 25.84 | 47.533 | 6.4 | 1.288 | 4.109 | 8621.63 | 1.695 | 97.9 | 76.1 | 1451 | 23.81 | 5604.1 | 1644.8 | 2080.6 | 2666.5 | 1214.2 | 0.61456 | 5.397
2024-12-09 | 23:36 | Data | 0 | 33.756 | 32.008 | 168.672 | 7.63 | 159.421 | 2233.37 | 25.84 | 47.533 | 6.4 | 1.288 | 4.107 | 8594.49 | 1.492 | 97.9 | 76.1 | 1452 | 23.81 | 5586.4 | 1637.7 | 2082 | 2664.1 | 1214.2 | 0.61316 | 5.395
2024-12-09 | 23:36 | Data | 0 | 33.972 | 32.035 | 168.672 | 7.64 | 159.466 | 2235.18 | 25.84 | 47.894 | 6.4 | 1.285 | 4.125 | 8580.93 | 1.749 | 97.9 | 76.2 | 1453 | 23.99 | 5577.6 | 1635.6 | 2089.5 | 2667.5 | 1214.3 | 0.6105 | 5.411
2024-12-09 | 23:36 | Data | 0 | 33.642 | 32.19 | 168.672 | 7.63 | 159.33 | 2239.7 | 25.84 | 48.255 | 6.41 | 1.291 | 4.125 | 8562.84 | 1.715 | 97.8 | 76.2 | 1456 | 24.08 | 5565.8 | 1640.6 | 2058.4 | 2648.1 | 1214.3 | 0.6162 | 5.416
2024-12-09 | 23:37 | Data | 0 | 33.642 | 32.028 | 168.627 | 7.63 | 159.285 | 2235.18 | 25.83 | 48.165 | 6.4 | 1.299 | 4.144 | 8558.31 | 1.614 | 97.8 | 76.1 | 1453 | 24.08 | 5562.9 | 1635 | 2082.1 | 2660.6 | 1214.3 | 0.61176 | 5.443
2024-12-09 | 23:37 | Data | 0 | 33.817 | 32.028 | 168.717 | 7.63 | 159.33 | 2235.18 | 25.84 | 48.165 | 6.4 | 1.288 | 4.139 | 8562.84 | 1.715 | 97.8 | 76.3 | 1452 | 24.08 | 5565.8 | 1657.9 | 2079.9 | 2674.6 | 1214.3 | 0.61328 | 5.426
2024-12-09 | 23:37 | Data | 0 | 33.878 | 32.035 | 168.672 | 7.63 | 159.421 | 2232.47 | 25.84 | 48.346 | 6.41 | 1.282 | 4.147 | 8558.31 | 1.715 | 97.8 | 76.4 | 1452 | 24.13 | 5562.9 | 1643.5 | 2053.7 | 2637.7 | 1214.3 | 0.62029 | 5.429
2024-12-09 | 23:37 | Data | 0 | 33.486 | 32.028 | 168.582 | 7.63 | 159.375 | 2233.37 | 25.83 | 48.436 | 6.41 | 1.289 | 4.129 | 8549.27 | 1.391 | 97.8 | 76.2 | 1451 | 24.17 | 5557 | 1645.1 | 2060.7 | 2651.6 | 1214.3 | 0.61752 | 5.417
2024-12-09 | 23:37 | Data | 0 | 33.642 | 32.028 | 168.491 | 7.64 | 159.24 | 2238.79 | 25.85 | 48.346 | 6.41 | 1.287 | 4.128 | 8540.22 | 1.62 | 97.8 | 76.2 | 1455 | 24.22 | 5551.1 | 1626.6 | 2050.3 | 2630.8 | 1214.3 | 0.61575 | 5.416
2024-12-09 | 23:37 | Data | 0 | 33.527 | 32.082 | 168.491 | 7.63 | 159.24 | 2239.7 | 25.84 | 48.526 | 6.41 | 1.278 | 4.14 | 8526.66 | 1.485 | 97.8 | 76.4 | 1455 | 24.22 | 5542.3 | 1647.2 | 2052.8 | 2647.3 | 1214.3 | 0.61985 | 5.418
2024-12-09 | 23:37 | Data | 0 | 33.648 | 32.028 | 168.627 | 7.64 | 159.285 | 2365.33 | 25.86 | 48.436 | 6.41 | 1.285 | 4.143 | 8526.66 | 1.614 | 98 | 76.3 | 1537 | 24.22 | 5542.3 | 1635.5 | 2044.7 | 2634.6 | 1214.3 | 0.61967 | 5.427
2024-12-09 | 23:37 | Data | 0 | 33.642 | 32.015 | 168.536 | 7.63 | 159.33 | 2247.83 | 25.86 | 48.346 | 6.41 | 1.285 | 4.122 | 8517.61 | 1.627 | 97.8 | 76.2 | 1461 | 24.22 | 5536.4 | 1626.8 | 2041 | 2626.1 | 1214.3 | 0.61676 | 5.407
2024-12-09 | 23:37 | Data | 0 | 33.864 | 32.035 | 168.672 | 7.64 | 159.375 | 2246.93 | 25.85 | 48.436 | 6.41 | 1.291 | 4.13 | 8526.66 | 1.661 | 97.8 | 76.2 | 1460 | 24.22 | 5542.3 | 1654.2 | 2053.6 | 2649.4 | 1214.3 | 0.62127 | 5.42
2024-12-09 | 23:37 | Data | 0 | 33.844 | 32.143 | 168.627 | 7.63 | 159.285 | 2249.64 | 25.84 | 48.346 | 6.41 | 1.284 | 4.112 | 8517.61 | 1.607 | 97.9 | 76.2 | 1462 | 24.17 | 5536.4 | 1622.6 | 2038.2 | 2616.6 | 1214.3 | 0.61619 | 5.397
2024-12-09 | 23:37 | Data | 0 | 33.662 | 32.001 | 168.672 | 7.63 | 159.33 | 2249.64 | 25.85 | 48.797 | 6.41 | 1.284 | 4.105 | 8495 | 1.499 | 97.8 | 76.2 | 1462 | 24.35 | 5521.8 | 1618.2 | 2060.2 | 2632.4 | 1214.3 | 0.61238 | 5.392
2024-12-09 | 23:37 | Data | 0 | 33.723 | 32.136 | 168.536 | 7.63 | 159.24 | 2244.22 | 25.86 | 48.526 | 6.41 | 1.284 | 4.104 | 8513.09 | 1.728 | 97.8 | 76.2 | 1459 | 24.17 | 5533.5 | 1632.1 | 2042.7 | 2627.2 | 1214.3 | 0.61849 | 5.388
2024-12-09 | 23:37 | Data | 0 | 33.412 | 31.981 | 168.627 | 7.63 | 159.285 | 2249.64 | 25.84 | 48.526 | 6.41 | 1.286 | 4.131 | 8513.09 | 1.526 | 97.9 | 76.3 | 1462 | 24.22 | 5533.5 | 1626.9 | 2052.3 | 2632.9 | 1214.3 | 0.61252 | 5.417
2024-12-09 | 23:37 | Data | 0 | 33.642 | 32.197 | 168.536 | 7.63 | 159.24 | 2246.93 | 25.86 | 48.436 | 6.41 | 1.288 | 4.111 | 8517.61 | 1.506 | 97.8 | 76.1 | 1461 | 24.22 | 5536.4 | 1610 | 2052.9 | 2625.2 | 1214.3 | 0.61158 | 5.398
2024-12-09 | 23:37 | Data | 0 | 33.466 | 32.001 | 168.491 | 7.63 | 159.24 | 2246.93 | 25.85 | 48.436 | 6.41 | 1.293 | 4.122 | 8526.66 | 1.533 | 97.8 | 76.1 | 1461 | 24.22 | 5542.3 | 1626.9 | 2048.1 | 2628.9 | 1214.3 | 0.61436 | 5.415
2024-12-09 | 23:37 | Data | 0 | 33.655 | 31.805 | 168.582 | 7.64 | 159.33 | 2246.93 | 25.85 | 48.436 | 6.41 | 1.291 | 4.134 | 8526.66 | 1.627 | 97.8 | 76.2 | 1461 | 24.17 | 5542.3 | 1637.5 | 2029.6 | 2622.4 | 1214.3 | 0.6214 | 5.425
2024-12-09 | 23:37 | Data | 0 | 33.628 | 32.231 | 168.536 | 7.64 | 159.24 | 2244.22 | 25.85 | 48.346 | 6.41 | 1.291 | 4.113 | 8522.14 | 1.506 | 97.8 | 76.1 | 1459 | 24.22 | 5539.4 | 1621.8 | 2064.5 | 2638.3 | 1214.3 | 0.61217 | 5.404
2024-12-09 | 23:38 | Data | 0 | 33.615 | 32.028 | 168.536 | 7.63 | 159.24 | 2244.22 | 25.84 | 48.436 | 6.41 | 1.293 | 4.148 | 8495 | 1.728 | 97.8 | 76.2 | 1458 | 24.22 | 5521.8 | 1646.7 | 2071.8 | 2660.2 | 1214.3 | 0.61449 | 5.442
2024-12-09 | 23:38 | Data | 0 | 33.466 | 31.805 | 168.536 | 7.64 | 159.195 | 2245.12 | 25.85 | 48.436 | 6.41 | 1.287 | 4.102 | 8485.96 | 1.614 | 97.8 | 76.1 | 1459 | 24.22 | 5515.9 | 1652.8 | 2069.3 | 2661.6 | 1214.3 | 0.61848 | 5.389
2024-12-09 | 23:38 | Data | 0 | 33.878 | 32.035 | 168.717 | 7.64 | 159.375 | 2244.22 | 25.83 | 48.436 | 6.42 | 1.276 | 4.116 | 8485.96 | 1.634 | 97.8 | 76.3 | 1459 | 24.17 | 5515.9 | 1635.8 | 2052.9 | 2639.7 | 1214.3 | 0.61715 | 5.392
2024-12-09 | 23:38 | Data | 0 | 33.419 | 31.812 | 168.627 | 7.64 | 159.24 | 2242.41 | 25.86 | 48.436 | 6.41 | 1.277 | 4.131 | 8485.96 | 1.573 | 97.8 | 76.4 | 1458 | 24.17 | 5515.9 | 1654.1 | 2022.6 | 2626.3 | 1214.3 | 0.62485 | 5.408
2024-12-09 | 23:38 | Data | 0 | 33.655 | 31.853 | 168.446 | 7.64 | 159.24 | 2242.41 | 25.84 | 48.346 | 6.41 | 1.276 | 4.136 | 8467.87 | 1.566 | 97.8 | 76.4 | 1457 | 24.22 | 5504.1 | 2724.3 | 2635 | 3921.1 | 1214.3 | 0.67755 | 5.412
2024-12-09 | 23:38 | Data | 0 | 33.412 | 32.001 | 168.446 | 7.64 | 159.24 | 2241.5 | 25.84 | 48.346 | 6.41 | 1.282 | 4.136 | 8467.87 | 1.614 | 97.8 | 76.3 | 1457 | 24.22 | 5504.1 | 2717.7 | 2647.5 | 3927.5 | 1214.3 | 0.67422 | 5.419
2024-12-09 | 23:38 | Data | 0 | 33.642 | 32.143 | 168.672 | 7.64 | 159.149 | 2241.5 | 25.83 | 48.526 | 6.41 | 1.294 | 4.136 | 8472.39 | 1.587 | 97.8 | 76.2 | 1457 | 24.22 | 5507.1 | 2719.1 | 2642 | 3918.7 | 1214.3 | 0.67666 | 5.43
2024-12-09 | 23:38 | Data | 0 | 33.189 | 31.799 | 168.491 | 7.64 | 159.195 | 2242.41 | 25.85 | 48.436 | 6.41 | 1.282 | 4.129 | 8454.3 | 1.499 | 97.8 | 76.3 | 1458 | 24.22 | 5495.3 | 2714.2 | 2648 | 3924.9 | 1214.3 | 0.67439 | 5.412
2024-12-09 | 23:38 | Data | 0 | 33.642 | 32.028 | 168.536 | 7.63 | 159.285 | 2243.31 | 25.86 | 48.436 | 6.41 | 1.287 | 4.122 | 8454.3 | 1.614 | 97.8 | 76.2 | 1459 | 24.26 | 5495.3 | 2719.3 | 2672.5 | 3942.3 | 1214.3 | 0.67391 | 5.409
2024-12-09 | 23:38 | Data | 0 | 33.642 | 32.19 | 168.582 | 7.64 | 159.285 | 2244.22 | 25.84 | 48.436 | 6.41 | 1.292 | 4.139 | 8458.83 | 1.668 | 97.8 | 76.2 | 1459 | 24.22 | 5498.2 | 2725 | 2653 | 3935.3 | 1214.3 | 0.67538 | 5.431
2024-12-09 | 23:38 | Data | 0 | 33.952 | 31.94 | 168.627 | 7.63 | 159.33 | 2241.5 | 25.86 | 48.436 | 6.41 | 1.284 | 4.115 | 8458.83 | 1.83 | 97.8 | 76.2 | 1457 | 24.22 | 5498.2 | 2706.5 | 2649.4 | 3912 | 1214.3 | 0.6727 | 5.4
2024-12-09 | 23:38 | Data | 0 | 33.412 | 31.913 | 168.536 | 7.64 | 159.149 | 2241.5 | 25.84 | 48.436 | 6.4 | 1.279 | 4.097 | 8458.83 | 1.789 | 97.8 | 76.2 | 1458 | 24.26 | 5498.2 | 2712.9 | 2663.1 | 3932.4 | 1214.3 | 0.67271 | 5.376
2024-12-09 | 23:38 | Data | 0 | 33.527 | 31.812 | 168.491 | 7.63 | 159.24 | 2241.5 | 25.85 | 48.436 | 6.41 | 1.28 | 4.097 | 8463.35 | 1.634 | 97.8 | 76.2 | 1457 | 24.17 | 5501.2 | 2714.9 | 2661 | 3931.9 | 1214.3 | 0.67359 | 5.379
2024-12-09 | 23:38 | Data | 0 | 33.324 | 31.974 | 168.536 | 7.63 | 159.195 | 2240.6 | 25.86 | 48.436 | 6.41 | 1.289 | 4.131 | 8472.39 | 1.573 | 97.8 | 76.2 | 1456 | 24.17 | 5507.1 | 2716 | 2667.1 | 3935.3 | 1214.3 | 0.67285 | 5.42
2024-12-09 | 23:38 | Data | 0 | 33.534 | 32.028 | 168.446 | 7.64 | 159.195 | 2242.41 | 25.84 | 48.346 | 6.41 | 1.291 | 4.116 | 8454.3 | 1.607 | 97.8 | 76.1 | 1457 | 24.22 | 5495.3 | 2722.4 | 2637 | 3919.7 | 1214.3 | 0.67684 | 5.408
2024-12-09 | 23:38 | Data | 0 | 33.554 | 31.805 | 168.582 | 7.64 | 159.285 | 2242.41 | 25.84 | 48.436 | 6.41 | 1.291 | 4.119 | 8467.87 | 1.418 | 97.8 | 76.1 | 1457 | 24.22 | 5504.1 | 2713.2 | 2654.3 | 3925.2 | 1214.3 | 0.67401 | 5.41
2024-12-09 | 23:38 | Data | 0 | 33.473 | 32.028 | 168.536 | 7.63 | 159.195 | 2241.5 | 25.84 | 48.165 | 6.41 | 1.29 | 4.115 | 8454.3 | 1.398 | 97.9 | 76.1 | 1458 | 24.08 | 5495.3 | 2721.7 | 2636 | 3918.1 | 1214.3 | 0.67784 | 5.405
2024-12-09 | 23:38 | Data | 0 | 33.426 | 31.974 | 168.536 | 7.63 | 159.24 | 2235.18 | 25.84 | 48.165 | 6.41 | 1.285 | 4.113 | 8445.26 | 1.614 | 97.8 | 76.2 | 1453 | 24.08 | 5489.4 | 2711.2 | 2640.7 | 3915.6 | 1214.3 | 0.67506 | 5.398
2024-12-09 | 23:39 | Data | 0 | 33.655 | 32.028 | 168.446 | 7.63 | 159.149 | 2235.18 | 25.84 | 48.075 | 6.41 | 1.275 | 4.138 | 8445.26 | 1.499 | 97.8 | 76.4 | 1453 | 24.08 | 5489.4 | 2721.2 | 2636.8 | 3917.5 | 1214.3 | 0.67781 | 5.413
2024-12-09 | 23:39 | Data | 0 | 33.021 | 31.515 | 168.355 | 7.63 | 159.104 | 2236.08 | 25.84 | 48.346 | 6.41 | 1.273 | 4.112 | 8440.74 | 1.62 | 97.8 | 76.3 | 1453 | 24.17 | 5486.5 | 2702.7 | 2648.2 | 3913.7 | 1214.3 | 0.67338 | 5.386
2024-12-09 | 23:39 | Data | 0 | 33.412 | 31.623 | 168.31 | 7.63 | 159.104 | 2238.79 | 25.84 | 48.436 | 6.41 | 1.287 | 4.089 | 8427.17 | 1.526 | 97.8 | 76.1 | 1455 | 24.22 | 5477.7 | 2707.8 | 2637.8 | 3909.2 | 1214.3 | 0.67463 | 5.376
2024-12-09 | 23:39 | Data | 0 | 33.412 | 31.63 | 168.401 | 7.63 | 159.104 | 2238.79 | 25.84 | 48.436 | 6.41 | 1.277 | 4.115 | 8427.17 | 1.728 | 97.8 | 76.3 | 1455 | 24.26 | 5477.7 | 2712.3 | 2652.2 | 3918.1 | 1214.3 | 0.67342 | 5.392
2024-12-09 | 23:39 | Data | 0 | 33.405 | 31.603 | 168.401 | 7.64 | 159.104 | 2239.7 | 25.85 | 48.436 | 6.41 | 1.28 | 4.144 | 8445.26 | 1.708 | 97.8 | 76.4 | 1456 | 24.22 | 5489.4 | 2693.7 | 2664.3 | 3919.5 | 1214.3 | 0.66844 | 5.424
2024-12-09 | 23:39 | Data | 0 | 33.628 | 31.799 | 168.446 | 7.63 | 159.195 | 2241.5 | 25.88 | 48.436 | 6.4 | 1.29 | 4.134 | 8440.74 | 1.789 | 97.8 | 76.2 | 1458 | 24.17 | 5486.5 | 2717.4 | 2653.5 | 3928 | 1214.3 | 0.67532 | 5.422
2024-12-09 | 23:39 | Data | 0 | 33.466 | 31.805 | 168.536 | 7.63 | 159.195 | 2246.02 | 25.89 | 48.346 | 6.41 | 1.293 | 4.136 | 8454.3 | 1.728 | 97.8 | 76.2 | 1460 | 24.17 | 5495.3 | 2704 | 2635.1 | 3896.9 | 1214.3 | 0.67478 | 5.43
2024-12-09 | 23:39 | Data | 0 | 33.412 | 31.799 | 168.536 | 7.64 | 159.24 | 2246.02 | 25.89 | 48.526 | 6.41 | 1.282 | 4.137 | 8458.83 | 1.614 | 97.8 | 76.3 | 1460 | 24.22 | 5498.2 | 2717.5 | 2615.9 | 3899.4 | 1214.3 | 0.68092 | 5.42
2024-12-09 | 23:39 | Data | 0 | 33.412 | 32.001 | 168.491 | 7.64 | 159.149 | 2246.02 | 25.88 | 48.436 | 6.41 | 1.282 | 4.149 | 8467.87 | 1.445 | 97.8 | 76.4 | 1461 | 24.17 | 5504.1 | 2710.9 | 2622.1 | 3897.1 | 1214.3 | 0.67801 | 5.43
2024-12-09 | 23:39 | Data | 0 | 33.837 | 31.839 | 168.491 | 7.63 | 159.33 | 2246.93 | 25.86 | 48.436 | 6.41 | 1.282 | 4.157 | 8472.39 | 1.782 | 97.8 | 76.4 | 1461 | 24.22 | 5507.1 | 2711.1 | 2643.3 | 3913.1 | 1214.3 | 0.67683 | 5.439
2024-12-09 | 23:39 | Data | 0 | 33.385 | 31.792 | 168.446 | 7.63 | 159.059 | 2247.83 | 25.89 | 48.436 | 6.41 | 1.288 | 4.133 | 8630.67 | 1.62 | 97.8 | 76.2 | 1461 | 24.22 | 5609.9 | 2697.6 | 2647.4 | 3898 | 1214.3 | 0.67286 | 5.42
2024-12-09 | 23:39 | Data | 0 | 33.864 | 31.94 | 168.536 | 7.64 | 159.24 | 2246.93 | 25.88 | 48.346 | 6.41 | 1.284 | 4.116 | 8662.33 | 1.735 | 97.8 | 76.2 | 1461 | 24.22 | 5630.5 | 2714.7 | 2642.4 | 3916.1 | 1214.4 | 0.67563 | 5.4
2024-12-09 | 23:39 | Data | 0 | 33.642 | 31.711 | 168.446 | 7.64 | 159.195 | 2255.97 | 25.88 | 48.436 | 6.41 | 1.288 | 4.124 | 8657.8 | 1.56 | 97.9 | 76.2 | 1466 | 24.22 | 5627.6 | 2710.5 | 2636.6 | 3910.1 | 1214.4 | 0.67549 | 5.411
2024-12-09 | 23:39 | Data | 0 | 33.412 | 31.805 | 168.401 | 7.64 | 159.149 | 2241.5 | 25.88 | 48.346 | 6.41 | 1.287 | 4.108 | 8666.85 | 1.56 | 97.8 | 76.1 | 1457 | 24.17 | 5633.5 | 2695.7 | 2640 | 3903.1 | 1214.4 | 0.67369 | 5.395
2024-12-09 | 23:39 | Data | 0 | 33.588 | 31.805 | 168.672 | 7.63 | 159.24 | 2244.22 | 25.88 | 48.436 | 6.41 | 1.293 | 4.095 | 8476.91 | 1.782 | 97.8 | 76 | 1459 | 24.17 | 5510 | 2717.1 | 2656.2 | 3928.9 | 1214.4 | 0.67344 | 5.388
2024-12-09 | 23:39 | Data | 0 | 33.412 | 31.846 | 168.446 | 7.64 | 159.195 | 2241.5 | 25.86 | 48.436 | 6.41 | 1.29 | 4.121 | 8467.87 | 1.587 | 97.8 | 76.2 | 1457 | 24.22 | 5504.1 | 2713.5 | 2652.1 | 3925 | 1214.4 | 0.67448 | 5.411
2024-12-09 | 23:39 | Data | 0 | 33.439 | 31.799 | 168.446 | 7.63 | 159.285 | 2241.5 | 25.86 | 48.436 | 6.41 | 1.282 | 4.129 | 8467.87 | 1.614 | 97.8 | 76.3 | 1457 | 24.22 | 5504.1 | 2691.7 | 2641.8 | 3900.8 | 1214.4 | 0.67259 | 5.411
2024-12-09 | 23:40 | Data | 0 | 33.419 | 32.028 | 168.582 | 7.64 | 159.195 | 2241.5 | 25.88 | 48.436 | 6.41 | 1.273 | 4.11 | 8467.87 | 1.506 | 97.8 | 76.3 | 1457 | 24.22 | 5504.1 | 2710.1 | 2620.9 | 3900.6 | 1214.4 | 0.67823 | 5.384
2024-12-09 | 23:40 | Data | 0 | 33.48 | 31.92 | 168.536 | 7.64 | 159.24 | 2239.7 | 25.86 | 48.346 | 6.41 | 1.282 | 4.107 | 8458.83 | 1.384 | 97.8 | 76.2 | 1455 | 24.17 | 5498.2 | 2714.1 | 2626.1 | 3904.8 | 1214.4 | 0.67814 | 5.39
2024-12-09 | 23:40 | Data | 0 | 33.635 | 32.021 | 168.491 | 7.64 | 159.195 | 2241.5 | 25.88 | 48.436 | 6.4 | 1.277 | 4.105 | 8454.3 | 1.641 | 97.8 | 76.3 | 1457 | 24.22 | 5495.3 | 2715.3 | 2635.8 | 3910 | 1214.4 | 0.67777 | 5.382
2024-12-09 | 23:40 | Data | 0 | 33.257 | 31.583 | 168.401 | 7.63 | 159.149 | 2240.6 | 25.89 | 48.436 | 6.41 | 1.282 | 4.122 | 8467.87 | 1.587 | 97.8 | 76.3 | 1457 | 24.22 | 5504.1 | 2710.4 | 2642.1 | 3914.2 | 1214.4 | 0.67601 | 5.404
2024-12-09 | 23:40 | Data | 0 | 33.608 | 31.853 | 168.536 | 7.63 | 159.149 | 2241.5 | 25.86 | 48.436 | 6.4 | 1.286 | 4.13 | 8476.91 | 1.728 | 97.8 | 76.3 | 1457 | 24.22 | 5510 | 2707.1 | 2652 | 3918.9 | 1214.4 | 0.67429 | 5.416
2024-12-09 | 23:40 | Data | 0 | 33.466 | 31.805 | 168.491 | 7.63 | 159.195 | 2241.5 | 25.88 | 48.436 | 6.41 | 1.291 | 4.12 | 8481.44 | 1.627 | 97.8 | 76.1 | 1457 | 24.17 | 5512.9 | 2692.5 | 2646.2 | 3901.9 | 1214.4 | 0.67241 | 5.411
2024-12-09 | 23:40 | Data | 0 | 33.702 | 32.008 | 168.582 | 7.64 | 159.33 | 2242.41 | 25.85 | 48.346 | 6.41 | 1.287 | 4.124 | 8495 | 1.492 | 97.8 | 76.2 | 1458 | 24.17 | 5521.8 | 2695 | 2655.1 | 3913.8 | 1214.4 | 0.6722 | 5.411
2024-12-09 | 23:40 | Data | 0 | 33.628 | 31.913 | 168.491 | 7.64 | 159.195 | 2241.5 | 25.86 | 48.436 | 6.41 | 1.284 | 4.105 | 8495 | 1.836 | 97.8 | 76.2 | 1456 | 24.22 | 5521.8 | 2710.2 | 2640.4 | 3910.8 | 1214.4 | 0.67481 | 5.389
2024-12-09 | 23:40 | Data | 0 | 33.419 | 32.001 | 168.491 | 7.64 | 159.24 | 2242.41 | 25.88 | 48.526 | 6.41 | 1.285 | 4.133 | 8499.53 | 1.614 | 97.8 | 76.3 | 1457 | 24.22 | 5524.7 | 2709.1 | 2651.1 | 3918.9 | 1214.4 | 0.67431 | 5.418
2024-12-09 | 23:40 | Data | 0 | 33.655 | 31.805 | 168.627 | 7.64 | 159.24 | 2238.79 | 25.85 | 48.526 | 6.41 | 1.293 | 4.101 | 8481.44 | 1.607 | 97.8 | 76 | 1455 | 24.22 | 5512.9 | 2722.4 | 2641.2 | 3914.9 | 1214.4 | 0.67899 | 5.395
2024-12-09 | 23:40 | Data | 0 | 33.642 | 32.251 | 168.672 | 7.64 | 159.24 | 2236.08 | 25.88 | 48.436 | 6.41 | 1.291 | 4.101 | 8476.91 | 1.438 | 97.8 | 76.1 | 1453 | 24.22 | 5510 | 2707.8 | 2636.4 | 3907.7 | 1214.4 | 0.67618 | 5.393
2024-12-09 | 23:40 | Data | 0 | 33.554 | 31.913 | 168.536 | 7.63 | 159.24 | 2236.08 | 25.88 | 48.346 | 6.41 | 1.284 | 4.126 | 8476.91 | 1.452 | 97.8 | 76.3 | 1453 | 24.22 | 5510 | 2708.7 | 2663.2 | 3926.8 | 1214.4 | 0.67282 | 5.411
2024-12-09 | 23:40 | Data | 0 | 33.419 | 31.812 | 168.627 | 7.63 | 159.24 | 2235.18 | 25.89 | 48.436 | 6.41 | 1.282 | 4.108 | 8481.44 | 1.587 | 97.8 | 76.2 | 1453 | 24.26 | 5512.9 | 2707.5 | 2649.4 | 3918.1 | 1214.4 | 0.67492 | 5.388
2024-12-09 | 23:40 | Data | 0 | 33.642 | 31.805 | 168.582 | 7.64 | 159.285 | 2236.08 | 25.88 | 48.436 | 6.41 | 1.295 | 4.133 | 8499.53 | 1.83 | 97.8 | 76.1 | 1453 | 24.22 | 5524.7 | 2693.5 | 2645 | 3905.1 | 1214.4 | 0.67217 | 5.428
2024-12-09 | 23:40 | Data | 0 | 33.635 | 31.913 | 168.627 | 7.64 | 159.195 | 2236.08 | 25.85 | 48.075 | 6.41 | 1.283 | 4.115 | 8526.66 | 1.641 | 97.8 | 76.2 | 1453 | 24.08 | 5542.3 | 2701.5 | 2653.4 | 3916.8 | 1214.4 | 0.67284 | 5.397
2024-12-09 | 23:40 | Data | 0 | 33.534 | 31.866 | 168.491 | 7.64 | 159.24 | 2235.18 | 25.89 | 48.165 | 6.41 | 1.279 | 4.131 | 8513.09 | 1.539 | 97.8 | 76.4 | 1453 | 24.08 | 5533.5 | 2705 | 2654.4 | 3914.3 | 1214.4 | 0.67529 | 5.41
2024-12-09 | 23:40 | Data | 0 | 33.642 | 31.913 | 168.401 | 7.63 | 159.149 | 2233.37 | 25.89 | 48.165 | 6.41 | 1.284 | 4.137 | 8490.48 | 1.553 | 97.8 | 76.3 | 1451 | 24.04 | 5518.8 | 2701.6 | 2662.6 | 3923 | 1214.4 | 0.67008 | 5.42
2024-12-09 | 23:40 | Data | 0 | 33.864 | 32.042 | 168.536 | 7.64 | 159.33 | 2229.75 | 25.86 | 48.436 | 6.41 | 1.282 | 4.134 | 8513.09 | 1.701 | 97.8 | 76.4 | 1450 | 24.22 | 5533.5 | 2716.5 | 2665.8 | 3929.3 | 1214.4 | 0.67454 | 5.414
2024-12-09 | 23:41 | Data | 0 | 33.621 | 31.826 | 168.536 | 7.63 | 159.195 | 2235.18 | 25.86 | 48.346 | 6.41 | 1.285 | 4.127 | 8495 | 1.728 | 97.8 | 76.3 | 1453 | 24.22 | 5521.8 | 2676.3 | 2665.5 | 3910.6 | 1214.4 | 0.66711 | 5.413
2024-12-09 | 23:41 | Data | 0 | 33.419 | 31.799 | 168.536 | 7.64 | 159.24 | 2238.79 | 25.85 | 48.436 | 6.41 | 1.293 | 4.129 | 8499.53 | 1.614 | 97.8 | 76.1 | 1456 | 24.22 | 5524.7 | 2691.2 | 2674.8 | 3929.8 | 1214.4 | 0.66809 | 5.422
2024-12-09 | 23:41 | Data | 0 | 33.642 | 31.826 | 168.491 | 7.63 | 159.24 | 2241.5 | 25.89 | 48.346 | 6.41 | 1.284 | 4.105 | 8485.96 | 1.789 | 97.8 | 76.2 | 1457 | 24.22 | 5515.9 | 2705.6 | 2670.5 | 3929.9 | 1214.4 | 0.66911 | 5.389
2024-12-09 | 23:41 | Data | 0 | 33.412 | 31.799 | 168.401 | 7.63 | 159.149 | 2241.5 | 25.88 | 48.436 | 6.41 | 1.285 | 4.109 | 8485.96 | 1.728 | 97.8 | 76.2 | 1457 | 24.22 | 5515.9 | 2693.5 | 2658.8 | 3911 | 1214.4 | 0.67125 | 5.393
2024-12-09 | 23:41 | Data | 0 | 33.486 | 31.92 | 168.627 | 7.64 | 159.285 | 2238.79 | 25.86 | 48.346 | 6.41 | 1.286 | 4.098 | 8499.53 | 1.512 | 97.8 | 76.1 | 1455 | 24.17 | 5524.7 | 2697.9 | 2657.8 | 3914.1 | 1214.4 | 0.67174 | 5.384
2024-12-09 | 23:41 | Data | 0 | 33.412 | 31.974 | 168.536 | 7.63 | 159.24 | 2241.5 | 25.88 | 48.346 | 6.41 | 1.291 | 4.118 | 8490.48 | 1.614 | 97.8 | 76.1 | 1457 | 24.22 | 5518.8 | 2704.6 | 2670.2 | 3926.4 | 1214.4 | 0.67311 | 5.41
2024-12-09 | 23:41 | Data | 0 | 33.426 | 31.913 | 168.446 | 7.63 | 159.24 | 2241.5 | 25.88 | 48.346 | 6.41 | 1.289 | 4.118 | 8495 | 1.614 | 97.8 | 76.2 | 1457 | 24.13 | 5521.8 | 2696.4 | 2657.1 | 3916.5 | 1214.4 | 0.66998 | 5.407
2024-12-09 | 23:41 | Data | 0 | 33.804 | 32.251 | 168.762 | 7.64 | 159.285 | 2238.79 | 25.86 | 48.526 | 6.41 | 1.27 | 4.116 | 8467.87 | 1.627 | 97.8 | 76.4 | 1456 | 24.22 | 5504.1 | 2686.9 | 2649.5 | 3904.6 | 1214.4 | 0.67171 | 5.386
2024-12-09 | 23:41 | Data | 0 | 33.75 | 32.028 | 168.627 | 7.64 | 159.195 | 2239.7 | 25.84 | 48.165 | 6.41 | 1.283 | 4.119 | 8458.83 | 1.627 | 97.8 | 76.2 | 1456 | 24.08 | 5498.2 | 2711.6 | 2656.3 | 3924.3 | 1214.4 | 0.67219 | 5.402
2024-12-09 | 23:41 | Data | 0 | 33.898 | 31.832 | 168.401 | 7.63 | 159.285 | 2239.7 | 25.88 | 48.165 | 6.42 | 1.289 | 4.119 | 8454.3 | 1.715 | 97.8 | 76.2 | 1456 | 24.08 | 5495.3 | 2685.3 | 2647.4 | 3900.7 | 1214.4 | 0.67047 | 5.406
2024-12-09 | 23:41 | Data | 0 | 33.412 | 31.799 | 168.491 | 7.64 | 159.285 | 2238.79 | 25.89 | 48.075 | 6.41 | 1.283 | 4.134 | 8454.3 | 1.614 | 97.9 | 76.3 | 1455 | 24.04 | 5495.3 | 2714.5 | 2654.1 | 3922.4 | 1214.4 | 0.67544 | 5.417
2024-12-09 | 23:41 | Data | 0 | 33.662 | 31.92 | 168.582 | 7.64 | 159.195 | 2238.79 | 25.88 | 48.165 | 6.41 | 1.277 | 4.126 | 8458.83 | 1.722 | 97.8 | 76.4 | 1455 | 24.08 | 5498.2 | 2693.2 | 2653.5 | 3911.3 | 1214.4 | 0.67259 | 5.402
2024-12-09 | 23:41 | Data | 0 | 33.419 | 31.853 | 168.582 | 7.64 | 159.285 | 2238.79 | 25.88 | 48.075 | 6.41 | 1.277 | 4.108 | 8476.91 | 1.506 | 97.8 | 76.3 | 1455 | 24.08 | 5510 | 2701.7 | 2631.8 | 3902.5 | 1214.4 | 0.67508 | 5.386
2024-12-09 | 23:41 | Data | 0 | 33.473 | 32.237 | 168.627 | 7.63 | 159.33 | 2239.7 | 25.88 | 48.165 | 6.41 | 1.275 | 4.127 | 8458.83 | 1.472 | 97.8 | 76.4 | 1456 | 24.08 | 5498.2 | 2696.1 | 2653.1 | 3912.7 | 1214.4 | 0.6714 | 5.402
2024-12-09 | 23:41 | Data | 0 | 33.588 | 31.859 | 168.582 | 7.64 | 159.285 | 2239.7 | 25.86 | 48.255 | 6.41 | 1.284 | 4.148 | 8454.3 | 1.647 | 97.8 | 76.4 | 1455 | 24.08 | 5495.3 | 2697 | 2635.8 | 3900.4 | 1214.4 | 0.67447 | 5.433
2024-12-09 | 23:41 | Data | 0 | 33.432 | 31.826 | 168.582 | 7.64 | 159.285 | 2241.5 | 25.85 | 48.436 | 6.4 | 1.288 | 4.097 | 8445.26 | 1.56 | 97.8 | 76.1 | 1457 | 24.22 | 5489.4 | 2698.2 | 2643 | 3911.6 | 1214.4 | 0.6721 | 5.384
2024-12-09 | 23:41 | Data | 0 | 33.628 | 32.244 | 168.627 | 7.63 | 159.285 | 2240.6 | 25.89 | 48.436 | 6.41 | 1.288 | 4.115 | 8418.13 | 1.58 | 97.8 | 76.2 | 1457 | 24.22 | 5471.8 | 2697.6 | 2624.6 | 3885.3 | 1214.5 | 0.67445 | 5.403
2024-12-09 | 23:41 | Data | 0 | 33.642 | 32.028 | 168.536 | 7.64 | 159.24 | 2244.22 | 25.86 | 48.436 | 6.41 | 1.283 | 4.14 | 8427.17 | 1.614 | 97.8 | 76.3 | 1459 | 24.22 | 5477.7 | 2707.3 | 2641.1 | 3910.2 | 1214.5 | 0.67618 | 5.422
2024-12-09 | 23:42 | Data | 0 | 33.756 | 31.826 | 168.582 | 7.64 | 159.285 | 2244.22 | 25.86 | 48.436 | 6.41 | 1.291 | 4.146 | 8440.74 | 1.627 | 97.8 | 76.2 | 1459 | 24.22 | 5486.5 | 2700.5 | 2654.6 | 3914.4 | 1214.5 | 0.67327 | 5.438
2024-12-09 | 23:42 | Data | 0 | 33.426 | 32.021 | 168.536 | 7.63 | 159.285 | 2245.12 | 25.88 | 48.436 | 6.41 | 1.283 | 4.124 | 8431.69 | 1.593 | 97.8 | 76.3 | 1459 | 24.22 | 5480.6 | 2701.9 | 2673.9 | 3931.1 | 1214.5 | 0.6703 | 5.408
2024-12-09 | 23:42 | Data | 0 | 33.642 | 31.974 | 168.627 | 7.64 | 159.24 | 2244.22 | 25.88 | 48.436 | 6.41 | 1.288 | 4.136 | 8481.44 | 1.668 | 97.8 | 76.3 | 1459 | 24.22 | 5512.9 | 2692.7 | 2684.9 | 3929.5 | 1214.5 | 0.66793 | 5.424
2024-12-09 | 23:42 | Data | 0 | 33.419 | 31.994 | 168.582 | 7.63 | 159.24 | 2244.22 | 25.85 | 48.436 | 6.41 | 1.293 | 4.143 | 8481.44 | 1.452 | 97.8 | 76.2 | 1459 | 24.22 | 5512.9 | 2711.3 | 2673.1 | 3933.9 | 1214.5 | 0.67191 | 5.436
2024-12-09 | 23:42 | Data | 0 | 33.412 | 31.805 | 168.446 | 7.64 | 159.285 | 2243.31 | 25.86 | 48.436 | 6.41 | 1.287 | 4.128 | 8481.44 | 1.6 | 97.8 | 76.2 | 1458 | 24.17 | 5512.9 | 2696.5 | 2678 | 3929.2 | 1214.5 | 0.66722 | 5.416
2024-12-09 | 23:42 | Data | 0 | 33.554 | 31.94 | 168.582 | 7.64 | 159.285 | 2241.5 | 25.89 | 48.436 | 6.41 | 1.282 | 4.132 | 8467.87 | 1.452 | 97.8 | 76.3 | 1458 | 24.17 | 5504.1 | 2703 | 2662.6 | 3922.2 | 1214.5 | 0.67156 | 5.412
2024-12-09 | 23:42 | Data | 0 | 33.588 | 31.859 | 168.627 | 7.64 | 159.285 | 2241.5 | 25.89 | 48.436 | 6.41 | 1.283 | 4.132 | 8458.83 | 1.519 | 97.8 | 76.3 | 1456 | 24.22 | 5498.2 | 2682.8 | 2657.3 | 3906.1 | 1214.5 | 0.66804 | 5.414
2024-12-09 | 23:42 | Data | 0 | 33.642 | 31.974 | 168.491 | 7.63 | 159.33 | 2244.22 | 25.88 | 48.436 | 6.41 | 1.293 | 4.134 | 8472.39 | 1.634 | 97.8 | 76.2 | 1459 | 24.22 | 5507.1 | 2692.8 | 2666.5 | 3918.1 | 1214.5 | 0.66913 | 5.427
2024-12-09 | 23:42 | Data | 0 | 33.743 | 32.028 | 168.491 | 7.64 | 159.24 | 2244.22 | 25.88 | 48.165 | 6.41 | 1.289 | 4.114 | 8472.39 | 1.634 | 97.9 | 76.1 | 1459 | 24.08 | 5507.1 | 2707.8 | 2660 | 3923.6 | 1214.5 | 0.67281 | 5.402
2024-12-09 | 23:42 | Data | 0 | 33.426 | 32.015 | 168.536 | 7.63 | 159.285 | 2244.22 | 25.86 | 48.165 | 6.41 | 1.283 | 4.138 | 8467.87 | 1.411 | 97.9 | 76.3 | 1459 | 24.04 | 5504.1 | 2720 | 2646.6 | 3921.9 | 1214.5 | 0.67643 | 5.421
2024-12-09 | 23:42 | Data | 0 | 33.837 | 32.028 | 168.536 | 7.64 | 159.24 | 2246.93 | 25.86 | 48.165 | 6.42 | 1.28 | 4.148 | 8467.87 | 1.661 | 97.9 | 76.4 | 1461 | 24.13 | 5504.1 | 2703.3 | 2657.8 | 3916.3 | 1214.5 | 0.67239 | 5.428
2024-12-09 | 23:42 | Data | 0 | 33.419 | 31.718 | 168.355 | 7.64 | 159.24 | 2246.93 | 25.86 | 48.075 | 6.41 | 1.282 | 4.146 | 8472.39 | 1.769 | 97.9 | 76.4 | 1461 | 24.08 | 5507.1 | 2700.3 | 2641.3 | 3902.8 | 1214.5 | 0.67554 | 5.429
2024-12-09 | 23:42 | Data | 0 | 33.696 | 31.974 | 168.536 | 7.63 | 159.285 | 2246.93 | 25.85 | 48.255 | 6.41 | 1.292 | 4.134 | 8481.44 | 1.634 | 97.9 | 76.2 | 1461 | 24.13 | 5512.9 | 2713.8 | 2656.6 | 3922.8 | 1214.5 | 0.67439 | 5.426
2024-12-09 | 23:42 | Data | 0 | 33.635 | 32.028 | 168.582 | 7.63 | 159.195 | 2246.93 | 25.89 | 48.165 | 6.41 | 1.296 | 4.126 | 8485.96 | 1.728 | 97.9 | 76.1 | 1461 | 24.04 | 5515.9 | 2710.8 | 2647.3 | 3919.7 | 1214.5 | 0.67294 | 5.422
2024-12-09 | 23:42 | Data | 0 | 33.419 | 31.974 | 168.536 | 7.63 | 159.285 | 2246.93 | 25.88 | 48.165 | 6.41 | 1.282 | 4.127 | 8481.44 | 1.614 | 97.9 | 76.3 | 1461 | 24.08 | 5512.9 | 2702.5 | 2666.4 | 3923 | 1214.5 | 0.67134 | 5.409
2024-12-09 | 23:42 | Data | 0 | 33.871 | 32.251 | 168.627 | 7.63 | 159.421 | 2246.93 | 25.88 | 48.165 | 6.41 | 1.278 | 4.12 | 8481.44 | 1.62 | 97.9 | 76.3 | 1461 | 24.13 | 5512.9 | 2704.8 | 2680.3 | 3939.7 | 1214.5 | 0.66988 | 5.398
2024-12-09 | 23:42 | Data | 0 | 33.743 | 31.927 | 168.491 | 7.64 | 159.33 | 2246.93 | 25.88 | 48.165 | 6.41 | 1.278 | 4.124 | 8495 | 1.83 | 97.9 | 76.3 | 1461 | 24.04 | 5521.8 | 2710.2 | 2641.5 | 3910.4 | 1214.5 | 0.67498 | 5.402
2024-12-09 | 23:42 | Data | 0 | 33.412 | 31.974 | 168.536 | 7.63 | 159.195 | 2246.93 | 25.88 | 48.165 | 6.41 | 1.277 | 4.13 | 8499.53 | 1.614 | 97.9 | 76.4 | 1461 | 24.08 | 5524.7 | 2688.2 | 2663.2 | 3914.3 | 1214.5 | 0.66976 | 5.406
2024-12-09 | 23:43 | Data | 0 | 33.642 | 31.853 | 168.446 | 7.64 | 159.33 | 2239.7 | 25.88 | 48.165 | 6.4 | 1.294 | 4.119 | 8472.39 | 1.614 | 97.8 | 76.1 | 1456 | 24.08 | 5507.1 | 2710.3 | 2666.8 | 3926.6 | 1214.5 | 0.67332 | 5.415
2024-12-09 | 23:43 | Data | 0 | 33.871 | 32.143 | 168.762 | 7.64 | 159.375 | 2244.22 | 25.88 | 48.165 | 6.41 | 1.285 | 4.125 | 8481.44 | 1.607 | 97.9 | 76.2 | 1459 | 24.08 | 5512.9 | 2691.7 | 2674.7 | 3921.9 | 1214.5 | 0.66965 | 5.411
2024-12-09 | 23:43 | Data | 0 | 33.419 | 32.028 | 168.491 | 7.63 | 159.285 | 2243.31 | 25.88 | 48.165 | 6.41 | 1.279 | 4.134 | 8495 | 1.56 | 97.9 | 76.4 | 1459 | 24.08 | 5521.8 | 2694.8 | 2691.7 | 3935 | 1214.5 | 0.66871 | 5.411
2024-12-09 | 23:43 | Data | 0 | 33.648 | 32.237 | 168.627 | 7.64 | 159.33 | 2246.93 | 25.88 | 48.075 | 6.41 | 1.285 | 4.145 | 8495 | 1.553 | 97.9 | 76.3 | 1461 | 24.08 | 5521.8 | 2701.1 | 2647.1 | 3904.6 | 1214.5 | 0.67563 | 5.43
2024-12-09 | 23:43 | Data | 0 | 33.635 | 31.812 | 168.536 | 7.63 | 159.285 | 2246.93 | 25.88 | 48.346 | 6.41 | 1.286 | 4.109 | 8485.96 | 1.782 | 97.8 | 76.2 | 1461 | 24.17 | 5515.9 | 2708 | 2668.3 | 3922.5 | 1214.5 | 0.6725 | 5.395
2024-12-09 | 23:43 | Data | 0 | 33.682 | 31.826 | 168.582 | 7.64 | 159.285 | 2246.93 | 25.89 | 48.165 | 6.42 | 1.292 | 4.125 | 8472.39 | 1.728 | 97.9 | 76.1 | 1460 | 24.08 | 5507.1 | 2710.8 | 2641.8 | 3910.7 | 1214.5 | 0.67634 | 5.418
2024-12-09 | 23:43 | Data | 0 | 33.486 | 31.812 | 168.536 | 7.63 | 159.33 | 2246.93 | 25.88 | 48.165 | 6.41 | 1.283 | 4.123 | 8481.44 | 1.6 | 97.9 | 76.3 | 1461 | 24.13 | 5512.9 | 2705.7 | 2659.3 | 3922.3 | 1214.5 | 0.67164 | 5.407
2024-12-09 | 23:43 | Data | 0 | 33.75 | 32.028 | 168.491 | 7.64 | 159.285 | 2244.22 | 25.86 | 48.075 | 6.41 | 1.279 | 4.105 | 8481.44 | 1.641 | 97.9 | 76.2 | 1459 | 24.08 | 5512.9 | 2693.9 | 2643.8 | 3903.1 | 1214.5 | 0.67255 | 5.384
2024-12-09 | 23:43 | Data | 0 | 33.426 | 32.001 | 168.491 | 7.63 | 159.195 | 2241.5 | 25.88 | 48.165 | 6.41 | 1.288 | 4.142 | 9123.59 | 1.627 | 97.9 | 76.3 | 1457 | 24.08 | 5930.3 | 2690.4 | 2628.2 | 3889.3 | 1214.5 | 0.67481 | 5.43
2024-12-09 | 23:43 | Data | 0 | 33.642 | 32.028 | 168.582 | 7.64 | 159.285 | 2241.5 | 25.88 | 48.255 | 6.41 | 1.289 | 4.143 | 8463.35 | 1.614 | 97.9 | 76.3 | 1457 | 24.08 | 5501.2 | 2702.1 | 2646.9 | 3909.3 | 1214.5 | 0.67348 | 5.432
2024-12-09 | 23:43 | Data | 0 | 33.696 | 31.826 | 168.401 | 7.64 | 159.195 | 2241.5 | 25.88 | 48.165 | 6.41 | 1.289 | 4.138 | 8458.83 | 1.681 | 97.9 | 76.3 | 1457 | 24.08 | 5498.2 | 2694.3 | 2652.8 | 3913 | 1214.5 | 0.67115 | 5.428
2024-12-09 | 23:43 | Data | 0 | 33.851 | 32.264 | 168.672 | 7.64 | 159.375 | 2238.79 | 25.88 | 48.165 | 6.41 | 1.277 | 4.147 | 8467.87 | 1.607 | 97.8 | 76.5 | 1456 | 24.08 | 5504.1 | 2691.4 | 2636 | 3896.1 | 1214.5 | 0.67331 | 5.424
2024-12-09 | 23:43 | Data | 0 | 33.642 | 31.853 | 168.536 | 7.63 | 159.195 | 2238.79 | 25.88 | 48.165 | 6.41 | 1.283 | 4.128 | 8422.65 | 1.614 | 97.9 | 76.3 | 1455 | 24.04 | 5474.7 | 2714.5 | 2641.1 | 3910.9 | 1214.5 | 0.67665 | 5.411
2024-12-09 | 23:43 | Data | 0 | 33.655 | 32.028 | 168.672 | 7.64 | 159.285 | 2236.08 | 25.86 | 48.165 | 6.41 | 1.283 | 4.123 | 8404.56 | 1.614 | 97.8 | 76.3 | 1453 | 24.08 | 5463 | 2717.4 | 2643.8 | 3917.3 | 1214.5 | 0.6768 | 5.408
2024-12-09 | 23:43 | Data | 0 | 33.642 | 32.453 | 168.672 | 7.64 | 159.375 | 2234.27 | 25.88 | 48.165 | 6.41 | 1.282 | 4.126 | 8418.13 | 1.526 | 97.8 | 76.3 | 1453 | 24.08 | 5471.8 | 2716.1 | 2632.6 | 3909.6 | 1214.5 | 0.67637 | 5.409
2024-12-09 | 23:43 | Data | 0 | 34.067 | 32.089 | 168.627 | 7.64 | 159.33 | 2236.08 | 25.88 | 48.075 | 6.41 | 1.291 | 4.129 | 8449.78 | 1.587 | 97.9 | 76.2 | 1453 | 24.04 | 5492.4 | 2710.1 | 2642.4 | 3913.5 | 1214.5 | 0.67408 | 5.419
2024-12-09 | 23:43 | Data | 0 | 33.486 | 31.859 | 168.672 | 7.63 | 159.33 | 2235.18 | 25.88 | 48.165 | 6.41 | 1.291 | 4.127 | 8449.78 | 1.573 | 97.8 | 76.2 | 1453 | 24.08 | 5492.4 | 2705.7 | 2642.2 | 3910.1 | 1214.5 | 0.67388 | 5.419
2024-12-09 | 23:44 | Data | 0 | 33.615 | 32.028 | 168.717 | 7.64 | 159.33 | 2236.08 | 25.88 | 48.255 | 6.41 | 1.282 | 4.128 | 8467.87 | 1.614 | 97.8 | 76.3 | 1453 | 24.13 | 5504.1 | 2695.2 | 2671 | 3923.7 | 1214.5 | 0.66913 | 5.41
2024-12-09 | 23:44 | Data | 0 | 33.729 | 32.042 | 168.582 | 7.63 | 159.33 | 2235.18 | 25.88 | 48.165 | 6.41 | 1.278 | 4.115 | 8454.3 | 1.715 | 97.8 | 76.3 | 1453 | 24.08 | 5495.3 | 2700.1 | 2639.1 | 3903.1 | 1214.5 | 0.67455 | 5.392
2024-12-09 | 23:44 | Data | 0 | 33.972 | 32.048 | 168.672 | 7.64 | 159.375 | 2236.08 | 25.88 | 48.165 | 6.41 | 1.293 | 4.127 | 8463.35 | 1.661 | 97.8 | 76.1 | 1453 | 24.08 | 5501.2 | 2709.3 | 2649.5 | 3916.6 | 1214.6 | 0.6735 | 5.42
2024-12-09 | 23:44 | Data | 0 | 33.419 | 32.021 | 168.627 | 7.63 | 159.285 | 2235.18 | 25.86 | 48.255 | 6.41 | 1.29 | 4.124 | 8467.87 | 1.6 | 97.8 | 76.2 | 1453 | 24.08 | 5504.1 | 2696.6 | 2629.6 | 3895.7 | 1214.6 | 0.67509 | 5.415
2024-12-09 | 23:44 | Data | 0 | 33.432 | 31.853 | 168.672 | 7.64 | 159.33 | 2235.18 | 25.88 | 48.165 | 6.41 | 1.278 | 4.105 | 8472.39 | 1.411 | 97.8 | 76.3 | 1453 | 24.08 | 5507.1 | 2699.5 | 2627.7 | 3894.9 | 1214.6 | 0.67483 | 5.383
2024-12-09 | 23:44 | Data | 0 | 33.642 | 31.913 | 168.627 | 7.64 | 159.24 | 2235.18 | 25.86 | 48.165 | 6.41 | 1.291 | 4.138 | 8467.87 | 1.728 | 97.8 | 76.2 | 1453 | 24.04 | 5504.1 | 2704.4 | 2629.5 | 3902 | 1214.6 | 0.67664 | 5.43
2024-12-09 | 23:44 | Data | 0 | 33.696 | 32.028 | 168.582 | 7.63 | 159.285 | 2231.56 | 25.88 | 48.436 | 6.4 | 1.278 | 4.14 | 8476.91 | 1.62 | 97.8 | 76.4 | 1451 | 24.26 | 5510 | 2712.3 | 2641 | 3911.6 | 1214.6 | 0.676 | 5.417
2024-12-09 | 23:44 | Data | 0 | 33.419 | 32.015 | 168.536 | 7.63 | 159.195 | 2235.18 | 25.88 | 48.436 | 6.41 | 1.278 | 4.149 | 8449.78 | 1.587 | 97.8 | 76.5 | 1453 | 24.22 | 5492.4 | 2695.9 | 2663.3 | 3923.9 | 1214.6 | 0.66934 | 5.427
2024-12-09 | 23:44 | Data | 0 | 33.804 | 32.028 | 168.582 | 7.63 | 159.285 | 2236.08 | 25.88 | 48.346 | 6.41 | 1.286 | 4.102 | 8445.26 | 1.836 | 97.8 | 76.1 | 1453 | 24.22 | 5489.4 | 2694.7 | 2628.1 | 3894.1 | 1214.6 | 0.6751 | 5.389
2024-12-09 | 23:44 | Data | 0 | 34.094 | 31.934 | 168.853 | 7.63 | 159.466 | 2235.18 | 25.88 | 48.436 | 6.41 | 1.282 | 4.106 | 8445.26 | 1.647 | 97.8 | 76.2 | 1453 | 24.22 | 5489.4 | 2706.7 | 2635.4 | 3907.1 | 1214.6 | 0.67496 | 5.389
2024-12-09 | 23:44 | Data | 0 | 33.615 | 32.035 | 168.536 | 7.64 | 159.285 | 2233.37 | 25.88 | 47.894 | 6.41 | 1.288 | 4.126 | 8454.3 | 1.587 | 97.9 | 76.2 | 1451 | 23.99 | 5495.3 | 2692.9 | 2633.5 | 3898.8 | 1214.6 | 0.67289 | 5.414
2024-12-09 | 23:44 | Data | 0 | 33.642 | 31.826 | 168.627 | 7.64 | 159.24 | 2235.18 | 25.88 | 48.436 | 6.41 | 1.288 | 4.12 | 8481.44 | 1.614 | 97.8 | 76.2 | 1453 | 24.22 | 5512.9 | 2699.4 | 2648.4 | 3910.5 | 1214.6 | 0.67349 | 5.409
2024-12-09 | 23:44 | Data | 0 | 33.642 | 31.832 | 168.627 | 7.63 | 159.24 | 2239.7 | 25.89 | 48.075 | 6.41 | 1.295 | 4.114 | 8481.44 | 1.701 | 97.8 | 76.1 | 1455 | 24.08 | 5512.9 | 2721.7 | 2645.3 | 3923.3 | 1214.6 | 0.67726 | 5.408
2024-12-09 | 23:44 | Data | 0 | 33.648 | 32.001 | 168.582 | 7.64 | 159.33 | 2242.41 | 25.85 | 48.346 | 6.41 | 1.286 | 4.12 | 8481.44 | 1.641 | 97.8 | 76.2 | 1458 | 24.17 | 5512.9 | 2693.3 | 2657.3 | 3911.6 | 1214.6 | 0.6706 | 5.406
2024-12-09 | 23:44 | Data | 0 | 33.682 | 32.035 | 168.627 | 7.63 | 159.33 | 2242.41 | 25.89 | 48.436 | 6.41 | 1.292 | 4.137 | 8467.87 | 1.62 | 97.8 | 76.2 | 1457 | 24.22 | 5504.1 | 2692.4 | 2660.2 | 3911.2 | 1214.6 | 0.67059 | 5.428
2024-12-09 | 23:44 | Data | 0 | 33.756 | 32.055 | 168.672 | 7.64 | 159.421 | 2246.93 | 25.88 | 48.346 | 6.41 | 1.287 | 4.132 | 8472.39 | 1.58 | 97.8 | 76.2 | 1461 | 24.17 | 5507.1 | 2712.2 | 2656.8 | 3925.1 | 1214.6 | 0.67226 | 5.419
2024-12-09 | 23:44 | Data | 0 | 33.601 | 32.116 | 168.491 | 7.64 | 159.285 | 2244.22 | 25.89 | 48.436 | 6.41 | 1.277 | 4.115 | 8458.83 | 1.701 | 97.8 | 76.3 | 1458 | 24.22 | 5498.2 | 2704.7 | 2655.9 | 3921.9 | 1214.6 | 0.67134 | 5.391
2024-12-09 | 23:44 | Data | 0 | 33.844 | 32.258 | 168.672 | 7.63 | 159.375 | 2246.93 | 25.89 | 48.346 | 6.41 | 1.282 | 4.129 | 8472.39 | 1.627 | 97.8 | 76.3 | 1461 | 24.17 | 5507.1 | 2707.8 | 2663.4 | 3924.6 | 1214.6 | 0.67357 | 5.41
2024-12-09 | 23:45 | Data | 0 | 33.527 | 32.028 | 168.627 | 7.64 | 159.33 | 2246.93 | 25.86 | 48.165 | 6.41 | 1.285 | 4.141 | 8472.39 | 1.445 | 97.9 | 76.3 | 1460 | 24.08 | 5507.1 | 2701 | 2661.5 | 3918.4 | 1214.6 | 0.67198 | 5.426
2024-12-09 | 23:45 | Data | 0 | 33.419 | 31.94 | 168.491 | 7.63 | 159.24 | 2244.22 | 25.86 | 48.255 | 6.41 | 1.295 | 4.143 | 8409.08 | 1.519 | 97.9 | 76.2 | 1459 | 24.08 | 5465.9 | 2700.2 | 2637.6 | 3901.1 | 1214.6 | 0.67414 | 5.439
2024-12-09 | 23:45 | Data | 0 | 33.642 | 32.028 | 168.582 | 7.64 | 159.33 | 2244.22 | 25.88 | 48.165 | 6.41 | 1.291 | 4.139 | 8431.69 | 1.614 | 97.9 | 76.2 | 1459 | 24.08 | 5480.6 | 2697.4 | 2622.6 | 3891.3 | 1214.6 | 0.6741 | 5.43
2024-12-09 | 23:45 | Data | 0 | 33.817 | 32.096 | 168.582 | 7.64 | 159.33 | 2240.6 | 25.88 | 48.165 | 6.41 | 1.278 | 4.121 | 8427.17 | 1.701 | 97.8 | 76.3 | 1457 | 24.13 | 5477.7 | 2714 | 2639.2 | 3909.5 | 1214.6 | 0.67671 | 5.4
2024-12-09 | 23:45 | Data | 0 | 33.75 | 32.204 | 168.627 | 7.64 | 159.33 | 2246.02 | 25.89 | 48.165 | 6.41 | 1.282 | 4.122 | 8418.13 | 1.506 | 97.9 | 76.3 | 1461 | 24.08 | 5471.8 | 2725.7 | 2646.8 | 3925.5 | 1214.6 | 0.67805 | 5.403
2024-12-09 | 23:45 | Data | 0 | 33.702 | 32.028 | 168.717 | 7.64 | 159.33 | 2241.5 | 25.89 | 48.165 | 6.41 | 1.282 | 4.111 | 8454.3 | 1.62 | 97.9 | 76.2 | 1458 | 24.08 | 5495.3 | 2710.9 | 2631.6 | 3908 | 1214.6 | 0.67763 | 5.392
2024-12-09 | 23:45 | Data | 0 | 33.844 | 32.258 | 168.762 | 7.64 | 159.466 | 2244.22 | 25.88 | 48.165 | 6.41 | 1.285 | 4.086 | 8454.3 | 1.627 | 97.9 | 76.1 | 1458 | 24.08 | 5495.3 | 2700.5 | 2640.1 | 3903.4 | 1214.6 | 0.67544 | 5.371
2024-12-09 | 23:45 | Data | 0 | 33.817 | 32.264 | 168.536 | 7.63 | 159.285 | 2241.5 | 25.85 | 48.165 | 6.41 | 1.282 | 4.115 | 8454.3 | 1.6 | 97.9 | 76.2 | 1457 | 24.08 | 5495.3 | 2704.7 | 2641.2 | 3907.3 | 1214.6 | 0.67477 | 5.398
2024-12-09 | 23:45 | Data | 0 | 33.642 | 31.934 | 168.582 | 7.64 | 159.24 | 2242.41 | 25.89 | 48.165 | 6.41 | 1.284 | 4.142 | 8463.35 | 1.809 | 97.9 | 76.3 | 1458 | 24.04 | 5501.2 | 2704.9 | 2622.3 | 3893.2 | 1214.6 | 0.67764 | 5.425
2024-12-09 | 23:45 | Data | 0 | 33.642 | 32.406 | 168.672 | 7.63 | 159.375 | 2242.41 | 25.88 | 48.165 | 6.41 | 1.291 | 4.124 | 8499.53 | 1.438 | 97.9 | 76.2 | 1457 | 24.08 | 5524.7 | 2699.1 | 2631 | 3894.7 | 1214.6 | 0.67632 | 5.413
2024-12-09 | 23:45 | Data | 0 | 33.81 | 32.204 | 168.627 | 7.63 | 159.285 | 2241.5 | 25.85 | 48.165 | 6.41 | 1.286 | 4.142 | 8499.53 | 1.668 | 97.9 | 76.3 | 1457 | 24.08 | 5524.7 | 2701.1 | 2639.9 | 3904.7 | 1214.6 | 0.67481 | 5.428
2024-12-09 | 23:45 | Data | 0 | 33.419 | 32.028 | 168.582 | 7.63 | 159.33 | 2241.5 | 25.88 | 48.165 | 6.41 | 1.287 | 4.124 | 8495 | 1.769 | 97.9 | 76.2 | 1458 | 24.08 | 5521.8 | 2701.2 | 2648.7 | 3907.9 | 1214.6 | 0.67501 | 5.41
2024-12-09 | 23:45 | Data | 0 | 33.534 | 32.028 | 168.672 | 7.63 | 159.33 | 2246.93 | 25.88 | 48.165 | 6.41 | 1.286 | 4.157 | 8513.09 | 1.458 | 97.9 | 76.4 | 1461 | 24.08 | 5533.5 | 2692.7 | 2629.2 | 3898.2 | 1214.6 | 0.67309 | 5.442
2024-12-09 | 23:45 | Data | 0 | 33.918 | 32.035 | 168.582 | 7.64 | 159.421 | 2246.93 | 25.88 | 48.165 | 6.41 | 1.285 | 4.137 | 8495 | 1.688 | 97.9 | 76.3 | 1461 | 24.13 | 5521.8 | 2702.1 | 2637.8 | 3902 | 1214.6 | 0.67477 | 5.422
2024-12-09 | 23:45 | Data | 0 | 33.817 | 32.264 | 168.627 | 7.63 | 159.285 | 2245.12 | 25.89 | 48.165 | 6.4 | 1.286 | 4.146 | 8495 | 1.755 | 97.9 | 76.3 | 1459 | 24.08 | 5521.8 | 2709 | 2646 | 3915.3 | 1214.6 | 0.67423 | 5.432
2024-12-09 | 23:45 | Data | 0 | 33.642 | 32.028 | 168.491 | 7.63 | 159.285 | 2246.02 | 25.85 | 48.165 | 6.41 | 1.288 | 4.144 | 8495 | 1.614 | 97.9 | 76.3 | 1461 | 24.13 | 5521.8 | 2732.4 | 2649.5 | 3921.3 | 1214.6 | 0.67745 | 5.432
2024-12-09 | 23:45 | Data | 0 | 33.669 | 32.028 | 168.582 | 7.63 | 159.33 | 2248.73 | 25.88 | 48.165 | 6.41 | 1.294 | 4.121 | 8495 | 1.62 | 97.9 | 76.1 | 1462 | 24.08 | 5521.8 | 2700.3 | 2638 | 3906 | 1214.6 | 0.67401 | 5.415
2024-12-09 | 23:45 | Data | 0 | 33.756 | 32.028 | 168.627 | 7.63 | 159.375 | 2246.93 | 25.85 | 48.165 | 6.41 | 1.296 | 4.116 | 8481.44 | 1.634 | 97.9 | 76.1 | 1461 | 24.08 | 5512.9 | 2713.5 | 2619.9 | 3897.3 | 1214.6 | 0.67905 | 5.411
2024-12-09 | 23:46 | Data | 0 | 33.912 | 32.089 | 168.672 | 7.63 | 159.421 | 2246.93 | 25.89 | 48.165 | 6.41 | 1.291 | 4.134 | 8485.96 | 1.607 | 97.9 | 76.2 | 1461 | 24.08 | 5515.9 | 2693.2 | 2621.7 | 3886.7 | 1214.6 | 0.67515 | 5.425
2024-12-09 | 23:46 | Data | 0 | 33.696 | 31.92 | 168.491 | 7.63 | 159.24 | 2246.93 | 25.86 | 48.165 | 6.41 | 1.301 | 4.15 | 8481.44 | 1.627 | 97.9 | 76.1 | 1460 | 24.04 | 5512.9 | 2711.3 | 2631.7 | 3906.5 | 1214.6 | 0.67867 | 5.449
2024-12-09 | 23:46 | Data | 0 | 33.81 | 32.143 | 168.672 | 7.64 | 159.33 | 2246.93 | 25.89 | 48.165 | 6.41 | 1.291 | 4.137 | 8476.91 | 1.654 | 97.9 | 76.2 | 1461 | 24.08 | 5510 | 2698.4 | 2654.4 | 3912.8 | 1214.6 | 0.67364 | 5.427
2024-12-09 | 23:46 | Data | 0 | 33.817 | 32.305 | 168.672 | 7.63 | 159.421 | 2252.35 | 25.88 | 48.165 | 6.41 | 1.294 | 4.152 | 8481.44 | 1.695 | 97.9 | 76.2 | 1465 | 24.08 | 5512.9 | 2699.8 | 2628.4 | 3896.7 | 1214.6 | 0.67641 | 5.446
2024-12-09 | 23:46 | Data | 0 | 33.642 | 32.028 | 168.627 | 7.63 | 159.24 | 2252.35 | 25.88 | 48.165 | 6.41 | 1.282 | 4.133 | 8499.53 | 1.614 | 97.9 | 76.3 | 1465 | 24.08 | 5524.7 | 2688.9 | 2619.4 | 3882.2 | 1214.6 | 0.67731 | 5.414
2024-12-09 | 23:46 | Data | 0 | 33.925 | 32.048 | 168.582 | 7.63 | 159.421 | 2248.73 | 25.89 | 48.165 | 6.41 | 1.282 | 4.127 | 8485.96 | 1.627 | 97.9 | 76.3 | 1462 | 24.08 | 5515.9 | 2705.9 | 2638.1 | 3912 | 1214.7 | 0.67503 | 5.41
2024-12-09 | 23:46 | Data | 0 | 33.696 | 32.028 | 168.536 | 7.64 | 159.285 | 2249.64 | 25.86 | 48.165 | 6.41 | 1.29 | 4.127 | 8472.39 | 1.634 | 97.9 | 76.2 | 1462 | 24.08 | 5507.1 | 2706.5 | 2653 | 3917.2 | 1214.7 | 0.67465 | 5.418
2024-12-09 | 23:46 | Data | 0 | 33.594 | 32.028 | 168.582 | 7.64 | 159.33 | 2248.73 | 25.86 | 48.165 | 6.41 | 1.291 | 4.121 | 8472.39 | 1.6 | 97.9 | 76.1 | 1462 | 24.08 | 5507.1 | 2704 | 2661.6 | 3924.4 | 1214.7 | 0.67154 | 5.412
2024-12-09 | 23:46 | Data | 0 | 33.642 | 32.028 | 168.627 | 7.64 | 159.375 | 2249.64 | 25.86 | 48.075 | 6.41 | 1.291 | 4.107 | 8472.39 | 1.452 | 97.9 | 76.1 | 1462 | 24.04 | 5507.1 | 2705.2 | 2661 | 3923.8 | 1214.7 | 0.6717 | 5.399
2024-12-09 | 23:46 | Data | 0 | 33.756 | 32.028 | 168.627 | 7.64 | 159.33 | 2248.73 | 25.85 | 48.165 | 6.41 | 1.291 | 4.116 | 8454.3 | 1.816 | 97.9 | 76.1 | 1462 | 24.13 | 5495.3 | 2700.9 | 2653.3 | 3911.8 | 1214.7 | 0.67517 | 5.406
2024-12-09 | 23:46 | Data | 0 | 33.871 | 32.123 | 168.627 | 7.64 | 159.33 | 2245.12 | 25.89 | 48.165 | 6.41 | 1.288 | 4.138 | 8467.87 | 1.479 | 97.8 | 76.3 | 1458 | 24.08 | 5504.1 | 2698 | 2638.1 | 3903.4 | 1214.7 | 0.6738 | 5.425
2024-12-09 | 23:46 | Data | 0 | 33.682 | 32.028 | 168.627 | 7.63 | 159.33 | 2247.83 | 25.88 | 48.165 | 6.41 | 1.29 | 4.153 | 8495 | 1.627 | 97.9 | 76.3 | 1461 | 24.08 | 5521.8 | 2707.9 | 2639.9 | 3910.7 | 1214.7 | 0.67575 | 5.443
2024-12-09 | 23:46 | Data | 0 | 33.615 | 32.028 | 168.582 | 7.64 | 159.33 | 2246.93 | 25.86 | 48.165 | 6.41 | 1.276 | 4.131 | 8499.53 | 1.607 | 97.9 | 76.4 | 1460 | 24.08 | 5524.7 | 2713.4 | 2639.7 | 3907.8 | 1214.7 | 0.6775 | 5.407
2024-12-09 | 23:46 | Data | 0 | 33.925 | 32.109 | 168.491 | 7.63 | 159.285 | 2244.22 | 25.86 | 48.165 | 6.41 | 1.283 | 4.122 | 8490.48 | 1.782 | 97.9 | 76.3 | 1459 | 24.08 | 5518.8 | 2710.9 | 2617.4 | 3896.6 | 1214.7 | 0.67802 | 5.405
2024-12-09 | 23:46 | Data | 0 | 33.473 | 31.974 | 168.491 | 7.64 | 159.285 | 2240.6 | 25.88 | 48.255 | 6.41 | 1.294 | 4.127 | 8481.44 | 1.62 | 97.9 | 76.1 | 1456 | 24.04 | 5512.9 | 2694.4 | 2643.3 | 3911.5 | 1214.7 | 0.67495 | 5.421
2024-12-09 | 23:46 | Data | 0 | 33.642 | 32.028 | 168.536 | 7.64 | 159.285 | 2242.41 | 25.88 | 48.165 | 6.41 | 1.299 | 4.128 | 8467.87 | 1.614 | 97.9 | 76.1 | 1457 | 24.08 | 5504.1 | 2700.1 | 2663.5 | 3920.2 | 1214.7 | 0.67133 | 5.427
2024-12-09 | 23:46 | Data | 0 | 33.419 | 32.15 | 168.672 | 7.64 | 159.285 | 2242.41 | 25.88 | 48.255 | 6.41 | 1.285 | 4.14 | 8458.83 | 1.499 | 97.9 | 76.3 | 1457 | 24.13 | 5498.2 | 2689.1 | 2649.7 | 3901.7 | 1214.7 | 0.67182 | 5.426
2024-12-09 | 23:46 | Data | 0 | 33.817 | 32.264 | 168.717 | 7.63 | 159.375 | 2242.41 | 25.89 | 48.165 | 6.41 | 1.291 | 4.13 | 8445.26 | 1.587 | 97.9 | 76.2 | 1458 | 24.08 | 5489.4 | 2699.5 | 2665.9 | 3918.7 | 1214.7 | 0.67219 | 5.422
2024-12-09 | 23:47 | Data | 0 | 33.77 | 32.082 | 168.627 | 7.64 | 159.33 | 2368.04 | 25.88 | 48.075 | 6.41 | 1.283 | 4.13 | 8481.44 | 1.587 | 98 | 76.3 | 1539 | 24.08 | 5512.9 | 2712.8 | 2652.2 | 3919.3 | 1214.7 | 0.67447 | 5.413
2024-12-09 | 23:47 | Data | 0 | 33.642 | 32.021 | 168.536 | 7.63 | 159.285 | 2246.93 | 25.89 | 48.075 | 6.41 | 1.278 | 4.137 | 8472.39 | 1.634 | 97.9 | 76.4 | 1460 | 24.08 | 5507.1 | 2697.6 | 2658.4 | 3915.7 | 1214.7 | 0.6712 | 5.415
2024-12-09 | 23:47 | Data | 0 | 33.648 | 32.075 | 168.717 | 7.64 | 159.375 | 2244.22 | 25.86 | 48.165 | 6.41 | 1.283 | 4.138 | 8481.44 | 1.438 | 97.9 | 76.3 | 1459 | 24.08 | 5512.9 | 2714.3 | 2649.5 | 3921.3 | 1214.7 | 0.67521 | 5.421
2024-12-09 | 23:47 | Data | 0 | 33.925 | 31.94 | 168.672 | 7.63 | 159.33 | 2244.22 | 25.85 | 48.165 | 6.41 | 1.288 | 4.138 | 8472.39 | 1.769 | 97.9 | 76.3 | 1459 | 24.04 | 5507.1 | 2697.3 | 2618.6 | 3886 | 1214.7 | 0.6773 | 5.426
2024-12-09 | 23:47 | Data | 0 | 33.885 | 32.048 | 168.717 | 7.64 | 159.375 | 2246.93 | 25.88 | 48.165 | 6.41 | 1.292 | 4.138 | 8490.48 | 1.809 | 97.9 | 76.2 | 1461 | 24.08 | 5518.8 | 2690.2 | 2646.1 | 3901.6 | 1214.7 | 0.67168 | 5.43
2024-12-09 | 23:47 | Data | 0 | 33.642 | 32.082 | 168.536 | 7.63 | 159.24 | 2238.79 | 25.89 | 48.165 | 6.41 | 1.291 | 4.112 | 8485.96 | 1.391 | 97.8 | 76.1 | 1455 | 24.08 | 5515.9 | 2691.3 | 2651.7 | 3904.6 | 1214.7 | 0.67215 | 5.402
2024-12-09 | 23:47 | Data | 0 | 33.871 | 32.028 | 168.627 | 7.64 | 159.375 | 2238.79 | 25.88 | 48.165 | 6.41 | 1.29 | 4.143 | 8458.83 | 1.634 | 97.8 | 76.2 | 1455 | 24.08 | 5498.2 | 2703.7 | 2641.4 | 3906 | 1214.7 | 0.67807 | 5.434
2024-12-09 | 23:47 | Data | 0 | 33.453 | 32.028 | 168.582 | 7.64 | 159.33 | 2238.79 | 25.89 | 48.075 | 6.41 | 1.289 | 4.119 | 8458.83 | 1.506 | 97.8 | 76.2 | 1456 | 24.08 | 5498.2 | 2716.4 | 2653.4 | 3917.9 | 1214.7 | 0.67549 | 5.409
2024-12-09 | 23:47 | Data | 0 | 33.426 | 32.129 | 168.491 | 7.63 | 159.24 | 2238.79 | 25.89 | 48.165 | 6.4 | 1.276 | 4.102 | 8463.35 | 1.573 | 97.8 | 76.3 | 1455 | 24.13 | 5501.2 | 2724.9 | 2654.7 | 3931.7 | 1214.7 | 0.67576 | 5.376
2024-12-09 | 23:47 | Data | 0 | 33.81 | 32.055 | 168.717 | 7.64 | 159.285 | 2238.79 | 25.89 | 47.714 | 6.41 | 1.278 | 4.13 | 8481.44 | 1.782 | 97.9 | 76.4 | 1455 | 23.86 | 5512.9 | 2712.9 | 2655.4 | 3913.1 | 1214.7 | 0.67437 | 5.408
2024-12-09 | 23:47 | Data | 0 | 33.615 | 32.143 | 168.627 | 7.64 | 159.285 | 2238.79 | 25.88 | 48.075 | 6.4 | 1.278 | 4.124 | 8481.44 | 1.695 | 97.9 | 76.3 | 1455 | 24.04 | 5512.9 | 2687.3 | 2640.4 | 3898.3 | 1214.7 | 0.6722 | 5.401
2024-12-09 | 23:47 | Data | 0 | 33.696 | 32.028 | 168.672 | 7.64 | 159.285 | 2238.79 | 25.88 | 48.165 | 6.41 | 1.283 | 4.131 | 8495 | 1.614 | 97.8 | 76.3 | 1453 | 24.08 | 5521.8 | 2710.8 | 2648.9 | 3916 | 1214.7 | 0.67534 | 5.414
2024-12-09 | 23:47 | Data | 0 | 33.696 | 32.15 | 168.627 | 7.64 | 159.375 | 2238.79 | 25.88 | 48.165 | 6.42 | 1.286 | 4.123 | 8476.91 | 1.722 | 97.8 | 76.2 | 1455 | 24.08 | 5510 | 2700.7 | 2641.7 | 3907.1 | 1214.7 | 0.6747 | 5.409
2024-12-09 | 23:47 | Data | 0 | 33.547 | 32.116 | 168.672 | 7.64 | 159.33 | 2235.18 | 25.88 | 48.165 | 6.41 | 1.28 | 4.12 | 8449.78 | 1.33 | 97.8 | 76.3 | 1453 | 24.08 | 5492.4 | 2704 | 2638 | 3904 | 1214.7 | 0.67712 | 5.401
2024-12-09 | 23:47 | Data | 0 | 33.642 | 32.008 | 168.672 | 7.63 | 159.33 | 2230.66 | 25.88 | 47.984 | 6.41 | 1.291 | 4.104 | 8427.17 | 1.634 | 97.8 | 76.1 | 1449 | 23.99 | 5477.7 | 2698.4 | 2647.9 | 3906.9 | 1214.7 | 0.67197 | 5.395
2024-12-09 | 23:47 | Data | 0 | 33.864 | 32.028 | 168.627 | 7.64 | 159.33 | 2233.37 | 25.85 | 48.075 | 6.41 | 1.279 | 4.102 | 8431.69 | 1.634 | 97.8 | 76.2 | 1452 | 24.08 | 5480.6 | 2707.8 | 2652.1 | 3912.5 | 1214.7 | 0.67594 | 5.381
2024-12-09 | 23:47 | Data | 0 | 34.134 | 32.264 | 168.762 | 7.63 | 159.375 | 2233.37 | 25.88 | 48.165 | 6.41 | 1.282 | 4.109 | 8409.08 | 1.614 | 97.8 | 76.2 | 1451 | 24.08 | 5465.9 | 2696.4 | 2630.8 | 3896.3 | 1214.7 | 0.67398 | 5.392
2024-12-09 | 23:48 | Data | 0 | 33.655 | 32.237 | 168.672 | 7.63 | 159.375 | 2232.47 | 25.88 | 48.165 | 6.41 | 1.289 | 4.138 | 8467.87 | 1.58 | 97.8 | 76.3 | 1451 | 24.08 | 5504.1 | 2698.8 | 2624.3 | 3891.8 | 1214.7 | 0.67573 | 5.426
2024-12-09 | 23:48 | Data | 0 | 34.155 | 32.325 | 168.808 | 7.64 | 159.421 | 2136.66 | 25.88 | 47.984 | 6.41 | 1.287 | 4.129 | 8463.35 | 1.634 | 97.8 | 76.2 | 1389 | 23.99 | 5501.2 | 2703.5 | 2644.3 | 3911.9 | 1214.7 | 0.67294 | 5.415
2024-12-09 | 23:48 | Data | 0 | 33.655 | 32.028 | 168.582 | 7.64 | 159.33 | 2241.5 | 25.89 | 48.255 | 6.41 | 1.292 | 4.071 | 8472.39 | 1.411 | 97.9 | 75.9 | 1456 | 24.04 | 5507.1 | 1608.7 | 2059.8 | 2640 | 1214.7 | 0.60964 | 5.364
2024-12-09 | 23:48 | Data | 0 | 34.033 | 32.264 | 168.762 | 7.64 | 159.375 | 2241.5 | 25.89 | 47.804 | 6.41 | 1.283 | 4.123 | 8657.8 | 1.62 | 97.9 | 76.3 | 1457 | 23.9 | 5627.6 | 1624 | 2068.9 | 2643.5 | 1214.7 | 0.61191 | 5.405
2024-12-09 | 23:48 | Data | 0 | 33.642 | 32.028 | 168.536 | 7.63 | 159.33 | 2241.5 | 25.86 | 47.894 | 6.41 | 1.279 | 4.138 | 8657.8 | 1.728 | 97.9 | 76.4 | 1456 | 23.95 | 5627.6 | 1620.1 | 2051.3 | 2627.6 | 1214.7 | 0.61358 | 5.415
2024-12-09 | 23:48 | Data | 0 | 33.77 | 32.028 | 168.808 | 7.64 | 159.466 | 2242.41 | 25.89 | 47.894 | 6.41 | 1.291 | 4.146 | 8662.33 | 1.506 | 97.9 | 76.3 | 1457 | 23.95 | 5630.5 | 1629.4 | 2080.4 | 2657.1 | 1214.7 | 0.61269 | 5.437
2024-12-09 | 23:48 | Data | 0 | 33.858 | 32.042 | 168.627 | 7.63 | 159.33 | 2244.22 | 25.86 | 47.894 | 6.41 | 1.294 | 4.163 | 8653.28 | 1.701 | 97.9 | 76.3 | 1459 | 23.95 | 5624.6 | 1623 | 2047.8 | 2629.5 | 1214.7 | 0.61378 | 5.457
2024-12-09 | 23:48 | Data | 0 | 33.844 | 32.366 | 167.903 | 7.64 | 158.652 | 2241.5 | 25.88 | 47.894 | 6.41 | 1.291 | 4.147 | 8454.3 | 1.735 | 97.9 | 76.3 | 1457 | 23.9 | 5495.3 | 1609.7 | 2029.9 | 2603.7 | 1214.7 | 0.61522 | 5.437
2024-12-09 | 23:48 | Data | 0 | 33.959 | 32.372 | 167.993 | 7.63 | 158.652 | 2241.5 | 25.89 | 47.804 | 6.41 | 1.279 | 4.115 | 8458.83 | 1.715 | 97.9 | 76.3 | 1457 | 23.95 | 5498.2 | 1607.9 | 2040.7 | 2611.2 | 1214.7 | 0.61369 | 5.394
2024-12-09 | 23:48 | Data | 0 | 33.756 | 32.042 | 167.903 | 7.63 | 158.562 | 2241.5 | 25.86 | 47.984 | 6.42 | 1.285 | 4.111 | 8467.87 | 1.634 | 97.9 | 76.2 | 1457 | 23.95 | 5504.1 | 1622.2 | 2070 | 2643 | 1214.7 | 0.61203 | 5.397
2024-12-09 | 23:48 | Data | 0 | 33.648 | 32.258 | 167.767 | 7.63 | 158.607 | 2238.79 | 25.86 | 48.165 | 6.4 | 1.279 | 4.113 | 8445.26 | 1.56 | 97.9 | 76.3 | 1455 | 24.04 | 5489.4 | 1613.8 | 2062.3 | 2631.9 | 1214.7 | 0.61044 | 5.391
2024-12-09 | 23:48 | Data | 0 | 34.074 | 32.143 | 167.858 | 7.63 | 158.652 | 2239.7 | 25.85 | 48.165 | 6.41 | 1.282 | 4.116 | 8418.13 | 1.708 | 97.8 | 76.2 | 1456 | 24.08 | 5471.8 | 1614 | 2098.2 | 2661.1 | 1214.7 | 0.60339 | 5.399
2024-12-09 | 23:48 | Data | 0 | 33.817 | 32.345 | 167.993 | 7.64 | 158.607 | 2239.7 | 25.86 | 48.165 | 6.41 | 1.275 | 4.119 | 8427.17 | 1.553 | 97.8 | 76.4 | 1455 | 24.08 | 5477.7 | 1613.7 | 2092.9 | 2657 | 1214.8 | 0.60495 | 5.394
2024-12-09 | 23:48 | Data | 0 | 33.696 | 32.237 | 167.858 | 7.64 | 158.652 | 2235.18 | 25.85 | 48.165 | 6.41 | 1.279 | 4.115 | 8418.13 | 1.634 | 97.8 | 76.3 | 1453 | 24.04 | 5471.8 | 1602 | 2078.6 | 2637.2 | 1214.8 | 0.60562 | 5.392
2024-12-09 | 23:48 | Data | 0 | 33.534 | 32.028 | 167.813 | 7.64 | 158.562 | 2241.5 | 25.86 | 48.165 | 6.41 | 1.286 | 4.109 | 8449.78 | 1.6 | 97.9 | 76.2 | 1456 | 24.08 | 5492.4 | 1609.1 | 2056.4 | 2623.7 | 1214.8 | 0.61085 | 5.395
2024-12-09 | 23:48 | Data | 0 | 34.047 | 32.372 | 167.903 | 7.63 | 158.698 | 2245.12 | 25.86 | 48.075 | 6.41 | 1.29 | 4.09 | 8440.74 | 1.6 | 97.9 | 76 | 1459 | 24.04 | 5486.5 | 1602 | 2050.9 | 2616.5 | 1214.8 | 0.6096 | 5.379
2024-12-09 | 23:49 | Data | 0 | 33.783 | 32.035 | 167.858 | 7.63 | 158.607 | 2241.5 | 25.86 | 48.165 | 6.42 | 1.292 | 4.113 | 8445.26 | 1.62 | 97.9 | 76.1 | 1457 | 24.08 | 5489.4 | 1600.5 | 2064.7 | 2626.9 | 1214.8 | 0.60681 | 5.406
2024-12-09 | 23:49 | Data | 0 | 33.756 | 32.366 | 167.767 | 7.64 | 158.652 | 2245.12 | 25.85 | 48.075 | 6.41 | 1.28 | 4.128 | 8472.39 | 1.56 | 97.9 | 76.3 | 1459 | 24.08 | 5507.1 | 1603.6 | 2040.6 | 2610.1 | 1214.8 | 0.61273 | 5.408
2024-12-09 | 23:49 | Data | 0 | 33.696 | 32.042 | 167.858 | 7.63 | 158.607 | 2244.22 | 25.84 | 48.255 | 6.41 | 1.287 | 4.121 | 8458.83 | 1.593 | 97.9 | 76.2 | 1459 | 24.08 | 5498.2 | 1620.8 | 2054.2 | 2629.8 | 1214.8 | 0.6141 | 5.409
2024-12-09 | 23:49 | Data | 0 | 34.148 | 32.177 | 167.993 | 7.63 | 158.743 | 2241.5 | 25.86 | 48.075 | 6.41 | 1.288 | 4.108 | 8445.26 | 1.634 | 97.9 | 76.1 | 1457 | 24.08 | 5489.4 | 1614.7 | 2040.1 | 2618.2 | 1214.8 | 0.61361 | 5.395
2024-12-09 | 23:49 | Data | 0 | 33.831 | 32.366 | 167.813 | 7.64 | 158.652 | 2238.79 | 25.85 | 48.165 | 6.41 | 1.279 | 4.073 | 8445.26 | 1.627 | 97.8 | 76.1 | 1455 | 24.08 | 5489.4 | 1594.7 | 2057.9 | 2594 | 1214.8 | 0.60629 | 5.353
2024-12-09 | 23:49 | Data | 0 | 33.925 | 32.264 | 167.858 | 7.63 | 158.607 | 2238.79 | 25.86 | 48.075 | 6.41 | 1.282 | 4.096 | 8445.26 | 1.634 | 97.8 | 76.2 | 1455 | 24.08 | 5489.4 | 1608.3 | 2044.1 | 2615.1 | 1214.8 | 0.61175 | 5.376
2024-12-09 | 23:49 | Data | 0 | 33.878 | 32.15 | 167.903 | 7.64 | 158.698 | 2238.79 | 25.85 | 48.165 | 6.42 | 1.275 | 4.107 | 8449.78 | 1.607 | 97.8 | 76.3 | 1455 | 24.08 | 5492.4 | 1607.6 | 2083.6 | 2641.4 | 1214.8 | 0.60474 | 5.382
2024-12-09 | 23:49 | Data | 0 | 33.756 | 32.089 | 167.948 | 7.64 | 158.698 | 2238.79 | 25.85 | 48.075 | 6.41 | 1.291 | 4.087 | 8454.3 | 1.438 | 97.9 | 76 | 1455 | 24.04 | 5495.3 | 1614.5 | 2114.4 | 2650.6 | 1214.8 | 0.60087 | 5.378
2024-12-09 | 23:49 | Data | 0 | 33.419 | 32.015 | 167.813 | 7.63 | 158.517 | 2238.79 | 25.84 | 48.255 | 6.41 | 1.29 | 4.104 | 8431.69 | 1.6 | 97.8 | 76.1 | 1455 | 24.08 | 5480.6 | 1629.5 | 2099.7 | 2669.6 | 1214.8 | 0.60778 | 5.392
2024-12-09 | 23:49 | Data | 0 | 33.864 | 32.264 | 167.813 | 7.63 | 158.607 | 2239.7 | 25.84 | 48.165 | 6.41 | 1.283 | 4.125 | 8431.69 | 1.607 | 97.8 | 76.3 | 1456 | 24.08 | 5480.6 | 1623.1 | 2090.4 | 2659.5 | 1214.8 | 0.61211 | 5.408
2024-12-09 | 23:49 | Data | 0 | 33.642 | 32.15 | 167.813 | 7.63 | 158.607 | 2238.79 | 25.85 | 48.165 | 6.41 | 1.278 | 4.128 | 8431.69 | 1.614 | 97.9 | 76.4 | 1455 | 24.08 | 5480.6 | 1613.1 | 2052 | 2623.3 | 1214.8 | 0.61283 | 5.407
2024-12-09 | 23:49 | Data | 0 | 33.756 | 32.264 | 167.903 | 7.64 | 158.607 | 2240.6 | 25.84 | 48.165 | 6.41 | 1.293 | 4.123 | 8427.17 | 1.391 | 97.9 | 76.1 | 1457 | 24.08 | 5477.7 | 1609.4 | 2059.1 | 2627.7 | 1214.8 | 0.60977 | 5.416
2024-12-09 | 23:49 | Data | 0 | 33.75 | 32.231 | 167.858 | 7.63 | 158.562 | 2244.22 | 25.84 | 48.165 | 6.41 | 1.294 | 4.087 | 8427.17 | 1.627 | 97.8 | 75.9 | 1459 | 24.08 | 5477.7 | 1611.4 | 2044.1 | 2616 | 1214.8 | 0.61316 | 5.382
2024-12-09 | 23:49 | Data | 0 | 33.486 | 32.231 | 167.767 | 7.64 | 158.607 | 2249.64 | 25.84 | 48.255 | 6.41 | 1.296 | 4.096 | 8431.69 | 1.337 | 97.9 | 76 | 1463 | 24.08 | 5480.6 | 1595.3 | 2045.1 | 2607.5 | 1214.8 | 0.60948 | 5.393
2024-12-09 | 23:49 | Data | 0 | 34.047 | 32.264 | 167.903 | 7.64 | 158.652 | 2246.02 | 25.85 | 48.436 | 6.41 | 1.288 | 4.118 | 8445.26 | 1.627 | 97.8 | 76.2 | 1460 | 24.26 | 5489.4 | 1602.8 | 2044.8 | 2610.2 | 1214.8 | 0.61249 | 5.405
2024-12-09 | 23:49 | Data | 0 | 33.81 | 32.028 | 167.722 | 7.64 | 158.562 | 2246.93 | 25.84 | 48.075 | 6.41 | 1.285 | 4.105 | 8476.91 | 1.634 | 97.9 | 76.2 | 1461 | 24.08 | 5510 | 1619.1 | 2057.8 | 2629.2 | 1214.8 | 0.61329 | 5.39
2024-12-09 | 23:49 | Data | 0 | 33.642 | 32.136 | 167.813 | 7.64 | 158.562 | 2246.93 | 25.84 | 48.075 | 6.41 | 1.283 | 4.116 | 8481.44 | 1.634 | 97.9 | 76.2 | 1461 | 24.08 | 5512.9 | 1613.6 | 2077 | 2645.8 | 1214.8 | 0.60897 | 5.4
2024-12-09 | 23:49 | Data | 0 | 33.588 | 32.258 | 167.813 | 7.64 | 158.562 | 2248.73 | 25.84 | 48.165 | 6.41 | 1.289 | 4.097 | 8467.87 | 1.566 | 97.9 | 76.1 | 1462 | 24.13 | 5504.1 | 1623.2 | 2074.6 | 2646.4 | 1214.8 | 0.61092 | 5.387
2024-12-09 | 23:50 | Data | 0 | 33.473 | 32.136 | 167.767 | 7.64 | 158.562 | 2252.35 | 25.85 | 48.165 | 6.41 | 1.284 | 4.115 | 8467.87 | 1.6 | 97.9 | 76.2 | 1464 | 24.08 | 5504.1 | 1615.4 | 2086.5 | 2652.8 | 1214.8 | 0.60622 | 5.4
2024-12-09 | 23:50 | Data | 0 | 33.952 | 32.46 | 167.858 | 7.64 | 158.607 | 2249.64 | 25.84 | 48.255 | 6.42 | 1.285 | 4.103 | 8445.26 | 1.627 | 97.9 | 76.1 | 1462 | 24.13 | 5489.4 | 1616.4 | 2065 | 2636.1 | 1214.8 | 0.6104 | 5.388
2024-12-09 | 23:50 | Data | 0 | 33.743 | 32.028 | 167.813 | 7.64 | 158.607 | 2249.64 | 25.84 | 48.075 | 6.41 | 1.293 | 4.099 | 8454.3 | 1.782 | 97.9 | 76 | 1462 | 24.08 | 5495.3 | 1619.3 | 2051.2 | 2626.2 | 1214.8 | 0.61364 | 5.392
2024-12-09 | 23:50 | Data | 0 | 33.729 | 32.035 | 167.903 | 7.63 | 158.652 | 2249.64 | 25.85 | 48.165 | 6.41 | 1.284 | 4.138 | 8454.3 | 1.404 | 97.9 | 76.3 | 1462 | 24.13 | 5495.3 | 1633.2 | 2059.7 | 2636.2 | 1214.8 | 0.61721 | 5.422
2024-12-09 | 23:50 | Data | 0 | 33.486 | 32.028 | 167.858 | 7.63 | 158.607 | 2246.93 | 25.84 | 48.165 | 6.42 | 1.29 | 4.122 | 8463.35 | 1.391 | 97.9 | 76.2 | 1461 | 24.08 | 5501.2 | 1638.3 | 2056.9 | 2642.6 | 1214.8 | 0.61172 | 5.411
2024-12-09 | 23:50 | Data | 0 | 33.588 | 32.008 | 167.722 | 7.64 | 158.517 | 2246.93 | 25.83 | 48.165 | 6.41 | 1.295 | 4.093 | 8440.74 | 1.789 | 97.9 | 76 | 1461 | 24.08 | 5486.5 | 1616.6 | 2055 | 2626.7 | 1214.8 | 0.61309 | 5.387
2024-12-09 | 23:50 | Data | 0 | 33.642 | 32.129 | 167.767 | 7.64 | 158.562 | 2139.37 | 25.84 | 48.255 | 6.41 | 1.286 | 4.09 | 8440.74 | 1.452 | 97.7 | 76.1 | 1391 | 24.13 | 5486.5 | 1599.8 | 2067.5 | 2628.8 | 1214.8 | 0.61106 | 5.375
2024-12-09 | 23:50 | Data | 0 | 33.419 | 32.015 | 167.767 | 7.63 | 158.472 | 2244.22 | 25.84 | 48.165 | 6.41 | 1.292 | 4.109 | 8431.69 | 1.445 | 97.9 | 76.1 | 1459 | 24.08 | 5480.6 | 1605.9 | 2047.7 | 2610.6 | 1214.8 | 0.6092 | 5.401
2024-12-09 | 23:50 | Data | 0 | 33.844 | 32.042 | 167.858 | 7.64 | 158.607 | 2243.31 | 25.84 | 48.165 | 6.41 | 1.278 | 4.104 | 8436.21 | 1.715 | 97.9 | 76.2 | 1459 | 24.08 | 5483.5 | 1601.5 | 2069.1 | 2630.5 | 1214.8 | 0.60622 | 5.381
2024-12-09 | 23:50 | Data | 0 | 33.864 | 31.832 | 167.858 | 7.64 | 158.607 | 2240.6 | 25.84 | 48.165 | 6.41 | 1.28 | 4.124 | 8445.26 | 1.668 | 97.9 | 76.3 | 1456 | 24.08 | 5489.4 | 1596.2 | 2102.8 | 2652.9 | 1214.8 | 0.60108 | 5.404
2024-12-09 | 23:50 | Data | 0 | 33.756 | 32.028 | 167.722 | 7.63 | 158.472 | 2242.41 | 25.84 | 48.165 | 6.41 | 1.282 | 4.126 | 8445.26 | 1.634 | 97.9 | 76.3 | 1457 | 24.04 | 5489.4 | 1607.8 | 2073.4 | 2635.7 | 1214.8 | 0.6074 | 5.408
2024-12-09 | 23:50 | Data | 0 | 33.662 | 32.204 | 167.767 | 7.63 | 158.517 | 2241.5 | 25.83 | 48.255 | 6.41 | 1.28 | 4.097 | 8440.74 | 1.647 | 97.9 | 76.2 | 1458 | 24.08 | 5486.5 | 1622.1 | 2067.1 | 2640.7 | 1214.8 | 0.60871 | 5.379
2024-12-09 | 23:50 | Data | 0 | 33.837 | 32.264 | 167.858 | 7.63 | 158.607 | 2242.41 | 25.85 | 48.165 | 6.41 | 1.28 | 4.092 | 8454.3 | 1.695 | 97.8 | 76.2 | 1458 | 24.08 | 5495.3 | 1609 | 2065.4 | 2631.6 | 1214.8 | 0.60809 | 5.374
2024-12-09 | 23:50 | Data | 0 | 33.756 | 32.258 | 167.903 | 7.63 | 158.652 | 2244.22 | 25.84 | 48.165 | 6.41 | 1.28 | 4.093 | 8472.39 | 1.6 | 97.9 | 76.2 | 1458 | 24.13 | 5507.1 | 1601.5 | 2067.3 | 2629.8 | 1214.8 | 0.61382 | 5.373
2024-12-09 | 23:50 | Data | 0 | 33.696 | 32.028 | 167.813 | 7.64 | 158.607 | 2244.22 | 25.84 | 48.165 | 6.41 | 1.29 | 4.099 | 8481.44 | 1.398 | 97.9 | 76.1 | 1459 | 24.08 | 5512.9 | 1612.7 | 2057.3 | 2626.7 | 1214.8 | 0.61174 | 5.389
2024-12-09 | 23:50 | Data | 0 | 33.439 | 32.001 | 167.767 | 7.63 | 158.472 | 2244.22 | 25.83 | 48.075 | 6.41 | 1.297 | 4.109 | 8481.44 | 1.533 | 97.9 | 76 | 1459 | 24.04 | 5512.9 | 1630.3 | 2070.1 | 2649 | 1214.8 | 0.61209 | 5.405
2024-12-09 | 23:50 | Data | 0 | 33.642 | 32.028 | 167.813 | 7.63 | 158.562 | 2244.22 | 25.84 | 48.165 | 6.41 | 1.289 | 4.088 | 8490.48 | 1.614 | 97.9 | 76 | 1459 | 24.08 | 5518.8 | 1625 | 2082.3 | 2654.2 | 1214.8 | 0.60994 | 5.377
2024-12-09 | 23:50 | Data | 0 | 33.642 | 32.028 | 167.722 | 7.63 | 158.472 | 2245.12 | 25.84 | 48.165 | 6.41 | 1.294 | 4.119 | 8472.39 | 1.614 | 97.9 | 76.1 | 1459 | 24.08 | 5507.1 | 1625.7 | 2077.3 | 2650.6 | 1214.8 | 0.61035 | 5.413
2024-12-09 | 23:51 | Data | 0 | 33.642 | 32.028 | 167.767 | 7.63 | 158.562 | 2243.31 | 25.83 | 48.165 | 6.41 | 1.294 | 4.113 | 8472.39 | 1.614 | 97.8 | 76.1 | 1458 | 24.08 | 5507.1 | 1631.7 | 2065.1 | 2645.3 | 1214.8 | 0.61446 | 5.407
2024-12-09 | 23:51 | Data | 0 | 33.628 | 32.021 | 167.586 | 7.64 | 158.472 | 2241.5 | 25.85 | 48.165 | 6.4 | 1.282 | 4.089 | 8458.83 | 1.62 | 97.9 | 76.1 | 1457 | 24.08 | 5498.2 | 1618.8 | 2081.7 | 2650.4 | 1214.8 | 0.60961 | 5.372
2024-12-09 | 23:51 | Data | 0 | 33.426 | 31.812 | 167.722 | 7.64 | 158.517 | 2242.41 | 25.85 | 48.165 | 6.41 | 1.282 | 4.116 | 8458.83 | 1.816 | 97.9 | 76.2 | 1457 | 24.08 | 5498.2 | 1606 | 2076.5 | 2637.9 | 1214.8 | 0.60465 | 5.399
2024-12-09 | 23:51 | Data | 0 | 33.858 | 32.163 | 167.813 | 7.64 | 158.562 | 2244.22 | 25.84 | 48.165 | 6.41 | 1.283 | 4.113 | 8467.87 | 1.701 | 97.9 | 76.2 | 1459 | 24.08 | 5504.1 | 1610.6 | 2050.4 | 2620.7 | 1214.8 | 0.61596 | 5.396
2024-12-09 | 23:51 | Data | 0 | 33.426 | 32.19 | 167.722 | 7.63 | 158.607 | 2245.12 | 25.84 | 48.165 | 6.41 | 1.285 | 4.11 | 8481.44 | 1.296 | 97.8 | 76.2 | 1459 | 24.13 | 5512.9 | 1607.2 | 2032.6 | 2604 | 1214.8 | 0.61748 | 5.394
2024-12-09 | 23:51 | Data | 0 | 33.844 | 32.163 | 167.858 | 7.63 | 158.652 | 2244.22 | 25.83 | 48.165 | 6.41 | 1.279 | 4.105 | 8463.35 | 1.519 | 97.9 | 76.3 | 1459 | 24.08 | 5501.2 | 1628.2 | 2057.5 | 2635.8 | 1214.8 | 0.61502 | 5.382
2024-12-09 | 23:51 | Data | 0 | 33.588 | 32.19 | 167.767 | 7.63 | 158.517 | 2242.41 | 25.85 | 47.623 | 6.41 | 1.278 | 4.094 | 8454.3 | 1.627 | 97.9 | 76.2 | 1458 | 23.86 | 5495.3 | 1623.7 | 2065.7 | 2639 | 1214.8 | 0.61297 | 5.372
2024-12-09 | 23:51 | Data | 0 | 33.615 | 32.021 | 167.722 | 7.63 | 158.562 | 2239.7 | 25.84 | 48.075 | 6.41 | 1.282 | 4.084 | 8472.39 | 1.62 | 97.8 | 76.1 | 1456 | 24.08 | 5507.1 | 1618.5 | 2074.3 | 2644.4 | 1214.8 | 0.61205 | 5.366
2024-12-09 | 23:51 | Data | 0 | 33.426 | 31.913 | 167.677 | 7.63 | 158.472 | 2236.98 | 25.84 | 48.165 | 6.41 | 1.296 | 4.085 | 8458.83 | 1.62 | 97.8 | 75.9 | 1455 | 24.08 | 5498.2 | 1611.3 | 2056.1 | 2623.2 | 1214.8 | 0.60668 | 5.38
2024-12-09 | 23:51 | Data | 0 | 33.696 | 32.028 | 167.767 | 7.63 | 158.562 | 2238.79 | 25.84 | 48.075 | 6.41 | 1.285 | 4.086 | 8463.35 | 1.614 | 97.9 | 76.1 | 1455 | 24.04 | 5501.2 | 2705.1 | 2681.1 | 3939.1 | 1214.8 | 0.66848 | 5.37
2024-12-09 | 23:51 | Data | 0 | 33.696 | 32.035 | 167.813 | 7.63 | 158.562 | 2238.79 | 25.85 | 48.165 | 6.41 | 1.272 | 4.079 | 8454.3 | 1.627 | 97.8 | 76.2 | 1455 | 24.08 | 5495.3 | 2688.3 | 2694.5 | 3933.3 | 1214.8 | 0.66572 | 5.352
2024-12-09 | 23:51 | Data | 0 | 33.858 | 32.042 | 167.722 | 7.63 | 158.562 | 2238.79 | 25.84 | 48.075 | 6.41 | 1.275 | 4.093 | 8472.39 | 1.769 | 97.8 | 76.2 | 1455 | 24.04 | 5507.1 | 2706.6 | 2675.6 | 3935.4 | 1214.8 | 0.66846 | 5.368
2024-12-09 | 23:51 | Data | 0 | 33.642 | 31.853 | 167.677 | 7.64 | 158.517 | 2238.79 | 25.84 | 48.255 | 6.41 | 1.279 | 4.133 | 8454.3 | 1.614 | 97.8 | 76.4 | 1455 | 24.08 | 5495.3 | 2689.3 | 2647.4 | 3905.9 | 1214.8 | 0.67068 | 5.411
2024-12-09 | 23:51 | Data | 0 | 33.473 | 32.028 | 167.677 | 7.63 | 158.472 | 2235.18 | 25.84 | 48.165 | 6.41 | 1.282 | 4.119 | 8449.78 | 1.506 | 97.8 | 76.2 | 1453 | 24.13 | 5492.4 | 2721.6 | 2660.3 | 3927.8 | 1214.8 | 0.67178 | 5.401
2024-12-09 | 23:51 | Data | 0 | 33.412 | 32.089 | 167.677 | 7.63 | 158.472 | 2235.18 | 25.83 | 48.075 | 6.41 | 1.28 | 4.116 | 8454.3 | 1.614 | 97.9 | 76.3 | 1453 | 24.08 | 5495.3 | 2687.2 | 2633.1 | 3887.7 | 1214.8 | 0.6744 | 5.397
2024-12-09 | 23:51 | Data | 0 | 33.635 | 32.143 | 167.813 | 7.64 | 158.472 | 2236.98 | 25.84 | 48.075 | 6.41 | 1.287 | 4.094 | 8449.78 | 1.62 | 97.9 | 76.1 | 1454 | 24.04 | 5492.4 | 2691.8 | 2653.4 | 3914.3 | 1214.8 | 0.67046 | 5.381
2024-12-09 | 23:51 | Data | 0 | 33.642 | 32.237 | 167.767 | 7.64 | 158.517 | 2238.79 | 25.84 | 48.255 | 6.42 | 1.295 | 4.084 | 8454.3 | 1.438 | 97.8 | 75.9 | 1455 | 24.08 | 5495.3 | 2687 | 2667.5 | 3912.3 | 1214.8 | 0.6698 | 5.379
2024-12-09 | 23:52 | Data | 0 | 33.412 | 31.974 | 167.767 | 7.63 | 158.517 | 2240.6 | 25.83 | 48.165 | 6.41 | 1.282 | 4.126 | 8440.74 | 1.553 | 97.9 | 76.3 | 1456 | 24.08 | 5486.5 | 2712.1 | 2653.9 | 3925.9 | 1214.8 | 0.67364 | 5.409
2024-12-09 | 23:52 | Data | 0 | 33.642 | 31.913 | 167.722 | 7.63 | 158.426 | 2241.5 | 25.84 | 48.436 | 6.41 | 1.279 | 4.109 | 8445.26 | 1.614 | 97.8 | 76.3 | 1458 | 24.22 | 5489.4 | 2693.4 | 2638.1 | 3897.3 | 1214.8 | 0.67214 | 5.389
2024-12-09 | 23:52 | Data | 0 | 33.588 | 31.853 | 167.722 | 7.63 | 158.472 | 2242.41 | 25.83 | 48.075 | 6.41 | 1.287 | 4.111 | 8454.3 | 1.614 | 97.9 | 76.2 | 1458 | 24.08 | 5495.3 | 2701 | 2663.4 | 3918.6 | 1214.9 | 0.67172 | 5.397
2024-12-09 | 23:52 | Data | 0 | 33.392 | 32.021 | 167.632 | 7.64 | 158.562 | 2241.5 | 25.84 | 48.165 | 6.41 | 1.282 | 4.124 | 8454.3 | 1.546 | 97.9 | 76.3 | 1457 | 24.08 | 5495.3 | 2692.9 | 2656.3 | 3909.5 | 1214.9 | 0.67141 | 5.405
2024-12-09 | 23:52 | Data | 0 | 33.669 | 32.028 | 167.813 | 7.64 | 158.562 | 2241.5 | 25.84 | 48.165 | 6.41 | 1.289 | 4.116 | 8454.3 | 1.445 | 97.9 | 76.2 | 1457 | 24.08 | 5495.3 | 2729.5 | 2665 | 3938.9 | 1214.9 | 0.66888 | 5.408
2024-12-09 | 23:52 | Data | 0 | 33.419 | 31.913 | 167.722 | 7.63 | 158.562 | 2241.5 | 25.84 | 48.165 | 6.41 | 1.277 | 4.11 | 8454.3 | 1.614 | 97.9 | 76.3 | 1457 | 24.08 | 5495.3 | 2697.4 | 2634.3 | 3897.7 | 1214.9 | 0.6768 | 5.385
2024-12-09 | 23:52 | Data | 0 | 33.588 | 31.826 | 167.677 | 7.64 | 158.426 | 2236.08 | 25.84 | 48.075 | 6.41 | 1.278 | 4.107 | 8445.26 | 1.722 | 97.8 | 76.3 | 1453 | 24.08 | 5489.4 | 2688.6 | 2653.3 | 3907.6 | 1214.9 | 0.67095 | 5.385
2024-12-09 | 23:52 | Data | 0 | 33.527 | 32.224 | 167.948 | 7.63 | 158.517 | 2241.5 | 25.84 | 48.075 | 6.41 | 1.282 | 4.119 | 8431.69 | 1.438 | 97.9 | 76.3 | 1458 | 24.08 | 5480.6 | 2725 | 2653.5 | 3924.5 | 1214.9 | 0.67761 | 5.401
2024-12-09 | 23:52 | Data | 0 | 33.534 | 32.204 | 167.722 | 7.63 | 158.562 | 2235.18 | 25.84 | 48.165 | 6.41 | 1.284 | 4.136 | 8418.13 | 1.58 | 97.8 | 76.3 | 1453 | 24.08 | 5471.8 | 2714.7 | 2662.7 | 3926.3 | 1214.9 | 0.67488 | 5.42
2024-12-09 | 23:52 | Data | 0 | 33.439 | 32.001 | 167.767 | 7.63 | 158.472 | 2242.41 | 25.84 | 48.165 | 6.41 | 1.278 | 4.109 | 8409.08 | 1.533 | 97.9 | 76.3 | 1457 | 24.04 | 5465.9 | 2712.6 | 2670.7 | 3929.3 | 1214.9 | 0.6734 | 5.387
2024-12-09 | 23:52 | Data | 0 | 33.466 | 31.92 | 167.586 | 7.63 | 158.517 | 2244.22 | 25.83 | 48.165 | 6.41 | 1.28 | 4.116 | 8427.17 | 1.614 | 97.9 | 76.3 | 1459 | 24.04 | 5477.7 | 2705.1 | 2639.3 | 3903.6 | 1214.9 | 0.67309 | 5.395
2024-12-09 | 23:52 | Data | 0 | 33.642 | 32.028 | 167.722 | 7.63 | 158.562 | 2248.73 | 25.84 | 48.165 | 6.41 | 1.275 | 4.086 | 8431.69 | 1.614 | 97.9 | 76.2 | 1462 | 24.08 | 5480.6 | 2670.1 | 2653 | 3897.6 | 1214.9 | 0.6677 | 5.361
2024-12-09 | 23:52 | Data | 0 | 33.642 | 32.143 | 167.813 | 7.64 | 158.517 | 2249.64 | 25.84 | 48.075 | 6.41 | 1.282 | 4.122 | 8436.21 | 1.614 | 97.9 | 76.3 | 1462 | 24.08 | 5483.5 | 2689.4 | 2646.9 | 3902.2 | 1214.9 | 0.67193 | 5.402
2024-12-09 | 23:52 | Data | 0 | 33.75 | 32.143 | 167.722 | 7.64 | 158.472 | 2248.73 | 25.83 | 48.255 | 6.4 | 1.274 | 4.124 | 8445.26 | 1.668 | 97.9 | 76.4 | 1462 | 24.08 | 5489.4 | 2685.1 | 2654.3 | 3896.5 | 1214.9 | 0.66927 | 5.4
2024-12-09 | 23:52 | Data | 0 | 33.419 | 31.974 | 167.722 | 7.63 | 158.426 | 2249.64 | 25.84 | 48.075 | 6.41 | 1.282 | 4.103 | 8449.78 | 1.499 | 97.9 | 76.2 | 1462 | 24.08 | 5492.4 | 2682.7 | 2668.3 | 3918.3 | 1214.9 | 0.66684 | 5.384
2024-12-09 | 23:52 | Data | 0 | 33.426 | 32.028 | 167.813 | 7.64 | 158.517 | 2248.73 | 25.83 | 48.165 | 6.41 | 1.284 | 4.101 | 8458.83 | 1.384 | 97.9 | 76.2 | 1462 | 24.08 | 5498.2 | 2696.3 | 2680.5 | 3930.3 | 1214.9 | 0.66726 | 5.385
2024-12-09 | 23:52 | Data | 0 | 33.864 | 32.035 | 167.813 | 7.64 | 158.517 | 2248.73 | 25.84 | 48.165 | 6.41 | 1.282 | 4.075 | 8454.3 | 1.695 | 97.9 | 76.1 | 1461 | 24.08 | 5495.3 | 2718.6 | 2687.7 | 3947.5 | 1214.9 | 0.67188 | 5.357
2024-12-09 | 23:52 | Data | 0 | 34.067 | 32.197 | 167.858 | 7.64 | 158.562 | 2248.73 | 25.84 | 48.165 | 6.41 | 1.279 | 4.103 | 8454.3 | 1.62 | 97.9 | 76.2 | 1462 | 24.08 | 5495.3 | 2696.2 | 2664 | 3923.6 | 1214.9 | 0.66873 | 5.382
2024-12-09 | 23:53 | Data | 0 | 33.466 | 32.001 | 167.677 | 7.64 | 158.517 | 2253.25 | 25.83 | 48.165 | 6.41 | 1.29 | 4.119 | 8454.3 | 1.614 | 97.9 | 76.2 | 1465 | 24.08 | 5495.3 | 2699.3 | 2655.1 | 3911.4 | 1214.9 | 0.67127 | 5.409
2024-12-09 | 23:53 | Data | 0 | 33.615 | 31.812 | 167.677 | 7.64 | 158.472 | 2247.83 | 25.84 | 48.075 | 6.41 | 1.292 | 4.09 | 8454.3 | 1.809 | 97.9 | 76 | 1461 | 24.08 | 5495.3 | 2684.3 | 2647.4 | 3906.8 | 1214.9 | 0.66902 | 5.383
2024-12-09 | 23:53 | Data | 0 | 33.419 | 32.116 | 167.813 | 7.63 | 158.607 | 2246.02 | 25.84 | 48.165 | 6.41 | 1.289 | 4.094 | 8431.69 | 1.674 | 97.9 | 76.1 | 1461 | 24.04 | 5480.6 | 2717.3 | 2664.9 | 3930.5 | 1214.9 | 0.67451 | 5.383
2024-12-09 | 23:53 | Data | 0 | 33.628 | 32.237 | 167.858 | 7.64 | 158.562 | 2244.22 | 25.84 | 48.165 | 6.41 | 1.279 | 4.084 | 8431.69 | 1.485 | 97.9 | 76.2 | 1459 | 24.04 | 5480.6 | 2691.8 | 2652.5 | 3908.8 | 1214.9 | 0.67183 | 5.363
2024-12-09 | 23:53 | Data | 0 | 33.419 | 31.805 | 167.813 | 7.64 | 158.517 | 2244.22 | 25.84 | 48.165 | 6.41 | 1.283 | 4.068 | 8431.69 | 1.607 | 97.9 | 76 | 1459 | 24.08 | 5480.6 | 2703.1 | 2659.4 | 3915.3 | 1214.9 | 0.67272 | 5.352
2024-12-09 | 23:53 | Data | 0 | 33.81 | 32.258 | 167.722 | 7.64 | 158.517 | 2244.22 | 25.84 | 48.165 | 6.41 | 1.282 | 4.094 | 8427.17 | 1.6 | 97.9 | 76.1 | 1459 | 24.08 | 5477.7 | 2693.2 | 2666.4 | 3916.4 | 1214.9 | 0.6714 | 5.377
2024-12-09 | 23:53 | Data | 0 | 33.844 | 32.258 | 167.903 | 7.64 | 158.607 | 2244.22 | 25.84 | 48.165 | 6.41 | 1.284 | 4.085 | 8431.69 | 1.607 | 97.9 | 76.1 | 1459 | 24.08 | 5480.6 | 2690.6 | 2661.9 | 3917.9 | 1214.9 | 0.66861 | 5.37
2024-12-09 | 23:53 | Data | 0 | 33.419 | 31.812 | 167.813 | 7.64 | 158.517 | 2244.22 | 25.84 | 48.075 | 6.41 | 1.285 | 4.099 | 8431.69 | 1.789 | 97.9 | 76.1 | 1458 | 24.08 | 5480.6 | 2705.7 | 2640.3 | 3904.7 | 1214.9 | 0.67503 | 5.383
2024-12-09 | 23:53 | Data | 0 | 33.628 | 32.028 | 167.813 | 7.64 | 158.426 | 2244.22 | 25.84 | 48.075 | 6.41 | 1.278 | 4.13 | 8440.74 | 1.614 | 97.9 | 76.4 | 1459 | 24.04 | 5486.5 | 2705.6 | 2645.5 | 3911.5 | 1214.9 | 0.67485 | 5.409
2024-12-09 | 23:53 | Data | 0 | 33.648 | 32.028 | 167.677 | 7.63 | 158.517 | 2244.22 | 25.84 | 48.165 | 6.41 | 1.274 | 4.103 | 8431.69 | 1.445 | 97.9 | 76.3 | 1459 | 24.08 | 5480.6 | 2692.8 | 2669.5 | 3917.3 | 1214.9 | 0.66896 | 5.376
2024-12-09 | 23:53 | Data | 0 | 33.527 | 31.812 | 167.632 | 7.64 | 158.472 | 2245.12 | 25.84 | 48.165 | 6.41 | 1.273 | 4.09 | 8418.13 | 1.519 | 97.9 | 76.3 | 1459 | 24.08 | 5471.8 | 2691.7 | 2648.8 | 3908.1 | 1214.9 | 0.6692 | 5.363
2024-12-09 | 23:53 | Data | 0 | 33.426 | 32.028 | 167.813 | 7.64 | 158.562 | 2246.93 | 25.83 | 48.165 | 6.41 | 1.278 | 4.089 | 8431.69 | 1.56 | 97.9 | 76.2 | 1461 | 24.08 | 5480.6 | 2709 | 2670.5 | 3927.9 | 1214.9 | 0.66842 | 5.366
2024-12-09 | 23:53 | Data | 0 | 33.75 | 32.264 | 167.858 | 7.64 | 158.607 | 2246.93 | 25.84 | 48.165 | 6.41 | 1.292 | 4.103 | 8418.13 | 1.553 | 97.9 | 76 | 1461 | 24.08 | 5471.8 | 2660.4 | 2676.2 | 3904.8 | 1214.9 | 0.661 | 5.395
2024-12-09 | 23:53 | Data | 0 | 33.615 | 32.028 | 167.858 | 7.64 | 158.562 | 2245.12 | 25.84 | 48.165 | 6.41 | 1.289 | 4.106 | 8431.69 | 1.809 | 97.9 | 76.1 | 1459 | 24.04 | 5480.6 | 2680.1 | 2687.1 | 3926.6 | 1214.9 | 0.66202 | 5.395
2024-12-09 | 23:53 | Data | 0 | 33.642 | 32.237 | 167.767 | 7.64 | 158.562 | 2239.7 | 25.84 | 48.165 | 6.41 | 1.285 | 4.147 | 8427.17 | 1.404 | 97.8 | 76.3 | 1456 | 24.08 | 5477.7 | 2689.8 | 2705.2 | 3945.3 | 1214.9 | 0.66249 | 5.432
2024-12-09 | 23:53 | Data | 0 | 33.588 | 32.109 | 167.767 | 7.64 | 158.472 | 2245.12 | 25.84 | 48.075 | 6.41 | 1.291 | 4.132 | 8431.69 | 1.634 | 97.9 | 76.2 | 1459 | 24.08 | 5480.6 | 2682.1 | 2687.8 | 3925.9 | 1214.9 | 0.66557 | 5.423
2024-12-09 | 23:53 | Data | 0 | 33.419 | 32.028 | 167.903 | 7.64 | 158.562 | 2241.5 | 25.83 | 48.075 | 6.41 | 1.286 | 4.125 | 8418.13 | 1.587 | 97.9 | 76.2 | 1458 | 24.08 | 5471.8 | 2668 | 2669.9 | 3909.1 | 1214.9 | 0.66434 | 5.412
2024-12-09 | 23:53 | Data | 0 | 33.588 | 32.204 | 167.858 | 7.63 | 158.562 | 2244.22 | 25.84 | 48.165 | 6.41 | 1.287 | 4.11 | 8400.04 | 1.661 | 97.9 | 76.2 | 1459 | 24.04 | 5460 | 2701.8 | 2667.8 | 3925.9 | 1214.9 | 0.67254 | 5.397
2024-12-09 | 23:54 | Data | 0 | 33.527 | 32.055 | 167.767 | 7.64 | 158.472 | 2246.93 | 25.84 | 48.165 | 6.41 | 1.295 | 4.093 | 8404.56 | 1.573 | 97.9 | 76 | 1461 | 24.08 | 5463 | 2704.5 | 2652.3 | 3915.4 | 1214.9 | 0.67458 | 5.388
2024-12-09 | 23:54 | Data | 0 | 33.75 | 31.913 | 167.813 | 7.64 | 158.517 | 2244.22 | 25.84 | 48.165 | 6.41 | 1.28 | 4.101 | 8400.04 | 1.654 | 97.9 | 76.2 | 1459 | 24.08 | 5460 | 2706.3 | 2637 | 3904.6 | 1214.9 | 0.67387 | 5.381
2024-12-09 | 23:54 | Data | 0 | 33.756 | 32.237 | 167.722 | 7.64 | 158.562 | 2244.22 | 25.84 | 48.165 | 6.4 | 1.275 | 4.098 | 8418.13 | 1.62 | 97.9 | 76.3 | 1459 | 24.08 | 5471.8 | 2720.5 | 2643.1 | 3919.5 | 1214.9 | 0.67608 | 5.373
2024-12-09 | 23:54 | Data | 0 | 33.642 | 32.15 | 167.858 | 7.63 | 158.562 | 2244.22 | 25.84 | 48.165 | 6.41 | 1.278 | 4.108 | 8409.08 | 1.614 | 97.9 | 76.3 | 1458 | 24.13 | 5465.9 | 2701.4 | 2655.8 | 3919.8 | 1214.9 | 0.67052 | 5.386
2024-12-09 | 23:54 | Data | 0 | 33.871 | 31.832 | 167.948 | 7.64 | 158.652 | 2241.5 | 25.84 | 48.165 | 6.4 | 1.276 | 4.111 | 8400.04 | 1.668 | 97.9 | 76.3 | 1457 | 24.08 | 5460 | 2683.8 | 2666.7 | 3912 | 1214.9 | 0.66631 | 5.387
2024-12-09 | 23:54 | Data | 0 | 33.642 | 32.082 | 167.767 | 7.64 | 158.517 | 2239.7 | 25.84 | 48.075 | 6.41 | 1.275 | 4.102 | 8386.47 | 1.681 | 97.8 | 76.3 | 1456 | 24.08 | 5451.2 | 2689.7 | 2709.5 | 3941.2 | 1214.9 | 0.66207 | 5.377
2024-12-09 | 23:54 | Data | 0 | 33.642 | 31.832 | 167.722 | 7.63 | 158.517 | 2235.18 | 25.83 | 48.165 | 6.41 | 1.283 | 4.121 | 8386.47 | 1.776 | 97.8 | 76.3 | 1453 | 24.08 | 5451.2 | 2703 | 2691.6 | 3942 | 1215 | 0.66781 | 5.405
2024-12-09 | 23:54 | Data | 0 | 33.628 | 32.028 | 167.858 | 7.63 | 158.562 | 2236.08 | 25.84 | 48.075 | 6.41 | 1.278 | 4.129 | 8404.56 | 1.62 | 97.9 | 76.4 | 1453 | 24.08 | 5463 | 2703.1 | 2699.8 | 3942.4 | 1215 | 0.6676 | 5.407
2024-12-09 | 23:54 | Data | 0 | 33.669 | 32.028 | 167.767 | 7.64 | 158.652 | 2235.18 | 25.84 | 48.165 | 6.41 | 1.282 | 4.115 | 8418.13 | 1.62 | 97.8 | 76.3 | 1453 | 24.13 | 5471.8 | 2688.2 | 2698.9 | 3949.1 | 1215 | 0.66525 | 5.397
2024-12-09 | 23:54 | Data | 0 | 33.426 | 31.927 | 167.677 | 7.63 | 158.562 | 2235.18 | 25.84 | 48.075 | 6.41 | 1.276 | 4.114 | 8400.04 | 1.701 | 97.8 | 76.3 | 1453 | 24.04 | 5460 | 2709.6 | 2706.2 | 3959.8 | 1215 | 0.66521 | 5.39
2024-12-09 | 23:54 | Data | 0 | 33.642 | 32.028 | 167.767 | 7.64 | 158.517 | 2236.08 | 25.83 | 48.165 | 6.41 | 1.279 | 4.102 | 8409.08 | 1.614 | 97.9 | 76.2 | 1453 | 24.08 | 5465.9 | 2694.5 | 2705.5 | 3944.6 | 1215 | 0.66304 | 5.382
2024-12-09 | 23:54 | Data | 0 | 33.601 | 31.805 | 167.767 | 7.64 | 158.607 | 2235.18 | 25.84 | 48.255 | 6.41 | 1.278 | 4.119 | 8418.13 | 1.83 | 97.8 | 76.3 | 1453 | 24.13 | 5471.8 | 2692.5 | 2689.2 | 3932.1 | 1215 | 0.66611 | 5.397
2024-12-09 | 23:54 | Data | 0 | 33.756 | 31.812 | 167.677 | 7.63 | 158.607 | 2236.08 | 25.84 | 48.255 | 6.41 | 1.274 | 4.103 | 8422.65 | 1.634 | 97.8 | 76.3 | 1453 | 24.08 | 5474.7 | 2705.6 | 2639.5 | 3905 | 1215 | 0.67659 | 5.377
2024-12-09 | 23:54 | Data | 0 | 33.696 | 32.008 | 167.858 | 7.63 | 158.562 | 2241.5 | 25.84 | 48.165 | 6.41 | 1.276 | 4.093 | 8431.69 | 1.701 | 97.9 | 76.2 | 1457 | 24.08 | 5480.6 | 2685.3 | 2684.3 | 3940.8 | 1215 | 0.66725 | 5.37
2024-12-09 | 23:54 | Data | 0 | 33.858 | 32.278 | 167.903 | 7.63 | 158.607 | 2228.85 | 25.84 | 47.623 | 6.41 | 1.278 | 4.111 | 8431.69 | 1.553 | 97.9 | 76.3 | 1449 | 23.81 | 5480.6 | 2681.6 | 2688.2 | 3930.7 | 1215 | 0.66517 | 5.389
2024-12-09 | 23:54 | Data | 0 | 33.655 | 32.15 | 167.813 | 7.63 | 158.562 | 2233.37 | 25.84 | 48.255 | 6.41 | 1.28 | 4.112 | 8440.74 | 1.492 | 97.8 | 76.3 | 1452 | 24.08 | 5486.5 | 2673.5 | 2672.9 | 3910.7 | 1215 | 0.66334 | 5.392
2024-12-09 | 23:54 | Data | 0 | 33.75 | 32.082 | 167.813 | 7.63 | 158.472 | 2233.37 | 25.84 | 48.165 | 6.41 | 1.282 | 4.098 | 8431.69 | 1.708 | 97.8 | 76.2 | 1452 | 24.08 | 5480.6 | 2717.8 | 2651.6 | 3920.8 | 1215 | 0.67751 | 5.382
2024-12-09 | 23:54 | Data | 0 | 33.554 | 32.001 | 167.813 | 7.64 | 158.562 | 2233.37 | 25.84 | 48.165 | 6.41 | 1.292 | 4.096 | 8454.3 | 1.641 | 97.8 | 76 | 1452 | 24.04 | 5495.3 | 2687.4 | 2699.4 | 3939.1 | 1215 | 0.66578 | 5.389
2024-12-09 | 23:55 | Data | 0 | 33.642 | 32.352 | 167.903 | 7.63 | 158.562 | 2236.08 | 25.84 | 48.165 | 6.41 | 1.293 | 4.09 | 8458.83 | 1.614 | 97.8 | 76 | 1453 | 24.08 | 5498.2 | 2689.5 | 2691.1 | 3935.3 | 1215 | 0.66598 | 5.382
2024-12-09 | 23:55 | Data | 0 | 33.696 | 32.028 | 167.722 | 7.63 | 158.607 | 2236.08 | 25.84 | 48.165 | 6.41 | 1.283 | 4.106 | 8467.87 | 1.62 | 97.8 | 76.2 | 1453 | 24.08 | 5504.1 | 2685 | 2703.2 | 3939.5 | 1215 | 0.66302 | 5.391
2024-12-09 | 23:55 | Data | 0 | 33.81 | 32.258 | 167.813 | 7.64 | 158.562 | 2233.37 | 25.84 | 48.165 | 6.41 | 1.274 | 4.11 | 8454.3 | 1.6 | 97.8 | 76.3 | 1452 | 24.08 | 5495.3 | 2707.7 | 2700 | 3943 | 1215 | 0.66266 | 5.384
2024-12-09 | 23:55 | Data | 0 | 33.527 | 32.001 | 167.813 | 7.64 | 158.562 | 2233.37 | 25.84 | 48.165 | 6.41 | 1.288 | 4.114 | 8454.3 | 1.742 | 97.8 | 76.2 | 1452 | 24.08 | 5495.3 | 2683.9 | 2690.1 | 3929.1 | 1215 | 0.6642 | 5.401
2024-12-09 | 23:55 | Data | 0 | 34.087 | 32.035 | 167.903 | 7.64 | 158.652 | 2233.37 | 25.84 | 48.075 | 6.41 | 1.295 | 4.105 | 8458.83 | 1.735 | 97.9 | 76 | 1452 | 23.99 | 5498.2 | 2684.1 | 2699.8 | 3938.2 | 1215 | 0.66412 | 5.4
2024-12-09 | 23:55 | Data | 0 | 33.675 | 32.035 | 167.813 | 7.64 | 158.607 | 2232.47 | 25.84 | 47.894 | 6.41 | 1.285 | 4.13 | 8454.3 | 1.445 | 97.9 | 76.3 | 1451 | 23.99 | 5495.3 | 2702.1 | 2695.7 | 3942.1 | 1215 | 0.66823 | 5.415
2024-12-09 | 23:55 | Data | 0 | 33.669 | 32.048 | 167.677 | 7.63 | 158.517 | 2235.18 | 25.84 | 47.894 | 6.41 | 1.282 | 4.111 | 8454.3 | 1.411 | 97.9 | 76.2 | 1453 | 23.95 | 5495.3 | 2683.9 | 2672 | 3916.4 | 1215 | 0.66557 | 5.394
2024-12-09 | 23:55 | Data | 0 | 33.817 | 32.258 | 167.858 | 7.63 | 158.562 | 2238.79 | 25.83 | 47.894 | 6.41 | 1.291 | 4.109 | 8472.39 | 1.607 | 97.9 | 76.1 | 1455 | 23.99 | 5507.1 | 2723.7 | 2676.9 | 3942.6 | 1215 | 0.67323 | 5.4
2024-12-09 | 23:55 | Data | 0 | 33.669 | 32.035 | 167.813 | 7.64 | 158.562 | 2241.5 | 25.83 | 47.894 | 6.41 | 1.29 | 4.085 | 8467.87 | 1.587 | 97.9 | 76 | 1457 | 23.95 | 5504.1 | 2683.6 | 2681.3 | 3921.9 | 1215 | 0.66576 | 5.373
2024-12-09 | 23:55 | Data | 0 | 34.047 | 32.062 | 167.903 | 7.63 | 158.743 | 2241.5 | 25.83 | 47.894 | 6.41 | 1.283 | 4.071 | 8454.3 | 1.796 | 97.9 | 76 | 1457 | 23.95 | 5495.3 | 2686.7 | 2684.5 | 3932.6 | 1215 | 0.66358 | 5.354
2024-12-09 | 23:55 | Data | 0 | 33.648 | 32.028 | 167.903 | 7.64 | 158.652 | 2241.5 | 25.85 | 47.894 | 6.41 | 1.28 | 4.081 | 8440.74 | 1.614 | 97.9 | 76.1 | 1457 | 23.95 | 5486.5 | 2696.6 | 2668.3 | 3925 | 1215 | 0.66945 | 5.363
2024-12-09 | 23:55 | Data | 0 | 33.959 | 32.082 | 167.858 | 7.64 | 158.607 | 2244.22 | 25.84 | 47.804 | 6.41 | 1.286 | 4.121 | 8440.74 | 1.749 | 97.9 | 76.2 | 1459 | 23.95 | 5486.5 | 2706.1 | 2677.9 | 3933.7 | 1215 | 0.67154 | 5.408
2024-12-09 | 23:55 | Data | 0 | 33.669 | 32.042 | 167.903 | 7.64 | 158.652 | 2244.22 | 25.83 | 47.894 | 6.41 | 1.282 | 4.132 | 8445.26 | 1.776 | 97.9 | 76.3 | 1458 | 23.95 | 5489.4 | 2692.6 | 2677.3 | 3930.1 | 1215 | 0.66646 | 5.414
2024-12-09 | 23:55 | Data | 0 | 33.864 | 32.264 | 167.813 | 7.63 | 158.607 | 2242.41 | 25.84 | 47.894 | 6.41 | 1.283 | 4.127 | 8440.74 | 1.607 | 97.9 | 76.3 | 1458 | 23.95 | 5486.5 | 2708.4 | 2708.1 | 3957.1 | 1215 | 0.66791 | 5.411
2024-12-09 | 23:55 | Data | 0 | 33.979 | 32.062 | 167.858 | 7.64 | 158.743 | 2242.41 | 25.84 | 47.894 | 6.41 | 1.276 | 4.109 | 8445.26 | 1.755 | 97.9 | 76.3 | 1458 | 23.95 | 5489.4 | 2711.7 | 2677.5 | 3939.5 | 1215 | 0.66919 | 5.386
2024-12-09 | 23:55 | Data | 0 | 33.642 | 32.204 | 167.813 | 7.64 | 158.562 | 2246.02 | 25.84 | 47.894 | 6.42 | 1.284 | 4.12 | 8427.17 | 1.641 | 97.9 | 76.2 | 1460 | 23.99 | 5477.7 | 2700.9 | 2684.8 | 3929.2 | 1215 | 0.66705 | 5.404
2024-12-09 | 23:55 | Data | 0 | 33.696 | 32.042 | 167.858 | 7.64 | 158.607 | 2241.5 | 25.84 | 47.804 | 6.41 | 1.288 | 4.129 | 8427.17 | 1.58 | 97.9 | 76.2 | 1457 | 23.9 | 5477.7 | 2712.2 | 2699.9 | 3949.4 | 1215 | 0.66879 | 5.416
2024-12-09 | 23:56 | Data | 0 | 33.898 | 32.089 | 167.948 | 7.63 | 158.652 | 2240.6 | 25.84 | 47.894 | 6.41 | 1.289 | 4.108 | 8409.08 | 1.782 | 97.9 | 76.1 | 1456 | 23.95 | 5465.9 | 2682.1 | 2692.9 | 3930.4 | 1215 | 0.66565 | 5.397
2024-12-09 | 23:56 | Data | 0 | 34.067 | 32.312 | 167.858 | 7.64 | 158.652 | 2238.79 | 25.84 | 47.804 | 6.41 | 1.291 | 4.101 | 8418.13 | 1.722 | 97.9 | 76 | 1455 | 23.9 | 5471.8 | 2698.8 | 2670.9 | 3925.8 | 1215 | 0.67044 | 5.392
2024-12-09 | 23:56 | Data | 0 | 33.743 | 32.136 | 167.948 | 7.63 | 158.607 | 2233.37 | 25.84 | 47.894 | 6.42 | 1.289 | 4.106 | 8427.17 | 1.607 | 97.9 | 76.1 | 1452 | 23.95 | 5477.7 | 2692.7 | 2670.4 | 3922.4 | 1215 | 0.66831 | 5.396
2024-12-09 | 23:56 | Data | 0 | 33.817 | 32.318 | 167.813 | 7.64 | 158.652 | 2232.47 | 25.84 | 47.894 | 6.41 | 1.291 | 4.09 | 8400.04 | 1.593 | 97.9 | 76 | 1452 | 23.99 | 5460 | 2708.3 | 2675.2 | 3932.2 | 1215 | 0.67074 | 5.382
2024-12-09 | 23:56 | Data | 0 | 33.763 | 32.055 | 167.903 | 7.63 | 158.607 | 2238.79 | 25.84 | 47.894 | 6.41 | 1.287 | 4.089 | 8400.04 | 1.533 | 97.9 | 76.1 | 1456 | 23.95 | 5460 | 2695.5 | 2633.8 | 3893.3 | 1215 | 0.67342 | 5.378
2024-12-09 | 23:56 | Data | 0 | 33.642 | 32.028 | 167.767 | 7.64 | 158.562 | 2238.79 | 25.84 | 47.894 | 6.4 | 1.292 | 4.111 | 8409.08 | 1.614 | 97.9 | 76.1 | 1455 | 23.95 | 5465.9 | 2699.4 | 2661.8 | 3925.7 | 1215 | 0.6722 | 5.404
2024-12-09 | 23:56 | Data | 0 | 33.871 | 32.237 | 167.903 | 7.64 | 158.607 | 2239.7 | 25.84 | 47.894 | 6.41 | 1.29 | 4.108 | 8418.13 | 1.641 | 97.9 | 76.1 | 1455 | 23.95 | 5471.8 | 2687.9 | 2656 | 3910.7 | 1215 | 0.66923 | 5.398
2024-12-09 | 23:56 | Data | 0 | 33.756 | 32.082 | 167.767 | 7.63 | 158.698 | 2238.79 | 25.84 | 47.894 | 6.41 | 1.288 | 4.12 | 8400.04 | 1.6 | 97.9 | 76.2 | 1454 | 23.95 | 5460 | 2683.4 | 2684.4 | 3921.1 | 1215 | 0.66486 | 5.408
2024-12-09 | 23:56 | Data | 0 | 33.696 | 32.042 | 167.813 | 7.64 | 158.607 | 2238.79 | 25.84 | 47.894 | 6.41 | 1.289 | 4.134 | 8386.47 | 1.607 | 97.9 | 76.2 | 1455 | 23.95 | 5451.2 | 2683.9 | 2674.6 | 3911.6 | 1215 | 0.66745 | 5.423
2024-12-09 | 23:56 | Data | 0 | 33.918 | 32.008 | 167.813 | 7.64 | 158.607 | 2238.79 | 25.83 | 47.894 | 6.41 | 1.285 | 4.134 | 8400.04 | 1.492 | 97.9 | 76.3 | 1456 | 23.95 | 5460 | 2703.3 | 2718.6 | 3960.8 | 1215 | 0.66376 | 5.421
2024-12-09 | 23:56 | Data | 0 | 34.08 | 32.271 | 167.948 | 7.64 | 158.607 | 2238.79 | 25.84 | 47.894 | 6.41 | 1.284 | 4.122 | 8395.51 | 1.654 | 97.9 | 76.2 | 1455 | 23.95 | 5457.1 | 2691.2 | 2715.2 | 3951.5 | 1215.1 | 0.66335 | 5.406
2024-12-09 | 23:56 | Data | 0 | 33.655 | 32.028 | 167.813 | 7.63 | 158.607 | 2229.75 | 25.84 | 47.894 | 6.41 | 1.282 | 4.103 | 8404.56 | 1.506 | 97.9 | 76.2 | 1449 | 23.9 | 5463 | 2697.2 | 2708.9 | 3934.5 | 1215.1 | 0.66263 | 5.384
2024-12-09 | 23:56 | Data | 0 | 33.642 | 32.264 | 167.813 | 7.63 | 158.607 | 2235.18 | 25.84 | 47.894 | 6.42 | 1.279 | 4.12 | 8436.21 | 1.56 | 97.9 | 76.3 | 1453 | 23.95 | 5483.5 | 2712.5 | 2687.6 | 3942.3 | 1215.1 | 0.672 | 5.399
2024-12-09 | 23:56 | Data | 0 | 33.891 | 32.035 | 167.813 | 7.64 | 158.607 | 2236.08 | 25.84 | 47.894 | 6.41 | 1.285 | 4.124 | 8440.74 | 1.634 | 97.9 | 76.2 | 1453 | 23.95 | 5486.5 | 2704.5 | 2674.9 | 3930.6 | 1215.1 | 0.6694 | 5.411
2024-12-09 | 23:56 | Data | 0 | 33.561 | 31.859 | 167.858 | 7.63 | 158.607 | 2236.08 | 25.84 | 47.894 | 6.41 | 1.291 | 4.126 | 8440.74 | 1.445 | 97.9 | 76.1 | 1453 | 23.95 | 5486.5 | 2707.5 | 2687.3 | 3941.8 | 1215.1 | 0.67054 | 5.419
2024-12-09 | 23:56 | Data | 0 | 33.858 | 32.177 | 167.903 | 7.63 | 158.607 | 2233.37 | 25.84 | 47.894 | 6.41 | 1.296 | 4.096 | 8445.26 | 1.776 | 97.9 | 76 | 1452 | 23.95 | 5489.4 | 2713.2 | 2687.6 | 3943.9 | 1215.1 | 0.6707 | 5.392
2024-12-09 | 23:56 | Data | 0 | 33.756 | 32.345 | 167.858 | 7.63 | 158.517 | 2233.37 | 25.84 | 47.804 | 6.41 | 1.294 | 4.115 | 8436.21 | 1.647 | 97.9 | 76.1 | 1452 | 23.95 | 5483.5 | 2684.1 | 2690.1 | 3932.3 | 1215.1 | 0.66429 | 5.41
2024-12-09 | 23:56 | Data | 0 | 33.642 | 32.028 | 167.903 | 7.63 | 158.652 | 2232.47 | 25.84 | 47.804 | 6.41 | 1.279 | 4.107 | 8440.74 | 1.816 | 97.9 | 76.3 | 1451 | 23.95 | 5486.5 | 2700.2 | 2685.2 | 3933 | 1215.1 | 0.66659 | 5.385
2024-12-09 | 23:57 | Data | 0 | 33.851 | 32.264 | 167.858 | 7.64 | 158.652 | 2235.18 | 25.84 | 47.894 | 6.41 | 1.282 | 4.122 | 8427.17 | 1.607 | 97.9 | 76.3 | 1453 | 23.95 | 5477.7 | 2689.9 | 2699 | 3935.4 | 1215.1 | 0.66044 | 5.404
2024-12-09 | 23:57 | Data | 0 | 34.02 | 32.379 | 167.993 | 7.63 | 158.607 | 2236.08 | 25.84 | 47.804 | 6.41 | 1.282 | 4.108 | 8458.83 | 1.823 | 97.9 | 76.2 | 1453 | 23.95 | 5498.2 | 2691.9 | 2700 | 3936.8 | 1215.1 | 0.66784 | 5.391
2024-12-09 | 23:57 | Data | 0 | 33.675 | 32.028 | 167.858 | 7.63 | 158.652 | 2238.79 | 25.84 | 47.894 | 6.41 | 1.287 | 4.113 | 8467.87 | 1.445 | 97.9 | 76.2 | 1455 | 23.95 | 5504.1 | 2670 | 2680.8 | 3911.1 | 1215.1 | 0.66303 | 5.4
2024-12-09 | 23:57 | Data | 0 | 34.094 | 32.102 | 167.903 | 7.64 | 158.652 | 2239.7 | 25.84 | 47.804 | 6.41 | 1.283 | 4.105 | 8458.83 | 1.614 | 97.9 | 76.2 | 1455 | 23.95 | 5498.2 | 2685.3 | 2698 | 3931.4 | 1215.1 | 0.66442 | 5.389
2024-12-09 | 23:57 | Data | 0 | 33.655 | 32.035 | 167.813 | 7.63 | 158.607 | 2239.7 | 25.84 | 48.165 | 6.4 | 1.285 | 4.091 | 8454.3 | 1.607 | 97.8 | 76.1 | 1456 | 24.08 | 5495.3 | 2708.7 | 2685.5 | 3937.7 | 1215.1 | 0.66898 | 5.376
2024-12-09 | 23:57 | Data | 0 | 33.642 | 32.028 | 167.722 | 7.64 | 158.562 | 2238.79 | 25.84 | 47.894 | 6.41 | 1.288 | 4.124 | 8445.26 | 1.614 | 97.9 | 76.2 | 1454 | 23.95 | 5489.4 | 2701.1 | 2650.5 | 3908.5 | 1215.1 | 0.6737 | 5.411
2024-12-09 | 23:57 | Data | 0 | 33.453 | 32.028 | 167.903 | 7.64 | 158.607 | 2235.18 | 25.84 | 47.804 | 6.41 | 1.279 | 4.101 | 8440.74 | 1.56 | 97.9 | 76.2 | 1453 | 23.95 | 5486.5 | 2681.7 | 2646.8 | 3896 | 1215.1 | 0.66923 | 5.38
2024-12-09 | 23:57 | Data | 0 | 33.655 | 32.028 | 167.813 | 7.64 | 158.607 | 2239.7 | 25.84 | 47.804 | 6.41 | 1.283 | 4.11 | 8436.21 | 1.62 | 97.9 | 76.2 | 1455 | 23.95 | 5483.5 | 2668.1 | 2647.3 | 3889 | 1215.1 | 0.66972 | 5.393
2024-12-09 | 23:57 | Data | 0 | 33.716 | 32.062 | 167.858 | 7.63 | 158.698 | 2238.79 | 25.84 | 47.894 | 6.41 | 1.276 | 4.088 | 8449.78 | 1.56 | 97.9 | 76.2 | 1455 | 23.95 | 5492.4 | 2704.6 | 2638.1 | 3903.3 | 1215.1 | 0.67503 | 5.365
2024-12-09 | 23:57 | Data | 0 | 33.932 | 32.062 | 167.948 | 7.64 | 158.698 | 2238.79 | 25.84 | 47.984 | 6.41 | 1.277 | 4.11 | 8467.87 | 1.614 | 97.9 | 76.3 | 1456 | 23.95 | 5504.1 | 2691.2 | 2656.4 | 3913 | 1215.1 | 0.66945 | 5.387
2024-12-09 | 23:57 | Data | 0 | 33.81 | 32.035 | 167.858 | 7.64 | 158.562 | 2236.98 | 25.84 | 47.984 | 6.41 | 1.282 | 4.109 | 8467.87 | 1.823 | 97.9 | 76.2 | 1454 | 23.99 | 5504.1 | 2715.1 | 2659.6 | 3925 | 1215.1 | 0.67542 | 5.39
2024-12-09 | 23:57 | Data | 0 | 33.871 | 31.866 | 167.813 | 7.63 | 158.607 | 2236.08 | 25.84 | 48.075 | 6.41 | 1.277 | 4.116 | 8458.83 | 1.769 | 97.9 | 76.3 | 1453 | 24.04 | 5498.2 | 2705.7 | 2669 | 3929.5 | 1215.1 | 0.67196 | 5.393
2024-12-09 | 23:57 | Data | 0 | 33.642 | 32.15 | 167.813 | 7.64 | 158.562 | 2236.08 | 25.84 | 48.255 | 6.41 | 1.294 | 4.102 | 8467.87 | 1.614 | 97.8 | 76 | 1453 | 24.08 | 5504.1 | 2703.9 | 2674.9 | 3931.3 | 1215.1 | 0.6693 | 5.395
2024-12-09 | 23:57 | Data | 0 | 33.696 | 32.028 | 167.722 | 7.64 | 158.607 | 2233.37 | 25.84 | 48.255 | 6.41 | 1.29 | 4.108 | 8427.17 | 1.62 | 97.8 | 76.1 | 1452 | 24.17 | 5477.7 | 2684.2 | 2685.1 | 3923.8 | 1215.1 | 0.66554 | 5.398
2024-12-09 | 23:57 | Data | 0 | 33.669 | 32.048 | 167.767 | 7.63 | 158.607 | 2230.66 | 25.84 | 48.165 | 6.41 | 1.277 | 4.094 | 8418.13 | 1.539 | 97.8 | 76.2 | 1449 | 24.08 | 5471.8 | 2670.9 | 2667.4 | 3905.3 | 1215.1 | 0.66443 | 5.372
2024-12-09 | 23:57 | Data | 0 | 33.75 | 32.251 | 167.858 | 7.63 | 158.562 | 2230.66 | 25.84 | 48.075 | 6.41 | 1.283 | 4.115 | 8418.13 | 1.62 | 97.8 | 76.2 | 1451 | 23.99 | 5471.8 | 2678.3 | 2645.1 | 3895.3 | 1215.1 | 0.67085 | 5.399
2024-12-09 | 23:58 | Data | 0 | 33.817 | 32.15 | 167.858 | 7.63 | 158.652 | 2233.37 | 25.83 | 48.075 | 6.4 | 1.294 | 4.145 | 8418.13 | 1.823 | 97.9 | 76.2 | 1452 | 23.99 | 5471.8 | 2712.2 | 2669.1 | 3926 | 1215.1 | 0.67156 | 5.439
2024-12-09 | 23:58 | Data | 0 | 34.074 | 32.318 | 167.903 | 7.63 | 158.652 | 2232.47 | 25.84 | 47.894 | 6.41 | 1.291 | 4.132 | 8427.17 | 1.607 | 97.9 | 76.2 | 1451 | 23.95 | 5477.7 | 2693.4 | 2636.2 | 3891.5 | 1215.1 | 0.67376 | 5.423
2024-12-09 | 23:58 | Data | 0 | 33.79 | 32.028 | 167.813 | 7.63 | 158.562 | 2232.47 | 25.84 | 47.894 | 6.41 | 1.293 | 4.105 | 8431.69 | 1.418 | 97.9 | 76 | 1451 | 23.95 | 5480.6 | 2706 | 2639.6 | 3903.4 | 1215.1 | 0.67543 | 5.399
2024-12-09 | 23:58 | Data | 0 | 33.642 | 32.237 | 167.813 | 7.64 | 158.652 | 2232.47 | 25.84 | 47.894 | 6.41 | 1.29 | 4.089 | 8458.83 | 1.546 | 97.9 | 76 | 1452 | 23.95 | 5498.2 | 2697.9 | 2631.9 | 3896.1 | 1215.1 | 0.67618 | 5.379
2024-12-09 | 23:58 | Data | 0 | 33.871 | 32.244 | 167.903 | 7.63 | 158.698 | 2230.66 | 25.83 | 47.894 | 6.41 | 1.287 | 4.079 | 8445.26 | 1.654 | 97.9 | 76 | 1450 | 23.95 | 5489.4 | 2715.5 | 2663.3 | 3922.4 | 1215.1 | 0.67257 | 5.366
2024-12-09 | 23:58 | Data | 0 | 33.642 | 32.028 | 167.858 | 7.64 | 158.652 | 2225.23 | 25.84 | 47.894 | 6.41 | 1.288 | 4.089 | 8400.04 | 1.614 | 97.8 | 76 | 1446 | 23.95 | 5460 | 2697 | 2661.3 | 3920.8 | 1215.1 | 0.6685 | 5.376
2024-12-09 | 23:58 | Data | 0 | 33.648 | 32.028 | 167.767 | 7.64 | 158.607 | 2229.75 | 25.84 | 47.894 | 6.41 | 1.282 | 4.081 | 8400.04 | 1.62 | 97.8 | 76.1 | 1449 | 23.99 | 5460 | 2688.2 | 2676.8 | 3919.1 | 1215.1 | 0.66728 | 5.363
2024-12-09 | 23:58 | Data | 0 | 33.75 | 31.812 | 167.767 | 7.64 | 158.517 | 2230.66 | 25.84 | 47.894 | 6.41 | 1.283 | 4.102 | 8400.04 | 1.769 | 97.9 | 76.2 | 1450 | 23.95 | 5460 | 2694 | 2670 | 3921.8 | 1215.1 | 0.67001 | 5.385
2024-12-09 | 23:58 | Data | 0 | 33.648 | 32.352 | 167.813 | 7.64 | 158.607 | 2230.66 | 25.84 | 47.894 | 6.41 | 1.289 | 4.108 | 8400.04 | 1.438 | 97.9 | 76.1 | 1449 | 23.99 | 5460 | 2693 | 2663.6 | 3913 | 1215.1 | 0.66974 | 5.398
2024-12-09 | 23:58 | Data | 0 | 33.871 | 32.156 | 167.858 | 7.63 | 158.698 | 2230.66 | 25.84 | 48.075 | 6.41 | 1.286 | 4.131 | 8427.17 | 1.715 | 97.8 | 76.3 | 1449 | 24.04 | 5477.7 | 1844.6 | 2165.6 | 2874.6 | 1215.1 | 0.62624 | 5.417
2024-12-09 | 23:58 | Data | 0 | 33.669 | 32.035 | 167.767 | 7.63 | 158.607 | 2230.66 | 25.83 | 48.165 | 6.41 | 1.282 | 4.119 | 8431.69 | 1.614 | 97.8 | 76.3 | 1450 | 24.08 | 5480.6 | 1600.6 | 2026.3 | 2587.8 | 1215.1 | 0.61302 | 5.401
2024-12-09 | 23:58 | Data | 0 | 33.493 | 32.237 | 167.903 | 7.63 | 158.698 | 2232.47 | 25.84 | 48.165 | 6.41 | 1.282 | 4.098 | 8427.17 | 1.384 | 97.8 | 76.2 | 1451 | 24.08 | 5477.7 | 1626.3 | 2057.5 | 2636.5 | 1215.1 | 0.61357 | 5.379
2024-12-09 | 23:58 | Data | 0 | 33.864 | 32.258 | 167.813 | 7.63 | 158.652 | 2233.37 | 25.84 | 47.804 | 6.41 | 1.282 | 4.103 | 8422.65 | 1.411 | 97.9 | 76.2 | 1452 | 23.95 | 5474.7 | 1613.2 | 2066.2 | 2636.4 | 1215.1 | 0.60878 | 5.384
2024-12-09 | 23:58 | Data | 0 | 33.642 | 32.278 | 167.903 | 7.64 | 158.652 | 2234.27 | 25.84 | 47.894 | 6.41 | 1.284 | 4.128 | 8422.65 | 1.533 | 97.9 | 76.3 | 1451 | 23.95 | 5474.7 | 1607 | 2074.1 | 2638.1 | 1215.1 | 0.60585 | 5.412
2024-12-09 | 23:58 | Data | 0 | 34.04 | 32.17 | 168.084 | 7.64 | 158.698 | 2233.37 | 25.84 | 47.894 | 6.41 | 1.282 | 4.101 | 8445.26 | 1.614 | 97.9 | 76.2 | 1452 | 23.95 | 5489.4 | 1609.4 | 2082.1 | 2643.6 | 1215.1 | 0.60617 | 5.382
2024-12-09 | 23:58 | Data | 0 | 33.844 | 32.143 | 167.858 | 7.63 | 158.607 | 2231.56 | 25.84 | 47.984 | 6.41 | 1.291 | 4.109 | 8440.74 | 1.607 | 97.9 | 76.1 | 1450 | 23.95 | 5486.5 | 1614.7 | 2065.7 | 2635.4 | 1215.1 | 0.61086 | 5.399
2024-12-09 | 23:58 | Data | 0 | 33.642 | 32.028 | 167.858 | 7.63 | 158.607 | 2227.95 | 25.84 | 47.894 | 6.41 | 1.285 | 4.11 | 8445.26 | 1.614 | 97.8 | 76.2 | 1448 | 23.99 | 5489.4 | 1624.7 | 2056.7 | 2633.8 | 1215.1 | 0.61412 | 5.395
2024-12-09 | 23:58 | Data | 0 | 33.871 | 32.055 | 167.767 | 7.64 | 158.607 | 2229.75 | 25.84 | 47.894 | 6.41 | 1.29 | 4.105 | 8454.3 | 1.553 | 97.9 | 76.1 | 1449 | 23.9 | 5495.3 | 1607.7 | 2074.8 | 2637.9 | 1215.2 | 0.60641 | 5.395
2024-12-09 | 23:59 | Data | 0 | 33.844 | 32.433 | 167.948 | 7.63 | 158.698 | 2229.75 | 25.84 | 47.894 | 6.41 | 1.289 | 4.102 | 8454.3 | 1.695 | 97.9 | 76.1 | 1449 | 23.95 | 5495.3 | 1595 | 2063.2 | 2622.4 | 1215.2 | 0.60547 | 5.391
2024-12-09 | 23:59 | Data | 0 | 33.75 | 32.035 | 167.858 | 7.64 | 158.562 | 2229.75 | 25.84 | 47.894 | 6.41 | 1.29 | 4.118 | 8454.3 | 1.62 | 97.9 | 76.2 | 1449 | 23.95 | 5495.3 | 1639.2 | 2077.1 | 2658.9 | 1215.2 | 0.61349 | 5.407
2024-12-09 | 23:59 | Data | 0 | 33.858 | 32.278 | 167.993 | 7.63 | 158.652 | 2229.75 | 25.84 | 47.984 | 6.41 | 1.284 | 4.11 | 8454.3 | 1.796 | 97.8 | 76.2 | 1450 | 23.99 | 5495.3 | 1619.3 | 2068.9 | 2641.3 | 1215.2 | 0.60966 | 5.394
2024-12-09 | 23:59 | Data | 0 | 33.642 | 32.028 | 167.813 | 7.64 | 158.562 | 2232.47 | 25.84 | 48.255 | 6.41 | 1.272 | 4.122 | 8440.74 | 1.614 | 97.8 | 76.4 | 1451 | 24.08 | 5486.5 | 1617.7 | 2086.4 | 2653.9 | 1215.2 | 0.60518 | 5.392
2024-12-09 | 23:59 | Data | 0 | 33.675 | 32.258 | 167.813 | 7.63 | 158.652 | 2227.95 | 25.83 | 48.165 | 6.41 | 1.277 | 4.124 | 8440.74 | 1.566 | 97.8 | 76.4 | 1448 | 24.04 | 5486.5 | 1627.1 | 2102.5 | 2671.5 | 1215.2 | 0.60605 | 5.4
2024-12-09 | 23:59 | Data | 0 | 33.871 | 32.143 | 167.858 | 7.64 | 158.698 | 2231.56 | 25.84 | 48.075 | 6.41 | 1.291 | 4.115 | 8445.26 | 1.519 | 97.8 | 76.1 | 1451 | 24.08 | 5489.4 | 1620.2 | 2094.3 | 2660.9 | 1215.2 | 0.60663 | 5.406
2024-12-09 | 23:59 | Data | 0 | 33.669 | 32.035 | 167.813 | 7.64 | 158.607 | 2235.18 | 25.84 | 48.075 | 6.41 | 1.282 | 4.127 | 8436.21 | 1.614 | 97.8 | 76.3 | 1453 | 24.04 | 5483.5 | 1606.1 | 2076.7 | 2640.3 | 1215.2 | 0.60497 | 5.408
2024-12-09 | 23:59 | Data | 0 | 34.04 | 32.17 | 167.903 | 7.63 | 158.652 | 2238.79 | 25.83 | 47.984 | 6.41 | 1.273 | 4.127 | 8440.74 | 1.593 | 97.9 | 76.4 | 1455 | 23.95 | 5486.5 | 1636.7 | 2087.1 | 2665.1 | 1215.2 | 0.61086 | 5.401
2024-12-09 | 23:59 | Data | 0 | 33.783 | 32.035 | 167.858 | 7.64 | 158.607 | 2240.6 | 25.84 | 47.894 | 6.41 | 1.278 | 4.103 | 8440.74 | 1.445 | 97.9 | 76.2 | 1456 | 23.95 | 5486.5 | 1601.9 | 2058.3 | 2622 | 1215.2 | 0.60796 | 5.382
2024-12-09 | 23:59 | Data | 0 | 33.858 | 32.264 | 167.903 | 7.64 | 158.652 | 2239.7 | 25.84 | 47.984 | 6.41 | 1.28 | 4.115 | 8445.26 | 1.607 | 97.9 | 76.3 | 1455 | 23.95 | 5489.4 | 1664.3 | 2062.7 | 2664.4 | 1215.2 | 0.6234 | 5.395
2024-12-09 | 23:59 | Data | 0 | 33.642 | 32.028 | 167.767 | 7.63 | 158.517 | 2240.6 | 25.84 | 47.894 | 6.41 | 1.285 | 4.115 | 8445.26 | 1.614 | 97.9 | 76.2 | 1456 | 23.95 | 5489.4 | 1652.1 | 2086.9 | 2674.8 | 1215.2 | 0.61468 | 5.399
2024-12-09 | 23:59 | Data | 0 | 33.871 | 32.264 | 167.948 | 7.64 | 158.698 | 2241.5 | 25.84 | 47.894 | 6.4 | 1.282 | 4.119 | 8427.17 | 1.607 | 97.9 | 76.3 | 1457 | 23.95 | 5477.7 | 1619.7 | 2057 | 2632.3 | 1215.2 | 0.61253 | 5.401
2024-12-09 | 23:59 | Data | 0 | 33.642 | 31.832 | 167.813 | 7.64 | 158.607 | 2241.5 | 25.84 | 47.894 | 6.41 | 1.285 | 4.132 | 8458.83 | 1.782 | 97.9 | 76.3 | 1458 | 23.95 | 5498.2 | 1622 | 2091.1 | 2663.4 | 1215.2 | 0.60544 | 5.415
2024-12-09 | 23:59 | Data | 0 | 34.074 | 32.042 | 167.948 | 7.64 | 158.652 | 2244.22 | 25.84 | 47.894 | 6.41 | 1.288 | 4.122 | 8445.26 | 1.782 | 97.9 | 76.2 | 1459 | 23.95 | 5489.4 | 1622.3 | 2106.5 | 2672.4 | 1215.2 | 0.60551 | 5.409
2024-12-09 | 23:59 | Data | 0 | 33.419 | 32.028 | 167.767 | 7.64 | 158.607 | 2240.6 | 25.84 | 47.894 | 6.41 | 1.292 | 4.121 | 8445.26 | 1.512 | 97.9 | 76.1 | 1456 | 23.95 | 5489.4 | 1641.1 | 2119.3 | 2695.8 | 1215.2 | 0.60515 | 5.413
2024-12-09 | 23:59 | Data | 0 | 33.925 | 32.035 | 167.858 | 7.63 | 158.607 | 2241.5 | 25.84 | 47.894 | 6.41 | 1.288 | 4.096 | 8445.26 | 1.661 | 97.9 | 76.1 | 1457 | 23.95 | 5489.4 | 1628.4 | 2114.2 | 2682.7 | 1215.2 | 0.6043 | 5.384
2024-12-09 | 23:59 | Data | 0 | 33.716 | 31.839 | 167.948 | 7.64 | 158.652 | 2241.5 | 25.84 | 47.894 | 6.4 | 1.284 | 4.114 | 8440.74 | 1.533 | 97.9 | 76.2 | 1457 | 23.9 | 5486.5 | 1635.6 | 2093.7 | 2669.4 | 1215.2 | 0.60921 | 5.397
2024-12-09 | 24:00 | Data | 0 | 33.648 | 32.055 | 167.903 | 7.64 | 158.562 | 2241.5 | 25.85 | 47.894 | 6.41 | 1.286 | 4.116 | 8431.69 | 1.627 | 97.9 | 76.2 | 1456 | 23.95 | 5480.6 | 1629.8 | 2101.4 | 2676.5 | 1215.2 | 0.60658 | 5.402
2024-12-09 | 24:00 | Data | 0 | 33.642 | 32.028 | 167.722 | 7.63 | 158.607 | 2241.5 | 25.84 | 47.894 | 6.41 | 1.283 | 4.118 | 8445.26 | 1.614 | 97.9 | 76.2 | 1457 | 23.95 | 5489.4 | 1651.9 | 2098.7 | 2684.5 | 1215.2 | 0.61243 | 5.4
2024-12-09 | 24:00 | Data | 0 | 33.871 | 32.096 | 167.903 | 7.64 | 158.652 | 2243.31 | 25.83 | 47.894 | 6.41 | 1.29 | 4.123 | 8418.13 | 1.708 | 97.9 | 76.2 | 1458 | 23.95 | 5471.8 | 1625.7 | 2075.1 | 2648.9 | 1215.2 | 0.61356 | 5.412
2024-12-09 | 24:00 | Data | 0 | 33.642 | 32.143 | 167.858 | 7.64 | 158.562 | 2243.31 | 25.84 | 47.894 | 6.4 | 1.285 | 4.12 | 8409.08 | 1.614 | 97.9 | 76.2 | 1459 | 23.95 | 5465.9 | 1637.9 | 2052.6 | 2639.2 | 1215.2 | 0.61753 | 5.405
2024-12-09 | 24:00 | Data | 0 | 33.844 | 32.089 | 167.858 | 7.64 | 158.562 | 2242.41 | 25.83 | 47.894 | 6.42 | 1.292 | 4.132 | 8418.13 | 1.749 | 97.9 | 76.2 | 1458 | 23.95 | 5471.8 | 1625.7 | 2064.1 | 2644.3 | 1215.2 | 0.61227 | 5.424
2024-12-09 | 24:00 | Data | 0 | 33.77 | 32.042 | 167.767 | 7.64 | 158.562 | 2244.22 | 25.84 | 47.894 | 6.41 | 1.289 | 4.124 | 8436.21 | 1.735 | 97.9 | 76.2 | 1459 | 23.95 | 5483.5 | 1647 | 2041.6 | 2637.8 | 1215.2 | 0.62203 | 5.411
2024-12-09 | 24:00 | Data | 0 | 33.642 | 32.116 | 167.767 | 7.64 | 158.517 | 2241.5 | 25.84 | 48.075 | 6.41 | 1.278 | 4.082 | 8454.3 | 1.722 | 97.9 | 76.2 | 1457 | 24.04 | 5495.3 | 1643.2 | 2045.8 | 2639 | 1215.2 | 0.61955 | 5.36
2024-12-09 | 24:00 | Data | 0 | 33.412 | 31.826 | 167.767 | 7.63 | 158.472 | 2241.5 | 25.84 | 47.894 | 6.41 | 1.274 | 4.092 | 8458.83 | 1.755 | 97.9 | 76.3 | 1457 | 23.95 | 5498.2 | 1653.2 | 2060.1 | 2653.5 | 1215.2 | 0.62078 | 5.366
2024-12-09 | 24:00 | Data | 0 | 33.615 | 32.251 | 167.858 | 7.63 | 158.607 | 2240.6 | 25.84 | 47.894 | 6.41 | 1.289 | 4.131 | 8458.83 | 1.6 | 97.9 | 76.2 | 1456 | 23.95 | 5498.2 | 1636.3 | 2071.6 | 2654.5 | 1215.2 | 0.61261 | 5.419
2024-12-10 | 0:00 | Data | 0 | 33.412 | 31.974 | 167.677 | 7.63 | 158.517 | 2241.5 | 25.83 | 47.984 | 6.41 | 1.282 | 4.115 | 8454.3 | 1.614 | 97.9 | 76.2 | 1457 | 23.9 | 5495.3 | 1633.1 | 2074.5 | 2654.2 | 1215.2 | 0.6113 | 5.397
2024-12-10 | 0:00 | Data | 0 | 33.628 | 32.42 | 167.767 | 7.64 | 158.562 | 2238.79 | 25.84 | 47.894 | 6.41 | 1.291 | 4.062 | 8427.17 | 1.614 | 97.9 | 75.9 | 1456 | 23.95 | 5477.7 | 1604.6 | 2094.7 | 2652.4 | 1215.2 | 0.60251 | 5.354
2024-12-10 | 0:00 | Data | 0 | 33.419 | 32.028 | 167.767 | 7.63 | 158.562 | 2244.22 | 25.84 | 47.894 | 6.41 | 1.292 | 4.069 | 8427.17 | 1.56 | 97.9 | 75.9 | 1459 | 23.95 | 5477.7 | 1609.8 | 2088.5 | 2650.9 | 1215.2 | 0.60411 | 5.361
2024-12-10 | 0:00 | Data | 0 | 33.615 | 31.812 | 167.722 | 7.64 | 158.472 | 2238.79 | 25.84 | 47.984 | 6.41 | 1.28 | 4.082 | 8418.13 | 1.782 | 97.9 | 76.1 | 1455 | 23.95 | 5471.8 | 1626.7 | 2095.1 | 2663.9 | 1215.2 | 0.60739 | 5.363
2024-12-10 | 0:00 | Data | 0 | 33.446 | 31.799 | 167.722 | 7.63 | 158.472 | 2238.79 | 25.84 | 47.894 | 6.41 | 1.288 | 4.118 | 8431.69 | 1.614 | 97.9 | 76.2 | 1456 | 23.9 | 5480.6 | 1610.7 | 2128 | 2683.4 | 1215.2 | 0.59785 | 5.403
2024-12-10 | 0:00 | Data | 0 | 33.527 | 32.305 | 167.813 | 7.64 | 158.517 | 2241.5 | 25.84 | 47.894 | 6.41 | 1.284 | 4.148 | 8422.65 | 1.614 | 97.9 | 76.4 | 1457 | 23.99 | 5474.7 | 1630.6 | 2108.1 | 2679.1 | 1215.2 | 0.60582 | 5.432
2024-12-10 | 0:00 | Data | 0 | 33.588 | 32.021 | 167.677 | 7.64 | 158.472 | 2238.79 | 25.85 | 47.984 | 6.4 | 1.279 | 4.118 | 8400.04 | 1.614 | 97.9 | 76.3 | 1456 | 23.95 | 5460 | 1617.7 | 2091.5 | 2656.1 | 1215.2 | 0.60652 | 5.397
2024-12-10 | 0:00 | Data | 0 | 33.426 | 32.028 | 167.722 | 7.64 | 158.517 | 2238.79 | 25.84 | 47.894 | 6.41 | 1.272 | 4.095 | 8400.04 | 1.587 | 97.9 | 76.3 | 1455 | 23.95 | 5460 | 1625.2 | 2105.6 | 2673.2 | 1215.2 | 0.60498 | 5.367
2024-12-10 | 0:00 | Data | 0 | 33.682 | 32.089 | 167.767 | 7.63 | 158.562 | 2235.18 | 25.84 | 47.894 | 6.41 | 1.278 | 4.087 | 8418.13 | 1.512 | 97.9 | 76.2 | 1453 | 23.95 | 5471.8 | 1609.9 | 2052.7 | 2622.7 | 1215.2 | 0.61045 | 5.365
2024-12-10 | 0:00 | Data | 0 | 33.446 | 31.826 | 167.767 | 7.63 | 158.517 | 2236.08 | 25.84 | 47.804 | 6.41 | 1.286 | 4.112 | 8418.13 | 1.519 | 97.9 | 76.2 | 1453 | 23.9 | 5471.8 | 1618.5 | 2044.9 | 2621.7 | 1215.2 | 0.61475 | 5.398
2024-12-10 | 0:01 | Data | 0 | 33.642 | 32.028 | 167.722 | 7.63 | 158.472 | 2235.18 | 25.84 | 47.894 | 6.41 | 1.286 | 4.101 | 8418.13 | 1.614 | 97.9 | 76.1 | 1453 | 23.95 | 5471.8 | 1629.9 | 2061.9 | 2644.9 | 1215.2 | 0.6127 | 5.388
2024-12-10 | 0:01 | Data | 0 | 33.642 | 31.988 | 167.722 | 7.63 | 158.426 | 2236.08 | 25.84 | 47.894 | 6.41 | 1.287 | 4.105 | 8404.56 | 1.654 | 97.9 | 76.1 | 1453 | 23.95 | 5463 | 1638 | 2089.6 | 2667.5 | 1215.2 | 0.61132 | 5.392
2024-12-10 | 0:01 | Data | 0 | 33.318 | 31.799 | 167.767 | 7.63 | 158.517 | 2236.08 | 25.83 | 47.894 | 6.41 | 1.282 | 4.119 | 8418.13 | 1.587 | 97.9 | 76.3 | 1453 | 23.95 | 5471.8 | 1634.3 | 2103 | 2676.9 | 1215.2 | 0.61084 | 5.402
2024-12-10 | 0:01 | Data | 0 | 33.635 | 31.913 | 167.722 | 7.64 | 158.426 | 2232.47 | 25.84 | 47.894 | 6.41 | 1.286 | 4.129 | 8422.65 | 1.614 | 97.9 | 76.3 | 1452 | 23.95 | 5474.7 | 1619.4 | 2077.2 | 2648 | 1215.2 | 0.60906 | 5.415
2024-12-10 | 0:01 | Data | 0 | 33.642 | 32.143 | 167.813 | 7.64 | 158.562 | 2233.37 | 25.84 | 47.894 | 6.41 | 1.283 | 4.134 | 8400.04 | 1.614 | 97.9 | 76.3 | 1451 | 23.95 | 5460 | 1647.3 | 2120.7 | 2698.7 | 1215.2 | 0.60711 | 5.418
2024-12-10 | 0:01 | Data | 0 | 33.446 | 32.028 | 167.813 | 7.63 | 158.562 | 2232.47 | 25.83 | 47.984 | 6.41 | 1.286 | 4.119 | 8418.13 | 1.391 | 97.9 | 76.2 | 1452 | 23.95 | 5471.8 | 1655.2 | 2107.1 | 2692 | 1215.2 | 0.61251 | 5.406
2024-12-10 | 0:01 | Data | 0 | 33.527 | 32.028 | 167.722 | 7.63 | 158.517 | 2232.47 | 25.83 | 47.894 | 6.41 | 1.29 | 4.103 | 8400.04 | 1.614 | 97.9 | 76.1 | 1451 | 23.99 | 5460 | 1634.8 | 2121.3 | 2692.6 | 1215.2 | 0.60472 | 5.393
2024-12-10 | 0:01 | Data | 0 | 33.642 | 32.028 | 167.813 | 7.64 | 158.472 | 2233.37 | 25.84 | 47.804 | 6.41 | 1.289 | 4.095 | 8431.69 | 1.499 | 97.9 | 76.1 | 1452 | 23.95 | 5480.6 | 2945.6 | 3214.3 | 4443.9 | 1215.2 | 0.63685 | 5.383
2024-12-10 | 0:01 | Data | 0 | 33.635 | 32.021 | 167.586 | 7.64 | 158.426 | 2232.47 | 25.84 | 47.894 | 6.41 | 1.272 | 4.108 | 8418.13 | 1.634 | 97.9 | 76.4 | 1451 | 23.95 | 5471.8 | 2703.4 | 2700.1 | 3947.7 | 1215.2 | 0.66697 | 5.381
2024-12-10 | 0:01 | Data | 0 | 33.743 | 32.028 | 167.767 | 7.63 | 158.472 | 2233.37 | 25.85 | 47.894 | 6.41 | 1.276 | 4.084 | 8418.13 | 1.634 | 97.9 | 76.2 | 1451 | 23.95 | 5471.8 | 2696.1 | 2696.1 | 3945.5 | 1215.2 | 0.66739 | 5.362
2024-12-10 | 0:01 | Data | 0 | 33.642 | 32.028 | 167.632 | 7.64 | 158.426 | 2232.47 | 25.84 | 47.894 | 6.41 | 1.272 | 4.086 | 8409.08 | 1.614 | 97.9 | 76.2 | 1451 | 23.95 | 5465.9 | 2703.9 | 2659.7 | 3927.9 | 1215.2 | 0.67013 | 5.359
2024-12-10 | 0:01 | Data | 0 | 33.682 | 31.853 | 167.813 | 7.64 | 158.562 | 2233.37 | 25.84 | 47.894 | 6.41 | 1.283 | 4.098 | 8418.13 | 1.803 | 97.9 | 76.1 | 1452 | 23.95 | 5471.8 | 2699.9 | 2658.7 | 3918.8 | 1215.2 | 0.67195 | 5.382
2024-12-10 | 0:01 | Data | 0 | 33.635 | 31.812 | 167.767 | 7.63 | 158.472 | 2232.47 | 25.83 | 47.894 | 6.41 | 1.291 | 4.092 | 8431.69 | 1.735 | 97.9 | 76 | 1452 | 23.95 | 5480.6 | 2697.4 | 2662.6 | 3920 | 1215.2 | 0.67007 | 5.383
2024-12-10 | 0:01 | Data | 0 | 33.419 | 31.799 | 167.677 | 7.63 | 158.472 | 2232.47 | 25.84 | 47.894 | 6.41 | 1.294 | 4.093 | 8431.69 | 1.614 | 97.9 | 76 | 1451 | 23.95 | 5480.6 | 2713.3 | 2698 | 3953.1 | 1215.2 | 0.66931 | 5.387
2024-12-10 | 0:01 | Data | 0 | 33.642 | 31.859 | 167.767 | 7.63 | 158.517 | 2234.27 | 25.84 | 47.804 | 6.41 | 1.289 | 4.111 | 8431.69 | 1.715 | 97.9 | 76.1 | 1453 | 23.95 | 5480.6 | 2708.8 | 2705.3 | 3960.1 | 1215.2 | 0.66455 | 5.399
2024-12-10 | 0:01 | Data | 0 | 33.635 | 31.913 | 167.722 | 7.63 | 158.472 | 2236.08 | 25.84 | 47.984 | 6.41 | 1.273 | 4.116 | 8431.69 | 1.614 | 97.9 | 76.4 | 1453 | 23.99 | 5480.6 | 2705.5 | 2720.2 | 3967 | 1215.2 | 0.66422 | 5.392
2024-12-10 | 0:01 | Data | 0 | 33.419 | 31.913 | 167.722 | 7.64 | 158.517 | 2230.66 | 25.84 | 48.165 | 6.41 | 1.279 | 4.111 | 8418.13 | 1.607 | 97.8 | 76.3 | 1450 | 24.04 | 5471.8 | 2681.7 | 2707 | 3945.7 | 1215.2 | 0.66248 | 5.389
2024-12-10 | 0:02 | Data | 0 | 33.304 | 31.967 | 167.632 | 7.63 | 158.517 | 2233.37 | 25.84 | 48.165 | 6.41 | 1.29 | 4.116 | 8427.17 | 1.587 | 97.8 | 76.1 | 1452 | 24.08 | 5477.7 | 2725.9 | 2699.7 | 3961.7 | 1215.2 | 0.67008 | 5.405
2024-12-10 | 0:02 | Data | 0 | 33.615 | 31.846 | 167.722 | 7.64 | 158.426 | 2236.08 | 25.84 | 48.255 | 6.41 | 1.286 | 4.101 | 8431.69 | 1.654 | 97.8 | 76.1 | 1453 | 24.08 | 5480.6 | 2708.6 | 2667.8 | 3927.5 | 1215.2 | 0.67327 | 5.387
2024-12-10 | 0:02 | Data | 0 | 33.351 | 31.792 | 167.541 | 7.64 | 158.291 | 2236.08 | 25.83 | 48.165 | 6.41 | 1.282 | 4.103 | 8427.17 | 1.701 | 97.8 | 76.2 | 1453 | 24.04 | 5477.7 | 2671.8 | 2666 | 3902.6 | 1215.2 | 0.66598 | 5.384
2024-12-10 | 0:02 | Data | 0 | 33.297 | 31.792 | 167.541 | 7.64 | 158.336 | 2236.08 | 25.83 | 48.165 | 6.41 | 1.291 | 4.076 | 8427.17 | 1.614 | 97.8 | 75.9 | 1453 | 24.08 | 5477.7 | 2699.9 | 2657.3 | 3920.1 | 1215.3 | 0.67042 | 5.366
2024-12-10 | 0:02 | Data | 0 | 33.338 | 31.859 | 167.586 | 7.63 | 158.472 | 2235.18 | 25.84 | 48.165 | 6.4 | 1.284 | 4.097 | 8418.13 | 1.512 | 97.8 | 76.1 | 1453 | 24.04 | 5471.8 | 2695.4 | 2654.8 | 3919.9 | 1215.3 | 0.66845 | 5.381
2024-12-10 | 0:02 | Data | 0 | 33.331 | 31.805 | 167.541 | 7.64 | 158.472 | 2238.79 | 25.84 | 48.165 | 6.41 | 1.285 | 4.098 | 8440.74 | 1.398 | 97.8 | 76.1 | 1455 | 24.08 | 5486.5 | 2695.3 | 2672.6 | 3935.2 | 1215.3 | 0.67014 | 5.383
2024-12-10 | 0:02 | Data | 0 | 33.419 | 32.015 | 167.767 | 7.64 | 158.562 | 2244.22 | 25.84 | 48.165 | 6.41 | 1.282 | 4.111 | 8445.26 | 1.526 | 97.9 | 76.2 | 1459 | 24.08 | 5489.4 | 2687.2 | 2667.4 | 3922.9 | 1215.3 | 0.66732 | 5.394
2024-12-10 | 0:02 | Data | 0 | 33.331 | 32.001 | 167.722 | 7.64 | 158.517 | 2244.22 | 25.84 | 48.165 | 6.4 | 1.279 | 4.119 | 8418.13 | 1.398 | 97.9 | 76.3 | 1459 | 24.08 | 5471.8 | 2722 | 2671.8 | 3943.6 | 1215.3 | 0.67404 | 5.4
2024-12-10 | 0:02 | Data | 0 | 33.581 | 31.907 | 167.677 | 7.64 | 158.472 | 2243.31 | 25.84 | 48.165 | 6.41 | 1.282 | 4.121 | 8404.56 | 1.634 | 97.9 | 76.3 | 1459 | 24.04 | 5463 | 2712.6 | 2700.9 | 3951.7 | 1215.3 | 0.66942 | 5.402
2024-12-10 | 0:02 | Data | 0 | 33.642 | 32.001 | 167.767 | 7.64 | 158.517 | 2247.83 | 25.84 | 48.165 | 6.41 | 1.284 | 4.096 | 8409.08 | 1.715 | 97.9 | 76.1 | 1461 | 24.04 | 5465.9 | 2697.8 | 2680.5 | 3931 | 1215.3 | 0.66757 | 5.38
2024-12-10 | 0:02 | Data | 0 | 33.588 | 31.805 | 167.722 | 7.63 | 158.472 | 2248.73 | 25.84 | 48.165 | 6.41 | 1.29 | 4.105 | 8386.47 | 1.83 | 97.9 | 76.1 | 1462 | 24.08 | 5451.2 | 2709.6 | 2680 | 3942.5 | 1215.3 | 0.66994 | 5.394
2024-12-10 | 0:02 | Data | 0 | 33.608 | 31.805 | 167.677 | 7.64 | 158.426 | 2249.64 | 25.84 | 48.165 | 6.41 | 1.282 | 4.108 | 8372.9 | 1.796 | 97.9 | 76.2 | 1462 | 24.08 | 5442.4 | 2680.8 | 2700.1 | 3938 | 1215.3 | 0.66287 | 5.392
2024-12-10 | 0:02 | Data | 0 | 33.756 | 31.859 | 167.858 | 7.63 | 158.517 | 2249.64 | 25.83 | 48.165 | 6.41 | 1.279 | 4.096 | 8386.47 | 1.519 | 97.9 | 76.2 | 1462 | 24.08 | 5451.2 | 2687.5 | 2688.1 | 3929.1 | 1215.3 | 0.66586 | 5.373
2024-12-10 | 0:02 | Data | 0 | 33.628 | 32.251 | 167.677 | 7.64 | 158.517 | 2248.73 | 25.84 | 48.165 | 6.41 | 1.278 | 4.109 | 8386.47 | 1.607 | 97.9 | 76.3 | 1462 | 24.08 | 5451.2 | 2676.3 | 2675 | 3919.5 | 1215.3 | 0.66439 | 5.387
2024-12-10 | 0:02 | Data | 0 | 33.439 | 31.799 | 167.632 | 7.64 | 158.472 | 2247.83 | 25.84 | 48.165 | 6.4 | 1.276 | 4.111 | 8381.95 | 1.614 | 97.9 | 76.3 | 1461 | 24.08 | 5448.3 | 2692.9 | 2645.1 | 3904.3 | 1215.3 | 0.67225 | 5.387
2024-12-10 | 0:02 | Data | 0 | 33.554 | 31.974 | 167.677 | 7.63 | 158.517 | 2244.22 | 25.84 | 48.165 | 6.4 | 1.284 | 4.094 | 8400.04 | 1.492 | 97.9 | 76.1 | 1459 | 24.08 | 5460 | 2727.3 | 2652.3 | 3928 | 1215.3 | 0.6739 | 5.378
2024-12-10 | 0:02 | Data | 0 | 33.635 | 31.812 | 167.586 | 7.63 | 158.426 | 2244.22 | 25.84 | 48.165 | 6.41 | 1.284 | 4.089 | 8395.51 | 1.816 | 97.9 | 76.1 | 1459 | 24.04 | 5457.1 | 2708.6 | 2627.5 | 3901.3 | 1215.3 | 0.67711 | 5.373
2024-12-10 | 0:02 | Data | 0 | 33.419 | 32.244 | 167.813 | 7.64 | 158.562 | 2246.02 | 25.84 | 48.165 | 6.41 | 1.277 | 4.091 | 8395.51 | 1.539 | 97.9 | 76.2 | 1460 | 24.08 | 5457.1 | 2718.8 | 2645.3 | 3916.4 | 1215.3 | 0.67742 | 5.368
2024-12-10 | 0:03 | Data | 0 | 33.743 | 32.197 | 167.858 | 7.63 | 158.517 | 2241.5 | 25.84 | 48.165 | 6.41 | 1.277 | 4.103 | 8400.04 | 1.661 | 97.8 | 76.3 | 1457 | 24.13 | 5460 | 2697.2 | 2654.2 | 3910.6 | 1215.3 | 0.67152 | 5.38
2024-12-10 | 0:03 | Data | 0 | 33.642 | 32.028 | 167.767 | 7.64 | 158.517 | 2244.22 | 25.84 | 48.165 | 6.41 | 1.282 | 4.097 | 8404.56 | 1.614 | 97.9 | 76.2 | 1459 | 24.04 | 5463 | 2690.2 | 2668.9 | 3925.7 | 1215.3 | 0.66722 | 5.377
2024-12-10 | 0:03 | Data | 0 | 33.844 | 32.143 | 167.858 | 7.63 | 158.517 | 2241.5 | 25.84 | 48.165 | 6.4 | 1.282 | 4.111 | 8418.13 | 1.6 | 97.9 | 76.2 | 1458 | 24.08 | 5471.8 | 2714.9 | 2671.4 | 3936.7 | 1215.3 | 0.67076 | 5.392
2024-12-10 | 0:03 | Data | 0 | 33.419 | 31.974 | 167.677 | 7.63 | 158.517 | 2242.41 | 25.85 | 48.075 | 6.4 | 1.275 | 4.096 | 8409.08 | 1.499 | 97.9 | 76.2 | 1457 | 24.08 | 5465.9 | 2710.2 | 2692.2 | 3944.5 | 1215.3 | 0.66891 | 5.372
2024-12-10 | 0:03 | Data | 0 | 33.642 | 32.251 | 167.722 | 7.64 | 158.562 | 2242.41 | 25.83 | 47.984 | 6.4 | 1.278 | 4.105 | 8418.13 | 1.593 | 97.9 | 76.3 | 1458 | 23.99 | 5471.8 | 2681.3 | 2701.4 | 3937.4 | 1215.3 | 0.66275 | 5.382
2024-12-10 | 0:03 | Data | 0 | 33.581 | 31.853 | 167.722 | 7.63 | 158.472 | 2242.41 | 25.84 | 47.894 | 6.41 | 1.272 | 4.099 | 8427.17 | 1.776 | 97.9 | 76.3 | 1458 | 23.95 | 5477.7 | 2698.8 | 2691.5 | 3944.7 | 1215.3 | 0.66226 | 5.371
2024-12-10 | 0:03 | Data | 0 | 33.419 | 31.826 | 167.722 | 7.64 | 158.426 | 2241.5 | 25.84 | 47.894 | 6.41 | 1.282 | 4.125 | 8427.17 | 1.553 | 97.9 | 76.3 | 1457 | 23.95 | 5477.7 | 2721.7 | 2678.8 | 3942.7 | 1215.3 | 0.6735 | 5.408
2024-12-10 | 0:03 | Data | 0 | 33.628 | 31.927 | 167.722 | 7.64 | 158.426 | 2240.6 | 25.84 | 47.894 | 6.4 | 1.274 | 4.136 | 8431.69 | 1.641 | 97.9 | 76.4 | 1457 | 23.95 | 5480.6 | 2720.2 | 2673 | 3938.7 | 1215.3 | 0.67355 | 5.411
2024-12-10 | 0:03 | Data | 0 | 33.412 | 31.974 | 167.677 | 7.63 | 158.472 | 2238.79 | 25.84 | 47.894 | 6.41 | 1.278 | 4.121 | 8436.21 | 1.614 | 97.9 | 76.3 | 1455 | 23.9 | 5483.5 | 2702 | 2664.6 | 3921.9 | 1215.3 | 0.67172 | 5.4
2024-12-10 | 0:03 | Data | 0 | 33.527 | 31.805 | 167.586 | 7.64 | 158.381 | 2238.79 | 25.84 | 47.984 | 6.4 | 1.279 | 4.101 | 8427.17 | 1.62 | 97.9 | 76.2 | 1455 | 23.95 | 5477.7 | 2682.6 | 2670.7 | 3921.7 | 1215.3 | 0.66554 | 5.379
2024-12-10 | 0:03 | Data | 0 | 33.426 | 31.805 | 167.813 | 7.64 | 158.517 | 2235.18 | 25.83 | 47.894 | 6.41 | 1.283 | 4.092 | 8427.17 | 1.607 | 97.9 | 76.1 | 1453 | 23.99 | 5477.7 | 2686.9 | 2675.6 | 3923 | 1215.3 | 0.66704 | 5.375
2024-12-10 | 0:03 | Data | 0 | 33.696 | 31.812 | 167.722 | 7.63 | 158.517 | 2233.37 | 25.84 | 47.894 | 6.41 | 1.282 | 4.098 | 8427.17 | 1.823 | 97.9 | 76.2 | 1452 | 23.95 | 5477.7 | 2687.6 | 2661.3 | 3911.8 | 1215.3 | 0.66931 | 5.38
2024-12-10 | 0:03 | Data | 0 | 33.696 | 32.042 | 167.813 | 7.63 | 158.562 | 2233.37 | 25.84 | 47.984 | 6.41 | 1.273 | 4.107 | 8427.17 | 1.438 | 97.9 | 76.3 | 1452 | 23.99 | 5477.7 | 2696.9 | 2683.2 | 3934.3 | 1215.3 | 0.66739 | 5.38
2024-12-10 | 0:03 | Data | 0 | 33.851 | 32.035 | 167.767 | 7.63 | 158.562 | 2229.75 | 25.85 | 47.804 | 6.4 | 1.282 | 4.104 | 8431.69 | 1.695 | 97.9 | 76.2 | 1450 | 23.9 | 5480.6 | 2688.5 | 2680.3 | 3928.9 | 1215.3 | 0.66784 | 5.385
2024-12-10 | 0:03 | Data | 0 | 33.635 | 32.028 | 167.677 | 7.64 | 158.472 | 2229.75 | 25.83 | 47.714 | 6.4 | 1.282 | 4.11 | 8422.65 | 1.614 | 97.9 | 76.2 | 1450 | 23.81 | 5474.7 | 2706.2 | 2694.5 | 3948.9 | 1215.3 | 0.66754 | 5.392
2024-12-10 | 0:03 | Data | 0 | 33.304 | 32.001 | 167.677 | 7.64 | 158.517 | 2230.66 | 25.84 | 47.714 | 6.41 | 1.288 | 4.108 | 8418.13 | 1.587 | 97.9 | 76.1 | 1450 | 23.86 | 5471.8 | 2716.1 | 2681.7 | 3941.2 | 1215.3 | 0.67172 | 5.396
2024-12-10 | 0:03 | Data | 0 | 33.642 | 31.92 | 167.767 | 7.64 | 158.517 | 2227.95 | 25.84 | 47.894 | 6.4 | 1.285 | 4.107 | 8427.17 | 1.722 | 97.9 | 76.2 | 1449 | 23.95 | 5477.7 | 2697.8 | 2695.3 | 3940.2 | 1215.3 | 0.66734 | 5.392
2024-12-10 | 0:04 | Data | 0 | 33.615 | 32.028 | 167.767 | 7.63 | 158.472 | 2227.95 | 25.84 | 47.894 | 6.41 | 1.297 | 4.122 | 8440.74 | 1.668 | 97.9 | 76.1 | 1448 | 23.99 | 5486.5 | 2685.3 | 2696.4 | 3934.5 | 1215.3 | 0.66496 | 5.419
2024-12-10 | 0:04 | Data | 0 | 33.534 | 32.028 | 167.813 | 7.63 | 158.607 | 2228.85 | 25.83 | 47.894 | 6.41 | 1.292 | 4.115 | 8445.26 | 1.56 | 97.9 | 76.1 | 1449 | 23.95 | 5489.4 | 2699.9 | 2695.5 | 3941.6 | 1215.3 | 0.66764 | 5.408
2024-12-10 | 0:04 | Data | 0 | 33.642 | 32.028 | 167.767 | 7.64 | 158.562 | 2230.66 | 25.84 | 47.894 | 6.4 | 1.291 | 4.106 | 8440.74 | 1.728 | 97.8 | 76.1 | 1449 | 23.95 | 5486.5 | 2684.8 | 2671.1 | 3920.9 | 1215.3 | 0.66798 | 5.399
2024-12-10 | 0:04 | Data | 0 | 33.642 | 31.805 | 167.722 | 7.64 | 158.562 | 2230.66 | 25.84 | 47.894 | 6.41 | 1.289 | 4.101 | 8445.26 | 1.701 | 97.9 | 76.1 | 1450 | 23.95 | 5489.4 | 2700.8 | 2678 | 3934.8 | 1215.3 | 0.66903 | 5.387
2024-12-10 | 0:04 | Data | 0 | 33.412 | 31.799 | 167.677 | 7.64 | 158.426 | 2229.75 | 25.84 | 47.984 | 6.41 | 1.28 | 4.126 | 8454.3 | 1.614 | 97.9 | 76.3 | 1450 | 23.95 | 5495.3 | 2700.8 | 2663.9 | 3918.7 | 1215.3 | 0.67321 | 5.406
2024-12-10 | 0:04 | Data | 0 | 33.952 | 32.264 | 167.813 | 7.64 | 158.517 | 2233.37 | 25.84 | 47.984 | 6.4 | 1.289 | 4.113 | 8445.26 | 1.695 | 97.9 | 76.1 | 1452 | 23.99 | 5489.4 | 2709.4 | 2655.8 | 3920.1 | 1215.3 | 0.67382 | 5.401
2024-12-10 | 0:04 | Data | 0 | 33.642 | 31.974 | 167.632 | 7.64 | 158.426 | 2232.47 | 25.83 | 47.984 | 6.4 | 1.285 | 4.094 | 8445.26 | 1.526 | 97.9 | 76.1 | 1451 | 23.95 | 5489.4 | 2689.2 | 2675.7 | 3923.7 | 1215.3 | 0.66586 | 5.379
2024-12-10 | 0:04 | Data | 0 | 33.588 | 32.197 | 167.722 | 7.64 | 158.517 | 2230.66 | 25.84 | 47.894 | 6.41 | 1.282 | 4.112 | 8427.17 | 1.654 | 97.9 | 76.2 | 1449 | 23.95 | 5477.7 | 2662.4 | 2702.2 | 3921.1 | 1215.4 | 0.66039 | 5.394
2024-12-10 | 0:04 | Data | 0 | 33.952 | 32.035 | 167.858 | 7.63 | 158.607 | 2230.66 | 25.84 | 47.804 | 6.41 | 1.273 | 4.109 | 8422.65 | 1.83 | 97.9 | 76.3 | 1449 | 23.95 | 5474.7 | 2686 | 2692.9 | 3931.5 | 1215.4 | 0.66527 | 5.382
2024-12-10 | 0:04 | Data | 0 | 33.669 | 32.028 | 167.813 | 7.63 | 158.607 | 2227.04 | 25.84 | 47.894 | 6.41 | 1.278 | 4.129 | 8418.13 | 1.438 | 97.8 | 76.4 | 1448 | 23.9 | 5471.8 | 2723.3 | 2704.7 | 3953.1 | 1215.4 | 0.67019 | 5.407
2024-12-10 | 0:04 | Data | 0 | 33.628 | 31.853 | 167.677 | 7.63 | 158.472 | 2227.04 | 25.84 | 47.894 | 6.41 | 1.291 | 4.115 | 8404.56 | 1.512 | 97.8 | 76.1 | 1448 | 23.9 | 5463 | 2688.8 | 2638.4 | 3895.3 | 1215.4 | 0.6745 | 5.407
2024-12-10 | 0:04 | Data | 0 | 33.54 | 31.805 | 167.813 | 7.64 | 158.562 | 2227.95 | 25.83 | 47.894 | 6.4 | 1.291 | 4.118 | 8404.56 | 1.647 | 97.9 | 76.1 | 1448 | 23.95 | 5463 | 2684.2 | 2641.5 | 3895.2 | 1215.4 | 0.67294 | 5.409
2024-12-10 | 0:04 | Data | 0 | 33.439 | 32.008 | 167.858 | 7.64 | 158.562 | 2227.95 | 25.84 | 47.894 | 6.41 | 1.289 | 4.113 | 8418.13 | 1.485 | 97.9 | 76.1 | 1449 | 23.95 | 5471.8 | 2702.5 | 2644.5 | 3910.7 | 1215.4 | 0.67469 | 5.401
2024-12-10 | 0:04 | Data | 0 | 33.432 | 31.805 | 167.722 | 7.64 | 158.426 | 2225.23 | 25.84 | 47.804 | 6.41 | 1.284 | 4.124 | 8418.13 | 1.607 | 97.8 | 76.2 | 1447 | 23.95 | 5471.8 | 2713.8 | 2634.9 | 3910.2 | 1215.4 | 0.67779 | 5.407
2024-12-10 | 0:04 | Data | 0 | 33.581 | 31.853 | 167.767 | 7.64 | 158.562 | 2231.56 | 25.84 | 47.894 | 6.41 | 1.29 | 4.14 | 8427.17 | 1.782 | 97.9 | 76.2 | 1450 | 23.95 | 5477.7 | 2684.5 | 2656.5 | 3904.5 | 1215.4 | 0.67092 | 5.43
2024-12-10 | 0:04 | Data | 0 | 33.426 | 31.92 | 167.813 | 7.64 | 158.562 | 2230.66 | 25.84 | 47.894 | 6.41 | 1.289 | 4.127 | 8431.69 | 1.614 | 97.9 | 76.2 | 1451 | 23.95 | 5480.6 | 2713.3 | 2663.6 | 3929.8 | 1215.4 | 0.67203 | 5.417
2024-12-10 | 0:04 | Data | 0 | 33.642 | 32.021 | 167.677 | 7.63 | 158.517 | 2229.75 | 25.83 | 47.894 | 6.4 | 1.282 | 4.11 | 8409.08 | 1.62 | 97.9 | 76.2 | 1449 | 23.95 | 5465.9 | 2689.7 | 2669 | 3921.1 | 1215.4 | 0.66718 | 5.392
2024-12-10 | 0:04 | Data | 0 | 33.81 | 32.082 | 167.858 | 7.64 | 158.607 | 2229.75 | 25.84 | 47.623 | 6.4 | 1.28 | 4.12 | 8418.13 | 1.614 | 97.9 | 76.3 | 1450 | 23.81 | 5471.8 | 2682.9 | 2681.6 | 3926.3 | 1215.4 | 0.66538 | 5.4
2024-12-10 | 0:05 | Data | 0 | 33.642 | 32.028 | 167.813 | 7.64 | 158.517 | 2230.66 | 25.84 | 47.894 | 6.41 | 1.278 | 4.102 | 8418.13 | 1.614 | 97.9 | 76.2 | 1449 | 23.95 | 5471.8 | 2684.6 | 2684.7 | 3925.6 | 1215.4 | 0.66314 | 5.38
2024-12-10 | 0:05 | Data | 0 | 33.534 | 32.028 | 167.813 | 7.64 | 158.517 | 2229.75 | 25.84 | 47.894 | 6.41 | 1.291 | 4.097 | 8418.13 | 1.411 | 97.9 | 76.1 | 1450 | 23.99 | 5471.8 | 2691.6 | 2663.4 | 3916.8 | 1215.4 | 0.67202 | 5.387
2024-12-10 | 0:05 | Data | 0 | 33.669 | 32.028 | 167.813 | 7.63 | 158.562 | 2233.37 | 25.84 | 47.894 | 6.4 | 1.288 | 4.11 | 8431.69 | 1.614 | 97.9 | 76.1 | 1451 | 23.95 | 5480.6 | 2698.2 | 2656.7 | 3917 | 1215.4 | 0.67095 | 5.398
2024-12-10 | 0:05 | Data | 0 | 33.669 | 31.859 | 167.858 | 7.63 | 158.607 | 2235.18 | 25.84 | 47.894 | 6.4 | 1.288 | 4.125 | 8445.26 | 1.614 | 97.9 | 76.2 | 1453 | 23.99 | 5489.4 | 2705.9 | 2617.3 | 3888.3 | 1215.4 | 0.67837 | 5.413
2024-12-10 | 0:05 | Data | 0 | 33.473 | 31.92 | 167.767 | 7.64 | 158.562 | 2238.79 | 25.84 | 47.894 | 6.41 | 1.291 | 4.143 | 8436.21 | 1.614 | 97.9 | 76.2 | 1455 | 23.95 | 5483.5 | 2710.4 | 2624.8 | 3896.4 | 1215.4 | 0.67795 | 5.434
2024-12-10 | 0:05 | Data | 0 | 33.615 | 31.92 | 167.677 | 7.64 | 158.517 | 2238.79 | 25.84 | 47.984 | 6.41 | 1.283 | 4.118 | 8436.21 | 1.715 | 97.9 | 76.2 | 1455 | 23.99 | 5483.5 | 2711.1 | 2631.6 | 3900.3 | 1215.4 | 0.67439 | 5.401
2024-12-10 | 0:05 | Data | 0 | 33.426 | 31.974 | 167.677 | 7.63 | 158.472 | 2235.18 | 25.84 | 47.894 | 6.4 | 1.278 | 4.126 | 8445.26 | 1.614 | 97.9 | 76.4 | 1453 | 23.95 | 5489.4 | 2700.7 | 2625.9 | 3893.4 | 1215.4 | 0.67662 | 5.404
2024-12-10 | 0:05 | Data | 0 | 33.642 | 32.028 | 167.767 | 7.63 | 158.472 | 2233.37 | 25.84 | 47.894 | 6.4 | 1.286 | 4.099 | 8440.74 | 1.614 | 97.9 | 76.1 | 1452 | 23.95 | 5486.5 | 2671.4 | 2643.3 | 3891.7 | 1215.4 | 0.66924 | 5.385
2024-12-10 | 0:05 | Data | 0 | 33.669 | 32.075 | 167.677 | 7.64 | 158.517 | 2234.27 | 25.84 | 47.894 | 6.41 | 1.277 | 4.101 | 8431.69 | 1.519 | 97.9 | 76.3 | 1453 | 23.9 | 5480.6 | 2671.7 | 2648.8 | 3896.9 | 1215.4 | 0.66729 | 5.378
2024-12-10 | 0:05 | Data | 0 | 33.439 | 31.846 | 167.722 | 7.64 | 158.562 | 2230.66 | 25.84 | 47.894 | 6.4 | 1.275 | 4.081 | 8431.69 | 1.769 | 97.9 | 76.2 | 1449 | 23.95 | 5480.6 | 2692.1 | 2641 | 3906.1 | 1215.4 | 0.67043 | 5.356
2024-12-10 | 0:05 | Data | 0 | 33.642 | 32.345 | 167.767 | 7.64 | 158.562 | 2227.95 | 25.83 | 47.623 | 6.4 | 1.285 | 4.091 | 8436.21 | 1.472 | 97.9 | 76.1 | 1448 | 23.81 | 5483.5 | 2703.4 | 2660.8 | 3918.5 | 1215.4 | 0.67298 | 5.376
2024-12-10 | 0:05 | Data | 0 | 33.837 | 31.873 | 167.813 | 7.63 | 158.698 | 2232.47 | 25.84 | 47.804 | 6.41 | 1.275 | 4.11 | 8445.26 | 1.681 | 97.9 | 76.3 | 1451 | 23.9 | 5489.4 | 2705.6 | 2651.3 | 3920.8 | 1215.4 | 0.67127 | 5.385
2024-12-10 | 0:05 | Data | 0 | 33.277 | 31.886 | 167.722 | 7.63 | 158.517 | 2233.37 | 25.84 | 47.804 | 6.4 | 1.278 | 4.088 | 8454.3 | 1.479 | 97.9 | 76.2 | 1451 | 23.9 | 5495.3 | 2693 | 2653.9 | 3906.2 | 1215.4 | 0.67288 | 5.367
2024-12-10 | 0:05 | Data | 0 | 33.642 | 32.015 | 167.813 | 7.64 | 158.562 | 2125.81 | 25.84 | 47.894 | 6.41 | 1.289 | 4.091 | 8458.83 | 1.668 | 97.7 | 76 | 1381 | 23.95 | 5498.2 | 2704.9 | 2663.6 | 3924.9 | 1215.4 | 0.67235 | 5.38
2024-12-10 | 0:05 | Data | 0 | 33.837 | 32.305 | 167.903 | 7.63 | 158.562 | 2235.18 | 25.83 | 47.894 | 6.41 | 1.274 | 4.097 | 8481.44 | 1.674 | 97.9 | 76.3 | 1453 | 23.9 | 5512.9 | 2688.9 | 2635.5 | 3895.9 | 1215.4 | 0.67279 | 5.373
2024-12-10 | 0:05 | Data | 0 | 33.932 | 32.089 | 167.813 | 7.64 | 158.607 | 2238.79 | 25.83 | 47.894 | 6.41 | 1.273 | 4.112 | 8481.44 | 1.62 | 97.9 | 76.4 | 1455 | 23.95 | 5512.9 | 2683.3 | 2629.1 | 3890.7 | 1215.4 | 0.67173 | 5.385
2024-12-10 | 0:05 | Data | 0 | 33.642 | 32.028 | 167.722 | 7.64 | 158.562 | 2238.79 | 25.85 | 47.804 | 6.41 | 1.285 | 4.106 | 8485.96 | 1.614 | 97.9 | 76.2 | 1455 | 23.95 | 5515.9 | 2706.2 | 2634.2 | 3905.7 | 1215.4 | 0.67476 | 5.392
2024-12-10 | 0:05 | Data | 0 | 33.446 | 31.974 | 167.767 | 7.64 | 158.562 | 2239.7 | 25.84 | 47.894 | 6.4 | 1.282 | 4.122 | 8472.39 | 1.614 | 97.9 | 76.3 | 1455 | 23.95 | 5507.1 | 2693.6 | 2657.6 | 3912.7 | 1215.4 | 0.67122 | 5.403
2024-12-10 | 0:06 | Data | 0 | 33.81 | 32.156 | 167.858 | 7.63 | 158.607 | 2236.98 | 25.84 | 47.894 | 6.41 | 1.283 | 4.128 | 8458.83 | 1.708 | 97.9 | 76.3 | 1454 | 23.95 | 5498.2 | 2696 | 2629 | 3896.2 | 1215.4 | 0.67427 | 5.411
2024-12-10 | 0:06 | Data | 0 | 33.642 | 32.028 | 167.722 | 7.64 | 158.517 | 2239.7 | 25.83 | 47.894 | 6.4 | 1.288 | 4.103 | 8458.83 | 1.614 | 97.9 | 76.1 | 1456 | 23.95 | 5498.2 | 2690.8 | 2644 | 3901.3 | 1215.4 | 0.6725 | 5.391
2024-12-10 | 0:06 | Data | 0 | 33.871 | 32.035 | 167.767 | 7.63 | 158.652 | 2239.7 | 25.84 | 47.894 | 6.41 | 1.284 | 4.124 | 8458.83 | 1.634 | 97.9 | 76.3 | 1455 | 23.95 | 5498.2 | 2689.1 | 2658.3 | 3911 | 1215.4 | 0.67209 | 5.409
2024-12-10 | 0:06 | Data | 0 | 33.871 | 32.055 | 167.858 | 7.64 | 158.562 | 2239.7 | 25.84 | 47.894 | 6.41 | 1.279 | 4.124 | 8440.74 | 1.641 | 97.9 | 76.3 | 1455 | 23.95 | 5486.5 | 2700.6 | 2590.5 | 3871.8 | 1215.4 | 0.67886 | 5.402
2024-12-10 | 0:06 | Data | 0 | 33.655 | 32.204 | 167.948 | 7.64 | 158.562 | 2238.79 | 25.84 | 47.984 | 6.4 | 1.283 | 4.128 | 8454.3 | 1.587 | 97.9 | 76.3 | 1456 | 23.95 | 5495.3 | 2697.4 | 2669.4 | 3924.8 | 1215.4 | 0.67111 | 5.411
2024-12-10 | 0:06 | Data | 0 | 33.419 | 32.001 | 167.722 | 7.63 | 158.517 | 2079.72 | 25.84 | 47.984 | 6.41 | 1.276 | 4.097 | 8467.87 | 1.438 | 97.7 | 76.3 | 1351 | 23.95 | 5504.1 | 2705.9 | 2634.7 | 3903.7 | 1215.4 | 0.67394 | 5.373
2024-12-10 | 0:06 | Data | 0 | 33.81 | 32.028 | 167.813 | 7.64 | 158.562 | 2211.68 | 25.84 | 47.804 | 6.4 | 1.289 | 4.112 | 8467.87 | 1.83 | 97.8 | 76.1 | 1439 | 23.95 | 5504.1 | 2683.3 | 2656.5 | 3905.6 | 1215.4 | 0.66767 | 5.401
2024-12-10 | 0:06 | Data | 0 | 33.952 | 32.028 | 167.767 | 7.63 | 158.652 | 2216.2 | 25.84 | 47.894 | 6.4 | 1.284 | 4.128 | 8467.87 | 1.674 | 97.8 | 76.3 | 1440 | 23.99 | 5504.1 | 2699.8 | 2658.5 | 3912.3 | 1215.4 | 0.67486 | 5.412
2024-12-10 | 0:06 | Data | 0 | 33.81 | 32.028 | 167.813 | 7.63 | 158.517 | 2216.2 | 25.84 | 47.984 | 6.41 | 1.278 | 4.123 | 8440.74 | 1.701 | 97.8 | 76.3 | 1441 | 23.95 | 5486.5 | 2691.1 | 2655.6 | 3908 | 1215.4 | 0.67083 | 5.401
2024-12-10 | 0:06 | Data | 0 | 33.696 | 32.035 | 167.858 | 7.63 | 158.562 | 2213.49 | 25.83 | 47.894 | 6.4 | 1.292 | 4.153 | 8445.26 | 1.627 | 97.8 | 76.3 | 1439 | 23.95 | 5489.4 | 2700.5 | 2646.9 | 3905 | 1215.4 | 0.67505 | 5.447
2024-12-10 | 0:06 | Data | 0 | 33.756 | 32.035 | 167.813 | 7.64 | 158.562 | 2242.41 | 25.84 | 47.894 | 6.41 | 1.282 | 4.091 | 8440.74 | 1.708 | 97.9 | 76.1 | 1458 | 23.95 | 5486.5 | 2688.3 | 2641.7 | 3902.5 | 1215.4 | 0.67415 | 5.373
2024-12-10 | 0:06 | Data | 0 | 33.972 | 32.271 | 167.903 | 7.64 | 158.652 | 2242.41 | 25.84 | 47.804 | 6.41 | 1.287 | 4.11 | 8431.69 | 1.803 | 97.9 | 76.2 | 1458 | 23.95 | 5480.6 | 2706.3 | 2615.9 | 3890.7 | 1215.5 | 0.67671 | 5.397
2024-12-10 | 0:06 | Data | 0 | 33.729 | 32.028 | 167.858 | 7.64 | 158.562 | 2238.79 | 25.85 | 47.894 | 6.41 | 1.292 | 4.112 | 8436.21 | 1.634 | 97.9 | 76.1 | 1456 | 23.99 | 5483.5 | 2708.3 | 2622.2 | 3895.1 | 1215.5 | 0.67813 | 5.404
2024-12-10 | 0:06 | Data | 0 | 33.696 | 32.028 | 167.858 | 7.64 | 158.562 | 2239.7 | 25.84 | 47.984 | 6.41 | 1.288 | 4.122 | 8440.74 | 1.614 | 97.9 | 76.2 | 1456 | 23.95 | 5486.5 | 2686.6 | 2624.2 | 3886 | 1215.5 | 0.6738 | 5.409
2024-12-10 | 0:06 | Data | 0 | 33.81 | 32.258 | 167.858 | 7.63 | 158.562 | 2238.79 | 25.83 | 47.894 | 6.4 | 1.282 | 4.138 | 8467.87 | 1.593 | 97.9 | 76.4 | 1455 | 23.95 | 5504.1 | 2701.8 | 2632.2 | 3902 | 1215.5 | 0.67332 | 5.42
2024-12-10 | 0:06 | Data | 0 | 33.54 | 32.001 | 167.722 | 7.64 | 158.562 | 2231.56 | 25.84 | 47.894 | 6.41 | 1.279 | 4.104 | 8427.17 | 1.499 | 97.8 | 76.2 | 1451 | 23.99 | 5477.7 | 2725.9 | 2634.6 | 3915.7 | 1215.5 | 0.67783 | 5.383
2024-12-10 | 0:06 | Data | 0 | 33.756 | 32.264 | 167.903 | 7.63 | 158.652 | 2236.98 | 25.83 | 47.894 | 6.4 | 1.283 | 4.109 | 8422.65 | 1.695 | 97.9 | 76.2 | 1454 | 23.95 | 5474.7 | 2709.4 | 2633.7 | 3899.6 | 1215.5 | 0.67859 | 5.391
2024-12-10 | 0:06 | Data | 0 | 33.642 | 32.035 | 167.813 | 7.64 | 158.562 | 2235.18 | 25.84 | 47.984 | 6.41 | 1.284 | 4.12 | 8409.08 | 1.776 | 97.9 | 76.2 | 1453 | 23.95 | 5465.9 | 2679.8 | 2630.6 | 3882.6 | 1215.5 | 0.67153 | 5.405
2024-12-10 | 0:07 | Data | 0 | 33.412 | 31.974 | 167.722 | 7.63 | 158.562 | 2236.98 | 25.84 | 47.894 | 6.41 | 1.292 | 4.134 | 8418.13 | 1.614 | 97.9 | 76.2 | 1454 | 23.9 | 5471.8 | 2686.8 | 2626 | 3888.3 | 1215.5 | 0.67345 | 5.427
2024-12-10 | 0:07 | Data | 0 | 33.642 | 32.028 | 167.767 | 7.64 | 158.517 | 2236.08 | 25.84 | 47.804 | 6.4 | 1.287 | 4.124 | 8418.13 | 1.614 | 97.9 | 76.2 | 1453 | 23.95 | 5471.8 | 2699.7 | 2620.8 | 3889.3 | 1215.5 | 0.67915 | 5.412
2024-12-10 | 0:07 | Data | 0 | 33.669 | 32.028 | 167.858 | 7.64 | 158.652 | 2236.08 | 25.84 | 47.894 | 6.41 | 1.282 | 4.088 | 8418.13 | 1.614 | 97.9 | 76.1 | 1453 | 23.95 | 5471.8 | 2678.5 | 2615.8 | 3872.7 | 1215.5 | 0.67516 | 5.371
2024-12-10 | 0:07 | Data | 0 | 33.817 | 32.042 | 167.858 | 7.64 | 158.652 | 2239.7 | 25.84 | 47.984 | 6.41 | 1.274 | 4.108 | 8400.04 | 1.776 | 97.9 | 76.3 | 1455 | 23.99 | 5460 | 2698.7 | 2631.1 | 3893.1 | 1215.5 | 0.67781 | 5.382
2024-12-10 | 0:07 | Data | 0 | 33.642 | 32.258 | 167.813 | 7.63 | 158.607 | 2238.79 | 25.84 | 47.894 | 6.41 | 1.277 | 4.111 | 8418.13 | 1.384 | 97.9 | 76.3 | 1455 | 23.95 | 5471.8 | 2695.7 | 2630.5 | 3894.7 | 1215.5 | 0.67692 | 5.389
2024-12-10 | 0:07 | Data | 0 | 33.527 | 31.988 | 167.767 | 7.64 | 158.607 | 2238.79 | 25.83 | 47.804 | 6.41 | 1.277 | 4.11 | 8418.13 | 1.614 | 97.9 | 76.3 | 1451 | 23.95 | 5471.8 | 2672.8 | 2618.3 | 3874.3 | 1215.5 | 0.67202 | 5.387
2024-12-10 | 0:07 | Data | 0 | 33.837 | 32.258 | 167.858 | 7.63 | 158.562 | 2127.62 | 25.84 | 47.894 | 6.4 | 1.289 | 4.115 | 8390.99 | 1.607 | 97.7 | 76.2 | 1383 | 23.95 | 5454.1 | 2704.7 | 2606.5 | 3882.4 | 1215.5 | 0.68085 | 5.403
2024-12-10 | 0:07 | Data | 0 | 33.756 | 32.406 | 168.084 | 7.63 | 158.562 | 2233.37 | 25.85 | 47.804 | 6.41 | 1.288 | 4.119 | 8400.04 | 1.668 | 97.9 | 76.2 | 1452 | 23.99 | 5460 | 2670.8 | 2596 | 3864.2 | 1215.5 | 0.67323 | 5.407
2024-12-10 | 0:07 | Data | 0 | 33.567 | 32.028 | 167.858 | 7.64 | 158.652 | 2241.5 | 25.84 | 47.894 | 6.4 | 1.28 | 4.104 | 8400.04 | 1.452 | 97.9 | 76.2 | 1457 | 23.95 | 5460 | 2684 | 2608.2 | 3864.1 | 1215.5 | 0.67161 | 5.383
2024-12-10 | 0:07 | Data | 0 | 33.817 | 32.258 | 167.948 | 7.64 | 158.652 | 2233.37 | 25.84 | 47.894 | 6.41 | 1.273 | 4.125 | 8404.56 | 1.607 | 97.9 | 76.4 | 1451 | 23.95 | 5463 | 2697.5 | 2619.8 | 3886.1 | 1215.5 | 0.67558 | 5.399
2024-12-10 | 0:07 | Data | 0 | 33.486 | 31.832 | 167.813 | 7.64 | 158.607 | 2233.37 | 25.83 | 47.894 | 6.4 | 1.274 | 4.126 | 8409.08 | 1.587 | 97.9 | 76.4 | 1451 | 23.95 | 5465.9 | 2671.7 | 2642.5 | 3888.7 | 1215.5 | 0.66989 | 5.4
2024-12-10 | 0:07 | Data | 0 | 33.648 | 32.028 | 167.903 | 7.63 | 158.698 | 2238.79 | 25.84 | 47.623 | 6.41 | 1.276 | 4.124 | 8409.08 | 1.62 | 97.9 | 76.4 | 1456 | 23.86 | 5465.9 | 2694.7 | 2639.5 | 3901 | 1215.5 | 0.67297 | 5.4
2024-12-10 | 0:07 | Data | 0 | 33.669 | 32.028 | 167.858 | 7.63 | 158.562 | 2235.18 | 25.84 | 47.894 | 6.4 | 1.28 | 4.105 | 8427.17 | 1.614 | 97.9 | 76.2 | 1453 | 23.9 | 5477.7 | 2689.7 | 2637.6 | 3897.8 | 1215.5 | 0.67302 | 5.384
2024-12-10 | 0:07 | Data | 0 | 33.439 | 31.988 | 167.813 | 7.64 | 158.426 | 2235.18 | 25.84 | 47.984 | 6.41 | 1.283 | 4.129 | 8418.13 | 1.593 | 97.9 | 76.3 | 1453 | 23.95 | 5471.8 | 2684.7 | 2636.7 | 3889.1 | 1215.5 | 0.6746 | 5.411
2024-12-10 | 0:07 | Data | 0 | 33.642 | 32.028 | 167.767 | 7.64 | 158.607 | 2236.08 | 25.84 | 47.894 | 6.4 | 1.282 | 4.152 | 8418.13 | 1.728 | 97.9 | 76.4 | 1453 | 23.9 | 5471.8 | 2697.5 | 2629 | 3897.1 | 1215.5 | 0.67562 | 5.433
2024-12-10 | 0:07 | Data | 0 | 33.648 | 32.028 | 167.858 | 7.63 | 158.562 | 2235.18 | 25.84 | 47.894 | 6.41 | 1.278 | 4.102 | 8404.56 | 1.62 | 97.9 | 76.2 | 1453 | 23.95 | 5463 | 2678.8 | 2631.5 | 3881.5 | 1215.5 | 0.67243 | 5.38
2024-12-10 | 0:07 | Data | 0 | 33.871 | 32.042 | 167.858 | 7.64 | 158.652 | 2233.37 | 25.84 | 47.894 | 6.41 | 1.282 | 4.091 | 8409.08 | 1.668 | 97.9 | 76.1 | 1451 | 23.95 | 5465.9 | 2710.2 | 2606.2 | 3885.5 | 1215.5 | 0.68052 | 5.373
2024-12-10 | 0:08 | Data | 0 | 33.567 | 32.028 | 167.858 | 7.64 | 158.607 | 2233.37 | 25.84 | 47.804 | 6.41 | 1.286 | 4.107 | 8418.13 | 1.404 | 97.9 | 76.2 | 1452 | 23.9 | 5471.8 | 2678.1 | 2616.5 | 3872.4 | 1215.5 | 0.67469 | 5.393
2024-12-10 | 0:08 | Data | 0 | 33.844 | 32.15 | 167.858 | 7.64 | 158.652 | 2232.47 | 25.83 | 47.894 | 6.41 | 1.283 | 4.11 | 8404.56 | 1.641 | 97.9 | 76.2 | 1452 | 23.99 | 5463 | 2692.8 | 2629.7 | 3892.9 | 1215.5 | 0.67531 | 5.393
2024-12-10 | 0:08 | Data | 0 | 33.756 | 32.048 | 167.858 | 7.64 | 158.562 | 2233.37 | 25.84 | 47.894 | 6.4 | 1.288 | 4.107 | 8400.04 | 1.634 | 97.9 | 76.1 | 1452 | 23.95 | 5460 | 2700.6 | 2648.5 | 3912.2 | 1215.5 | 0.67331 | 5.395
2024-12-10 | 0:08 | Data | 0 | 33.959 | 32.48 | 167.858 | 7.63 | 158.607 | 2233.37 | 25.84 | 47.984 | 6.41 | 1.282 | 4.109 | 8390.99 | 1.62 | 97.9 | 76.2 | 1451 | 23.9 | 5454.1 | 2712.5 | 2620.8 | 3893.9 | 1215.5 | 0.68023 | 5.391
2024-12-10 | 0:08 | Data | 0 | 33.642 | 32.15 | 167.767 | 7.64 | 158.607 | 2233.37 | 25.84 | 47.894 | 6.41 | 1.28 | 4.094 | 8400.04 | 1.668 | 97.9 | 76.2 | 1452 | 23.95 | 5460 | 2671.1 | 2638.2 | 3892.4 | 1215.5 | 0.66514 | 5.373
2024-12-10 | 0:08 | Data | 0 | 33.642 | 32.258 | 167.767 | 7.63 | 158.562 | 2232.47 | 25.83 | 47.804 | 6.41 | 1.294 | 4.13 | 8400.04 | 1.452 | 97.9 | 76.1 | 1452 | 23.95 | 5460 | 2698.1 | 2641.2 | 3904.8 | 1215.5 | 0.67365 | 5.423
2024-12-10 | 0:08 | Data | 0 | 33.729 | 32.035 | 167.813 | 7.64 | 158.652 | 2232.47 | 25.84 | 47.894 | 6.4 | 1.292 | 4.125 | 8400.04 | 1.445 | 97.9 | 76.1 | 1452 | 23.95 | 5460 | 2694.1 | 2638.7 | 3894.3 | 1215.5 | 0.67374 | 5.418
2024-12-10 | 0:08 | Data | 0 | 33.675 | 32.035 | 167.858 | 7.64 | 158.607 | 2233.37 | 25.84 | 47.894 | 6.4 | 1.289 | 4.123 | 8400.04 | 1.614 | 97.9 | 76.2 | 1452 | 23.95 | 5460 | 2676.3 | 2643.1 | 3892.8 | 1215.5 | 0.6668 | 5.411
2024-12-10 | 0:08 | Data | 0 | 33.756 | 32.258 | 167.813 | 7.63 | 158.607 | 2233.37 | 25.83 | 47.894 | 6.41 | 1.288 | 4.086 | 8386.47 | 1.6 | 97.9 | 76 | 1452 | 23.95 | 5451.2 | 2686.2 | 2653.4 | 3901.1 | 1215.5 | 0.66832 | 5.373
2024-12-10 | 0:08 | Data | 0 | 33.871 | 32.035 | 167.903 | 7.64 | 158.652 | 2232.47 | 25.84 | 47.984 | 6.4 | 1.286 | 4.084 | 8390.99 | 1.715 | 97.9 | 76.1 | 1452 | 23.95 | 5454.1 | 2693.8 | 2646 | 3902.5 | 1215.5 | 0.67174 | 5.37
2024-12-10 | 0:08 | Data | 0 | 33.446 | 32.028 | 167.858 | 7.63 | 158.652 | 2233.37 | 25.84 | 47.804 | 6.41 | 1.29 | 4.101 | 8400.04 | 1.391 | 97.9 | 76.1 | 1452 | 23.9 | 5460 | 2687.9 | 2636 | 3891.2 | 1215.5 | 0.67368 | 5.39
2024-12-10 | 0:08 | Data | 0 | 33.871 | 32.089 | 167.813 | 7.64 | 158.607 | 2232.47 | 25.84 | 47.894 | 6.41 | 1.274 | 4.13 | 8400.04 | 1.728 | 97.9 | 76.4 | 1451 | 23.99 | 5460 | 2690.4 | 2641.4 | 3899.4 | 1215.5 | 0.66936 | 5.404
2024-12-10 | 0:08 | Data | 0 | 33.925 | 31.954 | 167.903 | 7.64 | 158.652 | 2232.47 | 25.84 | 47.894 | 6.4 | 1.275 | 4.138 | 8381.95 | 1.762 | 97.9 | 76.4 | 1451 | 23.95 | 5448.3 | 2700.4 | 2639.1 | 3901.4 | 1215.5 | 0.67532 | 5.413
2024-12-10 | 0:08 | Data | 0 | 33.858 | 32.46 | 167.858 | 7.64 | 158.652 | 2232.47 | 25.83 | 47.894 | 6.41 | 1.272 | 4.126 | 8390.99 | 1.499 | 97.9 | 76.4 | 1451 | 23.95 | 5454.1 | 2693.7 | 2633.3 | 3900.9 | 1215.5 | 0.67304 | 5.399
2024-12-10 | 0:08 | Data | 0 | 33.432 | 32.028 | 167.858 | 7.63 | 158.607 | 2230.66 | 25.83 | 47.894 | 6.4 | 1.275 | 4.124 | 8381.95 | 1.56 | 97.8 | 76.4 | 1450 | 23.95 | 5448.3 | 2712.9 | 2618.8 | 3894.5 | 1215.5 | 0.68024 | 5.4
2024-12-10 | 0:08 | Data | 0 | 33.642 | 32.035 | 167.858 | 7.64 | 158.562 | 2230.66 | 25.83 | 47.894 | 6.41 | 1.288 | 4.09 | 8386.47 | 1.6 | 97.9 | 76.1 | 1450 | 23.95 | 5451.2 | 2692.8 | 2644.1 | 3902.1 | 1215.6 | 0.6721 | 5.379
2024-12-10 | 0:08 | Data | 0 | 33.871 | 31.927 | 167.813 | 7.63 | 158.607 | 2230.66 | 25.85 | 47.804 | 6.4 | 1.287 | 4.102 | 8386.47 | 1.668 | 97.9 | 76.1 | 1450 | 23.9 | 5451.2 | 2713.7 | 2643.2 | 3913.5 | 1215.6 | 0.674 | 5.389
2024-12-10 | 0:08 | Data | 0 | 33.851 | 32.055 | 167.767 | 7.64 | 158.607 | 2229.75 | 25.85 | 47.894 | 6.4 | 1.282 | 4.118 | 8386.47 | 1.695 | 97.9 | 76.3 | 1449 | 23.9 | 5451.2 | 2712.7 | 2638.2 | 3910.7 | 1215.6 | 0.67751 | 5.401
2024-12-10 | 0:09 | Data | 0 | 33.858 | 32.264 | 167.813 | 7.64 | 158.562 | 2229.75 | 25.84 | 47.984 | 6.4 | 1.274 | 4.131 | 8386.47 | 1.607 | 97.9 | 76.4 | 1449 | 23.95 | 5451.2 | 2705.4 | 2642.4 | 3896.5 | 1215.6 | 0.67525 | 5.407
2024-12-10 | 0:09 | Data | 0 | 33.642 | 32.028 | 167.813 | 7.63 | 158.652 | 2230.66 | 25.83 | 47.894 | 6.41 | 1.286 | 4.132 | 8372.9 | 1.614 | 97.9 | 76.3 | 1450 | 23.95 | 5442.4 | 2705.8 | 2648.4 | 3905.6 | 1215.6 | 0.67598 | 5.418
2024-12-10 | 0:09 | Data | 0 | 33.432 | 32.177 | 167.858 | 7.64 | 158.562 | 2230.66 | 25.83 | 47.894 | 6.4 | 1.289 | 4.11 | 8372.9 | 1.816 | 97.9 | 76.1 | 1451 | 23.95 | 5442.4 | 2711.2 | 2630.8 | 3900.9 | 1215.6 | 0.6777 | 5.4
2024-12-10 | 0:09 | Data | 0 | 33.885 | 32.042 | 167.903 | 7.63 | 158.607 | 2234.27 | 25.84 | 47.804 | 6.4 | 1.291 | 4.105 | 8381.95 | 1.661 | 97.9 | 76.1 | 1452 | 23.9 | 5448.3 | 2704.7 | 2634.6 | 3901.7 | 1215.6 | 0.67538 | 5.395
2024-12-10 | 0:09 | Data | 0 | 33.871 | 32.089 | 167.903 | 7.63 | 158.607 | 2229.75 | 25.84 | 47.714 | 6.4 | 1.291 | 4.115 | 8395.51 | 1.607 | 97.9 | 76.1 | 1449 | 23.86 | 5457.1 | 2714.9 | 2624.6 | 3900.8 | 1215.6 | 0.68101 | 5.407
2024-12-10 | 0:09 | Data | 0 | 33.675 | 32.075 | 167.813 | 7.64 | 158.562 | 2228.85 | 25.84 | 47.623 | 6.4 | 1.296 | 4.131 | 8409.08 | 1.533 | 97.9 | 76.1 | 1449 | 23.81 | 5465.9 | 2697.2 | 2606.4 | 3880.1 | 1215.6 | 0.68208 | 5.427
2024-12-10 | 0:09 | Data | 0 | 33.669 | 32.028 | 167.813 | 7.63 | 158.562 | 2227.95 | 25.84 | 47.533 | 6.41 | 1.289 | 4.109 | 8418.13 | 1.62 | 97.9 | 76.1 | 1448 | 23.77 | 5471.8 | 2707.9 | 2624.2 | 3898.5 | 1215.6 | 0.67532 | 5.399
2024-12-10 | 0:09 | Data | 0 | 33.871 | 32.264 | 167.813 | 7.64 | 158.652 | 2223.43 | 25.83 | 47.714 | 6.4 | 1.287 | 4.107 | 8436.21 | 1.431 | 97.9 | 76.1 | 1447 | 23.81 | 5483.5 | 2699.1 | 2641.1 | 3908.2 | 1215.6 | 0.67269 | 5.394
2024-12-10 | 0:09 | Data | 0 | 33.864 | 32.258 | 167.858 | 7.63 | 158.562 | 2227.95 | 25.84 | 47.623 | 6.41 | 1.285 | 4.098 | 8418.13 | 1.411 | 97.9 | 76.1 | 1448 | 23.86 | 5471.8 | 2686.6 | 2649.3 | 3900.3 | 1215.6 | 0.67046 | 5.384
2024-12-10 | 0:09 | Data | 0 | 33.817 | 32.055 | 167.813 | 7.63 | 158.562 | 2227.95 | 25.83 | 47.623 | 6.4 | 1.284 | 4.102 | 8418.13 | 1.695 | 97.9 | 76.2 | 1448 | 23.86 | 5471.8 | 2681.7 | 2641 | 3892.9 | 1215.6 | 0.6704 | 5.386
2024-12-10 | 0:09 | Data | 0 | 33.756 | 32.264 | 168.084 | 7.64 | 158.562 | 2229.75 | 25.84 | 47.623 | 6.41 | 1.279 | 4.107 | 8418.13 | 1.593 | 97.9 | 76.3 | 1450 | 23.81 | 5471.8 | 2707.4 | 2663.1 | 3923.1 | 1215.6 | 0.67136 | 5.386
2024-12-10 | 0:09 | Data | 0 | 33.642 | 32.028 | 167.767 | 7.64 | 158.562 | 2125.81 | 25.85 | 47.533 | 6.41 | 1.282 | 4.127 | 8418.13 | 1.614 | 97.8 | 76.3 | 1382 | 23.81 | 5471.8 | 2688.8 | 2671.6 | 3917.6 | 1215.6 | 0.66846 | 5.409
2024-12-10 | 0:09 | Data | 0 | 33.594 | 32.028 | 167.767 | 7.63 | 158.607 | 2235.18 | 25.84 | 47.623 | 6.41 | 1.279 | 4.098 | 8431.69 | 1.6 | 97.9 | 76.2 | 1452 | 23.81 | 5480.6 | 2695.7 | 2637.4 | 3904 | 1215.6 | 0.67392 | 5.377
2024-12-10 | 0:09 | Data | 0 | 33.696 | 31.947 | 167.813 | 7.64 | 158.652 | 2236.08 | 25.84 | 47.623 | 6.4 | 1.291 | 4.086 | 8431.69 | 1.674 | 97.9 | 76 | 1453 | 23.81 | 5480.6 | 2705 | 2647.7 | 3913.5 | 1215.6 | 0.67392 | 5.376
2024-12-10 | 0:09 | Data | 0 | 33.891 | 32.035 | 167.813 | 7.64 | 158.652 | 2230.66 | 25.83 | 47.623 | 6.4 | 1.28 | 4.086 | 8427.17 | 1.519 | 97.9 | 76.2 | 1451 | 23.81 | 5477.7 | 2700.7 | 2651 | 3905.5 | 1215.6 | 0.67238 | 5.366
2024-12-10 | 0:09 | Data | 0 | 33.669 | 32.204 | 167.903 | 7.64 | 158.652 | 2229.75 | 25.84 | 47.623 | 6.4 | 1.282 | 4.105 | 8427.17 | 1.445 | 97.9 | 76.2 | 1449 | 23.81 | 5477.7 | 2688.4 | 2623 | 3887.8 | 1215.6 | 0.67436 | 5.385
2024-12-10 | 0:09 | Data | 0 | 33.871 | 32.042 | 167.948 | 7.64 | 158.652 | 2230.66 | 25.84 | 47.623 | 6.4 | 1.288 | 4.101 | 8418.13 | 1.661 | 97.9 | 76.1 | 1450 | 23.81 | 5471.8 | 2677.8 | 2632.3 | 3884.2 | 1215.6 | 0.67167 | 5.388
2024-12-10 | 0:09 | Data | 0 | 33.756 | 32.028 | 167.903 | 7.63 | 158.652 | 2230.66 | 25.84 | 47.623 | 6.4 | 1.285 | 4.108 | 8395.51 | 1.62 | 97.9 | 76.2 | 1449 | 23.81 | 5457.1 | 2676 | 2635.9 | 3896.6 | 1215.6 | 0.67147 | 5.393
2024-12-10 | 0:10 | Data | 0 | 33.864 | 32.028 | 167.813 | 7.64 | 158.607 | 2232.47 | 25.84 | 47.623 | 6.4 | 1.284 | 4.122 | 8400.04 | 1.668 | 97.9 | 76.2 | 1452 | 23.81 | 5460 | 2682.1 | 2663.8 | 3908.6 | 1215.6 | 0.66701 | 5.406
2024-12-10 | 0:10 | Data | 0 | 34.033 | 32.271 | 167.948 | 7.64 | 158.698 | 2233.37 | 25.84 | 47.623 | 6.41 | 1.287 | 4.11 | 8422.65 | 1.769 | 97.9 | 76.2 | 1452 | 23.81 | 5474.7 | 2695.1 | 2665.3 | 3915.9 | 1215.6 | 0.66898 | 5.399
2024-12-10 | 0:10 | Data | 0 | 33.756 | 32.042 | 167.858 | 7.63 | 158.562 | 2232.47 | 25.84 | 47.714 | 6.4 | 1.29 | 4.092 | 8418.13 | 1.627 | 97.9 | 76 | 1451 | 23.81 | 5471.8 | 2690.4 | 2677.2 | 3926.4 | 1215.6 | 0.66832 | 5.382
2024-12-10 | 0:10 | Data | 0 | 33.959 | 32.089 | 167.858 | 7.63 | 158.607 | 2236.08 | 25.84 | 47.714 | 6.4 | 1.287 | 4.106 | 8431.69 | 1.742 | 97.9 | 76.1 | 1453 | 23.81 | 5480.6 | 2691.8 | 2671.8 | 3930.5 | 1215.6 | 0.67219 | 5.394
2024-12-10 | 0:10 | Data | 0 | 33.986 | 32.467 | 167.903 | 7.64 | 158.698 | 2233.37 | 25.83 | 47.623 | 6.4 | 1.288 | 4.114 | 8418.13 | 1.782 | 97.9 | 76.2 | 1451 | 23.86 | 5471.8 | 2688.5 | 2614.5 | 3882 | 1215.6 | 0.67473 | 5.401
2024-12-10 | 0:10 | Data | 0 | 33.871 | 32.089 | 167.813 | 7.63 | 158.652 | 2232.47 | 25.84 | 47.623 | 6.4 | 1.287 | 4.125 | 8400.04 | 1.614 | 97.9 | 76.2 | 1452 | 23.81 | 5460 | 1608.1 | 2069.1 | 2635.6 | 1215.6 | 0.60691 | 5.412
2024-12-10 | 0:10 | Data | 0 | 33.642 | 32.251 | 167.813 | 7.64 | 158.607 | 2233.37 | 25.84 | 47.714 | 6.4 | 1.289 | 4.099 | 8395.51 | 1.391 | 97.9 | 76.1 | 1452 | 23.86 | 5457.1 | 1583.6 | 2050.1 | 2615.4 | 1215.6 | 0.60916 | 5.388
2024-12-10 | 0:10 | Data | 0 | 33.648 | 32.251 | 167.858 | 7.64 | 158.607 | 2232.47 | 25.84 | 47.623 | 6.41 | 1.285 | 4.125 | 8386.47 | 1.438 | 97.9 | 76.2 | 1452 | 23.81 | 5451.2 | 1618.3 | 2059.9 | 2631.8 | 1215.6 | 0.61201 | 5.41
2024-12-10 | 0:10 | Data | 0 | 33.655 | 32.035 | 167.993 | 7.64 | 158.607 | 2224.33 | 25.84 | 47.714 | 6.41 | 1.288 | 4.108 | 8386.47 | 1.607 | 97.9 | 76.1 | 1446 | 23.86 | 5451.2 | 1616.8 | 2047.1 | 2620.6 | 1215.6 | 0.61142 | 5.396
2024-12-10 | 0:10 | Data | 0 | 33.642 | 32.035 | 167.813 | 7.64 | 158.562 | 2230.66 | 25.84 | 47.623 | 6.4 | 1.28 | 4.09 | 8400.04 | 1.654 | 97.9 | 76.1 | 1450 | 23.86 | 5460 | 1622.1 | 2037 | 2617.2 | 1215.6 | 0.61732 | 5.373
2024-12-10 | 0:10 | Data | 0 | 33.986 | 32.035 | 167.993 | 7.64 | 158.607 | 2230.66 | 25.84 | 47.533 | 6.41 | 1.291 | 4.102 | 8386.47 | 1.452 | 97.9 | 76.1 | 1450 | 23.77 | 5451.2 | 1597.5 | 2029.8 | 2589.7 | 1215.6 | 0.61441 | 5.392
2024-12-10 | 0:10 | Data | 0 | 33.642 | 32.042 | 167.903 | 7.64 | 158.562 | 2225.23 | 25.84 | 47.623 | 6.4 | 1.276 | 4.122 | 8386.47 | 1.6 | 97.9 | 76.4 | 1446 | 23.86 | 5451.2 | 1609.5 | 2041.3 | 2611 | 1215.6 | 0.61301 | 5.398
2024-12-10 | 0:10 | Data | 0 | 33.756 | 32.379 | 167.948 | 7.63 | 158.607 | 2229.75 | 25.84 | 47.623 | 6.4 | 1.284 | 4.105 | 8386.47 | 1.776 | 97.9 | 76.2 | 1449 | 23.81 | 5451.2 | 1631.9 | 2044.9 | 2629.7 | 1215.6 | 0.61815 | 5.39
2024-12-10 | 0:10 | Data | 0 | 33.648 | 32.474 | 167.767 | 7.64 | 158.698 | 2229.75 | 25.83 | 47.623 | 6.41 | 1.289 | 4.118 | 8390.99 | 1.519 | 97.9 | 76.2 | 1449 | 23.77 | 5454.1 | 1606.5 | 2043.3 | 2610.6 | 1215.6 | 0.61114 | 5.407
2024-12-10 | 0:10 | Data | 0 | 33.898 | 32.143 | 167.903 | 7.64 | 158.698 | 2230.66 | 25.84 | 47.623 | 6.4 | 1.279 | 4.08 | 8386.47 | 1.56 | 97.9 | 76.1 | 1450 | 23.81 | 5451.2 | 1618.5 | 2052.5 | 2625.6 | 1215.6 | 0.61456 | 5.359
2024-12-10 | 0:10 | Data | 0 | 33.743 | 32.372 | 167.767 | 7.64 | 158.562 | 2229.75 | 25.84 | 47.623 | 6.4 | 1.285 | 4.092 | 8381.95 | 1.708 | 97.9 | 76.1 | 1450 | 23.81 | 5448.3 | 1600.1 | 2053.1 | 2617.4 | 1215.6 | 0.60822 | 5.378
2024-12-10 | 0:10 | Data | 0 | 33.642 | 32.237 | 167.813 | 7.63 | 158.607 | 2235.18 | 25.84 | 47.623 | 6.4 | 1.291 | 4.108 | 8400.04 | 1.492 | 97.9 | 76.1 | 1453 | 23.81 | 5460 | 1620.5 | 2035.3 | 2615.6 | 1215.6 | 0.61691 | 5.397
2024-12-10 | 0:10 | Data | 0 | 33.756 | 32.42 | 167.993 | 7.64 | 158.652 | 2235.18 | 25.84 | 47.623 | 6.41 | 1.288 | 4.114 | 8400.04 | 1.492 | 97.9 | 76.2 | 1453 | 23.81 | 5460 | 1613.4 | 2071 | 2637.6 | 1215.6 | 0.60876 | 5.401
2024-12-10 | 0:11 | Data | 0 | 33.844 | 32.46 | 167.993 | 7.63 | 158.607 | 2238.79 | 25.83 | 47.623 | 6.4 | 1.284 | 4.137 | 8386.47 | 1.6 | 97.9 | 76.3 | 1454 | 23.86 | 5451.2 | 1622.6 | 2045.3 | 2622 | 1215.6 | 0.61715 | 5.421
2024-12-10 | 0:11 | Data | 0 | 33.669 | 32.028 | 167.767 | 7.64 | 158.562 | 2238.79 | 25.84 | 47.623 | 6.4 | 1.284 | 4.109 | 8400.04 | 1.499 | 97.9 | 76.2 | 1455 | 23.81 | 5460 | 1613.2 | 2064.3 | 2631.3 | 1215.6 | 0.61023 | 5.394
2024-12-10 | 0:11 | Data | 0 | 33.743 | 32.082 | 167.948 | 7.63 | 158.607 | 2234.27 | 25.84 | 47.714 | 6.41 | 1.291 | 4.094 | 8400.04 | 1.56 | 97.9 | 76 | 1452 | 23.81 | 5460 | 1614.6 | 2025.5 | 2605.6 | 1215.6 | 0.61658 | 5.385
2024-12-10 | 0:11 | Data | 0 | 33.669 | 32.028 | 167.813 | 7.63 | 158.517 | 2238.79 | 25.84 | 47.894 | 6.4 | 1.291 | 4.109 | 8386.47 | 1.614 | 97.9 | 76.1 | 1455 | 23.95 | 5451.2 | 1625 | 2026.5 | 2609.7 | 1215.6 | 0.62004 | 5.401
2024-12-10 | 0:11 | Data | 0 | 33.898 | 32.089 | 167.858 | 7.64 | 158.743 | 2163.77 | 25.84 | 47.804 | 6.4 | 1.284 | 4.104 | 8395.51 | 1.499 | 97.8 | 76.2 | 1402 | 23.95 | 5457.1 | 1628 | 2033.3 | 2617.1 | 1215.6 | 0.6191 | 5.387
2024-12-10 | 0:11 | Data | 0 | 33.642 | 32.028 | 167.813 | 7.63 | 158.607 | 2130.33 | 25.83 | 47.894 | 6.4 | 1.282 | 4.096 | 8386.47 | 1.614 | 97.8 | 76.2 | 1392 | 23.9 | 5451.2 | 1621.8 | 2043.1 | 2620.3 | 1215.6 | 0.61715 | 5.378
2024-12-10 | 0:11 | Data | 0 | 33.54 | 32.136 | 167.767 | 7.63 | 158.517 | 2236.08 | 25.84 | 47.984 | 6.41 | 1.277 | 4.086 | 8418.13 | 1.614 | 97.9 | 76.2 | 1453 | 23.95 | 5471.8 | 1601.4 | 2047.6 | 2613.6 | 1215.6 | 0.60989 | 5.362
2024-12-10 | 0:11 | Data | 0 | 33.756 | 32.237 | 167.903 | 7.63 | 158.607 | 2232.47 | 25.83 | 47.894 | 6.4 | 1.282 | 4.103 | 8400.04 | 1.654 | 97.9 | 76.2 | 1452 | 23.95 | 5460 | 1593.6 | 2020.6 | 2594.3 | 1215.6 | 0.61482 | 5.385
2024-12-10 | 0:11 | Data | 0 | 33.594 | 31.913 | 167.903 | 7.63 | 158.607 | 2236.08 | 25.84 | 47.894 | 6.41 | 1.29 | 4.079 | 8418.13 | 1.6 | 97.9 | 76 | 1453 | 23.9 | 5471.8 | 1590 | 2052.9 | 2610.3 | 1215.6 | 0.60718 | 5.368
2024-12-10 | 0:11 | Data | 0 | 33.615 | 32.15 | 167.903 | 7.64 | 158.652 | 2222.52 | 25.84 | 47.894 | 6.4 | 1.28 | 4.084 | 8400.04 | 1.776 | 97.8 | 76.1 | 1445 | 23.95 | 5460 | 1616 | 2025.8 | 2605 | 1215.6 | 0.61994 | 5.361
2024-12-10 | 0:11 | Data | 0 | 33.561 | 32.129 | 167.858 | 7.64 | 158.698 | 2232.47 | 25.84 | 47.894 | 6.4 | 1.287 | 4.107 | 8418.13 | 1.344 | 97.9 | 76.1 | 1452 | 23.9 | 5471.8 | 1603.9 | 2032.5 | 2602.4 | 1215.7 | 0.61413 | 5.394
2024-12-10 | 0:11 | Data | 0 | 33.756 | 32.035 | 167.813 | 7.64 | 158.607 | 2233.37 | 25.84 | 47.984 | 6.4 | 1.288 | 4.096 | 8400.04 | 1.614 | 97.9 | 76.1 | 1451 | 23.95 | 5460 | 1609.4 | 2048 | 2617.7 | 1215.7 | 0.61299 | 5.384
2024-12-10 | 0:11 | Data | 0 | 33.48 | 32.028 | 167.858 | 7.64 | 158.607 | 2236.08 | 25.84 | 47.804 | 6.41 | 1.282 | 4.098 | 8580.93 | 1.506 | 97.9 | 76.2 | 1453 | 23.95 | 5577.6 | 1614 | 2044 | 2616.3 | 1215.7 | 0.61448 | 5.381
2024-12-10 | 0:11 | Data | 0 | 33.844 | 32.028 | 167.903 | 7.64 | 158.652 | 2236.08 | 25.84 | 47.984 | 6.4 | 1.277 | 4.085 | 8599.01 | 1.634 | 97.9 | 76.2 | 1453 | 23.95 | 5589.4 | 1641.8 | 2055.8 | 2644.6 | 1215.7 | 0.61879 | 5.363
2024-12-10 | 0:11 | Data | 0 | 33.817 | 32.379 | 167.948 | 7.64 | 158.607 | 2235.18 | 25.85 | 47.894 | 6.41 | 1.284 | 4.076 | 8599.01 | 1.587 | 97.9 | 76 | 1453 | 23.9 | 5589.4 | 1604.8 | 2035.5 | 2607.2 | 1215.7 | 0.6128 | 5.36
2024-12-10 | 0:11 | Data | 0 | 33.642 | 32.204 | 167.858 | 7.64 | 158.652 | 2236.98 | 25.84 | 47.894 | 6.4 | 1.288 | 4.092 | 8608.06 | 1.607 | 97.9 | 76.1 | 1454 | 23.95 | 5595.2 | 1611.6 | 2045.7 | 2615.1 | 1215.7 | 0.61273 | 5.379
2024-12-10 | 0:11 | Data | 0 | 33.669 | 32.035 | 167.948 | 7.64 | 158.652 | 2238.79 | 25.84 | 47.894 | 6.41 | 1.292 | 4.111 | 8400.04 | 1.553 | 97.9 | 76.1 | 1455 | 23.9 | 5460 | 1605.3 | 2050.5 | 2618 | 1215.7 | 0.60857 | 5.403
2024-12-10 | 0:12 | Data | 0 | 33.959 | 32.156 | 167.813 | 7.63 | 158.652 | 2239.7 | 25.83 | 47.894 | 6.41 | 1.284 | 4.088 | 8386.47 | 1.674 | 97.9 | 76.1 | 1456 | 23.95 | 5451.2 | 1607.9 | 2040.2 | 2609.8 | 1215.7 | 0.61383 | 5.373
2024-12-10 | 0:12 | Data | 0 | 33.642 | 32.366 | 167.903 | 7.64 | 158.562 | 2235.18 | 25.84 | 47.894 | 6.41 | 1.288 | 4.105 | 8395.51 | 1.438 | 97.9 | 76.1 | 1453 | 23.95 | 5457.1 | 1609.7 | 2035.7 | 2603 | 1215.7 | 0.61561 | 5.393
2024-12-10 | 0:12 | Data | 0 | 33.642 | 32.028 | 167.858 | 7.63 | 158.517 | 2236.08 | 25.84 | 47.894 | 6.41 | 1.284 | 4.113 | 8386.47 | 1.614 | 97.9 | 76.2 | 1453 | 23.99 | 5451.2 | 1611.1 | 2010.5 | 2588.6 | 1215.7 | 0.62024 | 5.397
2024-12-10 | 0:12 | Data | 0 | 33.655 | 32.028 | 167.813 | 7.63 | 158.562 | 2234.27 | 25.84 | 47.894 | 6.41 | 1.277 | 4.132 | 8400.04 | 1.614 | 97.9 | 76.4 | 1453 | 23.95 | 5460 | 1604.5 | 2024.9 | 2596.9 | 1215.7 | 0.61733 | 5.409
2024-12-10 | 0:12 | Data | 0 | 33.642 | 32.028 | 167.767 | 7.64 | 158.562 | 2235.18 | 25.84 | 47.894 | 6.4 | 1.288 | 4.137 | 8386.47 | 1.614 | 97.9 | 76.2 | 1453 | 23.95 | 5451.2 | 1629.9 | 2037.1 | 2623.5 | 1215.7 | 0.61887 | 5.426
2024-12-10 | 0:12 | Data | 0 | 33.655 | 32.379 | 167.948 | 7.64 | 158.652 | 2238.79 | 25.84 | 47.894 | 6.41 | 1.289 | 4.14 | 8386.47 | 1.553 | 97.9 | 76.3 | 1456 | 23.95 | 5451.2 | 1597.8 | 2043.9 | 2606.8 | 1215.7 | 0.61086 | 5.429
2024-12-10 | 0:12 | Data | 0 | 34.087 | 32.264 | 167.903 | 7.64 | 158.607 | 2239.7 | 25.84 | 47.894 | 6.41 | 1.282 | 4.113 | 8386.47 | 1.634 | 97.9 | 76.2 | 1456 | 23.99 | 5451.2 | 1616.2 | 2062.7 | 2633.9 | 1215.7 | 0.6132 | 5.395
2024-12-10 | 0:12 | Data | 0 | 33.473 | 32.082 | 167.767 | 7.63 | 158.517 | 2239.7 | 25.84 | 47.894 | 6.4 | 1.287 | 4.128 | 8431.69 | 1.485 | 97.9 | 76.3 | 1456 | 23.95 | 5480.6 | 1605.8 | 2096.3 | 2660.9 | 1215.7 | 0.60211 | 5.415
2024-12-10 | 0:12 | Data | 0 | 33.412 | 32.231 | 167.767 | 7.64 | 158.517 | 2233.37 | 25.84 | 47.984 | 6.4 | 1.284 | 4.129 | 8427.17 | 1.6 | 97.9 | 76.3 | 1451 | 23.99 | 5477.7 | 1611.1 | 2040.2 | 2614.2 | 1215.7 | 0.61414 | 5.413
2024-12-10 | 0:12 | Data | 0 | 33.871 | 32.264 | 167.948 | 7.63 | 158.607 | 2239.7 | 25.84 | 47.894 | 6.41 | 1.287 | 4.111 | 8427.17 | 1.607 | 97.9 | 76.2 | 1456 | 23.95 | 5477.7 | 1609.5 | 2021.8 | 2597.5 | 1215.7 | 0.61618 | 5.398
2024-12-10 | 0:12 | Data | 0 | 33.858 | 31.832 | 167.722 | 7.64 | 158.562 | 2238.79 | 25.84 | 47.804 | 6.4 | 1.285 | 4.115 | 8427.17 | 1.749 | 97.9 | 76.2 | 1456 | 23.95 | 5477.7 | 1609.1 | 2001.5 | 2581.3 | 1215.7 | 0.61921 | 5.401
2024-12-10 | 0:12 | Data | 0 | 33.756 | 31.927 | 167.813 | 7.63 | 158.607 | 2235.18 | 25.84 | 47.984 | 6.4 | 1.278 | 4.114 | 8400.04 | 1.607 | 97.9 | 76.3 | 1453 | 23.99 | 5460 | 1594.3 | 2033.3 | 2598.6 | 1215.7 | 0.60963 | 5.392
2024-12-10 | 0:12 | Data | 0 | 33.48 | 31.913 | 167.767 | 7.63 | 158.562 | 2238.79 | 25.84 | 47.894 | 6.41 | 1.28 | 4.123 | 8400.04 | 1.566 | 97.9 | 76.3 | 1456 | 23.95 | 5460 | 1607.1 | 2014.5 | 2591 | 1215.7 | 0.61792 | 5.402
2024-12-10 | 0:12 | Data | 0 | 33.473 | 31.974 | 167.767 | 7.64 | 158.562 | 2239.7 | 25.84 | 47.894 | 6.4 | 1.283 | 4.109 | 8409.08 | 1.634 | 97.9 | 76.2 | 1456 | 23.95 | 5465.9 | 1607.3 | 2024.9 | 2599.2 | 1215.7 | 0.61581 | 5.392
2024-12-10 | 0:12 | Data | 0 | 33.635 | 32.028 | 167.767 | 7.63 | 158.562 | 2239.7 | 25.84 | 47.894 | 6.41 | 1.288 | 4.118 | 8395.51 | 1.614 | 97.9 | 76.2 | 1456 | 23.9 | 5457.1 | 1618.1 | 2013.2 | 2596.2 | 1215.7 | 0.62107 | 5.405
2024-12-10 | 0:12 | Data | 0 | 33.864 | 31.873 | 167.722 | 7.64 | 158.607 | 2236.98 | 25.84 | 47.894 | 6.41 | 1.273 | 4.123 | 8427.17 | 1.641 | 97.9 | 76.4 | 1455 | 23.95 | 5477.7 | 1611.3 | 2010.8 | 2590 | 1215.7 | 0.61923 | 5.395
2024-12-10 | 0:12 | Data | 0 | 33.925 | 32.035 | 167.858 | 7.63 | 158.562 | 2242.41 | 25.84 | 47.894 | 6.4 | 1.273 | 4.106 | 8409.08 | 1.546 | 97.9 | 76.3 | 1457 | 23.99 | 5465.9 | 1608.5 | 2036.3 | 2609 | 1215.7 | 0.61449 | 5.381
2024-12-10 | 0:12 | Data | 0 | 33.588 | 32.082 | 167.858 | 7.64 | 158.562 | 2241.5 | 25.83 | 47.984 | 6.4 | 1.284 | 4.103 | 8409.08 | 1.566 | 97.9 | 76.2 | 1458 | 23.99 | 5465.9 | 1631.9 | 2059.9 | 2639.8 | 1215.7 | 0.61623 | 5.388
2024-12-10 | 0:13 | Data | 0 | 33.662 | 32.028 | 167.903 | 7.64 | 158.472 | 2246.02 | 25.84 | 47.894 | 6.4 | 1.276 | 4.124 | 8418.13 | 1.62 | 97.9 | 76.4 | 1461 | 23.95 | 5471.8 | 1615.1 | 2026.6 | 2603.2 | 1215.7 | 0.61555 | 5.401
2024-12-10 | 0:13 | Data | 0 | 33.642 | 32.028 | 167.858 | 7.64 | 158.562 | 2238.79 | 25.84 | 47.804 | 6.4 | 1.282 | 4.115 | 8418.13 | 1.614 | 97.9 | 76.2 | 1455 | 23.9 | 5471.8 | 1612.5 | 2009.8 | 2590.1 | 1215.7 | 0.62017 | 5.397
2024-12-10 | 0:13 | Data | 0 | 33.642 | 31.812 | 167.813 | 7.63 | 158.517 | 2233.37 | 25.84 | 47.894 | 6.4 | 1.275 | 4.106 | 8409.08 | 1.816 | 97.9 | 76.3 | 1452 | 23.99 | 5465.9 | 1606.5 | 2026.5 | 2599.4 | 1215.7 | 0.61521 | 5.382
2024-12-10 | 0:13 | Data | 0 | 33.304 | 31.799 | 167.722 | 7.64 | 158.607 | 2239.7 | 25.83 | 47.894 | 6.4 | 1.275 | 4.102 | 8422.65 | 1.573 | 97.9 | 76.3 | 1456 | 23.95 | 5474.7 | 1611.9 | 2044.7 | 2618.6 | 1215.7 | 0.61329 | 5.377
2024-12-10 | 0:13 | Data | 0 | 33.642 | 32.028 | 167.858 | 7.64 | 158.517 | 2241.5 | 25.83 | 47.894 | 6.4 | 1.28 | 4.09 | 8427.17 | 1.614 | 97.9 | 76.2 | 1458 | 23.95 | 5477.7 | 1600.5 | 2029.8 | 2599.2 | 1215.7 | 0.61326 | 5.369
2024-12-10 | 0:13 | Data | 0 | 33.655 | 32.028 | 167.722 | 7.64 | 158.517 | 2241.5 | 25.84 | 47.894 | 6.41 | 1.278 | 4.074 | 8422.65 | 1.499 | 97.9 | 76.1 | 1456 | 23.95 | 5474.7 | 1620 | 2044.6 | 2621.1 | 1215.7 | 0.61315 | 5.352
2024-12-10 | 0:13 | Data | 0 | 33.621 | 32.028 | 167.677 | 7.63 | 158.517 | 2241.5 | 25.84 | 47.894 | 6.4 | 1.284 | 4.105 | 8418.13 | 1.6 | 97.9 | 76.2 | 1457 | 23.95 | 5471.8 | 1625.2 | 2059.7 | 2635.8 | 1215.7 | 0.61414 | 5.39
2024-12-10 | 0:13 | Data | 0 | 33.581 | 32.143 | 167.813 | 7.64 | 158.472 | 2248.73 | 25.84 | 47.984 | 6.41 | 1.287 | 4.108 | 8431.69 | 1.708 | 97.9 | 76.1 | 1462 | 23.95 | 5480.6 | 1629.2 | 2030.8 | 2614.7 | 1215.7 | 0.62079 | 5.396
2024-12-10 | 0:13 | Data | 0 | 33.574 | 32.028 | 167.767 | 7.63 | 158.517 | 2239.7 | 25.84 | 47.804 | 6.41 | 1.289 | 4.087 | 8418.13 | 1.803 | 97.9 | 76 | 1456 | 23.9 | 5471.8 | 1599.4 | 2011.4 | 2583.2 | 1215.7 | 0.61745 | 5.376
2024-12-10 | 0:13 | Data | 0 | 33.642 | 32.028 | 167.858 | 7.64 | 158.562 | 2239.7 | 25.83 | 47.984 | 6.4 | 1.291 | 4.107 | 8431.69 | 1.614 | 97.9 | 76.1 | 1455 | 23.95 | 5480.6 | 2715.6 | 2625.4 | 3899.8 | 1215.7 | 0.68072 | 5.4
2024-12-10 | 0:13 | Data | 0 | 33.642 | 32.015 | 167.767 | 7.64 | 158.472 | 2236.08 | 25.84 | 47.894 | 6.4 | 1.282 | 4.125 | 8418.13 | 1.789 | 97.9 | 76.3 | 1453 | 23.95 | 5471.8 | 2704.6 | 2627.2 | 3897.7 | 1215.7 | 0.67465 | 5.407
2024-12-10 | 0:13 | Data | 0 | 33.635 | 32.028 | 167.813 | 7.63 | 158.607 | 2236.08 | 25.84 | 47.894 | 6.41 | 1.279 | 4.114 | 8418.13 | 1.782 | 97.9 | 76.3 | 1453 | 23.95 | 5471.8 | 2702.3 | 2617.8 | 3889.2 | 1215.7 | 0.67832 | 5.392
2024-12-10 | 0:13 | Data | 0 | 33.399 | 31.799 | 167.767 | 7.63 | 158.426 | 2232.47 | 25.84 | 47.894 | 6.4 | 1.272 | 4.118 | 8418.13 | 1.722 | 97.9 | 76.4 | 1452 | 23.95 | 5471.8 | 2696.7 | 2636.2 | 3892.8 | 1215.7 | 0.67879 | 5.39
2024-12-10 | 0:13 | Data | 0 | 33.412 | 32.129 | 167.813 | 7.64 | 158.426 | 2229.75 | 25.84 | 47.804 | 6.41 | 1.275 | 4.116 | 8404.56 | 1.539 | 97.9 | 76.3 | 1450 | 23.9 | 5463 | 2677.3 | 2635.5 | 3886.7 | 1215.7 | 0.67236 | 5.392
2024-12-10 | 0:13 | Data | 0 | 33.918 | 32.042 | 167.767 | 7.64 | 158.607 | 2227.95 | 25.84 | 47.804 | 6.4 | 1.273 | 4.134 | 8418.13 | 1.681 | 97.8 | 76.4 | 1448 | 23.95 | 5471.8 | 2679.2 | 2644.4 | 3893.5 | 1215.7 | 0.66936 | 5.407
2024-12-10 | 0:13 | Data | 0 | 33.554 | 32.19 | 167.813 | 7.63 | 158.472 | 2230.66 | 25.84 | 47.894 | 6.4 | 1.283 | 4.124 | 8418.13 | 1.506 | 97.9 | 76.3 | 1450 | 23.95 | 5471.8 | 2680.8 | 2640.5 | 3886 | 1215.7 | 0.67269 | 5.408
2024-12-10 | 0:13 | Data | 0 | 33.696 | 32.028 | 167.677 | 7.64 | 158.517 | 2228.85 | 25.83 | 47.984 | 6.41 | 1.282 | 4.099 | 8418.13 | 1.411 | 97.8 | 76.2 | 1448 | 23.99 | 5471.8 | 2705.8 | 2625.2 | 3896.5 | 1215.7 | 0.67834 | 5.382
2024-12-10 | 0:14 | Data | 0 | 33.864 | 32.028 | 167.948 | 7.64 | 158.652 | 2228.85 | 25.84 | 47.894 | 6.4 | 1.274 | 4.119 | 8427.17 | 1.634 | 97.9 | 76.4 | 1448 | 23.99 | 5477.7 | 2707.1 | 2652 | 3915.1 | 1215.7 | 0.67484 | 5.393
2024-12-10 | 0:14 | Data | 0 | 33.642 | 32.015 | 167.767 | 7.63 | 158.562 | 2225.23 | 25.84 | 47.804 | 6.41 | 1.286 | 4.115 | 8431.69 | 1.627 | 97.9 | 76.2 | 1447 | 23.9 | 5480.6 | 2701.8 | 2633.6 | 3899 | 1215.7 | 0.67458 | 5.401
2024-12-10 | 0:14 | Data | 0 | 33.588 | 32.028 | 167.858 | 7.64 | 158.517 | 2224.33 | 25.84 | 47.894 | 6.41 | 1.288 | 4.07 | 8427.17 | 1.614 | 97.8 | 76 | 1446 | 23.95 | 5477.7 | 2693.3 | 2635.7 | 3891.5 | 1215.7 | 0.67728 | 5.359
2024-12-10 | 0:14 | Data | 0 | 33.628 | 31.826 | 167.677 | 7.64 | 158.426 | 2224.33 | 25.84 | 47.894 | 6.4 | 1.292 | 4.094 | 8427.17 | 1.722 | 97.8 | 76 | 1446 | 23.95 | 5477.7 | 2683.7 | 2646.9 | 3895.8 | 1215.7 | 0.67046 | 5.386
2024-12-10 | 0:14 | Data | 0 | 33.642 | 32.136 | 167.767 | 7.63 | 158.607 | 2225.23 | 25.81 | 47.804 | 6.41 | 1.291 | 4.11 | 8418.13 | 1.708 | 97.8 | 76.1 | 1445 | 23.95 | 5471.8 | 2675.2 | 2629.3 | 3880.1 | 1215.7 | 0.67319 | 5.401
2024-12-10 | 0:14 | Data | 0 | 33.426 | 32.028 | 167.677 | 7.64 | 158.472 | 2227.04 | 25.82 | 47.894 | 6.41 | 1.282 | 4.126 | 8400.04 | 1.6 | 97.8 | 76.3 | 1448 | 23.95 | 5460 | 2693.5 | 2619.9 | 3886.4 | 1215.7 | 0.67698 | 5.409
2024-12-10 | 0:14 | Data | 0 | 33.864 | 32.143 | 167.903 | 7.63 | 158.517 | 2227.95 | 25.82 | 47.804 | 6.4 | 1.287 | 4.12 | 8400.04 | 1.607 | 97.9 | 76.2 | 1448 | 23.95 | 5460 | 2695.5 | 2615.5 | 3891.1 | 1215.7 | 0.68061 | 5.408
2024-12-10 | 0:14 | Data | 0 | 33.642 | 32.028 | 167.722 | 7.63 | 158.517 | 2227.04 | 25.82 | 47.984 | 6.4 | 1.279 | 4.115 | 8390.99 | 1.614 | 97.8 | 76.3 | 1447 | 23.99 | 5454.1 | 2722.4 | 2617.2 | 3872.2 | 1215.7 | 0.68249 | 5.395
2024-12-10 | 0:14 | Data | 0 | 33.642 | 32.028 | 167.767 | 7.64 | 158.562 | 2225.23 | 25.82 | 47.894 | 6.4 | 1.286 | 4.114 | 8400.04 | 1.614 | 97.9 | 76.2 | 1446 | 23.9 | 5460 | 2695.6 | 2596.3 | 3885.9 | 1215.7 | 0.67417 | 5.401
2024-12-10 | 0:14 | Data | 0 | 33.527 | 31.913 | 167.722 | 7.64 | 158.472 | 2227.95 | 25.82 | 47.533 | 6.4 | 1.287 | 4.097 | 8409.08 | 1.627 | 97.9 | 76.1 | 1448 | 23.77 | 5465.9 | 2677.1 | 2641.3 | 3894 | 1215.7 | 0.66998 | 5.385
2024-12-10 | 0:14 | Data | 0 | 33.426 | 32.028 | 167.767 | 7.63 | 158.472 | 2227.95 | 25.82 | 47.623 | 6.4 | 1.288 | 4.077 | 8400.04 | 1.391 | 97.9 | 76 | 1448 | 23.81 | 5460 | 2707 | 2653.7 | 3917.8 | 1215.7 | 0.67234 | 5.365
2024-12-10 | 0:14 | Data | 0 | 33.615 | 32.021 | 167.722 | 7.64 | 158.517 | 2227.04 | 25.82 | 47.714 | 6.4 | 1.289 | 4.088 | 8395.51 | 1.634 | 97.9 | 76 | 1448 | 23.86 | 5457.1 | 2712.9 | 2637.4 | 3913 | 1215.8 | 0.67683 | 5.377
2024-12-10 | 0:14 | Data | 0 | 33.588 | 32.015 | 167.632 | 7.63 | 158.472 | 2227.04 | 25.81 | 47.894 | 6.4 | 1.283 | 4.106 | 8386.47 | 1.62 | 97.9 | 76.2 | 1448 | 23.95 | 5451.2 | 2675.9 | 2635.2 | 3884.3 | 1215.8 | 0.6708 | 5.391
2024-12-10 | 0:14 | Data | 0 | 33.419 | 32.021 | 167.767 | 7.63 | 158.517 | 2230.66 | 25.82 | 47.894 | 6.41 | 1.293 | 4.102 | 8400.04 | 1.566 | 97.9 | 76 | 1449 | 23.9 | 5460 | 2676.9 | 2634.9 | 3885.7 | 1215.8 | 0.67016 | 5.395
2024-12-10 | 0:14 | Data | 0 | 33.426 | 31.805 | 167.722 | 7.63 | 158.472 | 2229.75 | 25.83 | 47.623 | 6.4 | 1.291 | 4.086 | 8418.13 | 1.607 | 97.9 | 76 | 1450 | 23.81 | 5471.8 | 2706.5 | 2639 | 3904.2 | 1215.8 | 0.67576 | 5.378
2024-12-10 | 0:14 | Data | 0 | 33.642 | 32.204 | 167.858 | 7.64 | 158.517 | 2232.47 | 25.84 | 47.623 | 6.4 | 1.279 | 4.106 | 8418.13 | 1.614 | 97.9 | 76.3 | 1451 | 23.81 | 5471.8 | 2687.1 | 2654.3 | 3908.2 | 1215.8 | 0.67232 | 5.385
2024-12-10 | 0:14 | Data | 0 | 33.642 | 32.015 | 167.858 | 7.64 | 158.517 | 2232.47 | 25.83 | 47.623 | 6.4 | 1.286 | 4.116 | 8409.08 | 1.485 | 97.9 | 76.2 | 1452 | 23.81 | 5465.9 | 2702.3 | 2613.8 | 3895.7 | 1215.8 | 0.67654 | 5.402
2024-12-10 | 0:14 | Data | 0 | 33.466 | 31.913 | 167.767 | 7.64 | 158.562 | 2235.18 | 25.84 | 47.894 | 6.41 | 1.292 | 4.122 | 8400.04 | 1.62 | 97.9 | 76.1 | 1453 | 23.99 | 5460 | 2691.1 | 2622.8 | 3892.3 | 1215.8 | 0.67634 | 5.415
2024-12-10 | 0:15 | Data | 0 | 33.392 | 32.015 | 167.858 | 7.63 | 158.472 | 2233.37 | 25.84 | 47.623 | 6.41 | 1.299 | 4.098 | 8390.99 | 1.546 | 97.9 | 75.9 | 1452 | 23.81 | 5454.1 | 2680.2 | 2625.3 | 3881.3 | 1215.8 | 0.674 | 5.397
2024-12-10 | 0:15 | Data | 0 | 33.635 | 31.826 | 167.813 | 7.64 | 158.517 | 2233.37 | 25.84 | 47.714 | 6.4 | 1.287 | 4.098 | 8395.51 | 1.722 | 97.9 | 76.1 | 1452 | 23.81 | 5457.1 | 2685.4 | 2621 | 3888.8 | 1215.8 | 0.67042 | 5.385
2024-12-10 | 0:15 | Data | 0 | 33.75 | 31.859 | 167.767 | 7.63 | 158.562 | 2240.6 | 25.84 | 47.533 | 6.41 | 1.29 | 4.096 | 8395.51 | 1.634 | 97.9 | 76.1 | 1456 | 23.77 | 5457.1 | 2706.7 | 2616.7 | 3892.5 | 1215.8 | 0.67762 | 5.387
2024-12-10 | 0:15 | Data | 0 | 33.581 | 32.021 | 167.813 | 7.64 | 158.517 | 2241.5 | 25.83 | 47.623 | 6.4 | 1.299 | 4.127 | 8440.74 | 1.782 | 97.9 | 76.1 | 1457 | 23.86 | 5486.5 | 2703.8 | 2610.5 | 3881 | 1215.8 | 0.68196 | 5.425
2024-12-10 | 0:15 | Data | 0 | 33.743 | 31.853 | 167.948 | 7.63 | 158.517 | 2239.7 | 25.84 | 47.533 | 6.4 | 1.291 | 4.107 | 8445.26 | 1.391 | 97.9 | 76.1 | 1456 | 23.81 | 5489.4 | 2690.5 | 2640 | 3897 | 1215.8 | 0.67536 | 5.399
2024-12-10 | 0:15 | Data | 0 | 33.75 | 32.028 | 167.903 | 7.64 | 158.562 | 2239.7 | 25.83 | 47.353 | 6.41 | 1.278 | 4.086 | 8440.74 | 1.715 | 97.9 | 76.2 | 1456 | 23.63 | 5486.5 | 2708.2 | 2609.7 | 3882.9 | 1215.8 | 0.68003 | 5.363
2024-12-10 | 0:15 | Data | 0 | 33.621 | 32.251 | 167.722 | 7.64 | 158.517 | 2239.7 | 25.84 | 47.623 | 6.4 | 1.292 | 4.093 | 8440.74 | 1.573 | 97.9 | 76 | 1455 | 23.86 | 5486.5 | 2668.5 | 2638.1 | 3883.3 | 1215.8 | 0.66929 | 5.385
2024-12-10 | 0:15 | Data | 0 | 33.669 | 32.021 | 167.813 | 7.64 | 158.652 | 2239.7 | 25.83 | 47.623 | 6.4 | 1.285 | 4.113 | 8458.83 | 1.431 | 97.9 | 76.2 | 1456 | 23.86 | 5498.2 | 2697.7 | 2627.5 | 3891.6 | 1215.8 | 0.67605 | 5.398
2024-12-10 | 0:15 | Data | 0 | 33.635 | 31.927 | 167.767 | 7.63 | 158.517 | 2241.5 | 25.83 | 47.714 | 6.41 | 1.273 | 4.133 | 8454.3 | 1.789 | 97.9 | 76.4 | 1457 | 23.81 | 5495.3 | 2682.9 | 2624 | 3887.4 | 1215.8 | 0.67494 | 5.406
2024-12-10 | 0:15 | Data | 0 | 33.615 | 32.028 | 167.903 | 7.64 | 158.517 | 2244.22 | 25.84 | 47.623 | 6.4 | 1.278 | 4.104 | 8454.3 | 1.607 | 97.9 | 76.3 | 1459 | 23.81 | 5495.3 | 2696.7 | 2630.7 | 3894.5 | 1215.8 | 0.67569 | 5.38
2024-12-10 | 0:15 | Data | 0 | 33.912 | 31.805 | 167.813 | 7.63 | 158.517 | 2246.93 | 25.85 | 47.623 | 6.4 | 1.279 | 4.118 | 8467.87 | 1.708 | 97.9 | 76.3 | 1461 | 23.81 | 5504.1 | 2672.7 | 2605.9 | 3862.9 | 1215.8 | 0.67467 | 5.395
2024-12-10 | 0:15 | Data | 0 | 33.871 | 31.934 | 167.903 | 7.63 | 158.652 | 2251.45 | 25.84 | 47.623 | 6.4 | 1.275 | 4.125 | 8445.26 | 1.62 | 97.9 | 76.4 | 1463 | 23.81 | 5489.4 | 2707.6 | 2623.2 | 3906.1 | 1215.8 | 0.68055 | 5.401
2024-12-10 | 0:15 | Data | 0 | 33.588 | 32.021 | 167.722 | 7.64 | 158.517 | 2246.02 | 25.84 | 47.533 | 6.41 | 1.278 | 4.084 | 8440.74 | 1.62 | 97.9 | 76.2 | 1461 | 23.81 | 5486.5 | 2710.5 | 2615.6 | 3896 | 1215.8 | 0.6784 | 5.36
2024-12-10 | 0:15 | Data | 0 | 33.642 | 32.028 | 167.767 | 7.63 | 158.562 | 2245.12 | 25.84 | 47.623 | 6.4 | 1.288 | 4.096 | 8458.83 | 1.614 | 97.9 | 76.1 | 1459 | 23.81 | 5498.2 | 2690.6 | 2631.8 | 3896.9 | 1215.8 | 0.67341 | 5.383
2024-12-10 | 0:15 | Data | 0 | 33.439 | 32.028 | 167.767 | 7.64 | 158.607 | 2245.12 | 25.85 | 47.623 | 6.4 | 1.288 | 4.075 | 8472.39 | 1.56 | 97.9 | 76 | 1459 | 23.81 | 5507.1 | 2689.4 | 2644.2 | 3901.8 | 1215.8 | 0.67162 | 5.362
2024-12-10 | 0:15 | Data | 0 | 33.642 | 32.15 | 167.813 | 7.64 | 158.562 | 2241.5 | 25.84 | 47.623 | 6.4 | 1.283 | 4.08 | 8463.35 | 1.614 | 97.9 | 76.1 | 1457 | 23.81 | 5501.2 | 2692.7 | 2639.8 | 3902.1 | 1215.8 | 0.67283 | 5.363
2024-12-10 | 0:15 | Data | 0 | 33.507 | 32.096 | 167.813 | 7.64 | 158.607 | 2244.22 | 25.84 | 47.623 | 6.4 | 1.275 | 4.105 | 8463.35 | 1.506 | 97.9 | 76.3 | 1459 | 23.86 | 5501.2 | 2688.5 | 2639.3 | 3898.3 | 1215.8 | 0.67205 | 5.38
2024-12-10 | 0:15 | Data | 0 | 33.642 | 32.001 | 167.813 | 7.63 | 158.607 | 2241.5 | 25.83 | 47.623 | 6.41 | 1.276 | 4.116 | 8458.83 | 1.58 | 97.9 | 76.3 | 1456 | 23.77 | 5498.2 | 2688.6 | 2622.8 | 3882.7 | 1215.8 | 0.67436 | 5.392
2024-12-10 | 0:16 | Data | 0 | 33.412 | 32.028 | 167.722 | 7.64 | 158.562 | 2244.22 | 25.84 | 47.714 | 6.4 | 1.279 | 4.11 | 8472.39 | 1.6 | 97.9 | 76.3 | 1458 | 23.81 | 5507.1 | 2702.6 | 2610.2 | 3881.5 | 1215.8 | 0.6808 | 5.39
2024-12-10 | 0:16 | Data | 0 | 33.817 | 32.258 | 167.767 | 7.64 | 158.517 | 2236.98 | 25.84 | 47.623 | 6.4 | 1.282 | 4.115 | 8431.69 | 1.492 | 97.9 | 76.2 | 1454 | 23.81 | 5480.6 | 2703.6 | 2621 | 3893.9 | 1215.8 | 0.67647 | 5.395
2024-12-10 | 0:16 | Data | 0 | 33.486 | 32.15 | 167.858 | 7.64 | 158.607 | 2241.5 | 25.84 | 47.714 | 6.41 | 1.282 | 4.146 | 8431.69 | 1.512 | 97.9 | 76.4 | 1457 | 23.86 | 5480.6 | 2677.9 | 2621.1 | 3878.6 | 1215.8 | 0.67384 | 5.429
2024-12-10 | 0:16 | Data | 0 | 33.642 | 32.028 | 167.767 | 7.64 | 158.562 | 2242.41 | 25.84 | 48.075 | 6.41 | 1.282 | 4.131 | 8431.69 | 1.614 | 97.9 | 76.3 | 1458 | 23.99 | 5480.6 | 2707.3 | 2627.1 | 3893.4 | 1215.8 | 0.67802 | 5.413
2024-12-10 | 0:16 | Data | 0 | 33.642 | 32.258 | 167.813 | 7.63 | 158.607 | 2241.5 | 25.84 | 47.623 | 6.4 | 1.278 | 4.114 | 8427.17 | 1.614 | 97.9 | 76.3 | 1456 | 23.81 | 5477.7 | 2700.4 | 2658.8 | 3914.3 | 1215.8 | 0.67411 | 5.39
2024-12-10 | 0:16 | Data | 0 | 34.074 | 32.278 | 167.903 | 7.64 | 158.652 | 2238.79 | 25.84 | 47.533 | 6.41 | 1.28 | 4.111 | 8436.21 | 1.634 | 97.9 | 76.3 | 1455 | 23.81 | 5483.5 | 2707 | 2627.2 | 3901.9 | 1215.8 | 0.67576 | 5.389
2024-12-10 | 0:16 | Data | 0 | 33.81 | 32.305 | 167.858 | 7.64 | 158.562 | 2238.79 | 25.84 | 47.533 | 6.4 | 1.287 | 4.12 | 8431.69 | 1.445 | 97.9 | 76.2 | 1454 | 23.81 | 5480.6 | 2675.8 | 2658.4 | 3905.8 | 1215.8 | 0.66732 | 5.408
2024-12-10 | 0:16 | Data | 0 | 33.858 | 32.15 | 167.903 | 7.64 | 158.607 | 2238.79 | 25.84 | 48.165 | 6.41 | 1.282 | 4.113 | 8445.26 | 1.83 | 97.8 | 76.2 | 1455 | 24.08 | 5489.4 | 2707.3 | 2623.6 | 3898.9 | 1215.8 | 0.67097 | 5.394
2024-12-10 | 0:16 | Data | 0 | 33.419 | 32.028 | 167.903 | 7.64 | 158.607 | 2233.37 | 25.84 | 47.894 | 6.41 | 1.282 | 4.122 | 8445.26 | 1.6 | 97.9 | 76.3 | 1452 | 23.95 | 5489.4 | 2694.6 | 2623.7 | 3889.8 | 1215.8 | 0.67592 | 5.404
2024-12-10 | 0:16 | Data | 0 | 33.426 | 31.799 | 167.767 | 7.64 | 158.517 | 2239.7 | 25.83 | 47.623 | 6.41 | 1.282 | 4.114 | 8454.3 | 1.614 | 97.9 | 76.2 | 1455 | 23.81 | 5495.3 | 2688.3 | 2620.1 | 3885.9 | 1215.8 | 0.67461 | 5.395
2024-12-10 | 0:16 | Data | 0 | 33.412 | 31.913 | 167.677 | 7.63 | 158.472 | 2235.18 | 25.84 | 47.894 | 6.41 | 1.282 | 4.096 | 8445.26 | 1.614 | 97.9 | 76.2 | 1453 | 23.95 | 5489.4 | 2719.1 | 2625.5 | 3904.6 | 1215.8 | 0.6781 | 5.379
2024-12-10 | 0:16 | Data | 0 | 33.642 | 32.015 | 167.722 | 7.63 | 158.517 | 2230.66 | 25.84 | 47.804 | 6.4 | 1.291 | 4.108 | 8436.21 | 1.641 | 97.9 | 76.1 | 1449 | 23.95 | 5483.5 | 2689.4 | 2628.9 | 3889.9 | 1215.8 | 0.67557 | 5.4
2024-12-10 | 0:16 | Data | 0 | 33.669 | 31.859 | 167.813 | 7.64 | 158.562 | 2227.04 | 25.84 | 47.623 | 6.4 | 1.284 | 4.112 | 8445.26 | 1.452 | 97.9 | 76.2 | 1448 | 23.86 | 5489.4 | 2673.8 | 2645.7 | 3893.3 | 1215.8 | 0.66975 | 5.396
2024-12-10 | 0:16 | Data | 0 | 33.412 | 32.028 | 167.677 | 7.63 | 158.517 | 2225.23 | 25.84 | 47.623 | 6.41 | 1.289 | 4.121 | 8409.08 | 1.56 | 97.9 | 76.2 | 1446 | 23.81 | 5465.9 | 2703.5 | 2643.5 | 3910 | 1215.8 | 0.67315 | 5.411
2024-12-10 | 0:16 | Data | 0 | 33.743 | 31.913 | 167.767 | 7.64 | 158.562 | 2225.23 | 25.83 | 47.623 | 6.41 | 1.289 | 4.134 | 8431.69 | 1.695 | 97.9 | 76.2 | 1446 | 23.86 | 5480.6 | 2712.8 | 2636.7 | 3910.5 | 1215.9 | 0.67627 | 5.422
2024-12-10 | 0:16 | Data | 0 | 33.642 | 31.974 | 167.813 | 7.64 | 158.562 | 2227.95 | 25.84 | 47.714 | 6.41 | 1.284 | 4.115 | 8409.08 | 1.661 | 97.9 | 76.2 | 1448 | 23.81 | 5465.9 | 2680.6 | 2631 | 3886 | 1215.9 | 0.67243 | 5.4
2024-12-10 | 0:16 | Data | 0 | 33.696 | 31.853 | 167.813 | 7.63 | 158.562 | 2227.95 | 25.83 | 47.623 | 6.4 | 1.27 | 4.103 | 8418.13 | 1.641 | 97.9 | 76.4 | 1448 | 23.81 | 5471.8 | 2694.9 | 2663.7 | 3919.8 | 1215.9 | 0.66826 | 5.372
2024-12-10 | 0:16 | Data | 0 | 33.439 | 32.197 | 167.813 | 7.63 | 158.517 | 2229.75 | 25.84 | 47.623 | 6.4 | 1.274 | 4.092 | 8431.69 | 1.614 | 97.9 | 76.3 | 1449 | 23.86 | 5480.6 | 2704.8 | 2633.3 | 3902.2 | 1215.9 | 0.6754 | 5.367
2024-12-10 | 0:17 | Data | 0 | 33.864 | 31.839 | 167.767 | 7.63 | 158.652 | 2228.85 | 25.84 | 47.623 | 6.4 | 1.283 | 4.13 | 8422.65 | 1.722 | 97.9 | 76.3 | 1448 | 23.81 | 5474.7 | 2699.4 | 2630.7 | 3895.3 | 1215.9 | 0.67624 | 5.412
2024-12-10 | 0:17 | Data | 0 | 33.534 | 32.143 | 167.813 | 7.64 | 158.607 | 2227.95 | 25.84 | 47.894 | 6.4 | 1.29 | 4.111 | 8409.08 | 1.458 | 97.9 | 76.1 | 1448 | 23.95 | 5465.9 | 2680.2 | 2655.2 | 3901.1 | 1215.9 | 0.66998 | 5.401
2024-12-10 | 0:17 | Data | 0 | 33.75 | 31.92 | 167.767 | 7.63 | 158.562 | 2227.04 | 25.84 | 47.623 | 6.4 | 1.282 | 4.103 | 8409.08 | 1.62 | 97.9 | 76.2 | 1448 | 23.81 | 5465.9 | 2708.5 | 2649.4 | 3918.8 | 1215.9 | 0.67362 | 5.384
2024-12-10 | 0:17 | Data | 0 | 33.642 | 31.859 | 167.677 | 7.64 | 158.472 | 2229.75 | 25.84 | 47.623 | 6.4 | 1.286 | 4.115 | 8418.13 | 1.438 | 97.9 | 76.2 | 1449 | 23.81 | 5471.8 | 2718.2 | 2637.6 | 3914.2 | 1215.9 | 0.67749 | 5.401
2024-12-10 | 0:17 | Data | 0 | 33.473 | 32.15 | 167.767 | 7.63 | 158.562 | 2230.66 | 25.84 | 47.804 | 6.4 | 1.278 | 4.118 | 8400.04 | 1.512 | 97.9 | 76.3 | 1450 | 23.86 | 5460 | 2673.9 | 2651.3 | 3897.8 | 1215.9 | 0.6728 | 5.396
2024-12-10 | 0:17 | Data | 0 | 34.087 | 32.21 | 167.903 | 7.64 | 158.652 | 2231.56 | 25.84 | 47.714 | 6.4 | 1.275 | 4.114 | 8409.08 | 1.924 | 97.9 | 76.3 | 1451 | 23.86 | 5465.9 | 2716.1 | 2636.4 | 3908.8 | 1215.9 | 0.67671 | 5.39
2024-12-10 | 0:17 | Data | 0 | 33.871 | 32.251 | 167.813 | 7.64 | 158.652 | 2233.37 | 25.84 | 47.623 | 6.41 | 1.289 | 4.136 | 8418.13 | 1.708 | 97.9 | 76.2 | 1452 | 23.81 | 5471.8 | 2715.2 | 2637.1 | 3911.4 | 1215.9 | 0.67623 | 5.423
2024-12-10 | 0:17 | Data | 0 | 33.844 | 32.055 | 167.858 | 7.64 | 158.562 | 2233.37 | 25.83 | 47.894 | 6.4 | 1.295 | 4.124 | 8445.26 | 1.782 | 97.9 | 76.1 | 1452 | 23.95 | 5489.4 | 2717.6 | 2631.2 | 3909 | 1215.9 | 0.67646 | 5.42
2024-12-10 | 0:17 | Data | 0 | 33.756 | 32.028 | 167.813 | 7.64 | 158.517 | 2233.37 | 25.83 | 47.623 | 6.4 | 1.283 | 4.073 | 8445.26 | 1.627 | 97.9 | 76 | 1452 | 23.81 | 5489.4 | 2724.5 | 2651.1 | 3929 | 1215.9 | 0.67701 | 5.356
2024-12-10 | 0:17 | Data | 0 | 33.696 | 32.055 | 167.767 | 7.64 | 158.517 | 2232.47 | 25.84 | 47.714 | 6.41 | 1.28 | 4.106 | 8449.78 | 1.566 | 97.9 | 76.2 | 1451 | 23.86 | 5492.4 | 2693.4 | 2619.3 | 3886 | 1215.9 | 0.6761 | 5.385
2024-12-10 | 0:17 | Data | 0 | 33.642 | 32.028 | 167.767 | 7.64 | 158.562 | 2232.47 | 25.84 | 47.533 | 6.4 | 1.283 | 4.113 | 8445.26 | 1.614 | 97.9 | 76.2 | 1451 | 23.81 | 5489.4 | 2690.9 | 2629.2 | 3890.8 | 1215.9 | 0.67433 | 5.397
2024-12-10 | 0:17 | Data | 0 | 33.655 | 32.035 | 167.858 | 7.64 | 158.562 | 2232.47 | 25.84 | 47.623 | 6.41 | 1.285 | 4.105 | 8445.26 | 1.607 | 97.9 | 76.2 | 1451 | 23.86 | 5489.4 | 2695.1 | 2644.4 | 3907.1 | 1215.9 | 0.67149 | 5.39
2024-12-10 | 0:17 | Data | 0 | 33.432 | 31.974 | 167.813 | 7.64 | 158.517 | 2233.37 | 25.84 | 47.623 | 6.4 | 1.282 | 4.102 | 8454.3 | 1.499 | 97.9 | 76.2 | 1452 | 23.81 | 5495.3 | 2717.2 | 2637.2 | 3911.7 | 1215.9 | 0.67719 | 5.382
2024-12-10 | 0:17 | Data | 0 | 33.466 | 32.028 | 167.767 | 7.64 | 158.607 | 2233.37 | 25.84 | 47.623 | 6.4 | 1.279 | 4.114 | 8454.3 | 1.593 | 97.9 | 76.3 | 1452 | 23.81 | 5495.3 | 2698.1 | 2632.2 | 3897 | 1215.9 | 0.67411 | 5.392
2024-12-10 | 0:17 | Data | 0 | 33.48 | 31.927 | 167.858 | 7.63 | 158.607 | 2235.18 | 25.84 | 47.623 | 6.41 | 1.29 | 4.106 | 8472.39 | 1.492 | 97.9 | 76.1 | 1453 | 23.81 | 5507.1 | 2697.2 | 2654.5 | 3911.3 | 1215.9 | 0.67375 | 5.396
2024-12-10 | 0:17 | Data | 0 | 33.561 | 32.028 | 167.858 | 7.64 | 158.607 | 2235.18 | 25.84 | 47.623 | 6.4 | 1.29 | 4.096 | 8431.69 | 1.398 | 97.9 | 76 | 1453 | 23.81 | 5480.6 | 2713 | 2664.7 | 3929.5 | 1215.9 | 0.67154 | 5.386
2024-12-10 | 0:17 | Data | 0 | 33.871 | 32.217 | 167.813 | 7.64 | 158.562 | 2235.18 | 25.84 | 47.623 | 6.4 | 1.286 | 4.098 | 8427.17 | 1.519 | 97.9 | 76.1 | 1453 | 23.81 | 5477.7 | 2706.3 | 2654.9 | 3918.1 | 1215.9 | 0.67702 | 5.384
2024-12-10 | 0:18 | Data | 0 | 33.696 | 32.035 | 167.903 | 7.64 | 158.607 | 2236.08 | 25.84 | 47.714 | 6.4 | 1.28 | 4.113 | 8427.17 | 1.627 | 97.9 | 76.3 | 1453 | 23.81 | 5477.7 | 2686.2 | 2661.1 | 3909.4 | 1215.9 | 0.66919 | 5.392
2024-12-10 | 0:18 | Data | 0 | 33.561 | 32.028 | 167.858 | 7.64 | 158.652 | 2235.18 | 25.84 | 47.623 | 6.4 | 1.285 | 4.114 | 8431.69 | 1.391 | 97.9 | 76.2 | 1453 | 23.77 | 5480.6 | 2691.4 | 2665.9 | 3922.6 | 1215.9 | 0.66755 | 5.399
2024-12-10 | 0:18 | Data | 0 | 33.817 | 32.082 | 167.948 | 7.64 | 158.562 | 2236.08 | 25.84 | 47.623 | 6.41 | 1.282 | 4.086 | 8418.13 | 1.728 | 97.9 | 76.1 | 1453 | 23.81 | 5471.8 | 2703.9 | 2641.1 | 3904.9 | 1215.9 | 0.67697 | 5.368
2024-12-10 | 0:18 | Data | 0 | 33.756 | 32.055 | 167.903 | 7.64 | 158.607 | 2236.08 | 25.84 | 47.623 | 6.4 | 1.279 | 4.105 | 8418.13 | 1.553 | 97.9 | 76.2 | 1453 | 23.77 | 5471.8 | 2696.5 | 2644.8 | 3904.6 | 1215.9 | 0.67533 | 5.384
2024-12-10 | 0:18 | Data | 0 | 33.979 | 32.042 | 167.903 | 7.64 | 158.607 | 2236.08 | 25.84 | 47.623 | 6.41 | 1.284 | 4.125 | 8400.04 | 1.627 | 97.9 | 76.2 | 1452 | 23.81 | 5460 | 2700.8 | 2630 | 3896.5 | 1215.9 | 0.67618 | 5.411
2024-12-10 | 0:18 | Data | 0 | 33.709 | 32.028 | 167.813 | 7.64 | 158.562 | 2235.18 | 25.84 | 47.623 | 6.41 | 1.287 | 4.115 | 8400.04 | 1.512 | 97.9 | 76.2 | 1453 | 23.86 | 5460 | 2709.5 | 2613.6 | 3890.7 | 1215.9 | 0.67729 | 5.403
2024-12-10 | 0:18 | Data | 0 | 33.696 | 32.028 | 167.858 | 7.64 | 158.517 | 2233.37 | 25.83 | 47.714 | 6.41 | 1.282 | 4.105 | 8395.51 | 1.62 | 97.9 | 76.2 | 1451 | 23.81 | 5457.1 | 2703.7 | 2628.2 | 3901.7 | 1215.9 | 0.67384 | 5.386
2024-12-10 | 0:18 | Data | 0 | 33.54 | 32.001 | 167.858 | 7.63 | 158.607 | 2238.79 | 25.84 | 47.714 | 6.4 | 1.291 | 4.106 | 8400.04 | 1.506 | 97.9 | 76.1 | 1455 | 23.81 | 5460 | 2688 | 2643 | 3898 | 1215.9 | 0.67316 | 5.4
2024-12-10 | 0:18 | Data | 0 | 33.473 | 32.028 | 167.677 | 7.64 | 158.562 | 2230.66 | 25.83 | 47.623 | 6.4 | 1.291 | 4.134 | 8381.95 | 1.398 | 97.9 | 76.2 | 1449 | 23.81 | 5448.3 | 2700.6 | 2634.4 | 3908.6 | 1215.9 | 0.67337 | 5.424
2024-12-10 | 0:18 | Data | 0 | 33.635 | 32.258 | 167.948 | 7.63 | 158.607 | 2227.04 | 25.84 | 47.623 | 6.4 | 1.284 | 4.137 | 8400.04 | 1.587 | 97.9 | 76.3 | 1448 | 23.81 | 5460 | 2719.8 | 2662.9 | 3934 | 1215.9 | 0.67209 | 5.42
2024-12-10 | 0:18 | Data | 0 | 33.858 | 32.204 | 167.858 | 7.64 | 158.562 | 2229.75 | 25.84 | 47.623 | 6.4 | 1.274 | 4.127 | 8395.51 | 1.836 | 97.9 | 76.4 | 1449 | 23.77 | 5457.1 | 2688.2 | 2642.2 | 3894.8 | 1215.9 | 0.67347 | 5.401
2024-12-10 | 0:18 | Data | 0 | 33.642 | 32.028 | 167.813 | 7.63 | 158.652 | 2228.85 | 25.84 | 47.623 | 6.4 | 1.286 | 4.106 | 8390.99 | 1.614 | 97.9 | 76.2 | 1449 | 23.81 | 5454.1 | 2688.6 | 2644.3 | 3898.7 | 1215.9 | 0.67171 | 5.392
2024-12-10 | 0:18 | Data | 0 | 33.675 | 31.927 | 167.813 | 7.64 | 158.607 | 2227.95 | 25.84 | 47.714 | 6.4 | 1.288 | 4.101 | 8395.51 | 1.614 | 97.9 | 76.1 | 1449 | 23.81 | 5457.1 | 2670.6 | 2644.3 | 3892.2 | 1215.9 | 0.66829 | 5.388
2024-12-10 | 0:18 | Data | 0 | 33.642 | 32.028 | 167.722 | 7.64 | 158.607 | 2227.95 | 25.83 | 47.623 | 6.4 | 1.294 | 4.101 | 8381.95 | 1.614 | 97.9 | 76 | 1448 | 23.81 | 5448.3 | 2698.1 | 2648.4 | 3907.9 | 1215.9 | 0.67356 | 5.395
2024-12-10 | 0:18 | Data | 0 | 33.844 | 32.251 | 167.858 | 7.64 | 158.652 | 2227.95 | 25.84 | 47.623 | 6.4 | 1.29 | 4.114 | 8390.99 | 1.533 | 97.9 | 76.1 | 1448 | 23.81 | 5454.1 | 2697.4 | 2661.2 | 3918.9 | 1215.9 | 0.67088 | 5.403
2024-12-10 | 0:18 | Data | 0 | 33.527 | 32.15 | 167.767 | 7.63 | 158.607 | 2225.23 | 25.84 | 47.623 | 6.4 | 1.282 | 4.116 | 8372.9 | 1.56 | 97.9 | 76.3 | 1447 | 23.81 | 5442.4 | 2727.9 | 2647 | 3923.7 | 1215.9 | 0.67902 | 5.4
2024-12-10 | 0:18 | Data | 0 | 33.642 | 32.204 | 167.858 | 7.63 | 158.562 | 2218 | 25.84 | 47.623 | 6.41 | 1.278 | 4.115 | 8372.9 | 1.614 | 97.9 | 76.3 | 1442 | 23.81 | 5442.4 | 2700.6 | 2646.5 | 3904.7 | 1215.9 | 0.67364 | 5.392
2024-12-10 | 0:18 | Data | 0 | 33.642 | 32.042 | 167.858 | 7.64 | 158.562 | 2218.91 | 25.84 | 47.533 | 6.41 | 1.282 | 4.134 | 8368.38 | 1.681 | 97.9 | 76.3 | 1442 | 23.77 | 5439.4 | 2665.8 | 2654.8 | 3894.4 | 1215.9 | 0.66488 | 5.416
2024-12-10 | 0:19 | Data | 0 | 33.486 | 31.92 | 167.767 | 7.63 | 158.562 | 2218.91 | 25.83 | 47.623 | 6.41 | 1.282 | 4.115 | 8377.43 | 1.614 | 97.9 | 76.2 | 1442 | 23.81 | 5445.3 | 2702.6 | 2633.7 | 3899.4 | 1215.9 | 0.67547 | 5.399
2024-12-10 | 0:19 | Data | 0 | 33.817 | 32.035 | 167.858 | 7.64 | 158.652 | 2218.91 | 25.84 | 47.714 | 6.4 | 1.295 | 4.095 | 8386.47 | 1.647 | 97.8 | 76 | 1442 | 23.86 | 5451.2 | 2690.5 | 2658.4 | 3907.2 | 1216 | 0.67074 | 5.389
2024-12-10 | 0:19 | Data | 0 | 33.756 | 32.042 | 167.813 | 7.64 | 158.517 | 2218.91 | 25.83 | 47.623 | 6.4 | 1.277 | 4.092 | 8372.9 | 1.809 | 97.9 | 76.2 | 1443 | 23.81 | 5442.4 | 2703.1 | 2651.8 | 3909.5 | 1216 | 0.67482 | 5.368
2024-12-10 | 0:19 | Data | 0 | 33.77 | 32.028 | 167.813 | 7.64 | 158.607 | 2218 | 25.83 | 47.623 | 6.41 | 1.275 | 4.104 | 8381.95 | 1.62 | 97.9 | 76.3 | 1442 | 23.81 | 5448.3 | 2680 | 2655.1 | 3901.3 | 1216 | 0.66895 | 5.379
2024-12-10 | 0:19 | Data | 0 | 33.648 | 32.055 | 167.813 | 7.64 | 158.562 | 2218.91 | 25.84 | 47.623 | 6.41 | 1.292 | 4.119 | 8386.47 | 1.762 | 97.9 | 76.1 | 1442 | 23.81 | 5451.2 | 2675.2 | 2653.9 | 3899.1 | 1216 | 0.66618 | 5.411
2024-12-10 | 0:19 | Data | 0 | 33.419 | 32.028 | 167.858 | 7.64 | 158.698 | 2218.91 | 25.84 | 47.623 | 6.41 | 1.29 | 4.119 | 8377.43 | 1.566 | 97.8 | 76.2 | 1442 | 23.81 | 5445.3 | 2699.3 | 2643.3 | 3903.7 | 1216 | 0.67372 | 5.409
2024-12-10 | 0:19 | Data | 0 | 33.696 | 32.089 | 167.813 | 7.64 | 158.607 | 2216.2 | 25.84 | 47.714 | 6.4 | 1.279 | 4.105 | 8390.99 | 1.458 | 97.8 | 76.2 | 1441 | 23.81 | 5454.1 | 2700.5 | 2629.7 | 3895.7 | 1216 | 0.67599 | 5.384
2024-12-10 | 0:19 | Data | 0 | 33.756 | 32.251 | 167.858 | 7.64 | 158.607 | 2217.1 | 25.83 | 47.623 | 6.4 | 1.291 | 4.129 | 8400.04 | 1.614 | 97.9 | 76.2 | 1441 | 23.86 | 5460 | 2696.2 | 2648 | 3907.3 | 1216 | 0.67433 | 5.42
2024-12-10 | 0:19 | Data | 0 | 33.642 | 32.028 | 167.767 | 7.64 | 158.562 | 2216.2 | 25.84 | 47.623 | 6.41 | 1.288 | 4.139 | 8390.99 | 1.614 | 97.9 | 76.3 | 1441 | 23.81 | 5454.1 | 2705.7 | 2640.7 | 3904.2 | 1216 | 0.67665 | 5.427
2024-12-10 | 0:19 | Data | 0 | 33.763 | 32.312 | 167.993 | 7.64 | 158.652 | 2218.91 | 25.84 | 47.533 | 6.41 | 1.274 | 4.107 | 8381.95 | 1.438 | 97.9 | 76.3 | 1442 | 23.77 | 5448.3 | 2698.6 | 2655.6 | 3911.5 | 1216 | 0.67388 | 5.382
2024-12-10 | 0:19 | Data | 0 | 33.642 | 32.028 | 167.767 | 7.63 | 158.562 | 2218.91 | 25.84 | 47.623 | 6.41 | 1.276 | 4.093 | 8386.47 | 1.728 | 97.9 | 76.2 | 1442 | 23.81 | 5451.2 | 2703.3 | 2652.3 | 3915 | 1216 | 0.67281 | 5.369
2024-12-10 | 0:19 | Data | 0 | 34.067 | 32.318 | 167.948 | 7.64 | 158.698 | 2222.52 | 25.84 | 47.623 | 6.41 | 1.287 | 4.124 | 8377.43 | 1.668 | 97.9 | 76.2 | 1445 | 23.81 | 5445.3 | 2695.6 | 2653.5 | 3911 | 1216 | 0.66935 | 5.41
2024-12-10 | 0:19 | Data | 0 | 33.817 | 32.089 | 167.903 | 7.64 | 158.607 | 2225.23 | 25.83 | 47.623 | 6.4 | 1.29 | 4.098 | 8381.95 | 1.715 | 97.9 | 76.1 | 1446 | 23.81 | 5448.3 | 2690.1 | 2635.8 | 3893 | 1216 | 0.67262 | 5.388
2024-12-10 | 0:19 | Data | 0 | 33.642 | 32.129 | 167.813 | 7.63 | 158.517 | 2221.62 | 25.84 | 47.623 | 6.41 | 1.288 | 4.11 | 8386.47 | 1.438 | 97.9 | 76.1 | 1445 | 23.81 | 5451.2 | 2697.2 | 2667.5 | 3921 | 1216 | 0.66948 | 5.398
2024-12-10 | 0:19 | Data | 0 | 33.642 | 32.15 | 167.903 | 7.63 | 158.607 | 2225.23 | 25.84 | 47.714 | 6.4 | 1.283 | 4.107 | 8390.99 | 1.695 | 97.9 | 76.2 | 1446 | 23.81 | 5454.1 | 2714.3 | 2622.7 | 3902.3 | 1216 | 0.67759 | 5.391
2024-12-10 | 0:19 | Data | 0 | 33.655 | 31.988 | 167.948 | 7.64 | 158.607 | 2225.23 | 25.83 | 47.623 | 6.4 | 1.279 | 4.102 | 8390.99 | 1.722 | 97.9 | 76.2 | 1446 | 23.86 | 5454.1 | 2682.8 | 2626 | 3882.6 | 1216 | 0.67275 | 5.38
2024-12-10 | 0:19 | Data | 0 | 33.642 | 32.204 | 167.813 | 7.64 | 158.607 | 2223.43 | 25.84 | 47.623 | 6.41 | 1.272 | 4.113 | 8395.51 | 1.492 | 97.9 | 76.4 | 1445 | 23.81 | 5457.1 | 2693.1 | 2616.3 | 3888.5 | 1216 | 0.67718 | 5.385
2024-12-10 | 0:19 | Data | 0 | 34.074 | 32.318 | 167.993 | 7.64 | 158.743 | 2226.14 | 25.84 | 47.623 | 6.4 | 1.282 | 4.11 | 8400.04 | 1.782 | 97.9 | 76.2 | 1447 | 23.81 | 5460 | 2678.2 | 2622 | 3875.9 | 1216 | 0.67298 | 5.392
2024-12-10 | 0:20 | Data | 0 | 34.101 | 32.035 | 167.858 | 7.63 | 158.652 | 2229.75 | 25.84 | 47.262 | 6.41 | 1.284 | 4.099 | 8395.51 | 1.715 | 97.9 | 76.2 | 1449 | 23.63 | 5457.1 | 2692.6 | 2625.8 | 3893.4 | 1216 | 0.67401 | 5.385
2024-12-10 | 0:20 | Data | 0 | 33.655 | 32.035 | 167.903 | 7.64 | 158.652 | 2233.37 | 25.84 | 47.714 | 6.41 | 1.288 | 4.115 | 8386.47 | 1.499 | 97.9 | 76.2 | 1452 | 23.81 | 5451.2 | 2693.9 | 2632.5 | 3895.5 | 1216 | 0.67431 | 5.402
2024-12-10 | 0:20 | Data | 0 | 33.898 | 32.163 | 167.993 | 7.64 | 158.652 | 2233.37 | 25.84 | 47.533 | 6.41 | 1.282 | 4.124 | 8400.04 | 1.809 | 97.9 | 76.3 | 1451 | 23.72 | 5460 | 2699.6 | 2621.1 | 3887 | 1216 | 0.67647 | 5.406
2024-12-10 | 0:20 | Data | 0 | 33.817 | 32.372 | 167.903 | 7.64 | 158.652 | 2236.08 | 25.84 | 47.353 | 6.4 | 1.283 | 4.108 | 8400.04 | 1.593 | 97.9 | 76.2 | 1453 | 23.68 | 5460 | 2686.7 | 2631 | 3891.5 | 1216 | 0.67555 | 5.392
2024-12-10 | 0:20 | Data | 0 | 33.871 | 32.251 | 167.903 | 7.64 | 158.698 | 2236.08 | 25.84 | 47.443 | 6.41 | 1.287 | 4.125 | 8400.04 | 1.512 | 97.9 | 76.2 | 1453 | 23.68 | 5460 | 2674 | 2633.9 | 3881.8 | 1216 | 0.67109 | 5.412
2024-12-10 | 0:20 | Data | 0 | 33.817 | 32.055 | 167.903 | 7.64 | 158.698 | 2236.08 | 25.84 | 47.714 | 6.41 | 1.289 | 4.111 | 8400.04 | 1.695 | 97.9 | 76.1 | 1453 | 23.86 | 5460 | 2690.1 | 2637.3 | 3896.9 | 1216 | 0.67251 | 5.4
2024-12-10 | 0:20 | Data | 0 | 33.972 | 32.372 | 167.858 | 7.63 | 158.607 | 2236.08 | 25.84 | 47.353 | 6.41 | 1.276 | 4.088 | 8400.04 | 1.492 | 97.9 | 76.2 | 1453 | 23.72 | 5460 | 1618.9 | 2061 | 2634.7 | 1216 | 0.61167 | 5.364
2024-12-10 | 0:20 | Data | 0 | 33.642 | 32.204 | 167.858 | 7.63 | 158.607 | 2233.37 | 25.84 | 47.443 | 6.4 | 1.276 | 4.088 | 8431.69 | 1.614 | 97.9 | 76.2 | 1452 | 23.72 | 5480.6 | 1607.9 | 2059.8 | 2627.6 | 1216 | 0.6088 | 5.364
2024-12-10 | 0:20 | Data | 0 | 33.871 | 32.055 | 167.858 | 7.63 | 158.652 | 2232.47 | 25.84 | 47.623 | 6.41 | 1.283 | 4.103 | 8400.04 | 1.614 | 97.9 | 76.2 | 1452 | 23.81 | 5460 | 1600.5 | 2071.3 | 2631.6 | 1216 | 0.60868 | 5.386
2024-12-10 | 0:20 | Data | 0 | 33.864 | 32.035 | 167.767 | 7.63 | 158.698 | 2232.47 | 25.83 | 47.172 | 6.41 | 1.282 | 4.111 | 8404.56 | 1.654 | 97.9 | 76.2 | 1451 | 23.59 | 5463 | 1610.7 | 2058.7 | 2627 | 1216 | 0.61057 | 5.392
2024-12-10 | 0:20 | Data | 0 | 33.655 | 32.042 | 167.948 | 7.63 | 158.698 | 2233.37 | 25.84 | 47.353 | 6.4 | 1.282 | 4.119 | 8404.56 | 1.6 | 97.9 | 76.3 | 1451 | 23.68 | 5463 | 1618.6 | 2065.1 | 2637.4 | 1216 | 0.61115 | 5.401
2024-12-10 | 0:20 | Data | 0 | 33.75 | 32.258 | 167.813 | 7.63 | 158.607 | 2233.37 | 25.83 | 47.443 | 6.4 | 1.291 | 4.115 | 8400.04 | 1.452 | 97.9 | 76.1 | 1452 | 23.68 | 5460 | 1605.1 | 2041.1 | 2609.3 | 1216 | 0.61225 | 5.406
2024-12-10 | 0:20 | Data | 0 | 33.642 | 32.028 | 167.858 | 7.64 | 158.698 | 2227.95 | 25.85 | 47.353 | 6.4 | 1.297 | 4.132 | 8400.04 | 1.614 | 97.9 | 76.1 | 1448 | 23.68 | 5460 | 1608.1 | 2052.7 | 2620 | 1216 | 0.6118 | 5.429
2024-12-10 | 0:20 | Data | 0 | 33.446 | 32.204 | 167.858 | 7.64 | 158.607 | 2230.66 | 25.84 | 47.353 | 6.4 | 1.285 | 4.126 | 8400.04 | 1.391 | 97.9 | 76.3 | 1449 | 23.68 | 5460 | 1615.9 | 2040.9 | 2617.6 | 1216 | 0.61473 | 5.412
2024-12-10 | 0:20 | Data | 0 | 33.642 | 32.204 | 167.993 | 7.63 | 158.698 | 2227.04 | 25.84 | 47.443 | 6.4 | 1.279 | 4.096 | 8404.56 | 1.614 | 97.9 | 76.2 | 1448 | 23.72 | 5463 | 1592.1 | 2053.4 | 2613.9 | 1216 | 0.60629 | 5.373
2024-12-10 | 0:20 | Data | 0 | 33.716 | 32.035 | 167.903 | 7.63 | 158.743 | 2228.85 | 25.84 | 47.353 | 6.41 | 1.291 | 4.111 | 8404.56 | 1.418 | 97.9 | 76.1 | 1448 | 23.68 | 5463 | 1611 | 2048.3 | 2617.5 | 1216 | 0.61214 | 5.402
2024-12-10 | 0:20 | Data | 0 | 33.756 | 31.859 | 167.813 | 7.64 | 158.607 | 2227.95 | 25.84 | 47.443 | 6.4 | 1.29 | 4.134 | 8400.04 | 1.728 | 97.9 | 76.2 | 1448 | 23.68 | 5460 | 1628.4 | 2031.5 | 2615 | 1216 | 0.62034 | 5.423
2024-12-10 | 0:20 | Data | 0 | 33.648 | 32.028 | 167.858 | 7.64 | 158.652 | 2227.04 | 25.84 | 47.353 | 6.4 | 1.282 | 4.105 | 8390.99 | 1.627 | 97.9 | 76.2 | 1448 | 23.72 | 5454.1 | 1600.2 | 2049.4 | 2612.4 | 1216 | 0.61088 | 5.387
2024-12-10 | 0:21 | Data | 0 | 33.473 | 32.116 | 167.813 | 7.64 | 158.562 | 2227.04 | 25.84 | 47.443 | 6.4 | 1.283 | 4.091 | 8386.47 | 1.391 | 97.9 | 76.1 | 1448 | 23.68 | 5451.2 | 1588.2 | 2017.1 | 2580.9 | 1216 | 0.61151 | 5.374
2024-12-10 | 0:21 | Data | 0 | 33.635 | 32.028 | 167.858 | 7.63 | 158.607 | 2223.43 | 25.84 | 47.353 | 6.41 | 1.289 | 4.095 | 8390.99 | 1.715 | 97.9 | 76.1 | 1445 | 23.68 | 5454.1 | 1612.5 | 2026.2 | 2605.6 | 1216 | 0.61603 | 5.384
2024-12-10 | 0:21 | Data | 0 | 33.594 | 32.028 | 167.813 | 7.63 | 158.607 | 2224.33 | 25.84 | 47.533 | 6.41 | 1.287 | 4.074 | 8372.9 | 1.607 | 97.9 | 76 | 1445 | 23.81 | 5442.4 | 1601.3 | 2037.3 | 2606.2 | 1216 | 0.61155 | 5.361
2024-12-10 | 0:21 | Data | 0 | 33.844 | 32.204 | 167.903 | 7.64 | 158.562 | 2221.62 | 25.84 | 47.623 | 6.4 | 1.283 | 4.071 | 8386.47 | 1.58 | 97.9 | 76 | 1445 | 23.81 | 5451.2 | 1609.5 | 2050.2 | 2620.8 | 1216 | 0.61071 | 5.354
2024-12-10 | 0:21 | Data | 0 | 33.756 | 32.251 | 167.948 | 7.63 | 158.652 | 2221.62 | 25.84 | 47.804 | 6.4 | 1.287 | 4.11 | 8390.99 | 1.614 | 97.9 | 76.2 | 1443 | 23.81 | 5454.1 | 1618.1 | 2041.7 | 2617.4 | 1216 | 0.61791 | 5.397
2024-12-10 | 0:21 | Data | 0 | 33.844 | 32.359 | 167.858 | 7.64 | 158.652 | 2220.72 | 25.83 | 47.714 | 6.4 | 1.284 | 4.127 | 8381.95 | 1.614 | 97.8 | 76.3 | 1443 | 23.86 | 5448.3 | 1621.1 | 2051.7 | 2629.1 | 1216 | 0.61681 | 5.411
2024-12-10 | 0:21 | Data | 0 | 33.885 | 32.055 | 167.948 | 7.63 | 158.743 | 2218.91 | 25.84 | 47.623 | 6.41 | 1.292 | 4.133 | 8390.99 | 1.674 | 97.8 | 76.2 | 1442 | 23.81 | 5454.1 | 1615.2 | 2032.3 | 2607.3 | 1216 | 0.61731 | 5.425
2024-12-10 | 0:21 | Data | 0 | 34.04 | 32.271 | 167.948 | 7.64 | 158.698 | 2220.72 | 25.84 | 47.623 | 6.4 | 1.275 | 4.129 | 8381.95 | 1.647 | 97.9 | 76.4 | 1443 | 23.81 | 5448.3 | 1614.9 | 2040.9 | 2616.6 | 1216 | 0.61493 | 5.404
2024-12-10 | 0:21 | Data | 0 | 33.804 | 32.258 | 167.903 | 7.63 | 158.607 | 2218.91 | 25.82 | 47.623 | 6.41 | 1.29 | 4.121 | 8386.47 | 1.607 | 97.8 | 76.2 | 1442 | 23.86 | 5451.2 | 1634.2 | 2061.6 | 2641.8 | 1216 | 0.617 | 5.411
2024-12-10 | 0:21 | Data | 0 | 33.871 | 32.237 | 167.858 | 7.64 | 158.698 | 2218.91 | 25.84 | 47.623 | 6.41 | 1.288 | 4.138 | 8372.9 | 1.708 | 97.9 | 76.3 | 1442 | 23.81 | 5442.4 | 1610.9 | 2038.7 | 2610.5 | 1216 | 0.61326 | 5.425
2024-12-10 | 0:21 | Data | 0 | 33.743 | 32.028 | 167.858 | 7.63 | 158.562 | 2218.91 | 25.83 | 47.623 | 6.4 | 1.284 | 4.129 | 8377.43 | 1.512 | 97.9 | 76.3 | 1442 | 23.81 | 5445.3 | 1605.3 | 2040.4 | 2609 | 1216 | 0.61364 | 5.413
2024-12-10 | 0:21 | Data | 0 | 33.925 | 32.305 | 167.903 | 7.64 | 158.743 | 2222.52 | 25.84 | 47.623 | 6.41 | 1.293 | 4.125 | 8359.34 | 1.715 | 97.9 | 76.1 | 1445 | 23.81 | 5433.6 | 1602.6 | 2025.6 | 2604.2 | 1216 | 0.61761 | 5.419
2024-12-10 | 0:21 | Data | 0 | 33.635 | 32.237 | 167.903 | 7.64 | 158.652 | 2218.91 | 25.84 | 47.353 | 6.41 | 1.292 | 4.129 | 8368.38 | 1.607 | 97.9 | 76.2 | 1442 | 23.68 | 5439.4 | 1591 | 2020.6 | 2584.6 | 1216 | 0.6126 | 5.421
2024-12-10 | 0:21 | Data | 0 | 33.534 | 32.021 | 167.767 | 7.63 | 158.607 | 2218.91 | 25.84 | 47.623 | 6.4 | 1.288 | 4.112 | 8400.04 | 1.607 | 97.9 | 76.1 | 1442 | 23.81 | 5460 | 1612.5 | 2034.9 | 2609.9 | 1216 | 0.61548 | 5.4
2024-12-10 | 0:21 | Data | 0 | 33.48 | 32.123 | 167.903 | 7.63 | 158.652 | 2220.72 | 25.84 | 47.623 | 6.41 | 1.286 | 4.112 | 8409.08 | 1.438 | 97.9 | 76.2 | 1442 | 23.81 | 5465.9 | 1598.1 | 2040.7 | 2606 | 1216 | 0.61018 | 5.398
2024-12-10 | 0:21 | Data | 0 | 33.858 | 32.082 | 167.903 | 7.63 | 158.607 | 2218.91 | 25.84 | 47.623 | 6.41 | 1.295 | 4.105 | 8418.13 | 1.607 | 97.9 | 76 | 1442 | 23.81 | 5471.8 | 1610.4 | 2055.1 | 2623.5 | 1216.1 | 0.61122 | 5.401
2024-12-10 | 0:21 | Data | 0 | 33.642 | 32.028 | 167.722 | 7.63 | 158.517 | 2222.52 | 25.84 | 47.623 | 6.4 | 1.291 | 4.099 | 8409.08 | 1.614 | 97.9 | 76.1 | 1445 | 23.81 | 5465.9 | 1617.7 | 2038.7 | 2618.5 | 1216.1 | 0.61208 | 5.39
2024-12-10 | 0:22 | Data | 0 | 33.689 | 31.927 | 167.813 | 7.63 | 158.562 | 2225.23 | 25.83 | 47.623 | 6.4 | 1.288 | 4.118 | 8418.13 | 1.695 | 97.9 | 76.2 | 1446 | 23.81 | 5471.8 | 1621.4 | 2031 | 2611.5 | 1216.1 | 0.61888 | 5.406
2024-12-10 | 0:22 | Data | 0 | 34.101 | 31.961 | 167.993 | 7.63 | 158.698 | 2227.04 | 25.84 | 47.623 | 6.4 | 1.287 | 4.126 | 8418.13 | 1.674 | 97.9 | 76.2 | 1447 | 23.81 | 5471.8 | 1617.2 | 2040.6 | 2616 | 1216.1 | 0.61652 | 5.413
2024-12-10 | 0:22 | Data | 0 | 33.669 | 32.028 | 167.858 | 7.63 | 158.607 | 2218.91 | 25.84 | 47.623 | 6.41 | 1.282 | 4.105 | 8418.13 | 1.614 | 97.9 | 76.2 | 1443 | 23.77 | 5471.8 | 1623.5 | 2029.9 | 2614.1 | 1216.1 | 0.61846 | 5.386
2024-12-10 | 0:22 | Data | 0 | 33.844 | 32.109 | 167.903 | 7.64 | 158.562 | 2222.52 | 25.84 | 47.623 | 6.41 | 1.285 | 4.102 | 8418.13 | 1.411 | 97.9 | 76.1 | 1445 | 23.81 | 5471.8 | 1606.8 | 2027.3 | 2601.8 | 1216.1 | 0.61347 | 5.387
2024-12-10 | 0:22 | Data | 0 | 33.709 | 31.927 | 167.858 | 7.64 | 158.562 | 2222.52 | 25.84 | 47.623 | 6.41 | 1.296 | 4.091 | 8440.74 | 1.431 | 97.9 | 75.9 | 1445 | 23.81 | 5486.5 | 1625.3 | 2029.6 | 2613.7 | 1216.1 | 0.61908 | 5.387
2024-12-10 | 0:22 | Data | 0 | 33.412 | 32.244 | 167.767 | 7.64 | 158.607 | 2225.23 | 25.84 | 47.623 | 6.41 | 1.286 | 4.124 | 8431.69 | 1.587 | 97.9 | 76.2 | 1446 | 23.81 | 5480.6 | 1609.5 | 2022.2 | 2599.1 | 1216.1 | 0.61683 | 5.409
2024-12-10 | 0:22 | Data | 0 | 33.547 | 32.035 | 167.948 | 7.63 | 158.607 | 2223.43 | 25.84 | 47.714 | 6.4 | 1.277 | 4.118 | 8440.74 | 1.769 | 97.9 | 76.3 | 1444 | 23.86 | 5486.5 | 1607.1 | 2032.6 | 2605.6 | 1216.1 | 0.61453 | 5.395
2024-12-10 | 0:22 | Data | 0 | 33.844 | 32.258 | 167.858 | 7.64 | 158.607 | 2223.43 | 25.84 | 47.623 | 6.4 | 1.28 | 4.088 | 8440.74 | 1.722 | 97.9 | 76.2 | 1445 | 23.81 | 5486.5 | 1620 | 2036.5 | 2617.5 | 1216.1 | 0.61794 | 5.366
2024-12-10 | 0:22 | Data | 0 | 33.642 | 31.812 | 167.677 | 7.64 | 158.472 | 2227.95 | 25.82 | 47.623 | 6.4 | 1.296 | 4.094 | 8418.13 | 1.614 | 97.9 | 76 | 1448 | 23.81 | 5471.8 | 1606.3 | 2050.4 | 2619.1 | 1216.1 | 0.61198 | 5.39
2024-12-10 | 0:22 | Data | 0 | 33.844 | 32.028 | 167.858 | 7.63 | 158.607 | 2227.95 | 25.84 | 47.623 | 6.4 | 1.291 | 4.076 | 8400.04 | 1.654 | 97.9 | 75.9 | 1448 | 23.86 | 5460 | 1620.1 | 2029.4 | 2612 | 1216.1 | 0.61706 | 5.366
2024-12-10 | 0:22 | Data | 0 | 33.588 | 32.028 | 167.813 | 7.63 | 158.562 | 2227.95 | 25.84 | 47.714 | 6.4 | 1.285 | 4.096 | 8409.08 | 1.776 | 97.9 | 76.1 | 1448 | 23.81 | 5465.9 | 1648.2 | 2065.3 | 2654.8 | 1216.1 | 0.61887 | 5.381
2024-12-10 | 0:22 | Data | 0 | 33.439 | 32.028 | 167.813 | 7.64 | 158.562 | 2227.95 | 25.84 | 47.533 | 6.4 | 1.277 | 4.102 | 8418.13 | 1.506 | 97.9 | 76.3 | 1448 | 23.77 | 5471.8 | 1630.5 | 2050.6 | 2633.3 | 1216.1 | 0.6166 | 5.378
2024-12-10 | 0:22 | Data | 0 | 33.372 | 32.021 | 167.813 | 7.63 | 158.607 | 2227.95 | 25.84 | 47.623 | 6.4 | 1.286 | 4.11 | 8418.13 | 1.587 | 97.9 | 76.2 | 1448 | 23.77 | 5471.8 | 1632.4 | 2080.7 | 2658.6 | 1216.1 | 0.61296 | 5.395
2024-12-10 | 0:22 | Data | 0 | 33.642 | 32.143 | 167.903 | 7.64 | 158.517 | 2227.95 | 25.84 | 47.623 | 6.41 | 1.287 | 4.114 | 8418.13 | 1.614 | 97.9 | 76.2 | 1448 | 23.86 | 5471.8 | 1621.8 | 2058.5 | 2638.2 | 1216.1 | 0.61189 | 5.401
2024-12-10 | 0:22 | Data | 0 | 33.635 | 32.116 | 167.767 | 7.64 | 158.517 | 2229.75 | 25.83 | 47.623 | 6.4 | 1.278 | 4.127 | 8418.13 | 1.506 | 97.9 | 76.4 | 1450 | 23.81 | 5471.8 | 1626.5 | 2046.5 | 2628.4 | 1216.1 | 0.61619 | 5.405
2024-12-10 | 0:22 | Data | 0 | 33.635 | 32.028 | 167.767 | 7.63 | 158.562 | 2227.95 | 25.83 | 47.623 | 6.4 | 1.276 | 4.103 | 8418.13 | 1.614 | 97.9 | 76.3 | 1449 | 23.81 | 5471.8 | 1628 | 2061.9 | 2644 | 1216.1 | 0.61195 | 5.378
2024-12-10 | 0:22 | Data | 0 | 33.419 | 31.974 | 167.632 | 7.64 | 158.562 | 2233.37 | 25.85 | 47.623 | 6.4 | 1.279 | 4.089 | 8400.04 | 1.614 | 97.9 | 76.2 | 1452 | 23.81 | 5460 | 1622.6 | 2057.9 | 2635.6 | 1216.1 | 0.61334 | 5.368
2024-12-10 | 0:22 | Data | 0 | 33.642 | 32.237 | 167.767 | 7.64 | 158.562 | 2232.47 | 25.84 | 47.623 | 6.4 | 1.285 | 4.089 | 8381.95 | 1.614 | 97.9 | 76.1 | 1451 | 23.77 | 5448.3 | 1633 | 2042.8 | 2631.2 | 1216.1 | 0.61751 | 5.374
2024-12-10 | 0:23 | Data | 0 | 33.81 | 32.204 | 167.767 | 7.64 | 158.607 | 2236.08 | 25.84 | 47.623 | 6.4 | 1.286 | 4.121 | 8395.51 | 1.836 | 97.9 | 76.2 | 1453 | 23.86 | 5457.1 | 1623 | 2047 | 2625.7 | 1216.1 | 0.61543 | 5.408
2024-12-10 | 0:23 | Data | 0 | 33.439 | 31.92 | 167.767 | 7.64 | 158.517 | 2232.47 | 25.84 | 47.623 | 6.4 | 1.293 | 4.134 | 8400.04 | 1.607 | 97.9 | 76.2 | 1451 | 23.81 | 5460 | 1622.2 | 2047.4 | 2626.8 | 1216.1 | 0.61464 | 5.427
2024-12-10 | 0:23 | Data | 0 | 33.844 | 32.035 | 167.903 | 7.63 | 158.652 | 2231.56 | 25.84 | 47.714 | 6.41 | 1.291 | 4.11 | 8400.04 | 1.809 | 97.9 | 76.1 | 1450 | 23.81 | 5460 | 1646.3 | 2065.2 | 2655.8 | 1216.1 | 0.61744 | 5.4
2024-12-10 | 0:23 | Data | 0 | 33.642 | 32.028 | 167.767 | 7.64 | 158.562 | 2230.66 | 25.84 | 47.623 | 6.41 | 1.289 | 4.11 | 8400.04 | 1.614 | 97.9 | 76.1 | 1449 | 23.81 | 5460 | 1643.9 | 2054.2 | 2645.3 | 1216.1 | 0.61962 | 5.398
2024-12-10 | 0:23 | Data | 0 | 33.615 | 32.244 | 167.858 | 7.63 | 158.517 | 2227.04 | 25.84 | 47.623 | 6.4 | 1.287 | 4.124 | 8400.04 | 1.56 | 97.9 | 76.2 | 1448 | 23.81 | 5460 | 1637 | 2056.7 | 2641.6 | 1216.1 | 0.61746 | 5.41
2024-12-10 | 0:23 | Data | 0 | 33.756 | 31.832 | 167.767 | 7.63 | 158.562 | 2234.27 | 25.84 | 47.623 | 6.4 | 1.286 | 4.091 | 8395.51 | 1.755 | 97.9 | 76.1 | 1451 | 23.81 | 5457.1 | 1628.5 | 2057.9 | 2638.8 | 1216.1 | 0.61542 | 5.376
2024-12-10 | 0:23 | Data | 0 | 33.615 | 32.028 | 167.858 | 7.63 | 158.562 | 2225.23 | 25.84 | 47.623 | 6.4 | 1.285 | 4.098 | 8418.13 | 1.789 | 97.9 | 76.1 | 1446 | 23.77 | 5471.8 | 1634 | 2049 | 2634.5 | 1216.1 | 0.6183 | 5.383
2024-12-10 | 0:23 | Data | 0 | 33.925 | 31.873 | 167.813 | 7.64 | 158.652 | 2221.62 | 25.84 | 47.623 | 6.4 | 1.278 | 4.113 | 8418.13 | 1.634 | 97.9 | 76.3 | 1445 | 23.81 | 5471.8 | 1619.7 | 2045.9 | 2625.2 | 1216.1 | 0.61417 | 5.391
2024-12-10 | 0:23 | Data | 0 | 33.635 | 32.028 | 167.767 | 7.63 | 158.562 | 2224.33 | 25.82 | 47.714 | 6.41 | 1.275 | 4.096 | 8418.13 | 1.438 | 97.9 | 76.3 | 1446 | 23.9 | 5471.8 | 2748.8 | 2648 | 3949.5 | 1216.1 | 0.67809 | 5.373
2024-12-10 | 0:23 | Data | 0 | 34.033 | 32.089 | 167.858 | 7.64 | 158.652 | 2225.23 | 25.83 | 47.623 | 6.4 | 1.277 | 4.087 | 8418.13 | 1.688 | 97.9 | 76.2 | 1446 | 23.81 | 5471.8 | 2732.4 | 2650.7 | 3936.2 | 1216.1 | 0.67889 | 5.365
2024-12-10 | 0:23 | Data | 0 | 33.642 | 32.028 | 167.813 | 7.64 | 158.517 | 2225.23 | 25.84 | 47.623 | 6.4 | 1.285 | 4.097 | 8400.04 | 1.614 | 97.9 | 76.1 | 1446 | 23.81 | 5460 | 2635 | 2645.8 | 3869.9 | 1216.1 | 0.66248 | 5.383
2024-12-10 | 0:23 | Data | 0 | 33.412 | 31.913 | 167.722 | 7.64 | 158.426 | 2222.52 | 25.84 | 47.623 | 6.41 | 1.294 | 4.085 | 8400.04 | 1.789 | 97.9 | 75.9 | 1445 | 23.77 | 5460 | 2654.1 | 2626.4 | 3860.3 | 1216.1 | 0.66877 | 5.379
2024-12-10 | 0:23 | Data | 0 | 33.439 | 32.028 | 167.858 | 7.64 | 158.562 | 2222.52 | 25.85 | 47.623 | 6.4 | 1.283 | 4.131 | 8395.51 | 1.499 | 97.9 | 76.3 | 1444 | 23.81 | 5457.1 | 2632.3 | 2660.8 | 3874.6 | 1216.1 | 0.66984 | 5.414
2024-12-10 | 0:23 | Data | 0 | 33.527 | 31.805 | 167.632 | 7.64 | 158.472 | 2224.33 | 25.84 | 47.533 | 6.41 | 1.282 | 4.096 | 8400.04 | 1.614 | 97.9 | 76.2 | 1446 | 23.77 | 5460 | 2666.4 | 2632.6 | 3872.5 | 1216.1 | 0.6713 | 5.378
2024-12-10 | 0:23 | Data | 0 | 33.588 | 32.015 | 167.722 | 7.64 | 158.517 | 2226.14 | 25.84 | 47.623 | 6.4 | 1.284 | 4.077 | 8409.08 | 1.661 | 97.9 | 76 | 1447 | 23.81 | 5465.9 | 2618.1 | 2642.7 | 3864.2 | 1216.1 | 0.66506 | 5.362
2024-12-10 | 0:23 | Data | 0 | 33.743 | 32.008 | 167.903 | 7.64 | 158.562 | 2226.14 | 25.84 | 47.623 | 6.4 | 1.278 | 4.082 | 8409.08 | 1.668 | 97.9 | 76.2 | 1446 | 23.81 | 5465.9 | 2633.9 | 2613.9 | 3837.8 | 1216.1 | 0.66894 | 5.36
2024-12-10 | 0:23 | Data | 0 | 33.439 | 32.305 | 167.813 | 7.64 | 158.517 | 2223.43 | 25.83 | 47.623 | 6.4 | 1.277 | 4.124 | 8409.08 | 1.56 | 97.9 | 76.4 | 1445 | 23.81 | 5465.9 | 2653.2 | 2617 | 3855.6 | 1216.1 | 0.67101 | 5.401
2024-12-10 | 0:23 | Data | 0 | 33.615 | 31.927 | 167.813 | 7.64 | 158.472 | 2224.33 | 25.84 | 47.623 | 6.4 | 1.282 | 4.118 | 8386.47 | 1.735 | 97.9 | 76.3 | 1446 | 23.86 | 5451.2 | 2634.5 | 2628.2 | 3848.9 | 1216.1 | 0.66877 | 5.4
2024-12-10 | 0:24 | Data | 0 | 33.372 | 32.089 | 167.767 | 7.63 | 158.517 | 2223.43 | 25.84 | 47.623 | 6.4 | 1.279 | 4.108 | 8372.9 | 1.431 | 97.9 | 76.3 | 1445 | 23.81 | 5442.4 | 2723.9 | 2620.4 | 3915 | 1216.1 | 0.67699 | 5.387
2024-12-10 | 0:24 | Data | 0 | 33.426 | 31.799 | 167.632 | 7.63 | 158.472 | 2225.23 | 25.84 | 47.623 | 6.4 | 1.282 | 4.116 | 8390.99 | 1.614 | 97.9 | 76.3 | 1446 | 23.81 | 5454.1 | 2704.6 | 2665.3 | 3928.8 | 1216.1 | 0.67059 | 5.398
2024-12-10 | 0:24 | Data | 0 | 33.628 | 31.826 | 167.677 | 7.64 | 158.426 | 2230.66 | 25.84 | 47.533 | 6.4 | 1.276 | 4.134 | 8390.99 | 1.809 | 97.9 | 76.4 | 1450 | 23.81 | 5454.1 | 2697.1 | 2654.8 | 3922.5 | 1216.1 | 0.67041 | 5.411
2024-12-10 | 0:24 | Data | 0 | 33.527 | 31.913 | 167.767 | 7.63 | 158.562 | 2227.04 | 25.84 | 47.623 | 6.4 | 1.285 | 4.113 | 8395.51 | 1.398 | 97.9 | 76.2 | 1448 | 23.86 | 5457.1 | 2715.7 | 2671.8 | 3942.9 | 1216.1 | 0.67236 | 5.397
2024-12-10 | 0:24 | Data | 0 | 33.412 | 31.805 | 167.722 | 7.64 | 158.472 | 2227.95 | 25.83 | 47.623 | 6.4 | 1.294 | 4.111 | 8409.08 | 1.809 | 97.9 | 76.1 | 1447 | 23.81 | 5465.9 | 2713.2 | 2667.3 | 3932.6 | 1216.1 | 0.67263 | 5.405
2024-12-10 | 0:24 | Data | 0 | 33.554 | 31.812 | 167.767 | 7.64 | 158.607 | 2227.95 | 25.84 | 47.533 | 6.41 | 1.285 | 4.093 | 8400.04 | 1.701 | 97.9 | 76.1 | 1448 | 23.81 | 5460 | 2712 | 2662.7 | 3928.9 | 1216.1 | 0.6725 | 5.377
2024-12-10 | 0:24 | Data | 0 | 33.696 | 31.934 | 167.722 | 7.63 | 158.562 | 2227.95 | 25.84 | 47.623 | 6.4 | 1.282 | 4.121 | 8400.04 | 1.823 | 97.9 | 76.3 | 1448 | 23.81 | 5460 | 2722.8 | 2675.7 | 3950.6 | 1216.1 | 0.67298 | 5.403
2024-12-10 | 0:24 | Data | 0 | 33.527 | 32.244 | 167.767 | 7.64 | 158.517 | 2227.04 | 25.84 | 47.533 | 6.4 | 1.276 | 4.116 | 8422.65 | 1.553 | 97.9 | 76.3 | 1448 | 23.81 | 5474.7 | 2727.4 | 2668.8 | 3942.6 | 1216.1 | 0.67423 | 5.392
2024-12-10 | 0:24 | Data | 0 | 33.642 | 31.913 | 167.858 | 7.64 | 158.607 | 2225.23 | 25.84 | 47.623 | 6.4 | 1.282 | 4.119 | 8400.04 | 1.614 | 97.9 | 76.3 | 1446 | 23.77 | 5460 | 2700.4 | 2643.3 | 3909.9 | 1216.1 | 0.67301 | 5.401
2024-12-10 | 0:24 | Data | 0 | 33.412 | 32.015 | 167.813 | 7.64 | 158.472 | 2227.95 | 25.84 | 47.623 | 6.4 | 1.288 | 4.125 | 8386.47 | 1.526 | 97.9 | 76.2 | 1448 | 23.81 | 5451.2 | 2721.9 | 2622.1 | 3910.6 | 1216.1 | 0.67977 | 5.413
2024-12-10 | 0:24 | Data | 0 | 33.5 | 31.907 | 167.722 | 7.63 | 158.562 | 2227.95 | 25.84 | 47.623 | 6.41 | 1.283 | 4.084 | 8381.95 | 1.553 | 97.9 | 76.1 | 1448 | 23.81 | 5448.3 | 2733.1 | 2636.4 | 3923.1 | 1216.1 | 0.6814 | 5.368
2024-12-10 | 0:24 | Data | 0 | 33.554 | 31.812 | 167.677 | 7.64 | 158.562 | 2224.33 | 25.83 | 47.623 | 6.4 | 1.282 | 4.085 | 8386.47 | 1.627 | 97.9 | 76.1 | 1446 | 23.86 | 5451.2 | 2701.8 | 2654.8 | 3920.4 | 1216.1 | 0.67058 | 5.366
2024-12-10 | 0:24 | Data | 0 | 33.635 | 31.826 | 167.767 | 7.63 | 158.517 | 2222.52 | 25.84 | 47.353 | 6.41 | 1.278 | 4.098 | 8427.17 | 1.728 | 97.9 | 76.2 | 1445 | 23.68 | 5477.7 | 2692 | 2652.9 | 3915.5 | 1216.1 | 0.67088 | 5.376
2024-12-10 | 0:24 | Data | 0 | 33.642 | 32.231 | 167.813 | 7.63 | 158.517 | 2225.23 | 25.84 | 47.623 | 6.41 | 1.283 | 4.105 | 8422.65 | 1.614 | 97.9 | 76.2 | 1446 | 23.81 | 5474.7 | 2693.6 | 2664 | 3918.6 | 1216.2 | 0.67106 | 5.389
2024-12-10 | 0:24 | Data | 0 | 33.365 | 31.799 | 167.813 | 7.64 | 158.472 | 2221.62 | 25.85 | 47.533 | 6.4 | 1.28 | 4.085 | 8431.69 | 1.587 | 97.9 | 76.1 | 1443 | 23.77 | 5480.6 | 2725.5 | 2648.2 | 3930.9 | 1216.2 | 0.67471 | 5.364
2024-12-10 | 0:24 | Data | 0 | 33.473 | 31.805 | 167.722 | 7.64 | 158.562 | 2225.23 | 25.84 | 47.623 | 6.4 | 1.278 | 4.073 | 8431.69 | 1.634 | 97.9 | 76.1 | 1446 | 23.77 | 5480.6 | 2713.6 | 2642.2 | 3914.4 | 1216.2 | 0.67586 | 5.352
2024-12-10 | 0:24 | Data | 0 | 33.513 | 31.799 | 167.722 | 7.64 | 158.426 | 2224.33 | 25.84 | 47.714 | 6.4 | 1.279 | 4.121 | 8400.04 | 1.715 | 97.9 | 76.3 | 1446 | 23.86 | 5460 | 2729.5 | 2654.3 | 3936.4 | 1216.2 | 0.6752 | 5.401
2024-12-10 | 0:24 | Data | 0 | 33.419 | 31.819 | 167.767 | 7.64 | 158.472 | 2225.23 | 25.84 | 47.714 | 6.4 | 1.282 | 4.091 | 8395.51 | 1.634 | 97.9 | 76.1 | 1446 | 23.81 | 5457.1 | 2687.1 | 2619.8 | 3888 | 1216.2 | 0.67253 | 5.374
2024-12-10 | 0:25 | Data | 0 | 33.419 | 31.886 | 167.677 | 7.63 | 158.426 | 2225.23 | 25.84 | 47.623 | 6.4 | 1.272 | 4.096 | 8404.56 | 1.526 | 97.9 | 76.3 | 1446 | 23.81 | 5463 | 2689.1 | 2636.5 | 3891.9 | 1216.2 | 0.67297 | 5.368
2024-12-10 | 0:25 | Data | 0 | 33.412 | 31.799 | 167.632 | 7.64 | 158.426 | 2228.85 | 25.85 | 47.623 | 6.4 | 1.282 | 4.099 | 8386.47 | 1.614 | 97.9 | 76.2 | 1449 | 23.81 | 5451.2 | 2703.3 | 2656.1 | 3920.4 | 1216.2 | 0.67096 | 5.381
2024-12-10 | 0:25 | Data | 0 | 33.446 | 31.691 | 167.722 | 7.64 | 158.472 | 2229.75 | 25.84 | 47.623 | 6.4 | 1.282 | 4.102 | 8409.08 | 1.607 | 97.9 | 76.2 | 1450 | 23.81 | 5465.9 | 2690.1 | 2642 | 3899.3 | 1216.2 | 0.67053 | 5.383
2024-12-10 | 0:25 | Data | 0 | 33.439 | 32.028 | 167.767 | 7.64 | 158.472 | 2229.75 | 25.84 | 47.623 | 6.4 | 1.275 | 4.133 | 8400.04 | 1.587 | 97.9 | 76.4 | 1449 | 23.81 | 5460 | 2685.7 | 2646.4 | 3900.6 | 1216.2 | 0.66959 | 5.408
2024-12-10 | 0:25 | Data | 0 | 33.804 | 32.055 | 167.813 | 7.63 | 158.472 | 2229.75 | 25.84 | 47.714 | 6.4 | 1.28 | 4.124 | 8779.9 | 1.708 | 97.9 | 76.3 | 1449 | 23.81 | 5706.9 | 2715.7 | 2645.1 | 3917.2 | 1216.2 | 0.67646 | 5.405
2024-12-10 | 0:25 | Data | 0 | 33.419 | 31.913 | 167.858 | 7.64 | 158.607 | 2227.95 | 25.84 | 47.623 | 6.4 | 1.289 | 4.094 | 8400.04 | 1.607 | 97.9 | 76.1 | 1448 | 23.81 | 5460 | 2687.2 | 2652 | 3907.9 | 1216.2 | 0.66881 | 5.382
2024-12-10 | 0:25 | Data | 0 | 33.75 | 31.94 | 167.677 | 7.64 | 158.472 | 2225.23 | 25.84 | 47.623 | 6.4 | 1.282 | 4.118 | 8359.34 | 1.6 | 97.9 | 76.3 | 1446 | 23.81 | 5433.6 | 2700.7 | 2676.5 | 3931.9 | 1216.2 | 0.66998 | 5.4
2024-12-10 | 0:25 | Data | 0 | 33.196 | 31.832 | 167.586 | 7.64 | 158.426 | 2226.14 | 25.83 | 47.714 | 6.4 | 1.282 | 4.138 | 8359.34 | 1.512 | 97.9 | 76.4 | 1447 | 23.81 | 5433.6 | 2717.4 | 2677.2 | 3944 | 1216.2 | 0.67124 | 5.42
2024-12-10 | 0:25 | Data | 0 | 33.446 | 31.805 | 167.722 | 7.63 | 158.517 | 2227.04 | 25.84 | 47.714 | 6.4 | 1.282 | 4.12 | 8372.9 | 1.438 | 97.9 | 76.3 | 1448 | 23.86 | 5442.4 | 2693.1 | 2676.1 | 3924.6 | 1216.2 | 0.67142 | 5.401
2024-12-10 | 0:25 | Data | 0 | 33.419 | 31.799 | 167.677 | 7.64 | 158.472 | 2227.95 | 25.83 | 47.623 | 6.4 | 1.278 | 4.093 | 8354.81 | 1.614 | 97.9 | 76.2 | 1448 | 23.81 | 5430.6 | 2693.5 | 2657.3 | 3910.9 | 1216.2 | 0.66983 | 5.371
2024-12-10 | 0:25 | Data | 0 | 33.426 | 31.839 | 167.632 | 7.64 | 158.472 | 2282.18 | 25.84 | 47.714 | 6.41 | 1.283 | 4.087 | 8372.9 | 1.438 | 97.9 | 76.1 | 1483 | 23.81 | 5442.4 | 2689.5 | 2658.7 | 3916.6 | 1216.2 | 0.6673 | 5.372
2024-12-10 | 0:25 | Data | 0 | 33.851 | 31.819 | 167.767 | 7.63 | 158.517 | 2285.79 | 25.84 | 47.623 | 6.4 | 1.28 | 4.101 | 8377.43 | 1.688 | 97.9 | 76.2 | 1485 | 23.81 | 5445.3 | 2714.4 | 2638.3 | 3914.1 | 1216.2 | 0.67395 | 5.381
2024-12-10 | 0:25 | Data | 0 | 33.446 | 31.637 | 167.677 | 7.63 | 158.472 | 2284.89 | 25.83 | 47.623 | 6.4 | 1.282 | 4.104 | 8363.86 | 1.715 | 97.9 | 76.2 | 1485 | 23.86 | 5436.5 | 2704.5 | 2652 | 3914 | 1216.2 | 0.66935 | 5.386
2024-12-10 | 0:25 | Data | 0 | 33.534 | 31.826 | 167.767 | 7.64 | 158.517 | 2280.37 | 25.83 | 47.623 | 6.4 | 1.284 | 4.111 | 8377.43 | 1.56 | 97.9 | 76.2 | 1482 | 23.81 | 5445.3 | 2700.4 | 2650.6 | 3909.9 | 1216.2 | 0.67381 | 5.396
2024-12-10 | 0:25 | Data | 0 | 33.412 | 32.021 | 167.767 | 7.63 | 158.517 | 2225.23 | 25.84 | 47.623 | 6.41 | 1.294 | 4.125 | 8377.43 | 1.573 | 97.9 | 76.1 | 1446 | 23.81 | 5445.3 | 2689 | 2669 | 3913.9 | 1216.2 | 0.67003 | 5.419
2024-12-10 | 0:25 | Data | 0 | 33.419 | 31.819 | 167.722 | 7.64 | 158.517 | 2227.95 | 25.84 | 47.623 | 6.4 | 1.279 | 4.103 | 8381.95 | 1.553 | 97.9 | 76.2 | 1448 | 23.81 | 5448.3 | 2708.3 | 2655.6 | 3930.9 | 1216.2 | 0.67246 | 5.382
2024-12-10 | 0:25 | Data | 0 | 33.635 | 31.853 | 167.722 | 7.64 | 158.517 | 2235.18 | 25.85 | 47.804 | 6.4 | 1.28 | 4.109 | 8386.47 | 1.674 | 97.9 | 76.2 | 1453 | 23.95 | 5451.2 | 2708 | 2641.9 | 3910.7 | 1216.2 | 0.67534 | 5.391
2024-12-10 | 0:26 | Data | 0 | 33.621 | 31.832 | 167.767 | 7.64 | 158.517 | 2233.37 | 25.84 | 47.623 | 6.4 | 1.285 | 4.105 | 8386.47 | 1.776 | 97.9 | 76.2 | 1451 | 23.81 | 5451.2 | 2702.4 | 2660 | 3916.7 | 1216.2 | 0.67126 | 5.389
2024-12-10 | 0:26 | Data | 0 | 33.412 | 31.886 | 167.632 | 7.63 | 158.472 | 2242.41 | 25.84 | 47.623 | 6.4 | 1.278 | 4.099 | 8377.43 | 1.809 | 97.9 | 76.2 | 1458 | 23.81 | 5445.3 | 2711.5 | 2635.9 | 3909.1 | 1216.2 | 0.67628 | 5.377
2024-12-10 | 0:26 | Data | 0 | 33.257 | 32.001 | 167.767 | 7.64 | 158.517 | 2236.08 | 25.84 | 47.623 | 6.4 | 1.282 | 4.095 | 8372.9 | 1.364 | 97.9 | 76.1 | 1453 | 23.81 | 5442.4 | 2678.4 | 2648.9 | 3899.9 | 1216.2 | 0.66933 | 5.377
2024-12-10 | 0:26 | Data | 0 | 33.837 | 32.042 | 167.813 | 7.64 | 158.517 | 2236.08 | 25.84 | 47.623 | 6.4 | 1.28 | 4.09 | 8368.38 | 1.627 | 97.9 | 76.2 | 1453 | 23.81 | 5439.4 | 2707 | 2643.1 | 3905.8 | 1216.2 | 0.67394 | 5.369
2024-12-10 | 0:26 | Data | 0 | 33.419 | 32.001 | 167.767 | 7.64 | 158.426 | 2236.08 | 25.84 | 47.714 | 6.4 | 1.284 | 4.107 | 8377.43 | 1.553 | 97.9 | 76.2 | 1453 | 23.81 | 5445.3 | 2705.3 | 2656.5 | 3922.6 | 1216.2 | 0.67524 | 5.391
2024-12-10 | 0:26 | Data | 0 | 33.75 | 31.832 | 167.722 | 7.63 | 158.607 | 2238.79 | 25.84 | 47.623 | 6.4 | 1.283 | 4.123 | 8381.95 | 1.62 | 97.9 | 76.3 | 1455 | 23.81 | 5448.3 | 2675.3 | 2659.8 | 3900.8 | 1216.2 | 0.66945 | 5.407
2024-12-10 | 0:26 | Data | 0 | 33.412 | 31.63 | 167.632 | 7.63 | 158.472 | 2238.79 | 25.84 | 47.623 | 6.4 | 1.284 | 4.096 | 8395.51 | 1.587 | 97.9 | 76.1 | 1455 | 23.81 | 5457.1 | 2699.8 | 2655 | 3913.7 | 1216.2 | 0.67319 | 5.381
2024-12-10 | 0:26 | Data | 0 | 33.48 | 31.832 | 167.767 | 7.64 | 158.562 | 2238.79 | 25.84 | 47.443 | 6.4 | 1.289 | 4.116 | 8400.04 | 1.512 | 97.9 | 76.2 | 1456 | 23.72 | 5460 | 2717.4 | 2662 | 3926 | 1216.2 | 0.67559 | 5.407
2024-12-10 | 0:26 | Data | 0 | 33.844 | 32.055 | 167.767 | 7.64 | 158.517 | 2239.7 | 25.84 | 47.443 | 6.4 | 1.287 | 4.12 | 8400.04 | 1.722 | 97.9 | 76.2 | 1456 | 23.72 | 5460 | 2692.8 | 2649.2 | 3907.3 | 1216.2 | 0.67129 | 5.407
2024-12-10 | 0:26 | Data | 0 | 33.77 | 31.832 | 167.767 | 7.63 | 158.517 | 2238.79 | 25.84 | 47.623 | 6.4 | 1.278 | 4.12 | 8400.04 | 1.539 | 97.9 | 76.3 | 1456 | 23.86 | 5460 | 2695 | 2639.3 | 3902.8 | 1216.2 | 0.67375 | 5.398
2024-12-10 | 0:26 | Data | 0 | 33.642 | 32.244 | 167.767 | 7.64 | 158.472 | 2232.47 | 25.84 | 47.714 | 6.4 | 1.276 | 4.104 | 8418.13 | 1.634 | 97.9 | 76.3 | 1452 | 23.86 | 5471.8 | 2694.9 | 2658.7 | 3909.4 | 1216.2 | 0.6694 | 5.381
2024-12-10 | 0:26 | Data | 0 | 33.75 | 31.826 | 167.722 | 7.64 | 158.517 | 2238.79 | 25.84 | 47.623 | 6.4 | 1.285 | 4.105 | 8422.65 | 1.627 | 97.9 | 76.1 | 1455 | 23.86 | 5474.7 | 2693 | 2634.3 | 3893.3 | 1216.2 | 0.67407 | 5.392
2024-12-10 | 0:26 | Data | 0 | 33.203 | 31.745 | 167.632 | 7.63 | 158.472 | 2238.79 | 25.83 | 47.623 | 6.4 | 1.288 | 4.113 | 8404.56 | 1.553 | 97.9 | 76.2 | 1455 | 23.81 | 5463 | 2713 | 2642.5 | 3915.4 | 1216.2 | 0.67499 | 5.401
2024-12-10 | 0:26 | Data | 0 | 33.837 | 31.94 | 167.813 | 7.63 | 158.562 | 2235.18 | 25.83 | 47.353 | 6.4 | 1.28 | 4.128 | 8409.08 | 1.614 | 97.9 | 76.3 | 1453 | 23.68 | 5465.9 | 2688.4 | 2655.6 | 3910.5 | 1216.2 | 0.66977 | 5.407
2024-12-10 | 0:26 | Data | 0 | 33.412 | 31.907 | 167.677 | 7.64 | 158.426 | 2233.37 | 25.84 | 47.623 | 6.4 | 1.287 | 4.107 | 8395.51 | 1.526 | 97.9 | 76.1 | 1452 | 23.81 | 5457.1 | 2670.8 | 2660.8 | 3901.9 | 1216.2 | 0.66798 | 5.394
2024-12-10 | 0:26 | Data | 0 | 33.527 | 32.109 | 167.677 | 7.63 | 158.426 | 2233.37 | 25.84 | 47.623 | 6.4 | 1.284 | 4.102 | 8409.08 | 1.431 | 97.9 | 76.2 | 1452 | 23.81 | 5465.9 | 2703.1 | 2647 | 3913.4 | 1216.2 | 0.67318 | 5.386
2024-12-10 | 0:26 | Data | 0 | 33.804 | 32.082 | 167.767 | 7.64 | 158.517 | 2231.56 | 25.84 | 47.623 | 6.4 | 1.287 | 4.102 | 8404.56 | 1.607 | 97.9 | 76.1 | 1450 | 23.81 | 5463 | 2695.8 | 2640.3 | 3896.8 | 1216.2 | 0.67461 | 5.389
2024-12-10 | 0:26 | Data | 0 | 33.669 | 31.92 | 167.767 | 7.63 | 158.562 | 2238.79 | 25.84 | 47.443 | 6.4 | 1.282 | 4.111 | 8390.99 | 1.627 | 97.9 | 76.2 | 1455 | 23.72 | 5454.1 | 2695.3 | 2665.1 | 3917.3 | 1216.3 | 0.66959 | 5.393
2024-12-10 | 0:27 | Data | 0 | 33.831 | 31.832 | 167.722 | 7.63 | 158.562 | 2239.7 | 25.84 | 47.533 | 6.4 | 1.287 | 4.101 | 8400.04 | 1.83 | 97.9 | 76.1 | 1455 | 23.77 | 5460 | 2691.4 | 2649.9 | 3904 | 1216.3 | 0.67155 | 5.39
2024-12-10 | 0:27 | Data | 0 | 33.412 | 32.001 | 167.722 | 7.64 | 158.472 | 2235.18 | 25.83 | 47.443 | 6.4 | 1.284 | 4.121 | 8400.04 | 1.553 | 97.9 | 76.2 | 1453 | 23.68 | 5460 | 2696.4 | 2657.6 | 3913.1 | 1216.3 | 0.67231 | 5.406
2024-12-10 | 0:27 | Data | 0 | 33.243 | 31.9 | 167.677 | 7.64 | 158.426 | 2236.08 | 25.84 | 47.443 | 6.4 | 1.28 | 4.13 | 8422.65 | 1.425 | 97.9 | 76.3 | 1453 | 23.77 | 5474.7 | 2690.2 | 2652.1 | 3905.8 | 1216.3 | 0.67267 | 5.409
2024-12-10 | 0:27 | Data | 0 | 33.844 | 32.082 | 167.813 | 7.63 | 158.562 | 2236.98 | 25.83 | 47.533 | 6.4 | 1.287 | 4.105 | 8418.13 | 1.553 | 97.9 | 76.1 | 1454 | 23.77 | 5471.8 | 2692.3 | 2650.1 | 3908.6 | 1216.3 | 0.67098 | 5.392
2024-12-10 | 0:27 | Data | 0 | 33.412 | 31.967 | 167.632 | 7.64 | 158.381 | 2240.6 | 25.84 | 47.714 | 6.4 | 1.294 | 4.097 | 8418.13 | 1.614 | 97.9 | 76 | 1456 | 23.86 | 5471.8 | 2700.9 | 2624.8 | 3892.7 | 1216.3 | 0.67601 | 5.392
2024-12-10 | 0:27 | Data | 0 | 33.527 | 31.853 | 167.722 | 7.64 | 158.517 | 2235.18 | 25.84 | 47.623 | 6.4 | 1.294 | 4.104 | 8418.13 | 1.438 | 97.9 | 76 | 1453 | 23.81 | 5471.8 | 2684.6 | 2628.6 | 3891.9 | 1216.3 | 0.67427 | 5.397
2024-12-10 | 0:27 | Data | 0 | 33.372 | 32.001 | 167.767 | 7.63 | 158.426 | 2236.08 | 25.83 | 47.714 | 6.4 | 1.282 | 4.102 | 8418.13 | 1.607 | 97.9 | 76.2 | 1453 | 23.81 | 5471.8 | 2682.1 | 2644.3 | 3899.2 | 1216.3 | 0.66996 | 5.384
2024-12-10 | 0:27 | Data | 0 | 33.628 | 32.015 | 167.677 | 7.63 | 158.517 | 2236.08 | 25.84 | 47.623 | 6.4 | 1.275 | 4.106 | 8418.13 | 1.668 | 97.9 | 76.3 | 1453 | 23.86 | 5471.8 | 2697.3 | 2640.4 | 3904.3 | 1216.3 | 0.67187 | 5.382
2024-12-10 | 0:27 | Data | 0 | 33.642 | 31.826 | 167.767 | 7.64 | 158.517 | 2230.66 | 25.84 | 47.623 | 6.4 | 1.288 | 4.094 | 8395.51 | 1.614 | 97.9 | 76.1 | 1451 | 23.77 | 5457.1 | 2688.2 | 2659.1 | 3908.8 | 1216.3 | 0.66945 | 5.382
2024-12-10 | 0:27 | Data | 0 | 33.75 | 32.204 | 167.813 | 7.64 | 158.562 | 2230.66 | 25.83 | 47.623 | 6.4 | 1.277 | 4.097 | 8395.51 | 1.668 | 97.9 | 76.2 | 1449 | 23.81 | 5457.1 | 2687.6 | 2637.6 | 3901.7 | 1216.3 | 0.67034 | 5.375
2024-12-10 | 0:27 | Data | 0 | 33.635 | 32.231 | 167.677 | 7.64 | 158.472 | 2230.66 | 25.84 | 47.623 | 6.4 | 1.285 | 4.082 | 8400.04 | 1.62 | 97.9 | 76.1 | 1450 | 23.81 | 5460 | 2695.3 | 2642.6 | 3899.6 | 1216.3 | 0.674 | 5.369
2024-12-10 | 0:27 | Data | 0 | 33.797 | 32.028 | 167.767 | 7.64 | 158.517 | 2230.66 | 25.84 | 47.714 | 6.4 | 1.297 | 4.094 | 8404.56 | 1.654 | 97.9 | 75.9 | 1450 | 23.81 | 5463 | 2706.8 | 2656 | 3916.6 | 1216.3 | 0.67467 | 5.391
2024-12-10 | 0:27 | Data | 0 | 33.439 | 31.805 | 167.722 | 7.63 | 158.426 | 2229.75 | 25.84 | 47.623 | 6.41 | 1.292 | 4.121 | 8372.9 | 1.607 | 97.9 | 76.1 | 1449 | 23.81 | 5442.4 | 2708.3 | 2636.1 | 3907.9 | 1216.3 | 0.67481 | 5.413
2024-12-10 | 0:27 | Data | 0 | 33.635 | 31.913 | 167.767 | 7.64 | 158.517 | 2230.66 | 25.84 | 47.623 | 6.4 | 1.282 | 4.109 | 8372.9 | 1.438 | 97.9 | 76.2 | 1450 | 23.77 | 5442.4 | 2691 | 2643 | 3899.3 | 1216.3 | 0.67363 | 5.388
2024-12-10 | 0:27 | Data | 0 | 33.554 | 31.826 | 167.858 | 7.63 | 158.607 | 2229.75 | 25.84 | 47.082 | 6.4 | 1.276 | 4.096 | 8386.47 | 1.566 | 97.9 | 76.2 | 1450 | 23.59 | 5451.2 | 2668 | 2659.2 | 3901.6 | 1216.3 | 0.66626 | 5.373
2024-12-10 | 0:27 | Data | 0 | 33.405 | 31.913 | 167.722 | 7.64 | 158.517 | 2230.66 | 25.84 | 47.533 | 6.4 | 1.277 | 4.079 | 8400.04 | 1.816 | 97.9 | 76.2 | 1450 | 23.77 | 5460 | 2691.1 | 2648.4 | 3905.4 | 1216.3 | 0.67338 | 5.356
2024-12-10 | 0:27 | Data | 0 | 33.743 | 32.264 | 167.813 | 7.63 | 158.517 | 2230.66 | 25.84 | 47.714 | 6.4 | 1.282 | 4.119 | 8404.56 | 1.776 | 97.9 | 76.3 | 1449 | 23.86 | 5463 | 2685.7 | 2651.2 | 3905 | 1216.3 | 0.67035 | 5.4
2024-12-10 | 0:27 | Data | 0 | 33.473 | 31.92 | 167.767 | 7.64 | 158.517 | 2234.27 | 25.84 | 47.623 | 6.4 | 1.284 | 4.108 | 8386.47 | 1.607 | 97.9 | 76.2 | 1452 | 23.86 | 5451.2 | 2702.8 | 2636.7 | 3905.5 | 1216.3 | 0.67461 | 5.392
2024-12-10 | 0:28 | Data | 0 | 33.615 | 31.805 | 167.677 | 7.64 | 158.472 | 2233.37 | 25.83 | 47.623 | 6.41 | 1.282 | 4.111 | 8418.13 | 1.83 | 97.9 | 76.2 | 1452 | 23.86 | 5471.8 | 2680.1 | 2627.2 | 3885.3 | 1216.3 | 0.67557 | 5.393
2024-12-10 | 0:28 | Data | 0 | 33.527 | 32.021 | 167.767 | 7.64 | 158.517 | 2233.37 | 25.84 | 47.714 | 6.4 | 1.29 | 4.123 | 8400.04 | 1.593 | 97.9 | 76.2 | 1451 | 23.81 | 5460 | 2706.7 | 2648.9 | 3912.2 | 1216.3 | 0.6744 | 5.411
2024-12-10 | 0:28 | Data | 0 | 33.696 | 31.826 | 167.722 | 7.63 | 158.472 | 2229.75 | 25.84 | 47.533 | 6.4 | 1.283 | 4.101 | 8431.69 | 1.681 | 97.9 | 76.2 | 1449 | 23.81 | 5480.6 | 2694.6 | 2641.5 | 3899.8 | 1216.3 | 0.67317 | 5.384
2024-12-10 | 0:28 | Data | 0 | 33.473 | 31.805 | 167.767 | 7.64 | 158.472 | 2233.37 | 25.84 | 47.623 | 6.4 | 1.293 | 4.113 | 8427.17 | 1.6 | 97.9 | 76.1 | 1452 | 23.81 | 5477.7 | 2695.2 | 2631.1 | 3893.5 | 1216.3 | 0.67435 | 5.405
2024-12-10 | 0:28 | Data | 0 | 33.372 | 31.974 | 167.767 | 7.64 | 158.562 | 2233.37 | 25.84 | 47.623 | 6.4 | 1.288 | 4.105 | 8427.17 | 1.634 | 97.9 | 76.1 | 1452 | 23.81 | 5477.7 | 2699.2 | 2646.4 | 3905 | 1216.3 | 0.67347 | 5.392
2024-12-10 | 0:28 | Data | 0 | 33.648 | 31.819 | 167.813 | 7.64 | 158.562 | 2233.37 | 25.83 | 47.623 | 6.4 | 1.29 | 4.082 | 8431.69 | 1.769 | 97.9 | 76 | 1452 | 23.81 | 5480.6 | 2706.7 | 2656 | 3915.5 | 1216.3 | 0.67437 | 5.373
2024-12-10 | 0:28 | Data | 0 | 33.426 | 31.799 | 167.722 | 7.64 | 158.426 | 2233.37 | 25.84 | 47.714 | 6.4 | 1.294 | 4.086 | 8390.99 | 1.512 | 97.9 | 75.9 | 1451 | 23.81 | 5454.1 | 2690.5 | 2635 | 3900.5 | 1216.3 | 0.67034 | 5.381
2024-12-10 | 0:28 | Data | 0 | 33.419 | 32.217 | 167.813 | 7.64 | 158.517 | 2233.37 | 25.84 | 47.082 | 6.4 | 1.287 | 4.119 | 8386.47 | 1.418 | 97.9 | 76.2 | 1452 | 23.5 | 5451.2 | 2700.5 | 2644.7 | 3907.3 | 1216.3 | 0.67353 | 5.406
2024-12-10 | 0:28 | Data | 0 | 33.635 | 31.913 | 167.767 | 7.63 | 158.517 | 2232.47 | 25.85 | 47.623 | 6.4 | 1.279 | 4.108 | 8386.47 | 1.728 | 97.9 | 76.2 | 1451 | 23.86 | 5451.2 | 2698.3 | 2646.7 | 3906.9 | 1216.3 | 0.67209 | 5.388
2024-12-10 | 0:28 | Data | 0 | 33.574 | 32.028 | 167.722 | 7.64 | 158.517 | 2233.37 | 25.84 | 47.533 | 6.4 | 1.283 | 4.105 | 8390.99 | 1.6 | 97.9 | 76.2 | 1451 | 23.77 | 5454.1 | 2678 | 2638.4 | 3891.1 | 1216.3 | 0.66968 | 5.388
2024-12-10 | 0:28 | Data | 0 | 33.642 | 32.143 | 167.813 | 7.64 | 158.562 | 2235.18 | 25.83 | 47.623 | 6.4 | 1.28 | 4.094 | 8418.13 | 1.614 | 97.9 | 76.2 | 1453 | 23.81 | 5471.8 | 2704.4 | 2662.2 | 3916.8 | 1216.3 | 0.67154 | 5.373
2024-12-10 | 0:28 | Data | 0 | 33.412 | 31.799 | 167.677 | 7.63 | 158.517 | 2233.37 | 25.84 | 47.623 | 6.4 | 1.284 | 4.112 | 8422.65 | 1.816 | 97.9 | 76.2 | 1451 | 23.86 | 5474.7 | 2710.4 | 2644.9 | 3910.9 | 1216.3 | 0.67665 | 5.396
2024-12-10 | 0:28 | Data | 0 | 33.729 | 32.264 | 167.813 | 7.64 | 158.607 | 2235.18 | 25.83 | 47.714 | 6.41 | 1.284 | 4.111 | 8427.17 | 1.58 | 97.9 | 76.2 | 1453 | 23.86 | 5477.7 | 2669.4 | 2652.8 | 3895 | 1216.3 | 0.66728 | 5.395
2024-12-10 | 0:28 | Data | 0 | 33.527 | 32.015 | 167.767 | 7.64 | 158.517 | 2235.18 | 25.84 | 46.54 | 6.4 | 1.282 | 4.132 | 8418.13 | 1.627 | 97.9 | 76.3 | 1453 | 23.27 | 5471.8 | 2702.5 | 2636.7 | 3902 | 1216.3 | 0.67533 | 5.415
2024-12-10 | 0:28 | Data | 0 | 33.918 | 32.089 | 167.858 | 7.64 | 158.607 | 2239.7 | 25.85 | 47.533 | 6.4 | 1.287 | 4.123 | 8418.13 | 1.742 | 97.9 | 76.2 | 1456 | 23.81 | 5471.8 | 2700.1 | 2626.5 | 3899 | 1216.3 | 0.67484 | 5.411
2024-12-10 | 0:28 | Data | 0 | 33.642 | 32.204 | 167.858 | 7.64 | 158.517 | 2232.47 | 25.84 | 47.623 | 6.4 | 1.291 | 4.122 | 8422.65 | 1.614 | 97.9 | 76.1 | 1451 | 23.81 | 5474.7 | 2687.5 | 2619.4 | 3880.9 | 1216.3 | 0.67441 | 5.412
2024-12-10 | 0:28 | Data | 0 | 33.439 | 31.853 | 167.722 | 7.63 | 158.517 | 2232.47 | 25.84 | 47.623 | 6.4 | 1.293 | 4.11 | 8422.65 | 1.56 | 97.9 | 76.1 | 1451 | 23.81 | 5474.7 | 2698.2 | 2615.8 | 3887.9 | 1216.3 | 0.67793 | 5.403
2024-12-10 | 0:28 | Data | 0 | 33.642 | 32.028 | 167.722 | 7.63 | 158.517 | 2232.47 | 25.83 | 47.623 | 6.4 | 1.289 | 4.093 | 8431.69 | 1.614 | 97.9 | 76.1 | 1452 | 23.81 | 5480.6 | 2689.4 | 2650.8 | 3908.1 | 1216.3 | 0.67115 | 5.381
2024-12-10 | 0:29 | Data | 0 | 33.426 | 31.799 | 167.632 | 7.63 | 158.472 | 2233.37 | 25.84 | 47.623 | 6.41 | 1.275 | 4.118 | 8431.69 | 1.614 | 97.9 | 76.4 | 1452 | 23.81 | 5480.6 | 2696.6 | 2645.5 | 3907.5 | 1216.3 | 0.6721 | 5.392
2024-12-10 | 0:29 | Data | 0 | 33.642 | 31.819 | 167.813 | 7.63 | 158.562 | 2229.75 | 25.84 | 47.353 | 6.4 | 1.272 | 4.112 | 8427.17 | 1.809 | 97.9 | 76.4 | 1449 | 23.68 | 5477.7 | 2698.3 | 2643.2 | 3904.6 | 1216.3 | 0.67558 | 5.383
2024-12-10 | 0:29 | Data | 0 | 33.864 | 31.873 | 167.767 | 7.63 | 158.562 | 2229.75 | 25.84 | 47.623 | 6.41 | 1.287 | 4.077 | 8431.69 | 1.614 | 97.9 | 76 | 1449 | 23.81 | 5480.6 | 2692.9 | 2655.4 | 3911.8 | 1216.3 | 0.66794 | 5.364
2024-12-10 | 0:29 | Data | 0 | 33.54 | 31.859 | 167.767 | 7.64 | 158.562 | 2230.66 | 25.84 | 47.623 | 6.4 | 1.275 | 4.087 | 8418.13 | 1.587 | 97.9 | 76.2 | 1450 | 23.81 | 5471.8 | 2694.8 | 2656.5 | 3910.8 | 1216.4 | 0.6717 | 5.363
2024-12-10 | 0:29 | Data | 0 | 33.419 | 32.123 | 167.813 | 7.64 | 158.517 | 2230.66 | 25.84 | 47.533 | 6.4 | 1.284 | 4.106 | 8422.65 | 1.627 | 97.9 | 76.2 | 1450 | 23.77 | 5474.7 | 2699.1 | 2637.9 | 3903.2 | 1216.4 | 0.6735 | 5.392
2024-12-10 | 0:29 | Data | 0 | 33.419 | 32.143 | 167.813 | 7.63 | 158.517 | 2230.66 | 25.84 | 47.714 | 6.4 | 1.28 | 4.099 | 8422.65 | 1.472 | 97.9 | 76.2 | 1450 | 23.81 | 5474.7 | 2680.9 | 2619.7 | 3881.5 | 1216.4 | 0.67283 | 5.381
2024-12-10 | 0:29 | Data | 0 | 33.635 | 32.015 | 167.858 | 7.63 | 158.517 | 2229.75 | 25.84 | 47.443 | 6.4 | 1.283 | 4.077 | 8409.08 | 1.661 | 97.9 | 76.1 | 1450 | 23.77 | 5465.9 | 2701.4 | 2628.4 | 3899.3 | 1216.4 | 0.67371 | 5.362
2024-12-10 | 0:29 | Data | 0 | 33.635 | 31.839 | 167.722 | 7.64 | 158.517 | 2229.75 | 25.84 | 47.623 | 6.4 | 1.278 | 4.081 | 8422.65 | 1.58 | 97.9 | 76.2 | 1449 | 23.81 | 5474.7 | 2702.1 | 2618.8 | 3892.5 | 1216.4 | 0.67677 | 5.359
2024-12-10 | 0:29 | Data | 0 | 33.635 | 31.826 | 167.677 | 7.64 | 158.517 | 2227.95 | 25.84 | 47.533 | 6.4 | 1.286 | 4.075 | 8395.51 | 1.789 | 97.9 | 76 | 1448 | 23.81 | 5457.1 | 2699.4 | 2645 | 3911.2 | 1216.4 | 0.67278 | 5.361
2024-12-10 | 0:29 | Data | 0 | 33.419 | 32.015 | 167.677 | 7.64 | 158.426 | 2227.95 | 25.84 | 47.353 | 6.4 | 1.291 | 4.087 | 8395.51 | 1.499 | 97.9 | 76 | 1448 | 23.72 | 5457.1 | 2688.1 | 2635.8 | 3891.4 | 1216.4 | 0.67308 | 5.377
2024-12-10 | 0:29 | Data | 0 | 33.615 | 31.805 | 167.632 | 7.63 | 158.472 | 2227.04 | 25.84 | 47.714 | 6.41 | 1.283 | 4.105 | 8400.04 | 1.627 | 97.9 | 76.2 | 1448 | 23.86 | 5460 | 2662.4 | 2643.3 | 3884 | 1216.4 | 0.66733 | 5.387
2024-12-10 | 0:29 | Data | 0 | 33.628 | 31.826 | 167.722 | 7.64 | 158.562 | 2227.04 | 25.84 | 47.623 | 6.4 | 1.279 | 4.088 | 8395.51 | 1.728 | 97.9 | 76.2 | 1448 | 23.86 | 5457.1 | 2706.4 | 2638.6 | 3902.9 | 1216.4 | 0.67352 | 5.367
2024-12-10 | 0:29 | Data | 0 | 33.601 | 31.913 | 167.767 | 7.64 | 158.562 | 2225.23 | 25.83 | 47.623 | 6.4 | 1.287 | 4.108 | 8372.9 | 1.431 | 97.9 | 76.2 | 1446 | 23.81 | 5442.4 | 2668.7 | 2649.4 | 3894.6 | 1216.4 | 0.66695 | 5.396
2024-12-10 | 0:29 | Data | 0 | 33.419 | 32.001 | 167.677 | 7.63 | 158.562 | 2225.23 | 25.84 | 47.623 | 6.4 | 1.279 | 4.112 | 8368.38 | 1.506 | 97.9 | 76.3 | 1446 | 23.81 | 5439.4 | 2679.3 | 2625.3 | 3886.2 | 1216.4 | 0.67215 | 5.391
2024-12-10 | 0:29 | Data | 0 | 33.642 | 31.92 | 167.813 | 7.64 | 158.517 | 2227.95 | 25.84 | 47.623 | 6.4 | 1.278 | 4.102 | 8363.86 | 1.722 | 97.9 | 76.2 | 1448 | 23.81 | 5436.5 | 2693.4 | 2643.7 | 3898.6 | 1216.4 | 0.6738 | 5.38
2024-12-10 | 0:29 | Data | 0 | 33.473 | 31.913 | 167.813 | 7.64 | 158.562 | 2227.95 | 25.84 | 47.623 | 6.41 | 1.29 | 4.13 | 8377.43 | 1.634 | 97.9 | 76.2 | 1448 | 23.81 | 5445.3 | 2685.8 | 2633.5 | 3892.6 | 1216.4 | 0.67277 | 5.42
2024-12-10 | 0:29 | Data | 0 | 33.642 | 32.244 | 167.813 | 7.64 | 158.652 | 2227.95 | 25.84 | 47.443 | 6.4 | 1.291 | 4.123 | 8368.38 | 1.6 | 97.9 | 76.2 | 1448 | 23.68 | 5439.4 | 2710.4 | 2653.8 | 3916.9 | 1216.4 | 0.67499 | 5.413
2024-12-10 | 0:30 | Data | 0 | 33.642 | 32.258 | 167.722 | 7.64 | 158.472 | 2227.95 | 25.83 | 47.353 | 6.4 | 1.29 | 4.102 | 8372.9 | 1.587 | 97.9 | 76.1 | 1448 | 23.68 | 5442.4 | 2684.6 | 2650.9 | 3906.9 | 1216.4 | 0.66992 | 5.392
2024-12-10 | 0:30 | Data | 0 | 33.642 | 31.819 | 167.813 | 7.64 | 158.562 | 2220.72 | 25.84 | 47.353 | 6.4 | 1.289 | 4.108 | 8359.34 | 1.803 | 97.9 | 76.1 | 1443 | 23.68 | 5433.6 | 2711.7 | 2633 | 3903.9 | 1216.4 | 0.67751 | 5.398
2024-12-10 | 0:30 | Data | 0 | 33.696 | 32.028 | 167.858 | 7.64 | 158.562 | 2224.33 | 25.84 | 47.714 | 6.4 | 1.282 | 4.139 | 8359.34 | 1.62 | 97.9 | 76.4 | 1446 | 23.81 | 5433.6 | 2689.7 | 2616.1 | 3875.2 | 1216.4 | 0.67879 | 5.42
2024-12-10 | 0:30 | Data | 0 | 33.446 | 31.805 | 167.767 | 7.64 | 158.698 | 2225.23 | 25.84 | 47.623 | 6.4 | 1.273 | 4.134 | 8359.34 | 1.607 | 97.9 | 76.4 | 1446 | 23.81 | 5433.6 | 2673.3 | 2612.4 | 3872.4 | 1216.4 | 0.6727 | 5.407
2024-12-10 | 0:30 | Data | 0 | 33.696 | 32.021 | 167.858 | 7.64 | 158.562 | 2223.43 | 25.83 | 47.623 | 6.4 | 1.282 | 4.109 | 8350.29 | 1.641 | 97.9 | 76.2 | 1444 | 23.81 | 5427.7 | 2702.8 | 2632.6 | 3904.6 | 1216.4 | 0.67512 | 5.392
2024-12-10 | 0:30 | Data | 0 | 33.642 | 31.812 | 167.767 | 7.64 | 158.562 | 2222.52 | 25.85 | 47.714 | 6.4 | 1.287 | 4.127 | 8336.72 | 1.83 | 97.9 | 76.2 | 1444 | 23.81 | 5418.9 | 2684.3 | 2639.9 | 3894.9 | 1216.4 | 0.67245 | 5.414
2024-12-10 | 0:30 | Data | 0 | 33.925 | 32.089 | 167.858 | 7.64 | 158.652 | 2222.52 | 25.84 | 47.533 | 6.4 | 1.285 | 4.104 | 8359.34 | 1.627 | 97.9 | 76.2 | 1445 | 23.81 | 5433.6 | 2697.5 | 2613.7 | 3888.8 | 1216.4 | 0.67498 | 5.389
2024-12-10 | 0:30 | Data | 0 | 33.54 | 32.028 | 167.722 | 7.64 | 158.517 | 2221.62 | 25.84 | 47.714 | 6.41 | 1.278 | 4.075 | 8377.43 | 1.398 | 97.9 | 76.1 | 1444 | 23.81 | 5445.3 | 2692.3 | 2617.4 | 3885 | 1216.4 | 0.67662 | 5.353
2024-12-10 | 0:30 | Data | 0 | 33.642 | 31.92 | 167.722 | 7.64 | 158.562 | 2226.14 | 25.84 | 47.533 | 6.4 | 1.282 | 4.092 | 8386.47 | 1.715 | 97.9 | 76.1 | 1446 | 23.81 | 5451.2 | 2698.7 | 2635.3 | 3901 | 1216.4 | 0.67479 | 5.374
2024-12-10 | 0:30 | Data | 0 | 33.446 | 31.812 | 167.813 | 7.64 | 158.562 | 2225.23 | 25.84 | 47.353 | 6.4 | 1.289 | 4.113 | 8386.47 | 1.593 | 97.9 | 76.1 | 1446 | 23.72 | 5451.2 | 2688.9 | 2629.3 | 3884.5 | 1216.4 | 0.6733 | 5.401
2024-12-10 | 0:30 | Data | 0 | 33.527 | 32.028 | 167.767 | 7.64 | 158.562 | 2225.23 | 25.84 | 47.353 | 6.41 | 1.289 | 4.115 | 8386.47 | 1.573 | 97.9 | 76.2 | 1446 | 23.72 | 5451.2 | 2707.8 | 2625.3 | 3899.6 | 1216.4 | 0.67793 | 5.405
2024-12-10 | 0:30 | Data | 0 | 33.642 | 32.15 | 167.858 | 7.64 | 158.607 | 2227.95 | 25.84 | 47.623 | 6.41 | 1.283 | 4.094 | 8390.99 | 1.614 | 97.9 | 76.1 | 1448 | 23.81 | 5454.1 | 2692.2 | 2612.3 | 3881.3 | 1216.4 | 0.67617 | 5.377
2024-12-10 | 0:30 | Data | 0 | 33.642 | 32.136 | 167.767 | 7.64 | 158.652 | 2227.95 | 25.84 | 47.623 | 6.4 | 1.279 | 4.116 | 8400.04 | 1.641 | 97.9 | 76.3 | 1448 | 23.86 | 5460 | 2682.6 | 2648.2 | 3894.3 | 1216.4 | 0.67183 | 5.395
2024-12-10 | 0:30 | Data | 0 | 33.642 | 32.028 | 167.813 | 7.64 | 158.562 | 2227.95 | 25.84 | 47.533 | 6.4 | 1.284 | 4.134 | 8404.56 | 1.614 | 97.9 | 76.3 | 1448 | 23.81 | 5463 | 2698 | 2637.8 | 3898.4 | 1216.4 | 0.67521 | 5.419
2024-12-10 | 0:30 | Data | 0 | 33.756 | 32.048 | 167.858 | 7.64 | 158.562 | 2227.95 | 25.84 | 47.623 | 6.4 | 1.289 | 4.104 | 8400.04 | 1.782 | 97.9 | 76.1 | 1448 | 23.81 | 5460 | 2694.4 | 2643.4 | 3903.1 | 1216.4 | 0.67056 | 5.392
2024-12-10 | 0:30 | Data | 0 | 33.81 | 32.035 | 167.903 | 7.64 | 158.698 | 2230.66 | 25.84 | 47.714 | 6.41 | 1.29 | 4.105 | 8418.13 | 1.519 | 97.9 | 76.1 | 1450 | 23.86 | 5471.8 | 2684.6 | 2657.8 | 3905.7 | 1216.4 | 0.67174 | 5.393
2024-12-10 | 0:30 | Data | 0 | 33.783 | 31.92 | 167.813 | 7.64 | 158.607 | 2230.66 | 25.84 | 47.623 | 6.41 | 1.289 | 4.122 | 8427.17 | 1.566 | 97.9 | 76.2 | 1450 | 23.86 | 5477.7 | 2697.9 | 2615.2 | 3887.4 | 1216.4 | 0.67618 | 5.411
2024-12-10 | 0:30 | Data | 0 | 33.959 | 31.981 | 167.813 | 7.64 | 158.607 | 2227.95 | 25.84 | 47.623 | 6.4 | 1.277 | 4.137 | 8427.17 | 1.735 | 97.9 | 76.4 | 1448 | 23.86 | 5477.7 | 2700.9 | 2631.2 | 3895.4 | 1216.4 | 0.67597 | 5.414
2024-12-10 | 0:31 | Data | 0 | 33.642 | 32.251 | 167.813 | 7.64 | 158.607 | 2223.43 | 25.84 | 47.623 | 6.4 | 1.289 | 4.115 | 8427.17 | 1.573 | 97.9 | 76.1 | 1446 | 23.81 | 5477.7 | 2680.8 | 2638 | 3888.9 | 1216.4 | 0.67342 | 5.405
2024-12-10 | 0:31 | Data | 0 | 33.642 | 31.812 | 167.722 | 7.64 | 158.517 | 2229.75 | 25.84 | 47.714 | 6.4 | 1.284 | 4.106 | 8418.13 | 1.661 | 97.9 | 76.2 | 1449 | 23.86 | 5471.8 | 2698.7 | 2651.8 | 3899.8 | 1216.4 | 0.67187 | 5.391
2024-12-10 | 0:31 | Data | 0 | 33.871 | 31.873 | 168.084 | 7.63 | 158.652 | 2227.95 | 25.84 | 47.714 | 6.41 | 1.278 | 4.094 | 8418.13 | 1.749 | 97.9 | 76.2 | 1448 | 23.81 | 5471.8 | 2689.8 | 2626.3 | 3885.2 | 1216.4 | 0.67502 | 5.373
2024-12-10 | 0:31 | Data | 0 | 33.642 | 31.853 | 167.813 | 7.64 | 158.517 | 2224.33 | 25.83 | 47.623 | 6.4 | 1.276 | 4.091 | 8427.17 | 1.728 | 97.9 | 76.2 | 1446 | 23.81 | 5477.7 | 2693 | 2626.9 | 3891.9 | 1216.4 | 0.67428 | 5.366
2024-12-10 | 0:31 | Data | 0 | 33.642 | 31.859 | 167.767 | 7.64 | 158.562 | 2227.95 | 25.84 | 47.623 | 6.4 | 1.289 | 4.09 | 8409.08 | 1.715 | 97.9 | 76 | 1448 | 23.81 | 5465.9 | 2705.5 | 2639.1 | 3905.6 | 1216.4 | 0.67676 | 5.38
2024-12-10 | 0:31 | Data | 0 | 33.621 | 32.15 | 167.767 | 7.63 | 158.607 | 2227.95 | 25.84 | 47.353 | 6.4 | 1.286 | 4.107 | 8409.08 | 1.614 | 97.9 | 76.2 | 1448 | 23.68 | 5465.9 | 2707.7 | 2629 | 3902.2 | 1216.4 | 0.67619 | 5.393
2024-12-10 | 0:31 | Data | 0 | 33.804 | 32.264 | 167.903 | 7.64 | 158.562 | 2227.95 | 25.84 | 47.082 | 6.4 | 1.277 | 4.105 | 8395.51 | 1.688 | 97.9 | 76.3 | 1448 | 23.54 | 5457.1 | 2675.7 | 2617.3 | 3873.8 | 1216.4 | 0.67314 | 5.382
2024-12-10 | 0:31 | Data | 0 | 33.945 | 32.055 | 167.903 | 7.64 | 158.698 | 2233.37 | 25.84 | 47.443 | 6.4 | 1.279 | 4.134 | 8409.08 | 1.823 | 97.9 | 76.4 | 1452 | 23.68 | 5465.9 | 2668.3 | 2637.9 | 3884.3 | 1216.5 | 0.66934 | 5.413
2024-12-10 | 0:31 | Data | 0 | 33.473 | 32.204 | 167.722 | 7.63 | 158.562 | 2227.95 | 25.84 | 47.353 | 6.4 | 1.287 | 4.136 | 8418.13 | 1.479 | 97.9 | 76.3 | 1448 | 23.68 | 5471.8 | 2693.4 | 2639.7 | 3893.3 | 1216.5 | 0.67333 | 5.422
2024-12-10 | 0:31 | Data | 0 | 33.986 | 32.048 | 167.993 | 7.64 | 158.652 | 2227.95 | 25.84 | 47.353 | 6.4 | 1.283 | 4.092 | 8454.3 | 1.668 | 97.9 | 76.1 | 1448 | 23.68 | 5495.3 | 2679.3 | 2630.1 | 3883.6 | 1216.5 | 0.67323 | 5.375
2024-12-10 | 0:31 | Data | 0 | 33.635 | 31.866 | 167.767 | 7.64 | 158.562 | 2236.08 | 25.84 | 47.353 | 6.41 | 1.283 | 4.116 | 8445.26 | 1.6 | 97.9 | 76.2 | 1453 | 23.68 | 5489.4 | 2691.7 | 2646.1 | 3903.3 | 1216.5 | 0.67356 | 5.4
2024-12-10 | 0:31 | Data | 0 | 33.419 | 32.015 | 167.813 | 7.64 | 158.517 | 2229.75 | 25.84 | 47.623 | 6.4 | 1.29 | 4.118 | 8458.83 | 1.539 | 97.9 | 76.2 | 1449 | 23.81 | 5498.2 | 2674 | 2625.8 | 3874.2 | 1216.5 | 0.67332 | 5.408
2024-12-10 | 0:31 | Data | 0 | 33.844 | 32.055 | 167.903 | 7.64 | 158.652 | 2230.66 | 25.84 | 47.623 | 6.4 | 1.284 | 4.129 | 8454.3 | 1.607 | 97.9 | 76.3 | 1450 | 23.81 | 5495.3 | 2707.1 | 2655.6 | 3919.4 | 1216.5 | 0.67441 | 5.414
2024-12-10 | 0:31 | Data | 0 | 33.615 | 32.028 | 167.813 | 7.63 | 158.607 | 2229.75 | 25.84 | 47.623 | 6.4 | 1.277 | 4.114 | 8458.83 | 1.607 | 97.9 | 76.3 | 1450 | 23.81 | 5498.2 | 2693.7 | 2640.9 | 3898.9 | 1216.5 | 0.67286 | 5.391
2024-12-10 | 0:31 | Data | 0 | 33.615 | 31.94 | 167.858 | 7.64 | 158.607 | 2229.75 | 25.85 | 47.623 | 6.4 | 1.282 | 4.095 | 8463.35 | 1.715 | 97.9 | 76.1 | 1449 | 23.81 | 5501.2 | 2682.8 | 2639.6 | 3896.6 | 1216.5 | 0.67043 | 5.378
2024-12-10 | 0:31 | Data | 0 | 33.648 | 31.927 | 167.858 | 7.64 | 158.607 | 2229.75 | 25.84 | 47.623 | 6.4 | 1.286 | 4.113 | 8445.26 | 1.6 | 97.9 | 76.2 | 1449 | 23.86 | 5489.4 | 2690.7 | 2648.6 | 3902 | 1216.5 | 0.67213 | 5.398
2024-12-10 | 0:31 | Data | 0 | 33.642 | 32.035 | 167.767 | 7.64 | 158.562 | 2230.66 | 25.84 | 47.623 | 6.4 | 1.29 | 4.111 | 8445.26 | 1.553 | 97.9 | 76.1 | 1449 | 23.86 | 5489.4 | 2664 | 2637.8 | 3877.6 | 1216.5 | 0.67013 | 5.401
2024-12-10 | 0:31 | Data | 0 | 34.168 | 32.156 | 167.903 | 7.64 | 158.562 | 2230.66 | 25.84 | 47.533 | 6.4 | 1.288 | 4.115 | 8454.3 | 1.681 | 97.9 | 76.2 | 1450 | 23.81 | 5495.3 | 2690.7 | 2633.5 | 3892.1 | 1216.5 | 0.67442 | 5.403
2024-12-10 | 0:32 | Data | 0 | 33.628 | 32.028 | 167.858 | 7.64 | 158.652 | 2229.75 | 25.84 | 47.623 | 6.4 | 1.28 | 4.124 | 8454.3 | 1.607 | 97.9 | 76.3 | 1449 | 23.86 | 5495.3 | 2692.3 | 2617.8 | 3883.3 | 1216.5 | 0.67409 | 5.404
2024-12-10 | 0:32 | Data | 0 | 33.986 | 32.258 | 167.948 | 7.64 | 158.698 | 2233.37 | 25.84 | 47.714 | 6.4 | 1.291 | 4.105 | 8440.74 | 1.647 | 97.9 | 76.1 | 1452 | 23.86 | 5486.5 | 2666.7 | 2635 | 3880.4 | 1216.5 | 0.67016 | 5.395
2024-12-10 | 0:32 | Data | 0 | 33.446 | 31.974 | 167.858 | 7.64 | 158.562 | 2229.75 | 25.83 | 47.714 | 6.4 | 1.295 | 4.105 | 8454.3 | 1.62 | 97.9 | 76 | 1449 | 23.86 | 5495.3 | 2699 | 2632.2 | 3889.7 | 1216.5 | 0.67335 | 5.401
2024-12-10 | 0:32 | Data | 0 | 33.642 | 32.048 | 167.858 | 7.64 | 158.607 | 2229.75 | 25.84 | 47.623 | 6.4 | 1.29 | 4.089 | 8454.3 | 1.573 | 97.9 | 76 | 1450 | 23.81 | 5495.3 | 2692.3 | 2672.4 | 3916.2 | 1216.5 | 0.67152 | 5.38
2024-12-10 | 0:32 | Data | 0 | 33.48 | 32.028 | 167.813 | 7.64 | 158.652 | 2232.47 | 25.85 | 47.623 | 6.4 | 1.283 | 4.079 | 8463.35 | 1.593 | 97.9 | 76.1 | 1451 | 23.81 | 5501.2 | 2691 | 2673.6 | 3921.5 | 1216.5 | 0.66908 | 5.363
2024-12-10 | 0:32 | Data | 0 | 33.554 | 32.028 | 167.722 | 7.64 | 158.607 | 2233.37 | 25.84 | 47.623 | 6.4 | 1.275 | 4.079 | 8449.78 | 1.6 | 97.9 | 76.2 | 1451 | 23.81 | 5492.4 | 2690.6 | 2657.6 | 3913.8 | 1216.5 | 0.66845 | 5.354
2024-12-10 | 0:32 | Data | 0 | 33.642 | 32.352 | 167.813 | 7.64 | 158.562 | 2239.7 | 25.84 | 47.623 | 6.4 | 1.285 | 4.085 | 8458.83 | 1.553 | 97.9 | 76.1 | 1455 | 23.86 | 5498.2 | 2681.5 | 2626.8 | 3882.1 | 1216.5 | 0.67221 | 5.37
2024-12-10 | 0:32 | Data | 0 | 33.527 | 32.028 | 167.813 | 7.64 | 158.607 | 2236.08 | 25.83 | 47.443 | 6.4 | 1.291 | 4.102 | 8431.69 | 1.6 | 97.9 | 76.1 | 1453 | 23.72 | 5480.6 | 2703.9 | 2648.7 | 3905.8 | 1216.5 | 0.67487 | 5.392
2024-12-10 | 0:32 | Data | 0 | 33.486 | 31.832 | 167.858 | 7.64 | 158.607 | 2236.08 | 25.84 | 47.353 | 6.4 | 1.282 | 4.11 | 8431.69 | 1.479 | 97.9 | 76.2 | 1453 | 23.72 | 5480.6 | 2682.8 | 2644.2 | 3895.7 | 1216.5 | 0.67226 | 5.392
2024-12-10 | 0:32 | Data | 0 | 33.756 | 32.028 | 167.858 | 7.64 | 158.652 | 2125.81 | 25.84 | 47.623 | 6.4 | 1.282 | 4.109 | 8422.65 | 1.62 | 97.8 | 76.2 | 1382 | 23.81 | 5474.7 | 2695.6 | 2651.1 | 3904.9 | 1216.5 | 0.67487 | 5.392
2024-12-10 | 0:32 | Data | 0 | 33.979 | 32.089 | 167.813 | 7.64 | 158.698 | 2212.58 | 25.84 | 47.353 | 6.4 | 1.294 | 4.093 | 8418.13 | 1.661 | 97.9 | 76 | 1438 | 23.72 | 5471.8 | 2697.8 | 2651.9 | 3898.6 | 1216.5 | 0.67391 | 5.387
2024-12-10 | 0:32 | Data | 0 | 33.669 | 32.042 | 167.813 | 7.64 | 158.652 | 2213.49 | 25.84 | 47.623 | 6.4 | 1.291 | 4.102 | 8395.51 | 1.573 | 97.9 | 76.1 | 1439 | 23.72 | 5457.1 | 2700 | 2645.4 | 3906.3 | 1216.5 | 0.67042 | 5.392
2024-12-10 | 0:32 | Data | 0 | 33.675 | 32.028 | 167.858 | 7.64 | 158.607 | 2213.49 | 25.84 | 47.623 | 6.4 | 1.282 | 4.094 | 8427.17 | 1.614 | 97.8 | 76.2 | 1439 | 23.77 | 5477.7 | 2675.1 | 2633.2 | 3895.7 | 1216.5 | 0.66953 | 5.373
2024-12-10 | 0:32 | Data | 0 | 34.033 | 32.156 | 167.858 | 7.64 | 158.698 | 2211.68 | 25.84 | 47.443 | 6.4 | 1.284 | 4.091 | 8409.08 | 1.607 | 97.9 | 76.1 | 1438 | 23.68 | 5465.9 | 2704.1 | 2645.8 | 3909.8 | 1216.5 | 0.6748 | 5.376
2024-12-10 | 0:32 | Data | 0 | 33.837 | 32.042 | 167.858 | 7.64 | 158.607 | 2229.75 | 25.83 | 47.353 | 6.4 | 1.279 | 4.088 | 8427.17 | 1.809 | 97.9 | 76.2 | 1450 | 23.68 | 5477.7 | 2712.7 | 2616.3 | 3896.6 | 1216.5 | 0.67426 | 5.367
2024-12-10 | 0:32 | Data | 0 | 33.858 | 32.264 | 167.858 | 7.64 | 158.652 | 2230.66 | 25.84 | 47.443 | 6.4 | 1.273 | 4.131 | 8400.04 | 1.607 | 97.9 | 76.4 | 1450 | 23.68 | 5460 | 2703.3 | 2643.9 | 3906.2 | 1216.5 | 0.67468 | 5.405
2024-12-10 | 0:32 | Data | 0 | 34.074 | 32.062 | 167.903 | 7.64 | 158.652 | 2229.75 | 25.84 | 47.353 | 6.4 | 1.282 | 4.122 | 8395.51 | 1.755 | 97.9 | 76.3 | 1449 | 23.63 | 5457.1 | 2708.5 | 2643.7 | 3910.8 | 1216.5 | 0.67857 | 5.403
2024-12-10 | 0:33 | Data | 0 | 33.419 | 31.913 | 167.813 | 7.63 | 158.607 | 2229.75 | 25.84 | 47.623 | 6.41 | 1.286 | 4.104 | 8386.47 | 1.614 | 97.9 | 76.1 | 1449 | 23.81 | 5451.2 | 2686 | 2651.3 | 3893.3 | 1216.5 | 0.67091 | 5.39
2024-12-10 | 0:33 | Data | 0 | 33.871 | 32.264 | 167.993 | 7.64 | 158.652 | 2229.75 | 25.84 | 47.443 | 6.4 | 1.287 | 4.102 | 8381.95 | 1.607 | 97.9 | 76.1 | 1449 | 23.68 | 5448.3 | 2682.5 | 2648.3 | 3900 | 1216.5 | 0.6704 | 5.388
2024-12-10 | 0:33 | Data | 0 | 33.669 | 32.15 | 167.948 | 7.64 | 158.607 | 2235.18 | 25.83 | 47.353 | 6.4 | 1.288 | 4.119 | 8395.51 | 1.62 | 97.9 | 76.2 | 1453 | 23.68 | 5457.1 | 2709.3 | 2634.6 | 3907.3 | 1216.5 | 0.67539 | 5.407
2024-12-10 | 0:33 | Data | 0 | 33.642 | 32.028 | 167.767 | 7.64 | 158.562 | 2229.75 | 25.83 | 47.353 | 6.4 | 1.289 | 4.124 | 8404.56 | 1.499 | 97.9 | 76.2 | 1449 | 23.68 | 5463 | 2687.3 | 2661.3 | 3908.2 | 1216.5 | 0.67163 | 5.412
2024-12-10 | 0:33 | Data | 0 | 33.871 | 32.264 | 167.993 | 7.64 | 158.698 | 2230.66 | 25.84 | 47.353 | 6.4 | 1.289 | 4.105 | 8400.04 | 1.607 | 97.9 | 76.1 | 1449 | 23.68 | 5460 | 2684.2 | 2642.8 | 3897.8 | 1216.5 | 0.67284 | 5.394
2024-12-10 | 0:33 | Data | 0 | 33.912 | 32.264 | 167.903 | 7.64 | 158.652 | 2232.47 | 25.84 | 47.353 | 6.4 | 1.277 | 4.086 | 8386.47 | 1.614 | 97.9 | 76.2 | 1451 | 23.68 | 5451.2 | 2706.2 | 2662.5 | 3919 | 1216.5 | 0.67104 | 5.363
2024-12-10 | 0:33 | Data | 0 | 33.702 | 32.028 | 167.813 | 7.64 | 158.562 | 2232.47 | 25.84 | 47.262 | 6.4 | 1.282 | 4.087 | 8377.43 | 1.641 | 97.9 | 76.1 | 1452 | 23.63 | 5445.3 | 2674.4 | 2662.7 | 3903.9 | 1216.5 | 0.66763 | 5.369
2024-12-10 | 0:33 | Data | 0 | 33.642 | 32.143 | 167.858 | 7.64 | 158.562 | 2232.47 | 25.84 | 47.353 | 6.4 | 1.284 | 4.104 | 8359.34 | 1.614 | 97.9 | 76.2 | 1451 | 23.72 | 5433.6 | 2687.1 | 2654.3 | 3906.7 | 1216.5 | 0.66917 | 5.388
2024-12-10 | 0:33 | Data | 0 | 33.844 | 32.312 | 167.948 | 7.64 | 158.698 | 2231.56 | 25.84 | 47.353 | 6.4 | 1.279 | 4.112 | 8359.34 | 1.782 | 97.9 | 76.3 | 1449 | 23.68 | 5433.6 | 2676.6 | 2634 | 3885.5 | 1216.5 | 0.66978 | 5.391
2024-12-10 | 0:33 | Data | 0 | 33.419 | 32.116 | 167.767 | 7.64 | 158.607 | 2230.66 | 25.83 | 47.443 | 6.4 | 1.278 | 4.11 | 8372.9 | 1.614 | 97.9 | 76.3 | 1450 | 23.72 | 5442.4 | 2706 | 2657.2 | 3918.7 | 1216.5 | 0.67282 | 5.388
2024-12-10 | 0:33 | Data | 0 | 33.534 | 32.001 | 167.767 | 7.64 | 158.562 | 2230.66 | 25.84 | 47.353 | 6.4 | 1.282 | 4.122 | 8359.34 | 1.452 | 97.9 | 76.3 | 1450 | 23.68 | 5433.6 | 2699.5 | 2653.8 | 3909 | 1216.5 | 0.67508 | 5.403
2024-12-10 | 0:33 | Data | 0 | 33.669 | 32.008 | 167.858 | 7.64 | 158.562 | 2227.95 | 25.84 | 47.353 | 6.4 | 1.274 | 4.092 | 8386.47 | 1.668 | 97.9 | 76.3 | 1448 | 23.68 | 5451.2 | 2697.5 | 2635.4 | 3898.7 | 1216.6 | 0.67504 | 5.366
2024-12-10 | 0:33 | Data | 0 | 33.817 | 32.312 | 167.858 | 7.64 | 158.652 | 2227.04 | 25.83 | 47.353 | 6.4 | 1.279 | 4.067 | 8381.95 | 1.411 | 97.9 | 76.1 | 1448 | 23.72 | 5448.3 | 2683.2 | 2641.9 | 3898.8 | 1216.6 | 0.66944 | 5.346
2024-12-10 | 0:33 | Data | 0 | 33.642 | 32.028 | 167.813 | 7.63 | 158.607 | 2230.66 | 25.84 | 47.443 | 6.4 | 1.286 | 4.088 | 8386.47 | 1.614 | 97.9 | 76.1 | 1450 | 23.68 | 5451.2 | 2700.5 | 2650.1 | 3913 | 1216.6 | 0.67398 | 5.374
2024-12-10 | 0:33 | Data | 0 | 34.04 | 32.487 | 167.858 | 7.64 | 158.652 | 2230.66 | 25.84 | 47.443 | 6.4 | 1.285 | 4.105 | 8381.95 | 1.492 | 97.9 | 76.2 | 1450 | 23.72 | 5448.3 | 2704.4 | 2636 | 3904 | 1216.6 | 0.67676 | 5.389
2024-12-10 | 0:33 | Data | 0 | 33.642 | 32.42 | 167.903 | 7.64 | 158.607 | 2230.66 | 25.84 | 47.443 | 6.4 | 1.284 | 4.091 | 8345.77 | 1.56 | 97.9 | 76.1 | 1449 | 23.72 | 5424.8 | 2695.1 | 2638 | 3898.2 | 1216.6 | 0.676 | 5.375
2024-12-10 | 0:33 | Data | 0 | 33.898 | 32.042 | 167.813 | 7.64 | 158.652 | 2230.66 | 25.84 | 47.353 | 6.4 | 1.283 | 4.108 | 8350.29 | 1.647 | 97.9 | 76.2 | 1449 | 23.68 | 5427.7 | 2715.9 | 2639.5 | 3909.7 | 1216.6 | 0.67744 | 5.393
2024-12-10 | 0:33 | Data | 0 | 33.702 | 32.028 | 167.903 | 7.64 | 158.607 | 2230.66 | 25.84 | 47.353 | 6.4 | 1.294 | 4.115 | 8345.77 | 1.445 | 97.9 | 76.1 | 1449 | 23.68 | 5424.8 | 2698 | 2637.9 | 3904 | 1216.6 | 0.67325 | 5.41
2024-12-10 | 0:34 | Data | 0 | 33.702 | 32.129 | 167.858 | 7.64 | 158.698 | 2230.66 | 25.85 | 47.353 | 6.4 | 1.297 | 4.093 | 8350.29 | 1.458 | 97.9 | 75.9 | 1450 | 23.68 | 5427.7 | 2709.9 | 2634.8 | 3908.4 | 1216.6 | 0.6765 | 5.389
2024-12-10 | 0:34 | Data | 0 | 33.642 | 32.042 | 167.903 | 7.64 | 158.517 | 2230.66 | 25.84 | 47.353 | 6.4 | 1.282 | 4.124 | 8386.47 | 1.593 | 97.9 | 76.3 | 1449 | 23.68 | 5451.2 | 2702.5 | 2612.5 | 3885 | 1216.6 | 0.67667 | 5.406
2024-12-10 | 0:34 | Data | 0 | 33.669 | 32.15 | 167.903 | 7.64 | 158.607 | 2230.66 | 25.84 | 47.443 | 6.41 | 1.29 | 4.12 | 8372.9 | 1.62 | 97.9 | 76.2 | 1450 | 23.72 | 5442.4 | 2678.2 | 2641.3 | 3890.1 | 1216.6 | 0.67203 | 5.41
2024-12-10 | 0:34 | Data | 0 | 33.804 | 32.042 | 167.993 | 7.64 | 158.652 | 2235.18 | 25.84 | 47.353 | 6.4 | 1.286 | 4.124 | 8386.47 | 1.762 | 97.9 | 76.2 | 1453 | 23.68 | 5451.2 | 2705.7 | 2622.3 | 3894.1 | 1216.6 | 0.67664 | 5.41
2024-12-10 | 0:34 | Data | 0 | 33.642 | 32.204 | 167.813 | 7.64 | 158.562 | 2228.85 | 25.84 | 47.443 | 6.4 | 1.288 | 4.13 | 8368.38 | 1.614 | 97.9 | 76.2 | 1449 | 23.68 | 5439.4 | 2671 | 2646.2 | 3889.4 | 1216.6 | 0.67333 | 5.419
2024-12-10 | 0:34 | Data | 0 | 33.648 | 32.028 | 167.903 | 7.64 | 158.652 | 2233.37 | 25.84 | 47.353 | 6.4 | 1.284 | 4.141 | 8363.86 | 1.627 | 97.9 | 76.3 | 1452 | 23.68 | 5436.5 | 2701.4 | 2621.4 | 3890.5 | 1216.6 | 0.67647 | 5.425
2024-12-10 | 0:34 | Data | 0 | 33.756 | 31.866 | 167.813 | 7.64 | 158.607 | 2232.47 | 25.84 | 47.443 | 6.4 | 1.288 | 4.092 | 8354.81 | 1.499 | 97.9 | 76.1 | 1451 | 23.68 | 5430.6 | 2688.6 | 2669.2 | 3916 | 1216.6 | 0.67054 | 5.38
2024-12-10 | 0:34 | Data | 0 | 33.689 | 32.15 | 167.858 | 7.64 | 158.607 | 2232.47 | 25.84 | 47.353 | 6.4 | 1.283 | 4.101 | 8372.9 | 1.499 | 97.9 | 76.2 | 1452 | 23.68 | 5442.4 | 2660.8 | 2635.6 | 3879.4 | 1216.6 | 0.66757 | 5.384
2024-12-10 | 0:34 | Data | 0 | 33.642 | 32.042 | 167.813 | 7.64 | 158.607 | 2230.66 | 25.84 | 47.353 | 6.4 | 1.278 | 4.09 | 8345.77 | 1.688 | 97.9 | 76.2 | 1449 | 23.68 | 5424.8 | 2699.8 | 2634.7 | 3897.7 | 1216.6 | 0.67394 | 5.369
2024-12-10 | 0:34 | Data | 0 | 34.074 | 32.278 | 167.993 | 7.64 | 158.743 | 2229.75 | 25.84 | 47.443 | 6.4 | 1.278 | 4.096 | 8377.43 | 1.695 | 97.9 | 76.2 | 1449 | 23.72 | 5445.3 | 2671.8 | 2627 | 3876.2 | 1216.6 | 0.67189 | 5.373
2024-12-10 | 0:34 | Data | 0 | 33.81 | 32.379 | 167.993 | 7.64 | 158.652 | 2232.47 | 25.84 | 47.443 | 6.4 | 1.284 | 4.121 | 8372.9 | 1.776 | 97.9 | 76.2 | 1452 | 23.68 | 5442.4 | 2682.1 | 2657.6 | 3904.9 | 1216.6 | 0.66979 | 5.405
2024-12-10 | 0:34 | Data | 0 | 33.648 | 32.237 | 167.903 | 7.64 | 158.607 | 2232.47 | 25.84 | 47.353 | 6.4 | 1.287 | 4.098 | 8372.9 | 1.499 | 97.9 | 76.1 | 1451 | 23.68 | 5442.4 | 2697.8 | 2644.4 | 3901.6 | 1216.6 | 0.67217 | 5.385
2024-12-10 | 0:34 | Data | 0 | 33.75 | 32.055 | 167.903 | 7.64 | 158.607 | 2225.23 | 25.84 | 47.353 | 6.4 | 1.29 | 4.092 | 8386.47 | 1.6 | 97.9 | 76 | 1446 | 23.68 | 5451.2 | 2716.3 | 2639.3 | 3909.2 | 1216.6 | 0.67457 | 5.382
2024-12-10 | 0:34 | Data | 0 | 33.864 | 32.372 | 167.948 | 7.64 | 158.698 | 2229.75 | 25.84 | 47.443 | 6.4 | 1.286 | 4.101 | 8381.95 | 1.526 | 97.9 | 76.1 | 1449 | 23.68 | 5448.3 | 2684.2 | 2648.2 | 3901.9 | 1216.6 | 0.6712 | 5.389
2024-12-10 | 0:34 | Data | 0 | 33.871 | 32.035 | 167.948 | 7.64 | 158.607 | 2229.75 | 25.84 | 47.353 | 6.4 | 1.286 | 4.093 | 8386.47 | 1.634 | 97.9 | 76.1 | 1449 | 23.68 | 5451.2 | 2698.4 | 2649.8 | 3913.3 | 1216.6 | 0.6717 | 5.379
2024-12-10 | 0:34 | Data | 0 | 33.642 | 32.028 | 167.813 | 7.63 | 158.607 | 2226.14 | 25.84 | 47.353 | 6.4 | 1.288 | 4.087 | 8386.47 | 1.614 | 97.9 | 76 | 1447 | 23.68 | 5451.2 | 2680.5 | 2658.6 | 3905.3 | 1216.6 | 0.6693 | 5.375
2024-12-10 | 0:34 | Data | 0 | 33.642 | 32.251 | 167.903 | 7.64 | 158.652 | 2235.18 | 25.83 | 47.353 | 6.4 | 1.292 | 4.108 | 8390.99 | 1.593 | 97.9 | 76.1 | 1453 | 23.72 | 5454.1 | 2699.1 | 2640.4 | 3901.9 | 1216.6 | 0.6742 | 5.401
2024-12-10 | 0:34 | Data | 0 | 33.561 | 32.129 | 167.948 | 7.64 | 158.698 | 2236.08 | 25.84 | 47.262 | 6.4 | 1.282 | 4.134 | 8829.65 | 1.465 | 97.9 | 76.3 | 1453 | 23.68 | 5739.3 | 2688.4 | 2633.8 | 3895.9 | 1216.6 | 0.67282 | 5.416
2024-12-10 | 0:35 | Data | 0 | 33.642 | 32.204 | 167.813 | 7.64 | 158.607 | 2236.08 | 25.84 | 47.443 | 6.4 | 1.282 | 4.11 | 8386.47 | 1.492 | 97.9 | 76.2 | 1453 | 23.68 | 5451.2 | 2709.1 | 2670.2 | 3932.2 | 1216.6 | 0.67361 | 5.392
2024-12-10 | 0:35 | Data | 0 | 33.642 | 32.055 | 167.858 | 7.64 | 158.562 | 2236.08 | 25.84 | 47.353 | 6.4 | 1.287 | 4.096 | 8386.47 | 1.56 | 97.9 | 76.1 | 1453 | 23.68 | 5451.2 | 2697.7 | 2638.3 | 3902 | 1216.6 | 0.67412 | 5.384
2024-12-10 | 0:35 | Data | 0 | 33.858 | 32.028 | 167.903 | 7.64 | 158.652 | 2230.66 | 25.83 | 47.353 | 6.4 | 1.29 | 4.093 | 8386.47 | 1.641 | 97.9 | 76 | 1451 | 23.68 | 5451.2 | 2693.4 | 2643.5 | 3901.6 | 1216.6 | 0.67432 | 5.382
2024-12-10 | 0:35 | Data | 0 | 33.925 | 32.042 | 167.993 | 7.63 | 158.652 | 2235.18 | 25.84 | 47.353 | 6.4 | 1.291 | 4.092 | 8400.04 | 1.708 | 97.9 | 76 | 1453 | 23.72 | 5460 | 2686.6 | 2658.7 | 3907.1 | 1216.6 | 0.66956 | 5.383
2024-12-10 | 0:35 | Data | 0 | 33.817 | 32.237 | 167.767 | 7.64 | 158.607 | 2234.27 | 25.84 | 47.353 | 6.4 | 1.295 | 4.098 | 8377.43 | 1.661 | 97.9 | 76 | 1453 | 23.68 | 5445.3 | 2702.6 | 2640 | 3901.7 | 1216.6 | 0.67425 | 5.392
2024-12-10 | 0:35 | Data | 0 | 33.972 | 32.102 | 167.903 | 7.64 | 158.652 | 2234.27 | 25.84 | 47.443 | 6.4 | 1.283 | 4.109 | 8386.47 | 1.782 | 97.9 | 76.2 | 1453 | 23.68 | 5451.2 | 2697.3 | 2679 | 3928.2 | 1216.6 | 0.66941 | 5.392
2024-12-10 | 0:35 | Data | 0 | 34.08 | 32.102 | 167.948 | 7.64 | 158.743 | 2235.18 | 25.83 | 47.353 | 6.4 | 1.282 | 4.099 | 8386.47 | 1.809 | 97.9 | 76.2 | 1453 | 23.72 | 5451.2 | 2703 | 2665.3 | 3923.5 | 1216.6 | 0.67071 | 5.383
2024-12-10 | 0:35 | Data | 0 | 33.891 | 32.035 | 167.903 | 7.64 | 158.698 | 2234.27 | 25.83 | 47.353 | 6.4 | 1.272 | 4.072 | 8363.86 | 1.843 | 97.9 | 76.2 | 1452 | 23.72 | 5436.5 | 2708.4 | 2626.6 | 3896.7 | 1216.6 | 0.67986 | 5.345
2024-12-10 | 0:35 | Data | 0 | 33.858 | 32.055 | 167.903 | 7.63 | 158.607 | 2232.47 | 25.84 | 47.082 | 6.4 | 1.275 | 4.116 | 8372.9 | 1.614 | 97.9 | 76.3 | 1452 | 23.54 | 5442.4 | 2706.1 | 2622.4 | 3891.9 | 1216.6 | 0.67921 | 5.392
2024-12-10 | 0:35 | Data | 0 | 33.642 | 32.035 | 167.948 | 7.63 | 158.652 | 2232.47 | 25.84 | 46.721 | 6.4 | 1.288 | 4.086 | 8372.9 | 1.6 | 97.9 | 76 | 1451 | 23.36 | 5442.4 | 2697 | 2568.4 | 3850.4 | 1216.6 | 0.68514 | 5.375
2024-12-10 | 0:35 | Data | 0 | 33.655 | 32.237 | 167.948 | 7.64 | 158.698 | 2233.37 | 25.84 | 47.082 | 6.4 | 1.295 | 4.08 | 8372.9 | 1.553 | 97.9 | 75.9 | 1451 | 23.54 | 5442.4 | 2703.8 | 2647 | 3907.6 | 1216.6 | 0.6734 | 5.374
2024-12-10 | 0:35 | Data | 0 | 33.756 | 32.258 | 167.993 | 7.63 | 158.652 | 2233.37 | 25.84 | 47.172 | 6.4 | 1.294 | 4.07 | 8386.47 | 1.398 | 97.9 | 75.9 | 1452 | 23.59 | 5451.2 | 2699.1 | 2635.1 | 3901.8 | 1216.6 | 0.67295 | 5.363
2024-12-10 | 0:35 | Data | 0 | 33.419 | 32.15 | 167.858 | 7.63 | 158.607 | 2233.37 | 25.84 | 47.172 | 6.4 | 1.297 | 4.096 | 8386.47 | 1.701 | 97.9 | 76 | 1452 | 23.54 | 5451.2 | 2640.4 | 2652.8 | 3857.8 | 1216.6 | 0.66867 | 5.392
2024-12-10 | 0:35 | Data | 0 | 33.986 | 32.264 | 167.948 | 7.64 | 158.743 | 2232.47 | 25.84 | 47.172 | 6.4 | 1.296 | 4.09 | 8400.04 | 1.452 | 97.9 | 76 | 1451 | 23.59 | 5460 | 1601.3 | 2057.3 | 2619.9 | 1216.6 | 0.60878 | 5.385
2024-12-10 | 0:35 | Data | 0 | 33.696 | 32.143 | 167.948 | 7.64 | 158.698 | 2229.75 | 25.84 | 47.082 | 6.4 | 1.284 | 4.103 | 8404.56 | 1.506 | 97.9 | 76.2 | 1449 | 23.54 | 5463 | 1595.6 | 2056.5 | 2616.7 | 1216.6 | 0.60759 | 5.387
2024-12-10 | 0:35 | Data | 0 | 33.912 | 32.264 | 167.948 | 7.64 | 158.743 | 2232.47 | 25.84 | 47.082 | 6.4 | 1.288 | 4.112 | 8386.47 | 1.62 | 97.9 | 76.2 | 1451 | 23.54 | 5451.2 | 1611.6 | 2066.2 | 2628.6 | 1216.6 | 0.60968 | 5.399
2024-12-10 | 0:35 | Data | 0 | 33.844 | 32.204 | 167.858 | 7.64 | 158.698 | 2236.08 | 25.84 | 47.082 | 6.4 | 1.288 | 4.111 | 8381.95 | 1.627 | 97.9 | 76.1 | 1453 | 23.54 | 5448.3 | 1598.4 | 2051.9 | 2614.9 | 1216.7 | 0.60935 | 5.399
2024-12-10 | 0:36 | Data | 0 | 33.871 | 32.237 | 167.813 | 7.64 | 158.652 | 2232.47 | 25.84 | 47.443 | 6.4 | 1.282 | 4.113 | 8386.47 | 1.816 | 97.9 | 76.2 | 1451 | 23.68 | 5451.2 | 1622.9 | 2046.9 | 2625.6 | 1216.7 | 0.61513 | 5.395
2024-12-10 | 0:36 | Data | 0 | 33.642 | 32.028 | 167.813 | 7.64 | 158.652 | 2233.37 | 25.84 | 47.172 | 6.41 | 1.282 | 4.121 | 8400.04 | 1.816 | 97.9 | 76.3 | 1452 | 23.59 | 5460 | 1605.7 | 2050.1 | 2618.4 | 1216.7 | 0.61027 | 5.402
2024-12-10 | 0:36 | Data | 0 | 33.864 | 32.264 | 167.948 | 7.64 | 158.652 | 2229.75 | 25.84 | 47.082 | 6.4 | 1.291 | 4.11 | 8350.29 | 1.607 | 97.9 | 76.1 | 1450 | 23.59 | 5427.7 | 1610.6 | 2054.5 | 2623.2 | 1216.7 | 0.61122 | 5.401
2024-12-10 | 0:36 | Data | 0 | 34.08 | 32.096 | 167.993 | 7.64 | 158.743 | 2230.66 | 25.84 | 47.262 | 6.4 | 1.28 | 4.107 | 8359.34 | 1.83 | 97.9 | 76.2 | 1450 | 23.72 | 5433.6 | 1602.1 | 2040.7 | 2609.1 | 1216.7 | 0.61144 | 5.387
2024-12-10 | 0:36 | Data | 0 | 33.642 | 32.028 | 167.813 | 7.64 | 158.652 | 2230.66 | 25.84 | 47.262 | 6.4 | 1.283 | 4.098 | 8359.34 | 1.614 | 97.9 | 76.1 | 1449 | 23.59 | 5433.6 | 1610.6 | 2040.5 | 2613.1 | 1216.7 | 0.61384 | 5.381
2024-12-10 | 0:36 | Data | 0 | 33.642 | 32.264 | 167.813 | 7.64 | 158.607 | 2232.47 | 25.84 | 47.262 | 6.4 | 1.283 | 4.112 | 8368.38 | 1.384 | 97.9 | 76.2 | 1451 | 23.63 | 5439.4 | 1610.1 | 2040.1 | 2611.4 | 1216.7 | 0.6148 | 5.393
2024-12-10 | 0:36 | Data | 0 | 33.689 | 32.028 | 171.476 | 7.64 | 161.951 | 2235.18 | 25.84 | 47.262 | 6.4 | 1.282 | 4.124 | 8368.38 | 1.641 | 97.9 | 76.3 | 1453 | 23.68 | 5439.4 | 1628.1 | 2045.9 | 2628.5 | 1216.7 | 0.61638 | 5.406
2024-12-10 | 0:36 | Data | 0 | 33.412 | 31.785 | 176.407 | 7.64 | 166.471 | 2233.37 | 25.83 | 47.353 | 6.4 | 1.293 | 4.21 | 8359.34 | 1.668 | 97.9 | 76.5 | 1452 | 23.68 | 5433.6 | 1706 | 2103.4 | 2720.2 | 1216.7 | 0.62446 | 5.504
2024-12-10 | 0:36 | Data | 0 | 33.183 | 31.569 | 180.568 | 7.64 | 170.222 | 2230.66 | 25.84 | 47.353 | 6.4 | 1.309 | 4.33 | 8363.86 | 1.749 | 97.9 | 76.8 | 1450 | 23.72 | 5436.5 | 1724.2 | 2151.1 | 2769.1 | 1216.7 | 0.62273 | 5.638
2024-12-10 | 0:36 | Data | 0 | 32.953 | 31.11 | 183.915 | 7.64 | 173.295 | 2229.75 | 25.84 | 47.443 | 6.4 | 1.329 | 4.402 | 8377.43 | 1.843 | 97.9 | 76.8 | 1450 | 23.68 | 5445.3 | 1771.7 | 2189.7 | 2827.1 | 1216.7 | 0.62403 | 5.731
2024-12-10 | 0:36 | Data | 0 | 32.737 | 30.982 | 186.855 | 7.64 | 175.916 | 2227.95 | 25.84 | 47.353 | 6.4 | 1.336 | 4.453 | 8368.38 | 1.985 | 97.9 | 76.9 | 1448 | 23.68 | 5439.4 | 1784 | 2208.5 | 2849.1 | 1216.7 | 0.62402 | 5.788
2024-12-10 | 0:36 | Data | 0 | 32.588 | 30.651 | 188.981 | 7.64 | 177.995 | 2222.52 | 25.84 | 46.721 | 6.38 | 1.345 | 4.527 | 8386.47 | 2.052 | 97.9 | 77.1 | 1445 | 23.36 | 5451.2 | 1817.3 | 2245 | 2899.6 | 1216.7 | 0.62483 | 5.873
2024-12-10 | 0:36 | Data | 0 | 32.899 | 30.88 | 190.61 | 7.63 | 179.487 | 2227.95 | 25.83 | 46.54 | 6.39 | 1.344 | 4.603 | 8400.04 | 2.066 | 97.9 | 77.4 | 1448 | 23.27 | 5460 | 1829.2 | 2274.3 | 2935.9 | 1216.7 | 0.62391 | 5.947
2024-12-10 | 0:36 | Data | 0 | 32.568 | 30.435 | 191.876 | 7.64 | 180.662 | 2230.66 | 25.84 | 46.089 | 6.39 | 1.348 | 4.638 | 8409.08 | 2.066 | 97.9 | 77.5 | 1449 | 23 | 5465.9 | 1831.8 | 2254.1 | 2915.4 | 1216.7 | 0.62429 | 5.986
2024-12-10 | 0:36 | Data | 0 | 32.494 | 30.475 | 192.193 | 7.64 | 181.023 | 2230.66 | 25.82 | 45.727 | 6.39 | 1.355 | 4.66 | 8404.56 | 2.079 | 98 | 77.5 | 1450 | 22.86 | 5463 | 1838.1 | 2292.1 | 2948.8 | 1216.7 | 0.62097 | 6.017
2024-12-10 | 0:36 | Data | 0 | 32.669 | 30.82 | 193.188 | 7.63 | 181.837 | 2230.66 | 25.82 | 45.186 | 6.37 | 1.362 | 4.632 | 8436.21 | 2.235 | 98 | 77.3 | 1450 | 22.59 | 5483.5 | 1861 | 2301.1 | 2969.5 | 1216.7 | 0.62445 | 5.993
2024-12-10 | 0:36 | Data | 0 | 32.285 | 30.82 | 194.093 | 7.64 | 182.695 | 2230.66 | 25.82 | 44.825 | 6.38 | 1.361 | 4.658 | 8454.3 | 1.917 | 98 | 77.4 | 1449 | 22.41 | 5495.3 | 1875.7 | 2291.9 | 2972.9 | 1216.7 | 0.6282 | 6.018
2024-12-10 | 0:36 | Data | 0 | 32.467 | 30.624 | 194.002 | 7.64 | 182.605 | 2229.75 | 25.83 | 44.554 | 6.37 | 1.363 | 4.69 | 8463.35 | 2.127 | 98 | 77.5 | 1450 | 22.28 | 5501.2 | 1858.1 | 2310.4 | 2976 | 1216.7 | 0.62233 | 6.052
2024-12-10 | 0:37 | Data | 0 | 32.609 | 30.847 | 194.093 | 7.64 | 182.741 | 2229.75 | 25.82 | 44.283 | 6.37 | 1.364 | 4.672 | 8531.18 | 1.863 | 98 | 77.4 | 1449 | 22.19 | 5545.3 | 1862.2 | 2299.3 | 2969.5 | 1216.7 | 0.62476 | 6.037
2024-12-10 | 0:37 | Data | 0 | 32.723 | 30.536 | 194.409 | 7.64 | 182.921 | 2227.95 | 25.8 | 44.012 | 6.37 | 1.37 | 4.635 | 8549.27 | 2.1 | 98 | 77.2 | 1448 | 22.01 | 5557 | 1878.7 | 2288.3 | 2971.3 | 1216.7 | 0.62926 | 6.006
2024-12-10 | 0:37 | Data | 0 | 32.703 | 30.637 | 195.269 | 7.64 | 183.78 | 2232.47 | 25.81 | 44.102 | 6.37 | 1.367 | 4.647 | 8580.93 | 2.086 | 98 | 77.3 | 1451 | 22.05 | 5577.6 | 1869.9 | 2304 | 2979 | 1216.7 | 0.62552 | 6.015
2024-12-10 | 0:37 | Data | 0 | 32.946 | 30.259 | 195.585 | 7.64 | 184.142 | 2230.66 | 25.8 | 44.012 | 6.37 | 1.372 | 4.701 | 8599.01 | 2.133 | 98 | 77.4 | 1450 | 22.01 | 5589.4 | 1888.8 | 2298.5 | 2986.8 | 1216.7 | 0.62845 | 6.072
2024-12-10 | 0:37 | Data | 0 | 32.723 | 30.651 | 195.585 | 7.63 | 184.051 | 2233.37 | 25.8 | 43.832 | 6.37 | 1.367 | 4.721 | 8576.4 | 1.992 | 98 | 77.6 | 1452 | 21.92 | 5574.7 | 1876.5 | 2323.3 | 2998 | 1216.7 | 0.62341 | 6.086
2024-12-10 | 0:37 | Data | 0 | 32.548 | 30.374 | 195.495 | 7.64 | 184.051 | 2232.47 | 25.8 | 43.832 | 6.36 | 1.374 | 4.703 | 8576.4 | 2.275 | 98 | 77.4 | 1452 | 21.87 | 5574.7 | 1867.8 | 2307.8 | 2981.2 | 1216.7 | 0.62421 | 6.077
2024-12-10 | 0:37 | Data | 0 | 32.602 | 30.415 | 195.45 | 7.63 | 184.096 | 2233.37 | 25.8 | 43.832 | 6.36 | 1.378 | 4.715 | 8594.49 | 2.086 | 98 | 77.4 | 1452 | 21.87 | 5586.4 | 1865.5 | 2302.4 | 2974.2 | 1216.7 | 0.62455 | 6.093
2024-12-10 | 0:37 | Data | 0 | 32.453 | 30.469 | 195.495 | 7.63 | 184.006 | 2226.14 | 25.81 | 43.741 | 6.36 | 1.378 | 4.693 | 8612.58 | 2.025 | 98 | 77.3 | 1447 | 21.92 | 5598.2 | 1891.9 | 2316.2 | 2999.2 | 1216.7 | 0.62869 | 6.072
2024-12-10 | 0:37 | Data | 0 | 32.379 | 30.408 | 195.495 | 7.64 | 184.006 | 2229.75 | 25.8 | 43.561 | 6.36 | 1.372 | 4.704 | 8608.06 | 2.066 | 98 | 77.4 | 1449 | 21.78 | 5595.2 | 1873.7 | 2321.3 | 2997.7 | 1216.7 | 0.62531 | 6.076
2024-12-10 | 0:37 | Data | 0 | 32.737 | 30.421 | 195.631 | 7.64 | 184.096 | 2230.66 | 25.81 | 43.651 | 6.36 | 1.374 | 4.723 | 8612.58 | 1.978 | 98 | 77.5 | 1451 | 21.83 | 5598.2 | 1880.7 | 2339.2 | 3011.8 | 1216.7 | 0.62172 | 6.097
2024-12-10 | 0:37 | Data | 0 | 32.656 | 30.205 | 195.585 | 7.63 | 184.051 | 2233.37 | 25.81 | 43.2 | 6.36 | 1.365 | 4.721 | 8621.63 | 2.194 | 98.1 | 77.6 | 1452 | 21.6 | 5604.1 | 1884.5 | 2323.1 | 3001.9 | 1216.7 | 0.62569 | 6.086
2024-12-10 | 0:37 | Data | 0 | 32.717 | 30.475 | 195.585 | 7.63 | 184.142 | 2236.08 | 25.8 | 43.561 | 6.36 | 1.373 | 4.725 | 8644.24 | 2.073 | 98.1 | 77.5 | 1453 | 21.78 | 5618.8 | 1886.3 | 2302.1 | 2986.8 | 1216.7 | 0.62922 | 6.098
2024-12-10 | 0:37 | Data | 0 | 32.575 | 30.415 | 195.54 | 7.64 | 184.142 | 2241.5 | 25.81 | 43.561 | 6.36 | 1.374 | 4.702 | 8644.24 | 2.086 | 98.1 | 77.4 | 1457 | 21.78 | 5618.8 | 1885.5 | 2326.4 | 2999.6 | 1216.7 | 0.62571 | 6.075
2024-12-10 | 0:37 | Data | 0 | 32.298 | 30.246 | 195.585 | 7.64 | 184.006 | 2120.39 | 25.81 | 43.561 | 6.36 | 1.367 | 4.718 | 8644.24 | 1.857 | 97.9 | 77.5 | 1378 | 21.74 | 5618.8 | 1878.1 | 2314.1 | 2993.1 | 1216.7 | 0.62651 | 6.084
2024-12-10 | 0:37 | Data | 0 | 32.453 | 30.644 | 195.721 | 7.64 | 184.096 | 2227.95 | 25.81 | 43.741 | 6.36 | 1.369 | 4.711 | 8657.8 | 2.025 | 98 | 77.5 | 1448 | 21.92 | 5627.6 | 1880.2 | 2301.1 | 2981.4 | 1216.7 | 0.62819 | 6.082
2024-12-10 | 0:37 | Data | 0 | 32.919 | 30.489 | 195.631 | 7.64 | 184.232 | 2227.95 | 25.81 | 43.47 | 6.36 | 1.367 | 4.711 | 8662.33 | 2.12 | 98 | 77.5 | 1448 | 21.74 | 5630.5 | 1900.8 | 2310.2 | 3002.7 | 1216.7 | 0.63054 | 6.078
2024-12-10 | 0:37 | Data | 0 | 32.609 | 30.766 | 195.585 | 7.63 | 184.096 | 2227.95 | 25.8 | 43.741 | 6.36 | 1.375 | 4.7 | 8666.85 | 2.113 | 98 | 77.4 | 1448 | 21.92 | 5633.5 | 1868.6 | 2307.6 | 2981.9 | 1216.7 | 0.62377 | 6.074
2024-12-10 | 0:37 | Data | 0 | 32.777 | 30.448 | 195.585 | 7.64 | 184.096 | 2227.95 | 25.8 | 43.832 | 6.36 | 1.362 | 4.681 | 8662.33 | 2.1 | 98 | 77.5 | 1448 | 21.87 | 5630.5 | 1868.6 | 2300.8 | 2962.9 | 1216.7 | 0.62691 | 6.043
2024-12-10 | 0:38 | Data | 0 | 32.494 | 30.273 | 195.54 | 7.64 | 184.051 | 2227.95 | 25.8 | 43.832 | 6.36 | 1.372 | 4.704 | 8666.85 | 1.958 | 98 | 77.4 | 1448 | 21.87 | 5633.5 | 1873.9 | 2288.6 | 2966.9 | 1216.7 | 0.62958 | 6.076
2024-12-10 | 0:38 | Data | 0 | 32.919 | 30.712 | 195.54 | 7.64 | 184.096 | 2229.75 | 25.81 | 43.832 | 6.36 | 1.38 | 4.695 | 8680.41 | 2.174 | 98 | 77.3 | 1450 | 21.92 | 5642.3 | 1878.1 | 2297.9 | 2978.6 | 1216.7 | 0.62836 | 6.074
2024-12-10 | 0:38 | Data | 0 | 32.548 | 30.415 | 195.54 | 7.63 | 184.051 | 2229.75 | 25.81 | 43.832 | 6.36 | 1.369 | 4.711 | 8684.94 | 1.971 | 98 | 77.5 | 1450 | 21.87 | 5645.2 | 1891.7 | 2285.2 | 2976.8 | 1216.7 | 0.63294 | 6.078
2024-12-10 | 0:38 | Data | 0 | 32.69 | 30.469 | 195.495 | 7.64 | 184.096 | 2230.66 | 25.8 | 43.832 | 6.36 | 1.369 | 4.728 | 8721.11 | 2.059 | 98 | 77.5 | 1450 | 21.87 | 5668.7 | 1876.8 | 2340.6 | 3011.6 | 1216.7 | 0.62482 | 6.096
2024-12-10 | 0:38 | Data | 0 | 32.453 | 30.469 | 195.585 | 7.63 | 184.096 | 2230.66 | 25.8 | 43.741 | 6.36 | 1.371 | 4.716 | 8703.03 | 2.241 | 98 | 77.5 | 1450 | 21.87 | 5657 | 1879.6 | 2332.6 | 3008.5 | 1216.7 | 0.62339 | 6.087
2024-12-10 | 0:38 | Data | 0 | 32.946 | 30.543 | 195.676 | 7.64 | 184.142 | 2226.14 | 25.8 | 43.832 | 6.36 | 1.369 | 4.683 | 8707.55 | 2.127 | 98 | 77.4 | 1447 | 21.96 | 5659.9 | 1878.8 | 2332.2 | 3008.7 | 1216.7 | 0.62351 | 6.053
2024-12-10 | 0:38 | Data | 0 | 32.413 | 30.617 | 195.631 | 7.64 | 184.142 | 2236.08 | 25.8 | 43.741 | 6.36 | 1.374 | 4.703 | 8716.59 | 1.951 | 98 | 77.4 | 1453 | 21.92 | 5665.8 | 1883.8 | 2346.1 | 3018.6 | 1216.7 | 0.62168 | 6.078
2024-12-10 | 0:38 | Data | 0 | 32.379 | 30.185 | 195.45 | 7.63 | 184.006 | 2233.37 | 25.81 | 43.832 | 6.36 | 1.374 | 4.712 | 8680.41 | 2.268 | 98 | 77.4 | 1452 | 21.87 | 5642.3 | 1884.7 | 2382.7 | 3049.3 | 1216.7 | 0.61548 | 6.086
2024-12-10 | 0:38 | Data | 0 | 32.588 | 30.502 | 195.631 | 7.63 | 184.096 | 2235.18 | 25.81 | 43.561 | 6.36 | 1.367 | 4.669 | 8662.33 | 2.127 | 98 | 77.4 | 1453 | 21.83 | 5630.5 | 1871.2 | 2354.6 | 3010.8 | 1216.7 | 0.61477 | 6.036
2024-12-10 | 0:38 | Data | 0 | 32.494 | 30.583 | 195.495 | 7.64 | 184.051 | 2236.08 | 25.8 | 43.832 | 6.36 | 1.367 | 4.698 | 8689.46 | 2.025 | 98 | 77.5 | 1453 | 21.87 | 5648.1 | 1886.4 | 2354.3 | 3025.2 | 1216.7 | 0.62125 | 6.065
2024-12-10 | 0:38 | Data | 0 | 32.264 | 30.192 | 195.495 | 7.64 | 184.006 | 2230.66 | 25.8 | 43.832 | 6.36 | 1.376 | 4.731 | 8671.37 | 2.052 | 98 | 77.5 | 1450 | 21.92 | 5636.4 | 1871.4 | 2329.3 | 2997.7 | 1216.7 | 0.62178 | 6.105
2024-12-10 | 0:38 | Data | 0 | 32.818 | 30.334 | 195.495 | 7.64 | 184.142 | 2230.66 | 25.8 | 43.832 | 6.37 | 1.367 | 4.738 | 8716.59 | 2.228 | 98 | 77.6 | 1450 | 21.92 | 5665.8 | 3234.8 | 3123 | 4607.2 | 1216.7 | 0.67368 | 6.105
2024-12-10 | 0:38 | Data | 0 | 32.352 | 30.205 | 195.54 | 7.63 | 184.096 | 2230.66 | 25.8 | 43.832 | 6.36 | 1.378 | 4.725 | 8725.64 | 2.079 | 98 | 77.4 | 1450 | 21.87 | 5671.7 | 2962.6 | 2854.3 | 4230.5 | 1216.7 | 0.68183 | 6.103
2024-12-10 | 0:38 | Data | 0 | 32.669 | 30.529 | 195.676 | 7.64 | 184.006 | 2229.75 | 25.81 | 43.832 | 6.36 | 1.37 | 4.74 | 8721.11 | 2.073 | 98 | 77.6 | 1449 | 21.92 | 5668.7 | 2966.9 | 2871.7 | 4245.8 | 1216.7 | 0.68191 | 6.109
2024-12-10 | 0:38 | Data | 0 | 32.467 | 30.415 | 195.585 | 7.63 | 184.096 | 2229.75 | 25.81 | 43.741 | 6.36 | 1.375 | 4.721 | 8707.55 | 2.086 | 98 | 77.4 | 1450 | 21.87 | 5659.9 | 2972.2 | 2880.2 | 4250.9 | 1216.7 | 0.68153 | 6.098
2024-12-10 | 0:38 | Data | 0 | 32.339 | 30.361 | 195.45 | 7.64 | 184.096 | 2230.66 | 25.8 | 43.832 | 6.36 | 1.387 | 4.707 | 8703.03 | 1.769 | 98 | 77.2 | 1449 | 21.87 | 5657 | 2948.7 | 2883.3 | 4244 | 1216.7 | 0.67848 | 6.095
2024-12-10 | 0:38 | Data | 0 | 32.298 | 30.415 | 195.54 | 7.64 | 183.961 | 2230.66 | 25.81 | 43.832 | 6.36 | 1.373 | 4.709 | 8689.46 | 1.857 | 98 | 77.4 | 1450 | 21.92 | 5648.1 | 2938.8 | 2881.1 | 4228.9 | 1216.7 | 0.67791 | 6.082
2024-12-10 | 0:38 | Data | 0 | 32.609 | 30.374 | 195.45 | 7.64 | 184.051 | 2230.66 | 25.8 | 43.832 | 6.36 | 1.365 | 4.71 | 8689.46 | 2.005 | 98 | 77.5 | 1450 | 21.92 | 5648.1 | 2981 | 2922.3 | 4288 | 1216.8 | 0.67887 | 6.074
2024-12-10 | 0:39 | Data | 0 | 32.278 | 30.192 | 195.585 | 7.64 | 184.051 | 2229.75 | 25.8 | 43.741 | 6.36 | 1.37 | 4.693 | 8689.46 | 2.073 | 98 | 77.4 | 1449 | 21.92 | 5648.1 | 2965.6 | 2914.4 | 4270.7 | 1216.8 | 0.67816 | 6.064
2024-12-10 | 0:39 | Data | 0 | 32.271 | 30.3 | 195.404 | 7.63 | 184.006 | 2230.66 | 25.81 | 44.283 | 6.36 | 1.359 | 4.705 | 8671.37 | 2.079 | 98 | 77.6 | 1450 | 22.1 | 5636.4 | 2958.4 | 2915.2 | 4270.4 | 1216.8 | 0.67558 | 6.064
2024-12-10 | 0:39 | Data | 0 | 32.264 | 30.3 | 195.495 | 7.63 | 183.961 | 2229.75 | 25.8 | 44.012 | 6.36 | 1.36 | 4.712 | 8680.41 | 2.079 | 98 | 77.6 | 1450 | 22.05 | 5642.3 | 2974.1 | 2941.9 | 4293.3 | 1216.8 | 0.67545 | 6.074
2024-12-10 | 0:39 | Data | 0 | 32.467 | 30.401 | 195.585 | 7.63 | 183.916 | 2227.95 | 25.8 | 43.741 | 6.36 | 1.376 | 4.731 | 8693.98 | 2.093 | 98 | 77.5 | 1448 | 21.87 | 5651.1 | 2958.6 | 2912.5 | 4265.1 | 1216.8 | 0.67738 | 6.107
2024-12-10 | 0:39 | Data | 0 | 32.271 | 30.192 | 195.45 | 7.63 | 183.916 | 2217.1 | 25.78 | 43.832 | 6.36 | 1.364 | 4.727 | 8671.37 | 2.066 | 98 | 77.6 | 1441 | 21.96 | 5636.4 | 2956.5 | 2913.4 | 4266.1 | 1216.8 | 0.67545 | 6.091
2024-12-10 | 0:39 | Data | 0 | 32.487 | 30.185 | 195.404 | 7.64 | 183.961 | 2227.95 | 25.78 | 43.832 | 6.36 | 1.364 | 4.711 | 8689.46 | 2.106 | 98 | 77.6 | 1448 | 21.92 | 5648.1 | 2966 | 2898.4 | 4266 | 1216.8 | 0.67714 | 6.075
2024-12-10 | 0:39 | Data | 0 | 32.467 | 30.388 | 195.495 | 7.64 | 183.961 | 2227.95 | 25.78 | 43.741 | 6.36 | 1.377 | 4.697 | 8689.46 | 2.187 | 98 | 77.3 | 1448 | 21.87 | 5648.1 | 2960.4 | 2885.8 | 4245 | 1216.8 | 0.67975 | 6.074
2024-12-10 | 0:39 | Data | 0 | 32.669 | 30.543 | 195.631 | 7.64 | 184.142 | 2227.95 | 25.78 | 43.922 | 6.36 | 1.373 | 4.715 | 8689.46 | 1.978 | 98 | 77.4 | 1448 | 21.96 | 5648.1 | 2951.7 | 2879.5 | 4240.7 | 1216.8 | 0.67866 | 6.088
2024-12-10 | 0:39 | Data | 0 | 32.717 | 30.529 | 195.54 | 7.64 | 184.006 | 2222.52 | 25.78 | 43.741 | 6.36 | 1.375 | 4.714 | 8693.98 | 2.086 | 98 | 77.4 | 1445 | 21.92 | 5651.1 | 2970 | 2889.8 | 4255.8 | 1216.8 | 0.68184 | 6.089
2024-12-10 | 0:39 | Data | 0 | 32.035 | 30.185 | 195.54 | 7.63 | 184.051 | 2218.91 | 25.77 | 43.741 | 6.36 | 1.365 | 4.702 | 8707.55 | 2.019 | 98 | 77.5 | 1443 | 21.92 | 5659.9 | 2969.8 | 2885.6 | 4257.7 | 1216.8 | 0.67988 | 6.066
2024-12-10 | 0:39 | Data | 0 | 32.379 | 30.198 | 195.45 | 7.64 | 184.006 | 2218.91 | 25.78 | 43.741 | 6.35 | 1.36 | 4.703 | 8703.03 | 2.066 | 98 | 77.6 | 1443 | 21.87 | 5657 | 2939.5 | 2891.8 | 4242.6 | 1216.8 | 0.67499 | 6.063
2024-12-10 | 0:39 | Data | 0 | 32.271 | 30.361 | 195.404 | 7.63 | 184.051 | 2218.91 | 25.78 | 43.741 | 6.36 | 1.362 | 4.673 | 8703.03 | 2.019 | 98 | 77.4 | 1442 | 21.92 | 5657 | 2956.5 | 2873.3 | 4234.3 | 1216.8 | 0.6812 | 6.036
2024-12-10 | 0:39 | Data | 0 | 32.541 | 30.185 | 195.631 | 7.63 | 184.051 | 2213.49 | 25.78 | 43.832 | 6.37 | 1.359 | 4.71 | 8730.16 | 1.904 | 98 | 77.6 | 1439 | 21.92 | 5674.6 | 2953.9 | 2898.3 | 4253.2 | 1216.8 | 0.67653 | 6.069
2024-12-10 | 0:39 | Data | 0 | 32.264 | 30.367 | 195.54 | 7.63 | 184.006 | 2225.23 | 25.78 | 43.741 | 6.36 | 1.371 | 4.711 | 8707.55 | 2.167 | 98 | 77.4 | 1446 | 21.87 | 5659.9 | 2980.6 | 2917.1 | 4282.1 | 1216.8 | 0.67889 | 6.083
2024-12-10 | 0:39 | Data | 0 | 32.548 | 30.327 | 195.54 | 7.63 | 184.096 | 2222.52 | 25.77 | 43.832 | 6.36 | 1.374 | 4.725 | 8703.03 | 2.039 | 98 | 77.5 | 1445 | 21.92 | 5657 | 2972.2 | 2872.8 | 4246.8 | 1216.8 | 0.68339 | 6.099
2024-12-10 | 0:39 | Data | 0 | 32.474 | 30.745 | 195.54 | 7.64 | 184.096 | 2222.52 | 25.8 | 43.741 | 6.36 | 1.371 | 4.71 | 8703.03 | 1.971 | 98 | 77.5 | 1445 | 21.92 | 5657 | 2961.9 | 2904.3 | 4260.2 | 1216.8 | 0.67625 | 6.082
2024-12-10 | 0:39 | Data | 0 | 32.71 | 30.415 | 195.585 | 7.64 | 184.096 | 2222.52 | 25.8 | 43.741 | 6.36 | 1.363 | 4.721 | 8703.03 | 2.1 | 98 | 77.6 | 1444 | 21.92 | 5657 | 2950 | 2924.5 | 4270.2 | 1216.8 | 0.67398 | 6.083
2024-12-10 | 0:40 | Data | 0 | 32.521 | 30.198 | 195.631 | 7.63 | 184.142 | 2225.23 | 25.79 | 43.832 | 6.36 | 1.374 | 4.677 | 8712.07 | 2.079 | 98 | 77.3 | 1446 | 21.87 | 5662.8 | 2944 | 2908.8 | 4259.1 | 1216.8 | 0.6718 | 6.051
2024-12-10 | 0:40 | Data | 0 | 32.109 | 30.185 | 195.404 | 7.64 | 184.006 | 2225.23 | 25.8 | 43.832 | 6.36 | 1.363 | 4.683 | 8716.59 | 1.965 | 98 | 77.5 | 1446 | 21.92 | 5665.8 | 2963 | 2870 | 4241.3 | 1216.8 | 0.68156 | 6.045
2024-12-10 | 0:40 | Data | 0 | 32.44 | 30.617 | 195.495 | 7.63 | 183.961 | 2225.23 | 25.8 | 43.832 | 6.36 | 1.373 | 4.686 | 8716.59 | 2.039 | 98 | 77.3 | 1446 | 21.92 | 5665.8 | 2989.4 | 2900.5 | 4271.4 | 1216.8 | 0.68312 | 6.059
2024-12-10 | 0:40 | Data | 0 | 32.406 | 30.394 | 195.495 | 7.63 | 184.096 | 2225.23 | 25.79 | 43.741 | 6.36 | 1.373 | 4.7 | 8721.11 | 1.769 | 98 | 77.4 | 1446 | 21.92 | 5668.7 | 2942.6 | 2886.4 | 4242.9 | 1216.8 | 0.67626 | 6.073
2024-12-10 | 0:40 | Data | 0 | 32.406 | 30.307 | 195.54 | 7.63 | 184.051 | 2223.43 | 25.79 | 41.755 | 6.36 | 1.374 | 4.711 | 8712.07 | 2.079 | 98.1 | 77.4 | 1445 | 20.88 | 5662.8 | 2977.1 | 2911.9 | 4271.1 | 1216.8 | 0.68032 | 6.084
2024-12-10 | 0:40 | Data | 0 | 32.271 | 30.577 | 195.585 | 7.64 | 184.096 | 2222.52 | 25.8 | 43.109 | 6.36 | 1.367 | 4.694 | 8693.98 | 2.025 | 98.1 | 77.4 | 1445 | 21.55 | 5651.1 | 2930.3 | 2907.9 | 4246.1 | 1216.8 | 0.67266 | 6.062
2024-12-10 | 0:40 | Data | 0 | 32.44 | 30.644 | 195.631 | 7.64 | 184.096 | 2223.43 | 25.8 | 43.109 | 6.37 | 1.38 | 4.716 | 8689.46 | 2.025 | 98.1 | 77.3 | 1445 | 21.55 | 5648.1 | 2980.9 | 2903.3 | 4277 | 1216.8 | 0.67947 | 6.097
2024-12-10 | 0:40 | Data | 0 | 32.379 | 30.415 | 195.45 | 7.64 | 184.051 | 2220.72 | 25.8 | 43.2 | 6.36 | 1.374 | 4.698 | 8693.98 | 2.059 | 98.1 | 77.4 | 1443 | 21.6 | 5651.1 | 2940.1 | 2895.3 | 4241.5 | 1216.8 | 0.67643 | 6.073
2024-12-10 | 0:40 | Data | 0 | 32.069 | 30.388 | 195.404 | 7.64 | 184.006 | 2226.14 | 25.8 | 43.29 | 6.36 | 1.371 | 4.673 | 8680.41 | 1.877 | 98.1 | 77.3 | 1446 | 21.64 | 5642.3 | 2984.8 | 2883.4 | 4262.4 | 1216.8 | 0.68355 | 6.046
2024-12-10 | 0:40 | Data | 0 | 32.48 | 30.212 | 195.45 | 7.63 | 183.961 | 2224.33 | 25.79 | 43.832 | 6.36 | 1.371 | 4.663 | 8662.33 | 2.079 | 98 | 77.3 | 1446 | 21.92 | 5630.5 | 2967.6 | 2874.7 | 4246.9 | 1216.8 | 0.68097 | 6.033
2024-12-10 | 0:40 | Data | 0 | 32.487 | 30.401 | 195.54 | 7.64 | 184.051 | 2225.23 | 25.8 | 43.832 | 6.36 | 1.373 | 4.683 | 8680.41 | 2.093 | 98 | 77.3 | 1446 | 21.92 | 5642.3 | 2950.5 | 2912.6 | 4258.3 | 1216.8 | 0.67676 | 6.055
2024-12-10 | 0:40 | Data | 0 | 32.487 | 30.408 | 195.45 | 7.64 | 184.006 | 2225.23 | 25.79 | 43.741 | 6.36 | 1.372 | 4.711 | 8689.46 | 2.086 | 98 | 77.4 | 1446 | 21.87 | 5648.1 | 2954.6 | 2886.9 | 4240.3 | 1216.8 | 0.68025 | 6.083
2024-12-10 | 0:40 | Data | 0 | 32.642 | 30.313 | 195.54 | 7.64 | 184.187 | 2222.52 | 25.8 | 43.832 | 6.36 | 1.374 | 4.721 | 8689.46 | 2.025 | 98 | 77.5 | 1445 | 21.92 | 5648.1 | 2974.1 | 2891.8 | 4259 | 1216.8 | 0.68139 | 6.095
2024-12-10 | 0:40 | Data | 0 | 32.919 | 30.543 | 195.676 | 7.64 | 184.187 | 2225.23 | 25.79 | 43.561 | 6.36 | 1.376 | 4.711 | 8703.03 | 2.093 | 98.1 | 77.4 | 1446 | 21.55 | 5657 | 2940.2 | 2913.1 | 4254.9 | 1216.8 | 0.67365 | 6.086
2024-12-10 | 0:40 | Data | 0 | 32.494 | 30.361 | 195.54 | 7.64 | 184.096 | 2226.14 | 25.8 | 41.575 | 6.36 | 1.369 | 4.702 | 8707.55 | 2.187 | 98.1 | 77.4 | 1447 | 20.97 | 5659.9 | 2957.7 | 2923.5 | 4270.1 | 1216.8 | 0.67681 | 6.072
2024-12-10 | 0:40 | Data | 0 | 32.325 | 30.192 | 195.404 | 7.63 | 184.006 | 2225.23 | 25.8 | 43.741 | 6.36 | 1.37 | 4.699 | 8693.98 | 2.086 | 98 | 77.4 | 1447 | 21.92 | 5651.1 | 2966.8 | 2904.8 | 4266.3 | 1216.8 | 0.67853 | 6.069
2024-12-10 | 0:40 | Data | 0 | 32.494 | 30.415 | 195.495 | 7.63 | 184.142 | 2226.14 | 25.8 | 43.741 | 6.36 | 1.369 | 4.717 | 8680.41 | 1.965 | 98 | 77.5 | 1446 | 21.87 | 5642.3 | 2956.4 | 2931.8 | 4279.3 | 1216.8 | 0.67273 | 6.085
2024-12-10 | 0:40 | Data | 0 | 32.264 | 30.361 | 195.404 | 7.64 | 184.051 | 2225.23 | 25.8 | 43.832 | 6.36 | 1.381 | 4.709 | 8680.41 | 2.079 | 98 | 77.3 | 1446 | 21.92 | 5642.3 | 2963.1 | 2926 | 4278 | 1216.8 | 0.67573 | 6.09
2024-12-10 | 0:41 | Data | 0 | 32.278 | 30.367 | 195.495 | 7.63 | 184.006 | 2227.04 | 25.8 | 43.741 | 6.36 | 1.374 | 4.726 | 8689.46 | 2.167 | 98 | 77.5 | 1448 | 21.92 | 5648.1 | 2984.6 | 2912.6 | 4281.5 | 1216.9 | 0.67983 | 6.099
2024-12-10 | 0:41 | Data | 0 | 32.278 | 30.388 | 195.404 | 7.63 | 183.961 | 2227.95 | 25.8 | 43.741 | 6.36 | 1.369 | 4.726 | 8680.41 | 1.958 | 98 | 77.5 | 1448 | 21.87 | 5642.3 | 2947.6 | 2907 | 4253.5 | 1216.9 | 0.67467 | 6.094
2024-12-10 | 0:41 | Data | 0 | 32.831 | 30.489 | 195.676 | 7.63 | 184.142 | 2222.52 | 25.8 | 43.741 | 6.36 | 1.378 | 4.733 | 8693.98 | 2.079 | 98 | 77.4 | 1445 | 21.92 | 5651.1 | 2953.5 | 2917.6 | 4264.6 | 1216.9 | 0.6751 | 6.111
2024-12-10 | 0:41 | Data | 0 | 32.42 | 30.536 | 195.631 | 7.64 | 184.187 | 2216.2 | 25.79 | 43.832 | 6.36 | 1.37 | 4.698 | 8684.94 | 1.863 | 98 | 77.4 | 1441 | 21.96 | 5645.2 | 2973.9 | 2915.2 | 4274.1 | 1216.9 | 0.67947 | 6.067
2024-12-10 | 0:41 | Data | 0 | 32.379 | 30.185 | 195.495 | 7.64 | 184.006 | 2217.1 | 25.8 | 43.832 | 6.37 | 1.363 | 4.702 | 8703.03 | 2.093 | 98 | 77.5 | 1441 | 21.92 | 5657 | 2958.7 | 2891.5 | 4252.3 | 1216.9 | 0.67728 | 6.064
2024-12-10 | 0:41 | Data | 0 | 32.507 | 30.415 | 195.585 | 7.64 | 184.142 | 2218 | 25.79 | 43.741 | 6.36 | 1.367 | 4.711 | 8693.98 | 1.965 | 98 | 77.5 | 1441 | 21.87 | 5651.1 | 2939.7 | 2873.8 | 4224.4 | 1216.9 | 0.67649 | 6.076
2024-12-10 | 0:41 | Data | 0 | 32.285 | 30.388 | 195.45 | 7.63 | 184.006 | 2218 | 25.81 | 43.832 | 6.36 | 1.372 | 4.705 | 8680.41 | 2.106 | 98 | 77.4 | 1442 | 21.87 | 5642.3 | 2972.7 | 2883.2 | 4257.7 | 1216.9 | 0.67874 | 6.077
2024-12-10 | 0:41 | Data | 0 | 32.696 | 30.651 | 195.721 | 7.64 | 184.051 | 2218.91 | 25.81 | 43.741 | 6.36 | 1.374 | 4.705 | 8689.46 | 2.066 | 98 | 77.4 | 1442 | 21.92 | 5648.1 | 2957.5 | 2889.4 | 4248.6 | 1216.9 | 0.67971 | 6.079
2024-12-10 | 0:41 | Data | 0 | 32.521 | 30.415 | 195.585 | 7.64 | 184.096 | 2218.91 | 25.8 | 43.561 | 6.37 | 1.379 | 4.697 | 8716.59 | 2.086 | 98 | 77.3 | 1442 | 21.83 | 5665.8 | 2989 | 2885.1 | 4263.1 | 1216.9 | 0.68489 | 6.076
2024-12-10 | 0:41 | Data | 0 | 32.494 | 30.205 | 195.54 | 7.64 | 184.142 | 2218.91 | 25.8 | 43.832 | 6.36 | 1.381 | 4.704 | 8693.98 | 2.127 | 98 | 77.3 | 1442 | 21.87 | 5651.1 | 2978.7 | 2921.8 | 4279.5 | 1216.9 | 0.67816 | 6.085
2024-12-10 | 0:41 | Data | 0 | 32.285 | 30.408 | 195.54 | 7.64 | 184.096 | 2218.91 | 25.8 | 43.832 | 6.36 | 1.372 | 4.716 | 8721.11 | 2.039 | 98 | 77.5 | 1442 | 21.87 | 5668.7 | 2943.1 | 2917.4 | 4259.2 | 1216.9 | 0.67274 | 6.088
2024-12-10 | 0:41 | Data | 0 | 32.514 | 30.415 | 195.585 | 7.64 | 184.187 | 2216.2 | 25.81 | 43.832 | 6.36 | 1.372 | 4.71 | 8770.86 | 2.086 | 98 | 77.4 | 1441 | 21.92 | 5701.1 | 2955 | 2935.8 | 4279.9 | 1216.9 | 0.67266 | 6.081
2024-12-10 | 0:41 | Data | 0 | 32.494 | 30.624 | 195.585 | 7.63 | 184.142 | 2216.2 | 25.8 | 43.832 | 6.36 | 1.373 | 4.721 | 8788.95 | 1.904 | 98 | 77.5 | 1441 | 21.87 | 5712.8 | 2968 | 2919.8 | 4271.2 | 1216.9 | 0.67831 | 6.094
2024-12-10 | 0:41 | Data | 0 | 32.494 | 30.361 | 195.404 | 7.64 | 184.006 | 2216.2 | 25.79 | 43.741 | 6.36 | 1.367 | 4.726 | 8761.81 | 2.1 | 98 | 77.6 | 1441 | 21.87 | 5695.2 | 2952.6 | 2925.3 | 4269.4 | 1216.9 | 0.67407 | 6.092
2024-12-10 | 0:41 | Data | 0 | 32.271 | 30.286 | 195.585 | 7.64 | 184.096 | 2214.39 | 25.8 | 43.832 | 6.36 | 1.381 | 4.709 | 8775.38 | 2.019 | 98 | 77.3 | 1439 | 21.92 | 5704 | 2954.1 | 2905.3 | 4261.8 | 1216.9 | 0.6774 | 6.09
2024-12-10 | 0:41 | Data | 0 | 32.609 | 30.259 | 195.631 | 7.63 | 184.142 | 2218.91 | 25.8 | 43.741 | 6.36 | 1.371 | 4.698 | 8748.25 | 2.262 | 98 | 77.4 | 1442 | 21.87 | 5686.4 | 2968.4 | 2913 | 4272.1 | 1216.9 | 0.67734 | 6.069
2024-12-10 | 0:41 | Data | 0 | 32.94 | 30.259 | 195.631 | 7.64 | 184.096 | 2222.52 | 25.8 | 43.832 | 6.36 | 1.364 | 4.695 | 8743.73 | 2.241 | 98 | 77.5 | 1445 | 21.92 | 5683.4 | 2978.2 | 2910.4 | 4277.5 | 1216.9 | 0.67921 | 6.059
2024-12-10 | 0:42 | Data | 0 | 32.663 | 30.523 | 195.585 | 7.64 | 184.006 | 2218.91 | 25.8 | 43.741 | 6.36 | 1.378 | 4.701 | 8743.73 | 2.079 | 98 | 77.3 | 1442 | 21.87 | 5683.4 | 2950.9 | 2917.8 | 4264.8 | 1216.9 | 0.67405 | 6.078
2024-12-10 | 0:42 | Data | 0 | 32.487 | 30.415 | 195.631 | 7.64 | 183.961 | 2216.2 | 25.8 | 43.832 | 6.36 | 1.381 | 4.73 | 8743.73 | 2.079 | 98 | 77.4 | 1441 | 21.87 | 5683.4 | 2957.9 | 2892.9 | 4252 | 1216.9 | 0.67751 | 6.11
2024-12-10 | 0:42 | Data | 0 | 32.494 | 30.624 | 195.54 | 7.64 | 184.096 | 2218.91 | 25.81 | 43.832 | 6.36 | 1.381 | 4.722 | 8734.68 | 2.106 | 98 | 77.4 | 1442 | 21.87 | 5677.5 | 2972.8 | 2901.5 | 4279.7 | 1216.9 | 0.68237 | 6.103
2024-12-10 | 0:42 | Data | 0 | 32.649 | 30.644 | 195.585 | 7.64 | 184.051 | 2218.91 | 25.8 | 43.741 | 6.36 | 1.381 | 4.674 | 8748.25 | 2.1 | 98 | 77.2 | 1442 | 21.92 | 5686.4 | 2963.7 | 2907.6 | 4260.1 | 1216.9 | 0.67809 | 6.055
2024-12-10 | 0:42 | Data | 0 | 32.879 | 30.448 | 195.585 | 7.63 | 184.051 | 2218.91 | 25.81 | 43.832 | 6.36 | 1.388 | 4.702 | 8748.25 | 2.262 | 98 | 77.2 | 1442 | 21.92 | 5686.4 | 2968.9 | 2887.5 | 4258.6 | 1216.9 | 0.68012 | 6.091
2024-12-10 | 0:42 | Data | 0 | 32.177 | 30.3 | 195.45 | 7.63 | 184.051 | 2218.91 | 25.8 | 43.741 | 6.36 | 1.383 | 4.719 | 8743.73 | 2.066 | 98 | 77.3 | 1442 | 21.87 | 5683.4 | 2972 | 2892.4 | 4261.1 | 1216.9 | 0.67964 | 6.101
2024-12-10 | 0:42 | Data | 0 | 32.339 | 30.3 | 195.631 | 7.63 | 184.051 | 2220.72 | 25.81 | 43.832 | 6.37 | 1.386 | 4.717 | 8761.81 | 2.086 | 98 | 77.3 | 1443 | 21.92 | 5695.2 | 2962.1 | 2905.2 | 4264.9 | 1216.9 | 0.67808 | 6.103
2024-12-10 | 0:42 | Data | 0 | 32.224 | 30.286 | 195.585 | 7.64 | 184.051 | 2218.91 | 25.81 | 43.741 | 6.36 | 1.382 | 4.704 | 8757.29 | 2.086 | 98 | 77.3 | 1442 | 21.92 | 5692.2 | 2958.9 | 2917.1 | 4266 | 1216.9 | 0.67616 | 6.086
2024-12-10 | 0:42 | Data | 0 | 32.831 | 30.475 | 195.766 | 7.64 | 184.187 | 2218.91 | 25.79 | 43.741 | 6.36 | 1.367 | 4.69 | 8730.16 | 2.1 | 98 | 77.4 | 1442 | 21.87 | 5674.6 | 2969.5 | 2884 | 4250.2 | 1216.9 | 0.68125 | 6.057
2024-12-10 | 0:42 | Data | 0 | 32.467 | 30.86 | 195.585 | 7.64 | 184.051 | 2222.52 | 25.8 | 43.741 | 6.36 | 1.371 | 4.72 | 8748.25 | 1.998 | 98 | 77.5 | 1445 | 21.92 | 5686.4 | 2957.2 | 2931 | 4279.3 | 1216.9 | 0.67593 | 6.09
2024-12-10 | 0:42 | Data | 0 | 32.48 | 30.617 | 195.45 | 7.64 | 183.961 | 2225.23 | 25.81 | 43.651 | 6.37 | 1.367 | 4.697 | 8743.73 | 2.086 | 98 | 77.5 | 1446 | 21.83 | 5683.4 | 2963.9 | 2921.7 | 4268.4 | 1216.9 | 0.67741 | 6.064
2024-12-10 | 0:42 | Data | 0 | 32.359 | 30.361 | 195.495 | 7.63 | 184.142 | 2225.23 | 25.81 | 43.832 | 6.36 | 1.369 | 4.708 | 8775.38 | 1.971 | 98 | 77.5 | 1446 | 21.92 | 5704 | 2965.6 | 2934.7 | 4286.4 | 1216.9 | 0.67513 | 6.076
2024-12-10 | 0:42 | Data | 0 | 32.447 | 30.637 | 195.631 | 7.63 | 184.096 | 2225.23 | 25.8 | 43.832 | 6.36 | 1.381 | 4.695 | 8761.81 | 2.255 | 98 | 77.3 | 1446 | 21.92 | 5695.2 | 2957.7 | 2948.4 | 4288.8 | 1216.9 | 0.67016 | 6.075
2024-12-10 | 0:42 | Data | 0 | 32.46 | 30.408 | 195.54 | 7.63 | 183.961 | 2222.52 | 25.8 | 43.832 | 6.36 | 1.375 | 4.683 | 8761.81 | 2.086 | 98 | 77.3 | 1445 | 21.92 | 5695.2 | 2942.3 | 2931.5 | 4270.2 | 1216.9 | 0.6712 | 6.057
2024-12-10 | 0:42 | Data | 0 | 32.494 | 30.631 | 195.585 | 7.64 | 184.187 | 2225.23 | 25.8 | 43.741 | 6.36 | 1.377 | 4.725 | 8757.29 | 1.884 | 98 | 77.4 | 1446 | 21.92 | 5692.2 | 2972.7 | 2922.2 | 4278.3 | 1216.9 | 0.67615 | 6.102
2024-12-10 | 0:42 | Data | 0 | 32.609 | 30.415 | 195.585 | 7.63 | 184.142 | 2222.52 | 25.81 | 43.741 | 6.37 | 1.381 | 4.721 | 8730.16 | 1.971 | 98 | 77.4 | 1445 | 21.87 | 5674.6 | 2964.5 | 2902.5 | 4258.1 | 1216.9 | 0.67463 | 6.102
2024-12-10 | 0:42 | Data | 0 | 32.494 | 30.415 | 195.404 | 7.64 | 184.096 | 2222.52 | 25.8 | 43.741 | 6.37 | 1.378 | 4.702 | 8730.16 | 2.079 | 98 | 77.3 | 1444 | 21.92 | 5674.6 | 2959.2 | 2905.7 | 4269.1 | 1216.9 | 0.67588 | 6.079
2024-12-10 | 0:42 | Data | 0 | 32.332 | 30.415 | 195.631 | 7.64 | 184.096 | 2227.04 | 25.81 | 43.741 | 6.37 | 1.371 | 4.686 | 8739.2 | 1.87 | 98 | 77.4 | 1448 | 21.87 | 5680.5 | 2961.4 | 2867.6 | 4233.9 | 1216.9 | 0.68233 | 6.057
2024-12-10 | 0:43 | Data | 0 | 32.332 | 30.388 | 195.495 | 7.64 | 184.096 | 2224.33 | 25.8 | 43.832 | 6.36 | 1.366 | 4.675 | 8739.2 | 1.911 | 98 | 77.4 | 1446 | 21.92 | 5680.5 | 2966.9 | 2898.2 | 4255.8 | 1216.9 | 0.68174 | 6.041
2024-12-10 | 0:43 | Data | 0 | 32.379 | 30.367 | 195.585 | 7.64 | 184.006 | 2227.04 | 25.8 | 43.741 | 6.36 | 1.377 | 4.679 | 8693.98 | 2.106 | 98 | 77.3 | 1448 | 21.92 | 5651.1 | 2944.2 | 2919.5 | 4259.6 | 1217 | 0.67326 | 6.055
2024-12-10 | 0:43 | Data | 0 | 32.919 | 30.496 | 195.585 | 7.63 | 184.187 | 2229.75 | 25.8 | 43.741 | 6.36 | 1.371 | 4.704 | 8684.94 | 2.248 | 98 | 77.4 | 1450 | 21.92 | 5645.2 | 2966 | 2919.6 | 4272.9 | 1217 | 0.67697 | 6.074
2024-12-10 | 0:43 | Data | 0 | 32.548 | 30.752 | 195.585 | 7.63 | 184.187 | 2230.66 | 25.8 | 43.741 | 6.36 | 1.369 | 4.698 | 8689.46 | 2.019 | 98 | 77.5 | 1449 | 21.92 | 5648.1 | 2939.6 | 2945.6 | 4277.1 | 1217 | 0.67338 | 6.065
2024-12-10 | 0:43 | Data | 0 | 32.494 | 30.739 | 195.585 | 7.64 | 184.096 | 2226.14 | 25.8 | 43.741 | 6.37 | 1.364 | 4.702 | 8689.46 | 2.275 | 98 | 77.5 | 1447 | 21.92 | 5648.1 | 2971.3 | 2932.9 | 4285.2 | 1217 | 0.6754 | 6.065
2024-12-10 | 0:43 | Data | 0 | 32.831 | 30.475 | 195.631 | 7.64 | 184.096 | 2224.33 | 25.8 | 43.741 | 6.36 | 1.378 | 4.69 | 8757.29 | 2.012 | 98 | 77.3 | 1445 | 21.87 | 5692.2 | 2956.5 | 2964.7 | 4298.5 | 1217 | 0.67004 | 6.068
2024-12-10 | 0:43 | Data | 0 | 32.663 | 30.475 | 195.631 | 7.63 | 184.142 | 2221.62 | 25.81 | 43.832 | 6.36 | 1.376 | 4.719 | 8734.68 | 2.073 | 98 | 77.4 | 1445 | 21.87 | 5677.5 | 2954.7 | 2955.1 | 4288.6 | 1217 | 0.67108 | 6.093
2024-12-10 | 0:43 | Data | 0 | 32.494 | 30.3 | 195.54 | 7.64 | 184.096 | 2224.33 | 25.8 | 43.832 | 6.36 | 1.372 | 4.706 | 8734.68 | 2.079 | 98 | 77.4 | 1446 | 21.92 | 5677.5 | 2957.9 | 2938.5 | 4284.6 | 1217 | 0.67248 | 6.078
2024-12-10 | 0:43 | Data | 0 | 32.487 | 30.637 | 195.45 | 7.64 | 184.006 | 2224.33 | 25.8 | 43.832 | 6.36 | 1.376 | 4.686 | 8721.11 | 1.992 | 98 | 77.3 | 1446 | 21.92 | 5668.7 | 2960.6 | 2902.6 | 4261.4 | 1217 | 0.6771 | 6.061
2024-12-10 | 0:43 | Data | 0 | 32.595 | 30.651 | 195.585 | 7.64 | 184.096 | 2227.04 | 25.81 | 43.741 | 6.36 | 1.373 | 4.683 | 8716.59 | 2.268 | 98 | 77.3 | 1448 | 21.92 | 5665.8 | 2957.7 | 2866.8 | 4232.8 | 1217 | 0.68113 | 6.055
2024-12-10 | 0:43 | Data | 0 | 32.507 | 30.664 | 195.585 | 7.64 | 184.096 | 2225.23 | 25.8 | 43.741 | 6.36 | 1.367 | 4.707 | 8707.55 | 1.789 | 98 | 77.5 | 1446 | 21.87 | 5659.9 | 2945.6 | 2899.1 | 4248.7 | 1217 | 0.67564 | 6.074
2024-12-10 | 0:43 | Data | 0 | 32.494 | 30.313 | 195.585 | 7.64 | 184.187 | 2225.23 | 25.8 | 43.741 | 6.36 | 1.37 | 4.707 | 8707.55 | 2.187 | 98 | 77.5 | 1446 | 21.87 | 5659.9 | 2969.8 | 2931.6 | 4287.2 | 1217 | 0.67471 | 6.076
2024-12-10 | 0:43 | Data | 0 | 32.676 | 30.259 | 195.721 | 7.64 | 184.142 | 2226.14 | 25.81 | 43.832 | 6.36 | 1.377 | 4.717 | 8703.03 | 2.086 | 98 | 77.4 | 1446 | 21.87 | 5657 | 2958.2 | 2938.9 | 4284.7 | 1217 | 0.67287 | 6.093
2024-12-10 | 0:43 | Data | 0 | 32.696 | 30.421 | 195.54 | 7.64 | 184.096 | 2225.23 | 25.8 | 43.832 | 6.36 | 1.377 | 4.735 | 8703.03 | 1.769 | 98 | 77.5 | 1447 | 21.92 | 5657 | 2967.4 | 2937.4 | 4291.2 | 1217 | 0.67325 | 6.111
2024-12-10 | 0:43 | Data | 0 | 32.723 | 30.435 | 195.631 | 7.64 | 184.232 | 2227.95 | 25.81 | 43.741 | 6.36 | 1.373 | 4.722 | 8689.46 | 2.235 | 98 | 77.5 | 1448 | 21.87 | 5648.1 | 2963.9 | 2928.8 | 4279.1 | 1217 | 0.67566 | 6.096
2024-12-10 | 0:43 | Data | 0 | 32.487 | 30.408 | 195.495 | 7.63 | 184.006 | 2227.95 | 25.8 | 43.832 | 6.36 | 1.369 | 4.694 | 8693.98 | 2.106 | 98 | 77.4 | 1448 | 21.92 | 5651.1 | 2945.4 | 2925.3 | 4267 | 1217 | 0.67316 | 6.064
2024-12-10 | 0:44 | Data | 0 | 32.494 | 30.624 | 195.54 | 7.63 | 184.051 | 2218.91 | 25.8 | 43.741 | 6.36 | 1.37 | 4.703 | 8648.76 | 2.019 | 98 | 77.4 | 1442 | 21.92 | 5621.7 | 2947.5 | 2945.5 | 4283.7 | 1217 | 0.67119 | 6.074
2024-12-10 | 0:44 | Data | 0 | 32.723 | 30.421 | 195.585 | 7.63 | 184.096 | 2225.23 | 25.8 | 43.741 | 6.36 | 1.377 | 4.714 | 8644.24 | 2.181 | 98 | 77.4 | 1446 | 21.92 | 5618.8 | 2978.3 | 2898.1 | 4266.1 | 1217 | 0.68088 | 6.091
2024-12-10 | 0:44 | Data | 0 | 32.521 | 30.246 | 195.495 | 7.64 | 184.006 | 2222.52 | 25.8 | 43.832 | 6.37 | 1.369 | 4.688 | 8648.76 | 2.187 | 98 | 77.4 | 1445 | 21.87 | 5621.7 | 2959.5 | 2863.9 | 4231.6 | 1217 | 0.68073 | 6.057
2024-12-10 | 0:44 | Data | 0 | 32.494 | 30.637 | 195.585 | 7.64 | 184.142 | 2222.52 | 25.8 | 43.832 | 6.36 | 1.371 | 4.71 | 8648.76 | 2.106 | 98 | 77.5 | 1444 | 21.92 | 5621.7 | 2952.3 | 2884.8 | 4242.8 | 1217 | 0.67866 | 6.082
2024-12-10 | 0:44 | Data | 0 | 32.501 | 30.637 | 195.721 | 7.64 | 184.142 | 2220.72 | 25.8 | 43.832 | 6.36 | 1.372 | 4.725 | 8671.37 | 1.904 | 98 | 77.5 | 1442 | 21.87 | 5636.4 | 2969.8 | 2886.8 | 4253 | 1217 | 0.68206 | 6.097
2024-12-10 | 0:44 | Data | 0 | 32.669 | 30.705 | 195.631 | 7.64 | 184.142 | 2214.39 | 25.8 | 43.741 | 6.36 | 1.384 | 4.73 | 8648.76 | 2.059 | 98 | 77.4 | 1439 | 21.87 | 5621.7 | 2961.5 | 2870.6 | 4239.4 | 1217 | 0.68147 | 6.114
2024-12-10 | 0:44 | Data | 0 | 32.609 | 30.624 | 195.676 | 7.63 | 184.142 | 2218.91 | 25.81 | 43.832 | 6.36 | 1.377 | 4.744 | 8648.76 | 1.971 | 98 | 77.5 | 1442 | 21.87 | 5621.7 | 2949.9 | 2905.4 | 4253 | 1217 | 0.67576 | 6.121
2024-12-10 | 0:44 | Data | 0 | 32.447 | 30.752 | 195.631 | 7.64 | 184.142 | 2216.2 | 25.81 | 44.373 | 6.36 | 1.373 | 4.72 | 8644.24 | 2.032 | 98 | 77.5 | 1441 | 22.23 | 5618.8 | 2955.4 | 2922.2 | 4269.6 | 1217 | 0.67414 | 6.092
2024-12-10 | 0:44 | Data | 0 | 32.548 | 30.421 | 195.631 | 7.64 | 184.051 | 2222.52 | 25.81 | 43.741 | 6.36 | 1.381 | 4.695 | 8693.98 | 1.992 | 98 | 77.3 | 1444 | 21.92 | 5651.1 | 2945.4 | 2970 | 4296.3 | 1217 | 0.66706 | 6.076
2024-12-10 | 0:44 | Data | 0 | 32.723 | 30.651 | 195.631 | 7.64 | 184.187 | 2222.52 | 25.8 | 43.741 | 6.36 | 1.386 | 4.686 | 8671.37 | 2.073 | 98 | 77.2 | 1445 | 21.87 | 5636.4 | 2974.5 | 2932.8 | 4288.4 | 1217 | 0.6763 | 6.073
2024-12-10 | 0:44 | Data | 0 | 32.494 | 30.415 | 195.585 | 7.63 | 184.096 | 2223.43 | 25.81 | 43.741 | 6.36 | 1.384 | 4.719 | 8707.55 | 1.877 | 98 | 77.3 | 1445 | 21.92 | 5659.9 | 2957.8 | 2945.7 | 4285.8 | 1217 | 0.67317 | 6.102
2024-12-10 | 0:44 | Data | 0 | 32.582 | 30.34 | 195.585 | 7.63 | 184.187 | 2225.23 | 25.8 | 43.832 | 6.36 | 1.383 | 4.718 | 8689.46 | 2.073 | 98 | 77.3 | 1446 | 21.87 | 5648.1 | 2968.6 | 2904.4 | 4257.6 | 1217 | 0.67814 | 6.1
2024-12-10 | 0:44 | Data | 0 | 32.501 | 30.421 | 195.54 | 7.64 | 184.232 | 2218.91 | 25.81 | 43.741 | 6.36 | 1.365 | 4.692 | 8680.41 | 2.052 | 98 | 77.5 | 1442 | 21.92 | 5642.3 | 2968.2 | 2892 | 4258.3 | 1217 | 0.67986 | 6.057
2024-12-10 | 0:44 | Data | 0 | 32.521 | 30.415 | 195.54 | 7.63 | 184.096 | 2225.23 | 25.8 | 43.832 | 6.37 | 1.357 | 4.704 | 8703.03 | 1.965 | 98 | 77.6 | 1446 | 21.92 | 5657 | 2955.1 | 2866 | 4231.7 | 1217 | 0.681 | 6.062
2024-12-10 | 0:44 | Data | 0 | 32.723 | 30.428 | 195.721 | 7.64 | 184.142 | 2222.52 | 25.8 | 43.561 | 6.36 | 1.362 | 4.702 | 8689.46 | 1.985 | 98 | 77.5 | 1445 | 21.78 | 5648.1 | 2966.3 | 2873.7 | 4246.4 | 1217 | 0.67983 | 6.064
2024-12-10 | 0:44 | Data | 0 | 32.771 | 30.82 | 195.676 | 7.63 | 184.142 | 2222.52 | 25.8 | 43.832 | 6.36 | 1.374 | 4.705 | 8698.5 | 2.1 | 98 | 77.4 | 1445 | 21.92 | 5654 | 2955.3 | 2888.6 | 4248.1 | 1217 | 0.67807 | 6.079
2024-12-10 | 0:44 | Data | 0 | 32.406 | 30.415 | 195.495 | 7.64 | 184.051 | 2218.91 | 25.8 | 43.561 | 6.36 | 1.37 | 4.699 | 8693.98 | 2.059 | 98 | 77.4 | 1443 | 21.78 | 5651.1 | 2963.2 | 2912.1 | 4262.1 | 1217 | 0.67473 | 6.069
2024-12-10 | 0:44 | Data | 0 | 32.264 | 30.239 | 195.585 | 7.63 | 184.051 | 2221.62 | 25.8 | 43.561 | 6.36 | 1.369 | 4.674 | 8703.03 | 1.85 | 98 | 77.3 | 1445 | 21.78 | 5657 | 2951.4 | 2949.8 | 4276.6 | 1217 | 0.67268 | 6.045
2024-12-10 | 0:45 | Data | 0 | 32.379 | 30.408 | 195.54 | 7.64 | 184.096 | 2222.52 | 25.81 | 43.561 | 6.36 | 1.366 | 4.708 | 8703.03 | 1.998 | 98 | 77.5 | 1445 | 21.74 | 5657 | 2971.3 | 2941.4 | 4293 | 1217 | 0.67453 | 6.074
2024-12-10 | 0:45 | Data | 0 | 32.561 | 30.192 | 195.631 | 7.63 | 184.187 | 2222.52 | 25.81 | 43.561 | 6.36 | 1.372 | 4.715 | 8703.03 | 2.1 | 98 | 77.5 | 1444 | 21.74 | 5657 | 2984.1 | 2949.6 | 4310.1 | 1217 | 0.6752 | 6.086
2024-12-10 | 0:45 | Data | 0 | 32.494 | 30.516 | 195.54 | 7.64 | 184.096 | 2218.91 | 25.81 | 43.561 | 6.36 | 1.369 | 4.698 | 8716.59 | 2.079 | 98 | 77.5 | 1442 | 21.78 | 5665.8 | 2987.1 | 2957.3 | 4319 | 1217.1 | 0.67302 | 6.066
2024-12-10 | 0:45 | Data | 0 | 32.717 | 30.421 | 195.585 | 7.63 | 184.096 | 2221.62 | 25.8 | 43.561 | 6.36 | 1.37 | 4.72 | 8703.03 | 2.289 | 98 | 77.5 | 1444 | 21.74 | 5657 | 2960.1 | 2968.9 | 4306 | 1217.1 | 0.67037 | 6.089
2024-12-10 | 0:45 | Data | 0 | 32.521 | 30.421 | 195.54 | 7.64 | 184.096 | 2221.62 | 25.8 | 43.561 | 6.36 | 1.373 | 4.712 | 8703.03 | 2.079 | 98 | 77.4 | 1445 | 21.78 | 5657 | 2963.2 | 2941 | 4290.3 | 1217.1 | 0.67332 | 6.085
2024-12-10 | 0:45 | Data | 0 | 32.305 | 30.421 | 195.54 | 7.64 | 184.142 | 2222.52 | 25.8 | 43.47 | 6.36 | 1.365 | 4.682 | 8721.11 | 1.836 | 98 | 77.4 | 1445 | 21.78 | 5668.7 | 2970.6 | 2924.9 | 4285.2 | 1217.1 | 0.67469 | 6.046
2024-12-10 | 0:45 | Data | 0 | 32.71 | 30.469 | 195.585 | 7.64 | 184.051 | 2223.43 | 25.8 | 43.47 | 6.36 | 1.367 | 4.662 | 8703.03 | 1.958 | 98 | 77.3 | 1446 | 21.78 | 5657 | 2979.4 | 2899.4 | 4272.8 | 1217.1 | 0.68018 | 6.027
2024-12-10 | 0:45 | Data | 0 | 32.494 | 30.415 | 195.676 | 7.64 | 184.051 | 2226.14 | 25.81 | 43.29 | 6.36 | 1.371 | 4.681 | 8703.03 | 2.079 | 98 | 77.3 | 1447 | 21.78 | 5657 | 2994.5 | 2911.1 | 4294 | 1217.1 | 0.67901 | 6.052
2024-12-10 | 0:45 | Data | 0 | 32.973 | 30.448 | 195.631 | 7.64 | 184.187 | 2225.23 | 25.8 | 43.561 | 6.37 | 1.369 | 4.693 | 8703.03 | 2.1 | 98 | 77.4 | 1446 | 21.78 | 5657 | 2971 | 2964.7 | 4311.5 | 1217.1 | 0.67159 | 6.063
2024-12-10 | 0:45 | Data | 0 | 32.69 | 30.469 | 195.721 | 7.63 | 184.051 | 2222.52 | 25.81 | 43.47 | 6.36 | 1.373 | 4.721 | 8703.03 | 2.187 | 98 | 77.5 | 1445 | 21.78 | 5657 | 3000.2 | 2919.3 | 4300.5 | 1217.1 | 0.68023 | 6.092
2024-12-10 | 0:45 | Data | 0 | 32.568 | 30.415 | 195.495 | 7.64 | 184.142 | 2223.43 | 25.81 | 43.561 | 6.36 | 1.371 | 4.711 | 8703.03 | 1.965 | 98 | 77.5 | 1445 | 21.78 | 5657 | 2999.3 | 2943 | 4314.1 | 1217.1 | 0.67785 | 6.081
2024-12-10 | 0:45 | Data | 0 | 32.717 | 30.442 | 195.676 | 7.64 | 184.142 | 2227.95 | 25.81 | 43.561 | 6.36 | 1.377 | 4.71 | 8734.68 | 2.282 | 98 | 77.4 | 1448 | 21.74 | 5677.5 | 3001.7 | 2949.6 | 4319.8 | 1217.1 | 0.67703 | 6.086
2024-12-10 | 0:45 | Data | 0 | 32.595 | 30.469 | 195.585 | 7.64 | 184.142 | 2225.23 | 25.8 | 43.47 | 6.36 | 1.367 | 4.716 | 8739.2 | 1.965 | 98 | 77.5 | 1446 | 21.78 | 5680.5 | 2984.3 | 2969.6 | 4327.8 | 1217.1 | 0.67179 | 6.083
2024-12-10 | 0:45 | Data | 0 | 32.602 | 30.415 | 195.631 | 7.63 | 184.096 | 2220.72 | 25.8 | 43.47 | 6.37 | 1.374 | 4.728 | 8725.64 | 2.133 | 98 | 77.5 | 1443 | 21.74 | 5671.7 | 2980.2 | 2962.2 | 4318.7 | 1217.1 | 0.67315 | 6.102
2024-12-10 | 0:45 | Data | 0 | 32.379 | 30.415 | 195.45 | 7.64 | 183.961 | 2218.91 | 25.8 | 43.561 | 6.36 | 1.365 | 4.692 | 8734.68 | 2.052 | 98 | 77.5 | 1442 | 21.78 | 5677.5 | 2982.8 | 2951.9 | 4313.7 | 1217.1 | 0.67394 | 6.058
2024-12-10 | 0:45 | Data | 0 | 32.413 | 30.415 | 195.585 | 7.63 | 184.142 | 2213.49 | 25.8 | 43.47 | 6.36 | 1.367 | 4.711 | 8721.11 | 1.857 | 98 | 77.5 | 1439 | 21.74 | 5668.7 | 2974.8 | 2940.2 | 4301.3 | 1217.1 | 0.67333 | 6.079
2024-12-10 | 0:45 | Data | 0 | 32.642 | 30.448 | 195.585 | 7.64 | 184.142 | 2216.2 | 25.8 | 43.561 | 6.36 | 1.37 | 4.711 | 8716.59 | 1.89 | 98 | 77.5 | 1440 | 21.78 | 5665.8 | 2982.3 | 2939.9 | 4303 | 1217.1 | 0.67607 | 6.082
2024-12-10 | 0:45 | Data | 0 | 32.494 | 30.428 | 195.585 | 7.64 | 184.051 | 2216.2 | 25.81 | 43.561 | 6.36 | 1.361 | 4.721 | 8712.07 | 2.052 | 98 | 77.6 | 1441 | 21.74 | 5662.8 | 3002.6 | 2931.4 | 4310.8 | 1217.1 | 0.67869 | 6.083
2024-12-10 | 0:46 | Data | 0 | 32.609 | 30.415 | 195.54 | 7.63 | 184.096 | 2217.1 | 25.8 | 43.561 | 6.36 | 1.366 | 4.718 | 8703.03 | 2.14 | 98 | 77.6 | 1441 | 21.74 | 5657 | 2983.4 | 2933.7 | 4301 | 1217.1 | 0.67517 | 6.083
2024-12-10 | 0:46 | Data | 0 | 32.609 | 30.428 | 195.585 | 7.64 | 184.051 | 2214.39 | 25.81 | 43.561 | 6.36 | 1.371 | 4.715 | 8725.64 | 2.079 | 98 | 77.5 | 1439 | 21.78 | 5671.7 | 3016.4 | 2953.1 | 4332.8 | 1217.1 | 0.67863 | 6.086
2024-12-10 | 0:46 | Data | 0 | 32.906 | 30.766 | 195.676 | 7.64 | 184.187 | 2218.91 | 25.8 | 43.561 | 6.36 | 1.367 | 4.683 | 8703.03 | 2.289 | 98 | 77.4 | 1442 | 21.78 | 5657 | 2966.6 | 2951.8 | 4303.7 | 1217.1 | 0.67042 | 6.051
2024-12-10 | 0:46 | Data | 0 | 32.447 | 30.644 | 195.676 | 7.64 | 184.096 | 2216.2 | 25.8 | 43.561 | 6.36 | 1.367 | 4.698 | 8721.11 | 1.958 | 98 | 77.5 | 1441 | 21.78 | 5668.7 | 3001.4 | 2956.4 | 4327.3 | 1217.1 | 0.67547 | 6.065
2024-12-10 | 0:46 | Data | 0 | 32.494 | 30.307 | 195.766 | 7.64 | 184.096 | 2212.58 | 25.79 | 43.47 | 6.36 | 1.381 | 4.701 | 8693.98 | 2.275 | 98 | 77.3 | 1438 | 21.74 | 5651.1 | 3000.7 | 2950.5 | 4323.8 | 1217.1 | 0.67548 | 6.081
2024-12-10 | 0:46 | Data | 0 | 32.467 | 30.415 | 195.585 | 7.64 | 184.096 | 2216.2 | 25.8 | 43.561 | 6.37 | 1.374 | 4.703 | 8703.03 | 2.187 | 98 | 77.4 | 1440 | 21.78 | 5657 | 2978.2 | 2946.4 | 4308.3 | 1217.1 | 0.67325 | 6.077
2024-12-10 | 0:46 | Data | 0 | 32.609 | 30.624 | 195.585 | 7.64 | 184.187 | 2212.58 | 25.8 | 43.561 | 6.36 | 1.369 | 4.719 | 8716.59 | 2.133 | 98 | 77.5 | 1438 | 21.83 | 5665.8 | 3009.9 | 2923.5 | 4310.4 | 1217.1 | 0.6804 | 6.086
2024-12-10 | 0:46 | Data | 0 | 32.521 | 30.421 | 195.495 | 7.64 | 184.096 | 2222.52 | 25.79 | 43.561 | 6.36 | 1.373 | 4.74 | 8689.46 | 2.079 | 98 | 77.5 | 1445 | 21.78 | 5648.1 | 3011.2 | 2919.9 | 4309.8 | 1217.1 | 0.67987 | 6.112
2024-12-10 | 0:46 | Data | 0 | 32.359 | 30.415 | 195.631 | 7.63 | 184.187 | 2216.2 | 25.79 | 43.47 | 6.36 | 1.374 | 4.723 | 8689.46 | 1.89 | 98 | 77.5 | 1441 | 21.78 | 5648.1 | 2978.2 | 2978.8 | 4323 | 1217.1 | 0.67091 | 6.097
2024-12-10 | 0:46 | Data | 0 | 32.933 | 30.705 | 195.585 | 7.64 | 184.096 | 2215.29 | 25.8 | 43.561 | 6.36 | 1.365 | 4.667 | 8703.03 | 2.194 | 98 | 77.4 | 1440 | 21.74 | 5657 | 3008.9 | 2941.6 | 4324.1 | 1217.1 | 0.67815 | 6.032
2024-12-10 | 0:46 | Data | 0 | 32.717 | 30.442 | 195.54 | 7.63 | 184.142 | 2213.49 | 25.8 | 43.561 | 6.37 | 1.365 | 4.68 | 8703.03 | 2.194 | 98 | 77.4 | 1438 | 21.78 | 5657 | 2898.4 | 2893.1 | 4207.2 | 1217.1 | 0.67027 | 6.045
2024-12-10 | 0:46 | Data | 0 | 32.494 | 30.462 | 195.495 | 7.63 | 184.096 | 2213.49 | 25.81 | 43.47 | 6.36 | 1.38 | 4.719 | 8689.46 | 2.019 | 98 | 77.4 | 1439 | 21.74 | 5648.1 | 2893.5 | 2894.6 | 4211 | 1217.1 | 0.66903 | 6.099
2024-12-10 | 0:46 | Data | 0 | 32.494 | 30.3 | 195.45 | 7.63 | 184.051 | 2217.1 | 25.8 | 43.561 | 6.36 | 1.386 | 4.692 | 8662.33 | 2.073 | 98 | 77.2 | 1441 | 21.74 | 5630.5 | 2900.3 | 2889.4 | 4206.7 | 1217.1 | 0.67243 | 6.079
2024-12-10 | 0:46 | Data | 0 | 32.602 | 30.462 | 195.54 | 7.64 | 184.142 | 2217.1 | 25.8 | 43.561 | 6.37 | 1.38 | 4.701 | 8635.19 | 1.965 | 98 | 77.3 | 1441 | 21.78 | 5612.9 | 2875.8 | 2899.5 | 4214.4 | 1217.1 | 0.66986 | 6.082
2024-12-10 | 0:46 | Data | 0 | 32.494 | 30.421 | 195.495 | 7.63 | 184.051 | 2216.2 | 25.79 | 43.561 | 6.36 | 1.377 | 4.708 | 8648.76 | 2.147 | 98 | 77.4 | 1441 | 21.78 | 5621.7 | 2919.2 | 2913.2 | 4237.1 | 1217.1 | 0.67233 | 6.084
2024-12-10 | 0:46 | Data | 0 | 32.285 | 30.408 | 195.54 | 7.64 | 184.051 | 2218 | 25.8 | 43.47 | 6.36 | 1.372 | 4.709 | 8662.33 | 2.039 | 98 | 77.4 | 1442 | 21.78 | 5630.5 | 2896.1 | 2912.8 | 4221.2 | 1217.1 | 0.66885 | 6.082
2024-12-10 | 0:46 | Data | 0 | 32.44 | 30.435 | 195.495 | 7.64 | 184.006 | 2216.2 | 25.8 | 43.47 | 6.37 | 1.377 | 4.708 | 8657.8 | 2.235 | 98 | 77.4 | 1441 | 21.74 | 5627.6 | 2906 | 2909.1 | 4218.5 | 1217.1 | 0.67607 | 6.083
2024-12-10 | 0:46 | Data | 0 | 32.669 | 30.448 | 195.676 | 7.63 | 184.187 | 2221.62 | 25.8 | 43.47 | 6.36 | 1.375 | 4.736 | 8657.8 | 2.154 | 98 | 77.5 | 1444 | 21.74 | 5627.6 | 2936.9 | 2922.9 | 4249.4 | 1217.1 | 0.6742 | 6.111
2024-12-10 | 0:47 | Data | 0 | 32.264 | 30.192 | 195.495 | 7.63 | 184.096 | 2222.52 | 25.8 | 43.47 | 6.36 | 1.373 | 4.715 | 8662.33 | 2.248 | 98 | 77.5 | 1445 | 21.74 | 5630.5 | 2995.5 | 2956.7 | 4321.4 | 1217.1 | 0.67556 | 6.089
2024-12-10 | 0:47 | Data | 0 | 32.717 | 30.421 | 195.54 | 7.64 | 184.187 | 2222.52 | 25.79 | 43.561 | 6.37 | 1.372 | 4.711 | 8662.33 | 2.086 | 98 | 77.4 | 1445 | 21.78 | 5630.5 | 2974.6 | 2951.1 | 4301 | 1217.1 | 0.67344 | 6.083
2024-12-10 | 0:47 | Data | 0 | 32.318 | 30.313 | 195.54 | 7.64 | 184.051 | 2222.52 | 25.8 | 43.561 | 6.36 | 1.372 | 4.706 | 8671.37 | 2.262 | 98 | 77.4 | 1445 | 21.74 | 5636.4 | 2984.3 | 2956.9 | 4317.6 | 1217.2 | 0.67329 | 6.078
2024-12-10 | 0:47 | Data | 0 | 32.548 | 30.401 | 195.585 | 7.63 | 184.142 | 2222.52 | 25.8 | 43.561 | 6.36 | 1.371 | 4.687 | 8662.33 | 2.174 | 98 | 77.4 | 1445 | 21.78 | 5630.5 | 2982.2 | 2945 | 4309.8 | 1217.2 | 0.67002 | 6.058
2024-12-10 | 0:47 | Data | 0 | 32.717 | 30.475 | 195.54 | 7.64 | 184.096 | 2227.04 | 25.8 | 43.561 | 6.36 | 1.372 | 4.706 | 8671.37 | 1.985 | 98 | 77.4 | 1448 | 21.78 | 5636.4 | 2969 | 2937.5 | 4290.6 | 1217.2 | 0.67409 | 6.079
2024-12-10 | 0:47 | Data | 0 | 32.285 | 30.469 | 195.721 | 7.63 | 184.142 | 2224.33 | 25.79 | 43.47 | 6.36 | 1.385 | 4.708 | 8716.59 | 1.836 | 98 | 77.3 | 1445 | 21.74 | 5665.8 | 2969.4 | 2935.1 | 4293.4 | 1217.2 | 0.67507 | 6.092
2024-12-10 | 0:47 | Data | 0 | 32.494 | 30.388 | 195.54 | 7.64 | 184.096 | 2224.33 | 25.78 | 43.47 | 6.36 | 1.381 | 4.716 | 8703.03 | 2.019 | 98 | 77.3 | 1446 | 21.74 | 5657 | 2951.6 | 2941.3 | 4284.2 | 1217.2 | 0.6721 | 6.097
2024-12-10 | 0:47 | Data | 0 | 32.933 | 30.421 | 195.54 | 7.63 | 184.142 | 2227.95 | 25.8 | 43.741 | 6.37 | 1.374 | 4.727 | 8703.03 | 2.14 | 98 | 77.5 | 1448 | 21.83 | 5657 | 2972.8 | 2915.4 | 4280.3 | 1217.2 | 0.67736 | 6.101
2024-12-10 | 0:47 | Data | 0 | 32.494 | 30.415 | 195.495 | 7.64 | 184.051 | 2228.85 | 25.79 | 43.561 | 6.36 | 1.376 | 4.708 | 8730.16 | 2.079 | 98 | 77.4 | 1448 | 21.83 | 5674.6 | 2961 | 2937 | 4286.2 | 1217.2 | 0.67313 | 6.083
2024-12-10 | 0:47 | Data | 0 | 32.602 | 30.205 | 195.631 | 7.64 | 184.142 | 2227.04 | 25.8 | 43.561 | 6.36 | 1.366 | 4.693 | 8743.73 | 2.248 | 98 | 77.5 | 1448 | 21.74 | 5683.4 | 2956 | 2932.4 | 4285.6 | 1217.2 | 0.67202 | 6.058
2024-12-10 | 0:47 | Data | 0 | 32.933 | 30.705 | 195.631 | 7.63 | 184.187 | 2227.95 | 25.79 | 43.832 | 6.36 | 1.36 | 4.683 | 8730.16 | 1.904 | 98 | 77.5 | 1448 | 21.87 | 5674.6 | 2998.1 | 2918 | 4298.4 | 1217.2 | 0.68061 | 6.043
2024-12-10 | 0:47 | Data | 0 | 32.278 | 30.286 | 195.495 | 7.63 | 184.006 | 2225.23 | 25.8 | 43.561 | 6.37 | 1.362 | 4.707 | 8743.73 | 1.965 | 98 | 77.6 | 1446 | 21.78 | 5683.4 | 3001.6 | 2949.8 | 4313.3 | 1217.2 | 0.67597 | 6.069
2024-12-10 | 0:47 | Data | 0 | 32.379 | 30.59 | 195.495 | 7.63 | 184.006 | 2227.95 | 25.8 | 43.561 | 6.36 | 1.377 | 4.705 | 8707.55 | 2.214 | 98 | 77.4 | 1448 | 21.74 | 5659.9 | 3003.5 | 2958.4 | 4325.4 | 1217.2 | 0.67728 | 6.081
2024-12-10 | 0:47 | Data | 0 | 32.636 | 30.415 | 195.45 | 7.64 | 184.006 | 2227.95 | 25.79 | 43.741 | 6.36 | 1.378 | 4.702 | 8707.55 | 1.884 | 98 | 77.3 | 1448 | 21.92 | 5659.9 | 2963.2 | 2968.4 | 4314.7 | 1217.2 | 0.66834 | 6.08
2024-12-10 | 0:47 | Data | 0 | 32.48 | 30.239 | 195.585 | 7.63 | 184.051 | 2227.04 | 25.8 | 43.561 | 6.36 | 1.359 | 4.699 | 8703.03 | 2.079 | 98 | 77.6 | 1448 | 21.78 | 5657 | 2974.2 | 2988.6 | 4332.4 | 1217.2 | 0.66808 | 6.06
2024-12-10 | 0:47 | Data | 0 | 32.494 | 30.415 | 195.585 | 7.64 | 184.142 | 2227.95 | 25.79 | 43.47 | 6.36 | 1.367 | 4.712 | 8707.55 | 2.079 | 98 | 77.5 | 1448 | 21.74 | 5659.9 | 2969.1 | 2974.9 | 4320 | 1217.2 | 0.66929 | 6.08
2024-12-10 | 0:47 | Data | 0 | 32.575 | 30.246 | 195.45 | 7.64 | 184.142 | 2225.23 | 25.79 | 43.561 | 6.37 | 1.381 | 4.719 | 8752.77 | 2.457 | 98 | 77.4 | 1446 | 21.78 | 5689.3 | 2964.3 | 2967.9 | 4307 | 1217.2 | 0.67106 | 6.1
2024-12-10 | 0:48 | Data | 0 | 32.42 | 30.327 | 195.631 | 7.64 | 184.006 | 2229.75 | 25.8 | 43.561 | 6.37 | 1.374 | 4.695 | 8734.68 | 2.241 | 98.1 | 77.4 | 1450 | 21.78 | 5677.5 | 3003.3 | 2929.3 | 4291.9 | 1217.2 | 0.67846 | 6.068
2024-12-10 | 0:48 | Data | 0 | 32.494 | 30.442 | 195.54 | 7.64 | 184.006 | 2229.75 | 25.8 | 43.561 | 6.36 | 1.358 | 4.743 | 8725.64 | 2.127 | 98 | 77.7 | 1449 | 21.78 | 5671.7 | 2974.4 | 2923.2 | 4280.2 | 1217.2 | 0.67922 | 6.102
2024-12-10 | 0:48 | Data | 0 | 32.264 | 30.3 | 195.359 | 7.63 | 183.961 | 2230.66 | 25.79 | 43.561 | 6.37 | 1.367 | 4.721 | 8721.11 | 2.255 | 98 | 77.5 | 1449 | 21.78 | 5668.7 | 2959.1 | 2919.4 | 4268.9 | 1217.2 | 0.67517 | 6.087
2024-12-10 | 0:48 | Data | 0 | 32.44 | 30.583 | 195.45 | 7.63 | 184.096 | 2233.37 | 25.78 | 43.561 | 6.36 | 1.376 | 4.723 | 8712.07 | 2.133 | 98.1 | 77.4 | 1451 | 21.74 | 5662.8 | 2958.9 | 2913 | 4267.1 | 1217.2 | 0.67618 | 6.099
2024-12-10 | 0:48 | Data | 0 | 32.494 | 30.313 | 195.45 | 7.64 | 184.096 | 2233.37 | 25.78 | 43.561 | 6.36 | 1.372 | 4.693 | 8730.16 | 2.167 | 98.1 | 77.4 | 1451 | 21.74 | 5674.6 | 2969.1 | 2901.5 | 4266.5 | 1217.2 | 0.67867 | 6.065
2024-12-10 | 0:48 | Data | 0 | 32.44 | 30.523 | 195.631 | 7.64 | 184.051 | 2231.56 | 25.8 | 43.47 | 6.36 | 1.367 | 4.688 | 8721.11 | 2.181 | 98.1 | 77.4 | 1451 | 21.74 | 5668.7 | 2966.5 | 2913.9 | 4269.7 | 1217.2 | 0.67843 | 6.055
2024-12-10 | 0:48 | Data | 0 | 32.251 | 30.374 | 195.495 | 7.64 | 184.006 | 2231.56 | 25.8 | 43.741 | 6.36 | 1.371 | 4.714 | 8730.16 | 2.194 | 98 | 77.5 | 1450 | 21.83 | 5674.6 | 2987.4 | 2915.8 | 4287.2 | 1217.2 | 0.67957 | 6.083
2024-12-10 | 0:48 | Data | 0 | 32.46 | 30.401 | 195.45 | 7.63 | 184.006 | 2227.95 | 25.81 | 43.561 | 6.36 | 1.366 | 4.714 | 8730.16 | 2.113 | 98 | 77.5 | 1448 | 21.74 | 5674.6 | 2957.7 | 2939.9 | 4288.1 | 1217.2 | 0.67385 | 6.081
2024-12-10 | 0:48 | Data | 0 | 32.48 | 30.415 | 195.45 | 7.63 | 184.051 | 2228.85 | 25.81 | 43.47 | 6.36 | 1.377 | 4.698 | 8716.59 | 2.073 | 98.1 | 77.3 | 1449 | 21.74 | 5665.8 | 2968.3 | 2921.3 | 4278.3 | 1217.2 | 0.67622 | 6.074
2024-12-10 | 0:48 | Data | 0 | 32.291 | 30.185 | 195.404 | 7.64 | 183.961 | 2229.75 | 25.82 | 43.741 | 6.36 | 1.384 | 4.722 | 8689.46 | 1.992 | 98 | 77.3 | 1450 | 21.87 | 5648.1 | 2970.7 | 2922.3 | 4277.4 | 1217.2 | 0.67685 | 6.106
2024-12-10 | 0:48 | Data | 0 | 32.278 | 30.185 | 195.45 | 7.63 | 184.006 | 2227.95 | 25.82 | 43.561 | 6.36 | 1.376 | 4.74 | 8693.98 | 2.079 | 98 | 77.5 | 1448 | 21.78 | 5651.1 | 2955.9 | 2923.5 | 4272.1 | 1217.2 | 0.67319 | 6.115
2024-12-10 | 0:48 | Data | 0 | 32.285 | 30.577 | 195.54 | 7.64 | 184.096 | 2229.75 | 25.82 | 43.741 | 6.36 | 1.372 | 4.721 | 8671.37 | 1.971 | 98 | 77.5 | 1450 | 21.87 | 5636.4 | 2965.9 | 2949.7 | 4294.1 | 1217.2 | 0.67337 | 6.092
2024-12-10 | 0:48 | Data | 0 | 32.379 | 30.198 | 195.45 | 7.64 | 184.051 | 2229.75 | 25.82 | 43.47 | 6.36 | 1.377 | 4.708 | 8671.37 | 2.079 | 98.1 | 77.4 | 1450 | 21.78 | 5636.4 | 2952.1 | 2912.7 | 4262.3 | 1217.2 | 0.67503 | 6.085
2024-12-10 | 0:48 | Data | 0 | 32.089 | 30.185 | 195.495 | 7.63 | 183.961 | 2227.95 | 25.83 | 43.832 | 6.36 | 1.371 | 4.716 | 8684.94 | 1.857 | 98 | 77.5 | 1448 | 21.92 | 5645.2 | 2956.7 | 2898.9 | 4255.6 | 1217.2 | 0.67679 | 6.088
2024-12-10 | 0:48 | Data | 0 | 32.264 | 30.212 | 195.404 | 7.64 | 183.961 | 2225.23 | 25.83 | 43.832 | 6.36 | 1.369 | 4.71 | 8653.28 | 2.025 | 98 | 77.5 | 1446 | 21.92 | 5624.6 | 2965.7 | 2889.2 | 4250.1 | 1217.2 | 0.68104 | 6.077
2024-12-10 | 0:48 | Data | 0 | 32.264 | 30.388 | 195.495 | 7.64 | 184.006 | 2227.04 | 25.82 | 43.47 | 6.36 | 1.371 | 4.722 | 8680.41 | 2.019 | 98 | 77.5 | 1448 | 21.78 | 5642.3 | 2961 | 2880.4 | 4246 | 1217.2 | 0.68048 | 6.094
2024-12-10 | 0:48 | Data | 0 | 32.264 | 30.185 | 195.404 | 7.64 | 184.006 | 2218.91 | 25.82 | 43.832 | 6.37 | 1.367 | 4.72 | 8698.5 | 2.079 | 98 | 77.5 | 1442 | 21.87 | 5654 | 2956.7 | 2896 | 4246.4 | 1217.2 | 0.67947 | 6.086
2024-12-10 | 0:48 | Data | 0 | 32.521 | 30.415 | 195.631 | 7.63 | 184.096 | 2218.91 | 25.82 | 43.832 | 6.36 | 1.358 | 4.676 | 8689.46 | 2.079 | 98 | 77.5 | 1442 | 21.87 | 5648.1 | 2944 | 2909.1 | 4250.1 | 1217.2 | 0.67533 | 6.034
2024-12-10 | 0:49 | Data | 0 | 32.264 | 30.185 | 195.359 | 7.63 | 183.916 | 2218.91 | 25.82 | 43.47 | 6.37 | 1.367 | 4.71 | 8693.98 | 2.079 | 98 | 77.5 | 1443 | 21.74 | 5651.1 | 2970.4 | 2907.2 | 4269.9 | 1217.2 | 0.67645 | 6.075
2024-12-10 | 0:49 | Data | 0 | 32.264 | 30.496 | 195.314 | 7.64 | 183.961 | 2218.91 | 25.82 | 43.561 | 6.36 | 1.375 | 4.73 | 8689.46 | 2.12 | 98 | 77.5 | 1442 | 21.74 | 5648.1 | 2958.3 | 2939.9 | 4283.5 | 1217.2 | 0.67426 | 6.103
2024-12-10 | 0:49 | Data | 0 | 32.298 | 30.361 | 195.54 | 7.64 | 183.961 | 2216.2 | 25.82 | 43.741 | 6.36 | 1.379 | 4.708 | 8703.03 | 2.086 | 98 | 77.3 | 1441 | 21.87 | 5657 | 2957.6 | 2931.8 | 4278.8 | 1217.2 | 0.67275 | 6.087
2024-12-10 | 0:49 | Data | 0 | 32.372 | 30.185 | 195.54 | 7.64 | 183.961 | 2216.2 | 25.82 | 43.741 | 6.36 | 1.367 | 4.698 | 8703.03 | 2.093 | 98 | 77.5 | 1441 | 21.87 | 5657 | 2973.3 | 2918.8 | 4280.2 | 1217.3 | 0.67733 | 6.065
2024-12-10 | 0:49 | Data | 0 | 32.467 | 30.361 | 195.495 | 7.64 | 183.961 | 2218 | 25.83 | 43.741 | 6.36 | 1.361 | 4.702 | 8712.07 | 2.174 | 98 | 77.6 | 1442 | 21.92 | 5662.8 | 2959.3 | 2932.5 | 4276.3 | 1217.3 | 0.67478 | 6.064
2024-12-10 | 0:49 | Data | 0 | 32.325 | 30.415 | 195.585 | 7.64 | 184.051 | 2216.2 | 25.81 | 43.741 | 6.37 | 1.374 | 4.697 | 8703.03 | 1.877 | 98 | 77.4 | 1441 | 21.87 | 5657 | 2938.5 | 2904.9 | 4248 | 1217.3 | 0.67383 | 6.071
2024-12-10 | 0:49 | Data | 0 | 32.271 | 30.185 | 195.404 | 7.63 | 184.006 | 2216.2 | 25.83 | 43.832 | 6.36 | 1.377 | 4.701 | 8693.98 | 2.079 | 98 | 77.3 | 1441 | 21.92 | 5651.1 | 2954.8 | 2902.9 | 4256.1 | 1217.3 | 0.67662 | 6.076
2024-12-10 | 0:49 | Data | 0 | 32.264 | 30.185 | 195.45 | 7.64 | 183.916 | 2213.49 | 25.81 | 43.47 | 6.36 | 1.377 | 4.708 | 8707.55 | 2.079 | 98 | 77.4 | 1439 | 21.74 | 5659.9 | 2963.6 | 2929.1 | 4277.2 | 1217.3 | 0.67527 | 6.086
2024-12-10 | 0:49 | Data | 0 | 32.717 | 30.644 | 195.585 | 7.64 | 184.051 | 2213.49 | 25.81 | 43.741 | 6.36 | 1.365 | 4.701 | 8703.03 | 1.877 | 98 | 77.5 | 1439 | 21.87 | 5657 | 2956.6 | 2909.5 | 4261.5 | 1217.3 | 0.67617 | 6.065
2024-12-10 | 0:49 | Data | 0 | 32.264 | 30.185 | 195.54 | 7.63 | 184.006 | 2211.68 | 25.81 | 43.741 | 6.36 | 1.367 | 4.714 | 8703.03 | 2.282 | 98 | 77.5 | 1438 | 21.87 | 5657 | 2967 | 2896.6 | 4258.8 | 1217.3 | 0.67843 | 6.082
2024-12-10 | 0:49 | Data | 0 | 32.541 | 30.192 | 195.495 | 7.64 | 184.006 | 2210.77 | 25.81 | 43.561 | 6.36 | 1.372 | 4.704 | 8689.46 | 2.1 | 98 | 77.4 | 1437 | 21.78 | 5648.1 | 2955.3 | 2873.7 | 4235.3 | 1217.3 | 0.67978 | 6.076
2024-12-10 | 0:49 | Data | 0 | 32.278 | 30.361 | 195.45 | 7.64 | 184.006 | 2210.77 | 25.8 | 43.561 | 6.36 | 1.373 | 4.707 | 8671.37 | 2.14 | 98 | 77.4 | 1437 | 21.78 | 5636.4 | 2966.1 | 2899 | 4261.5 | 1217.3 | 0.67844 | 6.081
2024-12-10 | 0:49 | Data | 0 | 32.264 | 30.185 | 195.495 | 7.63 | 184.006 | 2211.68 | 25.8 | 43.47 | 6.36 | 1.365 | 4.717 | 8703.03 | 2.079 | 98 | 77.6 | 1438 | 21.78 | 5657 | 2942.7 | 2901.7 | 4249.5 | 1217.3 | 0.67515 | 6.083
2024-12-10 | 0:49 | Data | 0 | 32.393 | 30.259 | 195.45 | 7.63 | 184.096 | 2210.77 | 25.81 | 43.741 | 6.37 | 1.377 | 4.716 | 8707.55 | 2.019 | 98 | 77.4 | 1438 | 21.92 | 5659.9 | 2971.6 | 2897.2 | 4264.4 | 1217.3 | 0.67969 | 6.093
2024-12-10 | 0:49 | Data | 0 | 32.541 | 30.442 | 195.54 | 7.64 | 184.096 | 2208.97 | 25.81 | 43.741 | 6.37 | 1.377 | 4.705 | 8725.64 | 1.843 | 98 | 77.4 | 1436 | 21.87 | 5671.7 | 2959.5 | 2915.1 | 4269.1 | 1217.3 | 0.67523 | 6.081
2024-12-10 | 0:49 | Data | 0 | 32.487 | 30.415 | 195.45 | 7.63 | 184.051 | 2210.77 | 25.8 | 43.741 | 6.37 | 1.369 | 4.677 | 8730.16 | 2.079 | 98 | 77.4 | 1437 | 21.92 | 5674.6 | 2965.5 | 2946.6 | 4293.7 | 1217.3 | 0.67299 | 6.045
2024-12-10 | 0:49 | Data | 0 | 32.649 | 30.442 | 195.404 | 7.64 | 183.961 | 2213.49 | 25.81 | 43.741 | 6.37 | 1.362 | 4.708 | 8716.59 | 2.16 | 98 | 77.6 | 1439 | 21.92 | 5665.8 | 2947.9 | 2942.2 | 4279.7 | 1217.3 | 0.67093 | 6.07
2024-12-10 | 0:49 | Data | 0 | 32.494 | 30.185 | 195.45 | 7.63 | 184.006 | 2216.2 | 25.8 | 43.47 | 6.36 | 1.367 | 4.739 | 8734.68 | 2.133 | 98 | 77.6 | 1441 | 21.74 | 5677.5 | 2949.2 | 2942.3 | 4280.3 | 1217.3 | 0.67171 | 6.106
2024-12-10 | 0:50 | Data | 0 | 32.453 | 30.401 | 195.495 | 7.64 | 184.006 | 2208.97 | 25.81 | 43.561 | 6.36 | 1.373 | 4.71 | 8707.55 | 2.12 | 98 | 77.4 | 1435 | 21.83 | 5659.9 | 2950.7 | 2918.1 | 4264.1 | 1217.3 | 0.67351 | 6.083
2024-12-10 | 0:50 | Data | 0 | 32.332 | 30.192 | 195.45 | 7.63 | 184.006 | 2213.49 | 25.8 | 43.561 | 6.37 | 1.365 | 4.708 | 8693.98 | 2.079 | 98 | 77.5 | 1439 | 21.74 | 5651.1 | 2935.9 | 2876.6 | 4227.6 | 1217.3 | 0.67641 | 6.073
2024-12-10 | 0:50 | Data | 0 | 32.318 | 30.408 | 195.45 | 7.63 | 183.916 | 2211.68 | 25.82 | 43.561 | 6.37 | 1.373 | 4.73 | 8689.46 | 2.113 | 98 | 77.5 | 1438 | 21.78 | 5648.1 | 2961 | 2883.5 | 4249.5 | 1217.3 | 0.67952 | 6.104
2024-12-10 | 0:50 | Data | 0 | 32.339 | 30.192 | 195.54 | 7.64 | 184.051 | 2208.06 | 25.8 | 43.561 | 6.36 | 1.375 | 4.721 | 8693.98 | 1.978 | 98 | 77.4 | 1435 | 21.78 | 5651.1 | 2955.2 | 2882.4 | 4243.2 | 1217.3 | 0.68018 | 6.096
2024-12-10 | 0:50 | Data | 0 | 32.811 | 30.232 | 195.45 | 7.64 | 184.051 | 2207.16 | 25.8 | 43.561 | 6.36 | 1.371 | 4.708 | 8716.59 | 2.255 | 98 | 77.5 | 1435 | 21.78 | 5665.8 | 2949.8 | 2871.3 | 4233.4 | 1217.3 | 0.67965 | 6.078
2024-12-10 | 0:50 | Data | 0 | 32.649 | 30.334 | 195.585 | 7.63 | 184.051 | 2208.06 | 25.81 | 43.741 | 6.37 | 1.367 | 4.705 | 8707.55 | 2.289 | 98 | 77.5 | 1435 | 21.87 | 5659.9 | 2966.8 | 2876.6 | 4245.8 | 1217.3 | 0.67879 | 6.074
2024-12-10 | 0:50 | Data | 0 | 32.379 | 30.502 | 195.54 | 7.64 | 184.051 | 2208.06 | 25.8 | 43.741 | 6.36 | 1.378 | 4.71 | 8703.03 | 2.147 | 98 | 77.4 | 1436 | 21.83 | 5657 | 2973.6 | 2903.5 | 4267.9 | 1217.3 | 0.68001 | 6.088
2024-12-10 | 0:50 | Data | 0 | 32.487 | 30.415 | 195.404 | 7.64 | 183.916 | 2208.97 | 25.81 | 43.2 | 6.37 | 1.377 | 4.711 | 8716.59 | 2.079 | 98 | 77.4 | 1435 | 21.6 | 5665.8 | 2963.6 | 2899.1 | 4266.1 | 1217.3 | 0.68037 | 6.088
2024-12-10 | 0:50 | Data | 0 | 32.379 | 30.408 | 195.54 | 7.64 | 184.006 | 2208.97 | 25.8 | 43.47 | 6.36 | 1.378 | 4.715 | 8703.03 | 2.079 | 98 | 77.4 | 1435 | 21.78 | 5657 | 2955.6 | 2939.2 | 4283.2 | 1217.3 | 0.67218 | 6.092
2024-12-10 | 0:50 | Data | 0 | 32.73 | 30.637 | 195.54 | 7.64 | 184.142 | 2206.25 | 25.8 | 43.47 | 6.37 | 1.372 | 4.702 | 8703.03 | 1.877 | 98 | 77.4 | 1434 | 21.74 | 5657 | 2951.4 | 2936.5 | 4273.4 | 1217.3 | 0.67257 | 6.074
2024-12-10 | 0:50 | Data | 0 | 32.339 | 30.198 | 195.45 | 7.63 | 184.051 | 2208.97 | 25.81 | 43.561 | 6.37 | 1.366 | 4.689 | 8703.03 | 1.958 | 98 | 77.4 | 1436 | 21.83 | 5657 | 2960.2 | 2922.2 | 4277 | 1217.3 | 0.67642 | 6.055
2024-12-10 | 0:50 | Data | 0 | 32.278 | 30.388 | 195.495 | 7.63 | 184.006 | 2208.97 | 25.81 | 43.561 | 6.36 | 1.376 | 4.688 | 8707.55 | 1.877 | 98 | 77.3 | 1436 | 21.74 | 5659.9 | 2975 | 2904.6 | 4270.6 | 1217.3 | 0.67927 | 6.063
2024-12-10 | 0:50 | Data | 0 | 32.696 | 30.442 | 195.54 | 7.63 | 184.096 | 2208.06 | 25.82 | 43.561 | 6.36 | 1.371 | 4.704 | 8716.59 | 2.248 | 98 | 77.4 | 1435 | 21.78 | 5665.8 | 2961.3 | 2907 | 4276.6 | 1217.3 | 0.6753 | 6.076
2024-12-10 | 0:50 | Data | 0 | 32.21 | 30.361 | 195.495 | 7.64 | 183.961 | 2213.49 | 25.8 | 43.47 | 6.36 | 1.372 | 4.693 | 8721.11 | 2.181 | 98 | 77.4 | 1439 | 21.74 | 5668.7 | 2958.6 | 2873.7 | 4236.1 | 1217.3 | 0.6822 | 6.065
2024-12-10 | 0:50 | Data | 0 | 32.825 | 30.475 | 195.676 | 7.64 | 184.142 | 2208.06 | 25.81 | 43.561 | 6.36 | 1.376 | 4.723 | 8703.03 | 2.248 | 98 | 77.4 | 1435 | 21.74 | 5657 | 2968.1 | 2890.5 | 4255.9 | 1217.3 | 0.68073 | 6.098
2024-12-10 | 0:50 | Data | 0 | 32.717 | 30.313 | 195.45 | 7.64 | 184.006 | 2206.25 | 25.8 | 43.561 | 6.36 | 1.369 | 4.725 | 8712.07 | 2.208 | 98 | 77.5 | 1433 | 21.78 | 5662.8 | 2952.7 | 2891.7 | 4230.5 | 1217.3 | 0.68062 | 6.094
2024-12-10 | 0:50 | Data | 0 | 32.46 | 30.415 | 195.45 | 7.64 | 184.051 | 2199.93 | 25.8 | 43.561 | 6.36 | 1.376 | 4.711 | 8703.03 | 2.073 | 98 | 77.4 | 1429 | 21.78 | 5657 | 2984.7 | 2873.6 | 4255.6 | 1217.3 | 0.68482 | 6.087
2024-12-10 | 0:50 | Data | 0 | 32.494 | 30.415 | 195.54 | 7.63 | 184.006 | 2208.06 | 25.81 | 43.47 | 6.37 | 1.385 | 4.704 | 8703.03 | 2.079 | 98 | 77.3 | 1436 | 21.78 | 5657 | 2960.4 | 2877.8 | 4243.6 | 1217.3 | 0.68139 | 6.089
2024-12-10 | 0:51 | Data | 0 | 32.44 | 30.388 | 195.45 | 7.64 | 184.006 | 2208.06 | 25.81 | 43.561 | 6.37 | 1.381 | 4.702 | 8703.03 | 2.12 | 98 | 77.3 | 1435 | 21.74 | 5657 | 2944.7 | 2901.2 | 4247.2 | 1217.3 | 0.67602 | 6.083
2024-12-10 | 0:51 | Data | 0 | 32.548 | 30.435 | 195.585 | 7.64 | 184.006 | 2208.06 | 25.8 | 43.561 | 6.36 | 1.38 | 4.695 | 8689.46 | 1.863 | 98 | 77.3 | 1435 | 21.74 | 5648.1 | 2947.1 | 2900.6 | 4248.3 | 1217.3 | 0.67636 | 6.075
2024-12-10 | 0:51 | Data | 0 | 32.379 | 30.394 | 195.495 | 7.64 | 184.006 | 2210.77 | 25.8 | 43.47 | 6.36 | 1.377 | 4.715 | 8721.11 | 1.884 | 98 | 77.4 | 1437 | 21.64 | 5668.7 | 2952.8 | 2931.6 | 4274.7 | 1217.4 | 0.67347 | 6.092
2024-12-10 | 0:51 | Data | 0 | 32.278 | 30.415 | 195.585 | 7.64 | 184.096 | 2212.58 | 25.8 | 43.561 | 6.36 | 1.374 | 4.724 | 8707.55 | 1.857 | 98 | 77.5 | 1438 | 21.78 | 5659.9 | 2959.2 | 2929.1 | 4279.4 | 1217.4 | 0.67453 | 6.098
2024-12-10 | 0:51 | Data | 0 | 32.494 | 30.361 | 195.45 | 7.63 | 183.961 | 2213.49 | 25.8 | 43.561 | 6.37 | 1.36 | 4.716 | 8693.98 | 2.187 | 98 | 77.6 | 1439 | 21.74 | 5651.1 | 2947.4 | 2898.4 | 4250.1 | 1217.4 | 0.67614 | 6.078
2024-12-10 | 0:51 | Data | 0 | 32.494 | 30.624 | 195.585 | 7.64 | 183.916 | 2216.2 | 25.8 | 43.561 | 6.36 | 1.358 | 4.698 | 8703.03 | 1.965 | 98 | 77.6 | 1441 | 21.74 | 5657 | 2959.3 | 2891.9 | 4250.8 | 1217.4 | 0.67938 | 6.057
2024-12-10 | 0:51 | Data | 0 | 32.278 | 30.185 | 195.45 | 7.63 | 184.006 | 2216.2 | 25.81 | 43.29 | 6.37 | 1.369 | 4.702 | 8689.46 | 2.079 | 98 | 77.4 | 1441 | 21.64 | 5648.1 | 2943.8 | 2866.1 | 4221.2 | 1217.4 | 0.6814 | 6.071
2024-12-10 | 0:51 | Data | 0 | 32.447 | 30.198 | 195.45 | 7.63 | 184.051 | 2216.2 | 25.81 | 43.47 | 6.36 | 1.375 | 4.724 | 8680.41 | 1.911 | 98 | 77.5 | 1441 | 21.78 | 5642.3 | 2956.1 | 2897.2 | 4253 | 1217.4 | 0.67774 | 6.099
2024-12-10 | 0:51 | Data | 0 | 32.46 | 30.361 | 195.404 | 7.64 | 183.961 | 2216.2 | 25.8 | 43.561 | 6.37 | 1.382 | 4.68 | 8671.37 | 2.181 | 98 | 77.2 | 1441 | 21.78 | 5636.4 | 2944.9 | 2882.1 | 4238 | 1217.4 | 0.67808 | 6.062
2024-12-10 | 0:51 | Data | 0 | 32.305 | 30.198 | 195.495 | 7.63 | 184.051 | 2216.2 | 25.81 | 43.651 | 6.36 | 1.366 | 4.683 | 8680.41 | 2.073 | 98 | 77.4 | 1441 | 21.78 | 5642.3 | 2957.4 | 2888.2 | 4249.7 | 1217.4 | 0.68146 | 6.049
2024-12-10 | 0:51 | Data | 0 | 32.48 | 30.415 | 195.631 | 7.64 | 184.051 | 2216.2 | 25.8 | 43.561 | 6.36 | 1.363 | 4.689 | 8671.37 | 2.194 | 98 | 77.5 | 1441 | 21.74 | 5636.4 | 2945 | 2882.8 | 4238.1 | 1217.4 | 0.67711 | 6.052
2024-12-10 | 0:51 | Data | 0 | 32.494 | 30.408 | 195.54 | 7.63 | 184.096 | 2218.91 | 25.8 | 43.47 | 6.36 | 1.374 | 4.682 | 8680.41 | 2.093 | 98 | 77.3 | 1442 | 21.78 | 5642.3 | 2968.4 | 2854 | 4233.2 | 1217.4 | 0.68458 | 6.055
2024-12-10 | 0:51 | Data | 0 | 32.494 | 30.212 | 195.495 | 7.64 | 184.051 | 2222.52 | 25.81 | 43.47 | 6.36 | 1.376 | 4.684 | 8689.46 | 2.194 | 98 | 77.3 | 1445 | 21.74 | 5648.1 | 2950.4 | 2886 | 4239.6 | 1217.4 | 0.67844 | 6.06
2024-12-10 | 0:51 | Data | 0 | 32.285 | 30.367 | 195.495 | 7.64 | 184.096 | 2221.62 | 25.81 | 43.561 | 6.36 | 1.367 | 4.705 | 8693.98 | 2.012 | 98 | 77.5 | 1444 | 21.78 | 5651.1 | 2947.5 | 2899 | 4249.7 | 1217.4 | 0.67602 | 6.072
2024-12-10 | 0:51 | Data | 0 | 32.298 | 30.401 | 195.45 | 7.63 | 184.051 | 2218.91 | 25.8 | 43.47 | 6.36 | 1.366 | 4.711 | 8693.98 | 2.025 | 98 | 77.5 | 1442 | 21.78 | 5651.1 | 2987.4 | 2905.4 | 4280.8 | 1217.4 | 0.68047 | 6.077
2024-12-10 | 0:51 | Data | 0 | 32.717 | 30.502 | 195.54 | 7.63 | 184.051 | 2222.52 | 25.81 | 43.561 | 6.36 | 1.374 | 4.707 | 8689.46 | 1.931 | 98 | 77.4 | 1445 | 21.78 | 5648.1 | 2952.6 | 2897.1 | 4249.3 | 1217.4 | 0.67522 | 6.081
2024-12-10 | 0:51 | Data | 0 | 32.649 | 30.448 | 195.495 | 7.64 | 184.096 | 2220.72 | 25.8 | 43.47 | 6.37 | 1.372 | 4.714 | 8712.07 | 2.106 | 98 | 77.5 | 1442 | 21.74 | 5662.8 | 2954.4 | 2887.3 | 4243.6 | 1217.4 | 0.67901 | 6.085
2024-12-10 | 0:52 | Data | 0 | 32.501 | 30.408 | 195.54 | 7.63 | 184.006 | 2222.52 | 25.8 | 43.47 | 6.36 | 1.37 | 4.724 | 8712.07 | 2.093 | 98 | 77.5 | 1445 | 21.78 | 5662.8 | 2947 | 2878.5 | 4233.8 | 1217.4 | 0.67904 | 6.094
2024-12-10 | 0:52 | Data | 0 | 32.845 | 30.435 | 195.585 | 7.63 | 184.142 | 2221.62 | 25.81 | 43.47 | 6.37 | 1.38 | 4.705 | 8703.03 | 2.005 | 98 | 77.3 | 1444 | 21.78 | 5657 | 2967.3 | 2872.7 | 4242.8 | 1217.4 | 0.68212 | 6.086
2024-12-10 | 0:52 | Data | 0 | 32.406 | 30.198 | 195.631 | 7.63 | 184.051 | 2222.52 | 25.81 | 43.922 | 6.37 | 1.371 | 4.701 | 8698.5 | 2.039 | 98 | 77.4 | 1444 | 22.01 | 5654 | 2955.7 | 2872.2 | 4241.3 | 1217.4 | 0.67958 | 6.071
2024-12-10 | 0:52 | Data | 0 | 32.339 | 30.313 | 195.585 | 7.64 | 184.096 | 2222.52 | 25.8 | 43.47 | 6.37 | 1.377 | 4.708 | 8721.11 | 1.958 | 98 | 77.4 | 1445 | 21.74 | 5668.7 | 2943.6 | 2850.3 | 4210.2 | 1217.4 | 0.68061 | 6.085
2024-12-10 | 0:52 | Data | 0 | 32.271 | 30.408 | 195.631 | 7.64 | 184.051 | 2215.29 | 25.81 | 43.47 | 6.36 | 1.377 | 4.686 | 8721.11 | 1.971 | 98 | 77.3 | 1440 | 21.78 | 5668.7 | 2954.9 | 2832.9 | 4216.4 | 1217.4 | 0.68531 | 6.064
2024-12-10 | 0:52 | Data | 0 | 32.629 | 30.225 | 195.54 | 7.63 | 184.096 | 2217.1 | 25.8 | 43.561 | 6.36 | 1.377 | 4.695 | 8305.07 | 2.106 | 98 | 77.3 | 1441 | 21.83 | 5398.3 | 2964.2 | 2862.8 | 4235.5 | 1217.4 | 0.68206 | 6.073
2024-12-10 | 0:52 | Data | 0 | 32.69 | 30.219 | 195.585 | 7.63 | 184.096 | 2213.49 | 25.8 | 43.561 | 6.36 | 1.371 | 4.725 | 8671.37 | 2.302 | 98 | 77.5 | 1438 | 21.83 | 5636.4 | 2972.4 | 2865.2 | 4237.9 | 1217.4 | 0.68249 | 6.095
2024-12-10 | 0:52 | Data | 0 | 32.69 | 30.469 | 195.631 | 7.64 | 184.142 | 2213.49 | 25.8 | 43.47 | 6.37 | 1.362 | 4.699 | 8662.33 | 2.248 | 98 | 77.5 | 1439 | 21.74 | 5630.5 | 2962.6 | 2855.7 | 4230.2 | 1217.4 | 0.68293 | 6.061
2024-12-10 | 0:52 | Data | 0 | 32.264 | 30.617 | 195.585 | 7.63 | 184.096 | 2214.39 | 25.81 | 43.561 | 6.37 | 1.377 | 4.704 | 8666.85 | 2.181 | 98 | 77.4 | 1439 | 21.78 | 5633.5 | 2975.8 | 2878.3 | 4253.8 | 1217.4 | 0.68026 | 6.081
2024-12-10 | 0:52 | Data | 0 | 32.264 | 30.3 | 195.585 | 7.64 | 184.051 | 2213.49 | 25.8 | 43.47 | 6.37 | 1.369 | 4.717 | 8671.37 | 2.255 | 98 | 77.5 | 1439 | 21.78 | 5636.4 | 2972.1 | 2890 | 4258.2 | 1217.4 | 0.68051 | 6.086
2024-12-10 | 0:52 | Data | 0 | 32.494 | 30.624 | 195.54 | 7.64 | 184.051 | 2213.49 | 25.8 | 43.561 | 6.37 | 1.365 | 4.711 | 8300.55 | 2.079 | 98 | 77.5 | 1439 | 21.78 | 5395.4 | 2961.8 | 2919.9 | 4266.9 | 1217.4 | 0.67542 | 6.076
2024-12-10 | 0:52 | Data | 0 | 32.507 | 30.631 | 195.45 | 7.64 | 184.142 | 2214.39 | 25.82 | 43.561 | 6.37 | 1.375 | 4.693 | 8250.8 | 1.877 | 98 | 77.4 | 1439 | 21.78 | 5363 | 2951.9 | 2908.9 | 4256.5 | 1217.4 | 0.6769 | 6.067
2024-12-10 | 0:52 | Data | 0 | 32.494 | 30.415 | 195.495 | 7.63 | 184.006 | 2214.39 | 25.8 | 43.561 | 6.36 | 1.378 | 4.697 | 8635.19 | 2.079 | 98 | 77.3 | 1439 | 21.78 | 5612.9 | 2948.7 | 2893.5 | 4244.1 | 1217.4 | 0.67756 | 6.076
2024-12-10 | 0:52 | Data | 0 | 32.494 | 30.401 | 195.45 | 7.63 | 184.051 | 2213.49 | 25.81 | 43.561 | 6.37 | 1.378 | 4.724 | 8662.33 | 1.931 | 98 | 77.4 | 1439 | 21.78 | 5630.5 | 2974 | 2899.5 | 4264.4 | 1217.4 | 0.68043 | 6.102
2024-12-10 | 0:52 | Data | 0 | 32.44 | 30.624 | 195.54 | 7.63 | 184.142 | 2217.1 | 25.81 | 43.561 | 6.37 | 1.377 | 4.703 | 8820.6 | 2.1 | 98 | 77.3 | 1441 | 21.83 | 5733.4 | 2969.5 | 2880.4 | 4251 | 1217.4 | 0.68115 | 6.081
2024-12-10 | 0:52 | Data | 0 | 32.831 | 30.651 | 195.631 | 7.64 | 184.142 | 2216.2 | 25.8 | 43.47 | 6.36 | 1.376 | 4.695 | 8902 | 2.268 | 98 | 77.3 | 1441 | 21.78 | 5786.3 | 2962.6 | 2872.1 | 4243.8 | 1217.4 | 0.67792 | 6.07
2024-12-10 | 0:52 | Data | 0 | 32.521 | 30.617 | 195.45 | 7.64 | 184.051 | 2213.49 | 25.8 | 43.561 | 6.36 | 1.376 | 4.704 | 8883.91 | 1.971 | 98 | 77.4 | 1439 | 21.74 | 5774.5 | 2971.9 | 2857.9 | 4235.5 | 1217.4 | 0.68534 | 6.08
2024-12-10 | 0:52 | Data | 0 | 32.494 | 30.3 | 195.54 | 7.64 | 184.096 | 2213.49 | 25.81 | 43.561 | 6.37 | 1.374 | 4.683 | 8883.91 | 2.086 | 98 | 77.3 | 1439 | 21.78 | 5774.5 | 2945.2 | 2879.6 | 4233.8 | 1217.4 | 0.67887 | 6.058
2024-12-10 | 0:53 | Data | 0 | 32.386 | 30.307 | 195.631 | 7.64 | 184.142 | 2215.29 | 25.81 | 43.561 | 6.37 | 1.37 | 4.685 | 8793.47 | 2.086 | 98 | 77.4 | 1441 | 21.83 | 5715.8 | 2959.9 | 2866 | 4238 | 1217.4 | 0.68068 | 6.055
2024-12-10 | 0:53 | Data | 0 | 32.278 | 30.361 | 195.404 | 7.63 | 184.006 | 2213.49 | 25.8 | 43.741 | 6.37 | 1.377 | 4.679 | 8703.03 | 1.958 | 98 | 77.3 | 1439 | 21.92 | 5657 | 2952.7 | 2907.3 | 4258.2 | 1217.4 | 0.6758 | 6.054
2024-12-10 | 0:53 | Data | 0 | 32.44 | 30.637 | 195.495 | 7.63 | 184.096 | 2211.68 | 25.8 | 43.47 | 6.37 | 1.371 | 4.711 | 8707.55 | 2.046 | 98 | 77.5 | 1438 | 21.74 | 5659.9 | 2959 | 2899.9 | 4256.2 | 1217.4 | 0.67762 | 6.082
2024-12-10 | 0:53 | Data | 0 | 32.447 | 30.367 | 195.585 | 7.64 | 184.096 | 2208.06 | 25.81 | 43.561 | 6.37 | 1.379 | 4.734 | 8693.98 | 2.039 | 98 | 77.4 | 1436 | 21.78 | 5651.1 | 2963.5 | 2884.9 | 4246 | 1217.5 | 0.67981 | 6.113
2024-12-10 | 0:53 | Data | 0 | 32.71 | 30.428 | 195.585 | 7.64 | 184.096 | 2213.49 | 25.81 | 43.47 | 6.37 | 1.373 | 4.664 | 8707.55 | 2.282 | 98 | 77.3 | 1439 | 21.74 | 5659.9 | 2956.4 | 2896.9 | 4253.3 | 1217.5 | 0.67726 | 6.037
2024-12-10 | 0:53 | Data | 0 | 32.494 | 30.246 | 195.495 | 7.63 | 184.096 | 2214.39 | 25.81 | 43.561 | 6.37 | 1.367 | 4.683 | 8662.33 | 2.194 | 98 | 77.4 | 1439 | 21.78 | 5630.5 | 2959.6 | 2930 | 4277.1 | 1217.5 | 0.67504 | 6.05
2024-12-10 | 0:53 | Data | 0 | 32.609 | 30.313 | 195.631 | 7.64 | 184.142 | 2210.77 | 25.8 | 43.47 | 6.37 | 1.375 | 4.708 | 8680.41 | 2.194 | 98 | 77.4 | 1438 | 21.74 | 5642.3 | 2960.7 | 2907.8 | 4257.3 | 1217.5 | 0.67892 | 6.083
2024-12-10 | 0:53 | Data | 0 | 32.494 | 30.307 | 195.495 | 7.64 | 184.006 | 2213.49 | 25.81 | 43.561 | 6.37 | 1.369 | 4.715 | 8666.85 | 2.214 | 98 | 77.5 | 1439 | 21.78 | 5633.5 | 2964.8 | 2909.8 | 4265.6 | 1217.5 | 0.67906 | 6.084
2024-12-10 | 0:53 | Data | 0 | 32.494 | 30.691 | 195.585 | 7.63 | 184.142 | 2218 | 25.8 | 43.47 | 6.36 | 1.373 | 4.687 | 8680.41 | 2.086 | 98 | 77.4 | 1442 | 21.74 | 5642.3 | 2957.2 | 2867.7 | 4233.2 | 1217.5 | 0.68141 | 6.059
2024-12-10 | 0:53 | Data | 0 | 32.777 | 30.334 | 195.631 | 7.64 | 184.187 | 2218.91 | 25.8 | 43.47 | 6.37 | 1.387 | 4.699 | 8666.85 | 2.14 | 98 | 77.2 | 1442 | 21.78 | 5633.5 | 2942.6 | 2885.2 | 4239.7 | 1217.5 | 0.67624 | 6.085
2024-12-10 | 0:53 | Data | 0 | 32.494 | 30.307 | 195.631 | 7.64 | 183.961 | 2220.72 | 25.81 | 43.47 | 6.37 | 1.376 | 4.691 | 8653.28 | 2.181 | 98 | 77.3 | 1442 | 21.78 | 5624.6 | 2954 | 2889.9 | 4250.2 | 1217.5 | 0.67756 | 6.066
2024-12-10 | 0:53 | Data | 0 | 32.777 | 30.428 | 195.585 | 7.63 | 184.187 | 2218.91 | 25.82 | 43.561 | 6.37 | 1.374 | 4.699 | 8662.33 | 1.965 | 98 | 77.4 | 1442 | 21.78 | 5630.5 | 2958.6 | 2894 | 4251.3 | 1217.5 | 0.68004 | 6.072
2024-12-10 | 0:53 | Data | 0 | 32.501 | 30.469 | 195.676 | 7.64 | 184.096 | 2213.49 | 25.81 | 43.561 | 6.37 | 1.366 | 4.698 | 8644.24 | 1.87 | 98 | 77.5 | 1438 | 21.78 | 5618.8 | 2975.6 | 2861 | 4250.7 | 1217.5 | 0.68571 | 6.063
2024-12-10 | 0:53 | Data | 0 | 32.595 | 30.469 | 195.585 | 7.64 | 184.006 | 2213.49 | 25.81 | 43.561 | 6.37 | 1.359 | 4.718 | 8856.78 | 1.998 | 98 | 77.6 | 1439 | 21.78 | 5756.9 | 2954.9 | 2879.7 | 4245.2 | 1217.5 | 0.67813 | 6.077
2024-12-10 | 0:53 | Data | 0 | 32.494 | 30.219 | 195.585 | 7.64 | 184.096 | 2214.39 | 25.8 | 43.561 | 6.36 | 1.374 | 4.707 | 8856.78 | 2.241 | 98 | 77.4 | 1439 | 21.78 | 5756.9 | 2958 | 2910.4 | 4266.3 | 1217.5 | 0.67542 | 6.081
2024-12-10 | 0:53 | Data | 0 | 32.723 | 30.428 | 195.676 | 7.64 | 184.142 | 2213.49 | 25.8 | 43.561 | 6.37 | 1.386 | 4.703 | 8834.17 | 2.093 | 98 | 77.2 | 1439 | 21.78 | 5742.2 | 2984.1 | 2882.1 | 4263.5 | 1217.5 | 0.68326 | 6.09
2024-12-10 | 0:53 | Data | 0 | 32.278 | 30.523 | 195.45 | 7.63 | 184.142 | 2218.91 | 25.81 | 43.47 | 6.37 | 1.369 | 4.709 | 8838.69 | 1.911 | 98 | 77.5 | 1442 | 21.74 | 5745.1 | 2947.1 | 2917 | 4262 | 1217.5 | 0.67574 | 6.078
2024-12-10 | 0:53 | Data | 0 | 32.494 | 30.442 | 195.45 | 7.64 | 184.051 | 2114.97 | 25.81 | 43.561 | 6.37 | 1.373 | 4.71 | 8666.85 | 2.086 | 97.9 | 77.4 | 1375 | 21.78 | 5633.5 | 2968.1 | 2897.1 | 4261.1 | 1217.5 | 0.6786 | 6.083
2024-12-10 | 0:54 | Data | 0 | 32.379 | 30.84 | 195.631 | 7.63 | 184.096 | 2221.62 | 25.8 | 43.561 | 6.37 | 1.371 | 4.705 | 8684.94 | 1.978 | 98 | 77.4 | 1445 | 21.83 | 5645.2 | 2940.5 | 2887.6 | 4238.8 | 1217.5 | 0.67638 | 6.077
2024-12-10 | 0:54 | Data | 0 | 32.494 | 30.705 | 195.495 | 7.63 | 184.051 | 2225.23 | 25.8 | 43.561 | 6.37 | 1.367 | 4.686 | 8689.46 | 2.079 | 98 | 77.4 | 1446 | 21.74 | 5648.1 | 2963.4 | 2901.9 | 4259.1 | 1217.5 | 0.67948 | 6.053
2024-12-10 | 0:54 | Data | 0 | 32.669 | 30.428 | 195.495 | 7.64 | 184.096 | 2223.43 | 25.8 | 43.561 | 6.37 | 1.369 | 4.692 | 8707.55 | 2.289 | 98 | 77.4 | 1445 | 21.74 | 5659.9 | 2957 | 2884.2 | 4243.3 | 1217.5 | 0.68027 | 6.061
2024-12-10 | 0:54 | Data | 0 | 32.696 | 30.637 | 195.585 | 7.64 | 184.142 | 2225.23 | 25.81 | 43.561 | 6.37 | 1.376 | 4.707 | 8680.41 | 2.079 | 98 | 77.4 | 1446 | 21.78 | 5642.3 | 2981.6 | 2879.5 | 4255.9 | 1217.5 | 0.6834 | 6.083
2024-12-10 | 0:54 | Data | 0 | 32.548 | 30.415 | 195.585 | 7.64 | 184.051 | 2221.62 | 25.8 | 43.561 | 6.37 | 1.379 | 4.689 | 8707.55 | 1.884 | 98 | 77.3 | 1444 | 21.74 | 5659.9 | 2972.3 | 2898.9 | 4267.9 | 1217.5 | 0.67856 | 6.068
2024-12-10 | 0:54 | Data | 0 | 32.663 | 30.421 | 195.495 | 7.64 | 184.051 | 2218 | 25.81 | 43.561 | 6.36 | 1.378 | 4.725 | 8689.46 | 2.289 | 98 | 77.4 | 1442 | 21.74 | 5648.1 | 2965 | 2894.2 | 4257.8 | 1217.5 | 0.67907 | 6.104
2024-12-10 | 0:54 | Data | 0 | 32.494 | 30.415 | 195.585 | 7.64 | 184.051 | 2224.33 | 25.8 | 43.47 | 6.36 | 1.382 | 4.694 | 8671.37 | 2.079 | 98 | 77.3 | 1446 | 21.74 | 5636.4 | 2946.4 | 2840.1 | 4180.9 | 1217.5 | 0.69169 | 6.077
2024-12-10 | 0:54 | Data | 0 | 32.494 | 30.367 | 195.495 | 7.64 | 184.006 | 2227.95 | 25.8 | 43.47 | 6.37 | 1.371 | 4.706 | 8703.03 | 2.181 | 98 | 77.5 | 1448 | 21.78 | 5657 | 2948.8 | 2859.7 | 4223.4 | 1217.5 | 0.68075 | 6.076
2024-12-10 | 0:54 | Data | 0 | 32.359 | 30.198 | 195.45 | 7.63 | 184.096 | 2227.95 | 25.8 | 43.651 | 6.37 | 1.376 | 4.688 | 8703.03 | 2.066 | 98 | 77.3 | 1448 | 21.78 | 5657 | 2974.3 | 2896.7 | 4261.4 | 1217.5 | 0.68176 | 6.064
2024-12-10 | 0:54 | Data | 0 | 32.285 | 30.408 | 195.585 | 7.63 | 184.051 | 2227.04 | 25.8 | 43.651 | 6.37 | 1.381 | 4.695 | 8716.59 | 1.911 | 98 | 77.3 | 1448 | 21.78 | 5665.8 | 2989.7 | 2860.9 | 4252.4 | 1217.5 | 0.68561 | 6.076
2024-12-10 | 0:54 | Data | 0 | 32.271 | 30.219 | 195.495 | 7.64 | 184.051 | 2225.23 | 25.8 | 43.47 | 6.36 | 1.367 | 4.714 | 8712.07 | 2.221 | 98 | 77.5 | 1446 | 21.74 | 5662.8 | 2958.1 | 2872.6 | 4236.4 | 1217.5 | 0.68213 | 6.08
2024-12-10 | 0:54 | Data | 0 | 32.467 | 30.415 | 195.45 | 7.64 | 184.051 | 2230.66 | 25.8 | 43.561 | 6.37 | 1.381 | 4.731 | 8716.59 | 2.066 | 98 | 77.4 | 1450 | 21.78 | 5665.8 | 2960.6 | 2891.9 | 4251.8 | 1217.5 | 0.67959 | 6.112
2024-12-10 | 0:54 | Data | 0 | 32.494 | 30.644 | 195.631 | 7.64 | 184.051 | 2224.33 | 25.81 | 43.561 | 6.37 | 1.369 | 4.731 | 8703.03 | 2.019 | 98 | 77.6 | 1446 | 21.78 | 5657 | 2921.6 | 2861.3 | 4204.1 | 1217.5 | 0.67796 | 6.102
2024-12-10 | 0:54 | Data | 0 | 32.291 | 30.408 | 195.495 | 7.64 | 184.006 | 2229.75 | 25.8 | 43.561 | 6.37 | 1.367 | 4.692 | 8707.55 | 1.87 | 98.1 | 77.4 | 1450 | 21.74 | 5659.9 | 2950.4 | 2883.8 | 4234.6 | 1217.5 | 0.67538 | 6.059
2024-12-10 | 0:54 | Data | 0 | 32.494 | 30.415 | 195.585 | 7.63 | 184.051 | 2222.52 | 25.81 | 43.561 | 6.36 | 1.374 | 4.714 | 8712.07 | 2.079 | 98 | 77.4 | 1445 | 21.78 | 5662.8 | 2935.5 | 2870 | 4217.9 | 1217.5 | 0.67532 | 6.089
2024-12-10 | 0:54 | Data | 0 | 32.494 | 30.536 | 195.585 | 7.64 | 184.051 | 2218.91 | 25.83 | 43.47 | 6.37 | 1.377 | 4.723 | 8716.59 | 2.079 | 98.1 | 77.4 | 1442 | 21.64 | 5665.8 | 2973.2 | 2878.6 | 4253.4 | 1217.5 | 0.68231 | 6.101
2024-12-10 | 0:54 | Data | 0 | 32.595 | 30.415 | 195.631 | 7.64 | 184.142 | 2218.91 | 25.81 | 43.561 | 6.36 | 1.37 | 4.706 | 8730.16 | 2.086 | 98 | 77.5 | 1443 | 21.78 | 5674.6 | 2973.7 | 2892.6 | 4259.7 | 1217.5 | 0.681 | 6.076
2024-12-10 | 0:54 | Data | 0 | 32.44 | 30.59 | 195.676 | 7.64 | 184.096 | 2218.91 | 25.81 | 43.561 | 6.36 | 1.364 | 4.671 | 8730.16 | 2.059 | 98 | 77.4 | 1443 | 21.74 | 5674.6 | 2986.6 | 2893.3 | 4271.4 | 1217.5 | 0.68238 | 6.035
2024-12-10 | 0:55 | Data | 0 | 32.696 | 30.442 | 195.992 | 7.64 | 184.593 | 2218.91 | 25.8 | 43.561 | 6.36 | 1.365 | 4.65 | 8730.16 | 2.181 | 98 | 77.3 | 1442 | 21.78 | 5674.6 | 2953.2 | 2898.7 | 4254.4 | 1217.5 | 0.67727 | 6.015
2024-12-10 | 0:55 | Data | 0 | 32.906 | 30.664 | 196.173 | 7.64 | 184.684 | 2218.91 | 25.8 | 43.47 | 6.36 | 1.371 | 4.71 | 8730.16 | 2.113 | 98 | 77.5 | 1442 | 21.74 | 5674.6 | 2979.5 | 2930.4 | 4291.1 | 1217.5 | 0.68136 | 6.08
2024-12-10 | 0:55 | Data | 0 | 32.548 | 30.415 | 196.173 | 7.63 | 184.593 | 2218.91 | 25.8 | 43.47 | 6.37 | 1.367 | 4.72 | 8716.59 | 2.086 | 98 | 77.5 | 1442 | 21.74 | 5665.8 | 2972 | 2910.2 | 4271 | 1217.5 | 0.68003 | 6.086
2024-12-10 | 0:55 | Data | 0 | 32.555 | 30.597 | 196.128 | 7.63 | 184.593 | 2218 | 25.81 | 43.561 | 6.37 | 1.377 | 4.686 | 8721.11 | 1.911 | 98 | 77.3 | 1442 | 21.78 | 5668.7 | 2958.2 | 2897.5 | 4257 | 1217.6 | 0.68009 | 6.063
2024-12-10 | 0:55 | Data | 0 | 32.494 | 30.3 | 196.083 | 7.63 | 184.639 | 2218.91 | 25.8 | 43.561 | 6.37 | 1.377 | 4.702 | 8703.03 | 2.133 | 98 | 77.3 | 1442 | 21.78 | 5657 | 2956 | 2920.8 | 4270.9 | 1217.6 | 0.67588 | 6.079
2024-12-10 | 0:55 | Data | 0 | 32.636 | 30.421 | 196.219 | 7.63 | 184.729 | 2218.91 | 25.81 | 43.47 | 6.36 | 1.377 | 4.712 | 8716.59 | 2.079 | 98 | 77.4 | 1442 | 21.74 | 5665.8 | 2979.8 | 2922.8 | 4282.3 | 1217.6 | 0.67901 | 6.09
2024-12-10 | 0:55 | Data | 0 | 32.494 | 30.428 | 196.128 | 7.64 | 184.639 | 2221.62 | 25.81 | 43.561 | 6.37 | 1.369 | 4.693 | 8693.98 | 2.241 | 98 | 77.4 | 1443 | 21.78 | 5651.1 | 2960 | 2938.4 | 4282.4 | 1217.6 | 0.67356 | 6.063
2024-12-10 | 0:55 | Data | 0 | 32.548 | 30.252 | 195.992 | 7.64 | 184.548 | 2222.52 | 25.8 | 43.47 | 6.37 | 1.361 | 4.679 | 8693.98 | 2.14 | 98 | 77.5 | 1444 | 21.74 | 5651.1 | 2943.3 | 2923.3 | 4264.3 | 1217.6 | 0.67209 | 6.039
2024-12-10 | 0:55 | Data | 0 | 32.723 | 30.475 | 195.992 | 7.63 | 184.639 | 2216.2 | 25.81 | 43.561 | 6.37 | 1.358 | 4.717 | 8689.46 | 2.019 | 98 | 77.6 | 1441 | 21.78 | 5648.1 | 2980.6 | 2945.5 | 4302.1 | 1217.6 | 0.67377 | 6.075
2024-12-10 | 0:55 | Data | 0 | 32.696 | 30.644 | 196.219 | 7.64 | 184.729 | 2214.39 | 25.81 | 43.561 | 6.36 | 1.37 | 4.735 | 8689.46 | 2.079 | 98 | 77.6 | 1439 | 21.78 | 5648.1 | 2950.1 | 2923.5 | 4266 | 1217.6 | 0.67403 | 6.105
2024-12-10 | 0:55 | Data | 0 | 32.487 | 30.415 | 196.083 | 7.64 | 184.503 | 2211.68 | 25.8 | 43.561 | 6.37 | 1.371 | 4.735 | 8703.03 | 2.079 | 98 | 77.5 | 1437 | 21.83 | 5657 | 2976.2 | 2916.5 | 4279.3 | 1217.6 | 0.67867 | 6.106
2024-12-10 | 0:55 | Data | 0 | 32.406 | 30.691 | 196.219 | 7.63 | 184.639 | 2206.25 | 25.81 | 43.561 | 6.37 | 1.38 | 4.727 | 8693.98 | 2.167 | 98 | 77.4 | 1434 | 21.74 | 5651.1 | 2949.9 | 2902.6 | 4249.9 | 1217.6 | 0.67707 | 6.108
2024-12-10 | 0:55 | Data | 0 | 32.278 | 30.198 | 195.992 | 7.63 | 184.639 | 2213.49 | 25.8 | 43.561 | 6.37 | 1.381 | 4.704 | 8707.55 | 2.052 | 98 | 77.3 | 1439 | 21.78 | 5659.9 | 2962.5 | 2920 | 4262.3 | 1217.6 | 0.67561 | 6.084
2024-12-10 | 0:55 | Data | 0 | 32.413 | 30.415 | 196.083 | 7.63 | 184.684 | 2214.39 | 25.82 | 43.651 | 6.36 | 1.385 | 4.748 | 8730.16 | 2.066 | 98 | 77.4 | 1439 | 21.78 | 5674.6 | 2970.1 | 2880.4 | 4259.7 | 1217.6 | 0.68022 | 6.134
2024-12-10 | 0:55 | Data | 0 | 32.919 | 30.752 | 196.264 | 7.63 | 184.684 | 2210.77 | 25.8 | 43.47 | 6.37 | 1.378 | 4.746 | 8730.16 | 1.985 | 98 | 77.5 | 1438 | 21.74 | 5674.6 | 2975.5 | 2905.3 | 4266.9 | 1217.6 | 0.68127 | 6.123
2024-12-10 | 0:55 | Data | 0 | 32.494 | 30.442 | 196.128 | 7.64 | 184.639 | 2210.77 | 25.81 | 43.561 | 6.37 | 1.374 | 4.741 | 8730.16 | 1.884 | 98 | 77.5 | 1437 | 21.78 | 5674.6 | 2953.7 | 2900.9 | 4255.2 | 1217.6 | 0.67691 | 6.115
2024-12-10 | 0:55 | Data | 0 | 32.723 | 30.428 | 196.219 | 7.63 | 184.729 | 2213.49 | 25.81 | 43.561 | 6.37 | 1.375 | 4.723 | 8734.68 | 2.093 | 98 | 77.4 | 1439 | 21.78 | 5677.5 | 2963.1 | 2894.3 | 4254 | 1217.6 | 0.67914 | 6.099
2024-12-10 | 0:56 | Data | 0 | 32.271 | 30.415 | 196.173 | 7.64 | 184.639 | 2261.39 | 25.8 | 43.561 | 6.37 | 1.367 | 4.718 | 8734.68 | 2.052 | 98.1 | 77.5 | 1470 | 21.78 | 5677.5 | 2953.4 | 2918.5 | 4263.5 | 1217.6 | 0.67616 | 6.085
2024-12-10 | 0:56 | Data | 0 | 32.494 | 30.529 | 196.264 | 7.64 | 184.684 | 2271.33 | 25.8 | 43.109 | 6.37 | 1.367 | 4.737 | 8716.59 | 2.167 | 98.1 | 77.6 | 1476 | 21.6 | 5665.8 | 2982.8 | 2933.8 | 4297.7 | 1217.6 | 0.67598 | 6.105
2024-12-10 | 0:56 | Data | 0 | 32.865 | 30.34 | 196.128 | 7.64 | 184.548 | 2261.39 | 25.81 | 43.561 | 6.37 | 1.375 | 4.721 | 8707.55 | 2.275 | 98.1 | 77.4 | 1470 | 21.74 | 5659.9 | 2970.8 | 2910.6 | 4270.9 | 1217.6 | 0.6792 | 6.095
2024-12-10 | 0:56 | Data | 0 | 32.501 | 30.415 | 196.173 | 7.63 | 184.593 | 2270.43 | 25.81 | 43.561 | 6.37 | 1.377 | 4.721 | 8703.03 | 2.079 | 98.1 | 77.4 | 1476 | 21.78 | 5657 | 2960.8 | 2925 | 4274.8 | 1217.6 | 0.67564 | 6.099
2024-12-10 | 0:56 | Data | 0 | 32.48 | 30.691 | 196.128 | 7.64 | 184.548 | 2221.62 | 25.81 | 43.47 | 6.37 | 1.369 | 4.697 | 8721.11 | 2.012 | 98 | 77.4 | 1443 | 21.74 | 5668.7 | 2959.3 | 2924.6 | 4275.6 | 1217.6 | 0.67581 | 6.066
2024-12-10 | 0:56 | Data | 0 | 32.379 | 30.415 | 196.128 | 7.63 | 184.639 | 2218 | 25.81 | 43.2 | 6.37 | 1.377 | 4.707 | 8730.16 | 2.039 | 98.1 | 77.4 | 1442 | 21.6 | 5674.6 | 2957.8 | 2900.4 | 4257.7 | 1217.6 | 0.67717 | 6.084
2024-12-10 | 0:56 | Data | 0 | 32.264 | 30.617 | 196.173 | 7.64 | 184.593 | 2213.49 | 25.8 | 43.2 | 6.38 | 1.377 | 4.737 | 8734.68 | 1.978 | 98 | 77.5 | 1439 | 21.64 | 5677.5 | 2951.3 | 2897.8 | 4251.4 | 1217.6 | 0.67802 | 6.112
2024-12-10 | 0:56 | Data | 0 | 32.582 | 30.644 | 196.219 | 7.63 | 184.729 | 2213.49 | 25.8 | 43.561 | 6.37 | 1.377 | 4.763 | 8739.2 | 2.194 | 98 | 77.6 | 1439 | 21.74 | 5680.5 | 2973.3 | 2907.8 | 4271.5 | 1217.6 | 0.67884 | 6.14
2024-12-10 | 0:56 | Data | 0 | 32.298 | 30.361 | 196.173 | 7.63 | 184.639 | 2213.49 | 25.81 | 43.47 | 6.37 | 1.376 | 4.711 | 8730.16 | 2.086 | 98 | 77.4 | 1439 | 21.74 | 5674.6 | 2968.4 | 2870 | 4240.3 | 1217.6 | 0.68297 | 6.086
2024-12-10 | 0:56 | Data | 0 | 32.696 | 30.529 | 196.219 | 7.64 | 184.639 | 2210.77 | 25.8 | 43.2 | 6.37 | 1.375 | 4.683 | 8770.86 | 2.066 | 98 | 77.3 | 1437 | 21.64 | 5701.1 | 2954.4 | 2858.9 | 4227.6 | 1217.6 | 0.68173 | 6.056
2024-12-10 | 0:56 | Data | 0 | 32.609 | 30.415 | 196.173 | 7.64 | 184.639 | 2212.58 | 25.8 | 43.47 | 6.37 | 1.365 | 4.723 | 8757.29 | 2.093 | 98 | 77.6 | 1438 | 21.74 | 5692.2 | 2952.8 | 2908.3 | 4258.4 | 1217.6 | 0.67632 | 6.088
2024-12-10 | 0:56 | Data | 0 | 32.561 | 30.361 | 196.173 | 7.64 | 184.774 | 2214.39 | 25.81 | 43.561 | 6.37 | 1.367 | 4.72 | 8757.29 | 2.032 | 98 | 77.5 | 1439 | 21.78 | 5692.2 | 2965.9 | 2891.8 | 4257.3 | 1217.6 | 0.67937 | 6.088
2024-12-10 | 0:56 | Data | 0 | 32.298 | 30.367 | 196.173 | 7.64 | 184.684 | 2218.91 | 25.8 | 43.29 | 6.36 | 1.377 | 4.714 | 8743.73 | 2.019 | 98.1 | 77.4 | 1442 | 21.64 | 5683.4 | 2943.1 | 2901.1 | 4253.4 | 1217.6 | 0.67732 | 6.091
2024-12-10 | 0:56 | Data | 0 | 32.332 | 30.3 | 196.083 | 7.63 | 184.684 | 2213.49 | 25.8 | 43.47 | 6.37 | 1.374 | 4.704 | 8743.73 | 1.857 | 98 | 77.4 | 1439 | 21.83 | 5683.4 | 2942.2 | 2893.4 | 4240.6 | 1217.6 | 0.6777 | 6.077
2024-12-10 | 0:56 | Data | 0 | 32.602 | 30.536 | 196.128 | 7.64 | 184.639 | 2216.2 | 25.81 | 43.109 | 6.37 | 1.377 | 4.715 | 8752.77 | 1.971 | 98.1 | 77.4 | 1441 | 21.6 | 5689.3 | 2944.3 | 2938.7 | 4279.9 | 1217.6 | 0.66909 | 6.092
2024-12-10 | 0:56 | Data | 0 | 32.717 | 30.597 | 196.219 | 7.63 | 184.684 | 2221.62 | 25.81 | 43.2 | 6.37 | 1.366 | 4.734 | 8743.73 | 2.005 | 98.1 | 77.6 | 1444 | 21.6 | 5683.4 | 2965.5 | 2908.7 | 4262.9 | 1217.6 | 0.6775 | 6.1
2024-12-10 | 0:56 | Data | 0 | 32.582 | 30.739 | 195.992 | 7.64 | 184.639 | 2222.52 | 25.81 | 43.109 | 6.37 | 1.369 | 4.71 | 8730.16 | 1.917 | 98.1 | 77.5 | 1445 | 21.55 | 5674.6 | 2972 | 2933.7 | 4289 | 1217.6 | 0.67593 | 6.079
2024-12-10 | 0:56 | Data | 0 | 32.528 | 30.59 | 196.219 | 7.64 | 184.639 | 2218.91 | 25.81 | 43.561 | 6.37 | 1.378 | 4.703 | 8730.16 | 1.911 | 98 | 77.3 | 1442 | 21.74 | 5674.6 | 2977.7 | 2889.4 | 4265.8 | 1217.6 | 0.67973 | 6.082
2024-12-10 | 0:57 | Data | 0 | 32.44 | 30.583 | 196.128 | 7.63 | 184.639 | 2227.95 | 25.81 | 43.2 | 6.37 | 1.37 | 4.706 | 8721.11 | 2.073 | 98.1 | 77.5 | 1448 | 21.64 | 5668.7 | 2953.4 | 2890.1 | 4246.8 | 1217.6 | 0.67863 | 6.076
2024-12-10 | 0:57 | Data | 0 | 32.44 | 30.415 | 196.083 | 7.63 | 184.593 | 2227.95 | 25.8 | 43.109 | 6.37 | 1.369 | 4.692 | 8721.11 | 2.073 | 98.1 | 77.4 | 1448 | 21.6 | 5668.7 | 2953.2 | 2890.5 | 4249.7 | 1217.6 | 0.67862 | 6.062
2024-12-10 | 0:57 | Data | 0 | 32.494 | 30.644 | 196.128 | 7.64 | 184.593 | 2227.04 | 25.81 | 43.2 | 6.37 | 1.383 | 4.737 | 8716.59 | 2.032 | 98.1 | 77.4 | 1448 | 21.6 | 5665.8 | 2964.4 | 2900.5 | 4262.6 | 1217.6 | 0.67878 | 6.12
2024-12-10 | 0:57 | Data | 0 | 32.609 | 30.428 | 196.128 | 7.64 | 184.593 | 2225.23 | 25.8 | 43.47 | 6.37 | 1.38 | 4.714 | 8730.16 | 2.187 | 98 | 77.4 | 1446 | 21.74 | 5674.6 | 2961.4 | 2888.9 | 4253.9 | 1217.6 | 0.67953 | 6.094
2024-12-10 | 0:57 | Data | 0 | 32.771 | 30.374 | 196.173 | 7.64 | 184.774 | 2224.33 | 25.8 | 43.47 | 6.37 | 1.375 | 4.717 | 8716.59 | 2.079 | 98 | 77.4 | 1446 | 21.74 | 5665.8 | 2949 | 2895.5 | 4245.9 | 1217.7 | 0.6805 | 6.092
2024-12-10 | 0:57 | Data | 0 | 32.278 | 30.415 | 196.219 | 7.63 | 184.593 | 2225.23 | 25.81 | 43.47 | 6.37 | 1.371 | 4.721 | 8716.59 | 2.025 | 98 | 77.5 | 1446 | 21.78 | 5665.8 | 2952.9 | 2901.6 | 4256.9 | 1217.7 | 0.67735 | 6.092
2024-12-10 | 0:57 | Data | 0 | 32.71 | 30.644 | 196.219 | 7.63 | 184.639 | 2225.23 | 25.8 | 43.561 | 6.37 | 1.377 | 4.732 | 8716.59 | 2.079 | 98 | 77.5 | 1446 | 21.74 | 5665.8 | 2963.4 | 2903.3 | 4260.3 | 1217.7 | 0.67908 | 6.11
2024-12-10 | 0:57 | Data | 0 | 32.48 | 30.415 | 195.947 | 7.64 | 184.548 | 2221.62 | 25.8 | 43.561 | 6.37 | 1.378 | 4.721 | 8721.11 | 2.086 | 98 | 77.4 | 1444 | 21.83 | 5668.7 | 2961.1 | 2914 | 4269.1 | 1217.7 | 0.67703 | 6.101
2024-12-10 | 0:57 | Data | 0 | 32.696 | 30.428 | 196.083 | 7.64 | 184.593 | 2222.52 | 25.8 | 43.47 | 6.37 | 1.385 | 4.724 | 8264.37 | 2.059 | 98 | 77.3 | 1445 | 21.74 | 5371.8 | 2980.8 | 2915.3 | 4277.8 | 1217.7 | 0.67995 | 6.107
2024-12-10 | 0:57 | Data | 0 | 32.285 | 30.415 | 196.128 | 7.64 | 184.593 | 2215.29 | 25.8 | 43.561 | 6.37 | 1.382 | 4.703 | 8689.46 | 1.857 | 98 | 77.3 | 1441 | 21.78 | 5648.1 | 2974.8 | 2936.7 | 4289.4 | 1217.7 | 0.67572 | 6.085
2024-12-10 | 0:57 | Data | 0 | 32.501 | 30.523 | 196.083 | 7.63 | 184.593 | 2221.62 | 25.81 | 43.29 | 6.36 | 1.371 | 4.71 | 8666.85 | 2.1 | 98.1 | 77.5 | 1443 | 21.64 | 5633.5 | 2947.8 | 2929.6 | 4269 | 1217.7 | 0.67414 | 6.081
2024-12-10 | 0:57 | Data | 0 | 32.676 | 30.766 | 196.309 | 7.64 | 184.684 | 2222.52 | 25.81 | 43.2 | 6.36 | 1.356 | 4.715 | 8693.98 | 2.073 | 98.1 | 77.7 | 1445 | 21.64 | 5651.1 | 2976.1 | 2924.8 | 4283.7 | 1217.7 | 0.67542 | 6.071
2024-12-10 | 0:57 | Data | 0 | 32.521 | 30.705 | 196.264 | 7.63 | 184.593 | 2222.52 | 25.8 | 43.2 | 6.37 | 1.359 | 4.705 | 8734.68 | 1.958 | 98.1 | 77.6 | 1445 | 21.6 | 5677.5 | 2964.3 | 2896.9 | 4260.3 | 1217.7 | 0.67815 | 6.064
2024-12-10 | 0:57 | Data | 0 | 32.413 | 30.415 | 196.173 | 7.64 | 184.684 | 2222.52 | 25.8 | 43.2 | 6.37 | 1.377 | 4.702 | 8703.03 | 1.87 | 98.1 | 77.3 | 1445 | 21.6 | 5657 | 2970.4 | 2891.4 | 4260.9 | 1217.7 | 0.68051 | 6.08
2024-12-10 | 0:57 | Data | 0 | 32.717 | 30.664 | 196.309 | 7.64 | 184.684 | 2222.52 | 25.8 | 43.2 | 6.37 | 1.373 | 4.683 | 8703.03 | 2.019 | 98.1 | 77.3 | 1445 | 21.6 | 5657 | 2961.8 | 2900.2 | 4259.3 | 1217.7 | 0.67874 | 6.057
2024-12-10 | 0:57 | Data | 0 | 32.825 | 30.651 | 196.173 | 7.64 | 184.684 | 2222.52 | 25.8 | 43.2 | 6.37 | 1.373 | 4.705 | 8680.41 | 2.093 | 98.1 | 77.4 | 1445 | 21.6 | 5642.3 | 2973.9 | 2890.4 | 4264.3 | 1217.7 | 0.67984 | 6.077
2024-12-10 | 0:57 | Data | 0 | 32.831 | 30.664 | 196.354 | 7.64 | 184.729 | 2218.91 | 25.81 | 43.2 | 6.37 | 1.37 | 4.731 | 8716.59 | 2.194 | 98.1 | 77.5 | 1442 | 21.64 | 5665.8 | 2981 | 2907 | 4275.3 | 1217.7 | 0.68068 | 6.102
2024-12-10 | 0:57 | Data | 0 | 32.406 | 30.509 | 195.947 | 7.64 | 184.503 | 2218.91 | 25.81 | 42.929 | 6.37 | 1.37 | 4.72 | 8716.59 | 2.147 | 98.1 | 77.5 | 1443 | 21.46 | 5665.8 | 2979.3 | 2928.5 | 4282.1 | 1217.7 | 0.67849 | 6.09
2024-12-10 | 0:58 | Data | 0 | 32.494 | 30.631 | 196.083 | 7.63 | 184.593 | 2218.91 | 25.8 | 43.29 | 6.37 | 1.367 | 4.699 | 8730.16 | 1.863 | 98 | 77.5 | 1442 | 21.74 | 5674.6 | 2946.6 | 2909.1 | 4253.5 | 1217.7 | 0.67609 | 6.066
2024-12-10 | 0:58 | Data | 0 | 32.494 | 30.59 | 196.128 | 7.64 | 184.639 | 2218.91 | 25.8 | 43.47 | 6.37 | 1.382 | 4.702 | 8725.64 | 2.079 | 98 | 77.3 | 1442 | 21.78 | 5671.7 | 2980.6 | 2899 | 4270.9 | 1217.7 | 0.67955 | 6.084
2024-12-10 | 0:58 | Data | 0 | 32.501 | 30.415 | 196.128 | 7.63 | 184.684 | 2213.49 | 25.8 | 43.47 | 6.37 | 1.376 | 4.721 | 8648.76 | 2.073 | 98 | 77.4 | 1439 | 21.74 | 5621.7 | 2985.8 | 2915.8 | 4281.2 | 1217.7 | 0.68007 | 6.095
2024-12-10 | 0:58 | Data | 0 | 32.744 | 30.82 | 196.173 | 7.64 | 184.684 | 2216.2 | 25.8 | 43.561 | 6.36 | 1.373 | 4.723 | 8635.19 | 2.073 | 98 | 77.5 | 1441 | 21.78 | 5612.9 | 2972.1 | 2909.4 | 4273.4 | 1217.7 | 0.67803 | 6.095
2024-12-10 | 0:58 | Data | 0 | 32.379 | 30.739 | 196.264 | 7.63 | 184.639 | 2216.2 | 25.8 | 43.2 | 6.37 | 1.37 | 4.752 | 8635.19 | 2.059 | 98.1 | 77.6 | 1441 | 21.6 | 5612.9 | 2946.6 | 2908.8 | 4255.3 | 1217.7 | 0.67519 | 6.121
2024-12-10 | 0:58 | Data | 0 | 32.305 | 30.212 | 196.264 | 7.64 | 184.639 | 2214.39 | 25.8 | 43.2 | 6.37 | 1.367 | 4.727 | 8635.19 | 2.025 | 98.1 | 77.6 | 1439 | 21.6 | 5612.9 | 2958.2 | 2895.9 | 4255.3 | 1217.7 | 0.67848 | 6.094
2024-12-10 | 0:58 | Data | 0 | 32.825 | 30.671 | 196.128 | 7.64 | 184.684 | 2218.91 | 25.81 | 43.2 | 6.37 | 1.367 | 4.738 | 8671.37 | 2.167 | 98.1 | 77.6 | 1442 | 21.6 | 5636.4 | 2964.7 | 2867.6 | 4239.6 | 1217.7 | 0.68289 | 6.104
2024-12-10 | 0:58 | Data | 0 | 32.609 | 30.624 | 196.083 | 7.63 | 184.639 | 2218.91 | 25.81 | 43.2 | 6.37 | 1.363 | 4.716 | 8680.41 | 1.884 | 98.1 | 77.6 | 1442 | 21.6 | 5642.3 | 2960.6 | 2898.5 | 4256.6 | 1217.7 | 0.67744 | 6.08
2024-12-10 | 0:58 | Data | 0 | 32.494 | 30.469 | 196.128 | 7.64 | 184.593 | 2218 | 25.8 | 43.2 | 6.37 | 1.374 | 4.722 | 8662.33 | 1.971 | 98.1 | 77.5 | 1442 | 21.6 | 5630.5 | 2967.6 | 2874.6 | 4247.3 | 1217.7 | 0.68245 | 6.096
2024-12-10 | 0:58 | Data | 0 | 32.501 | 30.624 | 196.173 | 7.64 | 184.548 | 2218 | 25.8 | 43.29 | 6.37 | 1.371 | 4.711 | 8662.33 | 2.046 | 98.1 | 77.5 | 1441 | 21.64 | 5630.5 | 2953 | 2910.7 | 4266.8 | 1217.7 | 0.67497 | 6.082
2024-12-10 | 0:58 | Data | 0 | 32.649 | 30.759 | 196.264 | 7.64 | 184.684 | 2216.2 | 25.8 | 43.2 | 6.36 | 1.376 | 4.724 | 8671.37 | 2.052 | 98.1 | 77.4 | 1441 | 21.6 | 5636.4 | 2955.3 | 2898.7 | 4255.2 | 1217.7 | 0.67659 | 6.1
2024-12-10 | 0:58 | Data | 0 | 32.494 | 30.475 | 196.173 | 7.64 | 184.639 | 2216.2 | 25.81 | 43.2 | 6.37 | 1.38 | 4.721 | 8689.46 | 1.965 | 98.1 | 77.4 | 1441 | 21.6 | 5648.1 | 2941.5 | 2905.4 | 4251.5 | 1217.7 | 0.67506 | 6.102
2024-12-10 | 0:58 | Data | 0 | 32.413 | 30.644 | 196.219 | 7.63 | 184.639 | 2218.91 | 25.81 | 43.109 | 6.37 | 1.367 | 4.716 | 8693.98 | 1.843 | 98.1 | 77.5 | 1442 | 21.6 | 5651.1 | 2960 | 2906.6 | 4261.9 | 1217.7 | 0.67756 | 6.083
2024-12-10 | 0:58 | Data | 0 | 32.75 | 30.475 | 196.309 | 7.63 | 184.684 | 2218.91 | 25.81 | 43.109 | 6.37 | 1.366 | 4.734 | 8703.03 | 2.046 | 98.1 | 77.6 | 1442 | 21.55 | 5657 | 2969.1 | 2875.9 | 4247 | 1217.7 | 0.68191 | 6.101
2024-12-10 | 0:58 | Data | 0 | 32.555 | 30.536 | 196.219 | 7.64 | 184.729 | 2217.1 | 25.81 | 43.2 | 6.36 | 1.377 | 4.727 | 8693.98 | 2.181 | 98.1 | 77.4 | 1441 | 21.6 | 5651.1 | 2958.2 | 2897.7 | 4261.6 | 1217.7 | 0.6759 | 6.104
2024-12-10 | 0:58 | Data | 0 | 32.494 | 30.415 | 196.173 | 7.64 | 184.593 | 2216.2 | 25.8 | 43.2 | 6.36 | 1.379 | 4.719 | 8698.5 | 2.079 | 98.1 | 77.4 | 1441 | 21.6 | 5654 | 2963.1 | 2894.6 | 4247.6 | 1217.7 | 0.67925 | 6.099
2024-12-10 | 0:58 | Data | 0 | 32.555 | 30.469 | 196.083 | 7.64 | 184.593 | 2216.2 | 25.8 | 43.2 | 6.37 | 1.377 | 4.738 | 8703.03 | 2.181 | 98.1 | 77.5 | 1441 | 21.6 | 5657 | 2951 | 2891.7 | 4251.5 | 1217.7 | 0.67658 | 6.115
2024-12-10 | 0:59 | Data | 0 | 32.507 | 30.597 | 196.128 | 7.64 | 184.593 | 2213.49 | 25.8 | 43.2 | 6.37 | 1.382 | 4.712 | 8693.98 | 2.066 | 98.1 | 77.3 | 1439 | 21.6 | 5651.1 | 2960.2 | 2874.5 | 4243.2 | 1217.7 | 0.67961 | 6.095
2024-12-10 | 0:59 | Data | 0 | 33.108 | 30.759 | 196.309 | 7.63 | 184.819 | 2216.2 | 25.8 | 43.2 | 6.37 | 1.372 | 4.709 | 8725.64 | 2.174 | 98.1 | 77.4 | 1441 | 21.6 | 5671.7 | 2961 | 2908.9 | 4260.7 | 1217.7 | 0.68061 | 6.08
2024-12-10 | 0:59 | Data | 0 | 32.946 | 30.448 | 196.219 | 7.63 | 184.774 | 2218.91 | 25.81 | 43.741 | 6.37 | 1.381 | 4.753 | 8743.73 | 2.174 | 98 | 77.5 | 1442 | 21.87 | 5683.4 | 2945.2 | 2912.8 | 4258.6 | 1217.7 | 0.67665 | 6.134
2024-12-10 | 0:59 | Data | 0 | 32.555 | 30.637 | 196.128 | 7.64 | 184.593 | 2218 | 25.8 | 43.2 | 6.37 | 1.375 | 4.748 | 8734.68 | 2.086 | 98.1 | 77.5 | 1442 | 21.6 | 5677.5 | 2949.7 | 2910.4 | 4260.1 | 1217.7 | 0.67493 | 6.122
2024-12-10 | 0:59 | Data | 0 | 32.548 | 30.475 | 196.173 | 7.64 | 184.639 | 2214.39 | 25.8 | 43.741 | 6.37 | 1.374 | 4.707 | 8730.16 | 1.971 | 98 | 77.4 | 1439 | 21.87 | 5674.6 | 2975.7 | 2914.2 | 4279.7 | 1217.7 | 0.6784 | 6.082
2024-12-10 | 0:59 | Data | 0 | 32.879 | 30.766 | 196.219 | 7.64 | 184.639 | 2220.72 | 25.81 | 43.2 | 6.37 | 1.374 | 4.701 | 8721.11 | 2.066 | 98.1 | 77.4 | 1443 | 21.55 | 5668.7 | 2945.7 | 2921.3 | 4265.8 | 1217.8 | 0.67614 | 6.074
2024-12-10 | 0:59 | Data | 0 | 32.696 | 30.658 | 196.173 | 7.63 | 184.684 | 2218.91 | 25.8 | 43.2 | 6.36 | 1.372 | 4.709 | 8689.46 | 2.052 | 98.1 | 77.4 | 1442 | 21.6 | 5648.1 | 2969.7 | 2919.7 | 4284.1 | 1217.8 | 0.67514 | 6.081
2024-12-10 | 0:59 | Data | 0 | 32.994 | 30.772 | 196.354 | 7.63 | 184.729 | 2222.52 | 25.8 | 43.2 | 6.36 | 1.363 | 4.687 | 8689.46 | 2.221 | 98.1 | 77.5 | 1445 | 21.55 | 5648.1 | 2974.5 | 2893 | 4261.5 | 1217.8 | 0.68027 | 6.049
2024-12-10 | 0:59 | Data | 0 | 32.501 | 30.644 | 196.219 | 7.64 | 184.729 | 2221.62 | 25.8 | 43.2 | 6.37 | 1.374 | 4.725 | 8693.98 | 2.032 | 98.1 | 77.5 | 1445 | 21.55 | 5651.1 | 2958.1 | 2914.4 | 4268.3 | 1217.8 | 0.67566 | 6.099
2024-12-10 | 0:59 | Data | 0 | 32.305 | 30.415 | 196.219 | 7.64 | 184.684 | 2222.52 | 25.81 | 43.2 | 6.37 | 1.374 | 4.712 | 8707.55 | 1.863 | 98.1 | 77.4 | 1445 | 21.6 | 5659.9 | 2941.7 | 2904.3 | 4244.7 | 1217.8 | 0.67588 | 6.086
2024-12-10 | 0:59 | Data | 0 | 32.737 | 30.678 | 196.309 | 7.64 | 184.819 | 2217.1 | 25.81 | 43.2 | 6.37 | 1.38 | 4.706 | 8698.5 | 1.965 | 98.1 | 77.3 | 1441 | 21.55 | 5654 | 1890.9 | 2372.2 | 3044.9 | 1217.8 | 0.61859 | 6.085
2024-12-10 | 0:59 | Data | 0 | 32.44 | 30.793 | 196.354 | 7.64 | 184.639 | 2222.52 | 25.81 | 43.109 | 6.36 | 1.374 | 4.71 | 8716.59 | 2.059 | 98.1 | 77.4 | 1445 | 21.6 | 5665.8 | 1881.6 | 2363.5 | 3031.5 | 1217.8 | 0.61876 | 6.084
2024-12-10 | 0:59 | Data | 0 | 32.271 | 30.415 | 196.219 | 7.63 | 184.684 | 2222.52 | 25.8 | 43.2 | 6.37 | 1.367 | 4.714 | 8684.94 | 2.052 | 98.1 | 77.5 | 1445 | 21.6 | 5645.2 | 1881.8 | 2347.7 | 3024.9 | 1217.8 | 0.62303 | 6.083
2024-12-10 | 0:59 | Data | 0 | 32.501 | 30.59 | 196.173 | 7.63 | 184.593 | 2226.14 | 25.81 | 43.109 | 6.37 | 1.384 | 4.706 | 8693.98 | 1.958 | 98.1 | 77.3 | 1448 | 21.6 | 5651.1 | 1891.1 | 2363.5 | 3039 | 1217.8 | 0.61964 | 6.091
2024-12-10 | 0:59 | Data | 0 | 32.548 | 30.198 | 196.173 | 7.63 | 184.593 | 2223.43 | 25.8 | 43.109 | 6.37 | 1.376 | 4.733 | 8707.55 | 2.052 | 98.1 | 77.5 | 1445 | 21.6 | 5659.9 | 1881.4 | 2356.1 | 3027.2 | 1217.8 | 0.61915 | 6.108
2024-12-10 | 0:59 | Data | 0 | 32.879 | 30.705 | 196.264 | 7.64 | 184.865 | 2222.52 | 25.8 | 43.2 | 6.37 | 1.379 | 4.736 | 8703.03 | 2.046 | 98.1 | 77.4 | 1444 | 21.55 | 5657 | 1893.1 | 2369 | 3043 | 1217.8 | 0.61927 | 6.115
2024-12-10 | 0:59 | Data | 0 | 32.696 | 30.529 | 196.128 | 7.64 | 184.593 | 2225.23 | 25.81 | 43.2 | 6.37 | 1.376 | 4.714 | 8707.55 | 2.073 | 98.1 | 77.4 | 1446 | 21.6 | 5659.9 | 1881.8 | 2341.3 | 3014.8 | 1217.8 | 0.62236 | 6.09
2024-12-10 | 0:59 | Data | 0 | 32.501 | 30.415 | 196.128 | 7.64 | 184.729 | 2222.52 | 25.8 | 43.109 | 6.37 | 1.385 | 4.718 | 8703.03 | 2.282 | 98.1 | 77.3 | 1445 | 21.6 | 5657 | 1896.9 | 2373.3 | 3048.9 | 1217.8 | 0.61709 | 6.102
2024-12-10 | 1:00 | Data | 0 | 32.548 | 30.536 | 196.264 | 7.64 | 184.729 | 2223.43 | 25.81 | 43.2 | 6.36 | 1.378 | 4.692 | 8707.55 | 2.079 | 98.1 | 77.3 | 1445 | 21.55 | 5659.9 | 1877.2 | 2376.1 | 3040.4 | 1217.8 | 0.61457 | 6.07
2024-12-10 | 1:00 | Data | 0 | 32.494 | 30.401 | 196.219 | 7.63 | 184.548 | 2218.91 | 25.81 | 43.2 | 6.36 | 1.38 | 4.697 | 8689.46 | 2.221 | 98.1 | 77.3 | 1443 | 21.55 | 5648.1 | 1879.9 | 2377.2 | 3040.9 | 1217.8 | 0.61597 | 6.075
2024-12-10 | 1:00 | Data | 0 | 32.393 | 30.415 | 196.083 | 7.64 | 184.548 | 2218.91 | 25.8 | 43.2 | 6.37 | 1.385 | 4.743 | 8684.94 | 1.863 | 98.1 | 77.4 | 1442 | 21.6 | 5645.2 | 1878.8 | 2365.1 | 3032.5 | 1217.8 | 0.61672 | 6.127
2024-12-10 | 1:00 | Data | 0 | 32.946 | 30.198 | 196.309 | 7.64 | 184.729 | 2218.91 | 25.81 | 43.2 | 6.36 | 1.372 | 4.738 | 8703.03 | 2.154 | 98.1 | 77.6 | 1442 | 21.6 | 5657 | 1893.6 | 2376.3 | 3034.5 | 1217.8 | 0.61808 | 6.109
2024-12-10 | 1:00 | Data | 0 | 32.501 | 30.415 | 196.173 | 7.64 | 184.639 | 2218.91 | 25.8 | 43.109 | 6.37 | 1.369 | 4.727 | 8684.94 | 2.079 | 98.1 | 77.5 | 1443 | 21.55 | 5645.2 | 1885.4 | 2374.8 | 3038.4 | 1217.8 | 0.61571 | 6.096
2024-12-10 | 1:00 | Data | 0 | 32.555 | 30.367 | 196.128 | 7.64 | 184.593 | 2218.91 | 25.81 | 43.2 | 6.37 | 1.37 | 4.707 | 8680.41 | 2.289 | 98.1 | 77.5 | 1442 | 21.6 | 5642.3 | 1886.3 | 2357.9 | 3029.9 | 1217.8 | 0.62038 | 6.077
2024-12-10 | 1:00 | Data | 0 | 32.305 | 30.219 | 196.083 | 7.64 | 184.684 | 2218.91 | 25.81 | 43.2 | 6.37 | 1.373 | 4.695 | 8680.41 | 1.978 | 98.1 | 77.4 | 1442 | 21.51 | 5642.3 | 1892.6 | 2362 | 3037.4 | 1217.8 | 0.62263 | 6.068
2024-12-10 | 1:00 | Data | 0 | 32.858 | 30.266 | 196.219 | 7.63 | 184.684 | 2218.91 | 25.8 | 43.2 | 6.37 | 1.377 | 4.707 | 8657.8 | 2.16 | 98.1 | 77.4 | 1442 | 21.6 | 5627.6 | 1878.8 | 2347.5 | 3019.1 | 1217.8 | 0.61992 | 6.084
2024-12-10 | 1:00 | Data | 0 | 32.946 | 30.334 | 196.219 | 7.63 | 184.774 | 2218.91 | 25.8 | 43.2 | 6.37 | 1.374 | 4.729 | 8648.76 | 2.147 | 98.1 | 77.5 | 1442 | 21.55 | 5621.7 | 1875.5 | 2332.5 | 3004.2 | 1217.8 | 0.62176 | 6.102
2024-12-10 | 1:00 | Data | 0 | 32.669 | 30.847 | 196.173 | 7.63 | 184.639 | 2220.72 | 25.8 | 43.2 | 6.37 | 1.375 | 4.709 | 8648.76 | 2.019 | 98.1 | 77.4 | 1442 | 21.6 | 5621.7 | 1897.6 | 2342.5 | 3024.1 | 1217.8 | 0.62581 | 6.082
2024-12-10 | 1:00 | Data | 0 | 32.501 | 30.246 | 196.083 | 7.64 | 184.593 | 2218.91 | 25.81 | 43.109 | 6.37 | 1.372 | 4.707 | 8644.24 | 2.025 | 98.1 | 77.4 | 1442 | 21.6 | 5618.8 | 1871.7 | 2327.9 | 2997.7 | 1217.8 | 0.62217 | 6.079
2024-12-10 | 1:00 | Data | 0 | 33.129 | 30.489 | 196.173 | 7.64 | 184.729 | 2218.91 | 25.81 | 43.2 | 6.37 | 1.372 | 4.699 | 8653.28 | 2.316 | 98.1 | 77.4 | 1442 | 21.6 | 5624.6 | 1900.4 | 2352.5 | 3035.2 | 1217.8 | 0.62419 | 6.07
2024-12-10 | 1:00 | Data | 0 | 32.507 | 30.59 | 196.309 | 7.64 | 184.729 | 2218 | 25.8 | 43.2 | 6.36 | 1.371 | 4.683 | 8680.41 | 2.073 | 98.1 | 77.4 | 1442 | 21.6 | 5642.3 | 1885.3 | 2329.9 | 3007.9 | 1217.8 | 0.6245 | 6.053
2024-12-10 | 1:00 | Data | 0 | 32.433 | 30.239 | 196.173 | 7.64 | 184.593 | 2218 | 25.8 | 43.2 | 6.37 | 1.376 | 4.704 | 8680.41 | 2.174 | 98.1 | 77.4 | 1442 | 21.55 | 5642.3 | 1895.2 | 2358.4 | 3035.4 | 1217.8 | 0.6219 | 6.079
2024-12-10 | 1:00 | Data | 0 | 32.494 | 30.313 | 196.128 | 7.63 | 184.593 | 2218.91 | 25.8 | 43.109 | 6.37 | 1.365 | 4.726 | 8680.41 | 2.228 | 98.1 | 77.6 | 1442 | 21.55 | 5642.3 | 1893.6 | 2372.8 | 3046.5 | 1217.8 | 0.61911 | 6.092
2024-12-10 | 1:00 | Data | 0 | 32.649 | 30.415 | 196.128 | 7.64 | 184.639 | 2218 | 25.8 | 43.2 | 6.37 | 1.367 | 4.718 | 8671.37 | 2.289 | 98.1 | 77.5 | 1442 | 21.6 | 5636.4 | 1886.6 | 2366.1 | 3037.2 | 1217.8 | 0.61838 | 6.084
2024-12-10 | 1:00 | Data | 0 | 32.487 | 30.624 | 196.128 | 7.64 | 184.684 | 2216.2 | 25.8 | 43.2 | 6.37 | 1.366 | 4.706 | 8662.33 | 2.073 | 98.1 | 77.5 | 1441 | 21.6 | 5630.5 | 1886.7 | 2354.3 | 3027.8 | 1217.8 | 0.6206 | 6.073
2024-12-10 | 1:00 | Data | 0 | 32.548 | 30.246 | 196.219 | 7.64 | 184.684 | 2213.49 | 25.8 | 43.109 | 6.37 | 1.362 | 4.731 | 8648.76 | 1.992 | 98 | 77.7 | 1439 | 21.6 | 5621.7 | 1885.7 | 2357.5 | 3030.5 | 1217.8 | 0.6193 | 6.094
2024-12-10 | 1:01 | Data | 0 | 32.487 | 30.3 | 196.083 | 7.64 | 184.593 | 2217.1 | 25.8 | 43.019 | 6.37 | 1.376 | 4.711 | 8648.76 | 2.079 | 98.1 | 77.4 | 1441 | 21.51 | 5621.7 | 1883.3 | 2333.7 | 3010.3 | 1217.8 | 0.62354 | 6.086
2024-12-10 | 1:01 | Data | 0 | 32.501 | 30.415 | 196.264 | 7.64 | 184.684 | 2217.1 | 25.8 | 43.561 | 6.37 | 1.383 | 4.717 | 8644.24 | 2.079 | 98 | 77.3 | 1441 | 21.78 | 5618.8 | 1879.3 | 2338.7 | 3010.8 | 1217.8 | 0.62191 | 6.098
2024-12-10 | 1:01 | Data | 0 | 32.494 | 30.61 | 196.173 | 7.63 | 184.593 | 2218.91 | 25.81 | 43.832 | 6.37 | 1.376 | 4.705 | 8648.76 | 2.127 | 98 | 77.4 | 1442 | 21.87 | 5621.7 | 1865.9 | 2337.4 | 3002.3 | 1217.8 | 0.61884 | 6.081
2024-12-10 | 1:01 | Data | 0 | 32.318 | 30.415 | 195.992 | 7.64 | 184.548 | 2218.91 | 25.8 | 43.561 | 6.36 | 1.369 | 4.698 | 8635.19 | 2.039 | 98 | 77.4 | 1442 | 21.78 | 5612.9 | 1891.4 | 2353 | 3029.1 | 1217.8 | 0.6242 | 6.068
2024-12-10 | 1:01 | Data | 0 | 32.548 | 30.421 | 196.173 | 7.64 | 184.684 | 2222.52 | 25.8 | 43.47 | 6.37 | 1.366 | 4.71 | 8639.71 | 1.978 | 98 | 77.5 | 1445 | 21.74 | 5615.8 | 1886.2 | 2341.7 | 3030.3 | 1217.8 | 0.6193 | 6.075
2024-12-10 | 1:01 | Data | 0 | 32.609 | 30.252 | 196.173 | 7.64 | 184.729 | 2227.04 | 25.8 | 43.561 | 6.37 | 1.371 | 4.734 | 8653.28 | 2.086 | 98 | 77.5 | 1448 | 21.74 | 5624.6 | 1898.1 | 2363 | 3041.9 | 1217.8 | 0.62173 | 6.106
2024-12-10 | 1:01 | Data | 0 | 32.379 | 30.185 | 195.992 | 7.64 | 184.503 | 2221.62 | 25.81 | 43.47 | 6.37 | 1.375 | 4.709 | 8648.76 | 2.208 | 98 | 77.4 | 1445 | 21.74 | 5621.7 | 1886.5 | 2363.2 | 3035.1 | 1217.8 | 0.61931 | 6.083
2024-12-10 | 1:01 | Data | 0 | 32.298 | 30.3 | 196.083 | 7.64 | 184.593 | 2222.52 | 25.8 | 43.741 | 6.37 | 1.372 | 4.721 | 8680.41 | 2.079 | 98 | 77.5 | 1445 | 21.92 | 5642.3 | 1892.7 | 2357.5 | 3035.1 | 1217.8 | 0.62046 | 6.093
2024-12-10 | 1:01 | Data | 0 | 32.366 | 30.617 | 196.219 | 7.63 | 184.639 | 2222.52 | 25.8 | 43.47 | 6.37 | 1.37 | 4.707 | 8684.94 | 2.289 | 98 | 77.5 | 1445 | 21.78 | 5645.2 | 1871.4 | 2362.7 | 3025.7 | 1217.8 | 0.61654 | 6.078
2024-12-10 | 1:01 | Data | 0 | 32.507 | 30.739 | 196.219 | 7.64 | 184.684 | 2220.72 | 25.8 | 43.561 | 6.37 | 1.366 | 4.731 | 8689.46 | 1.958 | 98 | 77.6 | 1443 | 21.74 | 5648.1 | 1896.8 | 2394.2 | 3064 | 1217.8 | 0.61654 | 6.095
2024-12-10 | 1:01 | Data | 0 | 32.487 | 30.198 | 195.902 | 7.64 | 184.593 | 2218.91 | 25.81 | 43.47 | 6.37 | 1.373 | 4.743 | 8707.55 | 2.093 | 98 | 77.6 | 1442 | 21.74 | 5659.9 | 1888.3 | 2377.7 | 3046.5 | 1217.8 | 0.61731 | 6.116
2024-12-10 | 1:01 | Data | 0 | 32.44 | 30.401 | 196.173 | 7.64 | 184.548 | 2218.91 | 25.8 | 43.2 | 6.37 | 1.377 | 4.738 | 8707.55 | 2.093 | 98.1 | 77.5 | 1442 | 21.55 | 5659.9 | 1885.4 | 2381 | 3047.7 | 1217.8 | 0.61646 | 6.114
2024-12-10 | 1:01 | Data | 0 | 32.494 | 30.415 | 196.083 | 7.64 | 184.639 | 2218.91 | 25.81 | 43.109 | 6.37 | 1.379 | 4.714 | 8703.03 | 2.086 | 98.1 | 77.4 | 1442 | 21.55 | 5657 | 1885.8 | 2388.5 | 3054.9 | 1217.8 | 0.61497 | 6.093
2024-12-10 | 1:01 | Data | 0 | 32.271 | 30.415 | 196.173 | 7.63 | 184.503 | 2217.1 | 25.79 | 43.2 | 6.37 | 1.38 | 4.707 | 8712.07 | 2.052 | 98.1 | 77.3 | 1441 | 21.6 | 5662.8 | 1891.1 | 2373.9 | 3045.7 | 1217.8 | 0.61901 | 6.087
2024-12-10 | 1:01 | Data | 0 | 32.433 | 30.408 | 196.083 | 7.63 | 184.548 | 2216.2 | 25.8 | 42.929 | 6.37 | 1.38 | 4.708 | 8716.59 | 2.079 | 98.1 | 77.3 | 1441 | 21.46 | 5665.8 | 1882.8 | 2355.1 | 3026.5 | 1217.8 | 0.61995 | 6.088
2024-12-10 | 1:01 | Data | 0 | 32.595 | 30.205 | 196.128 | 7.63 | 184.593 | 2216.2 | 25.8 | 43.29 | 6.37 | 1.377 | 4.722 | 8693.98 | 2.268 | 98.1 | 77.4 | 1441 | 21.6 | 5651.1 | 1884.1 | 2350.2 | 3022.8 | 1217.8 | 0.62055 | 6.1
2024-12-10 | 1:01 | Data | 0 | 32.379 | 30.192 | 196.083 | 7.63 | 184.548 | 2216.2 | 25.8 | 43.2 | 6.37 | 1.371 | 4.706 | 8680.41 | 2.086 | 98 | 77.4 | 1441 | 21.6 | 5642.3 | 1881.2 | 2345.8 | 3019.2 | 1217.8 | 0.62073 | 6.077
2024-12-10 | 1:02 | Data | 0 | 32.44 | 30.394 | 195.902 | 7.64 | 184.548 | 2211.68 | 25.8 | 43.109 | 6.37 | 1.382 | 4.726 | 8689.46 | 2.147 | 98.1 | 77.4 | 1437 | 21.51 | 5648.1 | 1900.7 | 2351.9 | 3034.3 | 1217.8 | 0.62433 | 6.11
2024-12-10 | 1:02 | Data | 0 | 32.717 | 30.678 | 196.173 | 7.64 | 184.684 | 2215.29 | 25.81 | 43.2 | 6.37 | 1.379 | 4.721 | 8693.98 | 2.019 | 98 | 77.4 | 1441 | 21.6 | 5651.1 | 1898.7 | 2339.2 | 3023 | 1217.8 | 0.62578 | 6.101
2024-12-10 | 1:02 | Data | 0 | 32.744 | 30.421 | 196.083 | 7.64 | 184.548 | 2216.2 | 25.81 | 43.109 | 6.37 | 1.384 | 4.718 | 8721.11 | 1.931 | 98.1 | 77.3 | 1441 | 21.6 | 5668.7 | 1887.7 | 2359.4 | 3032.5 | 1217.8 | 0.62033 | 6.102
2024-12-10 | 1:02 | Data | 0 | 32.413 | 30.192 | 196.173 | 7.64 | 184.684 | 2216.2 | 25.8 | 43.2 | 6.37 | 1.369 | 4.722 | 8707.55 | 2.086 | 98.1 | 77.5 | 1441 | 21.55 | 5659.9 | 1887.6 | 2348.5 | 3022.5 | 1217.8 | 0.62265 | 6.092
2024-12-10 | 1:02 | Data | 0 | 32.264 | 30.388 | 195.857 | 7.63 | 184.548 | 2215.29 | 25.81 | 43.2 | 6.37 | 1.367 | 4.719 | 8693.98 | 2.052 | 98.1 | 77.5 | 1441 | 21.64 | 5651.1 | 1879.5 | 2346.5 | 3018.5 | 1217.8 | 0.62195 | 6.086
2024-12-10 | 1:02 | Data | 0 | 32.717 | 30.644 | 196.173 | 7.64 | 184.593 | 2217.1 | 25.81 | 43.2 | 6.37 | 1.374 | 4.69 | 8716.59 | 2.133 | 98.1 | 77.3 | 1441 | 21.6 | 5665.8 | 1895.9 | 2363 | 3040.3 | 1217.8 | 0.62107 | 6.064
2024-12-10 | 1:02 | Data | 0 | 32.575 | 30.205 | 195.992 | 7.63 | 184.593 | 2208.06 | 25.8 | 43.2 | 6.37 | 1.376 | 4.698 | 8671.37 | 2.174 | 98 | 77.4 | 1436 | 21.6 | 5636.4 | 2592.5 | 3593.7 | 4453.1 | 1217.9 | 0.59245 | 6.074
2024-12-10 | 1:02 | Data | 0 | 32.318 | 30.185 | 195.992 | 7.64 | 184.593 | 2213.49 | 25.8 | 43.109 | 6.37 | 1.38 | 4.708 | 8707.55 | 2.1 | 98 | 77.3 | 1439 | 21.6 | 5659.9 | 2973.4 | 2946.2 | 4296.1 | 1217.9 | 0.67521 | 6.087
2024-12-10 | 1:02 | Data | 0 | 32.663 | 30.111 | 195.992 | 7.64 | 184.458 | 2221.62 | 25.8 | 43.2 | 6.37 | 1.367 | 4.704 | 8703.03 | 2.059 | 98.1 | 77.5 | 1444 | 21.6 | 5657 | 2955.8 | 2915.6 | 4264.6 | 1217.9 | 0.67637 | 6.072
2024-12-10 | 1:02 | Data | 0 | 32.109 | 30.192 | 195.947 | 7.63 | 184.639 | 2216.2 | 25.8 | 43.109 | 6.37 | 1.377 | 4.692 | 8693.98 | 1.877 | 98.1 | 77.3 | 1441 | 21.55 | 5651.1 | 2966.6 | 2934.5 | 4279.9 | 1217.9 | 0.67466 | 6.068
2024-12-10 | 1:02 | Data | 0 | 32.42 | 30.293 | 196.173 | 7.63 | 184.458 | 2217.1 | 25.8 | 43.109 | 6.37 | 1.366 | 4.693 | 8689.46 | 2.174 | 98.1 | 77.5 | 1441 | 21.6 | 5648.1 | 2960.4 | 2917.7 | 4274.2 | 1217.9 | 0.67388 | 6.059
2024-12-10 | 1:02 | Data | 0 | 32.379 | 30.408 | 195.902 | 7.64 | 184.458 | 2212.58 | 25.8 | 43.29 | 6.37 | 1.369 | 4.711 | 8693.98 | 2.079 | 98 | 77.5 | 1438 | 21.64 | 5651.1 | 2970.9 | 2928 | 4284.9 | 1217.9 | 0.67737 | 6.082
2024-12-10 | 1:02 | Data | 0 | 32.575 | 30.401 | 196.128 | 7.64 | 184.684 | 2213.49 | 25.8 | 43.2 | 6.37 | 1.366 | 4.729 | 8689.46 | 1.884 | 98.1 | 77.6 | 1439 | 21.55 | 5648.1 | 2982.3 | 2951.1 | 4309.4 | 1217.9 | 0.67297 | 6.094
2024-12-10 | 1:02 | Data | 0 | 32.21 | 30.293 | 196.083 | 7.63 | 184.503 | 2214.39 | 25.79 | 43.109 | 6.37 | 1.365 | 4.698 | 8693.98 | 1.965 | 98 | 77.5 | 1439 | 21.6 | 5651.1 | 2959.8 | 2924.8 | 4276.7 | 1217.9 | 0.6745 | 6.062
2024-12-10 | 1:02 | Data | 0 | 32.487 | 30.415 | 196.083 | 7.64 | 184.548 | 2210.77 | 25.8 | 43.109 | 6.37 | 1.362 | 4.71 | 8716.59 | 1.971 | 98 | 77.6 | 1438 | 21.55 | 5665.8 | 2953.1 | 2902.8 | 4256.4 | 1217.9 | 0.67766 | 6.072
2024-12-10 | 1:02 | Data | 0 | 32.366 | 30.583 | 196.173 | 7.63 | 184.503 | 2208.97 | 25.78 | 43.109 | 6.37 | 1.369 | 4.719 | 8716.59 | 2.181 | 98 | 77.5 | 1436 | 21.55 | 5665.8 | 2956.4 | 2904.7 | 4262.1 | 1217.9 | 0.67629 | 6.088
2024-12-10 | 1:02 | Data | 0 | 32.487 | 30.192 | 195.947 | 7.64 | 184.548 | 2208.97 | 25.77 | 43.2 | 6.37 | 1.367 | 4.737 | 8721.11 | 2.295 | 98 | 77.6 | 1435 | 21.6 | 5668.7 | 2971.6 | 2902.8 | 4267.1 | 1217.9 | 0.6793 | 6.102
2024-12-10 | 1:02 | Data | 0 | 32.494 | 30.252 | 195.992 | 7.64 | 184.548 | 2208.97 | 25.78 | 43.2 | 6.37 | 1.377 | 4.721 | 8707.55 | 2.167 | 98 | 77.4 | 1436 | 21.6 | 5659.9 | 2964.7 | 2904.8 | 4266.4 | 1217.9 | 0.67845 | 6.097
2024-12-10 | 1:03 | Data | 0 | 32.379 | 30.205 | 195.857 | 7.64 | 184.458 | 2210.77 | 25.78 | 43.29 | 6.37 | 1.375 | 4.707 | 8703.03 | 2.241 | 98 | 77.4 | 1437 | 21.6 | 5657 | 2964.4 | 2900.8 | 4264.1 | 1217.9 | 0.67699 | 6.082
2024-12-10 | 1:03 | Data | 0 | 32.035 | 30.185 | 195.902 | 7.64 | 184.503 | 2210.77 | 25.78 | 43.109 | 6.37 | 1.381 | 4.724 | 8689.46 | 2.073 | 98 | 77.4 | 1437 | 21.6 | 5648.1 | 2957.8 | 2931 | 4279.2 | 1217.9 | 0.67401 | 6.104
2024-12-10 | 1:03 | Data | 0 | 32.649 | 30.469 | 196.128 | 7.64 | 184.684 | 2210.77 | 25.77 | 43.2 | 6.37 | 1.378 | 4.736 | 8703.03 | 2.268 | 98 | 77.5 | 1438 | 21.6 | 5657 | 2967.5 | 2925.2 | 4281.3 | 1217.9 | 0.67584 | 6.113
2024-12-10 | 1:03 | Data | 0 | 32.467 | 30.516 | 196.128 | 7.64 | 184.458 | 2210.77 | 25.78 | 43.2 | 6.37 | 1.377 | 4.705 | 8707.55 | 1.904 | 98 | 77.4 | 1438 | 21.6 | 5659.9 | 2977.1 | 2913.5 | 4280.2 | 1217.9 | 0.67825 | 6.082
2024-12-10 | 1:03 | Data | 0 | 32.271 | 30.144 | 195.947 | 7.64 | 184.458 | 2208.97 | 25.77 | 43.47 | 6.37 | 1.374 | 4.708 | 8689.46 | 2.16 | 98 | 77.4 | 1436 | 21.74 | 5648.1 | 2968.2 | 2917.6 | 4274.5 | 1217.9 | 0.67625 | 6.082
2024-12-10 | 1:03 | Data | 0 | 32.285 | 30.361 | 196.173 | 7.64 | 184.639 | 2204.45 | 25.77 | 43.2 | 6.36 | 1.365 | 4.711 | 8689.46 | 2.019 | 98 | 77.5 | 1433 | 21.6 | 5648.1 | 2960.6 | 2929.7 | 4278.7 | 1217.9 | 0.67551 | 6.075
2024-12-10 | 1:03 | Data | 0 | 32.44 | 30.516 | 196.128 | 7.64 | 184.593 | 2208.06 | 25.78 | 43.561 | 6.37 | 1.377 | 4.722 | 8693.98 | 2.079 | 98 | 77.4 | 1436 | 21.78 | 5651.1 | 2967.5 | 2934.8 | 4282.3 | 1217.9 | 0.67618 | 6.1
2024-12-10 | 1:03 | Data | 0 | 32.366 | 30.212 | 195.857 | 7.64 | 184.458 | 2208.97 | 25.77 | 43.109 | 6.37 | 1.369 | 4.728 | 8689.46 | 2.268 | 98 | 77.6 | 1436 | 21.6 | 5648.1 | 2957.1 | 2898 | 4255.5 | 1217.9 | 0.67707 | 6.095
2024-12-10 | 1:03 | Data | 0 | 32.393 | 30.192 | 195.992 | 7.63 | 184.593 | 2205.35 | 25.78 | 43.2 | 6.37 | 1.375 | 4.71 | 8671.37 | 2.093 | 98 | 77.4 | 1433 | 21.6 | 5636.4 | 2957.4 | 2897.2 | 4244.5 | 1217.9 | 0.67598 | 6.084
2024-12-10 | 1:03 | Data | 0 | 32.379 | 30.408 | 196.083 | 7.63 | 184.548 | 2206.25 | 25.78 | 43.109 | 6.37 | 1.369 | 4.707 | 8693.98 | 2.059 | 98 | 77.5 | 1433 | 21.55 | 5651.1 | 2961.9 | 2893.6 | 4261.6 | 1217.9 | 0.6798 | 6.076
2024-12-10 | 1:03 | Data | 0 | 32.636 | 30.205 | 196.219 | 7.64 | 184.684 | 2204.45 | 25.79 | 43.2 | 6.37 | 1.379 | 4.711 | 8689.46 | 2.14 | 98 | 77.4 | 1433 | 21.6 | 5648.1 | 2973.4 | 2886.7 | 4259.3 | 1217.9 | 0.68175 | 6.09
2024-12-10 | 1:03 | Data | 0 | 32.406 | 30.415 | 195.992 | 7.64 | 184.548 | 2111.35 | 25.78 | 43.109 | 6.37 | 1.379 | 4.72 | 8693.98 | 2.275 | 98 | 77.4 | 1373 | 21.55 | 5651.1 | 2969.6 | 2880.6 | 4252.6 | 1217.9 | 0.68101 | 6.1
2024-12-10 | 1:03 | Data | 0 | 32.291 | 30.212 | 196.128 | 7.64 | 184.503 | 2218.91 | 25.78 | 43.2 | 6.37 | 1.376 | 4.714 | 8671.37 | 1.992 | 98.1 | 77.4 | 1443 | 21.64 | 5636.4 | 2964.7 | 2869.2 | 4238.3 | 1217.9 | 0.68179 | 6.09
2024-12-10 | 1:03 | Data | 0 | 32.487 | 30.097 | 195.947 | 7.63 | 184.593 | 2218.91 | 25.77 | 43.109 | 6.37 | 1.383 | 4.717 | 8707.55 | 2.194 | 98.1 | 77.3 | 1442 | 21.6 | 5659.9 | 2970.8 | 2897.1 | 4262.3 | 1217.9 | 0.67807 | 6.099
2024-12-10 | 1:03 | Data | 0 | 32.548 | 30.192 | 195.947 | 7.64 | 184.593 | 2218.91 | 25.78 | 43.2 | 6.37 | 1.374 | 4.721 | 8707.55 | 2.093 | 98.1 | 77.5 | 1442 | 21.6 | 5659.9 | 2963.5 | 2883 | 4249.1 | 1217.9 | 0.68032 | 6.094
2024-12-10 | 1:03 | Data | 0 | 32.271 | 30.185 | 195.992 | 7.64 | 184.548 | 2216.2 | 25.78 | 43.109 | 6.36 | 1.377 | 4.735 | 8707.55 | 2.079 | 98.1 | 77.5 | 1441 | 21.6 | 5659.9 | 2962.2 | 2884.7 | 4248.7 | 1217.9 | 0.68022 | 6.111
2024-12-10 | 1:03 | Data | 0 | 32.744 | 30.421 | 196.264 | 7.64 | 184.729 | 2218.91 | 25.78 | 43.109 | 6.37 | 1.372 | 4.722 | 8662.33 | 2.127 | 98.1 | 77.5 | 1442 | 21.6 | 5630.5 | 2963.7 | 2878.3 | 4245.6 | 1217.9 | 0.6802 | 6.095
2024-12-10 | 1:03 | Data | 0 | 32.271 | 30.536 | 196.173 | 7.64 | 184.639 | 2218 | 25.78 | 43.109 | 6.37 | 1.371 | 4.705 | 8703.03 | 2.14 | 98.1 | 77.4 | 1443 | 21.6 | 5657 | 2962.5 | 2900.8 | 4254.7 | 1217.9 | 0.67796 | 6.077
2024-12-10 | 1:04 | Data | 0 | 32.102 | 30.502 | 196.083 | 7.63 | 184.593 | 2214.39 | 25.78 | 43.2 | 6.37 | 1.363 | 4.704 | 8680.41 | 1.944 | 98.1 | 77.5 | 1441 | 21.6 | 5642.3 | 2968.3 | 2886.6 | 4246.1 | 1217.9 | 0.68077 | 6.066
2024-12-10 | 1:04 | Data | 0 | 32.379 | 30.408 | 196.083 | 7.64 | 184.639 | 2218.91 | 25.78 | 43.2 | 6.37 | 1.363 | 4.728 | 8703.03 | 2.066 | 98.1 | 77.6 | 1442 | 21.64 | 5657 | 2956 | 2878.9 | 4245.5 | 1217.9 | 0.67905 | 6.092
2024-12-10 | 1:04 | Data | 0 | 32.487 | 30.415 | 195.992 | 7.64 | 184.593 | 2218.91 | 25.77 | 43.29 | 6.37 | 1.364 | 4.702 | 9159.77 | 2.073 | 98.1 | 77.5 | 1442 | 21.64 | 5953.9 | 2957.8 | 2887.2 | 4247.7 | 1217.9 | 0.68004 | 6.067
2024-12-10 | 1:04 | Data | 0 | 32.602 | 30.246 | 196.219 | 7.63 | 184.548 | 2222.52 | 25.78 | 43.109 | 6.37 | 1.367 | 4.717 | 8436.21 | 2.187 | 98.1 | 77.5 | 1445 | 21.55 | 5483.5 | 2952.9 | 2863.5 | 4230.3 | 1217.9 | 0.68077 | 6.083
2024-12-10 | 1:04 | Data | 0 | 32.494 | 30.401 | 196.128 | 7.64 | 184.639 | 2222.52 | 25.78 | 43.2 | 6.37 | 1.377 | 4.721 | 8449.78 | 2.019 | 98.1 | 77.4 | 1444 | 21.6 | 5492.4 | 2969 | 2862.9 | 4244.8 | 1217.9 | 0.68328 | 6.098
2024-12-10 | 1:04 | Data | 0 | 32.271 | 30.516 | 196.128 | 7.64 | 184.593 | 2222.52 | 25.79 | 43.109 | 6.37 | 1.373 | 4.711 | 8454.3 | 1.924 | 98.1 | 77.4 | 1445 | 21.55 | 5495.3 | 2960.8 | 2863.4 | 4231.7 | 1217.9 | 0.68229 | 6.083
2024-12-10 | 1:04 | Data | 0 | 32.271 | 30.192 | 196.083 | 7.63 | 184.548 | 2222.52 | 25.78 | 43.109 | 6.36 | 1.364 | 4.731 | 8870.35 | 2.235 | 98.1 | 77.6 | 1445 | 21.6 | 5765.7 | 2965 | 2864.4 | 4239.1 | 1218 | 0.68296 | 6.096
2024-12-10 | 1:04 | Data | 0 | 32.042 | 30.3 | 196.083 | 7.63 | 184.548 | 2223.43 | 25.78 | 43.2 | 6.37 | 1.377 | 4.714 | 8870.35 | 2.167 | 98.1 | 77.4 | 1445 | 21.55 | 5765.7 | 2957.9 | 2863.5 | 4228.1 | 1218 | 0.68245 | 6.092
2024-12-10 | 1:04 | Data | 0 | 32.663 | 30.556 | 196.219 | 7.64 | 184.593 | 2225.23 | 25.78 | 43.109 | 6.37 | 1.389 | 4.705 | 8879.39 | 1.971 | 98.1 | 77.2 | 1446 | 21.6 | 5771.6 | 2956.6 | 2883.4 | 4244 | 1218 | 0.67897 | 6.094
2024-12-10 | 1:04 | Data | 0 | 32.048 | 30.408 | 196.083 | 7.63 | 184.548 | 2222.52 | 25.78 | 43.2 | 6.37 | 1.377 | 4.692 | 8883.91 | 2.228 | 98.1 | 77.3 | 1444 | 21.6 | 5774.5 | 2981.5 | 2879.9 | 4257.6 | 1218 | 0.68183 | 6.07
2024-12-10 | 1:04 | Data | 0 | 32.413 | 30.3 | 196.128 | 7.63 | 184.639 | 2218.91 | 25.78 | 43.019 | 6.37 | 1.371 | 4.737 | 8879.39 | 1.985 | 98.1 | 77.6 | 1442 | 21.46 | 5771.6 | 2949.5 | 2886 | 4243.3 | 1218 | 0.67875 | 6.108
2024-12-10 | 1:04 | Data | 0 | 32.602 | 30.651 | 196.128 | 7.64 | 184.593 | 2218.91 | 25.78 | 43.2 | 6.37 | 1.377 | 4.705 | 8861.3 | 2.073 | 98.1 | 77.4 | 1442 | 21.6 | 5759.8 | 2965.5 | 2900.6 | 4260.8 | 1218 | 0.67845 | 6.081
2024-12-10 | 1:04 | Data | 0 | 32.582 | 30.442 | 196.128 | 7.63 | 184.593 | 2214.39 | 25.78 | 43.109 | 6.37 | 1.378 | 4.702 | 8856.78 | 2.201 | 98 | 77.3 | 1439 | 21.64 | 5756.9 | 2958.1 | 2891.9 | 4251.5 | 1218 | 0.67959 | 6.081
2024-12-10 | 1:04 | Data | 0 | 32.285 | 30.192 | 196.083 | 7.64 | 184.639 | 2218.91 | 25.78 | 43.109 | 6.37 | 1.374 | 4.699 | 8838.69 | 2.066 | 98.1 | 77.4 | 1442 | 21.6 | 5745.1 | 2971.9 | 2873.6 | 4251.1 | 1218 | 0.68182 | 6.073
2024-12-10 | 1:04 | Data | 0 | 32.183 | 30.178 | 196.173 | 7.63 | 184.593 | 2221.62 | 25.77 | 43.2 | 6.37 | 1.369 | 4.692 | 8816.08 | 1.857 | 98.1 | 77.4 | 1444 | 21.6 | 5730.5 | 2963.9 | 2889.7 | 4259.7 | 1218 | 0.67793 | 6.061
2024-12-10 | 1:04 | Data | 0 | 32.487 | 30.59 | 196.128 | 7.64 | 184.503 | 2220.72 | 25.78 | 43.109 | 6.36 | 1.372 | 4.732 | 8856.78 | 2.194 | 98.1 | 77.5 | 1443 | 21.55 | 5756.9 | 2960.7 | 2898.7 | 4256.4 | 1218 | 0.67762 | 6.104
2024-12-10 | 1:04 | Data | 0 | 32.595 | 30.415 | 195.992 | 7.63 | 184.548 | 2218.91 | 25.78 | 43.2 | 6.37 | 1.373 | 4.74 | 8513.09 | 2.106 | 98.1 | 77.6 | 1442 | 21.6 | 5533.5 | 2940.9 | 2889.9 | 4240.5 | 1218 | 0.67543 | 6.112
2024-12-10 | 1:04 | Data | 0 | 32.494 | 30.3 | 195.992 | 7.64 | 184.548 | 2218.91 | 25.79 | 43.29 | 6.37 | 1.367 | 4.712 | 8526.66 | 2.079 | 98.1 | 77.5 | 1442 | 21.6 | 5542.3 | 2957.3 | 2921.7 | 4274.1 | 1218 | 0.67425 | 6.08
2024-12-10 | 1:05 | Data | 0 | 32.521 | 30.442 | 196.264 | 7.63 | 184.865 | 2216.2 | 25.78 | 43.2 | 6.37 | 1.377 | 4.711 | 8535.7 | 1.971 | 98 | 77.4 | 1440 | 21.6 | 5548.2 | 2966 | 2913.4 | 4272.5 | 1218 | 0.67413 | 6.088
2024-12-10 | 1:05 | Data | 0 | 32.386 | 30.806 | 196.083 | 7.64 | 184.593 | 2212.58 | 25.78 | 43.2 | 6.37 | 1.374 | 4.72 | 8526.66 | 2.073 | 98 | 77.5 | 1439 | 21.6 | 5542.3 | 2961.9 | 2946.7 | 4290.4 | 1218 | 0.67376 | 6.093
2024-12-10 | 1:05 | Data | 0 | 32.453 | 30.205 | 196.083 | 7.64 | 184.684 | 2214.39 | 25.78 | 43.109 | 6.37 | 1.381 | 4.728 | 8513.09 | 2.1 | 98 | 77.4 | 1439 | 21.6 | 5533.5 | 2960.3 | 2940.1 | 4283.9 | 1218 | 0.67408 | 6.109
2024-12-10 | 1:05 | Data | 0 | 32.723 | 30.597 | 196.128 | 7.64 | 184.684 | 2216.2 | 25.79 | 43.2 | 6.37 | 1.381 | 4.724 | 8522.14 | 2.295 | 98 | 77.4 | 1441 | 21.6 | 5539.4 | 2953.4 | 2932.9 | 4275.7 | 1218 | 0.67379 | 6.104
2024-12-10 | 1:05 | Data | 0 | 32.494 | 30.28 | 196.128 | 7.63 | 184.548 | 2213.49 | 25.78 | 43.109 | 6.37 | 1.381 | 4.72 | 8517.61 | 2.383 | 98.1 | 77.4 | 1439 | 21.55 | 5536.4 | 2964 | 2923.6 | 4272 | 1218 | 0.67711 | 6.102
2024-12-10 | 1:05 | Data | 0 | 32.723 | 30.415 | 196.083 | 7.64 | 184.639 | 2213.49 | 25.78 | 43.2 | 6.37 | 1.381 | 4.729 | 8535.7 | 2.1 | 98 | 77.4 | 1439 | 21.6 | 5548.2 | 2961.1 | 2946.5 | 4287.6 | 1218 | 0.67371 | 6.11
2024-12-10 | 1:05 | Data | 0 | 32.514 | 30.246 | 196.083 | 7.63 | 184.503 | 2213.49 | 25.78 | 43.2 | 6.37 | 1.373 | 4.722 | 8544.75 | 2.052 | 98.1 | 77.5 | 1439 | 21.6 | 5554.1 | 2977.4 | 2944.9 | 4300 | 1218 | 0.67493 | 6.095
2024-12-10 | 1:05 | Data | 0 | 32.717 | 30.469 | 196.128 | 7.64 | 184.684 | 2214.39 | 25.78 | 43.109 | 6.37 | 1.367 | 4.703 | 8549.27 | 2.086 | 98 | 77.5 | 1439 | 21.6 | 5557 | 2965.5 | 2894.6 | 4257.6 | 1218 | 0.67785 | 6.07
2024-12-10 | 1:05 | Data | 0 | 32.271 | 30.185 | 195.902 | 7.63 | 184.548 | 2213.49 | 25.77 | 43.2 | 6.37 | 1.372 | 4.708 | 8562.84 | 2.079 | 98.1 | 77.4 | 1439 | 21.55 | 5565.8 | 2966.1 | 2896.7 | 4262.8 | 1218 | 0.67787 | 6.08
2024-12-10 | 1:05 | Data | 0 | 32.582 | 30.529 | 196.128 | 7.63 | 184.593 | 2213.49 | 25.78 | 43.2 | 6.37 | 1.375 | 4.702 | 8549.27 | 2.167 | 98 | 77.4 | 1439 | 21.6 | 5557 | 2958.9 | 2892.4 | 4252.7 | 1218 | 0.67921 | 6.077
2024-12-10 | 1:05 | Data | 0 | 32.264 | 30.401 | 195.902 | 7.64 | 184.593 | 2213.49 | 25.78 | 43.2 | 6.37 | 1.363 | 4.712 | 8553.79 | 2.066 | 98 | 77.6 | 1439 | 21.6 | 5560 | 2963.9 | 2876.7 | 4249.6 | 1218 | 0.68023 | 6.075
2024-12-10 | 1:05 | Data | 0 | 32.298 | 30.192 | 196.219 | 7.64 | 184.639 | 2213.49 | 25.79 | 43.109 | 6.37 | 1.374 | 4.732 | 8549.27 | 2.079 | 98 | 77.5 | 1439 | 21.6 | 5557 | 2955.6 | 2876.4 | 4240 | 1218 | 0.68016 | 6.106
2024-12-10 | 1:05 | Data | 0 | 32.271 | 30.293 | 196.083 | 7.64 | 184.593 | 2213.49 | 25.78 | 43.2 | 6.38 | 1.377 | 4.728 | 8567.36 | 1.884 | 98 | 77.4 | 1439 | 21.6 | 5568.8 | 2950.5 | 2880 | 4238.7 | 1218 | 0.67921 | 6.105
2024-12-10 | 1:05 | Data | 0 | 32.71 | 30.205 | 196.083 | 7.64 | 184.639 | 2213.49 | 25.78 | 43.109 | 6.37 | 1.374 | 4.683 | 8599.01 | 2.329 | 98 | 77.3 | 1438 | 21.6 | 5589.4 | 2965.4 | 2895.5 | 4258.1 | 1218 | 0.68004 | 6.055
2024-12-10 | 1:05 | Data | 0 | 32.771 | 30.651 | 196.173 | 7.64 | 184.684 | 2212.58 | 25.78 | 43.29 | 6.37 | 1.37 | 4.706 | 8621.63 | 2.093 | 98.1 | 77.4 | 1439 | 21.6 | 5604.1 | 2972.7 | 2884.1 | 4259.6 | 1218 | 0.68033 | 6.075
2024-12-10 | 1:05 | Data | 0 | 32.575 | 30.421 | 196.219 | 7.64 | 184.729 | 2213.49 | 25.78 | 43.2 | 6.37 | 1.377 | 4.707 | 8648.76 | 1.924 | 98 | 77.4 | 1439 | 21.6 | 5621.7 | 2971.8 | 2921.8 | 4278.3 | 1218 | 0.67809 | 6.083
2024-12-10 | 1:05 | Data | 0 | 32.264 | 30.313 | 195.811 | 7.63 | 184.593 | 2213.49 | 25.78 | 43.109 | 6.37 | 1.375 | 4.717 | 8648.76 | 2.052 | 98.1 | 77.4 | 1439 | 21.55 | 5621.7 | 2967.9 | 2925.6 | 4280.8 | 1218 | 0.67621 | 6.092
2024-12-10 | 1:06 | Data | 0 | 32.271 | 30.401 | 196.083 | 7.64 | 184.593 | 2215.29 | 25.78 | 43.29 | 6.37 | 1.364 | 4.72 | 8662.33 | 2.079 | 98 | 77.6 | 1440 | 21.64 | 5630.5 | 2968.4 | 2939.7 | 4293.4 | 1218 | 0.67525 | 6.083
2024-12-10 | 1:06 | Data | 0 | 32.298 | 30.415 | 196.128 | 7.64 | 184.548 | 2213.49 | 25.78 | 43.2 | 6.37 | 1.367 | 4.714 | 8653.28 | 1.857 | 98 | 77.5 | 1439 | 21.6 | 5624.6 | 2946.3 | 2913 | 4256.4 | 1218 | 0.67447 | 6.083
2024-12-10 | 1:06 | Data | 0 | 32.379 | 30.198 | 195.992 | 7.64 | 184.548 | 2213.49 | 25.78 | 43.2 | 6.37 | 1.367 | 4.688 | 8653.28 | 2.086 | 98.1 | 77.4 | 1439 | 21.6 | 5624.6 | 2965.4 | 2891 | 4255.5 | 1218 | 0.67938 | 6.055
2024-12-10 | 1:06 | Data | 0 | 32.703 | 30.415 | 196.173 | 7.64 | 184.684 | 2213.49 | 25.78 | 43.109 | 6.37 | 1.37 | 4.686 | 8648.76 | 2.174 | 98 | 77.4 | 1439 | 21.6 | 5621.7 | 2968.5 | 2899 | 4262.4 | 1218 | 0.67613 | 6.056
2024-12-10 | 1:06 | Data | 0 | 32.717 | 30.691 | 196.309 | 7.63 | 184.639 | 2213.49 | 25.78 | 43.109 | 6.37 | 1.371 | 4.699 | 8648.76 | 1.985 | 98.1 | 77.4 | 1439 | 21.55 | 5621.7 | 2970.2 | 2886.2 | 4253.9 | 1218 | 0.6806 | 6.07
2024-12-10 | 1:06 | Data | 0 | 32.777 | 30.529 | 196.173 | 7.63 | 184.639 | 2213.49 | 25.78 | 43.2 | 6.37 | 1.374 | 4.707 | 8680.41 | 2.079 | 98 | 77.4 | 1439 | 21.6 | 5642.3 | 2969.3 | 2900 | 4269.4 | 1218 | 0.67942 | 6.08
2024-12-10 | 1:06 | Data | 0 | 32.494 | 30.59 | 195.947 | 7.63 | 184.548 | 2214.39 | 25.78 | 43.29 | 6.37 | 1.386 | 4.727 | 8657.8 | 1.958 | 98 | 77.3 | 1439 | 21.64 | 5627.6 | 2961.2 | 2908.3 | 4263.8 | 1218.1 | 0.67776 | 6.113
2024-12-10 | 1:06 | Data | 0 | 32.548 | 30.307 | 196.128 | 7.64 | 184.684 | 2216.2 | 25.77 | 43.2 | 6.37 | 1.377 | 4.694 | 8666.85 | 2.1 | 98.1 | 77.3 | 1441 | 21.6 | 5633.5 | 2962.5 | 2876.7 | 4246.4 | 1218.1 | 0.67975 | 6.069
2024-12-10 | 1:06 | Data | 0 | 32.771 | 30.415 | 196.309 | 7.63 | 184.684 | 2217.1 | 25.78 | 43.2 | 6.36 | 1.367 | 4.725 | 8680.41 | 1.992 | 98.1 | 77.6 | 1441 | 21.6 | 5642.3 | 2956.9 | 2894.4 | 4251.9 | 1218.1 | 0.67876 | 6.092
2024-12-10 | 1:06 | Data | 0 | 32.42 | 30.347 | 196.173 | 7.63 | 184.548 | 2216.2 | 25.79 | 43.109 | 6.37 | 1.367 | 4.742 | 8684.94 | 2.187 | 98.1 | 77.6 | 1440 | 21.55 | 5645.2 | 2966.1 | 2888.5 | 4254.9 | 1218.1 | 0.68031 | 6.112
2024-12-10 | 1:06 | Data | 0 | 32.332 | 30.388 | 196.128 | 7.64 | 184.593 | 2212.58 | 25.78 | 43.2 | 6.37 | 1.371 | 4.719 | 8689.46 | 1.904 | 98.1 | 77.5 | 1438 | 21.55 | 5648.1 | 2958.3 | 2880.3 | 4244.6 | 1218.1 | 0.67918 | 6.089
2024-12-10 | 1:06 | Data | 0 | 32.933 | 30.475 | 196.309 | 7.64 | 184.684 | 2216.2 | 25.78 | 43.2 | 6.37 | 1.387 | 4.71 | 8698.5 | 2.052 | 98.1 | 77.2 | 1441 | 21.6 | 5654 | 2959.1 | 2888.9 | 4250.2 | 1218.1 | 0.67805 | 6.097
2024-12-10 | 1:06 | Data | 0 | 32.636 | 30.225 | 196.083 | 7.64 | 184.593 | 2213.49 | 25.78 | 43.2 | 6.37 | 1.379 | 4.738 | 8716.59 | 2.113 | 98 | 77.5 | 1439 | 21.6 | 5665.8 | 2962.4 | 2912 | 4267.6 | 1218.1 | 0.67674 | 6.117
2024-12-10 | 1:06 | Data | 0 | 32.933 | 30.698 | 196.309 | 7.63 | 184.774 | 2213.49 | 25.78 | 43.2 | 6.37 | 1.375 | 4.723 | 8752.77 | 1.911 | 98.1 | 77.5 | 1439 | 21.55 | 5689.3 | 2969.3 | 2915.1 | 4278.8 | 1218.1 | 0.67636 | 6.097
2024-12-10 | 1:06 | Data | 0 | 32.609 | 30.428 | 196.173 | 7.64 | 184.593 | 2213.49 | 25.78 | 43.2 | 6.37 | 1.367 | 4.73 | 8734.68 | 2.154 | 98 | 77.5 | 1439 | 21.55 | 5677.5 | 2975.7 | 2892.4 | 4264 | 1218.1 | 0.68084 | 6.099
2024-12-10 | 1:06 | Data | 0 | 32.494 | 30.246 | 196.083 | 7.63 | 184.639 | 2214.39 | 25.79 | 43.2 | 6.37 | 1.382 | 4.741 | 8730.16 | 2.025 | 98 | 77.4 | 1439 | 21.6 | 5674.6 | 2953.1 | 2864.5 | 4227.1 | 1218.1 | 0.68116 | 6.123
2024-12-10 | 1:06 | Data | 0 | 32.042 | 30.408 | 196.128 | 7.64 | 184.593 | 2211.68 | 25.78 | 43.2 | 6.37 | 1.386 | 4.746 | 8721.11 | 2.174 | 98 | 77.4 | 1437 | 21.55 | 5668.7 | 2965.3 | 2918.2 | 4284.3 | 1218.1 | 0.67807 | 6.132
2024-12-10 | 1:06 | Data | 0 | 32.48 | 30.617 | 196.173 | 7.64 | 184.639 | 2211.68 | 25.79 | 43.2 | 6.37 | 1.373 | 4.709 | 8716.59 | 2.086 | 98.1 | 77.4 | 1437 | 21.55 | 5665.8 | 2964.9 | 2897.8 | 4258.9 | 1218.1 | 0.67945 | 6.082
2024-12-10 | 1:07 | Data | 0 | 32.271 | 30.415 | 196.173 | 7.64 | 184.639 | 2214.39 | 25.78 | 42.929 | 6.37 | 1.371 | 4.694 | 8716.59 | 1.857 | 98.1 | 77.4 | 1439 | 21.51 | 5665.8 | 2973.1 | 2902.5 | 4266.8 | 1218.1 | 0.68035 | 6.064
2024-12-10 | 1:07 | Data | 0 | 32.811 | 30.448 | 196.309 | 7.64 | 184.684 | 2213.49 | 25.78 | 43.2 | 6.37 | 1.381 | 4.668 | 8721.11 | 2.262 | 98 | 77.2 | 1439 | 21.6 | 5668.7 | 2967.3 | 2879.7 | 4250.4 | 1218.1 | 0.68161 | 6.048
2024-12-10 | 1:07 | Data | 0 | 32.285 | 30.361 | 196.083 | 7.64 | 184.593 | 2211.68 | 25.78 | 43.2 | 6.37 | 1.376 | 4.699 | 8707.55 | 1.971 | 98 | 77.4 | 1437 | 21.6 | 5659.9 | 2982.9 | 2862.6 | 4249.4 | 1218.1 | 0.6857 | 6.074
2024-12-10 | 1:07 | Data | 0 | 32.44 | 30.415 | 196.128 | 7.63 | 184.639 | 2218.91 | 25.78 | 43.109 | 6.37 | 1.376 | 4.72 | 8716.59 | 2.201 | 98.1 | 77.4 | 1442 | 21.55 | 5665.8 | 2989.1 | 2876.3 | 4259.8 | 1218.1 | 0.6819 | 6.094
2024-12-10 | 1:07 | Data | 0 | 32.494 | 30.421 | 196.128 | 7.63 | 184.639 | 2218 | 25.8 | 43.2 | 6.37 | 1.374 | 4.717 | 8712.07 | 2.052 | 98.1 | 77.4 | 1442 | 21.55 | 5662.8 | 2961.2 | 2866.9 | 4238.2 | 1218.1 | 0.68216 | 6.091
2024-12-10 | 1:07 | Data | 0 | 32.548 | 30.219 | 196.219 | 7.63 | 184.684 | 2220.72 | 25.79 | 43.2 | 6.37 | 1.358 | 4.69 | 8716.59 | 2.241 | 98.1 | 77.5 | 1443 | 21.6 | 5665.8 | 2971.3 | 2860.3 | 4238.2 | 1218.1 | 0.68491 | 6.05
2024-12-10 | 1:07 | Data | 0 | 32.332 | 30.3 | 196.083 | 7.64 | 184.548 | 2222.52 | 25.77 | 43.2 | 6.37 | 1.377 | 4.682 | 8684.94 | 2.181 | 98.1 | 77.3 | 1445 | 21.55 | 5645.2 | 2965.6 | 2887.4 | 4257.2 | 1218.1 | 0.67908 | 6.059
2024-12-10 | 1:07 | Data | 0 | 32.804 | 30.475 | 196.173 | 7.64 | 184.729 | 2222.52 | 25.78 | 43.2 | 6.37 | 1.384 | 4.711 | 8716.59 | 2.275 | 98.1 | 77.3 | 1445 | 21.6 | 5665.8 | 2973.2 | 2895.8 | 4266.6 | 1218.1 | 0.68104 | 6.095
2024-12-10 | 1:07 | Data | 0 | 32.406 | 30.482 | 196.264 | 7.63 | 184.593 | 2223.43 | 25.78 | 43.109 | 6.37 | 1.367 | 4.723 | 8721.11 | 1.998 | 98.1 | 77.5 | 1445 | 21.6 | 5668.7 | 2957.5 | 2857.1 | 4227.3 | 1218.1 | 0.68339 | 6.091
2024-12-10 | 1:07 | Data | 0 | 32.332 | 30.212 | 196.128 | 7.64 | 184.639 | 2221.62 | 25.78 | 43.2 | 6.37 | 1.367 | 4.729 | 8721.11 | 2.032 | 98.1 | 77.6 | 1445 | 21.6 | 5668.7 | 2974.8 | 2877.5 | 4254.6 | 1218.1 | 0.68298 | 6.094
2024-12-10 | 1:07 | Data | 0 | 32.379 | 30.212 | 196.128 | 7.64 | 184.593 | 2222.52 | 25.78 | 43.2 | 6.36 | 1.375 | 4.73 | 8698.5 | 2.174 | 98.1 | 77.5 | 1445 | 21.6 | 5654 | 2975.4 | 2880 | 4256.6 | 1218.1 | 0.68193 | 6.103
2024-12-10 | 1:07 | Data | 0 | 32.494 | 30.415 | 196.128 | 7.64 | 184.593 | 2222.52 | 25.78 | 43.2 | 6.37 | 1.381 | 4.727 | 8689.46 | 2.079 | 98.1 | 77.4 | 1445 | 21.6 | 5648.1 | 2940.4 | 2846.5 | 4206.1 | 1218.1 | 0.6834 | 6.108
2024-12-10 | 1:07 | Data | 0 | 32.507 | 30.415 | 196.219 | 7.64 | 184.729 | 2223.43 | 25.78 | 43.109 | 6.37 | 1.383 | 4.734 | 8680.41 | 2.073 | 98.1 | 77.4 | 1445 | 21.55 | 5642.3 | 2964.6 | 2848.3 | 4228.3 | 1218.1 | 0.68439 | 6.116
2024-12-10 | 1:07 | Data | 0 | 32.811 | 30.266 | 196.264 | 7.63 | 184.684 | 2222.52 | 25.78 | 43.019 | 6.37 | 1.379 | 4.724 | 8680.41 | 2.322 | 98.1 | 77.4 | 1445 | 21.46 | 5642.3 | 2953 | 2850.8 | 4218.8 | 1218.1 | 0.68355 | 6.102
2024-12-10 | 1:07 | Data | 0 | 32.298 | 30.388 | 196.173 | 7.64 | 184.639 | 2222.52 | 25.78 | 43.2 | 6.37 | 1.377 | 4.725 | 8671.37 | 2.052 | 98.1 | 77.4 | 1445 | 21.6 | 5636.4 | 2972.6 | 2862.5 | 4239.7 | 1218.1 | 0.68406 | 6.102
2024-12-10 | 1:07 | Data | 0 | 32.609 | 30.556 | 196.264 | 7.63 | 184.774 | 2225.23 | 25.78 | 43.2 | 6.37 | 1.374 | 4.726 | 8680.41 | 2.079 | 98.1 | 77.5 | 1446 | 21.55 | 5642.3 | 2987.2 | 2868.6 | 4255.1 | 1218.1 | 0.68562 | 6.099
2024-12-10 | 1:07 | Data | 0 | 32.501 | 30.273 | 196.173 | 7.64 | 184.593 | 2225.23 | 25.79 | 43.741 | 6.37 | 1.373 | 4.74 | 8671.37 | 1.978 | 98 | 77.5 | 1446 | 21.87 | 5636.4 | 2952.2 | 2859.9 | 4228.7 | 1218.1 | 0.68149 | 6.112
2024-12-10 | 1:08 | Data | 0 | 32.602 | 30.421 | 196.219 | 7.64 | 184.639 | 2224.33 | 25.78 | 43.2 | 6.37 | 1.377 | 4.701 | 8680.41 | 2.106 | 98.1 | 77.3 | 1446 | 21.6 | 5642.3 | 2962 | 2856.1 | 4228.6 | 1218.1 | 0.68397 | 6.077
2024-12-10 | 1:08 | Data | 0 | 32.663 | 30.361 | 196.219 | 7.64 | 184.639 | 2225.23 | 25.8 | 43.109 | 6.37 | 1.37 | 4.709 | 8671.37 | 2.079 | 98.1 | 77.5 | 1446 | 21.55 | 5636.4 | 2975.3 | 2875.9 | 4253 | 1218.1 | 0.68231 | 6.078
2024-12-10 | 1:08 | Data | 0 | 32.386 | 30.415 | 196.128 | 7.63 | 184.684 | 2227.95 | 25.78 | 43.2 | 6.36 | 1.362 | 4.716 | 8689.46 | 1.863 | 98.1 | 77.6 | 1448 | 21.6 | 5648.1 | 2970.5 | 2883.9 | 4260.7 | 1218.1 | 0.6798 | 6.079
2024-12-10 | 1:08 | Data | 0 | 32.494 | 30.388 | 196.219 | 7.64 | 184.729 | 2223.43 | 25.78 | 43.109 | 6.37 | 1.369 | 4.704 | 8693.98 | 2.187 | 98.1 | 77.5 | 1445 | 21.55 | 5651.1 | 2989.9 | 2877.8 | 4267.9 | 1218.1 | 0.6834 | 6.074
2024-12-10 | 1:08 | Data | 0 | 32.332 | 30.192 | 196.083 | 7.63 | 184.684 | 2218.91 | 25.79 | 43.2 | 6.37 | 1.38 | 4.71 | 8703.03 | 1.911 | 98.1 | 77.3 | 1442 | 21.6 | 5657 | 2987.1 | 2875.7 | 4263 | 1218.1 | 0.6852 | 6.09
2024-12-10 | 1:08 | Data | 0 | 32.467 | 30.408 | 196.083 | 7.63 | 184.593 | 2225.23 | 25.79 | 43.109 | 6.37 | 1.373 | 4.731 | 8703.03 | 2.086 | 98.1 | 77.5 | 1446 | 21.55 | 5657 | 2987.1 | 2850.4 | 4247.3 | 1218.1 | 0.68633 | 6.104
2024-12-10 | 1:08 | Data | 0 | 32.609 | 30.421 | 196.219 | 7.63 | 184.639 | 2223.43 | 25.78 | 43.109 | 6.37 | 1.374 | 4.711 | 8703.03 | 2.174 | 98.1 | 77.4 | 1445 | 21.6 | 5657 | 2987.6 | 2877.8 | 4265.3 | 1218.1 | 0.68317 | 6.084
2024-12-10 | 1:08 | Data | 0 | 32.305 | 30.361 | 196.128 | 7.63 | 184.684 | 2220.72 | 25.78 | 43.2 | 6.37 | 1.377 | 4.701 | 8703.03 | 2.086 | 98.1 | 77.3 | 1442 | 21.55 | 5657 | 2983.6 | 2871.6 | 4258.5 | 1218.2 | 0.68328 | 6.076
2024-12-10 | 1:08 | Data | 0 | 32.339 | 30.219 | 196.264 | 7.64 | 184.774 | 2216.2 | 25.78 | 43.109 | 6.37 | 1.366 | 4.73 | 8693.98 | 2.039 | 98.1 | 77.6 | 1441 | 21.55 | 5651.1 | 2981.3 | 2883.7 | 4265.6 | 1218.2 | 0.68245 | 6.094
2024-12-10 | 1:08 | Data | 0 | 32.494 | 30.3 | 196.173 | 7.63 | 184.639 | 2216.2 | 25.78 | 43.2 | 6.37 | 1.369 | 4.734 | 8703.03 | 2.086 | 98.1 | 77.6 | 1441 | 21.6 | 5657 | 2989.2 | 2876.6 | 4266.9 | 1218.2 | 0.68349 | 6.104
2024-12-10 | 1:08 | Data | 0 | 32.352 | 30.307 | 196.219 | 7.64 | 184.774 | 2220.72 | 25.77 | 43.2 | 6.37 | 1.377 | 4.714 | 8716.59 | 2.086 | 98.1 | 77.4 | 1442 | 21.6 | 5665.8 | 3006.8 | 2882 | 4275.8 | 1218.2 | 0.68595 | 6.092
2024-12-10 | 1:08 | Data | 0 | 32.487 | 30.415 | 196.219 | 7.64 | 184.639 | 2218.91 | 25.78 | 43.2 | 6.37 | 1.376 | 4.725 | 8689.46 | 2.079 | 98.1 | 77.5 | 1442 | 21.55 | 5648.1 | 2994.9 | 2864.1 | 4263.2 | 1218.2 | 0.68546 | 6.101
2024-12-10 | 1:08 | Data | 0 | 32.575 | 30.401 | 196.128 | 7.64 | 184.639 | 2218.91 | 25.78 | 43.2 | 6.37 | 1.384 | 4.694 | 8698.5 | 1.877 | 98.1 | 77.2 | 1442 | 21.6 | 5654 | 2992 | 2867.5 | 4262.7 | 1218.2 | 0.68494 | 6.078
2024-12-10 | 1:08 | Data | 0 | 32.548 | 30.3 | 196.128 | 7.64 | 184.684 | 2218 | 25.78 | 43.109 | 6.37 | 1.377 | 4.732 | 8712.07 | 1.911 | 98.1 | 77.5 | 1442 | 21.6 | 5662.8 | 2994 | 2861.1 | 4260.7 | 1218.2 | 0.68534 | 6.109
2024-12-10 | 1:08 | Data | 0 | 32.494 | 30.651 | 196.219 | 7.64 | 184.729 | 2213.49 | 25.78 | 43.2 | 6.37 | 1.362 | 4.73 | 8707.55 | 1.971 | 98 | 77.6 | 1439 | 21.6 | 5659.9 | 3003 | 2871.4 | 4273.3 | 1218.2 | 0.6856 | 6.092
2024-12-10 | 1:08 | Data | 0 | 32.48 | 30.469 | 196.128 | 7.63 | 184.639 | 2214.39 | 25.78 | 43.109 | 6.37 | 1.374 | 4.736 | 8703.03 | 2.262 | 98 | 77.5 | 1439 | 21.6 | 5657 | 2998.4 | 2869.7 | 4265.2 | 1218.2 | 0.68425 | 6.11
2024-12-10 | 1:08 | Data | 0 | 33.041 | 30.475 | 196.264 | 7.64 | 184.729 | 2206.25 | 25.77 | 43.2 | 6.37 | 1.376 | 4.741 | 8703.03 | 2.208 | 98 | 77.5 | 1434 | 21.6 | 5657 | 3010 | 2894.3 | 4293.8 | 1218.2 | 0.6859 | 6.116
2024-12-10 | 1:08 | Data | 0 | 32.663 | 30.806 | 196.264 | 7.64 | 184.593 | 2210.77 | 25.78 | 43.2 | 6.37 | 1.379 | 4.726 | 8703.03 | 2.127 | 98.1 | 77.4 | 1437 | 21.6 | 5657 | 2979.7 | 2879.4 | 4260 | 1218.2 | 0.68296 | 6.105
2024-12-10 | 1:09 | Data | 0 | 32.285 | 30.624 | 196.219 | 7.64 | 184.729 | 2213.49 | 25.78 | 43.2 | 6.37 | 1.376 | 4.71 | 8730.16 | 2.019 | 98.1 | 77.4 | 1439 | 21.55 | 5674.6 | 2999.3 | 2867.2 | 4267.2 | 1218.2 | 0.68526 | 6.086
2024-12-10 | 1:09 | Data | 0 | 32.278 | 30.388 | 195.947 | 7.64 | 184.548 | 2213.49 | 25.78 | 43.29 | 6.37 | 1.367 | 4.723 | 8725.64 | 1.965 | 98 | 77.6 | 1439 | 21.6 | 5671.7 | 3009.8 | 2883.5 | 4285.4 | 1218.2 | 0.68537 | 6.089
2024-12-10 | 1:09 | Data | 0 | 32.494 | 30.307 | 196.128 | 7.64 | 184.593 | 2222.52 | 25.78 | 43.2 | 6.36 | 1.372 | 4.694 | 8716.59 | 2.275 | 98.1 | 77.4 | 1445 | 21.55 | 5665.8 | 2984.7 | 2892.6 | 4277.8 | 1218.2 | 0.67984 | 6.066
2024-12-10 | 1:09 | Data | 0 | 32.271 | 30.388 | 195.992 | 7.63 | 184.548 | 2216.2 | 25.78 | 43.109 | 6.37 | 1.367 | 4.702 | 8730.16 | 2.079 | 98.1 | 77.5 | 1441 | 21.6 | 5674.6 | 2989.9 | 2863.8 | 4262.3 | 1218.2 | 0.68556 | 6.068
2024-12-10 | 1:09 | Data | 0 | 32.595 | 30.435 | 196.083 | 7.64 | 184.593 | 2214.39 | 25.78 | 43.2 | 6.37 | 1.373 | 4.712 | 8707.55 | 2.275 | 98 | 77.4 | 1439 | 21.6 | 5659.9 | 2999.1 | 2880.6 | 4282.5 | 1218.2 | 0.68409 | 6.085
2024-12-10 | 1:09 | Data | 0 | 32.757 | 30.529 | 196.309 | 7.64 | 184.684 | 2216.2 | 25.78 | 43.2 | 6.37 | 1.371 | 4.702 | 8721.11 | 2.106 | 98.1 | 77.4 | 1441 | 21.6 | 5668.7 | 2999.6 | 2876.3 | 4275.6 | 1218.2 | 0.6843 | 6.074
2024-12-10 | 1:09 | Data | 0 | 32.271 | 30.185 | 195.992 | 7.63 | 184.548 | 2216.2 | 25.78 | 43.2 | 6.37 | 1.377 | 4.724 | 8703.03 | 2.079 | 98.1 | 77.4 | 1441 | 21.6 | 5657 | 2982.2 | 2868.9 | 4255.1 | 1218.2 | 0.68365 | 6.102
2024-12-10 | 1:09 | Data | 0 | 32.379 | 30.185 | 195.947 | 7.63 | 184.548 | 2217.1 | 25.77 | 43.2 | 6.37 | 1.369 | 4.721 | 8680.41 | 2.127 | 98.1 | 77.5 | 1441 | 21.6 | 5642.3 | 3005.7 | 2885.2 | 4285.8 | 1218.2 | 0.68375 | 6.09
2024-12-10 | 1:09 | Data | 0 | 32.332 | 30.617 | 196.128 | 7.64 | 184.684 | 2216.2 | 25.78 | 43.2 | 6.37 | 1.371 | 4.731 | 8693.98 | 2.079 | 98 | 77.5 | 1441 | 21.6 | 5651.1 | 3000.5 | 2879 | 4274.2 | 1218.2 | 0.68494 | 6.102
2024-12-10 | 1:09 | Data | 0 | 32.44 | 30.415 | 196.128 | 7.64 | 184.548 | 2216.2 | 25.78 | 43.2 | 6.36 | 1.373 | 4.73 | 8671.37 | 2.066 | 98.1 | 77.5 | 1440 | 21.6 | 5636.4 | 2996.6 | 2869.9 | 4266.7 | 1218.2 | 0.6846 | 6.102
2024-12-10 | 1:09 | Data | 0 | 32.379 | 30.496 | 195.947 | 7.64 | 184.548 | 2217.1 | 25.78 | 43.109 | 6.37 | 1.373 | 4.708 | 8648.76 | 2.093 | 98.1 | 77.4 | 1442 | 21.6 | 5621.7 | 2912.9 | 2868.5 | 4198.5 | 1218.2 | 0.67712 | 6.081
2024-12-10 | 1:09 | Data | 0 | 32.548 | 30.192 | 196.173 | 7.64 | 184.639 | 2220.72 | 25.78 | 43.2 | 6.37 | 1.374 | 4.702 | 8662.33 | 2.046 | 98.1 | 77.4 | 1443 | 21.6 | 5630.5 | 2927 | 2876.7 | 4215.1 | 1218.2 | 0.67906 | 6.075
2024-12-10 | 1:09 | Data | 0 | 32.298 | 30.408 | 196.128 | 7.64 | 184.639 | 2218.91 | 25.78 | 43.2 | 6.37 | 1.375 | 4.702 | 8680.41 | 1.978 | 98.1 | 77.4 | 1443 | 21.6 | 5642.3 | 2907.7 | 2851.3 | 4181.6 | 1218.2 | 0.6774 | 6.077
2024-12-10 | 1:09 | Data | 0 | 32.676 | 30.442 | 196.219 | 7.63 | 184.729 | 2218.91 | 25.78 | 43.2 | 6.37 | 1.377 | 4.706 | 8684.94 | 1.951 | 98.1 | 77.4 | 1442 | 21.6 | 5645.2 | 2927.7 | 2886.6 | 4218.3 | 1218.2 | 0.67856 | 6.082
2024-12-10 | 1:09 | Data | 0 | 32.75 | 30.307 | 196.083 | 7.64 | 184.593 | 2218.91 | 25.78 | 43.2 | 6.37 | 1.376 | 4.715 | 8693.98 | 2.1 | 98.1 | 77.4 | 1443 | 21.6 | 5651.1 | 2931.7 | 2861.2 | 4199.1 | 1218.2 | 0.68018 | 6.091
2024-12-10 | 1:09 | Data | 0 | 32.831 | 30.421 | 196.219 | 7.63 | 184.684 | 2218.91 | 25.78 | 43.109 | 6.37 | 1.367 | 4.705 | 8684.94 | 2.032 | 98.1 | 77.5 | 1442 | 21.6 | 5645.2 | 2912.6 | 2851.9 | 4191.5 | 1218.2 | 0.67878 | 6.072
2024-12-10 | 1:09 | Data | 0 | 32.494 | 30.408 | 196.173 | 7.63 | 184.684 | 2218.91 | 25.78 | 43.109 | 6.37 | 1.367 | 4.71 | 8693.98 | 2.086 | 98.1 | 77.5 | 1442 | 21.55 | 5651.1 | 2911.3 | 2857.5 | 4191.6 | 1218.2 | 0.67916 | 6.076
2024-12-10 | 1:09 | Data | 0 | 32.494 | 30.307 | 196.173 | 7.63 | 184.593 | 2224.33 | 25.78 | 43.2 | 6.37 | 1.38 | 4.725 | 8689.46 | 2.208 | 98.1 | 77.4 | 1446 | 21.55 | 5648.1 | 2927.6 | 2860.9 | 4203.1 | 1218.2 | 0.68109 | 6.106
2024-12-10 | 1:10 | Data | 0 | 32.44 | 30.388 | 196.173 | 7.63 | 184.639 | 2225.23 | 25.79 | 43.2 | 6.38 | 1.374 | 4.728 | 8693.98 | 2.127 | 98.1 | 77.5 | 1446 | 21.6 | 5651.1 | 2944.1 | 2877.4 | 4234.1 | 1218.2 | 0.67801 | 6.102
2024-12-10 | 1:10 | Data | 0 | 32.406 | 30.144 | 196.128 | 7.63 | 184.639 | 2225.23 | 25.77 | 43.2 | 6.37 | 1.376 | 4.723 | 8689.46 | 2.174 | 98.1 | 77.4 | 1446 | 21.55 | 5648.1 | 2968.9 | 2876.2 | 4250.2 | 1218.2 | 0.68157 | 6.1
2024-12-10 | 1:10 | Data | 0 | 32.588 | 30.192 | 196.128 | 7.63 | 184.684 | 2224.33 | 25.78 | 43.29 | 6.37 | 1.373 | 4.72 | 8693.98 | 2.133 | 98.1 | 77.5 | 1446 | 21.6 | 5651.1 | 2958.7 | 2867.3 | 4239.2 | 1218.2 | 0.68182 | 6.092
2024-12-10 | 1:10 | Data | 0 | 32.271 | 30.523 | 196.128 | 7.63 | 184.593 | 2225.23 | 25.78 | 43.2 | 6.37 | 1.377 | 4.712 | 8671.37 | 1.904 | 98.1 | 77.4 | 1446 | 21.6 | 5636.4 | 2963.2 | 2849.4 | 4233.4 | 1218.2 | 0.68212 | 6.09
2024-12-10 | 1:10 | Data | 0 | 32.15 | 30.401 | 196.173 | 7.64 | 184.503 | 2225.23 | 25.78 | 43.2 | 6.36 | 1.379 | 4.724 | 8671.37 | 2.039 | 98.1 | 77.4 | 1446 | 21.6 | 5636.4 | 2977.2 | 2866.7 | 4250.1 | 1218.2 | 0.68379 | 6.102
2024-12-10 | 1:10 | Data | 0 | 32.791 | 30.637 | 196.264 | 7.63 | 184.593 | 2215.29 | 25.78 | 43.2 | 6.37 | 1.367 | 4.728 | 8662.33 | 2.289 | 98 | 77.6 | 1439 | 21.6 | 5630.5 | 2975.5 | 2881.6 | 4259.1 | 1218.2 | 0.68283 | 6.095
2024-12-10 | 1:10 | Data | 0 | 32.379 | 30.239 | 196.128 | 7.63 | 184.548 | 2218.91 | 25.78 | 43.2 | 6.37 | 1.379 | 4.706 | 8693.98 | 2.073 | 98.1 | 77.3 | 1442 | 21.55 | 5651.1 | 2970.7 | 2857.5 | 4236.9 | 1218.2 | 0.68499 | 6.085
2024-12-10 | 1:10 | Data | 0 | 32.237 | 30.401 | 196.083 | 7.63 | 184.548 | 2218.91 | 25.77 | 43.2 | 6.37 | 1.386 | 4.704 | 8693.98 | 2.16 | 98.1 | 77.2 | 1443 | 21.6 | 5651.1 | 2976.8 | 2895.7 | 4266 | 1218.3 | 0.67997 | 6.091
2024-12-10 | 1:10 | Data | 0 | 32.264 | 30.644 | 196.083 | 7.64 | 184.593 | 2220.72 | 25.78 | 43.2 | 6.37 | 1.374 | 4.714 | 8689.46 | 2.059 | 98.1 | 77.4 | 1442 | 21.6 | 5648.1 | 2962.1 | 2873 | 4249.2 | 1218.3 | 0.68405 | 6.087
2024-12-10 | 1:10 | Data | 0 | 32.804 | 30.644 | 196.173 | 7.63 | 184.639 | 2218.91 | 25.78 | 43.2 | 6.37 | 1.372 | 4.725 | 8703.03 | 2.235 | 98.1 | 77.5 | 1442 | 21.6 | 5657 | 2955.3 | 2894.4 | 4252.3 | 1218.3 | 0.67949 | 6.096
2024-12-10 | 1:10 | Data | 0 | 32.264 | 30.185 | 196.128 | 7.64 | 184.639 | 2218.91 | 25.78 | 43.2 | 6.37 | 1.367 | 4.72 | 8707.55 | 2.079 | 98.1 | 77.5 | 1442 | 21.6 | 5659.9 | 2983.9 | 2885.8 | 4255.7 | 1218.3 | 0.68273 | 6.085
2024-12-10 | 1:10 | Data | 0 | 32.494 | 30.732 | 196.264 | 7.64 | 184.639 | 2217.1 | 25.78 | 43.019 | 6.37 | 1.377 | 4.716 | 8693.98 | 1.917 | 98.1 | 77.4 | 1441 | 21.55 | 5651.1 | 2979.3 | 2874.9 | 4258.4 | 1218.3 | 0.68102 | 6.092
2024-12-10 | 1:10 | Data | 0 | 32.717 | 30.259 | 196.309 | 7.64 | 184.639 | 2216.2 | 25.78 | 43.2 | 6.37 | 1.371 | 4.727 | 8680.41 | 2.187 | 98.1 | 77.5 | 1441 | 21.6 | 5642.3 | 2983.9 | 2878 | 4260.2 | 1218.3 | 0.68392 | 6.097
2024-12-10 | 1:10 | Data | 0 | 32.487 | 30.212 | 195.992 | 7.63 | 184.593 | 2216.2 | 25.77 | 43.2 | 6.37 | 1.371 | 4.707 | 8680.41 | 2.079 | 98.1 | 77.4 | 1441 | 21.55 | 5642.3 | 2988.3 | 2881 | 4264.9 | 1218.3 | 0.68407 | 6.078
2024-12-10 | 1:10 | Data | 0 | 32.352 | 30.192 | 195.992 | 7.63 | 184.548 | 2221.62 | 25.78 | 43.2 | 6.37 | 1.366 | 4.733 | 8689.46 | 2.221 | 98.1 | 77.6 | 1445 | 21.6 | 5648.1 | 2987.4 | 2886.8 | 4268.8 | 1218.3 | 0.68316 | 6.099
2024-12-10 | 1:10 | Data | 0 | 32.44 | 30.232 | 195.902 | 7.63 | 184.548 | 2217.1 | 25.78 | 43.109 | 6.37 | 1.366 | 4.721 | 8689.46 | 2.086 | 98.1 | 77.6 | 1441 | 21.6 | 5648.1 | 2964.9 | 2918.1 | 4276.4 | 1218.3 | 0.67724 | 6.087
2024-12-10 | 1:10 | Data | 0 | 32.602 | 30.225 | 195.992 | 7.63 | 184.593 | 2218.91 | 25.78 | 43.2 | 6.37 | 1.375 | 4.679 | 8716.59 | 2.194 | 98.1 | 77.3 | 1442 | 21.6 | 5665.8 | 2978.9 | 2897.1 | 4266.4 | 1218.3 | 0.68146 | 6.055
2024-12-10 | 1:10 | Data | 0 | 32.372 | 30.529 | 195.992 | 7.63 | 184.593 | 2218.91 | 25.78 | 43.2 | 6.37 | 1.377 | 4.67 | 8721.11 | 2.066 | 98.1 | 77.2 | 1442 | 21.6 | 5668.7 | 2981.8 | 2892.4 | 4270.6 | 1218.3 | 0.68137 | 6.047
2024-12-10 | 1:11 | Data | 0 | 32.096 | 30.185 | 196.083 | 7.63 | 184.593 | 2218.91 | 25.78 | 43.2 | 6.37 | 1.376 | 4.704 | 8725.64 | 1.877 | 98.1 | 77.4 | 1442 | 21.6 | 5671.7 | 2979.6 | 2882.4 | 4260.5 | 1218.3 | 0.68263 | 6.08
2024-12-10 | 1:11 | Data | 0 | 32.177 | 30.07 | 195.992 | 7.64 | 184.548 | 2218.91 | 25.78 | 43.2 | 6.37 | 1.374 | 4.721 | 8730.16 | 1.911 | 98.1 | 77.5 | 1442 | 21.55 | 5674.6 | 2958.9 | 2869.8 | 4238.2 | 1218.3 | 0.68211 | 6.095
2024-12-10 | 1:11 | Data | 0 | 32.264 | 30.225 | 196.128 | 7.63 | 184.593 | 2220.72 | 25.77 | 43.2 | 6.37 | 1.367 | 4.709 | 8680.41 | 2.079 | 98.1 | 77.5 | 1443 | 21.6 | 5642.3 | 2960.2 | 2859.1 | 4226.1 | 1218.3 | 0.68458 | 6.077
2024-12-10 | 1:11 | Data | 0 | 32.507 | 30.3 | 196.128 | 7.64 | 184.684 | 2218.91 | 25.78 | 43.109 | 6.37 | 1.372 | 4.729 | 8671.37 | 2.079 | 98.1 | 77.5 | 1442 | 21.6 | 5636.4 | 2969.3 | 2863.3 | 4238.6 | 1218.3 | 0.68367 | 6.102
2024-12-10 | 1:11 | Data | 0 | 32.42 | 30.239 | 195.992 | 7.64 | 184.503 | 2218 | 25.78 | 43.109 | 6.37 | 1.37 | 4.724 | 8662.33 | 2.194 | 98.1 | 77.5 | 1442 | 21.51 | 5630.5 | 2959.6 | 2862.5 | 4233.5 | 1218.3 | 0.68296 | 6.093
2024-12-10 | 1:11 | Data | 0 | 32.069 | 30.185 | 195.947 | 7.63 | 184.548 | 2220.72 | 25.78 | 43.019 | 6.37 | 1.375 | 4.726 | 8689.46 | 1.863 | 98.1 | 77.5 | 1443 | 21.55 | 5648.1 | 2954.9 | 2869.7 | 4235.2 | 1218.3 | 0.68082 | 6.1
2024-12-10 | 1:11 | Data | 0 | 32.339 | 30.192 | 196.128 | 7.63 | 184.639 | 2221.62 | 25.8 | 43.2 | 6.37 | 1.376 | 4.729 | 8680.41 | 2.093 | 98.1 | 77.5 | 1444 | 21.55 | 5642.3 | 2955 | 2873 | 4234.2 | 1218.3 | 0.68087 | 6.104
2024-12-10 | 1:11 | Data | 0 | 32.602 | 30.246 | 195.902 | 7.64 | 184.548 | 2220.72 | 25.8 | 43.2 | 6.37 | 1.379 | 4.718 | 8680.41 | 2.093 | 98.1 | 77.4 | 1443 | 21.6 | 5642.3 | 2957.9 | 2856.6 | 4231.8 | 1218.3 | 0.68023 | 6.096
2024-12-10 | 1:11 | Data | 0 | 32.372 | 30.381 | 196.173 | 7.63 | 184.548 | 2225.23 | 25.8 | 43.29 | 6.37 | 1.384 | 4.725 | 8684.94 | 2.147 | 98.1 | 77.3 | 1446 | 21.64 | 5645.2 | 2964.5 | 2878 | 4249.3 | 1218.3 | 0.67992 | 6.109
2024-12-10 | 1:11 | Data | 0 | 32.264 | 30.016 | 195.947 | 7.63 | 184.368 | 2225.23 | 25.8 | 43.2 | 6.37 | 1.379 | 4.701 | 8671.37 | 2.079 | 98.1 | 77.3 | 1446 | 21.6 | 5636.4 | 2966.3 | 2864.8 | 4237.7 | 1218.3 | 0.6831 | 6.081
2024-12-10 | 1:11 | Data | 0 | 32.548 | 30.03 | 196.083 | 7.63 | 184.684 | 2225.23 | 25.8 | 43.2 | 6.37 | 1.384 | 4.701 | 8689.46 | 2.194 | 98.1 | 77.2 | 1446 | 21.6 | 5648.1 | 2958 | 2894.5 | 4253.6 | 1218.3 | 0.67815 | 6.086
2024-12-10 | 1:11 | Data | 0 | 32.237 | 30.185 | 195.992 | 7.64 | 184.639 | 2222.52 | 25.81 | 43.2 | 6.37 | 1.385 | 4.725 | 8689.46 | 1.924 | 98.1 | 77.3 | 1445 | 21.6 | 5648.1 | 2967.3 | 2880.2 | 4244.5 | 1218.3 | 0.68284 | 6.11
2024-12-10 | 1:11 | Data | 0 | 32.352 | 30.388 | 196.083 | 7.64 | 184.503 | 2222.52 | 25.81 | 43.109 | 6.37 | 1.372 | 4.729 | 8703.03 | 2.106 | 98.1 | 77.5 | 1445 | 21.6 | 5657 | 2965.1 | 2870.1 | 4246.5 | 1218.3 | 0.68255 | 6.101
2024-12-10 | 1:11 | Data | 0 | 32.285 | 30.185 | 196.083 | 7.63 | 184.458 | 2222.52 | 25.81 | 43.2 | 6.37 | 1.381 | 4.724 | 8693.98 | 2.093 | 98.1 | 77.4 | 1444 | 21.6 | 5651.1 | 2963 | 2862.7 | 4230.3 | 1218.3 | 0.68262 | 6.105
2024-12-10 | 1:11 | Data | 0 | 32.325 | 30.401 | 195.992 | 7.63 | 184.503 | 2220.72 | 25.8 | 43.2 | 6.37 | 1.376 | 4.721 | 8712.07 | 1.924 | 98.1 | 77.4 | 1443 | 21.6 | 5662.8 | 2957.1 | 2880.6 | 4245.3 | 1218.3 | 0.67915 | 6.095
2024-12-10 | 1:11 | Data | 0 | 32.332 | 30.198 | 196.173 | 7.63 | 184.639 | 2218.91 | 25.8 | 43.2 | 6.37 | 1.37 | 4.719 | 8716.59 | 2.039 | 98.1 | 77.5 | 1442 | 21.55 | 5665.8 | 2967.8 | 2865.9 | 4243.9 | 1218.3 | 0.68337 | 6.09
2024-12-10 | 1:11 | Data | 0 | 32.271 | 30.408 | 195.992 | 7.63 | 184.639 | 2218.91 | 25.8 | 43.2 | 6.37 | 1.379 | 4.706 | 8693.98 | 2.181 | 98.1 | 77.3 | 1442 | 21.6 | 5651.1 | 2952.7 | 2884.8 | 4241.3 | 1218.3 | 0.67944 | 6.085
2024-12-10 | 1:12 | Data | 0 | 32.426 | 30.455 | 196.128 | 7.63 | 184.458 | 2218.91 | 25.81 | 43.109 | 6.37 | 1.377 | 4.698 | 8680.41 | 2.005 | 98.1 | 77.3 | 1442 | 21.55 | 5642.3 | 2970.3 | 2886.3 | 4257.9 | 1218.3 | 0.68089 | 6.075
2024-12-10 | 1:12 | Data | 0 | 32.602 | 30.631 | 196.128 | 7.63 | 184.593 | 2221.62 | 25.8 | 43.109 | 6.37 | 1.37 | 4.709 | 8680.41 | 2.079 | 98.1 | 77.4 | 1444 | 21.6 | 5642.3 | 2949.6 | 2869.6 | 4230 | 1218.3 | 0.68144 | 6.08
2024-12-10 | 1:12 | Data | 0 | 32.258 | 30.3 | 196.128 | 7.64 | 184.548 | 2222.52 | 25.8 | 43.2 | 6.37 | 1.38 | 4.718 | 8680.41 | 2.079 | 98.1 | 77.4 | 1445 | 21.6 | 5642.3 | 2974.1 | 2874.4 | 4247.6 | 1218.3 | 0.68512 | 6.097
2024-12-10 | 1:12 | Data | 0 | 32.244 | 30.361 | 195.992 | 7.64 | 184.593 | 2222.52 | 25.8 | 43.2 | 6.37 | 1.383 | 4.709 | 8680.41 | 2.133 | 98.1 | 77.3 | 1445 | 21.6 | 5642.3 | 2988.5 | 2873.3 | 4258.3 | 1218.3 | 0.68614 | 6.092
2024-12-10 | 1:12 | Data | 0 | 32.271 | 30.178 | 195.902 | 7.64 | 184.503 | 2217.1 | 25.8 | 43.2 | 6.36 | 1.378 | 4.724 | 8662.33 | 1.924 | 98 | 77.4 | 1441 | 21.64 | 5630.5 | 2965.9 | 2854.5 | 4228.1 | 1218.3 | 0.68463 | 6.102
2024-12-10 | 1:12 | Data | 0 | 32.379 | 30.185 | 196.173 | 7.64 | 184.593 | 2217.1 | 25.8 | 43.109 | 6.37 | 1.377 | 4.732 | 8662.33 | 1.998 | 98.1 | 77.5 | 1441 | 21.55 | 5630.5 | 2961.7 | 2888.2 | 4249.3 | 1218.3 | 0.68403 | 6.11
2024-12-10 | 1:12 | Data | 0 | 32.271 | 30.239 | 195.902 | 7.63 | 184.593 | 2216.2 | 25.8 | 43.109 | 6.37 | 1.386 | 4.704 | 8671.37 | 2.086 | 98.1 | 77.2 | 1441 | 21.6 | 5636.4 | 2971.6 | 2866.1 | 4248.8 | 1218.3 | 0.68666 | 6.091
2024-12-10 | 1:12 | Data | 0 | 32.264 | 30.3 | 195.947 | 7.63 | 184.458 | 2216.2 | 25.8 | 43.019 | 6.37 | 1.384 | 4.7 | 8666.85 | 1.965 | 98.1 | 77.3 | 1441 | 21.55 | 5633.5 | 2940.4 | 2884.8 | 4238.6 | 1218.3 | 0.67555 | 6.084
2024-12-10 | 1:12 | Data | 0 | 32.494 | 30.198 | 195.947 | 7.64 | 184.503 | 2211.68 | 25.79 | 43.2 | 6.37 | 1.366 | 4.745 | 8671.37 | 2.106 | 98 | 77.7 | 1439 | 21.64 | 5636.4 | 2972.4 | 2869 | 4245 | 1218.4 | 0.68254 | 6.111
2024-12-10 | 1:12 | Data | 0 | 32.318 | 30.3 | 196.083 | 7.64 | 184.593 | 2217.1 | 25.8 | 43.2 | 6.37 | 1.373 | 4.74 | 8662.33 | 1.904 | 98.1 | 77.6 | 1441 | 21.6 | 5630.5 | 2973.1 | 2860.3 | 4238.3 | 1218.4 | 0.68442 | 6.112
2024-12-10 | 1:12 | Data | 0 | 32.548 | 30.246 | 196.128 | 7.64 | 184.639 | 2217.1 | 25.8 | 43.2 | 6.37 | 1.377 | 4.721 | 8662.33 | 2.032 | 98.1 | 77.4 | 1441 | 21.6 | 5630.5 | 2959.3 | 2863.5 | 4234.3 | 1218.4 | 0.68289 | 6.098
2024-12-10 | 1:12 | Data | 0 | 32.413 | 30.415 | 195.857 | 7.64 | 184.593 | 2216.2 | 25.8 | 43.109 | 6.37 | 1.367 | 4.73 | 8662.33 | 1.688 | 98.1 | 77.6 | 1441 | 21.6 | 5630.5 | 2984.4 | 2871.9 | 4254 | 1218.4 | 0.68479 | 6.099
2024-12-10 | 1:12 | Data | 0 | 32.291 | 30.361 | 196.173 | 7.64 | 184.639 | 2214.39 | 25.8 | 43.2 | 6.37 | 1.372 | 4.732 | 8653.28 | 1.971 | 98.1 | 77.5 | 1439 | 21.6 | 5624.6 | 2960.7 | 2852 | 4226.7 | 1218.4 | 0.68279 | 6.103
2024-12-10 | 1:12 | Data | 0 | 32.494 | 30.388 | 195.992 | 7.63 | 184.593 | 2214.39 | 25.8 | 43.109 | 6.37 | 1.369 | 4.717 | 8666.85 | 2.187 | 98.1 | 77.5 | 1439 | 21.55 | 5633.5 | 2955.2 | 2857.3 | 4228.3 | 1218.4 | 0.68146 | 6.085
2024-12-10 | 1:12 | Data | 0 | 32.663 | 30.469 | 196.173 | 7.63 | 184.639 | 2215.29 | 25.79 | 43.2 | 6.37 | 1.369 | 4.699 | 8662.33 | 2.066 | 98 | 77.4 | 1439 | 21.6 | 5630.5 | 2957.7 | 2863.2 | 4229.7 | 1218.4 | 0.68239 | 6.069
2024-12-10 | 1:12 | Data | 0 | 32.291 | 30.401 | 196.173 | 7.64 | 184.548 | 2218.91 | 25.8 | 43.2 | 6.37 | 1.37 | 4.705 | 8662.33 | 2.025 | 98.1 | 77.5 | 1442 | 21.6 | 5630.5 | 2963.9 | 2864.9 | 4235.7 | 1218.4 | 0.68189 | 6.074
2024-12-10 | 1:12 | Data | 0 | 32.534 | 30.212 | 195.992 | 7.64 | 184.639 | 2218.91 | 25.79 | 43.2 | 6.37 | 1.377 | 4.694 | 8671.37 | 2.113 | 98.1 | 77.3 | 1442 | 21.6 | 5636.4 | 2960.2 | 2851.3 | 4228.1 | 1218.4 | 0.68213 | 6.072
2024-12-10 | 1:13 | Data | 0 | 32.521 | 30.415 | 196.083 | 7.64 | 184.639 | 2218.91 | 25.8 | 43.2 | 6.37 | 1.376 | 4.719 | 8693.98 | 1.978 | 98.1 | 77.4 | 1442 | 21.6 | 5651.1 | 2961 | 2871.9 | 4239.8 | 1218.4 | 0.68298 | 6.095
2024-12-10 | 1:13 | Data | 0 | 32.305 | 30.185 | 195.902 | 7.63 | 184.458 | 2218.91 | 25.8 | 43.109 | 6.37 | 1.385 | 4.692 | 8693.98 | 1.971 | 98.1 | 77.2 | 1442 | 21.6 | 5651.1 | 2963.7 | 2876.2 | 4249.1 | 1218.4 | 0.6802 | 6.077
2024-12-10 | 1:13 | Data | 0 | 32.271 | 30.631 | 196.083 | 7.63 | 184.639 | 2218 | 25.8 | 43.29 | 6.37 | 1.387 | 4.702 | 8721.11 | 1.931 | 98 | 77.2 | 1442 | 21.64 | 5668.7 | 2974.6 | 2904.2 | 4270.1 | 1218.4 | 0.67999 | 6.09
2024-12-10 | 1:13 | Data | 0 | 32.366 | 30.361 | 196.083 | 7.64 | 184.548 | 2220.72 | 25.8 | 43.109 | 6.37 | 1.376 | 4.705 | 8716.59 | 2.248 | 98.1 | 77.4 | 1442 | 21.6 | 5665.8 | 2964.2 | 2888.1 | 4251.8 | 1218.4 | 0.68024 | 6.08
2024-12-10 | 1:13 | Data | 0 | 32.764 | 30.475 | 195.992 | 7.63 | 184.593 | 2218.91 | 25.79 | 43.019 | 6.37 | 1.37 | 4.732 | 8707.55 | 2.086 | 98.1 | 77.5 | 1442 | 21.51 | 5659.9 | 2966 | 2888.5 | 4254.8 | 1218.4 | 0.68106 | 6.102
2024-12-10 | 1:13 | Data | 0 | 32.366 | 30.185 | 196.083 | 7.64 | 184.593 | 2218.91 | 25.79 | 42.929 | 6.37 | 1.366 | 4.717 | 8671.37 | 2.241 | 98.1 | 77.5 | 1443 | 21.46 | 5636.4 | 2945.1 | 2845.6 | 4237.8 | 1218.4 | 0.68383 | 6.083
2024-12-10 | 1:13 | Data | 0 | 32.602 | 30.192 | 196.128 | 7.63 | 184.593 | 2222.52 | 25.79 | 42.838 | 6.37 | 1.371 | 4.716 | 8703.03 | 2.295 | 98.1 | 77.5 | 1445 | 21.42 | 5657 | 2970.5 | 2881 | 4250.9 | 1218.4 | 0.68291 | 6.086
2024-12-10 | 1:13 | Data | 0 | 32.278 | 30.185 | 195.857 | 7.64 | 184.503 | 2222.52 | 25.8 | 42.929 | 6.37 | 1.367 | 4.721 | 8703.03 | 2.086 | 98.1 | 77.6 | 1445 | 21.51 | 5657 | 2956.5 | 2848.2 | 4216.2 | 1218.4 | 0.68529 | 6.088
2024-12-10 | 1:13 | Data | 0 | 32.69 | 30.421 | 196.173 | 7.64 | 184.593 | 2218 | 25.79 | 43.109 | 6.37 | 1.367 | 4.72 | 8689.46 | 2.12 | 98.1 | 77.5 | 1442 | 21.64 | 5648.1 | 2955.3 | 2870.3 | 4237 | 1218.4 | 0.68218 | 6.087
2024-12-10 | 1:13 | Data | 0 | 32.744 | 30.219 | 196.083 | 7.64 | 184.639 | 2224.33 | 25.79 | 43.109 | 6.37 | 1.377 | 4.739 | 8671.37 | 2.302 | 98.1 | 77.5 | 1446 | 21.55 | 5636.4 | 2982.7 | 2858 | 4245.6 | 1218.4 | 0.68784 | 6.116
2024-12-10 | 1:13 | Data | 0 | 32.69 | 30.219 | 196.173 | 7.63 | 184.593 | 2227.04 | 25.8 | 43.2 | 6.37 | 1.37 | 4.736 | 8693.98 | 2.079 | 98.1 | 77.6 | 1448 | 21.6 | 5651.1 | 2956.9 | 2875.1 | 4239.4 | 1218.4 | 0.68048 | 6.105
2024-12-10 | 1:13 | Data | 0 | 32.379 | 30.401 | 196.128 | 7.63 | 184.548 | 2227.95 | 25.79 | 43.2 | 6.37 | 1.369 | 4.707 | 8680.41 | 2.079 | 98.1 | 77.5 | 1448 | 21.6 | 5642.3 | 2978.8 | 2861.3 | 4245.3 | 1218.4 | 0.68234 | 6.076
2024-12-10 | 1:13 | Data | 0 | 32.467 | 30.408 | 196.083 | 7.63 | 184.548 | 2224.33 | 25.8 | 42.929 | 6.37 | 1.375 | 4.714 | 8684.94 | 2.093 | 98.1 | 77.4 | 1446 | 21.51 | 5645.2 | 2958.8 | 2874.5 | 4235.8 | 1218.4 | 0.68301 | 6.09
2024-12-10 | 1:13 | Data | 0 | 32.379 | 30.388 | 196.128 | 7.64 | 184.503 | 2224.33 | 25.79 | 43.2 | 6.37 | 1.373 | 4.732 | 8703.03 | 2.093 | 98.1 | 77.5 | 1446 | 21.6 | 5657 | 2958.9 | 2858.2 | 4229.4 | 1218.4 | 0.68336 | 6.104
2024-12-10 | 1:13 | Data | 0 | 32.271 | 30.273 | 195.992 | 7.64 | 184.639 | 2218.91 | 25.8 | 43.109 | 6.37 | 1.358 | 4.736 | 8703.03 | 1.971 | 98.1 | 77.7 | 1442 | 21.6 | 5657 | 2956.6 | 2854.5 | 4220.9 | 1218.4 | 0.68382 | 6.094
2024-12-10 | 1:13 | Data | 0 | 32.44 | 30.577 | 196.083 | 7.63 | 184.548 | 2230.66 | 25.8 | 43.2 | 6.37 | 1.362 | 4.721 | 8689.46 | 2.127 | 98.1 | 77.6 | 1450 | 21.55 | 5648.1 | 2963.6 | 2868.8 | 4239.4 | 1218.4 | 0.68215 | 6.083
2024-12-10 | 1:13 | Data | 0 | 32.332 | 29.989 | 196.083 | 7.64 | 184.639 | 2229.75 | 25.8 | 43.2 | 6.37 | 1.371 | 4.729 | 8684.94 | 2.133 | 98.1 | 77.5 | 1449 | 21.6 | 5645.2 | 2969.8 | 2852.9 | 4232 | 1218.4 | 0.68423 | 6.099
2024-12-10 | 1:14 | Data | 0 | 32.386 | 30.577 | 196.264 | 7.63 | 184.548 | 2229.75 | 25.79 | 43.2 | 6.37 | 1.373 | 4.722 | 8671.37 | 2.079 | 98.1 | 77.5 | 1449 | 21.6 | 5636.4 | 2952.8 | 2854.1 | 4219.3 | 1218.4 | 0.68367 | 6.095
2024-12-10 | 1:14 | Data | 0 | 32.487 | 30.415 | 196.128 | 7.64 | 184.548 | 2230.66 | 25.8 | 43.2 | 6.37 | 1.373 | 4.711 | 8666.85 | 2.194 | 98.1 | 77.4 | 1450 | 21.6 | 5633.5 | 2961.9 | 2873.1 | 4239.4 | 1218.4 | 0.68255 | 6.084
2024-12-10 | 1:14 | Data | 0 | 32.609 | 30.651 | 196.219 | 7.63 | 184.684 | 2121.29 | 25.78 | 43.2 | 6.37 | 1.377 | 4.726 | 8684.94 | 1.857 | 98 | 77.4 | 1379 | 21.6 | 5645.2 | 2980.6 | 2860.7 | 4240.7 | 1218.4 | 0.68605 | 6.102
2024-12-10 | 1:14 | Data | 0 | 32.372 | 30.361 | 195.992 | 7.64 | 184.503 | 2196.31 | 25.8 | 43.2 | 6.37 | 1.377 | 4.705 | 8662.33 | 2.133 | 98 | 77.4 | 1428 | 21.55 | 5630.5 | 2954.2 | 2884.2 | 4247.4 | 1218.4 | 0.67902 | 6.083
2024-12-10 | 1:14 | Data | 0 | 32.035 | 30.144 | 195.902 | 7.64 | 184.458 | 2203.54 | 25.8 | 43.2 | 6.37 | 1.372 | 4.683 | 8662.33 | 2.052 | 98 | 77.3 | 1432 | 21.6 | 5630.5 | 2964.4 | 2866.8 | 4238 | 1218.4 | 0.68244 | 6.055
2024-12-10 | 1:14 | Data | 0 | 32.831 | 30.219 | 196.219 | 7.64 | 184.729 | 2203.54 | 25.78 | 43.109 | 6.37 | 1.373 | 4.704 | 8662.33 | 2.032 | 98 | 77.4 | 1432 | 21.55 | 5630.5 | 2966.2 | 2890.8 | 4257.3 | 1218.4 | 0.68006 | 6.077
2024-12-10 | 1:14 | Data | 0 | 32.156 | 30.198 | 196.128 | 7.64 | 184.548 | 2205.35 | 25.8 | 43.109 | 6.37 | 1.374 | 4.739 | 8662.33 | 2.025 | 98 | 77.5 | 1433 | 21.6 | 5630.5 | 2963.9 | 2885.4 | 4250.2 | 1218.4 | 0.68085 | 6.112
2024-12-10 | 1:14 | Data | 0 | 32.717 | 30.415 | 196.083 | 7.63 | 184.593 | 2221.62 | 25.78 | 43.2 | 6.37 | 1.372 | 4.717 | 8684.94 | 2.194 | 98.1 | 77.5 | 1444 | 21.6 | 5645.2 | 2965.2 | 2879.2 | 4246.8 | 1218.4 | 0.6805 | 6.09
2024-12-10 | 1:14 | Data | 0 | 32.278 | 30.401 | 196.173 | 7.64 | 184.639 | 2222.52 | 25.8 | 43.2 | 6.37 | 1.375 | 4.685 | 8689.46 | 1.911 | 98.1 | 77.3 | 1444 | 21.6 | 5648.1 | 2964 | 2869.4 | 4242.6 | 1218.5 | 0.68094 | 6.06
2024-12-10 | 1:14 | Data | 0 | 32.379 | 30.408 | 196.219 | 7.63 | 184.593 | 2223.43 | 25.77 | 43.109 | 6.37 | 1.374 | 4.717 | 8693.98 | 2.046 | 98.1 | 77.5 | 1445 | 21.6 | 5651.1 | 2970.9 | 2870.7 | 4245.3 | 1218.5 | 0.68322 | 6.09
2024-12-10 | 1:14 | Data | 0 | 32.723 | 30.671 | 196.173 | 7.64 | 184.684 | 2223.43 | 25.79 | 43.2 | 6.37 | 1.382 | 4.735 | 8680.41 | 2.032 | 98.1 | 77.4 | 1445 | 21.6 | 5642.3 | 2975.9 | 2855.5 | 4237.4 | 1218.5 | 0.68527 | 6.118
2024-12-10 | 1:14 | Data | 0 | 32.494 | 30.442 | 196.128 | 7.64 | 184.684 | 2222.52 | 25.8 | 43.2 | 6.37 | 1.383 | 4.716 | 8689.46 | 2.201 | 98.1 | 77.3 | 1445 | 21.6 | 5648.1 | 2976.2 | 2863.7 | 4242.2 | 1218.5 | 0.68488 | 6.1
2024-12-10 | 1:14 | Data | 0 | 32.717 | 30.529 | 196.128 | 7.64 | 184.639 | 2225.23 | 25.78 | 43.2 | 6.37 | 1.386 | 4.745 | 8698.5 | 2.073 | 98.1 | 77.4 | 1446 | 21.6 | 5654 | 2966.6 | 2855.5 | 4231.6 | 1218.5 | 0.6825 | 6.131
2024-12-10 | 1:14 | Data | 0 | 32.494 | 30.523 | 195.992 | 7.63 | 184.639 | 2225.23 | 25.79 | 43.741 | 6.37 | 1.383 | 4.73 | 8707.55 | 2.059 | 98 | 77.4 | 1446 | 21.87 | 5659.9 | 2954 | 2865.6 | 4231.2 | 1218.5 | 0.68208 | 6.112
2024-12-10 | 1:14 | Data | 0 | 32.102 | 30.3 | 196.128 | 7.64 | 184.593 | 2225.23 | 25.79 | 43.2 | 6.37 | 1.371 | 4.725 | 8698.5 | 2.032 | 98.1 | 77.5 | 1446 | 21.55 | 5654 | 2971.6 | 2855.8 | 4236.3 | 1218.5 | 0.68489 | 6.095
2024-12-10 | 1:14 | Data | 0 | 32.271 | 30.3 | 195.992 | 7.63 | 184.548 | 2224.33 | 25.78 | 42.929 | 6.37 | 1.376 | 4.741 | 8689.46 | 2.079 | 98.1 | 77.5 | 1446 | 21.46 | 5648.1 | 2956.1 | 2890.2 | 4249.7 | 1218.5 | 0.67851 | 6.118
2024-12-10 | 1:14 | Data | 0 | 32.379 | 30.401 | 196.128 | 7.63 | 184.548 | 2225.23 | 25.8 | 43.29 | 6.37 | 1.374 | 4.715 | 8698.5 | 2.079 | 98.1 | 77.4 | 1446 | 21.6 | 5654 | 2977.1 | 2879.8 | 4254.8 | 1218.5 | 0.68382 | 6.089
2024-12-10 | 1:14 | Data | 0 | 32.271 | 30.388 | 196.083 | 7.63 | 184.639 | 2222.52 | 25.8 | 43.2 | 6.37 | 1.373 | 4.699 | 8693.98 | 2.079 | 98.1 | 77.4 | 1444 | 21.6 | 5651.1 | 2959.1 | 2846.4 | 4221.5 | 1218.5 | 0.68374 | 6.072
2024-12-10 | 1:15 | Data | 0 | 32.582 | 30.637 | 195.992 | 7.63 | 184.548 | 2218.91 | 25.8 | 43.2 | 6.37 | 1.377 | 4.699 | 8689.46 | 2.066 | 98.1 | 77.3 | 1442 | 21.55 | 5648.1 | 2949.8 | 2854.3 | 4219.8 | 1218.5 | 0.6821 | 6.076
2024-12-10 | 1:15 | Data | 0 | 32.602 | 30.415 | 196.083 | 7.63 | 184.639 | 2216.2 | 25.79 | 43.2 | 6.37 | 1.375 | 4.707 | 8698.5 | 2.106 | 98.1 | 77.4 | 1441 | 21.6 | 5654 | 2954.4 | 2834.7 | 4210 | 1218.5 | 0.6877 | 6.081
2024-12-10 | 1:15 | Data | 0 | 32.271 | 30.286 | 196.128 | 7.64 | 184.548 | 2216.2 | 25.78 | 43.109 | 6.37 | 1.377 | 4.711 | 8734.68 | 2.093 | 98.1 | 77.4 | 1440 | 21.55 | 5677.5 | 2944 | 2847.3 | 4209.8 | 1218.5 | 0.68699 | 6.088
2024-12-10 | 1:15 | Data | 0 | 32.237 | 30.408 | 196.083 | 7.64 | 184.639 | 2216.2 | 25.79 | 43.2 | 6.38 | 1.369 | 4.699 | 8743.73 | 1.978 | 98.1 | 77.4 | 1441 | 21.55 | 5683.4 | 2964.3 | 2853 | 4229.6 | 1218.5 | 0.68427 | 6.068
2024-12-10 | 1:15 | Data | 0 | 32.474 | 30.529 | 196.083 | 7.63 | 184.729 | 2213.49 | 25.8 | 43.2 | 6.37 | 1.372 | 4.692 | 8730.16 | 2.019 | 98 | 77.4 | 1439 | 21.6 | 5674.6 | 2960.3 | 2863.2 | 4228.2 | 1218.5 | 0.68379 | 6.064
2024-12-10 | 1:15 | Data | 0 | 32.494 | 30.415 | 195.947 | 7.63 | 184.639 | 2214.39 | 25.8 | 43.109 | 6.37 | 1.367 | 4.706 | 8721.11 | 2.079 | 98 | 77.5 | 1439 | 21.55 | 5668.7 | 2976.3 | 2882.1 | 4254 | 1218.5 | 0.68281 | 6.074
2024-12-10 | 1:15 | Data | 0 | 32.494 | 30.327 | 196.219 | 7.64 | 184.684 | 2213.49 | 25.79 | 43.2 | 6.37 | 1.387 | 4.692 | 8707.55 | 2.167 | 98 | 77.2 | 1439 | 21.6 | 5659.9 | 2969.9 | 2880.6 | 4253.4 | 1218.5 | 0.68128 | 6.079
2024-12-10 | 1:15 | Data | 0 | 32.507 | 30.192 | 196.128 | 7.64 | 184.639 | 2214.39 | 25.78 | 43.2 | 6.37 | 1.383 | 4.725 | 8707.55 | 2.167 | 98 | 77.4 | 1439 | 21.6 | 5659.9 | 2980 | 2867.7 | 4246.8 | 1218.5 | 0.68434 | 6.107
2024-12-10 | 1:15 | Data | 0 | 32.264 | 30.361 | 196.083 | 7.63 | 184.593 | 2213.49 | 25.79 | 43.2 | 6.37 | 1.376 | 4.751 | 8730.16 | 2.14 | 98 | 77.6 | 1439 | 21.6 | 5674.6 | 2955.3 | 2859.6 | 4228 | 1218.5 | 0.68176 | 6.126
2024-12-10 | 1:15 | Data | 0 | 32.521 | 30.192 | 195.992 | 7.64 | 184.593 | 2214.39 | 25.78 | 43.2 | 6.37 | 1.371 | 4.701 | 8730.16 | 2.181 | 98 | 77.4 | 1439 | 21.6 | 5674.6 | 2962.6 | 2851.7 | 4228.9 | 1218.5 | 0.68344 | 6.073
2024-12-10 | 1:15 | Data | 0 | 32.366 | 30.09 | 196.083 | 7.64 | 184.548 | 2212.58 | 25.79 | 43.2 | 6.37 | 1.362 | 4.699 | 8716.59 | 2.187 | 98 | 77.5 | 1439 | 21.6 | 5665.8 | 2981.4 | 2856.8 | 4241.4 | 1218.5 | 0.68654 | 6.061
2024-12-10 | 1:15 | Data | 0 | 32.271 | 30.361 | 195.992 | 7.64 | 184.548 | 2213.49 | 25.79 | 43.2 | 6.37 | 1.376 | 4.71 | 8707.55 | 2.194 | 98 | 77.4 | 1439 | 21.6 | 5659.9 | 2981.3 | 2858.7 | 4244.8 | 1218.5 | 0.68536 | 6.086
2024-12-10 | 1:15 | Data | 0 | 32.224 | 30.502 | 196.128 | 7.64 | 184.593 | 2208.97 | 25.78 | 42.929 | 6.36 | 1.363 | 4.699 | 8716.59 | 2.066 | 98.1 | 77.5 | 1436 | 21.46 | 5665.8 | 2958.9 | 2883.4 | 4246.4 | 1218.5 | 0.68081 | 6.062
2024-12-10 | 1:15 | Data | 0 | 32.183 | 30.185 | 196.173 | 7.63 | 184.684 | 2208.97 | 25.79 | 43.109 | 6.37 | 1.369 | 4.685 | 8716.59 | 1.857 | 98 | 77.4 | 1436 | 21.55 | 5665.8 | 2998.4 | 2876.9 | 4265.8 | 1218.5 | 0.68553 | 6.055
2024-12-10 | 1:15 | Data | 0 | 32.548 | 30.361 | 196.219 | 7.64 | 184.639 | 2210.77 | 25.8 | 42.929 | 6.36 | 1.367 | 4.73 | 8693.98 | 2.073 | 98.1 | 77.6 | 1437 | 21.46 | 5651.1 | 2966.7 | 2895.5 | 4258.9 | 1218.5 | 0.68017 | 6.097
2024-12-10 | 1:15 | Data | 0 | 32.278 | 30.644 | 196.173 | 7.64 | 184.684 | 2208.97 | 25.79 | 42.929 | 6.37 | 1.37 | 4.746 | 8671.37 | 1.85 | 98.1 | 77.6 | 1435 | 21.46 | 5636.4 | 2959.8 | 2902.3 | 4261.3 | 1218.5 | 0.67808 | 6.117
2024-12-10 | 1:15 | Data | 0 | 32.494 | 30.523 | 196.083 | 7.63 | 184.593 | 2213.49 | 25.8 | 42.929 | 6.37 | 1.379 | 4.714 | 8680.41 | 1.998 | 98.1 | 77.4 | 1439 | 21.51 | 5642.3 | 2982.6 | 2882 | 4259.5 | 1218.5 | 0.68261 | 6.093
2024-12-10 | 1:15 | Data | 0 | 32.548 | 30.415 | 195.992 | 7.64 | 184.684 | 2199.93 | 25.79 | 42.838 | 6.37 | 1.377 | 4.715 | 8689.46 | 1.971 | 98 | 77.4 | 1430 | 21.46 | 5648.1 | 2979.4 | 2896.5 | 4269.2 | 1218.5 | 0.68193 | 6.091
2024-12-10 | 1:16 | Data | 0 | 32.494 | 30.415 | 196.309 | 7.64 | 184.593 | 2199.93 | 25.78 | 42.838 | 6.37 | 1.369 | 4.726 | 8693.98 | 2.079 | 98 | 77.5 | 1430 | 21.46 | 5651.1 | 2956.6 | 2874.8 | 4236.8 | 1218.5 | 0.68117 | 6.095
2024-12-10 | 1:16 | Data | 0 | 32.494 | 30.59 | 196.219 | 7.63 | 184.593 | 2203.54 | 25.8 | 42.929 | 6.37 | 1.362 | 4.698 | 8693.98 | 2.019 | 98.1 | 77.5 | 1432 | 21.46 | 5651.1 | 2982.2 | 2884.2 | 4262.8 | 1218.5 | 0.68379 | 6.06
2024-12-10 | 1:16 | Data | 0 | 32.48 | 30.09 | 195.992 | 7.63 | 184.503 | 2205.35 | 25.78 | 42.929 | 6.37 | 1.375 | 4.722 | 8707.55 | 2.187 | 98 | 77.4 | 1433 | 21.46 | 5659.9 | 2979 | 2900.3 | 4268.7 | 1218.5 | 0.68088 | 6.098
2024-12-10 | 1:16 | Data | 0 | 32.285 | 30.523 | 196.128 | 7.63 | 184.639 | 2208.06 | 25.78 | 43.2 | 6.37 | 1.379 | 4.739 | 8693.98 | 1.917 | 98 | 77.5 | 1435 | 21.6 | 5651.1 | 2961.4 | 2889.9 | 4251.2 | 1218.5 | 0.67957 | 6.118
2024-12-10 | 1:16 | Data | 0 | 32.332 | 30.536 | 196.128 | 7.64 | 184.548 | 2211.68 | 25.78 | 43.2 | 6.37 | 1.38 | 4.747 | 8689.46 | 2.032 | 98.1 | 77.5 | 1438 | 21.55 | 5648.1 | 2971.3 | 2888.5 | 4253.3 | 1218.5 | 0.68282 | 6.128
2024-12-10 | 1:16 | Data | 0 | 32.386 | 30.212 | 196.128 | 7.64 | 184.639 | 2210.77 | 25.79 | 43.2 | 6.37 | 1.369 | 4.709 | 8671.37 | 2.025 | 98 | 77.5 | 1436 | 21.6 | 5636.4 | 2967.1 | 2887.9 | 4248.6 | 1218.5 | 0.68224 | 6.078
2024-12-10 | 1:16 | Data | 0 | 32.44 | 30.516 | 196.173 | 7.64 | 184.593 | 2213.49 | 25.8 | 43.2 | 6.37 | 1.374 | 4.702 | 8671.37 | 2.14 | 98.1 | 77.4 | 1438 | 21.55 | 5636.4 | 2971.2 | 2891.8 | 4256.2 | 1218.5 | 0.68163 | 6.075
2024-12-10 | 1:16 | Data | 0 | 32.494 | 30.624 | 196.128 | 7.64 | 184.639 | 2213.49 | 25.8 | 42.838 | 6.37 | 1.377 | 4.715 | 8707.55 | 2.187 | 98.1 | 77.4 | 1439 | 21.42 | 5659.9 | 2974.2 | 2878.4 | 4250.7 | 1218.5 | 0.68385 | 6.092
2024-12-10 | 1:16 | Data | 0 | 32.379 | 30.313 | 196.128 | 7.64 | 184.684 | 2209.87 | 25.8 | 43.019 | 6.37 | 1.369 | 4.714 | 8657.8 | 2.181 | 98.1 | 77.5 | 1436 | 21.46 | 5627.6 | 2950.6 | 2876.1 | 4235.3 | 1218.6 | 0.68073 | 6.084
2024-12-10 | 1:16 | Data | 0 | 32.494 | 30.644 | 196.173 | 7.64 | 184.639 | 2214.39 | 25.79 | 43.109 | 6.37 | 1.376 | 4.715 | 8689.46 | 2.019 | 98 | 77.4 | 1439 | 21.6 | 5648.1 | 2969.5 | 2881.4 | 4250.7 | 1218.6 | 0.6813 | 6.091
2024-12-10 | 1:16 | Data | 0 | 32.609 | 30.307 | 196.128 | 7.64 | 184.593 | 2213.49 | 25.78 | 43.2 | 6.37 | 1.37 | 4.728 | 8680.41 | 2.079 | 98 | 77.5 | 1438 | 21.64 | 5642.3 | 2957.7 | 2914.8 | 4264.3 | 1218.6 | 0.67807 | 6.098
2024-12-10 | 1:16 | Data | 0 | 32.285 | 30.415 | 196.083 | 7.64 | 184.593 | 2210.77 | 25.79 | 43.2 | 6.37 | 1.372 | 4.732 | 8707.55 | 2.025 | 98.1 | 77.5 | 1437 | 21.55 | 5659.9 | 2966.9 | 2911.3 | 4264.7 | 1218.6 | 0.67768 | 6.104
2024-12-10 | 1:16 | Data | 0 | 32.501 | 30.252 | 196.173 | 7.63 | 184.684 | 2208.06 | 25.78 | 43.2 | 6.37 | 1.377 | 4.724 | 8707.55 | 2.032 | 98 | 77.4 | 1435 | 21.6 | 5659.9 | 2980.2 | 2906.9 | 4275.4 | 1218.6 | 0.67963 | 6.102
2024-12-10 | 1:16 | Data | 0 | 32.305 | 30.415 | 196.128 | 7.64 | 184.548 | 2208.06 | 25.8 | 43.2 | 6.37 | 1.38 | 4.716 | 8128.7 | 1.857 | 98 | 77.3 | 1435 | 21.55 | 5283.7 | 2966.5 | 2893.4 | 4259.3 | 1218.6 | 0.67928 | 6.096
2024-12-10 | 1:16 | Data | 0 | 32.332 | 30.246 | 196.128 | 7.63 | 184.639 | 2208.06 | 25.8 | 43.109 | 6.37 | 1.385 | 4.71 | 8608.06 | 2.174 | 98 | 77.3 | 1436 | 21.6 | 5595.2 | 2962.5 | 2875.2 | 4247.9 | 1218.6 | 0.67998 | 6.094
2024-12-10 | 1:16 | Data | 0 | 32.467 | 30.408 | 196.128 | 7.64 | 184.639 | 2208.06 | 25.8 | 43.2 | 6.37 | 1.374 | 4.72 | 8951.75 | 2.086 | 98 | 77.5 | 1435 | 21.6 | 5818.6 | 2968.1 | 2897 | 4260.7 | 1218.6 | 0.68013 | 6.093
2024-12-10 | 1:16 | Data | 0 | 32.561 | 30.361 | 196.128 | 7.63 | 184.639 | 2208.06 | 25.8 | 43.109 | 6.37 | 1.37 | 4.707 | 8879.39 | 2.079 | 98 | 77.5 | 1436 | 21.55 | 5771.6 | 2973.4 | 2887.3 | 4256.7 | 1218.6 | 0.68269 | 6.077
2024-12-10 | 1:17 | Data | 0 | 32.494 | 30.192 | 195.992 | 7.63 | 184.593 | 2201.74 | 25.78 | 43.2 | 6.37 | 1.377 | 4.704 | 8662.33 | 2.255 | 98 | 77.4 | 1431 | 21.6 | 5630.5 | 2963 | 2879.1 | 4249.2 | 1218.6 | 0.67978 | 6.08
2024-12-10 | 1:17 | Data | 0 | 32.366 | 30.313 | 196.219 | 7.64 | 184.684 | 2208.06 | 25.8 | 43.2 | 6.37 | 1.378 | 4.677 | 8653.28 | 2.073 | 98 | 77.2 | 1436 | 21.55 | 5624.6 | 2971.2 | 2874.7 | 4250.8 | 1218.6 | 0.68185 | 6.055
2024-12-10 | 1:17 | Data | 0 | 32.285 | 30.401 | 196.128 | 7.63 | 184.729 | 2205.35 | 25.79 | 43.109 | 6.37 | 1.371 | 4.705 | 8653.28 | 2.106 | 98 | 77.4 | 1433 | 21.6 | 5624.6 | 2970.2 | 2898.9 | 4263.6 | 1218.6 | 0.6796 | 6.076
2024-12-10 | 1:17 | Data | 0 | 32.379 | 30.388 | 196.128 | 7.63 | 184.639 | 2206.25 | 25.79 | 43.2 | 6.37 | 1.367 | 4.684 | 8644.24 | 2.012 | 98 | 77.4 | 1434 | 21.6 | 5618.8 | 2959.9 | 2897.2 | 4253.5 | 1218.6 | 0.67915 | 6.051
2024-12-10 | 1:17 | Data | 0 | 32.811 | 30.529 | 196.083 | 7.63 | 184.684 | 2208.06 | 25.8 | 43.109 | 6.37 | 1.371 | 4.711 | 8662.33 | 2.1 | 98 | 77.5 | 1435 | 21.55 | 5630.5 | 2961.2 | 2903.5 | 4258.4 | 1218.6 | 0.67856 | 6.082
2024-12-10 | 1:17 | Data | 0 | 32.71 | 30.415 | 196.309 | 7.63 | 184.729 | 2208.97 | 25.79 | 43.109 | 6.37 | 1.374 | 4.721 | 8680.41 | 2.174 | 98 | 77.5 | 1436 | 21.6 | 5642.3 | 2969.4 | 2890.2 | 4257.7 | 1218.6 | 0.68091 | 6.093
2024-12-10 | 1:17 | Data | 0 | 32.879 | 30.698 | 196.219 | 7.64 | 184.684 | 2208.97 | 25.78 | 43.2 | 6.37 | 1.381 | 4.708 | 8648.76 | 2.133 | 98 | 77.3 | 1436 | 21.6 | 5621.7 | 2961 | 2893.8 | 4254.6 | 1218.6 | 0.67679 | 6.089
2024-12-10 | 1:17 | Data | 0 | 32.494 | 30.415 | 196.128 | 7.64 | 184.639 | 2208.06 | 25.79 | 43.29 | 6.37 | 1.384 | 4.718 | 8648.76 | 2.079 | 98 | 77.3 | 1436 | 21.6 | 5621.7 | 2972.2 | 2903.8 | 4268.9 | 1218.6 | 0.67895 | 6.102
2024-12-10 | 1:17 | Data | 0 | 32.69 | 30.651 | 196.173 | 7.63 | 184.639 | 2207.16 | 25.79 | 43.2 | 6.37 | 1.381 | 4.725 | 8630.67 | 2.073 | 98 | 77.4 | 1435 | 21.55 | 5609.9 | 2966.6 | 2880.5 | 4249 | 1218.6 | 0.68078 | 6.107
2024-12-10 | 1:17 | Data | 0 | 32.73 | 30.259 | 196.173 | 7.63 | 184.729 | 2208.06 | 25.79 | 43.109 | 6.37 | 1.379 | 4.74 | 8635.19 | 2.147 | 98 | 77.5 | 1435 | 21.55 | 5612.9 | 2974.8 | 2888.1 | 4259.2 | 1218.6 | 0.68058 | 6.119
2024-12-10 | 1:17 | Data | 0 | 32.264 | 30.401 | 196.083 | 7.64 | 184.548 | 2208.97 | 25.79 | 43.2 | 6.37 | 1.371 | 4.718 | 8639.71 | 2.079 | 98 | 77.5 | 1436 | 21.6 | 5615.8 | 2972.6 | 2882.1 | 4263.1 | 1218.6 | 0.67872 | 6.091
2024-12-10 | 1:17 | Data | 0 | 32.501 | 30.469 | 196.264 | 7.63 | 184.774 | 2208.06 | 25.8 | 43.2 | 6.37 | 1.377 | 4.699 | 8626.15 | 2.187 | 98 | 77.3 | 1435 | 21.55 | 5607 | 2979.8 | 2900.9 | 4271.9 | 1218.6 | 0.68111 | 6.074
2024-12-10 | 1:17 | Data | 0 | 32.271 | 30.3 | 196.219 | 7.64 | 184.593 | 2207.16 | 25.78 | 43.2 | 6.37 | 1.366 | 4.711 | 8644.24 | 2.079 | 98 | 77.5 | 1435 | 21.6 | 5618.8 | 2957.4 | 2902.7 | 4261.2 | 1218.6 | 0.67738 | 6.075
2024-12-10 | 1:17 | Data | 0 | 32.278 | 30.293 | 196.219 | 7.63 | 184.684 | 2208.97 | 25.78 | 43.109 | 6.37 | 1.366 | 4.702 | 8639.71 | 2.086 | 98 | 77.5 | 1436 | 21.6 | 5615.8 | 2962.6 | 2894.9 | 4254.7 | 1218.6 | 0.67817 | 6.07
2024-12-10 | 1:17 | Data | 0 | 32.514 | 30.59 | 196.219 | 7.64 | 184.593 | 2211.68 | 25.8 | 43.2 | 6.37 | 1.371 | 4.727 | 8644.24 | 2.079 | 98 | 77.5 | 1438 | 21.6 | 5618.8 | 2968 | 2887.8 | 4254 | 1218.6 | 0.68069 | 6.098
2024-12-10 | 1:17 | Data | 0 | 32.271 | 30.394 | 196.219 | 7.64 | 184.593 | 2210.77 | 25.79 | 43.2 | 6.37 | 1.371 | 4.742 | 8653.28 | 2.093 | 98 | 77.6 | 1437 | 21.6 | 5624.6 | 2951.4 | 2880.8 | 4244.2 | 1218.6 | 0.67784 | 6.112
2024-12-10 | 1:17 | Data | 0 | 32.48 | 30.59 | 196.173 | 7.63 | 184.684 | 2210.77 | 25.78 | 43.2 | 6.37 | 1.367 | 4.693 | 8666.85 | 2.16 | 98.1 | 77.5 | 1438 | 21.55 | 5633.5 | 2970.2 | 2889 | 4258.6 | 1218.6 | 0.68082 | 6.061
2024-12-10 | 1:17 | Data | 0 | 32.919 | 30.34 | 196.219 | 7.64 | 184.729 | 2209.87 | 25.78 | 43.2 | 6.37 | 1.378 | 4.716 | 8648.76 | 2.241 | 98.1 | 77.4 | 1437 | 21.55 | 5621.7 | 2968.4 | 2890.5 | 4257.9 | 1218.6 | 0.68111 | 6.093
2024-12-10 | 1:18 | Data | 0 | 32.602 | 30.415 | 196.309 | 7.63 | 184.684 | 2211.68 | 25.78 | 43.109 | 6.36 | 1.376 | 4.723 | 8653.28 | 1.917 | 98 | 77.4 | 1438 | 21.55 | 5624.6 | 2947.1 | 2896.8 | 4252.2 | 1218.6 | 0.6787 | 6.1
2024-12-10 | 1:18 | Data | 0 | 32.696 | 30.421 | 196.219 | 7.63 | 184.684 | 2213.49 | 25.78 | 43.2 | 6.37 | 1.367 | 4.717 | 8657.8 | 2.16 | 98 | 77.5 | 1439 | 21.6 | 5627.6 | 2959.3 | 2907.6 | 4261.8 | 1218.6 | 0.67755 | 6.083
2024-12-10 | 1:18 | Data | 0 | 32.271 | 30.502 | 196.128 | 7.64 | 184.639 | 2218.91 | 25.79 | 43.2 | 6.37 | 1.367 | 4.714 | 8635.19 | 2.079 | 98.1 | 77.5 | 1442 | 21.6 | 5612.9 | 2958.9 | 2892.6 | 4253.9 | 1218.6 | 0.67728 | 6.081
2024-12-10 | 1:18 | Data | 0 | 32.44 | 30.415 | 196.219 | 7.64 | 184.729 | 2218.91 | 25.8 | 43.2 | 6.37 | 1.377 | 4.73 | 8662.33 | 2.073 | 98.1 | 77.4 | 1442 | 21.6 | 5630.5 | 2945.6 | 2880.8 | 4236.9 | 1218.6 | 0.67795 | 6.107
2024-12-10 | 1:18 | Data | 0 | 32.521 | 30.529 | 196.173 | 7.64 | 184.729 | 2218 | 25.78 | 42.929 | 6.37 | 1.384 | 4.72 | 8662.33 | 1.877 | 98.1 | 77.3 | 1442 | 21.51 | 5630.5 | 2962.3 | 2910.3 | 4265.5 | 1218.6 | 0.67686 | 6.104
2024-12-10 | 1:18 | Data | 0 | 32.933 | 30.334 | 196.219 | 7.64 | 184.729 | 2218.91 | 25.78 | 42.838 | 6.36 | 1.385 | 4.709 | 8666.85 | 2.127 | 98.1 | 77.3 | 1442 | 21.46 | 5633.5 | 2962.5 | 2902.1 | 4257.1 | 1218.6 | 0.6801 | 6.093
2024-12-10 | 1:18 | Data | 0 | 32.71 | 30.651 | 196.264 | 7.63 | 184.729 | 2226.14 | 25.78 | 43.109 | 6.36 | 1.379 | 4.71 | 8662.33 | 2.073 | 98.1 | 77.4 | 1448 | 21.6 | 5630.5 | 2970 | 2912.2 | 4272.3 | 1218.6 | 0.67859 | 6.09
2024-12-10 | 1:18 | Data | 0 | 32.271 | 30.415 | 196.083 | 7.64 | 184.593 | 2224.33 | 25.78 | 43.2 | 6.37 | 1.376 | 4.723 | 8680.41 | 1.965 | 98.1 | 77.4 | 1446 | 21.6 | 5642.3 | 2957.6 | 2891.7 | 4252.9 | 1218.6 | 0.67729 | 6.098
2024-12-10 | 1:18 | Data | 0 | 32.609 | 30.448 | 196.219 | 7.63 | 184.729 | 2228.85 | 25.78 | 43.019 | 6.37 | 1.376 | 4.701 | 8680.41 | 2.012 | 98.1 | 77.4 | 1449 | 21.55 | 5642.3 | 2951.5 | 2891.3 | 4249.4 | 1218.6 | 0.67713 | 6.077
2024-12-10 | 1:18 | Data | 0 | 32.379 | 30.415 | 196.128 | 7.63 | 184.684 | 2227.95 | 25.78 | 43.109 | 6.37 | 1.369 | 4.662 | 8657.8 | 1.924 | 98.1 | 77.3 | 1448 | 21.51 | 5627.6 | 2955.6 | 2886.1 | 4246.3 | 1218.7 | 0.67825 | 6.031
2024-12-10 | 1:18 | Data | 0 | 32.636 | 30.415 | 196.309 | 7.64 | 184.819 | 2229.75 | 25.78 | 43.109 | 6.37 | 1.376 | 4.693 | 8653.28 | 1.924 | 98.1 | 77.3 | 1449 | 21.55 | 5624.6 | 2969.6 | 2887.1 | 4258.1 | 1218.7 | 0.68167 | 6.07
2024-12-10 | 1:18 | Data | 0 | 32.494 | 30.752 | 196.219 | 7.63 | 184.593 | 2229.75 | 25.79 | 43.019 | 6.37 | 1.384 | 4.736 | 8662.33 | 2.025 | 98.1 | 77.4 | 1449 | 21.46 | 5630.5 | 2960.3 | 2889.2 | 4255.7 | 1218.7 | 0.68002 | 6.119
2024-12-10 | 1:18 | Data | 0 | 32.494 | 30.415 | 195.992 | 7.63 | 184.684 | 2230.66 | 25.78 | 42.838 | 6.37 | 1.374 | 4.74 | 8653.28 | 2.079 | 98.1 | 77.5 | 1450 | 21.46 | 5624.6 | 2960.3 | 2852.5 | 4243.9 | 1218.7 | 0.68223 | 6.115
2024-12-10 | 1:18 | Data | 0 | 32.872 | 30.806 | 196.083 | 7.64 | 184.684 | 2229.75 | 25.77 | 42.929 | 6.37 | 1.366 | 4.694 | 8666.85 | 1.897 | 98.1 | 77.5 | 1449 | 21.46 | 5633.5 | 2947.9 | 2880.6 | 4238.2 | 1218.7 | 0.67813 | 6.059
2024-12-10 | 1:18 | Data | 0 | 32.494 | 30.415 | 196.083 | 7.63 | 184.593 | 2227.04 | 25.78 | 42.929 | 6.37 | 1.366 | 4.726 | 8680.41 | 2.079 | 98.1 | 77.6 | 1448 | 21.46 | 5642.3 | 2953.6 | 2866.7 | 4228.6 | 1218.7 | 0.68101 | 6.092
2024-12-10 | 1:18 | Data | 0 | 32.447 | 30.86 | 196.309 | 7.64 | 184.729 | 2225.23 | 25.78 | 42.929 | 6.36 | 1.385 | 4.731 | 8693.98 | 1.958 | 98.1 | 77.3 | 1446 | 21.46 | 5651.1 | 2960.3 | 2870.5 | 4241 | 1218.7 | 0.67929 | 6.118
2024-12-10 | 1:18 | Data | 0 | 32.271 | 30.367 | 196.128 | 7.64 | 184.639 | 2221.62 | 25.78 | 42.116 | 6.37 | 1.38 | 4.711 | 8693.98 | 1.992 | 98.1 | 77.3 | 1444 | 21.1 | 5651.1 | 2961.4 | 2892.9 | 4251.9 | 1218.7 | 0.6797 | 6.091
2024-12-10 | 1:18 | Data | 0 | 32.831 | 30.489 | 196.354 | 7.63 | 184.729 | 2222.52 | 25.78 | 42.838 | 6.36 | 1.38 | 4.707 | 8693.98 | 2.052 | 98.1 | 77.3 | 1445 | 21.46 | 5651.1 | 2965.7 | 2920.1 | 4271.5 | 1218.7 | 0.67916 | 6.086
2024-12-10 | 1:19 | Data | 0 | 32.399 | 30.374 | 196.219 | 7.64 | 184.774 | 2227.04 | 25.79 | 42.838 | 6.37 | 1.373 | 4.712 | 8707.55 | 1.911 | 98.1 | 77.4 | 1448 | 21.46 | 5659.9 | 2975 | 2917.6 | 4280.2 | 1218.7 | 0.67672 | 6.085
2024-12-10 | 1:19 | Data | 0 | 32.494 | 30.624 | 196.264 | 7.64 | 184.639 | 2227.04 | 25.79 | 42.838 | 6.37 | 1.37 | 4.699 | 8666.85 | 1.904 | 98.1 | 77.4 | 1448 | 21.46 | 5633.5 | 2959.9 | 2904.4 | 4267.4 | 1218.7 | 0.67725 | 6.069
2024-12-10 | 1:19 | Data | 0 | 32.494 | 30.415 | 196.173 | 7.64 | 184.639 | 2230.66 | 25.78 | 43.019 | 6.37 | 1.371 | 4.706 | 8693.98 | 2.079 | 98.1 | 77.4 | 1449 | 21.46 | 5651.1 | 2970.1 | 2904.2 | 4267.4 | 1218.7 | 0.67802 | 6.077
2024-12-10 | 1:19 | Data | 0 | 32.264 | 30.3 | 195.992 | 7.63 | 184.548 | 2230.66 | 25.78 | 42.929 | 6.37 | 1.372 | 4.709 | 8689.46 | 2.079 | 98.1 | 77.4 | 1449 | 21.42 | 5648.1 | 2950.8 | 2911.6 | 4259.5 | 1218.7 | 0.67693 | 6.082
2024-12-10 | 1:19 | Data | 0 | 32.636 | 30.415 | 196.354 | 7.64 | 184.774 | 2230.66 | 25.77 | 42.838 | 6.37 | 1.366 | 4.701 | 8689.46 | 2.093 | 98.1 | 77.5 | 1451 | 21.42 | 5648.1 | 2988.7 | 2898.7 | 4276.6 | 1218.7 | 0.6811 | 6.067
2024-12-10 | 1:19 | Data | 0 | 32.494 | 30.246 | 196.173 | 7.64 | 184.593 | 2225.23 | 25.78 | 42.929 | 6.37 | 1.377 | 4.699 | 8703.03 | 2.066 | 98.1 | 77.3 | 1446 | 21.42 | 5657 | 2968.5 | 2894.4 | 4259.1 | 1218.7 | 0.68044 | 6.076
2024-12-10 | 1:19 | Data | 0 | 32.264 | 30.502 | 196.309 | 7.64 | 184.639 | 2227.95 | 25.78 | 42.929 | 6.37 | 1.378 | 4.738 | 8693.98 | 2.106 | 98.1 | 77.5 | 1448 | 21.46 | 5651.1 | 2945.7 | 2902.2 | 4252.2 | 1218.7 | 0.67427 | 6.116
2024-12-10 | 1:19 | Data | 0 | 32.494 | 30.415 | 196.219 | 7.64 | 184.639 | 2227.95 | 25.77 | 42.929 | 6.37 | 1.377 | 4.736 | 8693.98 | 1.863 | 98.1 | 77.5 | 1448 | 21.46 | 5651.1 | 2954.3 | 2904.9 | 4256.9 | 1218.7 | 0.67719 | 6.113
2024-12-10 | 1:19 | Data | 0 | 32.723 | 30.428 | 196.354 | 7.64 | 184.684 | 2227.95 | 25.78 | 42.748 | 6.37 | 1.379 | 4.726 | 8716.59 | 2.073 | 98.1 | 77.4 | 1448 | 21.37 | 5665.8 | 2955.2 | 2891.7 | 4253.4 | 1218.7 | 0.676 | 6.104
2024-12-10 | 1:19 | Data | 0 | 32.393 | 30.3 | 196.128 | 7.64 | 184.684 | 2222.52 | 25.78 | 42.929 | 6.37 | 1.369 | 4.717 | 8734.68 | 1.911 | 98.1 | 77.5 | 1445 | 21.51 | 5677.5 | 2959.1 | 2886.2 | 4249.9 | 1218.7 | 0.67896 | 6.086
2024-12-10 | 1:19 | Data | 0 | 32.609 | 30.847 | 196.354 | 7.64 | 184.729 | 2216.2 | 25.78 | 43.29 | 6.37 | 1.364 | 4.72 | 8716.59 | 2.073 | 98.1 | 77.6 | 1441 | 21.64 | 5665.8 | 2950.6 | 2887.9 | 4247.4 | 1218.7 | 0.67616 | 6.083
2024-12-10 | 1:19 | Data | 0 | 32.521 | 30.421 | 196.128 | 7.64 | 184.639 | 2218 | 25.78 | 42.929 | 6.37 | 1.37 | 4.72 | 8730.16 | 2.059 | 98.1 | 77.5 | 1441 | 21.46 | 5674.6 | 2963.4 | 2863.2 | 4236.1 | 1218.7 | 0.68182 | 6.09
2024-12-10 | 1:19 | Data | 0 | 32.44 | 30.442 | 196.083 | 7.64 | 184.548 | 2218 | 25.78 | 43.019 | 6.37 | 1.375 | 4.726 | 8730.16 | 2.025 | 98.1 | 77.5 | 1442 | 21.46 | 5674.6 | 2966.9 | 2866.2 | 4234.7 | 1218.7 | 0.68402 | 6.1
2024-12-10 | 1:19 | Data | 0 | 32.663 | 30.421 | 196.128 | 7.64 | 184.593 | 2216.2 | 25.79 | 42.838 | 6.37 | 1.383 | 4.707 | 8730.16 | 2.268 | 98.1 | 77.3 | 1441 | 21.46 | 5674.6 | 2962.4 | 2882.2 | 4248 | 1218.7 | 0.68067 | 6.089
2024-12-10 | 1:19 | Data | 0 | 32.69 | 30.307 | 196.219 | 7.64 | 184.684 | 2216.2 | 25.78 | 43.2 | 6.36 | 1.373 | 4.694 | 8743.73 | 2.329 | 98.1 | 77.4 | 1441 | 21.55 | 5683.4 | 2952.9 | 2910.3 | 4260.2 | 1218.7 | 0.675 | 6.067
2024-12-10 | 1:19 | Data | 0 | 32.487 | 30.583 | 196.219 | 7.63 | 184.639 | 2216.2 | 25.78 | 43.2 | 6.37 | 1.37 | 4.733 | 8743.73 | 2.154 | 98.1 | 77.6 | 1440 | 21.6 | 5683.4 | 2963.3 | 2902.2 | 4259.1 | 1218.7 | 0.68148 | 6.103
2024-12-10 | 1:19 | Data | 0 | 32.69 | 30.421 | 196.264 | 7.63 | 184.729 | 2216.2 | 25.78 | 43.2 | 6.37 | 1.38 | 4.749 | 8743.73 | 2.181 | 98.1 | 77.5 | 1441 | 21.6 | 5683.4 | 2964.7 | 2891 | 4252.6 | 1218.7 | 0.67914 | 6.13
2024-12-10 | 1:20 | Data | 0 | 32.494 | 30.367 | 196.219 | 7.64 | 184.729 | 2220.72 | 25.78 | 43.2 | 6.36 | 1.378 | 4.734 | 8730.16 | 2.181 | 98.1 | 77.5 | 1442 | 21.6 | 5674.6 | 2957.5 | 2860.9 | 4226.5 | 1218.7 | 0.68265 | 6.112
2024-12-10 | 1:20 | Data | 0 | 32.777 | 30.475 | 196.264 | 7.63 | 184.774 | 2216.2 | 25.78 | 43.2 | 6.37 | 1.367 | 4.725 | 8721.11 | 2.093 | 98.1 | 77.6 | 1441 | 21.55 | 5668.7 | 2962.1 | 2868.7 | 4238.9 | 1218.7 | 0.68309 | 6.092
2024-12-10 | 1:20 | Data | 0 | 32.811 | 30.442 | 196.309 | 7.63 | 184.729 | 2214.39 | 25.78 | 43.2 | 6.37 | 1.359 | 4.739 | 8721.11 | 2.336 | 98.1 | 77.7 | 1439 | 21.55 | 5668.7 | 2949 | 2883 | 4242.1 | 1218.7 | 0.67721 | 6.098
2024-12-10 | 1:20 | Data | 0 | 32.399 | 30.198 | 196.264 | 7.63 | 184.684 | 2213.49 | 25.78 | 43.109 | 6.37 | 1.37 | 4.722 | 8716.59 | 2.073 | 98 | 77.5 | 1439 | 21.6 | 5665.8 | 2961.7 | 2893.5 | 4255.3 | 1218.7 | 0.67917 | 6.092
2024-12-10 | 1:20 | Data | 0 | 32.825 | 30.651 | 196.173 | 7.63 | 184.639 | 2211.68 | 25.78 | 43.2 | 6.37 | 1.369 | 4.729 | 8703.03 | 2.12 | 98.1 | 77.5 | 1438 | 21.55 | 5657 | 2959.4 | 2881.3 | 4244.7 | 1218.7 | 0.68016 | 6.099
2024-12-10 | 1:20 | Data | 0 | 32.548 | 30.381 | 196.354 | 7.64 | 184.729 | 2210.77 | 25.78 | 43.109 | 6.37 | 1.376 | 4.723 | 8703.03 | 2.248 | 98.1 | 77.4 | 1437 | 21.6 | 5657 | 2963.8 | 2894.9 | 4252.4 | 1218.7 | 0.68103 | 6.1
2024-12-10 | 1:20 | Data | 0 | 32.609 | 30.624 | 196.173 | 7.63 | 184.593 | 2208.97 | 25.78 | 43.2 | 6.36 | 1.376 | 4.715 | 8707.55 | 2.079 | 98 | 77.4 | 1436 | 21.64 | 5659.9 | 2965.2 | 2898 | 4263.8 | 1218.7 | 0.67876 | 6.091
2024-12-10 | 1:20 | Data | 0 | 32.69 | 30.428 | 196.173 | 7.64 | 184.729 | 2212.58 | 25.77 | 43.2 | 6.37 | 1.376 | 4.735 | 8716.59 | 2.093 | 98 | 77.5 | 1439 | 21.6 | 5665.8 | 2964.6 | 2914.6 | 4270.1 | 1218.7 | 0.67728 | 6.111
2024-12-10 | 1:20 | Data | 0 | 32.663 | 30.644 | 196.219 | 7.64 | 184.729 | 2216.2 | 25.78 | 43.2 | 6.37 | 1.371 | 4.726 | 8671.37 | 2.073 | 98.1 | 77.5 | 1440 | 21.6 | 5636.4 | 2975.1 | 2915.1 | 4281.7 | 1218.7 | 0.67787 | 6.097
2024-12-10 | 1:20 | Data | 0 | 32.501 | 30.59 | 196.128 | 7.63 | 184.729 | 2212.58 | 25.78 | 43.109 | 6.37 | 1.365 | 4.714 | 8671.37 | 2.073 | 98 | 77.6 | 1439 | 21.6 | 5636.4 | 2950.3 | 2860.5 | 4225 | 1218.8 | 0.68199 | 6.08
2024-12-10 | 1:20 | Data | 0 | 32.399 | 30.415 | 196.173 | 7.64 | 184.729 | 2213.49 | 25.78 | 43.109 | 6.38 | 1.377 | 4.715 | 8680.41 | 1.911 | 98.1 | 77.4 | 1438 | 21.55 | 5642.3 | 2978.6 | 2881.7 | 4257.9 | 1218.8 | 0.68299 | 6.092
2024-12-10 | 1:20 | Data | 0 | 32.663 | 30.421 | 196.083 | 7.63 | 184.729 | 2213.49 | 25.78 | 43.2 | 6.37 | 1.377 | 4.728 | 8648.76 | 2.106 | 98 | 77.4 | 1438 | 21.6 | 5621.7 | 2957.7 | 2875.4 | 4239 | 1218.8 | 0.6816 | 6.104
2024-12-10 | 1:20 | Data | 0 | 32.494 | 30.462 | 196.309 | 7.64 | 184.639 | 2213.49 | 25.78 | 43.2 | 6.37 | 1.37 | 4.735 | 8684.94 | 1.958 | 98 | 77.6 | 1439 | 21.6 | 5645.2 | 2950.5 | 2878.1 | 4237.5 | 1218.8 | 0.68105 | 6.105
2024-12-10 | 1:20 | Data | 0 | 32.467 | 30.583 | 196.219 | 7.64 | 184.684 | 2214.39 | 25.77 | 42.929 | 6.37 | 1.365 | 4.726 | 8671.37 | 2.079 | 98.1 | 77.6 | 1440 | 21.46 | 5636.4 | 2967.7 | 2874.9 | 4247.6 | 1218.8 | 0.68154 | 6.09
2024-12-10 | 1:20 | Data | 0 | 32.764 | 30.475 | 196.309 | 7.63 | 184.774 | 2211.68 | 25.78 | 42.929 | 6.37 | 1.364 | 4.702 | 8707.55 | 2.255 | 98.1 | 77.5 | 1438 | 21.42 | 5659.9 | 2956.8 | 2859.9 | 4234.3 | 1218.8 | 0.68187 | 6.065
2024-12-10 | 1:20 | Data | 0 | 32.94 | 30.475 | 196.219 | 7.63 | 184.729 | 2215.29 | 25.78 | 42.929 | 6.37 | 1.37 | 4.721 | 8721.11 | 2.1 | 98.1 | 77.5 | 1440 | 21.46 | 5668.7 | 2965.7 | 2876.5 | 4246.4 | 1218.8 | 0.68127 | 6.092
2024-12-10 | 1:20 | Data | 0 | 32.467 | 30.86 | 196.219 | 7.63 | 184.774 | 2216.2 | 25.78 | 43.2 | 6.37 | 1.37 | 4.721 | 8707.55 | 1.998 | 98.1 | 77.5 | 1441 | 21.6 | 5659.9 | 2966.3 | 2876.7 | 4248 | 1218.8 | 0.68068 | 6.092
2024-12-10 | 1:20 | Data | 0 | 32.494 | 30.59 | 196.354 | 7.64 | 184.774 | 2217.1 | 25.78 | 42.929 | 6.37 | 1.376 | 4.7 | 8707.55 | 2.079 | 98.1 | 77.4 | 1441 | 21.46 | 5659.9 | 2972 | 2865.7 | 4243.9 | 1218.8 | 0.68267 | 6.074
2024-12-10 | 1:21 | Data | 0 | 33.021 | 30.347 | 196.128 | 7.63 | 184.729 | 2213.49 | 25.78 | 42.838 | 6.37 | 1.378 | 4.728 | 8707.55 | 2.268 | 98.1 | 77.4 | 1439 | 21.46 | 5659.9 | 2968.6 | 2868.3 | 4242.5 | 1218.8 | 0.68264 | 6.106
2024-12-10 | 1:21 | Data | 0 | 32.845 | 30.259 | 196.264 | 7.64 | 184.774 | 2214.39 | 25.78 | 43.019 | 6.36 | 1.37 | 4.682 | 8698.5 | 2.086 | 98.1 | 77.4 | 1439 | 21.46 | 5654 | 2963 | 2862.9 | 4234.6 | 1218.8 | 0.68206 | 6.052
2024-12-10 | 1:21 | Data | 0 | 32.386 | 30.415 | 196.264 | 7.64 | 184.684 | 2213.49 | 25.78 | 42.929 | 6.37 | 1.371 | 4.69 | 8698.5 | 1.877 | 98.1 | 77.4 | 1439 | 21.46 | 5654 | 2989.7 | 2890.9 | 4268 | 1218.8 | 0.68419 | 6.062
2024-12-10 | 1:21 | Data | 0 | 32.514 | 30.415 | 196.264 | 7.63 | 184.684 | 2213.49 | 25.78 | 42.838 | 6.37 | 1.377 | 4.676 | 8707.55 | 2.079 | 98.1 | 77.2 | 1439 | 21.42 | 5659.9 | 2965.6 | 2897.2 | 4258.8 | 1218.8 | 0.67943 | 6.054
2024-12-10 | 1:21 | Data | 0 | 32.669 | 30.475 | 196.219 | 7.64 | 184.774 | 2216.2 | 25.78 | 42.929 | 6.37 | 1.381 | 4.717 | 8707.55 | 1.998 | 98.1 | 77.4 | 1441 | 21.46 | 5659.9 | 2953.5 | 2886.6 | 4244.7 | 1218.8 | 0.6782 | 6.098
2024-12-10 | 1:21 | Data | 0 | 32.298 | 30.415 | 196.264 | 7.64 | 184.729 | 2215.29 | 25.79 | 42.929 | 6.37 | 1.369 | 4.697 | 8707.55 | 1.863 | 98.1 | 77.4 | 1441 | 21.46 | 5659.9 | 2952.8 | 2873.7 | 4236.6 | 1218.8 | 0.68012 | 6.066
2024-12-10 | 1:21 | Data | 0 | 32.399 | 30.577 | 196.399 | 7.63 | 184.865 | 2218.91 | 25.77 | 42.929 | 6.37 | 1.37 | 4.698 | 8707.55 | 1.965 | 98.1 | 77.4 | 1442 | 21.46 | 5659.9 | 2969.9 | 2854 | 4229.1 | 1218.8 | 0.68601 | 6.067
2024-12-10 | 1:21 | Data | 0 | 32.507 | 30.415 | 196.219 | 7.64 | 184.684 | 2216.2 | 25.78 | 42.748 | 6.37 | 1.376 | 4.719 | 8716.59 | 2.086 | 98.1 | 77.4 | 1441 | 21.37 | 5665.8 | 2965.6 | 2878.6 | 4246.7 | 1218.8 | 0.68173 | 6.095
2024-12-10 | 1:21 | Data | 0 | 32.548 | 30.442 | 196.173 | 7.63 | 184.684 | 2213.49 | 25.79 | 43.109 | 6.36 | 1.37 | 4.711 | 8703.03 | 2.005 | 98.1 | 77.5 | 1439 | 21.55 | 5657 | 2963.1 | 2883.2 | 4250.6 | 1218.8 | 0.67979 | 6.083
2024-12-10 | 1:21 | Data | 0 | 32.71 | 30.644 | 196.264 | 7.64 | 184.729 | 2216.2 | 25.78 | 42.929 | 6.37 | 1.38 | 4.7 | 8734.68 | 2.079 | 98.1 | 77.3 | 1441 | 21.42 | 5677.5 | 2954.5 | 2874.7 | 4235 | 1218.8 | 0.68115 | 6.08
2024-12-10 | 1:21 | Data | 0 | 32.494 | 30.631 | 196.128 | 7.63 | 184.684 | 2215.29 | 25.78 | 42.929 | 6.37 | 1.371 | 4.701 | 8716.59 | 1.917 | 98.1 | 77.4 | 1441 | 21.46 | 5665.8 | 2965.4 | 2867.5 | 4242.8 | 1218.8 | 0.68246 | 6.071
2024-12-10 | 1:21 | Data | 0 | 32.44 | 30.523 | 196.128 | 7.63 | 184.684 | 2220.72 | 25.78 | 42.838 | 6.37 | 1.378 | 4.687 | 8721.11 | 2.1 | 98.1 | 77.3 | 1442 | 21.42 | 5668.7 | 2964.9 | 2875.5 | 4244.2 | 1218.8 | 0.6821 | 6.065
2024-12-10 | 1:21 | Data | 0 | 32.852 | 30.705 | 196.309 | 7.64 | 184.729 | 2218.91 | 25.78 | 42.929 | 6.37 | 1.38 | 4.708 | 8716.59 | 2.268 | 98.1 | 77.3 | 1442 | 21.42 | 5665.8 | 2968.7 | 2855.7 | 4234.7 | 1218.8 | 0.68506 | 6.088
2024-12-10 | 1:21 | Data | 0 | 32.514 | 30.644 | 196.49 | 7.64 | 184.819 | 2218.91 | 25.78 | 42.929 | 6.37 | 1.373 | 4.735 | 8703.03 | 2.059 | 98.1 | 77.5 | 1442 | 21.46 | 5657 | 2960.3 | 2857.6 | 4227.6 | 1218.8 | 0.6838 | 6.108
2024-12-10 | 1:21 | Data | 0 | 32.548 | 30.219 | 196.173 | 7.64 | 184.729 | 2218 | 25.78 | 42.748 | 6.37 | 1.375 | 4.709 | 8730.16 | 2.093 | 98.1 | 77.4 | 1442 | 21.33 | 5674.6 | 2936.5 | 2869.1 | 4224.3 | 1218.8 | 0.67705 | 6.085
2024-12-10 | 1:21 | Data | 0 | 32.386 | 30.698 | 196.309 | 7.64 | 184.639 | 2218.91 | 25.78 | 42.929 | 6.37 | 1.378 | 4.718 | 8689.46 | 2.073 | 98.1 | 77.4 | 1442 | 21.46 | 5648.1 | 2961.4 | 2880.4 | 4245.6 | 1218.8 | 0.68161 | 6.096
2024-12-10 | 1:21 | Data | 0 | 32.636 | 30.421 | 196.219 | 7.64 | 184.729 | 2216.2 | 25.77 | 42.929 | 6.37 | 1.365 | 4.721 | 8680.41 | 2.127 | 98.1 | 77.6 | 1441 | 21.46 | 5642.3 | 2984 | 2874.1 | 4255.7 | 1218.8 | 0.68461 | 6.086
2024-12-10 | 1:21 | Data | 0 | 32.696 | 30.442 | 196.173 | 7.64 | 184.729 | 2216.2 | 25.78 | 42.929 | 6.37 | 1.376 | 4.719 | 8671.37 | 2.248 | 98.1 | 77.4 | 1441 | 21.46 | 5636.4 | 2952.3 | 2868 | 4231.1 | 1218.8 | 0.67991 | 6.094
2024-12-10 | 1:22 | Data | 0 | 32.582 | 30.442 | 196.219 | 7.63 | 184.729 | 2210.77 | 25.78 | 42.929 | 6.37 | 1.375 | 4.729 | 8680.41 | 2.241 | 98.1 | 77.5 | 1438 | 21.46 | 5642.3 | 2962.1 | 2873.2 | 4238.9 | 1218.8 | 0.68179 | 6.102
2024-12-10 | 1:22 | Data | 0 | 32.75 | 30.658 | 196.309 | 7.63 | 184.819 | 2214.39 | 25.78 | 42.929 | 6.37 | 1.367 | 4.73 | 8712.07 | 2.052 | 98.1 | 77.6 | 1439 | 21.46 | 5662.8 | 2956.7 | 2856.3 | 4226 | 1218.8 | 0.68251 | 6.096
2024-12-10 | 1:22 | Data | 0 | 32.507 | 30.59 | 196.173 | 7.63 | 184.684 | 2210.77 | 25.78 | 42.929 | 6.37 | 1.37 | 4.734 | 8716.59 | 1.965 | 98.1 | 77.6 | 1438 | 21.42 | 5665.8 | 2945.5 | 2880.2 | 4235.6 | 1218.8 | 0.67904 | 6.103
2024-12-10 | 1:22 | Data | 0 | 32.609 | 30.59 | 196.309 | 7.64 | 184.684 | 2211.68 | 25.78 | 42.929 | 6.37 | 1.376 | 4.688 | 8703.03 | 2.174 | 98.1 | 77.3 | 1438 | 21.42 | 5657 | 2974.2 | 2857.7 | 4236 | 1218.8 | 0.68601 | 6.064
2024-12-10 | 1:22 | Data | 0 | 32.919 | 30.55 | 196.264 | 7.64 | 184.819 | 2211.68 | 25.78 | 42.929 | 6.37 | 1.377 | 4.682 | 8707.55 | 2.241 | 98.1 | 77.3 | 1437 | 21.46 | 5659.9 | 2967.5 | 2885.5 | 4253.2 | 1218.8 | 0.68093 | 6.056
2024-12-10 | 1:22 | Data | 0 | 32.609 | 30.219 | 196.128 | 7.63 | 184.639 | 2208.97 | 25.78 | 42.929 | 6.37 | 1.386 | 4.722 | 8693.98 | 2.255 | 98.1 | 77.3 | 1436 | 21.42 | 5651.1 | 2980.9 | 2879.6 | 4258.6 | 1218.8 | 0.68359 | 6.108
2024-12-10 | 1:22 | Data | 0 | 32.764 | 30.867 | 196.354 | 7.64 | 184.729 | 2208.06 | 25.78 | 42.929 | 6.37 | 1.373 | 4.723 | 8703.03 | 2.12 | 98.1 | 77.5 | 1435 | 21.46 | 5657 | 2973.4 | 2870.7 | 4247.4 | 1218.8 | 0.68396 | 6.096
2024-12-10 | 1:22 | Data | 0 | 32.379 | 30.408 | 196.219 | 7.64 | 184.593 | 2210.77 | 25.78 | 42.838 | 6.37 | 1.372 | 4.703 | 8693.98 | 2.046 | 98.1 | 77.4 | 1437 | 21.42 | 5651.1 | 2980.9 | 2874.2 | 4252.9 | 1218.8 | 0.68206 | 6.077
2024-12-10 | 1:22 | Data | 0 | 32.656 | 30.415 | 196.173 | 7.64 | 184.729 | 2210.77 | 25.78 | 42.929 | 6.37 | 1.383 | 4.692 | 8693.98 | 2.295 | 98.1 | 77.2 | 1437 | 21.46 | 5651.1 | 2976.5 | 2897 | 4272.3 | 1218.8 | 0.67913 | 6.074
2024-12-10 | 1:22 | Data | 0 | 32.447 | 30.205 | 196.173 | 7.64 | 184.684 | 2211.68 | 25.79 | 42.748 | 6.37 | 1.375 | 4.709 | 8721.11 | 2.167 | 98.1 | 77.4 | 1438 | 21.33 | 5668.7 | 2954.7 | 2882.2 | 4240.9 | 1218.9 | 0.68026 | 6.084
2024-12-10 | 1:22 | Data | 0 | 32.494 | 30.617 | 196.219 | 7.64 | 184.684 | 2209.87 | 25.78 | 43.019 | 6.36 | 1.376 | 4.709 | 8721.11 | 1.985 | 98.1 | 77.4 | 1437 | 21.51 | 5668.7 | 2959.8 | 2888.5 | 4246.7 | 1218.9 | 0.67875 | 6.083
2024-12-10 | 1:22 | Data | 0 | 32.582 | 30.408 | 196.128 | 7.64 | 184.503 | 2212.58 | 25.78 | 42.838 | 6.37 | 1.38 | 4.704 | 8703.03 | 2.289 | 98.1 | 77.3 | 1438 | 21.42 | 5657 | 2969.2 | 2869.8 | 4244.3 | 1218.9 | 0.68212 | 6.085
2024-12-10 | 1:22 | Data | 0 | 32.332 | 30.523 | 196.219 | 7.63 | 184.639 | 2212.58 | 25.79 | 42.929 | 6.37 | 1.374 | 4.706 | 8712.07 | 1.924 | 98.1 | 77.4 | 1438 | 21.46 | 5662.8 | 2958.3 | 2874 | 4248.7 | 1218.9 | 0.68081 | 6.079
2024-12-10 | 1:22 | Data | 0 | 32.73 | 30.59 | 196.309 | 7.63 | 184.774 | 2212.58 | 25.78 | 42.929 | 6.37 | 1.377 | 4.72 | 8734.68 | 2.019 | 98.1 | 77.4 | 1438 | 21.46 | 5677.5 | 2944.2 | 2889.7 | 4241.5 | 1218.9 | 0.67714 | 6.096
2024-12-10 | 1:22 | Data | 0 | 32.298 | 30.475 | 196.173 | 7.64 | 184.684 | 2213.49 | 25.78 | 43.2 | 6.37 | 1.378 | 4.726 | 8734.68 | 2.086 | 98 | 77.4 | 1438 | 21.6 | 5677.5 | 2972.4 | 2892.5 | 4261.9 | 1218.9 | 0.67946 | 6.104
2024-12-10 | 1:22 | Data | 0 | 32.494 | 30.415 | 196.219 | 7.63 | 184.729 | 2211.68 | 25.78 | 42.929 | 6.37 | 1.377 | 4.71 | 8743.73 | 2.079 | 98.1 | 77.4 | 1438 | 21.46 | 5683.4 | 2972.1 | 2893.9 | 4260.3 | 1218.9 | 0.68049 | 6.087
2024-12-10 | 1:22 | Data | 0 | 32.71 | 30.651 | 196.219 | 7.63 | 184.684 | 2211.68 | 25.78 | 42.929 | 6.37 | 1.376 | 4.719 | 8730.16 | 2.073 | 98.1 | 77.4 | 1438 | 21.46 | 5674.6 | 2971.4 | 2878.3 | 4251.6 | 1218.9 | 0.68221 | 6.092
2024-12-10 | 1:22 | Data | 0 | 32.879 | 30.651 | 196.309 | 7.64 | 184.865 | 2208.06 | 25.78 | 42.929 | 6.37 | 1.378 | 4.711 | 8712.07 | 2.268 | 98.1 | 77.4 | 1435 | 21.46 | 5662.8 | 2977.8 | 2916 | 4266.9 | 1218.9 | 0.67877 | 6.09
2024-12-10 | 1:23 | Data | 0 | 32.838 | 30.651 | 196.309 | 7.64 | 184.819 | 2206.25 | 25.78 | 42.929 | 6.37 | 1.375 | 4.707 | 8698.5 | 2.086 | 98.1 | 77.4 | 1434 | 21.46 | 5654 | 2957.9 | 2900.7 | 4254.4 | 1218.9 | 0.67836 | 6.082
2024-12-10 | 1:23 | Data | 0 | 32.771 | 30.482 | 196.309 | 7.63 | 184.819 | 2206.25 | 25.78 | 42.838 | 6.37 | 1.378 | 4.695 | 8693.98 | 2.14 | 98.1 | 77.3 | 1434 | 21.42 | 5651.1 | 2963.4 | 2887.5 | 4251.1 | 1218.9 | 0.68017 | 6.074
2024-12-10 | 1:23 | Data | 0 | 32.312 | 30.421 | 196.309 | 7.64 | 184.819 | 2206.25 | 25.78 | 42.838 | 6.37 | 1.367 | 4.692 | 8689.46 | 1.857 | 98.1 | 77.4 | 1434 | 21.46 | 5648.1 | 2974.2 | 2897.9 | 4264.2 | 1218.9 | 0.6808 | 6.06
2024-12-10 | 1:23 | Data | 0 | 32.717 | 30.428 | 196.354 | 7.63 | 184.729 | 2206.25 | 25.78 | 42.929 | 6.37 | 1.37 | 4.71 | 8693.98 | 2.14 | 98.1 | 77.5 | 1433 | 21.46 | 5651.1 | 2958.8 | 2898.9 | 4259.1 | 1218.9 | 0.67936 | 6.079
2024-12-10 | 1:23 | Data | 0 | 32.568 | 30.421 | 196.219 | 7.64 | 184.774 | 2208.06 | 25.78 | 43.019 | 6.37 | 1.376 | 4.705 | 8730.16 | 1.978 | 98.1 | 77.4 | 1435 | 21.46 | 5674.6 | 2972 | 2894.1 | 4264.6 | 1218.9 | 0.67864 | 6.08
2024-12-10 | 1:23 | Data | 0 | 32.771 | 30.975 | 196.264 | 7.64 | 184.819 | 2210.77 | 25.78 | 43.019 | 6.37 | 1.377 | 4.731 | 8716.59 | 2.066 | 98.1 | 77.5 | 1437 | 21.46 | 5665.8 | 2947.2 | 2879.5 | 4237.1 | 1218.9 | 0.67908 | 6.109
2024-12-10 | 1:23 | Data | 0 | 32.831 | 30.435 | 196.264 | 7.63 | 184.819 | 2211.68 | 25.78 | 42.838 | 6.37 | 1.373 | 4.728 | 8730.16 | 2.268 | 98.1 | 77.5 | 1438 | 21.42 | 5674.6 | 2967.2 | 2880.3 | 4249.9 | 1218.9 | 0.6813 | 6.101
2024-12-10 | 1:23 | Data | 0 | 32.649 | 30.847 | 196.309 | 7.64 | 184.819 | 2210.77 | 25.78 | 42.929 | 6.37 | 1.378 | 4.717 | 8730.16 | 2.1 | 98.1 | 77.4 | 1437 | 21.46 | 5674.6 | 2955 | 2904 | 4256.7 | 1218.9 | 0.67763 | 6.094
2024-12-10 | 1:23 | Data | 0 | 32.696 | 30.442 | 196.083 | 7.64 | 184.639 | 2211.68 | 25.78 | 42.838 | 6.37 | 1.367 | 4.715 | 8703.03 | 2.187 | 98.1 | 77.5 | 1438 | 21.46 | 5657 | 2985.9 | 2909.6 | 4281 | 1218.9 | 0.67976 | 6.083
2024-12-10 | 1:23 | Data | 0 | 32.501 | 30.428 | 196.219 | 7.63 | 184.729 | 2214.39 | 25.77 | 42.929 | 6.37 | 1.379 | 4.714 | 8689.46 | 2.052 | 98.1 | 77.4 | 1439 | 21.51 | 5648.1 | 2737.7 | 2707.8 | 3946.5 | 1218.9 | 0.67046 | 6.092
2024-12-10 | 1:23 | Data | 0 | 32.696 | 30.651 | 196.219 | 7.64 | 184.774 | 2212.58 | 25.78 | 42.929 | 6.37 | 1.377 | 4.712 | 8698.5 | 2.066 | 98.1 | 77.4 | 1438 | 21.46 | 5654 | 1886 | 2339.5 | 3016.3 | 1218.9 | 0.62362 | 6.092
2024-12-10 | 1:23 | Data | 0 | 32.609 | 30.651 | 196.264 | 7.64 | 184.774 | 2217.1 | 25.78 | 42.929 | 6.37 | 1.369 | 4.706 | 8703.03 | 1.857 | 98.1 | 77.5 | 1441 | 21.46 | 5657 | 1893.9 | 2328.7 | 3011.8 | 1218.9 | 0.62655 | 6.074
2024-12-10 | 1:23 | Data | 0 | 32.494 | 30.631 | 196.219 | 7.64 | 184.684 | 2216.2 | 25.78 | 42.929 | 6.36 | 1.375 | 4.707 | 8653.28 | 1.877 | 98.1 | 77.4 | 1441 | 21.46 | 5624.6 | 1888.3 | 2329.1 | 3010 | 1218.9 | 0.62522 | 6.082
2024-12-10 | 1:23 | Data | 0 | 32.582 | 30.415 | 196.354 | 7.64 | 184.774 | 2216.2 | 25.78 | 42.929 | 6.37 | 1.383 | 4.695 | 8657.8 | 2.093 | 98.1 | 77.2 | 1441 | 21.42 | 5627.6 | 1875.4 | 2316 | 2991 | 1218.9 | 0.62441 | 6.077
2024-12-10 | 1:23 | Data | 0 | 32.811 | 30.651 | 196.219 | 7.64 | 184.774 | 2216.2 | 25.78 | 42.929 | 6.36 | 1.379 | 4.726 | 8648.76 | 2.275 | 98.1 | 77.4 | 1441 | 21.46 | 5621.7 | 1887.1 | 2322.9 | 3004.9 | 1218.9 | 0.62497 | 6.105
2024-12-10 | 1:23 | Data | 0 | 32.669 | 30.536 | 196.219 | 7.63 | 184.729 | 2268.62 | 25.78 | 42.929 | 6.37 | 1.376 | 4.714 | 8648.76 | 2.133 | 98.1 | 77.4 | 1474 | 21.46 | 5621.7 | 1889.1 | 2327 | 3009 | 1218.9 | 0.6251 | 6.09
2024-12-10 | 1:23 | Data | 0 | 32.548 | 30.604 | 196.264 | 7.64 | 184.729 | 2268.62 | 25.78 | 42.929 | 6.37 | 1.371 | 4.711 | 8680.41 | 2.14 | 98.1 | 77.5 | 1475 | 21.42 | 5642.3 | 1892 | 2333.1 | 3014.6 | 1218.9 | 0.62485 | 6.082
2024-12-10 | 1:24 | Data | 0 | 32.467 | 30.59 | 196.173 | 7.63 | 184.684 | 2268.62 | 25.78 | 42.929 | 6.37 | 1.375 | 4.73 | 8680.41 | 2.133 | 98.1 | 77.5 | 1475 | 21.46 | 5642.3 | 1880.9 | 2328.6 | 3005.6 | 1218.9 | 0.62331 | 6.106
2024-12-10 | 1:24 | Data | 0 | 32.399 | 30.3 | 196.219 | 7.63 | 184.684 | 2271.33 | 25.76 | 42.838 | 6.37 | 1.381 | 4.718 | 8666.85 | 1.87 | 98.1 | 77.4 | 1476 | 21.51 | 5633.5 | 1897.5 | 2321.9 | 3009.4 | 1218.9 | 0.62829 | 6.098
2024-12-10 | 1:24 | Data | 0 | 32.764 | 30.84 | 196.399 | 7.63 | 184.774 | 2220.72 | 25.77 | 42.838 | 6.37 | 1.367 | 4.697 | 8689.46 | 2.154 | 98.1 | 77.5 | 1443 | 21.46 | 5648.1 | 1886.3 | 2306.3 | 2990.8 | 1218.9 | 0.62833 | 6.065
2024-12-10 | 1:24 | Data | 0 | 32.609 | 30.415 | 196.128 | 7.64 | 184.729 | 2225.23 | 25.78 | 42.929 | 6.37 | 1.367 | 4.692 | 8693.98 | 2.093 | 98.1 | 77.4 | 1446 | 21.46 | 5651.1 | 1889.4 | 2345.6 | 3023 | 1218.9 | 0.62467 | 6.058
2024-12-10 | 1:24 | Data | 0 | 32.609 | 30.847 | 196.219 | 7.64 | 184.729 | 2225.23 | 25.78 | 42.929 | 6.37 | 1.372 | 4.685 | 8689.46 | 2.235 | 98.1 | 77.3 | 1446 | 21.46 | 5648.1 | 1883.5 | 2331 | 3008.4 | 1218.9 | 0.62392 | 6.057
2024-12-10 | 1:24 | Data | 0 | 32.291 | 30.415 | 196.264 | 7.63 | 184.774 | 2223.43 | 25.77 | 42.929 | 6.36 | 1.385 | 4.701 | 8684.94 | 2.025 | 98.1 | 77.2 | 1445 | 21.46 | 5645.2 | 1884.1 | 2326.5 | 3003.9 | 1218.9 | 0.62442 | 6.085
2024-12-10 | 1:24 | Data | 0 | 32.609 | 30.415 | 196.219 | 7.64 | 184.684 | 2222.52 | 25.76 | 42.838 | 6.37 | 1.384 | 4.717 | 8684.94 | 2.1 | 98.1 | 77.3 | 1445 | 21.42 | 5645.2 | 1879.2 | 2317.7 | 3008.4 | 1218.9 | 0.62697 | 6.101
2024-12-10 | 1:24 | Data | 0 | 32.521 | 30.739 | 196.264 | 7.64 | 184.819 | 2222.52 | 25.78 | 43.019 | 6.37 | 1.375 | 4.698 | 8703.03 | 1.911 | 98.1 | 77.4 | 1445 | 21.46 | 5657 | 1890.4 | 2329.2 | 3010 | 1218.9 | 0.6262 | 6.074
2024-12-10 | 1:24 | Data | 0 | 32.933 | 30.448 | 196.309 | 7.63 | 184.819 | 2220.72 | 25.76 | 42.929 | 6.37 | 1.376 | 4.699 | 8703.03 | 2.329 | 98.1 | 77.4 | 1442 | 21.51 | 5657 | 1879.3 | 2323.6 | 3000.2 | 1218.9 | 0.62345 | 6.074
2024-12-10 | 1:24 | Data | 0 | 32.885 | 30.225 | 196.309 | 7.63 | 184.819 | 2218.91 | 25.76 | 42.838 | 6.37 | 1.381 | 4.72 | 8693.98 | 1.978 | 98.1 | 77.4 | 1442 | 21.46 | 5651.1 | 1889.7 | 2321.4 | 3004.6 | 1218.9 | 0.62688 | 6.101
2024-12-10 | 1:24 | Data | 0 | 32.271 | 30.185 | 195.992 | 7.63 | 184.729 | 2221.62 | 25.77 | 42.929 | 6.36 | 1.378 | 4.723 | 8703.03 | 2.194 | 98.1 | 77.4 | 1444 | 21.46 | 5657 | 1881.5 | 2324 | 3001.7 | 1218.9 | 0.62383 | 6.102
2024-12-10 | 1:24 | Data | 0 | 32.588 | 30.415 | 196.219 | 7.64 | 184.684 | 2221.62 | 25.78 | 42.838 | 6.37 | 1.377 | 4.705 | 8689.46 | 2.127 | 98.1 | 77.4 | 1445 | 21.42 | 5648.1 | 1875.3 | 2333.7 | 3004.5 | 1218.9 | 0.62252 | 6.081
2024-12-10 | 1:24 | Data | 0 | 32.285 | 30.408 | 196.173 | 7.64 | 184.729 | 2218 | 25.77 | 42.929 | 6.37 | 1.37 | 4.714 | 8666.85 | 1.978 | 98.1 | 77.5 | 1442 | 21.42 | 5633.5 | 1902.9 | 2335 | 3018.3 | 1218.9 | 0.62696 | 6.083
2024-12-10 | 1:24 | Data | 0 | 32.595 | 30.59 | 196.173 | 7.64 | 184.639 | 2217.1 | 25.77 | 42.929 | 6.37 | 1.37 | 4.708 | 8657.8 | 2.12 | 98.1 | 77.5 | 1441 | 21.46 | 5627.6 | 1882.5 | 2314.9 | 2994.4 | 1218.9 | 0.62288 | 6.078
2024-12-10 | 1:24 | Data | 0 | 32.501 | 30.624 | 196.128 | 7.64 | 184.729 | 2222.52 | 25.76 | 42.929 | 6.37 | 1.379 | 4.703 | 8666.85 | 2.019 | 98.1 | 77.3 | 1445 | 21.46 | 5633.5 | 1888.3 | 2327.9 | 3007.7 | 1218.9 | 0.62528 | 6.083
2024-12-10 | 1:24 | Data | 0 | 32.69 | 30.469 | 196.128 | 7.63 | 184.774 | 2216.2 | 25.77 | 42.838 | 6.37 | 1.375 | 4.723 | 8662.33 | 2.194 | 98.1 | 77.5 | 1440 | 21.46 | 5630.5 | 1890.8 | 2332.4 | 3012.5 | 1218.9 | 0.62522 | 6.099
2024-12-10 | 1:24 | Data | 0 | 32.44 | 30.475 | 196.128 | 7.63 | 184.684 | 2216.2 | 25.76 | 42.838 | 6.37 | 1.367 | 4.703 | 8662.33 | 1.951 | 98.1 | 77.5 | 1441 | 21.51 | 5630.5 | 1889.3 | 2341.3 | 3019 | 1218.9 | 0.62371 | 6.072
2024-12-10 | 1:24 | Data | 0 | 32.602 | 30.421 | 196.173 | 7.64 | 184.639 | 2216.2 | 25.77 | 42.838 | 6.37 | 1.373 | 4.705 | 8671.37 | 2.106 | 98.1 | 77.4 | 1441 | 21.46 | 5636.4 | 1873 | 2319.6 | 2992.2 | 1218.9 | 0.6235 | 6.079
2024-12-10 | 1:25 | Data | 0 | 32.224 | 30.556 | 196.173 | 7.64 | 184.593 | 2216.2 | 25.77 | 42.838 | 6.37 | 1.379 | 4.683 | 8680.41 | 1.992 | 98.1 | 77.3 | 1441 | 21.42 | 5642.3 | 1869.1 | 2324.4 | 2994.2 | 1218.9 | 0.62192 | 6.063
2024-12-10 | 1:25 | Data | 0 | 32.467 | 30.394 | 196.173 | 7.63 | 184.684 | 2212.58 | 25.76 | 42.929 | 6.37 | 1.376 | 4.714 | 8662.33 | 2.16 | 98.1 | 77.4 | 1438 | 21.46 | 5630.5 | 1878 | 2310.3 | 2987 | 1218.9 | 0.62621 | 6.09
2024-12-10 | 1:25 | Data | 0 | 32.379 | 30.192 | 196.128 | 7.64 | 184.639 | 2214.39 | 25.76 | 42.929 | 6.37 | 1.377 | 4.721 | 8657.8 | 2.079 | 98.1 | 77.4 | 1439 | 21.46 | 5627.6 | 1884.7 | 2329.6 | 3006.5 | 1219 | 0.62479 | 6.096
2024-12-10 | 1:25 | Data | 0 | 32.393 | 30.273 | 196.173 | 7.64 | 184.729 | 2213.49 | 25.76 | 43.019 | 6.37 | 1.382 | 4.715 | 8648.76 | 2.005 | 98.1 | 77.3 | 1439 | 21.46 | 5621.7 | 1878.6 | 2308.3 | 2987.9 | 1219 | 0.62549 | 6.097
2024-12-10 | 1:25 | Data | 0 | 32.494 | 30.239 | 196.264 | 7.63 | 184.729 | 2210.77 | 25.76 | 43.47 | 6.37 | 1.377 | 4.741 | 8644.24 | 1.877 | 98 | 77.5 | 1437 | 21.74 | 5618.8 | 1890.6 | 2329.5 | 3010.3 | 1219 | 0.62622 | 6.119
2024-12-10 | 1:25 | Data | 0 | 32.595 | 30.644 | 196.173 | 7.64 | 184.639 | 2095.99 | 25.77 | 42.929 | 6.37 | 1.375 | 4.707 | 8648.76 | 2.025 | 98 | 77.4 | 1362 | 21.46 | 5621.7 | 1880.8 | 2300.4 | 2982.4 | 1219 | 0.62812 | 6.083
2024-12-10 | 1:25 | Data | 0 | 32.494 | 30.624 | 195.992 | 7.64 | 184.639 | 2201.74 | 25.77 | 42.838 | 6.37 | 1.376 | 4.692 | 8666.85 | 2.039 | 98.1 | 77.3 | 1431 | 21.42 | 5633.5 | 1876.9 | 2331.6 | 3002.5 | 1219 | 0.62353 | 6.069
2024-12-10 | 1:25 | Data | 0 | 32.744 | 30.428 | 196.219 | 7.64 | 184.684 | 2206.25 | 25.77 | 42.838 | 6.37 | 1.367 | 4.707 | 8662.33 | 2.113 | 98.1 | 77.5 | 1433 | 21.46 | 5630.5 | 1893.5 | 2327.6 | 3011.3 | 1219 | 0.62646 | 6.074
2024-12-10 | 1:25 | Data | 0 | 32.379 | 30.577 | 196.083 | 7.63 | 184.593 | 2203.54 | 25.76 | 42.929 | 6.37 | 1.371 | 4.703 | 8648.76 | 1.985 | 98.1 | 77.4 | 1433 | 21.46 | 5621.7 | 1882.3 | 2323.7 | 3001.7 | 1219 | 0.62451 | 6.074
2024-12-10 | 1:25 | Data | 0 | 32.339 | 30.415 | 196.083 | 7.63 | 184.729 | 2217.1 | 25.76 | 43.109 | 6.37 | 1.374 | 4.705 | 8648.76 | 1.87 | 98.1 | 77.4 | 1441 | 21.6 | 5621.7 | 1895.7 | 2325.2 | 3010.5 | 1219 | 0.62733 | 6.08
2024-12-10 | 1:25 | Data | 0 | 32.946 | 30.556 | 196.399 | 7.64 | 184.819 | 2218 | 25.77 | 42.929 | 6.37 | 1.371 | 4.712 | 8662.33 | 2.106 | 98.1 | 77.5 | 1441 | 21.42 | 5630.5 | 1903.2 | 2330.3 | 3019.3 | 1219 | 0.62765 | 6.083
2024-12-10 | 1:25 | Data | 0 | 32.271 | 30.732 | 196.128 | 7.63 | 184.639 | 2222.52 | 25.77 | 42.929 | 6.37 | 1.369 | 4.699 | 8657.8 | 1.931 | 98.1 | 77.5 | 1445 | 21.42 | 5627.6 | 1900.6 | 2342.9 | 3026.3 | 1219 | 0.62566 | 6.065
2024-12-10 | 1:25 | Data | 0 | 32.042 | 30.408 | 196.173 | 7.64 | 184.684 | 2217.1 | 25.77 | 42.929 | 6.37 | 1.377 | 4.707 | 8666.85 | 2.073 | 98.1 | 77.4 | 1441 | 21.42 | 5633.5 | 1888.3 | 2322.5 | 3003.9 | 1219 | 0.62566 | 6.083
2024-12-10 | 1:25 | Data | 0 | 32.44 | 30.421 | 196.173 | 7.63 | 184.593 | 2218.91 | 25.76 | 42.929 | 6.37 | 1.374 | 4.703 | 8693.98 | 2.066 | 98.1 | 77.4 | 1442 | 21.46 | 5651.1 | 1878.4 | 2327.6 | 3003 | 1219 | 0.62316 | 6.077
2024-12-10 | 1:25 | Data | 0 | 32.048 | 30.3 | 195.992 | 7.63 | 184.684 | 2218 | 25.76 | 42.838 | 6.37 | 1.384 | 4.675 | 8648.76 | 2.025 | 98.1 | 77.2 | 1442 | 21.46 | 5621.7 | 1887.2 | 2303.9 | 2989.7 | 1219 | 0.62843 | 6.058
2024-12-10 | 1:25 | Data | 0 | 32.494 | 30.219 | 195.947 | 7.64 | 184.639 | 2220.72 | 25.77 | 42.929 | 6.37 | 1.376 | 4.716 | 8657.8 | 2.241 | 98.1 | 77.4 | 1442 | 21.46 | 5627.6 | 1869.1 | 2295.7 | 2972.3 | 1219 | 0.62623 | 6.092
2024-12-10 | 1:25 | Data | 0 | 32.69 | 30.442 | 196.128 | 7.63 | 184.639 | 2216.2 | 25.76 | 42.929 | 6.36 | 1.374 | 4.702 | 8662.33 | 2.133 | 98.1 | 77.4 | 1441 | 21.46 | 5630.5 | 1874.9 | 2317.6 | 2991.5 | 1219 | 0.62445 | 6.075
2024-12-10 | 1:25 | Data | 0 | 32.467 | 30.421 | 195.992 | 7.64 | 184.548 | 2216.2 | 25.76 | 42.748 | 6.37 | 1.378 | 4.72 | 8680.41 | 2.154 | 98.1 | 77.4 | 1441 | 21.42 | 5642.3 | 1872.1 | 2313.4 | 2987 | 1219 | 0.62456 | 6.099
2024-12-10 | 1:26 | Data | 0 | 32.534 | 30.273 | 196.128 | 7.64 | 184.593 | 2216.2 | 25.77 | 42.929 | 6.37 | 1.379 | 4.711 | 8648.76 | 2.181 | 98.1 | 77.4 | 1441 | 21.51 | 5621.7 | 1870.3 | 2306.5 | 2980.7 | 1219 | 0.62504 | 6.091
2024-12-10 | 1:26 | Data | 0 | 32.899 | 30.516 | 196.173 | 7.63 | 184.684 | 2216.2 | 25.76 | 42.929 | 6.37 | 1.38 | 4.689 | 8648.76 | 2.187 | 98.1 | 77.3 | 1441 | 21.42 | 5621.7 | 1893.7 | 2239.6 | 2944.5 | 1219 | 0.64111 | 6.07
2024-12-10 | 1:26 | Data | 0 | 32.858 | 30.651 | 196.219 | 7.63 | 184.729 | 2216.2 | 25.76 | 42.929 | 6.37 | 1.376 | 4.675 | 8662.33 | 2.262 | 98.1 | 77.3 | 1441 | 21.42 | 5630.5 | 1880.2 | 2313.6 | 2992.4 | 1219 | 0.62575 | 6.051
2024-12-10 | 1:26 | Data | 0 | 32.494 | 30.415 | 196.083 | 7.64 | 184.684 | 2216.2 | 25.76 | 42.929 | 6.37 | 1.378 | 4.689 | 8684.94 | 2.106 | 98.1 | 77.3 | 1441 | 21.46 | 5645.2 | 1888.8 | 2329.4 | 3010.6 | 1219 | 0.62558 | 6.066
2024-12-10 | 1:26 | Data | 0 | 32.102 | 30.016 | 196.128 | 7.63 | 184.639 | 2217.1 | 25.76 | 42.929 | 6.37 | 1.374 | 4.693 | 8703.03 | 1.87 | 98.1 | 77.4 | 1441 | 21.42 | 5657 | 1877.7 | 2306.7 | 2984.7 | 1219 | 0.62684 | 6.067
2024-12-10 | 1:26 | Data | 0 | 32.278 | 30.361 | 195.947 | 7.63 | 184.593 | 2217.1 | 25.76 | 42.838 | 6.37 | 1.372 | 4.711 | 8689.46 | 1.971 | 98.1 | 77.4 | 1441 | 21.46 | 5648.1 | 1895 | 2333.6 | 3017.4 | 1219 | 0.62581 | 6.084
2024-12-10 | 1:26 | Data | 0 | 32.379 | 30.401 | 195.902 | 7.64 | 184.548 | 2216.2 | 25.77 | 42.838 | 6.37 | 1.372 | 4.72 | 8716.59 | 2.079 | 98.1 | 77.5 | 1441 | 21.46 | 5665.8 | 3107 | 3221.2 | 4627.2 | 1219 | 0.66782 | 6.091
2024-12-10 | 1:26 | Data | 0 | 32.062 | 30.401 | 196.083 | 7.64 | 184.368 | 2214.39 | 25.77 | 42.929 | 6.37 | 1.384 | 4.717 | 8680.41 | 1.884 | 98.1 | 77.3 | 1439 | 21.42 | 5642.3 | 2984.5 | 2877.9 | 4257.2 | 1219 | 0.68513 | 6.1
2024-12-10 | 1:26 | Data | 0 | 32.46 | 30.198 | 195.947 | 7.64 | 184.639 | 2213.49 | 25.77 | 42.929 | 6.37 | 1.383 | 4.69 | 8689.46 | 2.174 | 98.1 | 77.3 | 1439 | 21.46 | 5648.1 | 2946.8 | 2868.2 | 4229.9 | 1219 | 0.6799 | 6.071
2024-12-10 | 1:26 | Data | 0 | 32.75 | 30.192 | 196.264 | 7.64 | 184.684 | 2211.68 | 25.76 | 42.838 | 6.37 | 1.377 | 4.702 | 8712.07 | 1.965 | 98.1 | 77.3 | 1438 | 21.46 | 5662.8 | 2973.8 | 2866 | 4244.4 | 1219 | 0.68279 | 6.079
2024-12-10 | 1:26 | Data | 0 | 32.575 | 30.408 | 196.173 | 7.64 | 184.684 | 2208.97 | 25.77 | 42.929 | 6.37 | 1.379 | 4.687 | 8693.98 | 2.127 | 98.1 | 77.3 | 1436 | 21.42 | 5651.1 | 2959.7 | 2861.9 | 4232.5 | 1219 | 0.68224 | 6.066
2024-12-10 | 1:26 | Data | 0 | 32.379 | 30.523 | 195.992 | 7.64 | 184.639 | 2208.97 | 25.77 | 42.929 | 6.37 | 1.377 | 4.718 | 8693.98 | 2.059 | 98.1 | 77.4 | 1436 | 21.46 | 5651.1 | 2944.6 | 2866.8 | 4225.4 | 1219 | 0.67922 | 6.095
2024-12-10 | 1:26 | Data | 0 | 32.312 | 30.185 | 196.083 | 7.63 | 184.639 | 2207.16 | 25.76 | 42.929 | 6.37 | 1.377 | 4.74 | 8721.11 | 2.079 | 98.1 | 77.5 | 1435 | 21.46 | 5668.7 | 2974.2 | 2869.2 | 4259.8 | 1219 | 0.68316 | 6.115
2024-12-10 | 1:26 | Data | 0 | 32.264 | 30.415 | 196.083 | 7.63 | 184.639 | 2205.35 | 25.77 | 42.929 | 6.37 | 1.375 | 4.731 | 8721.11 | 2.167 | 98.1 | 77.5 | 1434 | 21.46 | 5668.7 | 2977.5 | 2892 | 4262.9 | 1219 | 0.68195 | 6.107
2024-12-10 | 1:26 | Data | 0 | 32.71 | 30.219 | 196.219 | 7.64 | 184.639 | 2205.35 | 25.76 | 42.929 | 6.37 | 1.375 | 4.718 | 8716.59 | 2.106 | 98.1 | 77.4 | 1434 | 21.46 | 5665.8 | 2957.6 | 2877.6 | 4243.7 | 1219 | 0.68043 | 6.092
2024-12-10 | 1:26 | Data | 0 | 32.163 | 30.185 | 196.128 | 7.63 | 184.684 | 2205.35 | 25.76 | 42.929 | 6.37 | 1.369 | 4.665 | 8721.11 | 1.978 | 98.1 | 77.3 | 1434 | 21.46 | 5668.7 | 2970.5 | 2881.9 | 4249.5 | 1219 | 0.68231 | 6.035
2024-12-10 | 1:26 | Data | 0 | 32.305 | 30.165 | 196.128 | 7.64 | 184.639 | 2208.97 | 25.76 | 42.929 | 6.37 | 1.367 | 4.674 | 8716.59 | 2.073 | 98.1 | 77.4 | 1435 | 21.42 | 5665.8 | 2951.4 | 2884.1 | 4261.5 | 1219 | 0.67948 | 6.041
2024-12-10 | 1:26 | Data | 0 | 32.332 | 30.198 | 196.083 | 7.64 | 184.729 | 2211.68 | 25.76 | 42.929 | 6.37 | 1.373 | 4.697 | 8721.11 | 2.073 | 98.1 | 77.4 | 1438 | 21.46 | 5668.7 | 2976.9 | 2893.6 | 4260.6 | 1219 | 0.67966 | 6.07
2024-12-10 | 1:27 | Data | 0 | 32.575 | 30.415 | 196.083 | 7.63 | 184.639 | 2206.25 | 25.76 | 43.019 | 6.37 | 1.379 | 4.685 | 8734.68 | 2.154 | 98.1 | 77.3 | 1434 | 21.51 | 5677.5 | 2972.9 | 2900.4 | 4268.9 | 1219 | 0.67869 | 6.064
2024-12-10 | 1:27 | Data | 0 | 32.312 | 30.246 | 196.173 | 7.63 | 184.684 | 2208.97 | 25.76 | 42.929 | 6.37 | 1.374 | 4.699 | 8721.11 | 1.85 | 98.1 | 77.4 | 1436 | 21.46 | 5668.7 | 2948.4 | 2881.7 | 4239.8 | 1219 | 0.67829 | 6.074
2024-12-10 | 1:27 | Data | 0 | 32.507 | 30.415 | 196.128 | 7.63 | 184.684 | 2208.06 | 25.76 | 42.929 | 6.37 | 1.372 | 4.711 | 8707.55 | 2.079 | 98.1 | 77.4 | 1435 | 21.46 | 5659.9 | 2983.5 | 2897.2 | 4270.8 | 1219 | 0.67942 | 6.083
2024-12-10 | 1:27 | Data | 0 | 32.69 | 30.239 | 196.083 | 7.64 | 184.548 | 2208.97 | 25.75 | 42.929 | 6.37 | 1.374 | 4.739 | 8689.46 | 2.289 | 98.1 | 77.5 | 1436 | 21.42 | 5648.1 | 2952.7 | 2886.1 | 4244.5 | 1219 | 0.67867 | 6.112
2024-12-10 | 1:27 | Data | 0 | 32.291 | 30.185 | 196.083 | 7.64 | 184.593 | 2208.06 | 25.75 | 42.929 | 6.37 | 1.382 | 4.71 | 8716.59 | 1.877 | 98.1 | 77.3 | 1435 | 21.46 | 5665.8 | 2945.5 | 2880.7 | 4237.9 | 1219 | 0.67732 | 6.092
2024-12-10 | 1:27 | Data | 0 | 32.453 | 30.415 | 195.947 | 7.64 | 184.639 | 2208.97 | 25.75 | 42.929 | 6.37 | 1.382 | 4.707 | 8716.59 | 2.086 | 98.1 | 77.3 | 1436 | 21.46 | 5665.8 | 2961.3 | 2876.6 | 4245.8 | 1219 | 0.68067 | 6.09
2024-12-10 | 1:27 | Data | 0 | 32.514 | 30.3 | 196.128 | 7.64 | 184.729 | 2205.35 | 25.76 | 42.929 | 6.37 | 1.377 | 4.667 | 8707.55 | 1.965 | 98.1 | 77.2 | 1434 | 21.46 | 5659.9 | 2963.4 | 2865.2 | 4236.8 | 1219 | 0.68257 | 6.044
2024-12-10 | 1:27 | Data | 0 | 32.831 | 30.435 | 196.173 | 7.64 | 184.729 | 2206.25 | 25.76 | 42.929 | 6.37 | 1.362 | 4.712 | 8689.46 | 2.275 | 98.1 | 77.6 | 1433 | 21.46 | 5648.1 | 2953.4 | 2869.7 | 4230.5 | 1219 | 0.68197 | 6.076
2024-12-10 | 1:27 | Data | 0 | 32.69 | 30.259 | 196.219 | 7.64 | 184.684 | 2200.83 | 25.77 | 42.929 | 6.37 | 1.365 | 4.735 | 9141.68 | 2.133 | 98 | 77.6 | 1431 | 21.46 | 5942.1 | 2939.3 | 2859.5 | 4216 | 1219 | 0.68021 | 6.1
2024-12-10 | 1:27 | Data | 0 | 32.636 | 30.469 | 196.083 | 7.64 | 184.684 | 2200.83 | 25.76 | 42.929 | 6.37 | 1.378 | 4.726 | 8662.33 | 2.302 | 98 | 77.4 | 1430 | 21.46 | 5630.5 | 2969.4 | 2850.5 | 4227.5 | 1219 | 0.68615 | 6.104
2024-12-10 | 1:27 | Data | 0 | 32.251 | 30.185 | 196.128 | 7.64 | 184.593 | 2203.54 | 25.76 | 42.838 | 6.36 | 1.377 | 4.718 | 8680.41 | 2.133 | 98.1 | 77.4 | 1432 | 21.42 | 5642.3 | 2965.3 | 2880.2 | 4250.4 | 1219.1 | 0.68113 | 6.095
2024-12-10 | 1:27 | Data | 0 | 32.622 | 30.313 | 196.128 | 7.63 | 184.729 | 2201.74 | 25.76 | 42.929 | 6.37 | 1.37 | 4.71 | 8657.8 | 2.079 | 98.1 | 77.5 | 1432 | 21.46 | 5627.6 | 2956.3 | 2880.7 | 4241.9 | 1219.1 | 0.68185 | 6.08
2024-12-10 | 1:27 | Data | 0 | 32.413 | 30.219 | 196.219 | 7.63 | 184.684 | 2205.35 | 25.76 | 43.019 | 6.37 | 1.381 | 4.707 | 8657.8 | 2.059 | 98.1 | 77.3 | 1434 | 21.51 | 5627.6 | 2951.8 | 2897.3 | 4241.4 | 1219.1 | 0.6766 | 6.088
2024-12-10 | 1:27 | Data | 0 | 32.588 | 30.415 | 196.128 | 7.64 | 184.639 | 2205.35 | 25.75 | 42.929 | 6.37 | 1.378 | 4.706 | 8680.41 | 2.275 | 98.1 | 77.3 | 1433 | 21.46 | 5642.3 | 2955.1 | 2889 | 4256.9 | 1219.1 | 0.67939 | 6.084
2024-12-10 | 1:27 | Data | 0 | 32.494 | 30.415 | 196.219 | 7.63 | 184.684 | 2206.25 | 25.76 | 42.929 | 6.37 | 1.378 | 4.707 | 8666.85 | 1.904 | 98.1 | 77.3 | 1433 | 21.46 | 5633.5 | 2974.1 | 2899.6 | 4264.5 | 1219.1 | 0.67963 | 6.084
2024-12-10 | 1:27 | Data | 0 | 32.264 | 30.388 | 196.173 | 7.64 | 184.639 | 2213.49 | 25.77 | 42.929 | 6.37 | 1.365 | 4.692 | 8657.8 | 2.079 | 98.1 | 77.5 | 1438 | 21.46 | 5627.6 | 2970.6 | 2895.2 | 4256.9 | 1219.1 | 0.68056 | 6.055
2024-12-10 | 1:27 | Data | 0 | 32.723 | 30.651 | 196.219 | 7.64 | 184.774 | 2208.06 | 25.76 | 42.929 | 6.37 | 1.371 | 4.692 | 8657.8 | 2.073 | 98.1 | 77.4 | 1435 | 21.46 | 5627.6 | 2965.8 | 2884.7 | 4252.9 | 1219.1 | 0.68119 | 6.063
2024-12-10 | 1:28 | Data | 0 | 32.264 | 30.361 | 196.083 | 7.63 | 184.593 | 2210.77 | 25.76 | 42.929 | 6.37 | 1.383 | 4.701 | 8264.37 | 2.079 | 98.1 | 77.3 | 1437 | 21.46 | 5371.8 | 2960.7 | 2867.1 | 4233.9 | 1219.1 | 0.68182 | 6.083
2024-12-10 | 1:28 | Data | 0 | 32.744 | 30.381 | 196.264 | 7.64 | 184.774 | 2214.39 | 25.76 | 42.929 | 6.37 | 1.377 | 4.706 | 8892.96 | 1.971 | 98.1 | 77.4 | 1439 | 21.46 | 5780.4 | 2956.4 | 2887.4 | 4244.9 | 1219.1 | 0.67757 | 6.083
2024-12-10 | 1:28 | Data | 0 | 32.494 | 30.415 | 195.992 | 7.63 | 184.593 | 2216.2 | 25.77 | 42.929 | 6.36 | 1.373 | 4.674 | 8892.96 | 2.079 | 98.1 | 77.3 | 1441 | 21.46 | 5780.4 | 2957.3 | 2909.1 | 4264.5 | 1219.1 | 0.67604 | 6.047
2024-12-10 | 1:28 | Data | 0 | 32.717 | 30.435 | 196.173 | 7.64 | 184.639 | 2216.2 | 25.76 | 42.838 | 6.37 | 1.377 | 4.701 | 8463.35 | 2.147 | 98.1 | 77.3 | 1441 | 21.46 | 5501.2 | 2955 | 2882.5 | 4244.5 | 1219.1 | 0.67924 | 6.077
2024-12-10 | 1:28 | Data | 0 | 32.352 | 30.185 | 195.902 | 7.64 | 184.593 | 2216.2 | 25.77 | 42.929 | 6.37 | 1.376 | 4.721 | 8476.91 | 2.289 | 98.1 | 77.4 | 1441 | 21.46 | 5510 | 2984.6 | 2890.1 | 4267.8 | 1219.1 | 0.68087 | 6.096
2024-12-10 | 1:28 | Data | 0 | 32.744 | 30.252 | 196.264 | 7.63 | 184.774 | 2217.1 | 25.77 | 43.019 | 6.37 | 1.367 | 4.72 | 8481.44 | 2.127 | 98.1 | 77.5 | 1441 | 21.46 | 5512.9 | 2959.7 | 2904.1 | 4261.7 | 1219.1 | 0.67778 | 6.086
2024-12-10 | 1:28 | Data | 0 | 32.487 | 30.408 | 196.083 | 7.64 | 184.684 | 2216.2 | 25.76 | 42.929 | 6.37 | 1.366 | 4.735 | 8472.39 | 1.971 | 98.1 | 77.6 | 1441 | 21.46 | 5507.1 | 2964.5 | 2905.6 | 4261.4 | 1219.1 | 0.67652 | 6.101
2024-12-10 | 1:28 | Data | 0 | 32.379 | 30.401 | 195.947 | 7.63 | 184.548 | 2217.1 | 25.76 | 42.929 | 6.36 | 1.366 | 4.721 | 8454.3 | 2.079 | 98.1 | 77.6 | 1441 | 21.42 | 5495.3 | 2967.6 | 2920 | 4273.7 | 1219.1 | 0.67708 | 6.086
2024-12-10 | 1:28 | Data | 0 | 32.055 | 30.388 | 196.173 | 7.64 | 184.593 | 2214.39 | 25.77 | 42.929 | 6.37 | 1.365 | 4.712 | 8467.87 | 1.904 | 98.1 | 77.6 | 1439 | 21.46 | 5504.1 | 2962.1 | 2883.9 | 4259.7 | 1219.1 | 0.68143 | 6.076
2024-12-10 | 1:28 | Data | 0 | 32.494 | 30.3 | 196.219 | 7.64 | 184.548 | 2213.49 | 25.76 | 42.929 | 6.36 | 1.367 | 4.697 | 8467.87 | 2.019 | 98.1 | 77.4 | 1438 | 21.46 | 5504.1 | 2972.9 | 2874.5 | 4250.5 | 1219.1 | 0.68118 | 6.066
2024-12-10 | 1:28 | Data | 0 | 32.602 | 30.192 | 196.128 | 7.64 | 184.729 | 2213.49 | 25.76 | 42.929 | 6.37 | 1.377 | 4.693 | 8513.09 | 2.133 | 98.1 | 77.3 | 1439 | 21.46 | 5533.5 | 2957.3 | 2881.2 | 4243.4 | 1219.1 | 0.67988 | 6.071
2024-12-10 | 1:28 | Data | 0 | 32.494 | 30.401 | 196.128 | 7.64 | 184.684 | 2213.49 | 25.76 | 42.929 | 6.36 | 1.362 | 4.697 | 8526.66 | 2.093 | 98.1 | 77.5 | 1439 | 21.46 | 5542.3 | 2967.7 | 2885.3 | 4251.9 | 1219.1 | 0.68033 | 6.059
2024-12-10 | 1:28 | Data | 0 | 32.264 | 30.185 | 196.128 | 7.64 | 184.639 | 2213.49 | 25.76 | 42.929 | 6.37 | 1.383 | 4.698 | 8526.66 | 2.079 | 98.1 | 77.3 | 1439 | 21.42 | 5542.3 | 2956.5 | 2894.1 | 4250.3 | 1219.1 | 0.67982 | 6.08
2024-12-10 | 1:28 | Data | 0 | 32.649 | 30.637 | 196.173 | 7.64 | 184.774 | 2217.1 | 25.76 | 42.929 | 6.37 | 1.371 | 4.717 | 8540.22 | 2.214 | 98.1 | 77.5 | 1442 | 21.46 | 5551.1 | 2971.3 | 2910.9 | 4272.1 | 1219.1 | 0.67767 | 6.088
2024-12-10 | 1:28 | Data | 0 | 32.555 | 30.401 | 196.128 | 7.64 | 184.729 | 2218.91 | 25.77 | 42.929 | 6.37 | 1.366 | 4.708 | 8567.36 | 1.911 | 98.1 | 77.5 | 1442 | 21.46 | 5568.8 | 2959.2 | 2896.5 | 4254.9 | 1219.1 | 0.6775 | 6.074
2024-12-10 | 1:28 | Data | 0 | 32.548 | 30.3 | 196.128 | 7.64 | 184.548 | 2217.1 | 25.76 | 42.929 | 6.37 | 1.367 | 4.714 | 8580.93 | 1.87 | 98.1 | 77.5 | 1442 | 21.42 | 5577.6 | 2987.1 | 2881.8 | 4259.9 | 1219.1 | 0.68464 | 6.079
2024-12-10 | 1:28 | Data | 0 | 32.46 | 30.516 | 196.128 | 7.64 | 184.639 | 2218.91 | 25.76 | 42.929 | 6.37 | 1.376 | 4.694 | 8594.49 | 2.214 | 98.1 | 77.3 | 1442 | 21.51 | 5586.4 | 2955.4 | 2883.6 | 4246.6 | 1219.1 | 0.67876 | 6.07
2024-12-10 | 1:28 | Data | 0 | 32.271 | 30.185 | 196.128 | 7.63 | 184.593 | 2218.91 | 25.76 | 42.838 | 6.37 | 1.376 | 4.699 | 8594.49 | 2.079 | 98.1 | 77.4 | 1442 | 21.46 | 5586.4 | 2967.2 | 2886.3 | 4248.9 | 1219.1 | 0.68043 | 6.074
2024-12-10 | 1:29 | Data | 0 | 32.831 | 30.705 | 196.219 | 7.64 | 184.774 | 2213.49 | 25.76 | 42.929 | 6.36 | 1.377 | 4.735 | 8594.49 | 2.039 | 98.1 | 77.5 | 1439 | 21.46 | 5586.4 | 2963.1 | 2867.7 | 4238.1 | 1219.1 | 0.68216 | 6.112
2024-12-10 | 1:29 | Data | 0 | 32.278 | 30.388 | 196.128 | 7.64 | 184.593 | 2216.2 | 25.76 | 42.929 | 6.37 | 1.377 | 4.74 | 8608.06 | 2.086 | 98.1 | 77.5 | 1441 | 21.46 | 5595.2 | 2971 | 2874.3 | 4256.3 | 1219.1 | 0.68263 | 6.118
2024-12-10 | 1:29 | Data | 0 | 32.696 | 30.651 | 196.219 | 7.64 | 184.729 | 2216.2 | 25.76 | 42.838 | 6.37 | 1.377 | 4.702 | 8617.1 | 2.073 | 98.1 | 77.3 | 1441 | 21.46 | 5601.1 | 2983.3 | 2887 | 4268.4 | 1219.1 | 0.68092 | 6.079
2024-12-10 | 1:29 | Data | 0 | 32.494 | 30.307 | 196.128 | 7.64 | 184.639 | 2213.49 | 25.76 | 42.929 | 6.37 | 1.369 | 4.717 | 8639.71 | 2.295 | 98.1 | 77.5 | 1438 | 21.46 | 5615.8 | 2967.8 | 2860.8 | 4232.4 | 1219.1 | 0.68505 | 6.084
2024-12-10 | 1:29 | Data | 0 | 32.656 | 30.428 | 196.083 | 7.64 | 184.684 | 2206.25 | 25.76 | 42.929 | 6.36 | 1.37 | 4.7 | 8621.63 | 2.221 | 98.1 | 77.4 | 1434 | 21.46 | 5604.1 | 2962.7 | 2839.9 | 4224.3 | 1219.1 | 0.68396 | 6.07
2024-12-10 | 1:29 | Data | 0 | 32.15 | 30.388 | 196.173 | 7.64 | 184.684 | 2210.77 | 25.76 | 42.838 | 6.37 | 1.372 | 4.714 | 8621.63 | 2.275 | 98.1 | 77.5 | 1437 | 21.46 | 5604.1 | 2948.6 | 2865.4 | 4231.3 | 1219.1 | 0.67959 | 6.083
2024-12-10 | 1:29 | Data | 0 | 32.467 | 30.415 | 196.173 | 7.64 | 184.639 | 2211.68 | 25.76 | 42.838 | 6.37 | 1.375 | 4.749 | 8635.19 | 2.079 | 98.1 | 77.6 | 1437 | 21.46 | 5612.9 | 2954.4 | 2886.3 | 4245.4 | 1219.1 | 0.6801 | 6.124
2024-12-10 | 1:29 | Data | 0 | 32.278 | 30.388 | 196.173 | 7.64 | 184.684 | 2210.77 | 25.76 | 43.019 | 6.37 | 1.365 | 4.708 | 8648.76 | 1.958 | 98.1 | 77.5 | 1437 | 21.46 | 5621.7 | 2969.5 | 2890.3 | 4258.3 | 1219.1 | 0.68126 | 6.074
2024-12-10 | 1:29 | Data | 0 | 32.278 | 30.307 | 196.219 | 7.64 | 184.729 | 2213.49 | 25.76 | 42.929 | 6.37 | 1.372 | 4.73 | 8621.63 | 2.268 | 98.1 | 77.5 | 1439 | 21.46 | 5604.1 | 2975.8 | 2852.8 | 4236.8 | 1219.1 | 0.68522 | 6.102
2024-12-10 | 1:29 | Data | 0 | 32.879 | 30.691 | 196.173 | 7.63 | 184.774 | 2214.39 | 25.76 | 42.929 | 6.37 | 1.378 | 4.719 | 8662.33 | 2.106 | 98.1 | 77.4 | 1439 | 21.46 | 5630.5 | 2954.1 | 2861.6 | 4227.7 | 1219.1 | 0.68172 | 6.099
2024-12-10 | 1:29 | Data | 0 | 32.683 | 30.644 | 196.219 | 7.64 | 184.684 | 2214.39 | 25.76 | 42.929 | 6.36 | 1.372 | 4.693 | 8662.33 | 2.275 | 98.1 | 77.4 | 1439 | 21.46 | 5630.5 | 2961.5 | 2882.8 | 4248.8 | 1219.1 | 0.68035 | 6.064
2024-12-10 | 1:29 | Data | 0 | 32.379 | 30.415 | 196.219 | 7.63 | 184.774 | 2216.2 | 25.77 | 42.929 | 6.37 | 1.371 | 4.68 | 8657.8 | 1.87 | 98.1 | 77.3 | 1441 | 21.46 | 5627.6 | 2957 | 2873.7 | 4233.8 | 1219.2 | 0.6804 | 6.052
2024-12-10 | 1:29 | Data | 0 | 32.339 | 30.374 | 196.083 | 7.63 | 184.684 | 2218.91 | 25.75 | 42.838 | 6.37 | 1.372 | 4.719 | 8671.37 | 1.965 | 98.1 | 77.5 | 1442 | 21.46 | 5636.4 | 2957 | 2879.9 | 4239.7 | 1219.2 | 0.68208 | 6.092
2024-12-10 | 1:29 | Data | 0 | 32.339 | 30.617 | 196.264 | 7.64 | 184.729 | 2215.29 | 25.76 | 42.929 | 6.37 | 1.382 | 4.703 | 8703.03 | 2.127 | 98.1 | 77.3 | 1441 | 21.42 | 5657 | 2957.8 | 2916.6 | 4269.9 | 1219.2 | 0.67805 | 6.084
2024-12-10 | 1:29 | Data | 0 | 32.467 | 30.408 | 196.128 | 7.64 | 184.593 | 2217.1 | 25.76 | 42.838 | 6.37 | 1.382 | 4.704 | 8698.5 | 2.079 | 98.1 | 77.3 | 1441 | 21.42 | 5654 | 2965.3 | 2904.4 | 4261.5 | 1219.2 | 0.67851 | 6.086
2024-12-10 | 1:29 | Data | 0 | 32.548 | 30.415 | 196.173 | 7.64 | 184.774 | 2216.2 | 25.76 | 43.019 | 6.37 | 1.379 | 4.722 | 8716.59 | 2.106 | 98.1 | 77.4 | 1441 | 21.46 | 5665.8 | 2955.7 | 2869.7 | 4235.6 | 1219.2 | 0.68094 | 6.102
2024-12-10 | 1:29 | Data | 0 | 32.777 | 30.205 | 196.219 | 7.63 | 184.729 | 2217.1 | 25.77 | 43.019 | 6.37 | 1.377 | 4.719 | 8730.16 | 2.1 | 98.1 | 77.4 | 1441 | 21.51 | 5674.6 | 2965.4 | 2887.8 | 4249 | 1219.2 | 0.68137 | 6.096
2024-12-10 | 1:30 | Data | 0 | 32.271 | 30.732 | 195.992 | 7.63 | 184.639 | 2216.2 | 25.76 | 42.929 | 6.37 | 1.371 | 4.692 | 8721.11 | 1.917 | 98.1 | 77.4 | 1441 | 21.46 | 5668.7 | 2954 | 2899.6 | 4256.1 | 1219.2 | 0.67706 | 6.064
2024-12-10 | 1:30 | Data | 0 | 32.892 | 30.739 | 196.264 | 7.64 | 184.684 | 2215.29 | 25.76 | 42.929 | 6.37 | 1.377 | 4.709 | 8693.98 | 2.032 | 98.1 | 77.4 | 1441 | 21.46 | 5651.1 | 2974.7 | 2886 | 4260.2 | 1219.2 | 0.68052 | 6.086
2024-12-10 | 1:30 | Data | 0 | 32.312 | 30.361 | 195.992 | 7.63 | 184.684 | 2216.2 | 25.76 | 42.929 | 6.37 | 1.362 | 4.752 | 8707.55 | 1.965 | 98.1 | 77.7 | 1441 | 21.46 | 5659.9 | 2986.2 | 2894.7 | 4274.4 | 1219.2 | 0.68144 | 6.114
2024-12-10 | 1:30 | Data | 0 | 32.494 | 30.59 | 196.173 | 7.64 | 184.593 | 2215.29 | 25.77 | 42.929 | 6.36 | 1.369 | 4.725 | 8707.55 | 1.965 | 98.1 | 77.5 | 1440 | 21.46 | 5659.9 | 2980.8 | 2880.5 | 4255.4 | 1219.2 | 0.68374 | 6.095
2024-12-10 | 1:30 | Data | 0 | 32.44 | 30.198 | 196.173 | 7.64 | 184.774 | 2218.91 | 25.77 | 42.929 | 6.37 | 1.373 | 4.701 | 8721.11 | 2.235 | 98.1 | 77.4 | 1442 | 21.46 | 5668.7 | 2968.5 | 2888.3 | 4259.2 | 1219.2 | 0.67948 | 6.073
2024-12-10 | 1:30 | Data | 0 | 32.386 | 30.361 | 196.219 | 7.64 | 184.684 | 2222.52 | 25.76 | 42.838 | 6.37 | 1.378 | 4.711 | 8716.59 | 2.086 | 98.1 | 77.4 | 1445 | 21.42 | 5665.8 | 2963.7 | 2869.7 | 4240.9 | 1219.2 | 0.68181 | 6.089
2024-12-10 | 1:30 | Data | 0 | 32.696 | 30.415 | 196.173 | 7.63 | 184.729 | 2222.52 | 25.76 | 42.929 | 6.37 | 1.375 | 4.699 | 8730.16 | 2.106 | 98.1 | 77.4 | 1445 | 21.51 | 5674.6 | 2969.4 | 2865.5 | 4240.4 | 1219.2 | 0.68437 | 6.073
2024-12-10 | 1:30 | Data | 0 | 32.44 | 30.415 | 196.128 | 7.64 | 184.639 | 2220.72 | 25.76 | 42.929 | 6.37 | 1.372 | 4.702 | 8752.77 | 2.241 | 98.1 | 77.4 | 1442 | 21.42 | 5689.3 | 2966.6 | 2888.9 | 4256.9 | 1219.2 | 0.67936 | 6.074
2024-12-10 | 1:30 | Data | 0 | 32.69 | 30.563 | 196.219 | 7.64 | 184.684 | 2222.52 | 25.76 | 42.929 | 6.37 | 1.371 | 4.718 | 8788.95 | 1.985 | 98.1 | 77.5 | 1444 | 21.51 | 5712.8 | 2973.4 | 2896.5 | 4260.6 | 1219.2 | 0.6825 | 6.089
2024-12-10 | 1:30 | Data | 0 | 32.494 | 30.401 | 196.173 | 7.63 | 184.729 | 2222.52 | 25.76 | 42.838 | 6.37 | 1.364 | 4.716 | 8788.95 | 2.093 | 98.1 | 77.6 | 1445 | 21.42 | 5712.8 | 2979.4 | 2910.7 | 4277.1 | 1219.2 | 0.68149 | 6.08
2024-12-10 | 1:30 | Data | 0 | 32.487 | 30.421 | 196.173 | 7.64 | 184.593 | 2218.91 | 25.75 | 42.838 | 6.37 | 1.366 | 4.725 | 8797.99 | 2.255 | 98.1 | 77.6 | 1442 | 21.46 | 5718.7 | 2977.9 | 2919.7 | 4282.1 | 1219.2 | 0.67773 | 6.092
2024-12-10 | 1:30 | Data | 0 | 32.271 | 30.185 | 196.128 | 7.63 | 184.684 | 2217.1 | 25.77 | 43.109 | 6.37 | 1.372 | 4.709 | 8775.38 | 2.187 | 98.1 | 77.4 | 1441 | 21.55 | 5704 | 2956.3 | 2935.1 | 4281.4 | 1219.2 | 0.67232 | 6.081
2024-12-10 | 1:30 | Data | 0 | 32.683 | 30.59 | 196.173 | 7.63 | 184.684 | 2217.1 | 25.76 | 42.929 | 6.37 | 1.369 | 4.68 | 8748.25 | 2.187 | 98.1 | 77.4 | 1442 | 21.51 | 5686.4 | 2976.9 | 2904.6 | 4257.5 | 1219.2 | 0.67966 | 6.047
2024-12-10 | 1:30 | Data | 0 | 32.21 | 30.59 | 196.219 | 7.64 | 184.729 | 2213.49 | 25.76 | 43.019 | 6.37 | 1.367 | 4.719 | 8743.73 | 2.221 | 98.1 | 77.5 | 1439 | 21.46 | 5683.4 | 2976.8 | 2905.1 | 4274.6 | 1219.2 | 0.67872 | 6.085
2024-12-10 | 1:30 | Data | 0 | 32.879 | 30.469 | 196.309 | 7.63 | 184.729 | 2214.39 | 25.76 | 42.929 | 6.37 | 1.363 | 4.731 | 8739.2 | 2.16 | 98.1 | 77.6 | 1439 | 21.42 | 5680.5 | 2981.2 | 2887.2 | 4270.1 | 1219.2 | 0.68149 | 6.094
2024-12-10 | 1:30 | Data | 0 | 32.332 | 30.415 | 196.219 | 7.63 | 184.684 | 2214.39 | 25.76 | 42.838 | 6.37 | 1.367 | 4.722 | 8730.16 | 1.992 | 98.1 | 77.6 | 1440 | 21.42 | 5674.6 | 2957.5 | 2885.1 | 4245 | 1219.2 | 0.68058 | 6.089
2024-12-10 | 1:30 | Data | 0 | 32.379 | 30.408 | 196.128 | 7.64 | 184.639 | 2211.68 | 25.77 | 42.929 | 6.36 | 1.374 | 4.711 | 8716.59 | 2.073 | 98.1 | 77.4 | 1438 | 21.46 | 5665.8 | 2955.5 | 2864.2 | 4227.1 | 1219.2 | 0.68189 | 6.085
2024-12-10 | 1:30 | Data | 0 | 32.717 | 30.415 | 196.083 | 7.64 | 184.639 | 2216.2 | 25.75 | 42.929 | 6.37 | 1.375 | 4.694 | 8743.73 | 2.086 | 98.1 | 77.3 | 1441 | 21.51 | 5683.4 | 2958.3 | 2892.9 | 4254.3 | 1219.2 | 0.67843 | 6.069
2024-12-10 | 1:31 | Data | 0 | 32.501 | 30.421 | 196.264 | 7.63 | 184.729 | 2217.1 | 25.76 | 42.929 | 6.37 | 1.361 | 4.692 | 8730.16 | 2.066 | 98.1 | 77.5 | 1441 | 21.42 | 5674.6 | 2963 | 2872.8 | 4240.6 | 1219.2 | 0.68213 | 6.053
2024-12-10 | 1:31 | Data | 0 | 32.494 | 30.415 | 196.173 | 7.63 | 184.729 | 2217.1 | 25.76 | 42.929 | 6.37 | 1.366 | 4.701 | 8721.11 | 2.079 | 98.1 | 77.5 | 1441 | 21.46 | 5668.7 | 2982.2 | 2909.8 | 4286.4 | 1219.2 | 0.67799 | 6.066
2024-12-10 | 1:31 | Data | 0 | 32.71 | 30.543 | 196.264 | 7.64 | 184.774 | 2224.33 | 25.76 | 42.929 | 6.37 | 1.383 | 4.677 | 8703.03 | 2.133 | 98.1 | 77.2 | 1446 | 21.46 | 5657 | 2990.3 | 2887.5 | 4267.8 | 1219.2 | 0.679 | 6.06
2024-12-10 | 1:31 | Data | 0 | 32.804 | 30.225 | 196.309 | 7.63 | 184.819 | 2217.1 | 25.77 | 42.929 | 6.37 | 1.383 | 4.692 | 8716.59 | 2.187 | 98.1 | 77.2 | 1441 | 21.46 | 5665.8 | 2980.1 | 2915.5 | 4282.4 | 1219.2 | 0.67823 | 6.074
2024-12-10 | 1:31 | Data | 0 | 32.521 | 30.198 | 196.219 | 7.64 | 184.774 | 2216.2 | 25.76 | 42.929 | 6.37 | 1.378 | 4.707 | 8716.59 | 2.14 | 98.1 | 77.3 | 1441 | 21.46 | 5665.8 | 2968.3 | 2904.1 | 4271 | 1219.2 | 0.67885 | 6.085
2024-12-10 | 1:31 | Data | 0 | 32.494 | 30.624 | 196.309 | 7.63 | 184.774 | 2217.1 | 25.77 | 42.929 | 6.37 | 1.377 | 4.704 | 8712.07 | 2.12 | 98.1 | 77.4 | 1441 | 21.46 | 5662.8 | 2996.7 | 2890.3 | 4283 | 1219.2 | 0.68307 | 6.08
2024-12-10 | 1:31 | Data | 0 | 32.696 | 30.421 | 196.309 | 7.64 | 184.819 | 2216.2 | 25.76 | 42.929 | 6.37 | 1.379 | 4.675 | 8698.5 | 2.289 | 98.1 | 77.2 | 1441 | 21.46 | 5654 | 2982.3 | 2889.2 | 4263.7 | 1219.2 | 0.68238 | 6.055
2024-12-10 | 1:31 | Data | 0 | 32.339 | 30.192 | 196.083 | 7.64 | 184.729 | 2216.2 | 25.76 | 43.019 | 6.37 | 1.376 | 4.68 | 8671.37 | 2.093 | 98.1 | 77.3 | 1441 | 21.46 | 5636.4 | 2996.6 | 2886.2 | 4272.7 | 1219.2 | 0.68398 | 6.055
2024-12-10 | 1:31 | Data | 0 | 32.663 | 30.442 | 196.219 | 7.64 | 184.729 | 2214.39 | 25.76 | 42.929 | 6.37 | 1.375 | 4.672 | 8657.8 | 2.079 | 98.1 | 77.3 | 1439 | 21.46 | 5627.6 | 2976.4 | 2878.3 | 4262.3 | 1219.2 | 0.68372 | 6.045
2024-12-10 | 1:31 | Data | 0 | 32.71 | 30.435 | 196.219 | 7.64 | 184.639 | 2213.49 | 25.76 | 42.929 | 6.37 | 1.387 | 4.672 | 8648.76 | 2.1 | 98.1 | 77.1 | 1439 | 21.46 | 5621.7 | 2994.1 | 2891.3 | 4279.2 | 1219.2 | 0.68039 | 6.058
2024-12-10 | 1:31 | Data | 0 | 32.595 | 30.415 | 196.219 | 7.64 | 184.774 | 2213.49 | 25.76 | 42.929 | 6.37 | 1.37 | 4.717 | 8648.76 | 2.275 | 98.1 | 77.5 | 1439 | 21.46 | 5621.7 | 2994.4 | 2905.9 | 4288.4 | 1219.2 | 0.68079 | 6.087
2024-12-10 | 1:31 | Data | 0 | 32.494 | 30.415 | 196.128 | 7.63 | 184.729 | 2213.49 | 25.77 | 42.838 | 6.36 | 1.367 | 4.707 | 8680.41 | 2.086 | 98.1 | 77.5 | 1439 | 21.42 | 5642.3 | 2986 | 2911.3 | 4285.7 | 1219.2 | 0.67938 | 6.075
2024-12-10 | 1:31 | Data | 0 | 32.717 | 30.482 | 196.264 | 7.64 | 184.729 | 2213.49 | 25.77 | 42.929 | 6.37 | 1.385 | 4.666 | 8648.76 | 2.174 | 98.1 | 77.1 | 1439 | 21.46 | 5621.7 | 2989.5 | 2910.2 | 4286.9 | 1219.3 | 0.68079 | 6.051
2024-12-10 | 1:31 | Data | 0 | 32.656 | 30.644 | 196.264 | 7.63 | 184.639 | 2216.2 | 25.76 | 42.929 | 6.36 | 1.383 | 4.683 | 8657.8 | 2.079 | 98.1 | 77.2 | 1441 | 21.46 | 5627.6 | 2999.2 | 2910.9 | 4298.2 | 1219.3 | 0.68028 | 6.065
2024-12-10 | 1:31 | Data | 0 | 32.831 | 30.192 | 196.219 | 7.64 | 184.684 | 2216.2 | 25.76 | 42.929 | 6.37 | 1.367 | 4.714 | 8680.41 | 2.113 | 98.1 | 77.5 | 1441 | 21.46 | 5642.3 | 3008.5 | 2895.1 | 4288.3 | 1219.3 | 0.68327 | 6.081
2024-12-10 | 1:31 | Data | 0 | 32.325 | 30.212 | 196.128 | 7.63 | 184.729 | 2217.1 | 25.76 | 43.019 | 6.37 | 1.377 | 4.703 | 8671.37 | 1.998 | 98.1 | 77.4 | 1441 | 21.46 | 5636.4 | 2981.7 | 2894.9 | 4276.9 | 1219.3 | 0.67965 | 6.08
2024-12-10 | 1:31 | Data | 0 | 32.271 | 30.361 | 196.128 | 7.63 | 184.684 | 2218.91 | 25.76 | 42.838 | 6.36 | 1.377 | 4.714 | 8657.8 | 1.965 | 98.1 | 77.4 | 1442 | 21.46 | 5627.6 | 3022.6 | 2922 | 4314.7 | 1219.3 | 0.68388 | 6.089
2024-12-10 | 1:31 | Data | 0 | 32.548 | 30.577 | 196.219 | 7.64 | 184.639 | 2218.91 | 25.76 | 43.561 | 6.37 | 1.379 | 4.726 | 8662.33 | 2.012 | 98 | 77.4 | 1442 | 21.74 | 5630.5 | 2986.3 | 2918.7 | 4294.3 | 1219.3 | 0.67783 | 6.106
2024-12-10 | 1:32 | Data | 0 | 32.285 | 30.388 | 196.309 | 7.64 | 184.684 | 2218.91 | 25.76 | 42.838 | 6.37 | 1.376 | 4.711 | 8657.8 | 2.073 | 98.1 | 77.4 | 1442 | 21.46 | 5627.6 | 2990.7 | 2923.3 | 4297.4 | 1219.3 | 0.67903 | 6.086
2024-12-10 | 1:32 | Data | 0 | 32.818 | 30.489 | 196.264 | 7.64 | 184.865 | 2218 | 25.76 | 42.929 | 6.37 | 1.363 | 4.703 | 8662.33 | 2.039 | 98.1 | 77.5 | 1442 | 21.46 | 5630.5 | 3003.1 | 2932.1 | 4312.8 | 1219.3 | 0.67964 | 6.067
2024-12-10 | 1:32 | Data | 0 | 32.271 | 30.198 | 196.128 | 7.63 | 184.684 | 2218.91 | 25.76 | 42.929 | 6.37 | 1.366 | 4.707 | 8644.24 | 2.052 | 98.1 | 77.5 | 1442 | 21.51 | 5618.8 | 2999.5 | 2948.8 | 4323.9 | 1219.3 | 0.67677 | 6.073
2024-12-10 | 1:32 | Data | 0 | 32.514 | 30.678 | 196.399 | 7.63 | 184.865 | 2218 | 25.76 | 42.929 | 6.37 | 1.366 | 4.723 | 8635.19 | 1.992 | 98.1 | 77.6 | 1442 | 21.51 | 5612.9 | 3007.9 | 2947 | 4326.4 | 1219.3 | 0.67574 | 6.089
2024-12-10 | 1:32 | Data | 0 | 32.696 | 30.651 | 196.264 | 7.63 | 184.729 | 2218.91 | 25.77 | 42.929 | 6.37 | 1.365 | 4.729 | 8644.24 | 2.073 | 98.1 | 77.6 | 1442 | 21.46 | 5618.8 | 2999.9 | 2943.6 | 4319.2 | 1219.3 | 0.67684 | 6.094
2024-12-10 | 1:32 | Data | 0 | 32.818 | 30.246 | 196.399 | 7.64 | 184.729 | 2218.91 | 25.77 | 42.929 | 6.37 | 1.374 | 4.731 | 8626.15 | 1.971 | 98.1 | 77.5 | 1442 | 21.42 | 5607 | 2993 | 2932.9 | 4305.9 | 1219.3 | 0.67839 | 6.104
2024-12-10 | 1:32 | Data | 0 | 32.933 | 30.651 | 196.309 | 7.64 | 184.774 | 2218.91 | 25.77 | 42.929 | 6.37 | 1.373 | 4.69 | 8648.76 | 2.174 | 98.1 | 77.4 | 1442 | 21.46 | 5621.7 | 2992.4 | 2905.5 | 4293 | 1219.3 | 0.68045 | 6.063
2024-12-10 | 1:32 | Data | 0 | 32.494 | 30.475 | 196.173 | 7.64 | 184.684 | 2218.91 | 25.76 | 42.929 | 6.37 | 1.367 | 4.663 | 8635.19 | 2.079 | 98.1 | 77.3 | 1442 | 21.46 | 5612.9 | 2982.3 | 2912.4 | 4288.4 | 1219.3 | 0.67898 | 6.03
2024-12-10 | 1:32 | Data | 0 | 32.636 | 30.192 | 196.264 | 7.64 | 184.865 | 2223.43 | 25.76 | 42.568 | 6.37 | 1.366 | 4.723 | 8648.76 | 2.086 | 98.1 | 77.6 | 1445 | 21.28 | 5621.7 | 2987.4 | 2901.7 | 4276.1 | 1219.3 | 0.68139 | 6.088
2024-12-10 | 1:32 | Data | 0 | 32.318 | 30.415 | 195.992 | 7.63 | 184.593 | 2223.43 | 25.76 | 42.838 | 6.36 | 1.373 | 4.741 | 8693.98 | 2.032 | 98.1 | 77.5 | 1445 | 21.42 | 5651.1 | 3004.1 | 2901.6 | 4296.6 | 1219.3 | 0.68157 | 6.114
2024-12-10 | 1:32 | Data | 0 | 32.548 | 30.59 | 196.309 | 7.64 | 184.729 | 2223.43 | 25.78 | 42.929 | 6.37 | 1.382 | 4.752 | 8703.03 | 2.106 | 98.1 | 77.5 | 1445 | 21.46 | 5657 | 2919.6 | 2888.4 | 4217.5 | 1219.3 | 0.67585 | 6.134
2024-12-10 | 1:32 | Data | 0 | 32.777 | 30.246 | 196.354 | 7.63 | 184.774 | 2218 | 25.77 | 42.929 | 6.37 | 1.378 | 4.706 | 8693.98 | 2.005 | 98.1 | 77.3 | 1442 | 21.46 | 5651.1 | 2915.1 | 2888.7 | 4211.8 | 1219.3 | 0.67525 | 6.084
2024-12-10 | 1:32 | Data | 0 | 32.71 | 30.428 | 196.128 | 7.64 | 184.593 | 2226.14 | 25.76 | 42.929 | 6.36 | 1.367 | 4.692 | 8693.98 | 2.079 | 98.1 | 77.4 | 1448 | 21.51 | 5651.1 | 2913.6 | 2877.1 | 4207.4 | 1219.3 | 0.67657 | 6.06
2024-12-10 | 1:32 | Data | 0 | 32.487 | 30.3 | 196.128 | 7.63 | 184.684 | 2222.52 | 25.76 | 42.838 | 6.37 | 1.364 | 4.701 | 8662.33 | 2.086 | 98.1 | 77.5 | 1444 | 21.42 | 5630.5 | 2922.6 | 2876.3 | 4210.9 | 1219.3 | 0.67844 | 6.065
2024-12-10 | 1:32 | Data | 0 | 32.494 | 30.415 | 196.128 | 7.64 | 184.593 | 2222.52 | 25.77 | 42.929 | 6.37 | 1.365 | 4.685 | 8657.8 | 2.079 | 98.1 | 77.5 | 1445 | 21.46 | 5627.6 | 2919.9 | 2887.2 | 4216.5 | 1219.3 | 0.67473 | 6.05
2024-12-10 | 1:32 | Data | 0 | 32.501 | 30.415 | 196.128 | 7.64 | 184.684 | 2223.43 | 25.76 | 43.019 | 6.37 | 1.376 | 4.697 | 8680.41 | 1.965 | 98.1 | 77.3 | 1445 | 21.46 | 5642.3 | 2934.3 | 2885.1 | 4223.5 | 1219.3 | 0.6778 | 6.073
2024-12-10 | 1:32 | Data | 0 | 32.318 | 30.144 | 196.083 | 7.63 | 184.593 | 2224.33 | 25.76 | 42.929 | 6.37 | 1.375 | 4.714 | 8662.33 | 2.127 | 98.1 | 77.4 | 1446 | 21.46 | 5630.5 | 2929.8 | 2879.2 | 4206.2 | 1219.3 | 0.67885 | 6.088
2024-12-10 | 1:32 | Data | 0 | 32.163 | 30.084 | 196.083 | 7.64 | 184.593 | 2225.23 | 25.76 | 42.838 | 6.36 | 1.379 | 4.723 | 8662.33 | 2.073 | 98.1 | 77.4 | 1446 | 21.42 | 5630.5 | 2934.5 | 2893 | 4227.2 | 1219.3 | 0.67629 | 6.102
2024-12-10 | 1:33 | Data | 0 | 32.541 | 30.198 | 196.264 | 7.63 | 184.729 | 2216.2 | 25.77 | 42.929 | 6.37 | 1.381 | 4.721 | 8680.41 | 2.127 | 98.1 | 77.4 | 1441 | 21.46 | 5642.3 | 2975.7 | 2916.2 | 4280.7 | 1219.3 | 0.67925 | 6.101
2024-12-10 | 1:33 | Data | 0 | 32.271 | 30.293 | 196.173 | 7.63 | 184.684 | 2218.91 | 25.76 | 42.929 | 6.36 | 1.376 | 4.714 | 8671.37 | 2.1 | 98.1 | 77.4 | 1442 | 21.46 | 5636.4 | 2983.4 | 2898.9 | 4273.1 | 1219.3 | 0.68135 | 6.09
2024-12-10 | 1:33 | Data | 0 | 32.379 | 30.583 | 196.128 | 7.63 | 184.684 | 2218.91 | 25.75 | 42.929 | 6.37 | 1.374 | 4.679 | 8666.85 | 2.052 | 98.1 | 77.3 | 1442 | 21.46 | 5633.5 | 2972.9 | 2891.9 | 4262.7 | 1219.3 | 0.67989 | 6.053
2024-12-10 | 1:33 | Data | 0 | 32.494 | 30.192 | 196.173 | 7.64 | 184.639 | 2217.1 | 25.77 | 42.929 | 6.37 | 1.383 | 4.717 | 8693.98 | 2.282 | 98.1 | 77.3 | 1441 | 21.46 | 5651.1 | 2987.6 | 2916.5 | 4286.2 | 1219.3 | 0.68191 | 6.099
2024-12-10 | 1:33 | Data | 0 | 32.595 | 30.509 | 196.128 | 7.63 | 184.684 | 2216.2 | 25.76 | 42.838 | 6.37 | 1.375 | 4.715 | 8680.41 | 2.322 | 98.1 | 77.4 | 1441 | 21.42 | 5642.3 | 2954.3 | 2899 | 4258.2 | 1219.3 | 0.67682 | 6.09
2024-12-10 | 1:33 | Data | 0 | 32.487 | 30.212 | 196.083 | 7.63 | 184.593 | 2216.2 | 25.76 | 42.929 | 6.37 | 1.375 | 4.717 | 8693.98 | 2.106 | 98.1 | 77.4 | 1441 | 21.46 | 5651.1 | 2966.5 | 2898.9 | 4262.7 | 1219.3 | 0.67821 | 6.092
2024-12-10 | 1:33 | Data | 0 | 32.264 | 30.408 | 196.083 | 7.64 | 184.503 | 2217.1 | 25.76 | 42.929 | 6.37 | 1.379 | 4.7 | 8703.03 | 2.032 | 98.1 | 77.3 | 1441 | 21.46 | 5657 | 2964.5 | 2905.3 | 4265.7 | 1219.3 | 0.67699 | 6.079
2024-12-10 | 1:33 | Data | 0 | 32.696 | 30.415 | 196.083 | 7.64 | 184.684 | 2216.2 | 25.76 | 43.019 | 6.36 | 1.373 | 4.702 | 8693.98 | 2.181 | 98.1 | 77.4 | 1441 | 21.46 | 5651.1 | 2962 | 2901.4 | 4262.1 | 1219.3 | 0.67804 | 6.075
2024-12-10 | 1:33 | Data | 0 | 32.156 | 30.225 | 196.128 | 7.63 | 184.593 | 2218.91 | 25.76 | 42.929 | 6.37 | 1.377 | 4.706 | 8703.03 | 2.14 | 98.1 | 77.3 | 1442 | 21.46 | 5657 | 2967 | 2888.1 | 4254 | 1219.3 | 0.68101 | 6.084
2024-12-10 | 1:33 | Data | 0 | 32.494 | 30.442 | 196.083 | 7.64 | 184.639 | 2218.91 | 25.76 | 42.929 | 6.37 | 1.387 | 4.702 | 8693.98 | 1.978 | 98.1 | 77.2 | 1442 | 21.42 | 5651.1 | 2963.2 | 2899.5 | 4260.9 | 1219.3 | 0.67813 | 6.089
2024-12-10 | 1:33 | Data | 0 | 32.271 | 30.185 | 196.128 | 7.64 | 184.684 | 2218.91 | 25.75 | 42.929 | 6.37 | 1.384 | 4.7 | 8671.37 | 2.079 | 98.1 | 77.3 | 1442 | 21.46 | 5636.4 | 2960.2 | 2895.4 | 4256.5 | 1219.3 | 0.67709 | 6.083
2024-12-10 | 1:33 | Data | 0 | 32.21 | 30.3 | 196.173 | 7.64 | 184.593 | 2222.52 | 25.74 | 42.929 | 6.37 | 1.377 | 4.686 | 8680.41 | 2.066 | 98.1 | 77.3 | 1445 | 21.42 | 5642.3 | 2981.4 | 2875.3 | 4262.8 | 1219.3 | 0.68308 | 6.063
2024-12-10 | 1:33 | Data | 0 | 32.298 | 30.185 | 196.083 | 7.64 | 184.639 | 2221.62 | 25.76 | 42.929 | 6.36 | 1.361 | 4.709 | 8689.46 | 2.086 | 98.1 | 77.6 | 1445 | 21.46 | 5648.1 | 2991.8 | 2905.2 | 4284.6 | 1219.4 | 0.67956 | 6.07
2024-12-10 | 1:33 | Data | 0 | 32.15 | 30.185 | 195.992 | 7.64 | 184.548 | 2222.52 | 25.75 | 42.929 | 6.37 | 1.376 | 4.708 | 8693.98 | 1.904 | 98.1 | 77.4 | 1445 | 21.46 | 5651.1 | 2986.8 | 2908.5 | 4286.6 | 1219.4 | 0.67958 | 6.084
2024-12-10 | 1:33 | Data | 0 | 32.575 | 30.442 | 196.219 | 7.64 | 184.684 | 2222.52 | 25.75 | 43.019 | 6.37 | 1.374 | 4.725 | 8689.46 | 2.329 | 98.1 | 77.5 | 1445 | 21.46 | 5648.1 | 2973.4 | 2929.5 | 4291.1 | 1219.4 | 0.67462 | 6.098
2024-12-10 | 1:33 | Data | 0 | 32.123 | 30.185 | 196.083 | 7.64 | 184.684 | 2216.2 | 25.77 | 42.929 | 6.37 | 1.373 | 4.7 | 8707.55 | 1.857 | 98.1 | 77.4 | 1441 | 21.46 | 5659.9 | 2964.9 | 2901.5 | 4265.8 | 1219.4 | 0.67672 | 6.072
2024-12-10 | 1:33 | Data | 0 | 32.264 | 30.185 | 196.128 | 7.64 | 184.593 | 2217.1 | 25.75 | 42.838 | 6.37 | 1.367 | 4.697 | 8680.41 | 2.079 | 98.1 | 77.4 | 1441 | 21.46 | 5642.3 | 2978.3 | 2943.6 | 4311.3 | 1219.4 | 0.67674 | 6.064
2024-12-10 | 1:34 | Data | 0 | 32.467 | 30.388 | 196.128 | 7.64 | 184.593 | 2217.1 | 25.75 | 42.929 | 6.37 | 1.373 | 4.73 | 8671.37 | 2.181 | 98.1 | 77.5 | 1441 | 21.46 | 5636.4 | 2974.1 | 2950.6 | 4302.8 | 1219.4 | 0.67513 | 6.102
2024-12-10 | 1:34 | Data | 0 | 32.102 | 30.185 | 195.947 | 7.63 | 184.593 | 2213.49 | 25.76 | 42.658 | 6.36 | 1.369 | 4.727 | 8648.76 | 1.877 | 98.1 | 77.5 | 1439 | 21.33 | 5621.7 | 2960.2 | 2906.7 | 4262.5 | 1219.4 | 0.6775 | 6.097
2024-12-10 | 1:34 | Data | 0 | 32.312 | 30.354 | 195.992 | 7.64 | 184.548 | 2210.77 | 25.76 | 42.658 | 6.37 | 1.374 | 4.7 | 8693.98 | 2.093 | 98.1 | 77.4 | 1438 | 21.33 | 5651.1 | 2968.4 | 2888.4 | 4262.3 | 1219.4 | 0.67863 | 6.074
2024-12-10 | 1:34 | Data | 0 | 32.494 | 30.198 | 195.947 | 7.64 | 184.548 | 2217.1 | 25.76 | 42.748 | 6.36 | 1.377 | 4.7 | 8707.55 | 2.14 | 98.1 | 77.3 | 1441 | 21.33 | 5659.9 | 2951 | 2877.6 | 4236.1 | 1219.4 | 0.67955 | 6.076
2024-12-10 | 1:34 | Data | 0 | 32.264 | 30.246 | 195.992 | 7.63 | 184.593 | 2214.39 | 25.75 | 42.658 | 6.37 | 1.378 | 4.691 | 8693.98 | 1.992 | 98.1 | 77.3 | 1439 | 21.28 | 5651.1 | 2965.5 | 2876 | 4242 | 1219.4 | 0.6819 | 6.07
2024-12-10 | 1:34 | Data | 0 | 32.264 | 30.185 | 195.992 | 7.64 | 184.503 | 2206.25 | 25.75 | 42.658 | 6.37 | 1.37 | 4.673 | 8698.5 | 2.079 | 98.1 | 77.3 | 1434 | 21.28 | 5654 | 2962.7 | 2885.2 | 4247.9 | 1219.4 | 0.68147 | 6.045
2024-12-10 | 1:34 | Data | 0 | 32.379 | 30.415 | 195.992 | 7.63 | 184.593 | 2214.39 | 25.77 | 42.658 | 6.36 | 1.367 | 4.722 | 8689.46 | 2.059 | 98.1 | 77.6 | 1439 | 21.33 | 5648.1 | 2970 | 2882.6 | 4252.4 | 1219.4 | 0.68187 | 6.088
2024-12-10 | 1:34 | Data | 0 | 32.44 | 30.631 | 196.083 | 7.64 | 184.639 | 2210.77 | 25.75 | 42.748 | 6.37 | 1.377 | 4.709 | 8671.37 | 2.059 | 98.1 | 77.4 | 1437 | 21.37 | 5636.4 | 2953.7 | 2912.7 | 4268.3 | 1219.4 | 0.67418 | 6.085
2024-12-10 | 1:34 | Data | 0 | 32.264 | 30.286 | 196.128 | 7.64 | 184.593 | 2211.68 | 25.76 | 42.658 | 6.37 | 1.379 | 4.708 | 8680.41 | 2.052 | 98.1 | 77.4 | 1438 | 21.37 | 5642.3 | 2972.3 | 2918 | 4276.4 | 1219.4 | 0.67826 | 6.086
2024-12-10 | 1:34 | Data | 0 | 32.264 | 30.185 | 196.128 | 7.63 | 184.639 | 2211.68 | 25.75 | 42.658 | 6.37 | 1.378 | 4.733 | 8671.37 | 2.275 | 98.1 | 77.5 | 1438 | 21.33 | 5636.4 | 2959.8 | 2898.9 | 4255.4 | 1219.4 | 0.67781 | 6.11
2024-12-10 | 1:34 | Data | 0 | 32.663 | 30.529 | 196.173 | 7.63 | 184.729 | 2208.97 | 25.77 | 42.929 | 6.37 | 1.378 | 4.733 | 8662.33 | 2.133 | 98.1 | 77.4 | 1435 | 21.42 | 5630.5 | 2982.8 | 2916.5 | 4281.7 | 1219.4 | 0.67982 | 6.111
2024-12-10 | 1:34 | Data | 0 | 32.467 | 30.502 | 196.083 | 7.64 | 184.593 | 2206.25 | 25.76 | 42.748 | 6.36 | 1.377 | 4.736 | 8662.33 | 1.958 | 98.1 | 77.5 | 1433 | 21.33 | 5630.5 | 2967 | 2909.8 | 4270.3 | 1219.4 | 0.67797 | 6.113
2024-12-10 | 1:34 | Data | 0 | 32.717 | 30.327 | 195.992 | 7.64 | 184.684 | 2205.35 | 25.78 | 42.658 | 6.37 | 1.371 | 4.732 | 8671.37 | 2.133 | 98.1 | 77.6 | 1434 | 21.33 | 5636.4 | 2960.1 | 2912.8 | 4265.1 | 1219.4 | 0.67789 | 6.103
2024-12-10 | 1:34 | Data | 0 | 32.271 | 30.313 | 196.083 | 7.64 | 184.684 | 2208.06 | 25.76 | 42.748 | 6.36 | 1.369 | 4.721 | 8653.28 | 2.066 | 98.1 | 77.5 | 1435 | 21.33 | 5624.6 | 2950 | 2911.6 | 4263 | 1219.4 | 0.67481 | 6.091
2024-12-10 | 1:34 | Data | 0 | 32.264 | 30.388 | 196.083 | 7.63 | 184.548 | 2208.97 | 25.78 | 42.658 | 6.37 | 1.369 | 4.742 | 8662.33 | 2.079 | 98.1 | 77.6 | 1435 | 21.37 | 5630.5 | 2960.5 | 2895.9 | 4254.1 | 1219.4 | 0.68011 | 6.111
2024-12-10 | 1:34 | Data | 0 | 32.69 | 30.597 | 196.128 | 7.64 | 184.684 | 2208.06 | 25.76 | 42.568 | 6.36 | 1.365 | 4.726 | 8653.28 | 2.174 | 98.1 | 77.6 | 1435 | 21.33 | 5624.6 | 2970.1 | 2870.5 | 4245.9 | 1219.4 | 0.68277 | 6.091
2024-12-10 | 1:34 | Data | 0 | 32.433 | 30.3 | 195.992 | 7.63 | 184.593 | 2208.97 | 25.76 | 42.658 | 6.37 | 1.37 | 4.69 | 8644.24 | 2.181 | 98.1 | 77.4 | 1435 | 21.28 | 5618.8 | 2963.1 | 2886.4 | 4256.5 | 1219.4 | 0.67927 | 6.059
2024-12-10 | 1:34 | Data | 0 | 32.325 | 30.084 | 195.992 | 7.63 | 184.593 | 2208.06 | 25.78 | 42.929 | 6.36 | 1.374 | 4.703 | 8648.76 | 2.187 | 98.1 | 77.4 | 1435 | 21.46 | 5621.7 | 2973.8 | 2864.6 | 4241.3 | 1219.4 | 0.68394 | 6.077
2024-12-10 | 1:35 | Data | 0 | 32.379 | 30.185 | 196.083 | 7.64 | 184.593 | 2208.06 | 25.78 | 42.568 | 6.37 | 1.372 | 4.712 | 8648.76 | 2.086 | 98.1 | 77.5 | 1435 | 21.33 | 5621.7 | 2968.3 | 2857.4 | 4234.3 | 1219.4 | 0.68365 | 6.084
2024-12-10 | 1:35 | Data | 0 | 32.271 | 30.617 | 196.128 | 7.63 | 184.729 | 2210.77 | 25.76 | 42.658 | 6.37 | 1.369 | 4.69 | 8653.28 | 1.978 | 98.1 | 77.4 | 1438 | 21.33 | 5624.6 | 2963.4 | 2889.5 | 4254.6 | 1219.4 | 0.68036 | 6.06
2024-12-10 | 1:35 | Data | 0 | 32.663 | 30.469 | 196.173 | 7.64 | 184.819 | 2210.77 | 25.76 | 42.929 | 6.37 | 1.377 | 4.717 | 8662.33 | 2.248 | 98.1 | 77.4 | 1437 | 21.46 | 5630.5 | 2979.9 | 2875.6 | 4255.7 | 1219.4 | 0.68189 | 6.094
2024-12-10 | 1:35 | Data | 0 | 32.366 | 30.131 | 196.128 | 7.64 | 184.684 | 2210.77 | 25.76 | 42.838 | 6.36 | 1.38 | 4.731 | 8648.76 | 2.343 | 98.1 | 77.4 | 1437 | 21.42 | 5621.7 | 2971.6 | 2904.4 | 4274.3 | 1219.4 | 0.68084 | 6.111
2024-12-10 | 1:35 | Data | 0 | 32.271 | 30.232 | 195.992 | 7.63 | 184.548 | 2209.87 | 25.77 | 42.929 | 6.36 | 1.383 | 4.735 | 8644.24 | 1.877 | 98.1 | 77.4 | 1437 | 21.46 | 5618.8 | 2959.6 | 2877.3 | 4242.4 | 1219.4 | 0.68068 | 6.116
2024-12-10 | 1:35 | Data | 0 | 32.298 | 30.192 | 196.128 | 7.64 | 184.639 | 2217.1 | 25.77 | 42.838 | 6.37 | 1.378 | 4.722 | 8617.1 | 2.073 | 98.1 | 77.4 | 1441 | 21.42 | 5601.1 | 2960.4 | 2884.7 | 4251.5 | 1219.4 | 0.67971 | 6.102
2024-12-10 | 1:35 | Data | 0 | 32.048 | 30.388 | 196.128 | 7.64 | 184.639 | 2213.49 | 25.76 | 42.929 | 6.36 | 1.369 | 4.701 | 8594.49 | 1.971 | 98.1 | 77.5 | 1438 | 21.46 | 5586.4 | 2960.9 | 2884.8 | 4246.6 | 1219.4 | 0.67904 | 6.069
2024-12-10 | 1:35 | Data | 0 | 32.771 | 30.307 | 196.173 | 7.63 | 184.729 | 2216.2 | 25.76 | 42.929 | 6.36 | 1.369 | 4.689 | 8603.54 | 1.931 | 98.1 | 77.4 | 1441 | 21.46 | 5592.3 | 2947.7 | 2870.7 | 4229.9 | 1219.4 | 0.67859 | 6.059
2024-12-10 | 1:35 | Data | 0 | 32.602 | 30.415 | 196.128 | 7.64 | 184.593 | 2109.54 | 25.75 | 42.929 | 6.37 | 1.379 | 4.721 | 8594.49 | 2.086 | 98 | 77.4 | 1371 | 21.46 | 5586.4 | 2964.3 | 2901.9 | 4263.9 | 1219.4 | 0.67862 | 6.1
2024-12-10 | 1:35 | Data | 0 | 32.271 | 30.185 | 196.083 | 7.63 | 184.503 | 2218.91 | 25.76 | 43.019 | 6.37 | 1.385 | 4.711 | 8599.01 | 2.079 | 98.1 | 77.3 | 1442 | 21.46 | 5589.4 | 2958.1 | 2906.7 | 4264.5 | 1219.4 | 0.67734 | 6.096
2024-12-10 | 1:35 | Data | 0 | 32.204 | 30.401 | 196.128 | 7.63 | 184.593 | 2216.2 | 25.76 | 42.929 | 6.37 | 1.383 | 4.721 | 8219.15 | 2.073 | 98.1 | 77.4 | 1441 | 21.46 | 5342.4 | 2948.2 | 2869.5 | 4230.7 | 1219.4 | 0.67971 | 6.103
2024-12-10 | 1:35 | Data | 0 | 32.717 | 30.327 | 196.083 | 7.63 | 184.684 | 2216.2 | 25.76 | 42.929 | 6.36 | 1.374 | 4.707 | 8237.24 | 2.14 | 98.1 | 77.4 | 1441 | 21.42 | 5354.2 | 2960.4 | 2897 | 4246.7 | 1219.4 | 0.67615 | 6.081
2024-12-10 | 1:35 | Data | 0 | 32.426 | 30.239 | 195.947 | 7.64 | 184.503 | 2216.2 | 25.77 | 42.658 | 6.37 | 1.373 | 4.697 | 8630.67 | 2.181 | 98.1 | 77.4 | 1441 | 21.28 | 5609.9 | 2961.3 | 2880.5 | 4246.6 | 1219.5 | 0.67938 | 6.07
2024-12-10 | 1:35 | Data | 0 | 32.379 | 30.239 | 196.173 | 7.63 | 184.593 | 2216.2 | 25.76 | 42.838 | 6.37 | 1.373 | 4.717 | 8635.19 | 2.073 | 98.1 | 77.5 | 1441 | 21.46 | 5612.9 | 2959 | 2887.8 | 4252.3 | 1219.5 | 0.67881 | 6.089
2024-12-10 | 1:35 | Data | 0 | 32.663 | 30.469 | 196.219 | 7.64 | 184.684 | 2217.1 | 25.76 | 43.019 | 6.37 | 1.38 | 4.714 | 8662.33 | 2.066 | 98.1 | 77.4 | 1441 | 21.46 | 5630.5 | 2962.2 | 2901.8 | 4259.1 | 1219.5 | 0.67825 | 6.095
2024-12-10 | 1:35 | Data | 0 | 32.19 | 30.165 | 196.128 | 7.64 | 184.639 | 2213.49 | 25.76 | 42.929 | 6.36 | 1.372 | 4.69 | 8662.33 | 1.924 | 98.1 | 77.4 | 1439 | 21.42 | 5630.5 | 2953.2 | 2911.8 | 4263.8 | 1219.5 | 0.67582 | 6.062
2024-12-10 | 1:35 | Data | 0 | 32.48 | 30.198 | 196.128 | 7.64 | 184.639 | 2215.29 | 25.75 | 42.929 | 6.37 | 1.369 | 4.71 | 8648.76 | 2.093 | 98.1 | 77.5 | 1440 | 21.42 | 5621.7 | 2963.3 | 2873.4 | 4241.5 | 1219.5 | 0.68256 | 6.079
2024-12-10 | 1:35 | Data | 0 | 32.298 | 30.192 | 196.083 | 7.64 | 184.593 | 2217.1 | 25.77 | 42.929 | 6.37 | 1.371 | 4.714 | 8657.8 | 1.87 | 98.1 | 77.5 | 1441 | 21.46 | 5627.6 | 2958.3 | 2881.9 | 4246.7 | 1219.5 | 0.68019 | 6.083
2024-12-10 | 1:36 | Data | 0 | 32.109 | 30.347 | 196.083 | 7.63 | 184.639 | 2216.2 | 25.77 | 42.929 | 6.37 | 1.371 | 4.704 | 8680.41 | 1.911 | 98.1 | 77.4 | 1440 | 21.51 | 5642.3 | 2962.7 | 2885.3 | 4247.1 | 1219.5 | 0.68113 | 6.074
2024-12-10 | 1:36 | Data | 0 | 32.332 | 30.192 | 196.128 | 7.64 | 184.639 | 2216.2 | 25.76 | 42.929 | 6.37 | 1.372 | 4.71 | 8657.8 | 2.052 | 98.1 | 77.4 | 1441 | 21.51 | 5627.6 | 2961 | 2901.6 | 4260.3 | 1219.5 | 0.67779 | 6.083
2024-12-10 | 1:36 | Data | 0 | 32.595 | 30.617 | 196.173 | 7.64 | 184.684 | 2217.1 | 25.76 | 42.929 | 6.37 | 1.372 | 4.752 | 8680.41 | 2.133 | 98.1 | 77.6 | 1441 | 21.42 | 5642.3 | 2957.4 | 2917 | 4269.4 | 1219.5 | 0.67552 | 6.124
2024-12-10 | 1:36 | Data | 0 | 32.298 | 30.185 | 196.083 | 7.64 | 184.639 | 2218.91 | 25.76 | 42.929 | 6.36 | 1.356 | 4.726 | 8662.33 | 2.093 | 98.1 | 77.7 | 1442 | 21.42 | 5630.5 | 2962.8 | 2903.3 | 4263 | 1219.5 | 0.67678 | 6.083
2024-12-10 | 1:36 | Data | 0 | 32.278 | 30.212 | 195.947 | 7.63 | 184.593 | 2218.91 | 25.76 | 42.929 | 6.36 | 1.353 | 4.704 | 8671.37 | 1.863 | 98.1 | 77.7 | 1443 | 21.42 | 5636.4 | 2956.8 | 2898.3 | 4252.2 | 1219.5 | 0.67804 | 6.056
2024-12-10 | 1:36 | Data | 0 | 32.372 | 30.307 | 196.083 | 7.63 | 184.593 | 2218.91 | 25.76 | 42.929 | 6.37 | 1.371 | 4.708 | 8662.33 | 2.079 | 98.1 | 77.5 | 1442 | 21.46 | 5630.5 | 2967.8 | 2898.4 | 4261.1 | 1219.5 | 0.6782 | 6.078
2024-12-10 | 1:36 | Data | 0 | 32.669 | 30.55 | 192.102 | 7.64 | 181.023 | 2218.91 | 25.76 | 42.929 | 6.37 | 1.372 | 4.683 | 8666.85 | 2.268 | 98.1 | 77.3 | 1442 | 21.46 | 5633.5 | 2933.6 | 2879.3 | 4227.7 | 1219.5 | 0.6766 | 6.055
2024-12-10 | 1:36 | Data | 0 | 32.838 | 31.299 | 187.127 | 7.64 | 176.278 | 2218.91 | 25.76 | 42.838 | 6.37 | 1.359 | 4.598 | 8680.41 | 1.857 | 98.1 | 77.2 | 1442 | 21.42 | 5642.3 | 2887.1 | 2808.7 | 4148.6 | 1219.5 | 0.67896 | 5.958
2024-12-10 | 1:36 | Data | 0 | 33.054 | 31.123 | 183.056 | 7.64 | 172.708 | 2218.91 | 25.76 | 42.838 | 6.37 | 1.339 | 4.488 | 8684.94 | 2.032 | 98.1 | 77 | 1442 | 21.46 | 5645.2 | 2837.3 | 2778.8 | 4094.9 | 1219.5 | 0.67628 | 5.827
2024-12-10 | 1:36 | Data | 0 | 32.96 | 31.339 | 179.935 | 7.64 | 169.815 | 2217.1 | 25.76 | 42.929 | 6.36 | 1.339 | 4.389 | 8680.41 | 1.728 | 98.1 | 76.6 | 1441 | 21.46 | 5642.3 | 2815.6 | 2741.8 | 4054.4 | 1219.5 | 0.67747 | 5.726
2024-12-10 | 1:36 | Data | 0 | 33.635 | 31.515 | 177.538 | 7.63 | 167.646 | 2216.2 | 25.76 | 42.748 | 6.37 | 1.326 | 4.327 | 8680.41 | 1.708 | 98.1 | 76.5 | 1441 | 21.37 | 5642.3 | 2791.5 | 2726.1 | 4025 | 1219.5 | 0.6755 | 5.653
2024-12-10 | 1:36 | Data | 0 | 33.237 | 31.346 | 175.412 | 7.63 | 165.657 | 2216.2 | 25.76 | 43.47 | 6.37 | 1.322 | 4.305 | 8671.37 | 1.674 | 98 | 76.5 | 1440 | 21.74 | 5636.4 | 2774.3 | 2725.6 | 4013.9 | 1219.5 | 0.67385 | 5.628
2024-12-10 | 1:36 | Data | 0 | 33.412 | 31.596 | 173.783 | 7.64 | 164.166 | 2211.68 | 25.76 | 43.651 | 6.37 | 1.313 | 4.252 | 8680.41 | 1.728 | 98 | 76.4 | 1437 | 21.87 | 5642.3 | 2749.7 | 2692.5 | 3974.1 | 1219.5 | 0.67335 | 5.564
2024-12-10 | 1:36 | Data | 0 | 33.358 | 32.015 | 172.381 | 7.63 | 162.946 | 2216.2 | 25.77 | 44.012 | 6.38 | 1.311 | 4.233 | 8630.67 | 1.614 | 98 | 76.3 | 1441 | 22.01 | 5609.9 | 2725.1 | 2691.8 | 3956.8 | 1219.5 | 0.67044 | 5.543
2024-12-10 | 1:36 | Data | 0 | 33.216 | 31.799 | 171.205 | 7.63 | 161.725 | 2216.2 | 25.77 | 44.373 | 6.38 | 1.295 | 4.209 | 8626.15 | 1.566 | 98 | 76.5 | 1441 | 22.23 | 5607 | 2729.6 | 2656.6 | 3932.9 | 1219.5 | 0.67604 | 5.504
2024-12-10 | 1:36 | Data | 0 | 33.304 | 31.799 | 170.255 | 7.63 | 160.867 | 2216.2 | 25.78 | 44.825 | 6.38 | 1.285 | 4.174 | 8594.49 | 1.587 | 98 | 76.5 | 1441 | 22.41 | 5586.4 | 2724.3 | 2672.9 | 3943.4 | 1219.5 | 0.6716 | 5.459
2024-12-10 | 1:36 | Data | 0 | 33.628 | 32.177 | 170.391 | 7.63 | 160.957 | 2216.2 | 25.77 | 45.005 | 6.39 | 1.285 | 4.156 | 8608.06 | 1.83 | 98 | 76.4 | 1441 | 22.46 | 5595.2 | 2703.4 | 2668.8 | 3929.2 | 1219.5 | 0.67129 | 5.441
2024-12-10 | 1:36 | Data | 0 | 33.243 | 31.751 | 170.119 | 7.64 | 160.731 | 2128.52 | 25.78 | 45.457 | 6.39 | 1.297 | 4.132 | 8576.4 | 1.715 | 97.9 | 76.1 | 1382 | 22.77 | 5574.7 | 2712.5 | 2667.4 | 3929.3 | 1219.5 | 0.67134 | 5.429
2024-12-10 | 1:37 | Data | 0 | 33.412 | 31.799 | 170.165 | 7.64 | 160.731 | 2161.97 | 25.78 | 45.637 | 6.39 | 1.297 | 4.17 | 8553.79 | 1.614 | 97.9 | 76.3 | 1412 | 22.86 | 5560 | 2714.4 | 2675.1 | 3941.6 | 1219.5 | 0.67208 | 5.467
2024-12-10 | 1:37 | Data | 0 | 33.412 | 32.015 | 170.119 | 7.64 | 160.822 | 2216.2 | 25.79 | 45.998 | 6.39 | 1.293 | 4.168 | 8535.7 | 1.526 | 97.9 | 76.3 | 1441 | 23 | 5548.2 | 2725.4 | 2685.9 | 3952.4 | 1219.5 | 0.67255 | 5.461
2024-12-10 | 1:37 | Data | 0 | 33.318 | 31.799 | 170.3 | 7.64 | 160.912 | 2218.91 | 25.78 | 45.908 | 6.4 | 1.274 | 4.133 | 8481.44 | 1.445 | 97.9 | 76.4 | 1442 | 22.95 | 5512.9 | 2720.3 | 2673.2 | 3940.4 | 1219.5 | 0.67337 | 5.407
2024-12-10 | 1:37 | Data | 0 | 33.419 | 31.846 | 170.3 | 7.64 | 160.867 | 2218.91 | 25.78 | 45.908 | 6.41 | 1.283 | 4.144 | 8454.3 | 1.587 | 97.9 | 76.4 | 1442 | 22.95 | 5495.3 | 2723 | 2672.8 | 3931.8 | 1219.5 | 0.67362 | 5.427
2024-12-10 | 1:37 | Data | 0 | 33.864 | 31.805 | 170.165 | 7.63 | 160.867 | 2218.91 | 25.78 | 45.998 | 6.4 | 1.294 | 4.161 | 8445.26 | 1.654 | 97.9 | 76.3 | 1443 | 23 | 5489.4 | 2726.8 | 2657.7 | 3943.1 | 1219.5 | 0.67429 | 5.457
2024-12-10 | 1:37 | Data | 0 | 33.412 | 31.92 | 170.255 | 7.63 | 160.822 | 2218.91 | 25.78 | 46.269 | 6.41 | 1.295 | 4.121 | 8431.69 | 1.701 | 97.9 | 76.1 | 1442 | 23.09 | 5480.6 | 2700.5 | 2645.4 | 3908 | 1219.5 | 0.67418 | 5.416
2024-12-10 | 1:37 | Data | 0 | 33.412 | 32.001 | 170.074 | 7.63 | 160.686 | 2217.1 | 25.78 | 46.179 | 6.41 | 1.291 | 4.124 | 8440.74 | 1.614 | 97.9 | 76.2 | 1441 | 23.13 | 5486.5 | 2702 | 2631.2 | 3899.6 | 1219.5 | 0.67381 | 5.416
2024-12-10 | 1:37 | Data | 0 | 33.864 | 31.826 | 170.3 | 7.63 | 160.867 | 2216.2 | 25.78 | 46.269 | 6.41 | 1.283 | 4.122 | 8445.26 | 1.728 | 97.9 | 76.3 | 1441 | 23.13 | 5489.4 | 2696.8 | 2613.8 | 3887.7 | 1219.5 | 0.67618 | 5.404
2024-12-10 | 1:37 | Data | 0 | 33.466 | 31.603 | 170.165 | 7.64 | 160.731 | 2217.1 | 25.78 | 46.269 | 6.4 | 1.288 | 4.161 | 8427.17 | 1.668 | 97.9 | 76.4 | 1441 | 23.13 | 5477.7 | 2705 | 2652.6 | 3916.1 | 1219.5 | 0.67399 | 5.449
2024-12-10 | 1:37 | Data | 0 | 33.648 | 31.691 | 170.074 | 7.64 | 160.731 | 2216.2 | 25.78 | 46.269 | 6.4 | 1.282 | 4.173 | 8431.69 | 1.647 | 97.9 | 76.5 | 1440 | 23.13 | 5480.6 | 2702.5 | 2658.6 | 3924 | 1219.5 | 0.67114 | 5.455
2024-12-10 | 1:37 | Data | 0 | 33.567 | 31.967 | 170.119 | 7.64 | 160.686 | 2223.43 | 25.78 | 46.269 | 6.4 | 1.287 | 4.158 | 8386.47 | 1.722 | 97.9 | 76.4 | 1445 | 23.09 | 5451.2 | 2720.9 | 2670.4 | 3941.8 | 1219.5 | 0.67131 | 5.444
2024-12-10 | 1:37 | Data | 0 | 33.412 | 31.576 | 170.074 | 7.64 | 160.641 | 2222.52 | 25.78 | 46.269 | 6.41 | 1.289 | 4.167 | 8377.43 | 1.715 | 97.9 | 76.4 | 1445 | 23.13 | 5445.3 | 2714.8 | 2664.6 | 3931.2 | 1219.5 | 0.67315 | 5.457
2024-12-10 | 1:37 | Data | 0 | 33.385 | 31.859 | 169.938 | 7.63 | 160.505 | 2223.43 | 25.78 | 46.269 | 6.41 | 1.301 | 4.158 | 8372.9 | 1.722 | 97.9 | 76.2 | 1445 | 23.09 | 5442.4 | 2700 | 2672.1 | 3923.8 | 1219.5 | 0.67004 | 5.458
2024-12-10 | 1:37 | Data | 0 | 33.527 | 32.244 | 169.984 | 7.64 | 160.55 | 2218.91 | 25.78 | 46.179 | 6.41 | 1.297 | 4.132 | 8345.77 | 1.566 | 97.9 | 76.1 | 1442 | 23.13 | 5424.8 | 2697 | 2658.3 | 3914.7 | 1219.5 | 0.672 | 5.428
2024-12-10 | 1:37 | Data | 0 | 33.615 | 31.711 | 169.938 | 7.63 | 160.505 | 2216.2 | 25.78 | 46.269 | 6.41 | 1.291 | 4.116 | 8372.9 | 1.722 | 97.9 | 76.1 | 1441 | 23.13 | 5442.4 | 2716.7 | 2673.8 | 3937.3 | 1219.6 | 0.67061 | 5.407
2024-12-10 | 1:37 | Data | 0 | 33.642 | 31.799 | 169.984 | 7.64 | 160.55 | 2216.2 | 25.78 | 46.179 | 6.42 | 1.294 | 4.133 | 8377.43 | 1.641 | 97.9 | 76.2 | 1441 | 23.09 | 5445.3 | 2706.5 | 2687.5 | 3940.8 | 1219.6 | 0.67057 | 5.427
2024-12-10 | 1:37 | Data | 0 | 33.412 | 31.839 | 169.893 | 7.63 | 160.55 | 2216.2 | 25.78 | 46.179 | 6.41 | 1.291 | 4.158 | 8359.34 | 1.701 | 97.9 | 76.3 | 1441 | 23.09 | 5433.6 | 2706.7 | 2639.6 | 3910 | 1219.6 | 0.67498 | 5.447
2024-12-10 | 1:38 | Data | 0 | 33.412 | 31.974 | 169.984 | 7.63 | 160.55 | 2216.2 | 25.78 | 46.269 | 6.41 | 1.285 | 4.16 | 8350.29 | 1.641 | 97.9 | 76.4 | 1441 | 23.13 | 5427.7 | 2710.5 | 2654.7 | 3922.1 | 1219.6 | 0.67349 | 5.445
2024-12-10 | 1:38 | Data | 0 | 33.635 | 32.001 | 169.938 | 7.64 | 160.55 | 2216.2 | 25.77 | 46.269 | 6.41 | 1.307 | 4.164 | 8386.47 | 1.836 | 97.9 | 76.1 | 1441 | 23.13 | 5451.2 | 2729.7 | 2647.5 | 3927.4 | 1219.6 | 0.67831 | 5.47
2024-12-10 | 1:38 | Data | 0 | 33.804 | 31.859 | 170.029 | 7.63 | 160.55 | 2216.2 | 25.78 | 46.269 | 6.4 | 1.295 | 4.162 | 8386.47 | 1.796 | 97.9 | 76.3 | 1441 | 23.13 | 5451.2 | 2720.2 | 2648.5 | 3924.6 | 1219.6 | 0.67557 | 5.458
2024-12-10 | 1:38 | Data | 0 | 33.426 | 31.799 | 169.984 | 7.63 | 160.55 | 2216.2 | 25.79 | 46.179 | 6.41 | 1.299 | 4.141 | 8372.9 | 1.614 | 97.9 | 76.1 | 1441 | 23.09 | 5442.4 | 2734.4 | 2682.9 | 3952.6 | 1219.6 | 0.67454 | 5.438
2024-12-10 | 1:38 | Data | 0 | 33.615 | 31.812 | 169.893 | 7.64 | 160.55 | 2216.2 | 25.79 | 46.269 | 6.4 | 1.292 | 4.142 | 8372.9 | 1.769 | 97.9 | 76.2 | 1441 | 23.13 | 5442.4 | 2712.9 | 2675.2 | 3933.6 | 1219.6 | 0.67172 | 5.434
2024-12-10 | 1:38 | Data | 0 | 33.615 | 32.021 | 169.984 | 7.63 | 160.596 | 2216.2 | 25.78 | 45.998 | 6.4 | 1.283 | 4.16 | 8386.47 | 1.614 | 97.9 | 76.4 | 1441 | 23 | 5451.2 | 2719.2 | 2675.7 | 3940.8 | 1219.6 | 0.67349 | 5.443
2024-12-10 | 1:38 | Data | 0 | 33.628 | 31.799 | 169.893 | 7.64 | 160.505 | 2217.1 | 25.77 | 46.269 | 6.4 | 1.291 | 4.108 | 8386.47 | 1.668 | 97.9 | 76.1 | 1441 | 23.09 | 5451.2 | 2724.2 | 2655 | 3929.9 | 1219.6 | 0.67683 | 5.399
2024-12-10 | 1:38 | Data | 0 | 33.412 | 31.799 | 169.893 | 7.64 | 160.596 | 2217.1 | 25.79 | 46.269 | 6.4 | 1.293 | 4.134 | 8386.47 | 1.816 | 97.9 | 76.2 | 1441 | 23.13 | 5451.2 | 2718.2 | 2646.5 | 3918.5 | 1219.6 | 0.67693 | 5.427
2024-12-10 | 1:38 | Data | 0 | 33.426 | 32.021 | 169.938 | 7.63 | 160.55 | 2217.1 | 25.78 | 46.269 | 6.4 | 1.286 | 4.163 | 8390.99 | 1.398 | 97.9 | 76.4 | 1441 | 23.09 | 5454.1 | 2712.5 | 2675.1 | 3937.6 | 1219.6 | 0.67043 | 5.449
2024-12-10 | 1:38 | Data | 0 | 33.635 | 31.805 | 169.758 | 7.63 | 160.505 | 2215.29 | 25.78 | 46.269 | 6.4 | 1.301 | 4.153 | 8400.04 | 1.634 | 97.9 | 76.2 | 1441 | 23.13 | 5460 | 2726.6 | 2680.8 | 3951.6 | 1219.6 | 0.67123 | 5.454
2024-12-10 | 1:38 | Data | 0 | 33.412 | 31.799 | 169.848 | 7.64 | 160.505 | 2217.1 | 25.78 | 46.179 | 6.41 | 1.3 | 4.15 | 8409.08 | 1.614 | 97.9 | 76.2 | 1441 | 23.09 | 5465.9 | 2707.9 | 2681.1 | 3936.9 | 1219.6 | 0.67012 | 5.449
2024-12-10 | 1:38 | Data | 0 | 33.412 | 32.075 | 170.074 | 7.64 | 160.55 | 2216.2 | 25.78 | 46.269 | 6.4 | 1.302 | 4.128 | 8381.95 | 1.566 | 97.9 | 76 | 1441 | 23.13 | 5448.3 | 2698.3 | 2665.7 | 3921.6 | 1219.6 | 0.67119 | 5.43
2024-12-10 | 1:38 | Data | 0 | 33.385 | 31.799 | 169.848 | 7.63 | 160.505 | 2215.29 | 25.78 | 46.269 | 6.41 | 1.291 | 4.131 | 8386.47 | 1.728 | 97.9 | 76.2 | 1441 | 23.09 | 5451.2 | 2701.3 | 2658.7 | 3918.3 | 1219.6 | 0.67279 | 5.422
2024-12-10 | 1:38 | Data | 0 | 33.223 | 31.684 | 169.938 | 7.64 | 160.596 | 2216.2 | 25.78 | 46.269 | 6.4 | 1.289 | 4.114 | 8386.47 | 1.391 | 97.9 | 76.1 | 1441 | 23.13 | 5451.2 | 2715.3 | 2657.2 | 3923.2 | 1219.6 | 0.67518 | 5.402
2024-12-10 | 1:38 | Data | 0 | 33.858 | 31.826 | 169.938 | 7.64 | 160.55 | 2216.2 | 25.78 | 46.269 | 6.41 | 1.29 | 4.124 | 8400.04 | 1.688 | 97.9 | 76.2 | 1440 | 23.09 | 5460 | 2723.6 | 2645.9 | 3926.1 | 1219.6 | 0.67513 | 5.414
2024-12-10 | 1:38 | Data | 0 | 33.439 | 31.758 | 169.758 | 7.64 | 160.596 | 2216.2 | 25.78 | 45.998 | 6.41 | 1.284 | 4.13 | 8386.47 | 1.701 | 97.9 | 76.3 | 1441 | 23 | 5451.2 | 2723.1 | 2653.6 | 3928.5 | 1219.6 | 0.67472 | 5.413
2024-12-10 | 1:38 | Data | 0 | 33.412 | 31.853 | 169.938 | 7.63 | 160.505 | 2218 | 25.78 | 45.908 | 6.4 | 1.293 | 4.145 | 8386.47 | 1.62 | 97.9 | 76.2 | 1442 | 23 | 5451.2 | 2732.3 | 2635.3 | 3922.3 | 1219.6 | 0.67917 | 5.439
2024-12-10 | 1:38 | Data | 0 | 33.729 | 32.109 | 170.029 | 7.63 | 160.596 | 2217.1 | 25.79 | 46.269 | 6.41 | 1.285 | 4.119 | 8386.47 | 1.661 | 97.9 | 76.2 | 1441 | 23.13 | 5451.2 | 2715.1 | 2655.5 | 3929.1 | 1219.6 | 0.67398 | 5.404
2024-12-10 | 1:39 | Data | 0 | 33.412 | 31.974 | 170.029 | 7.63 | 160.505 | 2215.29 | 25.78 | 45.908 | 6.41 | 1.287 | 4.173 | 8422.65 | 1.809 | 97.9 | 76.4 | 1440 | 23 | 5474.7 | 2710.5 | 2683.8 | 3941.7 | 1219.6 | 0.67 | 5.46
2024-12-10 | 1:39 | Data | 0 | 33.743 | 32.055 | 169.667 | 7.64 | 160.324 | 2212.58 | 25.78 | 45.998 | 6.4 | 1.289 | 4.155 | 8418.13 | 1.762 | 97.9 | 76.3 | 1438 | 23 | 5471.8 | 2707.5 | 2669.1 | 3926.4 | 1219.6 | 0.67289 | 5.443
2024-12-10 | 1:39 | Data | 0 | 33.642 | 32.028 | 169.712 | 7.64 | 160.324 | 2214.39 | 25.78 | 45.908 | 6.41 | 1.288 | 4.129 | 8404.56 | 1.614 | 97.9 | 76.2 | 1440 | 22.95 | 5463 | 2702.5 | 2667.4 | 3927.2 | 1219.6 | 0.67083 | 5.415
2024-12-10 | 1:39 | Data | 0 | 33.615 | 31.805 | 169.712 | 7.63 | 160.324 | 2214.39 | 25.77 | 45.998 | 6.4 | 1.288 | 4.132 | 8377.43 | 1.816 | 97.9 | 76.2 | 1439 | 23 | 5445.3 | 2721.7 | 2661.9 | 3930.4 | 1219.6 | 0.67488 | 5.419
2024-12-10 | 1:39 | Data | 0 | 33.75 | 31.94 | 169.622 | 7.64 | 160.37 | 2213.49 | 25.78 | 45.998 | 6.41 | 1.289 | 4.13 | 8354.81 | 1.668 | 97.9 | 76.2 | 1439 | 23 | 5430.6 | 2722.9 | 2663.9 | 3939.1 | 1219.6 | 0.67284 | 5.418
2024-12-10 | 1:39 | Data | 0 | 33.588 | 31.826 | 169.622 | 7.64 | 160.324 | 2213.49 | 25.78 | 45.998 | 6.41 | 1.3 | 4.162 | 8372.9 | 1.809 | 97.9 | 76.2 | 1438 | 23 | 5442.4 | 2711 | 2666.1 | 3929.5 | 1219.6 | 0.6747 | 5.462
2024-12-10 | 1:39 | Data | 0 | 33.621 | 32.237 | 169.848 | 7.64 | 160.37 | 2213.49 | 25.78 | 45.998 | 6.41 | 1.3 | 4.13 | 8359.34 | 1.607 | 97.9 | 76.1 | 1439 | 22.95 | 5433.6 | 2726.2 | 2654 | 3929.5 | 1219.6 | 0.67709 | 5.43
2024-12-10 | 1:39 | Data | 0 | 33.642 | 32.028 | 169.712 | 7.64 | 160.324 | 2214.39 | 25.78 | 45.908 | 6.4 | 1.296 | 4.106 | 8368.38 | 1.614 | 97.9 | 76 | 1439 | 22.95 | 5439.4 | 2690.5 | 2644.3 | 3901.7 | 1219.6 | 0.67407 | 5.401
2024-12-10 | 1:39 | Data | 0 | 33.5 | 32.224 | 169.486 | 7.64 | 160.234 | 2213.49 | 25.79 | 45.998 | 6.41 | 1.296 | 4.134 | 8372.9 | 1.607 | 97.9 | 76.1 | 1439 | 23 | 5442.4 | 2706.1 | 2650.5 | 3916.4 | 1219.6 | 0.6727 | 5.43
2024-12-10 | 1:39 | Data | 0 | 33.851 | 32.035 | 169.622 | 7.63 | 160.279 | 2213.49 | 25.78 | 45.998 | 6.4 | 1.296 | 4.148 | 8363.86 | 1.803 | 97.9 | 76.2 | 1439 | 23 | 5436.5 | 2705.7 | 2671.2 | 3931.8 | 1219.6 | 0.67134 | 5.444
2024-12-10 | 1:39 | Data | 0 | 33.419 | 31.826 | 169.667 | 7.63 | 160.37 | 2214.39 | 25.78 | 45.998 | 6.41 | 1.299 | 4.156 | 8372.9 | 1.762 | 97.9 | 76.2 | 1439 | 23.04 | 5442.4 | 2724.6 | 2661.5 | 3932.9 | 1219.6 | 0.67411 | 5.453
2024-12-10 | 1:39 | Data | 0 | 33.648 | 31.859 | 169.712 | 7.64 | 160.37 | 2214.39 | 25.78 | 45.998 | 6.4 | 1.296 | 4.134 | 8359.34 | 1.782 | 97.9 | 76.1 | 1439 | 23 | 5433.6 | 2700.1 | 2673.9 | 3925.9 | 1219.6 | 0.67007 | 5.43
2024-12-10 | 1:39 | Data | 0 | 33.696 | 31.927 | 169.758 | 7.63 | 160.415 | 2213.49 | 25.78 | 45.908 | 6.41 | 1.29 | 4.13 | 8368.38 | 1.722 | 97.9 | 76.2 | 1439 | 22.95 | 5439.4 | 2711.4 | 2660.2 | 3932.7 | 1219.6 | 0.67385 | 5.42
2024-12-10 | 1:39 | Data | 0 | 33.196 | 31.974 | 169.712 | 7.64 | 160.37 | 2212.58 | 25.78 | 45.998 | 6.41 | 1.285 | 4.152 | 8368.38 | 1.587 | 97.9 | 76.4 | 1439 | 23 | 5439.4 | 2732.7 | 2670.1 | 3947.4 | 1219.6 | 0.67583 | 5.436
2024-12-10 | 1:39 | Data | 0 | 33.642 | 32.028 | 169.622 | 7.64 | 160.279 | 2213.49 | 25.78 | 45.998 | 6.4 | 1.288 | 4.177 | 8372.9 | 1.512 | 97.9 | 76.4 | 1439 | 22.95 | 5442.4 | 2696.2 | 2676.2 | 3927.1 | 1219.6 | 0.66902 | 5.464
2024-12-10 | 1:39 | Data | 0 | 33.642 | 32.251 | 169.848 | 7.64 | 160.46 | 2214.39 | 25.78 | 45.908 | 6.4 | 1.288 | 4.159 | 8363.86 | 1.641 | 97.9 | 76.4 | 1439 | 23 | 5436.5 | 2710.3 | 2659.4 | 3917.7 | 1219.6 | 0.6754 | 5.448
2024-12-10 | 1:39 | Data | 0 | 33.54 | 31.812 | 169.758 | 7.63 | 160.415 | 2218 | 25.78 | 45.908 | 6.4 | 1.288 | 4.146 | 8345.77 | 1.533 | 97.9 | 76.3 | 1442 | 22.95 | 5424.8 | 2702.2 | 2650.7 | 3914.2 | 1219.6 | 0.67346 | 5.434
2024-12-10 | 1:39 | Data | 0 | 33.642 | 31.799 | 169.622 | 7.64 | 160.279 | 2213.49 | 25.77 | 45.908 | 6.4 | 1.294 | 4.162 | 8345.77 | 1.722 | 97.9 | 76.3 | 1439 | 22.95 | 5424.8 | 2706.5 | 2649.6 | 3917 | 1219.6 | 0.67098 | 5.457
2024-12-10 | 1:40 | Data | 0 | 33.412 | 31.812 | 169.622 | 7.64 | 160.279 | 2213.49 | 25.78 | 45.998 | 6.41 | 1.292 | 4.162 | 8341.25 | 1.587 | 97.9 | 76.3 | 1439 | 23 | 5421.8 | 2709.7 | 2644.2 | 3912.1 | 1219.7 | 0.67521 | 5.456
2024-12-10 | 1:40 | Data | 0 | 33.642 | 31.812 | 169.712 | 7.64 | 160.324 | 2211.68 | 25.78 | 45.908 | 6.4 | 1.278 | 4.156 | 8354.81 | 1.735 | 97.9 | 76.5 | 1438 | 22.95 | 5430.6 | 2717.6 | 2637 | 3913.2 | 1219.7 | 0.67703 | 5.433
2024-12-10 | 1:40 | Data | 0 | 33.635 | 31.913 | 169.667 | 7.63 | 160.324 | 2210.77 | 25.78 | 45.998 | 6.4 | 1.278 | 4.152 | 8372.9 | 1.83 | 97.9 | 76.5 | 1437 | 23 | 5442.4 | 2729.7 | 2668.9 | 3939.1 | 1219.7 | 0.67645 | 5.43
2024-12-10 | 1:40 | Data | 0 | 33.588 | 32.015 | 169.712 | 7.63 | 160.415 | 2213.49 | 25.78 | 45.998 | 6.4 | 1.286 | 4.134 | 8350.29 | 1.62 | 97.9 | 76.3 | 1439 | 23 | 5427.7 | 2693.6 | 2658.6 | 3915.2 | 1219.7 | 0.67063 | 5.42
2024-12-10 | 1:40 | Data | 0 | 33.642 | 31.799 | 169.667 | 7.64 | 160.46 | 2213.49 | 25.78 | 46.089 | 6.4 | 1.293 | 4.12 | 8395.51 | 1.722 | 97.9 | 76.1 | 1439 | 23.04 | 5457.1 | 2704.6 | 2651.5 | 3913.4 | 1219.7 | 0.67349 | 5.413
2024-12-10 | 1:40 | Data | 0 | 33.203 | 31.799 | 169.667 | 7.64 | 160.37 | 2216.2 | 25.78 | 45.998 | 6.4 | 1.297 | 4.158 | 8770.86 | 1.499 | 97.9 | 76.2 | 1441 | 22.95 | 5701.1 | 2698.8 | 2642.5 | 3914.8 | 1219.7 | 0.6745 | 5.455
2024-12-10 | 1:40 | Data | 0 | 33.588 | 32.028 | 169.712 | 7.63 | 160.324 | 2213.49 | 25.78 | 45.998 | 6.41 | 1.292 | 4.152 | 8345.77 | 1.614 | 97.9 | 76.3 | 1439 | 22.95 | 5424.8 | 2713 | 2650.5 | 3919.2 | 1219.7 | 0.67349 | 5.443
2024-12-10 | 1:40 | Data | 0 | 33.777 | 32.028 | 169.758 | 7.64 | 160.37 | 2212.58 | 25.79 | 45.908 | 6.4 | 1.285 | 4.122 | 8336.72 | 1.418 | 97.9 | 76.2 | 1439 | 22.95 | 5418.9 | 2706.5 | 2641.3 | 3908.3 | 1219.7 | 0.67726 | 5.406
2024-12-10 | 1:40 | Data | 0 | 33.81 | 32.028 | 169.758 | 7.64 | 160.415 | 2218.91 | 25.79 | 45.908 | 6.41 | 1.283 | 4.134 | 8336.72 | 1.661 | 97.9 | 76.3 | 1442 | 23 | 5418.9 | 2695.3 | 2644.4 | 3906.1 | 1219.7 | 0.67521 | 5.417
2024-12-10 | 1:40 | Data | 0 | 33.608 | 32.021 | 169.712 | 7.64 | 160.279 | 2213.49 | 25.78 | 45.908 | 6.41 | 1.291 | 4.138 | 8345.77 | 1.681 | 97.9 | 76.2 | 1439 | 23 | 5424.8 | 2706.1 | 2640.6 | 3905.8 | 1219.7 | 0.67659 | 5.43
2024-12-10 | 1:40 | Data | 0 | 33.419 | 31.974 | 169.758 | 7.64 | 160.37 | 2213.49 | 25.78 | 45.998 | 6.4 | 1.288 | 4.152 | 8350.29 | 1.641 | 97.9 | 76.3 | 1439 | 23 | 5427.7 | 2715.3 | 2646.3 | 3921.6 | 1219.7 | 0.67515 | 5.439
2024-12-10 | 1:40 | Data | 0 | 33.527 | 32.015 | 169.848 | 7.64 | 160.324 | 2211.68 | 25.78 | 45.998 | 6.4 | 1.277 | 4.157 | 8345.77 | 1.438 | 97.9 | 76.5 | 1438 | 22.95 | 5424.8 | 2710.5 | 2647.2 | 3913.3 | 1219.7 | 0.67609 | 5.434
2024-12-10 | 1:40 | Data | 0 | 33.588 | 32.237 | 169.667 | 7.64 | 160.37 | 2210.77 | 25.78 | 45.998 | 6.41 | 1.285 | 4.151 | 8363.86 | 1.695 | 97.9 | 76.4 | 1437 | 22.95 | 5436.5 | 2698.9 | 2655.2 | 3913.9 | 1219.7 | 0.67228 | 5.437
2024-12-10 | 1:40 | Data | 0 | 33.588 | 32.116 | 169.667 | 7.64 | 160.324 | 2208.06 | 25.78 | 45.998 | 6.4 | 1.29 | 4.148 | 8372.9 | 1.722 | 97.9 | 76.3 | 1435 | 23 | 5442.4 | 2703.9 | 2667.4 | 3923.4 | 1219.7 | 0.67186 | 5.437
2024-12-10 | 1:40 | Data | 0 | 33.756 | 31.805 | 169.712 | 7.64 | 160.415 | 2210.77 | 25.77 | 45.998 | 6.41 | 1.287 | 4.116 | 8345.77 | 1.62 | 97.9 | 76.2 | 1437 | 23 | 5424.8 | 2703.3 | 2673.6 | 3928.6 | 1219.7 | 0.67099 | 5.403
2024-12-10 | 1:40 | Data | 0 | 33.702 | 31.751 | 169.667 | 7.63 | 160.415 | 2201.74 | 25.79 | 45.908 | 6.41 | 1.3 | 4.153 | 8350.29 | 1.506 | 97.9 | 76.2 | 1431 | 22.95 | 5427.7 | 2692.6 | 2659.5 | 3911.1 | 1219.7 | 0.67103 | 5.453
2024-12-10 | 1:40 | Data | 0 | 33.466 | 31.994 | 169.622 | 7.63 | 160.279 | 2211.68 | 25.78 | 45.998 | 6.41 | 1.305 | 4.165 | 8336.72 | 1.445 | 97.9 | 76.1 | 1438 | 22.95 | 5418.9 | 2709.4 | 2649.8 | 3918.4 | 1219.7 | 0.67307 | 5.47
2024-12-10 | 1:40 | Data | 0 | 33.871 | 32.042 | 169.893 | 7.64 | 160.55 | 2210.77 | 25.78 | 45.998 | 6.4 | 1.295 | 4.172 | 8350.29 | 1.641 | 97.9 | 76.3 | 1438 | 23.04 | 5427.7 | 2708.5 | 2659.5 | 3918.9 | 1219.7 | 0.67449 | 5.468
2024-12-10 | 1:41 | Data | 0 | 33.419 | 31.812 | 169.758 | 7.63 | 160.37 | 2211.68 | 25.78 | 45.908 | 6.41 | 1.294 | 4.134 | 8332.2 | 1.769 | 97.9 | 76.2 | 1438 | 23 | 5415.9 | 2698.8 | 2643.8 | 3906.6 | 1219.7 | 0.67306 | 5.428
2024-12-10 | 1:41 | Data | 0 | 33.419 | 32.001 | 169.577 | 7.64 | 160.279 | 2210.77 | 25.78 | 45.998 | 6.41 | 1.291 | 4.126 | 8336.72 | 1.587 | 97.9 | 76.2 | 1437 | 22.95 | 5418.9 | 2718.3 | 2633.1 | 3909.1 | 1219.7 | 0.67856 | 5.417
2024-12-10 | 1:41 | Data | 0 | 33.635 | 32.028 | 169.622 | 7.63 | 160.324 | 2208.97 | 25.79 | 45.998 | 6.41 | 1.292 | 4.141 | 8345.77 | 1.607 | 97.9 | 76.2 | 1436 | 22.95 | 5424.8 | 2709.6 | 2643.3 | 3908.2 | 1219.7 | 0.67643 | 5.434
2024-12-10 | 1:41 | Data | 0 | 33.615 | 31.812 | 169.622 | 7.64 | 160.415 | 2208.06 | 25.78 | 45.998 | 6.41 | 1.299 | 4.147 | 8359.34 | 1.897 | 97.9 | 76.1 | 1436 | 23 | 5433.6 | 2708.7 | 2649 | 3916.1 | 1219.7 | 0.67331 | 5.447
2024-12-10 | 1:41 | Data | 0 | 33.419 | 31.799 | 169.622 | 7.64 | 160.324 | 2211.68 | 25.78 | 45.998 | 6.41 | 1.291 | 4.13 | 8359.34 | 1.62 | 97.9 | 76.2 | 1437 | 23 | 5433.6 | 2708.4 | 2651.3 | 3912.4 | 1219.7 | 0.67782 | 5.421
2024-12-10 | 1:41 | Data | 0 | 33.446 | 31.974 | 169.758 | 7.64 | 160.324 | 2211.68 | 25.78 | 45.908 | 6.4 | 1.294 | 4.124 | 8345.77 | 1.62 | 97.9 | 76.1 | 1438 | 22.95 | 5424.8 | 2709.1 | 2641.5 | 3908.2 | 1219.7 | 0.67635 | 5.42
2024-12-10 | 1:41 | Data | 0 | 34.04 | 32.156 | 169.667 | 7.63 | 160.37 | 2208.06 | 25.77 | 45.998 | 6.4 | 1.284 | 4.13 | 8345.77 | 1.681 | 97.9 | 76.3 | 1435 | 23 | 5424.8 | 2711.4 | 2647 | 3920.3 | 1219.7 | 0.67447 | 5.414
2024-12-10 | 1:41 | Data | 0 | 33.642 | 32.015 | 169.577 | 7.64 | 160.279 | 2208.06 | 25.78 | 45.998 | 6.41 | 1.289 | 4.124 | 8336.72 | 1.641 | 97.9 | 76.2 | 1435 | 23 | 5418.9 | 2706.4 | 2648.9 | 3917.8 | 1219.7 | 0.67545 | 5.414
2024-12-10 | 1:41 | Data | 0 | 33.223 | 31.913 | 169.622 | 7.64 | 160.415 | 2208.97 | 25.78 | 45.998 | 6.41 | 1.282 | 4.154 | 8345.77 | 1.506 | 97.9 | 76.4 | 1435 | 22.95 | 5424.8 | 2710.7 | 2656.7 | 3924.4 | 1219.7 | 0.67366 | 5.439
2024-12-10 | 1:41 | Data | 0 | 33.81 | 32.028 | 169.712 | 7.64 | 160.324 | 2208.06 | 25.78 | 45.998 | 6.41 | 1.279 | 4.14 | 8345.77 | 1.83 | 97.9 | 76.4 | 1435 | 23 | 5424.8 | 2714.3 | 2652.3 | 3920.6 | 1219.7 | 0.67502 | 5.418
2024-12-10 | 1:41 | Data | 0 | 33.756 | 31.664 | 169.712 | 7.64 | 160.415 | 2208.97 | 25.78 | 45.998 | 6.41 | 1.282 | 4.104 | 8336.72 | 1.728 | 97.9 | 76.2 | 1436 | 23 | 5418.9 | 2696.6 | 2661 | 3920.3 | 1219.7 | 0.67021 | 5.386
2024-12-10 | 1:41 | Data | 0 | 33.858 | 32.251 | 169.848 | 7.64 | 160.46 | 2208.97 | 25.78 | 45.998 | 6.4 | 1.282 | 4.098 | 8332.2 | 1.661 | 97.9 | 76.2 | 1435 | 23 | 5415.9 | 2702.9 | 2646.3 | 3915.1 | 1219.7 | 0.67337 | 5.382
2024-12-10 | 1:41 | Data | 0 | 33.878 | 31.92 | 169.758 | 7.63 | 160.415 | 2208.97 | 25.78 | 45.908 | 6.41 | 1.286 | 4.127 | 8309.59 | 1.634 | 97.9 | 76.2 | 1436 | 22.95 | 5401.2 | 2698.2 | 2645.3 | 3909.6 | 1219.7 | 0.67279 | 5.413
2024-12-10 | 1:41 | Data | 0 | 33.432 | 31.799 | 169.667 | 7.63 | 160.324 | 2208.06 | 25.78 | 45.998 | 6.41 | 1.287 | 4.153 | 8291.5 | 1.614 | 97.9 | 76.3 | 1435 | 23 | 5389.5 | 2707.4 | 2643.5 | 3912.4 | 1219.7 | 0.6756 | 5.439
2024-12-10 | 1:41 | Data | 0 | 33.419 | 32.015 | 169.667 | 7.64 | 160.37 | 2208.06 | 25.78 | 45.908 | 6.41 | 1.301 | 4.143 | 8291.5 | 1.607 | 97.9 | 76.1 | 1435 | 22.95 | 5389.5 | 2690.1 | 2662.8 | 3916.7 | 1219.7 | 0.6704 | 5.445
2024-12-10 | 1:41 | Data | 0 | 33.439 | 31.974 | 169.712 | 7.63 | 160.37 | 2208.97 | 25.78 | 45.908 | 6.41 | 1.292 | 4.12 | 8291.5 | 1.62 | 97.9 | 76.1 | 1435 | 22.95 | 5389.5 | 2707.5 | 2667.2 | 3926.3 | 1219.7 | 0.67315 | 5.412
2024-12-10 | 1:41 | Data | 0 | 33.756 | 32.082 | 169.712 | 7.64 | 160.37 | 2208.06 | 25.78 | 45.998 | 6.41 | 1.3 | 4.123 | 8314.11 | 1.641 | 97.9 | 76 | 1435 | 22.95 | 5404.2 | 2703.8 | 2653.4 | 3914.8 | 1219.7 | 0.67156 | 5.422
2024-12-10 | 1:42 | Data | 0 | 33.588 | 31.805 | 169.622 | 7.63 | 160.415 | 2206.25 | 25.78 | 45.908 | 6.41 | 1.291 | 4.114 | 8318.64 | 1.701 | 97.9 | 76.1 | 1434 | 22.95 | 5407.1 | 2724.9 | 2643.8 | 3927.8 | 1219.7 | 0.67612 | 5.404
2024-12-10 | 1:42 | Data | 0 | 33.473 | 31.913 | 169.848 | 7.63 | 160.505 | 2201.74 | 25.78 | 45.998 | 6.4 | 1.284 | 4.105 | 8314.11 | 1.526 | 97.9 | 76.2 | 1431 | 22.95 | 5404.2 | 2695.3 | 2636.5 | 3903.5 | 1219.7 | 0.67431 | 5.389
2024-12-10 | 1:42 | Data | 0 | 33.648 | 32.197 | 169.848 | 7.64 | 160.415 | 2205.35 | 25.79 | 45.998 | 6.41 | 1.271 | 4.134 | 8314.11 | 1.506 | 97.9 | 76.5 | 1434 | 22.95 | 5404.2 | 2723 | 2656.6 | 3933.8 | 1219.7 | 0.67503 | 5.404
2024-12-10 | 1:42 | Data | 0 | 33.642 | 32.001 | 169.893 | 7.63 | 160.46 | 2206.25 | 25.78 | 45.908 | 6.41 | 1.292 | 4.123 | 8318.64 | 1.641 | 97.9 | 76.1 | 1433 | 22.95 | 5407.1 | 2698.5 | 2643.9 | 3901.6 | 1219.7 | 0.6748 | 5.415
2024-12-10 | 1:42 | Data | 0 | 33.635 | 32.048 | 169.938 | 7.63 | 160.415 | 2208.06 | 25.78 | 46.089 | 6.4 | 1.293 | 4.156 | 8314.11 | 1.593 | 97.9 | 76.3 | 1435 | 23 | 5404.2 | 2707.5 | 2638 | 3907.8 | 1219.8 | 0.67939 | 5.449
2024-12-10 | 1:42 | Data | 0 | 33.628 | 32.028 | 169.848 | 7.63 | 160.415 | 2206.25 | 25.78 | 46.089 | 6.41 | 1.287 | 4.142 | 8318.64 | 1.614 | 97.9 | 76.3 | 1433 | 23 | 5407.1 | 2712.2 | 2649.5 | 3915.7 | 1219.8 | 0.67571 | 5.429
2024-12-10 | 1:42 | Data | 0 | 33.858 | 32.278 | 169.848 | 7.64 | 160.55 | 2208.06 | 25.78 | 45.998 | 6.41 | 1.293 | 4.126 | 8314.11 | 1.587 | 97.9 | 76.1 | 1435 | 22.95 | 5404.2 | 2702.5 | 2637.9 | 3903.2 | 1219.8 | 0.67572 | 5.42
2024-12-10 | 1:42 | Data | 0 | 33.918 | 31.839 | 169.758 | 7.63 | 160.46 | 2208.97 | 25.78 | 45.908 | 6.4 | 1.291 | 4.139 | 8336.72 | 1.836 | 97.9 | 76.2 | 1436 | 23 | 5418.9 | 2702.1 | 2641.6 | 3895.6 | 1219.8 | 0.67455 | 5.43
2024-12-10 | 1:42 | Data | 0 | 33.554 | 32.204 | 169.893 | 7.64 | 160.415 | 2208.06 | 25.78 | 45.998 | 6.41 | 1.293 | 4.158 | 8336.72 | 1.479 | 97.9 | 76.3 | 1435 | 23 | 5418.9 | 2707.8 | 2636.9 | 3905.2 | 1219.8 | 0.67802 | 5.451
2024-12-10 | 1:42 | Data | 0 | 33.473 | 31.974 | 169.712 | 7.64 | 160.324 | 2210.77 | 25.78 | 45.998 | 6.41 | 1.299 | 4.138 | 8350.29 | 1.647 | 97.9 | 76.1 | 1437 | 23 | 5427.7 | 2702.3 | 2648 | 3908.7 | 1219.8 | 0.67407 | 5.437
2024-12-10 | 1:42 | Data | 0 | 33.642 | 32.197 | 169.848 | 7.63 | 160.46 | 2211.68 | 25.78 | 45.908 | 6.4 | 1.301 | 4.161 | 8341.25 | 1.506 | 97.9 | 76.2 | 1437 | 23 | 5421.8 | 2715.1 | 2644.7 | 3915.3 | 1219.8 | 0.67475 | 5.461
2024-12-10 | 1:42 | Data | 0 | 33.635 | 31.913 | 169.848 | 7.63 | 160.37 | 2213.49 | 25.79 | 45.908 | 6.41 | 1.293 | 4.142 | 8359.34 | 1.607 | 97.9 | 76.2 | 1439 | 23 | 5433.6 | 2714.3 | 2633.7 | 3909.7 | 1219.8 | 0.67691 | 5.435
2024-12-10 | 1:42 | Data | 0 | 33.858 | 32.055 | 169.893 | 7.63 | 160.415 | 2208.06 | 25.79 | 45.908 | 6.41 | 1.293 | 4.14 | 8363.86 | 1.776 | 97.9 | 76.2 | 1435 | 22.95 | 5436.5 | 2696.4 | 2627.5 | 3896.4 | 1219.8 | 0.67452 | 5.432
2024-12-10 | 1:42 | Data | 0 | 33.601 | 31.907 | 169.667 | 7.63 | 160.37 | 2213.49 | 25.78 | 45.998 | 6.4 | 1.289 | 4.149 | 8363.86 | 1.607 | 97.9 | 76.3 | 1439 | 23 | 5436.5 | 2710 | 2637.3 | 3908.7 | 1219.8 | 0.6769 | 5.437
2024-12-10 | 1:42 | Data | 0 | 33.844 | 32.305 | 169.667 | 7.63 | 160.46 | 2211.68 | 25.78 | 45.908 | 6.41 | 1.29 | 4.16 | 8372.9 | 1.695 | 97.9 | 76.3 | 1437 | 22.95 | 5442.4 | 2699.1 | 2648.7 | 3909.7 | 1219.8 | 0.67337 | 5.45
2024-12-10 | 1:42 | Data | 0 | 33.419 | 31.826 | 169.848 | 7.64 | 160.279 | 2207.16 | 25.78 | 45.998 | 6.41 | 1.289 | 4.157 | 8381.95 | 1.776 | 97.9 | 76.3 | 1435 | 22.95 | 5448.3 | 2708.3 | 2652.6 | 3918.4 | 1219.8 | 0.6751 | 5.446
2024-12-10 | 1:42 | Data | 0 | 33.642 | 32.015 | 169.712 | 7.64 | 160.324 | 2210.77 | 25.78 | 45.908 | 6.41 | 1.284 | 4.178 | 8386.47 | 1.654 | 97.9 | 76.5 | 1437 | 23 | 5451.2 | 2693.6 | 2639.4 | 3898.3 | 1219.8 | 0.67361 | 5.462
2024-12-10 | 1:42 | Data | 0 | 33.615 | 32.089 | 169.667 | 7.63 | 160.279 | 2211.68 | 25.78 | 45.908 | 6.41 | 1.286 | 4.14 | 8390.99 | 1.823 | 97.9 | 76.3 | 1437 | 23 | 5454.1 | 2699.7 | 2654.6 | 3921.9 | 1219.8 | 0.67433 | 5.427
2024-12-10 | 1:43 | Data | 0 | 33.561 | 32.021 | 169.622 | 7.63 | 160.37 | 2212.58 | 25.78 | 45.818 | 6.41 | 1.283 | 4.141 | 8372.9 | 1.398 | 97.9 | 76.4 | 1439 | 22.86 | 5442.4 | 2711.3 | 2663.2 | 3927.8 | 1219.8 | 0.67331 | 5.423
2024-12-10 | 1:43 | Data | 0 | 33.756 | 32.21 | 169.758 | 7.63 | 160.415 | 2211.68 | 25.78 | 45.908 | 6.4 | 1.285 | 4.146 | 8345.77 | 1.506 | 97.9 | 76.3 | 1438 | 22.91 | 5424.8 | 2706.4 | 2628 | 3902.1 | 1219.8 | 0.67648 | 5.431
2024-12-10 | 1:43 | Data | 0 | 33.419 | 32.028 | 169.938 | 7.64 | 160.415 | 2212.58 | 25.78 | 45.727 | 6.4 | 1.289 | 4.158 | 8336.72 | 1.566 | 97.9 | 76.3 | 1439 | 22.86 | 5418.9 | 2703.3 | 2647.4 | 3908.4 | 1219.8 | 0.6739 | 5.447
2024-12-10 | 1:43 | Data | 0 | 34.04 | 32.089 | 169.938 | 7.64 | 160.46 | 2214.39 | 25.78 | 45.727 | 6.41 | 1.289 | 4.136 | 8341.25 | 1.647 | 97.9 | 76.2 | 1439 | 22.86 | 5421.8 | 2708.7 | 2655.6 | 3918.8 | 1219.8 | 0.67465 | 5.426
2024-12-10 | 1:43 | Data | 0 | 33.851 | 32.035 | 169.758 | 7.64 | 160.37 | 2213.49 | 25.77 | 45.727 | 6.41 | 1.29 | 4.134 | 8345.77 | 1.823 | 97.9 | 76.2 | 1439 | 22.86 | 5424.8 | 2698.5 | 2637 | 3903.1 | 1219.8 | 0.67574 | 5.422
2024-12-10 | 1:43 | Data | 0 | 33.669 | 32.028 | 169.893 | 7.64 | 160.505 | 2213.49 | 25.78 | 45.727 | 6.4 | 1.291 | 4.16 | 8323.16 | 1.62 | 97.9 | 76.3 | 1439 | 22.86 | 5410.1 | 2689.4 | 2641.7 | 3899.9 | 1219.8 | 0.67295 | 5.451
2024-12-10 | 1:43 | Data | 0 | 33.628 | 32.204 | 169.712 | 7.63 | 160.46 | 2214.39 | 25.79 | 45.637 | 6.4 | 1.287 | 4.143 | 8314.11 | 1.83 | 97.9 | 76.3 | 1439 | 22.82 | 5404.2 | 2710.1 | 2671.4 | 3932.9 | 1219.8 | 0.67213 | 5.431
2024-12-10 | 1:43 | Data | 0 | 33.756 | 32.028 | 169.893 | 7.63 | 160.505 | 2213.49 | 25.79 | 45.727 | 6.4 | 1.282 | 4.134 | 8309.59 | 1.661 | 97.9 | 76.3 | 1439 | 22.86 | 5401.2 | 2710.5 | 2658.4 | 3924.3 | 1219.8 | 0.67427 | 5.414
2024-12-10 | 1:43 | Data | 0 | 33.648 | 32.015 | 169.712 | 7.64 | 160.37 | 2216.2 | 25.78 | 45.727 | 6.4 | 1.296 | 4.147 | 8305.07 | 1.634 | 97.9 | 76.2 | 1441 | 22.86 | 5398.3 | 2704 | 2635 | 3901.3 | 1219.8 | 0.67598 | 5.443
2024-12-10 | 1:43 | Data | 0 | 33.783 | 31.866 | 169.848 | 7.63 | 160.46 | 2217.1 | 25.78 | 45.998 | 6.4 | 1.295 | 4.152 | 8305.07 | 1.553 | 97.9 | 76.2 | 1441 | 22.95 | 5398.3 | 2697.5 | 2644.2 | 3904.6 | 1219.8 | 0.67348 | 5.447
2024-12-10 | 1:43 | Data | 0 | 33.756 | 32.042 | 169.938 | 7.64 | 160.505 | 2216.2 | 25.78 | 45.727 | 6.4 | 1.286 | 4.152 | 8318.64 | 1.6 | 97.9 | 76.4 | 1441 | 22.86 | 5407.1 | 2679.7 | 2638.1 | 3889.5 | 1219.8 | 0.67225 | 5.439
2024-12-10 | 1:43 | Data | 0 | 33.858 | 32.264 | 169.758 | 7.64 | 160.505 | 2216.2 | 25.78 | 45.637 | 6.41 | 1.286 | 4.134 | 8314.11 | 1.809 | 97.9 | 76.3 | 1441 | 22.82 | 5404.2 | 2700.8 | 2639.3 | 3905 | 1219.8 | 0.67427 | 5.42
2024-12-10 | 1:43 | Data | 0 | 33.864 | 32.042 | 169.758 | 7.64 | 160.46 | 2216.2 | 25.78 | 45.727 | 6.4 | 1.297 | 4.131 | 8314.11 | 1.816 | 97.9 | 76.1 | 1441 | 22.82 | 5404.2 | 2711.9 | 2629 | 3903.7 | 1219.8 | 0.67898 | 5.427
2024-12-10 | 1:43 | Data | 0 | 33.419 | 32.075 | 169.938 | 7.64 | 160.46 | 2216.2 | 25.78 | 45.818 | 6.41 | 1.291 | 4.144 | 8309.59 | 1.614 | 97.9 | 76.2 | 1441 | 22.86 | 5401.2 | 2715.9 | 2652.2 | 3925.9 | 1219.8 | 0.6747 | 5.436
2024-12-10 | 1:43 | Data | 0 | 33.925 | 32.042 | 169.848 | 7.63 | 160.46 | 2210.77 | 25.78 | 45.637 | 6.41 | 1.295 | 4.129 | 8318.64 | 1.755 | 97.9 | 76.1 | 1437 | 22.86 | 5407.1 | 2706 | 2643.3 | 3913.1 | 1219.8 | 0.67557 | 5.424
2024-12-10 | 1:43 | Data | 0 | 33.54 | 32.028 | 169.758 | 7.64 | 160.37 | 2210.77 | 25.78 | 45.998 | 6.41 | 1.291 | 4.115 | 8336.72 | 1.573 | 97.9 | 76.1 | 1437 | 23 | 5418.9 | 2712.2 | 2649.3 | 3915.2 | 1219.8 | 0.67534 | 5.406
2024-12-10 | 1:43 | Data | 0 | 33.642 | 31.853 | 169.712 | 7.64 | 160.415 | 2210.77 | 25.78 | 45.908 | 6.41 | 1.287 | 4.155 | 8332.2 | 1.573 | 97.9 | 76.4 | 1437 | 23 | 5415.9 | 2704 | 2639.6 | 3910.5 | 1219.8 | 0.67405 | 5.442
2024-12-10 | 1:43 | Data | 0 | 33.648 | 32.366 | 169.712 | 7.64 | 160.415 | 2212.58 | 25.78 | 45.998 | 6.4 | 1.286 | 4.136 | 8323.16 | 1.553 | 97.9 | 76.3 | 1438 | 23 | 5410.1 | 2701.7 | 2661.3 | 3919.7 | 1219.8 | 0.67247 | 5.422
2024-12-10 | 1:44 | Data | 0 | 33.642 | 32.123 | 169.622 | 7.63 | 160.37 | 2211.68 | 25.78 | 45.998 | 6.41 | 1.291 | 4.151 | 8332.2 | 1.661 | 97.9 | 76.3 | 1437 | 23 | 5415.9 | 2692.5 | 2640.5 | 3899.9 | 1219.8 | 0.67227 | 5.44
2024-12-10 | 1:44 | Data | 0 | 33.648 | 32.028 | 169.667 | 7.64 | 160.415 | 2210.77 | 25.77 | 45.998 | 6.4 | 1.284 | 4.155 | 8336.72 | 1.614 | 97.9 | 76.4 | 1438 | 23.04 | 5418.9 | 1617.7 | 2038.2 | 2614.7 | 1219.8 | 0.61625 | 5.439
2024-12-10 | 1:44 | Data | 0 | 33.412 | 32.19 | 169.984 | 7.64 | 160.37 | 2207.16 | 25.78 | 45.998 | 6.4 | 1.291 | 4.131 | 8323.16 | 1.539 | 97.9 | 76.2 | 1435 | 23 | 5410.1 | 1632.2 | 2037.3 | 2624.2 | 1219.8 | 0.61917 | 5.421
2024-12-10 | 1:44 | Data | 0 | 33.75 | 32.035 | 169.712 | 7.64 | 160.415 | 2211.68 | 25.78 | 45.908 | 6.41 | 1.292 | 4.149 | 8336.72 | 1.647 | 97.9 | 76.2 | 1438 | 22.95 | 5418.9 | 1631.8 | 2040.7 | 2628.5 | 1219.8 | 0.61844 | 5.441
2024-12-10 | 1:44 | Data | 0 | 33.925 | 31.947 | 169.893 | 7.64 | 160.505 | 2211.68 | 25.78 | 45.908 | 6.4 | 1.287 | 4.162 | 8345.77 | 1.614 | 97.9 | 76.4 | 1438 | 22.95 | 5424.8 | 1639.8 | 2046.5 | 2635.8 | 1219.8 | 0.61947 | 5.449
2024-12-10 | 1:44 | Data | 0 | 33.439 | 31.974 | 169.758 | 7.64 | 160.37 | 2211.68 | 25.78 | 45.908 | 6.4 | 1.299 | 4.148 | 8345.77 | 1.506 | 97.9 | 76.2 | 1438 | 23 | 5424.8 | 1620.6 | 2047.9 | 2625.3 | 1219.8 | 0.61399 | 5.448
2024-12-10 | 1:44 | Data | 0 | 33.642 | 32.231 | 169.712 | 7.64 | 160.324 | 2210.77 | 25.78 | 45.998 | 6.4 | 1.291 | 4.154 | 8350.29 | 1.634 | 97.9 | 76.3 | 1437 | 23 | 5427.7 | 1635.5 | 2046 | 2632.9 | 1219.8 | 0.61916 | 5.444
2024-12-10 | 1:44 | Data | 0 | 33.642 | 32.028 | 169.758 | 7.64 | 160.37 | 2210.77 | 25.78 | 45.998 | 6.41 | 1.292 | 4.146 | 8359.34 | 1.6 | 97.9 | 76.2 | 1437 | 23 | 5433.6 | 1619.2 | 2027.9 | 2608.9 | 1219.8 | 0.62283 | 5.438
2024-12-10 | 1:44 | Data | 0 | 33.615 | 32.001 | 169.712 | 7.63 | 160.37 | 2211.68 | 25.78 | 45.908 | 6.41 | 1.291 | 4.124 | 8345.77 | 1.83 | 97.9 | 76.2 | 1437 | 23 | 5424.8 | 1635.6 | 2046.2 | 2633.7 | 1219.8 | 0.6187 | 5.415
2024-12-10 | 1:44 | Data | 0 | 33.426 | 32.001 | 169.622 | 7.63 | 160.415 | 2210.77 | 25.76 | 45.998 | 6.41 | 1.293 | 4.127 | 8372.9 | 1.553 | 97.9 | 76.1 | 1436 | 23 | 5442.4 | 1630.7 | 2062.4 | 2642.7 | 1219.8 | 0.61475 | 5.422
2024-12-10 | 1:44 | Data | 0 | 33.419 | 32.123 | 169.848 | 7.63 | 160.46 | 2210.77 | 25.78 | 45.908 | 6.41 | 1.293 | 4.127 | 8377.43 | 1.607 | 97.9 | 76.1 | 1438 | 22.95 | 5445.3 | 1619.1 | 2058.7 | 2632.4 | 1219.8 | 0.61275 | 5.42
2024-12-10 | 1:44 | Data | 0 | 33.648 | 32.028 | 169.622 | 7.64 | 160.324 | 2210.77 | 25.76 | 45.998 | 6.41 | 1.291 | 4.126 | 8395.51 | 1.398 | 97.9 | 76.2 | 1437 | 23.04 | 5457.1 | 1626.4 | 2046.1 | 2626.5 | 1219.8 | 0.61739 | 5.418
2024-12-10 | 1:44 | Data | 0 | 33.696 | 31.812 | 169.848 | 7.64 | 160.415 | 2211.68 | 25.76 | 45.998 | 6.4 | 1.295 | 4.137 | 8404.56 | 1.823 | 97.9 | 76.2 | 1438 | 23 | 5463 | 1623 | 2024.3 | 2608.8 | 1219.9 | 0.61978 | 5.431
2024-12-10 | 1:44 | Data | 0 | 33.959 | 32.096 | 169.758 | 7.64 | 160.46 | 2210.77 | 25.77 | 45.998 | 6.41 | 1.292 | 4.159 | 8400.04 | 1.823 | 97.9 | 76.3 | 1437 | 23 | 5460 | 1638.8 | 2027.9 | 2624.8 | 1219.9 | 0.62084 | 5.451
2024-12-10 | 1:44 | Data | 0 | 33.844 | 32.028 | 169.667 | 7.64 | 160.37 | 2210.77 | 25.77 | 45.998 | 6.4 | 1.287 | 4.157 | 8418.13 | 1.661 | 97.9 | 76.3 | 1437 | 23 | 5471.8 | 1622.5 | 2016.1 | 2600.8 | 1219.9 | 0.62193 | 5.445
2024-12-10 | 1:44 | Data | 0 | 33.642 | 31.805 | 169.758 | 7.64 | 160.37 | 2210.77 | 25.76 | 45.998 | 6.41 | 1.29 | 4.14 | 8400.04 | 1.661 | 97.9 | 76.2 | 1437 | 23 | 5460 | 1630.3 | 2030.9 | 2609.2 | 1219.9 | 0.61873 | 5.43
2024-12-10 | 1:44 | Data | 0 | 33.709 | 31.832 | 169.712 | 7.64 | 160.37 | 2212.58 | 25.77 | 45.998 | 6.4 | 1.289 | 4.129 | 8400.04 | 1.506 | 97.9 | 76.2 | 1439 | 23 | 5460 | 1643.6 | 2043.8 | 2634.7 | 1219.9 | 0.62171 | 5.417
2024-12-10 | 1:45 | Data | 0 | 33.554 | 32.197 | 169.758 | 7.64 | 160.324 | 2213.49 | 25.76 | 45.908 | 6.4 | 1.292 | 4.129 | 8400.04 | 1.553 | 97.9 | 76.2 | 1439 | 22.95 | 5460 | 1614.2 | 2020.1 | 2599.3 | 1219.9 | 0.61764 | 5.421
2024-12-10 | 1:45 | Data | 0 | 33.669 | 32.028 | 169.712 | 7.64 | 160.279 | 2211.68 | 25.76 | 45.818 | 6.4 | 1.297 | 4.134 | 8400.04 | 1.614 | 97.9 | 76.1 | 1438 | 22.91 | 5460 | 1635.5 | 2008.5 | 2605.5 | 1219.9 | 0.62481 | 5.433
2024-12-10 | 1:45 | Data | 0 | 33.642 | 32.204 | 169.758 | 7.64 | 160.415 | 2210.77 | 25.76 | 45.727 | 6.4 | 1.285 | 4.124 | 8359.34 | 1.614 | 97.9 | 76.2 | 1437 | 22.86 | 5433.6 | 1622.8 | 2024.2 | 2608.6 | 1219.9 | 0.61943 | 5.409
2024-12-10 | 1:45 | Data | 0 | 33.574 | 32.258 | 169.893 | 7.63 | 160.46 | 2211.68 | 25.76 | 45.727 | 6.4 | 1.284 | 4.166 | 8359.34 | 1.6 | 97.9 | 76.4 | 1438 | 22.86 | 5433.6 | 1636.6 | 2022.3 | 2613.2 | 1219.9 | 0.62396 | 5.45
2024-12-10 | 1:45 | Data | 0 | 33.588 | 31.812 | 169.712 | 7.63 | 160.324 | 2213.49 | 25.77 | 45.727 | 6.41 | 1.273 | 4.163 | 8354.81 | 1.701 | 97.9 | 76.6 | 1438 | 22.86 | 5430.6 | 1623.5 | 2044 | 2624.4 | 1219.9 | 0.61673 | 5.437
2024-12-10 | 1:45 | Data | 0 | 33.426 | 31.974 | 169.938 | 7.64 | 160.46 | 2213.49 | 25.76 | 45.727 | 6.41 | 1.285 | 4.14 | 8372.9 | 1.614 | 97.9 | 76.3 | 1439 | 22.82 | 5442.4 | 1620.3 | 2039.8 | 2618.3 | 1219.9 | 0.6164 | 5.426
2024-12-10 | 1:45 | Data | 0 | 33.756 | 32.035 | 169.758 | 7.64 | 160.415 | 2214.39 | 25.76 | 45.727 | 6.41 | 1.286 | 4.143 | 8395.51 | 1.614 | 97.9 | 76.3 | 1439 | 22.86 | 5457.1 | 1636.9 | 2027.1 | 2621.9 | 1219.9 | 0.62095 | 5.43
2024-12-10 | 1:45 | Data | 0 | 33.412 | 31.913 | 169.667 | 7.64 | 160.37 | 2208.06 | 25.77 | 45.727 | 6.4 | 1.284 | 4.141 | 8400.04 | 1.614 | 97.9 | 76.3 | 1436 | 22.86 | 5460 | 1630.5 | 2053.2 | 2638 | 1219.9 | 0.61761 | 5.424
2024-12-10 | 1:45 | Data | 0 | 33.419 | 31.812 | 169.622 | 7.64 | 160.234 | 2214.39 | 25.77 | 45.637 | 6.4 | 1.292 | 4.138 | 8404.56 | 1.701 | 97.9 | 76.2 | 1439 | 22.86 | 5463 | 1625.3 | 2043.8 | 2632.9 | 1219.9 | 0.61306 | 5.43
2024-12-10 | 1:45 | Data | 0 | 33.588 | 31.799 | 169.667 | 7.64 | 160.324 | 2212.58 | 25.76 | 45.727 | 6.41 | 1.283 | 4.148 | 8418.13 | 1.816 | 97.9 | 76.4 | 1439 | 22.91 | 5471.8 | 1637.2 | 2050.6 | 2636.7 | 1219.9 | 0.61735 | 5.431
2024-12-10 | 1:45 | Data | 0 | 33.588 | 31.805 | 169.622 | 7.64 | 160.37 | 2208.97 | 25.77 | 45.637 | 6.4 | 1.29 | 4.133 | 8390.99 | 1.803 | 97.9 | 76.2 | 1436 | 22.82 | 5454.1 | 1629.1 | 2061.8 | 2641.2 | 1219.9 | 0.614 | 5.422
2024-12-10 | 1:45 | Data | 0 | 33.642 | 31.974 | 169.712 | 7.63 | 160.324 | 2213.49 | 25.77 | 45.727 | 6.41 | 1.291 | 4.118 | 8386.47 | 1.722 | 97.9 | 76.1 | 1439 | 22.86 | 5451.2 | 1627.4 | 2049.5 | 2629.4 | 1219.9 | 0.6161 | 5.407
2024-12-10 | 1:45 | Data | 0 | 33.446 | 31.805 | 169.622 | 7.64 | 160.37 | 2213.49 | 25.77 | 45.727 | 6.41 | 1.291 | 4.128 | 8372.9 | 1.593 | 97.9 | 76.2 | 1439 | 22.82 | 5442.4 | 1621.1 | 2040.2 | 2619.3 | 1219.9 | 0.61649 | 5.418
2024-12-10 | 1:45 | Data | 0 | 33.635 | 31.826 | 169.938 | 7.63 | 160.415 | 2210.77 | 25.76 | 45.727 | 6.4 | 1.28 | 4.134 | 8372.9 | 1.701 | 97.9 | 76.4 | 1437 | 22.86 | 5442.4 | 1631.1 | 2046.8 | 2631.2 | 1219.9 | 0.61724 | 5.412
2024-12-10 | 1:45 | Data | 0 | 33.864 | 32.035 | 169.758 | 7.64 | 160.415 | 2210.77 | 25.77 | 45.818 | 6.4 | 1.295 | 4.123 | 8372.9 | 1.654 | 97.9 | 76.1 | 1437 | 22.86 | 5442.4 | 1624 | 2031.2 | 2615.8 | 1219.9 | 0.61822 | 5.418
2024-12-10 | 1:45 | Data | 0 | 33.635 | 32.028 | 169.622 | 7.63 | 160.324 | 2211.68 | 25.76 | 45.727 | 6.4 | 1.293 | 4.145 | 8359.34 | 1.62 | 97.9 | 76.2 | 1438 | 22.82 | 5433.6 | 1622.2 | 2037.8 | 2619.1 | 1219.9 | 0.61634 | 5.439
2024-12-10 | 1:45 | Data | 0 | 33.615 | 31.799 | 169.712 | 7.63 | 160.46 | 2215.29 | 25.76 | 45.637 | 6.41 | 1.284 | 4.148 | 8363.86 | 1.823 | 97.9 | 76.4 | 1441 | 22.86 | 5436.5 | 1619.2 | 2039.1 | 2616.9 | 1219.9 | 0.61598 | 5.433
2024-12-10 | 1:45 | Data | 0 | 33.412 | 31.799 | 169.667 | 7.64 | 160.415 | 2210.77 | 25.76 | 45.727 | 6.4 | 1.292 | 4.124 | 8350.29 | 1.614 | 97.9 | 76.1 | 1438 | 22.86 | 5427.7 | 1636.7 | 2043 | 2629.8 | 1219.9 | 0.62049 | 5.417
2024-12-10 | 1:46 | Data | 0 | 33.554 | 31.805 | 169.893 | 7.63 | 160.505 | 2213.49 | 25.76 | 45.818 | 6.41 | 1.286 | 4.13 | 8341.25 | 1.627 | 97.9 | 76.3 | 1439 | 22.91 | 5421.8 | 1633.3 | 2054.9 | 2639 | 1219.9 | 0.61626 | 5.417
2024-12-10 | 1:46 | Data | 0 | 33.419 | 31.846 | 169.712 | 7.64 | 160.324 | 2213.49 | 25.76 | 45.998 | 6.4 | 1.284 | 4.13 | 8332.2 | 1.512 | 97.9 | 76.3 | 1439 | 23 | 5415.9 | 1628.6 | 2049.4 | 2630.4 | 1219.9 | 0.61658 | 5.415
2024-12-10 | 1:46 | Data | 0 | 33.655 | 32.015 | 169.622 | 7.64 | 160.279 | 2213.49 | 25.76 | 45.998 | 6.41 | 1.293 | 4.116 | 8314.11 | 1.715 | 97.9 | 76.1 | 1439 | 23 | 5404.2 | 1637.9 | 2036.4 | 2626.8 | 1219.9 | 0.62107 | 5.41
2024-12-10 | 1:46 | Data | 0 | 33.527 | 31.812 | 169.667 | 7.64 | 160.37 | 2213.49 | 25.76 | 45.998 | 6.4 | 1.292 | 4.14 | 8336.72 | 1.614 | 97.9 | 76.2 | 1439 | 23 | 5418.9 | 1624 | 2040.9 | 2621.4 | 1219.9 | 0.61611 | 5.432
2024-12-10 | 1:46 | Data | 0 | 33.642 | 31.826 | 169.848 | 7.64 | 160.37 | 2211.68 | 25.76 | 45.908 | 6.4 | 1.294 | 4.157 | 8332.2 | 1.789 | 97.9 | 76.3 | 1438 | 23 | 5415.9 | 1634.1 | 2047.1 | 2632.7 | 1219.9 | 0.61847 | 5.45
2024-12-10 | 1:46 | Data | 0 | 33.756 | 32.251 | 169.848 | 7.63 | 160.37 | 2216.2 | 25.76 | 45.998 | 6.41 | 1.292 | 4.143 | 8332.2 | 1.668 | 97.9 | 76.2 | 1441 | 23 | 5415.9 | 1635.9 | 2054.9 | 2642 | 1219.9 | 0.61943 | 5.436
2024-12-10 | 1:46 | Data | 0 | 33.392 | 31.812 | 169.758 | 7.64 | 160.279 | 2217.1 | 25.77 | 45.998 | 6.41 | 1.299 | 4.15 | 8332.2 | 1.715 | 97.9 | 76.2 | 1441 | 23 | 5415.9 | 1625.7 | 2028.1 | 2613 | 1219.9 | 0.62013 | 5.447
2024-12-10 | 1:46 | Data | 0 | 33.412 | 31.819 | 169.848 | 7.64 | 160.37 | 2217.1 | 25.76 | 45.998 | 6.4 | 1.293 | 4.155 | 8666.85 | 1.553 | 97.9 | 76.3 | 1441 | 22.95 | 5633.5 | 1627.7 | 2042.7 | 2625.7 | 1219.9 | 0.61818 | 5.449
2024-12-10 | 1:46 | Data | 0 | 33.527 | 31.805 | 169.758 | 7.64 | 160.37 | 2214.39 | 25.76 | 45.998 | 6.4 | 1.289 | 4.164 | 8427.17 | 1.647 | 97.9 | 76.4 | 1439 | 23 | 5477.7 | 1624.4 | 2018.6 | 2606.1 | 1219.9 | 0.62118 | 5.454
2024-12-10 | 1:46 | Data | 0 | 33.358 | 32.021 | 169.712 | 7.63 | 160.279 | 2214.39 | 25.77 | 45.998 | 6.41 | 1.294 | 4.131 | 8345.77 | 1.566 | 97.9 | 76.1 | 1439 | 22.95 | 5424.8 | 1639.6 | 2054.1 | 2642 | 1219.9 | 0.61943 | 5.425
2024-12-10 | 1:46 | Data | 0 | 33.372 | 31.785 | 169.622 | 7.64 | 160.279 | 2213.49 | 25.76 | 45.998 | 6.41 | 1.286 | 4.131 | 8350.29 | 1.62 | 97.9 | 76.3 | 1439 | 23 | 5427.7 | 1632.6 | 2058.2 | 2641 | 1219.9 | 0.61618 | 5.417
2024-12-10 | 1:46 | Data | 0 | 33.412 | 31.785 | 169.667 | 7.64 | 160.37 | 2213.49 | 25.76 | 45.998 | 6.41 | 1.293 | 4.137 | 8345.77 | 1.661 | 97.9 | 76.2 | 1439 | 23 | 5424.8 | 1630.4 | 2054.4 | 2635.6 | 1219.9 | 0.61235 | 5.43
2024-12-10 | 1:46 | Data | 0 | 33.412 | 31.974 | 169.712 | 7.64 | 160.279 | 2213.49 | 25.76 | 45.998 | 6.4 | 1.289 | 4.116 | 8341.25 | 1.499 | 97.9 | 76.2 | 1439 | 23 | 5421.8 | 1613.2 | 2063.7 | 2632.7 | 1219.9 | 0.6101 | 5.405
2024-12-10 | 1:46 | Data | 0 | 33.331 | 31.799 | 169.712 | 7.64 | 160.415 | 2213.49 | 25.76 | 45.908 | 6.41 | 1.284 | 4.103 | 8314.11 | 1.708 | 97.9 | 76.1 | 1439 | 23 | 5404.2 | 1640.4 | 2047.5 | 2637.5 | 1219.9 | 0.61811 | 5.388
2024-12-10 | 1:46 | Data | 0 | 33.527 | 32.136 | 169.758 | 7.63 | 160.37 | 2209.87 | 25.77 | 45.908 | 6.41 | 1.293 | 4.12 | 8323.16 | 1.553 | 97.9 | 76.1 | 1436 | 22.95 | 5410.1 | 1647 | 2093 | 2674.5 | 1219.9 | 0.61341 | 5.412
2024-12-10 | 1:46 | Data | 0 | 33.412 | 31.9 | 169.758 | 7.64 | 160.279 | 2215.29 | 25.76 | 45.998 | 6.41 | 1.296 | 4.125 | 8318.64 | 1.668 | 97.9 | 76.1 | 1440 | 23 | 5407.1 | 1630.1 | 2086.1 | 2660.1 | 1219.9 | 0.61016 | 5.422
2024-12-10 | 1:46 | Data | 0 | 33.311 | 31.758 | 169.712 | 7.63 | 160.279 | 2215.29 | 25.76 | 45.908 | 6.41 | 1.301 | 4.131 | 8309.59 | 1.735 | 97.9 | 76 | 1440 | 23 | 5401.2 | 1625.1 | 2056 | 2635 | 1219.9 | 0.61371 | 5.433
2024-12-10 | 1:46 | Data | 0 | 33.628 | 31.637 | 169.486 | 7.64 | 160.324 | 2217.1 | 25.75 | 45.908 | 6.41 | 1.288 | 4.138 | 8323.16 | 1.789 | 97.9 | 76.3 | 1441 | 22.95 | 5410.1 | 1622.8 | 2060.9 | 2639.4 | 1219.9 | 0.61254 | 5.426
2024-12-10 | 1:47 | Data | 0 | 33.534 | 32.028 | 169.667 | 7.64 | 160.415 | 2255.97 | 25.76 | 45.998 | 6.4 | 1.301 | 4.114 | 8305.07 | 1.776 | 98 | 76 | 1473 | 23 | 5398.3 | 1630.5 | 2058.3 | 2641.1 | 1219.9 | 0.61516 | 5.414
2024-12-10 | 1:47 | Data | 0 | 33.75 | 31.805 | 169.622 | 7.63 | 160.37 | 2293.93 | 25.77 | 45.998 | 6.4 | 1.297 | 4.142 | 8309.59 | 1.668 | 98 | 76.1 | 1483 | 22.95 | 5401.2 | 1640.7 | 2060.4 | 2645.4 | 1219.9 | 0.61853 | 5.44
2024-12-10 | 1:47 | Data | 0 | 33.635 | 31.826 | 169.531 | 7.64 | 160.324 | 2216.2 | 25.76 | 45.998 | 6.4 | 1.291 | 4.155 | 8296.02 | 1.614 | 97.9 | 76.3 | 1440 | 23 | 5392.4 | 1630.3 | 2055.9 | 2636.7 | 1219.9 | 0.61632 | 5.447
2024-12-10 | 1:47 | Data | 0 | 33.412 | 31.886 | 169.622 | 7.64 | 160.324 | 2216.2 | 25.77 | 45.998 | 6.4 | 1.288 | 4.156 | 8314.11 | 1.715 | 97.9 | 76.3 | 1441 | 23 | 5404.2 | 1639.9 | 2044.1 | 2633.2 | 1219.9 | 0.62034 | 5.444
2024-12-10 | 1:47 | Data | 0 | 33.203 | 31.913 | 169.622 | 7.64 | 160.279 | 2216.2 | 25.76 | 45.908 | 6.41 | 1.294 | 4.125 | 8300.55 | 1.56 | 97.9 | 76.1 | 1441 | 23 | 5395.4 | 2713.5 | 2630.4 | 3909 | 1219.9 | 0.67513 | 5.42
2024-12-10 | 1:47 | Data | 0 | 33.527 | 31.799 | 169.667 | 7.64 | 160.37 | 2217.1 | 25.77 | 45.998 | 6.41 | 1.294 | 4.101 | 8305.07 | 1.614 | 97.9 | 76 | 1441 | 23 | 5398.3 | 2721.5 | 2638.4 | 3918.8 | 1219.9 | 0.67734 | 5.394
2024-12-10 | 1:47 | Data | 0 | 33.412 | 32.015 | 169.667 | 7.64 | 160.234 | 2216.2 | 25.76 | 45.908 | 6.41 | 1.3 | 4.127 | 8305.07 | 1.398 | 97.9 | 76.1 | 1441 | 22.95 | 5398.3 | 2699.3 | 2648.6 | 3910.5 | 1219.9 | 0.67346 | 5.427
2024-12-10 | 1:47 | Data | 0 | 33.25 | 32.001 | 169.622 | 7.63 | 160.279 | 2210.77 | 25.76 | 45.998 | 6.41 | 1.294 | 4.137 | 8336.72 | 1.398 | 97.9 | 76.2 | 1437 | 22.95 | 5418.9 | 2719.9 | 2660.3 | 3933.6 | 1219.9 | 0.67347 | 5.431
2024-12-10 | 1:47 | Data | 0 | 33.297 | 32.231 | 169.531 | 7.63 | 160.234 | 2213.49 | 25.76 | 45.908 | 6.41 | 1.293 | 4.162 | 8332.2 | 1.533 | 97.9 | 76.3 | 1439 | 23 | 5415.9 | 2709.7 | 2673 | 3937.1 | 1219.9 | 0.67208 | 5.456
2024-12-10 | 1:47 | Data | 0 | 33.412 | 31.799 | 169.712 | 7.63 | 160.324 | 2216.2 | 25.77 | 45.908 | 6.41 | 1.294 | 4.134 | 8345.77 | 1.614 | 97.9 | 76.2 | 1441 | 23 | 5424.8 | 2711.5 | 2657.4 | 3920.8 | 1219.9 | 0.67474 | 5.429
2024-12-10 | 1:47 | Data | 0 | 33.412 | 32.001 | 169.848 | 7.64 | 160.37 | 2216.2 | 25.76 | 46.089 | 6.41 | 1.289 | 4.124 | 8350.29 | 1.614 | 97.9 | 76.2 | 1441 | 23 | 5427.7 | 2703.1 | 2649.3 | 3914.9 | 1219.9 | 0.67404 | 5.413
2024-12-10 | 1:47 | Data | 0 | 33.412 | 31.799 | 169.622 | 7.64 | 160.415 | 2216.2 | 25.76 | 46.089 | 6.41 | 1.279 | 4.139 | 8345.77 | 1.809 | 97.9 | 76.4 | 1441 | 23 | 5424.8 | 2706.3 | 2669.3 | 3929.1 | 1219.9 | 0.6717 | 5.418
2024-12-10 | 1:47 | Data | 0 | 33.412 | 31.799 | 169.622 | 7.64 | 160.234 | 2216.2 | 25.76 | 45.998 | 6.41 | 1.283 | 4.13 | 8332.2 | 1.614 | 97.9 | 76.3 | 1441 | 23 | 5415.9 | 2720.3 | 2647.5 | 3924.4 | 1219.9 | 0.67673 | 5.414
2024-12-10 | 1:47 | Data | 0 | 33.412 | 31.967 | 169.622 | 7.63 | 160.37 | 2216.2 | 25.76 | 45.908 | 6.4 | 1.29 | 4.137 | 8350.29 | 1.688 | 97.9 | 76.2 | 1441 | 22.95 | 5427.7 | 2726.7 | 2660.7 | 3936.6 | 1219.9 | 0.67595 | 5.427
2024-12-10 | 1:47 | Data | 0 | 33.527 | 31.92 | 169.758 | 7.64 | 160.415 | 2216.2 | 25.76 | 45.998 | 6.4 | 1.295 | 4.16 | 8345.77 | 1.546 | 97.9 | 76.3 | 1441 | 23 | 5424.8 | 2700.4 | 2662.2 | 3922.8 | 1219.9 | 0.67155 | 5.455
2024-12-10 | 1:47 | Data | 0 | 33.588 | 31.826 | 169.667 | 7.63 | 160.37 | 2216.2 | 25.77 | 45.998 | 6.41 | 1.29 | 4.16 | 8336.72 | 1.728 | 97.9 | 76.3 | 1441 | 23 | 5418.9 | 2706.2 | 2659.3 | 3923.5 | 1219.9 | 0.67348 | 5.45
2024-12-10 | 1:47 | Data | 0 | 33.412 | 31.799 | 169.712 | 7.64 | 160.37 | 2217.1 | 25.74 | 45.998 | 6.41 | 1.278 | 4.124 | 8323.16 | 1.789 | 97.9 | 76.3 | 1441 | 23 | 5410.1 | 2700.7 | 2649.4 | 3914.6 | 1220 | 0.67328 | 5.401
2024-12-10 | 1:48 | Data | 0 | 33.642 | 31.799 | 169.622 | 7.64 | 160.324 | 2217.1 | 25.75 | 45.908 | 6.4 | 1.282 | 4.126 | 8350.29 | 1.627 | 97.9 | 76.3 | 1441 | 22.95 | 5427.7 | 2701.5 | 2673 | 3932.9 | 1220 | 0.6703 | 5.409
2024-12-10 | 1:48 | Data | 0 | 33.419 | 31.799 | 169.622 | 7.63 | 160.324 | 2216.2 | 25.75 | 45.998 | 6.4 | 1.291 | 4.143 | 8323.16 | 1.614 | 97.9 | 76.2 | 1441 | 22.95 | 5410.1 | 2713.9 | 2656.3 | 3933 | 1220 | 0.67135 | 5.434
2024-12-10 | 1:48 | Data | 0 | 33.75 | 31.859 | 169.712 | 7.63 | 160.37 | 2215.29 | 25.75 | 45.998 | 6.41 | 1.284 | 4.128 | 8350.29 | 1.735 | 97.9 | 76.3 | 1441 | 23 | 5427.7 | 2713.8 | 2670.5 | 3930 | 1220 | 0.67499 | 5.412
2024-12-10 | 1:48 | Data | 0 | 33.412 | 31.778 | 169.712 | 7.63 | 160.324 | 2217.1 | 25.75 | 45.908 | 6.4 | 1.29 | 4.165 | 8336.72 | 1.634 | 97.9 | 76.4 | 1441 | 22.95 | 5418.9 | 2696 | 2657.8 | 3917.4 | 1220 | 0.66922 | 5.455
2024-12-10 | 1:48 | Data | 0 | 33.405 | 32.001 | 169.622 | 7.63 | 160.324 | 2216.2 | 25.74 | 45.998 | 6.4 | 1.301 | 4.162 | 8350.29 | 1.782 | 97.9 | 76.2 | 1441 | 22.95 | 5427.7 | 2691.4 | 2644.8 | 3905.5 | 1220 | 0.6729 | 5.463
2024-12-10 | 1:48 | Data | 0 | 33.412 | 32.143 | 169.758 | 7.64 | 160.415 | 2216.2 | 25.75 | 45.998 | 6.4 | 1.293 | 4.129 | 8345.77 | 1.56 | 97.9 | 76.1 | 1441 | 22.95 | 5424.8 | 2701.4 | 2652.3 | 3916.5 | 1220 | 0.67225 | 5.421
2024-12-10 | 1:48 | Data | 0 | 33.412 | 31.799 | 169.577 | 7.64 | 160.324 | 2217.1 | 25.74 | 46.089 | 6.4 | 1.297 | 4.133 | 8359.34 | 1.614 | 97.9 | 76.1 | 1441 | 23 | 5433.6 | 2700.9 | 2647.5 | 3909.4 | 1220 | 0.6737 | 5.428
2024-12-10 | 1:48 | Data | 0 | 33.736 | 31.812 | 169.622 | 7.63 | 160.324 | 2217.1 | 25.74 | 45.998 | 6.41 | 1.291 | 4.152 | 8354.81 | 1.843 | 97.9 | 76.3 | 1441 | 22.95 | 5430.6 | 2710.5 | 2655.3 | 3919.2 | 1220 | 0.67437 | 5.442
2024-12-10 | 1:48 | Data | 0 | 33.426 | 31.967 | 169.667 | 7.63 | 160.324 | 2216.2 | 25.75 | 45.998 | 6.41 | 1.29 | 4.141 | 8359.34 | 1.661 | 97.9 | 76.2 | 1441 | 22.95 | 5433.6 | 2704.1 | 2681.9 | 3933.2 | 1220 | 0.67012 | 5.431
2024-12-10 | 1:48 | Data | 0 | 33.75 | 32.028 | 169.622 | 7.64 | 160.37 | 2214.39 | 25.75 | 45.908 | 6.4 | 1.286 | 4.146 | 8359.34 | 1.641 | 97.9 | 76.3 | 1439 | 22.95 | 5433.6 | 2715 | 2663.8 | 3935.2 | 1220 | 0.673 | 5.431
2024-12-10 | 1:48 | Data | 0 | 33.27 | 31.805 | 169.712 | 7.64 | 160.415 | 2213.49 | 25.75 | 45.908 | 6.4 | 1.291 | 4.141 | 8359.34 | 1.398 | 97.9 | 76.2 | 1439 | 23 | 5433.6 | 2709.5 | 2662 | 3925 | 1220 | 0.67327 | 5.432
2024-12-10 | 1:48 | Data | 0 | 33.797 | 31.913 | 169.758 | 7.63 | 160.37 | 2216.2 | 25.75 | 45.908 | 6.41 | 1.295 | 4.131 | 8350.29 | 1.512 | 97.9 | 76.1 | 1441 | 22.95 | 5427.7 | 2711 | 2682.9 | 3944 | 1220 | 0.66957 | 5.425
2024-12-10 | 1:48 | Data | 0 | 33.432 | 31.907 | 169.667 | 7.63 | 160.324 | 2213.49 | 25.76 | 45.998 | 6.4 | 1.289 | 4.147 | 8363.86 | 1.593 | 97.9 | 76.3 | 1439 | 23 | 5436.5 | 2711 | 2666.1 | 3937.3 | 1220 | 0.67366 | 5.437
2024-12-10 | 1:48 | Data | 0 | 33.635 | 32.143 | 169.758 | 7.63 | 160.324 | 2217.1 | 25.77 | 45.908 | 6.41 | 1.289 | 4.167 | 8359.34 | 1.607 | 97.9 | 76.4 | 1441 | 23 | 5433.6 | 2702.6 | 2655.1 | 3915.7 | 1220 | 0.67474 | 5.455
2024-12-10 | 1:48 | Data | 0 | 33.412 | 31.799 | 169.667 | 7.64 | 160.324 | 2216.2 | 25.76 | 45.998 | 6.4 | 1.288 | 4.144 | 8372.9 | 1.789 | 97.9 | 76.3 | 1441 | 23 | 5442.4 | 2725 | 2657.9 | 3936 | 1220 | 0.67604 | 5.432
2024-12-10 | 1:48 | Data | 0 | 33.642 | 32.028 | 169.667 | 7.64 | 160.37 | 2114.97 | 25.77 | 45.998 | 6.41 | 1.287 | 4.143 | 8395.51 | 1.614 | 97.8 | 76.3 | 1375 | 23 | 5457.1 | 2706 | 2647.4 | 3911.6 | 1220 | 0.67478 | 5.43
2024-12-10 | 1:48 | Data | 0 | 33.412 | 31.974 | 169.758 | 7.64 | 160.324 | 2199.93 | 25.75 | 45.998 | 6.4 | 1.291 | 4.131 | 8377.43 | 1.614 | 97.9 | 76.2 | 1431 | 23 | 5445.3 | 2705.7 | 2667 | 3926.8 | 1220 | 0.67191 | 5.421
2024-12-10 | 1:48 | Data | 0 | 33.426 | 32.021 | 169.758 | 7.63 | 160.46 | 2214.39 | 25.77 | 45.998 | 6.41 | 1.299 | 4.115 | 8386.47 | 1.566 | 97.9 | 76 | 1439 | 22.95 | 5451.2 | 2694.3 | 2630.5 | 3893.3 | 1220 | 0.6758 | 5.412
2024-12-10 | 1:49 | Data | 0 | 33.473 | 31.63 | 169.577 | 7.64 | 160.37 | 2216.2 | 25.77 | 45.998 | 6.41 | 1.296 | 4.134 | 8400.04 | 1.789 | 97.9 | 76.1 | 1441 | 22.95 | 5460 | 2718 | 2636 | 3910.9 | 1220 | 0.67892 | 5.43
2024-12-10 | 1:49 | Data | 0 | 33.628 | 32.075 | 169.667 | 7.64 | 160.324 | 2213.49 | 25.76 | 45.998 | 6.4 | 1.286 | 4.146 | 8400.04 | 1.661 | 97.9 | 76.3 | 1439 | 23 | 5460 | 2707.9 | 2643.2 | 3910.7 | 1220 | 0.67452 | 5.431
2024-12-10 | 1:49 | Data | 0 | 33.446 | 31.812 | 169.848 | 7.64 | 160.46 | 2215.29 | 25.76 | 45.998 | 6.4 | 1.291 | 4.12 | 8400.04 | 1.6 | 97.9 | 76.1 | 1439 | 23 | 5460 | 2709.5 | 2658.2 | 3925.9 | 1220 | 0.67315 | 5.411
2024-12-10 | 1:49 | Data | 0 | 33.527 | 32.224 | 169.667 | 7.63 | 160.324 | 2214.39 | 25.76 | 45.998 | 6.4 | 1.302 | 4.129 | 8386.47 | 1.641 | 97.9 | 76 | 1439 | 23 | 5451.2 | 2706.4 | 2668.3 | 3929.2 | 1220 | 0.67248 | 5.431
2024-12-10 | 1:49 | Data | 0 | 33.783 | 32.089 | 169.848 | 7.64 | 160.37 | 2213.49 | 25.76 | 45.998 | 6.41 | 1.29 | 4.134 | 8332.2 | 1.809 | 97.9 | 76.2 | 1439 | 23 | 5415.9 | 2702.4 | 2655.7 | 3916.5 | 1220 | 0.67381 | 5.424
2024-12-10 | 1:49 | Data | 0 | 33.642 | 31.853 | 169.938 | 7.63 | 160.46 | 2214.39 | 25.77 | 45.998 | 6.4 | 1.291 | 4.126 | 8345.77 | 1.728 | 97.9 | 76.2 | 1439 | 23 | 5424.8 | 2703.7 | 2650.6 | 3912.5 | 1220 | 0.67307 | 5.418
2024-12-10 | 1:49 | Data | 0 | 33.419 | 31.994 | 169.712 | 7.64 | 160.37 | 2215.29 | 25.77 | 45.908 | 6.4 | 1.286 | 4.131 | 8314.11 | 1.445 | 97.9 | 76.3 | 1441 | 23 | 5404.2 | 2691.6 | 2661 | 3929.3 | 1220 | 0.67185 | 5.417
2024-12-10 | 1:49 | Data | 0 | 33.412 | 32.129 | 169.758 | 7.64 | 160.46 | 2216.2 | 25.76 | 45.908 | 6.41 | 1.294 | 4.152 | 8314.11 | 1.587 | 97.9 | 76.2 | 1441 | 22.91 | 5404.2 | 2708 | 2657.2 | 3919.8 | 1220 | 0.67362 | 5.448
2024-12-10 | 1:49 | Data | 0 | 33.453 | 31.974 | 169.667 | 7.63 | 160.37 | 2220.72 | 25.76 | 45.998 | 6.41 | 1.283 | 4.142 | 8359.34 | 1.418 | 97.9 | 76.3 | 1442 | 23 | 5433.6 | 2712.9 | 2658.1 | 3923.9 | 1220 | 0.6756 | 5.426
2024-12-10 | 1:49 | Data | 0 | 33.432 | 32.008 | 169.667 | 7.64 | 160.37 | 2218.91 | 25.76 | 45.998 | 6.41 | 1.282 | 4.134 | 8372.9 | 1.431 | 97.9 | 76.3 | 1443 | 23 | 5442.4 | 2710.2 | 2648.9 | 3918.2 | 1220 | 0.67446 | 5.419
2024-12-10 | 1:49 | Data | 0 | 33.864 | 32.082 | 169.758 | 7.63 | 160.415 | 2218.91 | 25.76 | 46.089 | 6.4 | 1.292 | 4.149 | 8372.9 | 1.614 | 97.9 | 76.3 | 1442 | 23 | 5442.4 | 2715.2 | 2671 | 3939.1 | 1220 | 0.67111 | 5.44
2024-12-10 | 1:49 | Data | 0 | 33.446 | 31.853 | 169.758 | 7.64 | 160.37 | 2224.33 | 25.76 | 45.998 | 6.4 | 1.289 | 4.134 | 8354.81 | 1.526 | 97.9 | 76.2 | 1446 | 23 | 5430.6 | 2705 | 2650.3 | 3917.9 | 1220 | 0.67348 | 5.423
2024-12-10 | 1:49 | Data | 0 | 33.75 | 31.866 | 169.758 | 7.64 | 160.46 | 2225.23 | 25.76 | 45.908 | 6.41 | 1.282 | 4.13 | 8350.29 | 1.62 | 97.9 | 76.3 | 1446 | 23 | 5427.7 | 2704 | 2658.6 | 3921.4 | 1220 | 0.67233 | 5.412
2024-12-10 | 1:49 | Data | 0 | 33.304 | 31.799 | 169.667 | 7.64 | 160.324 | 2215.29 | 25.77 | 45.998 | 6.41 | 1.285 | 4.107 | 8336.72 | 1.715 | 97.9 | 76.2 | 1441 | 23 | 5418.9 | 2709.1 | 2642 | 3914.1 | 1220 | 0.67541 | 5.392
2024-12-10 | 1:49 | Data | 0 | 33.419 | 31.839 | 169.622 | 7.64 | 160.37 | 2216.2 | 25.76 | 45.998 | 6.41 | 1.292 | 4.12 | 8336.72 | 1.445 | 97.9 | 76.1 | 1441 | 23 | 5418.9 | 2696.2 | 2642.9 | 3904.1 | 1220 | 0.67317 | 5.412
2024-12-10 | 1:49 | Data | 0 | 33.702 | 31.859 | 169.758 | 7.64 | 160.46 | 2216.2 | 25.76 | 45.998 | 6.41 | 1.285 | 4.129 | 8336.72 | 1.627 | 97.9 | 76.3 | 1441 | 23 | 5418.9 | 2698.1 | 2655.8 | 3919.3 | 1220 | 0.67241 | 5.414
2024-12-10 | 1:49 | Data | 0 | 33.628 | 31.826 | 169.667 | 7.64 | 160.415 | 2216.2 | 25.76 | 45.998 | 6.41 | 1.285 | 4.138 | 8350.29 | 1.735 | 97.9 | 76.3 | 1441 | 23 | 5427.7 | 2715.2 | 2674.1 | 3935.7 | 1220 | 0.67227 | 5.424
2024-12-10 | 1:49 | Data | 0 | 33.412 | 32.001 | 169.712 | 7.64 | 160.37 | 2214.39 | 25.76 | 45.998 | 6.4 | 1.284 | 4.131 | 8323.16 | 1.641 | 97.9 | 76.3 | 1439 | 23 | 5410.1 | 2712.6 | 2642.1 | 3920.3 | 1220 | 0.67495 | 5.415
2024-12-10 | 1:50 | Data | 0 | 33.662 | 32.028 | 169.893 | 7.63 | 160.46 | 2212.58 | 25.77 | 45.998 | 6.41 | 1.286 | 4.139 | 8345.77 | 1.627 | 97.9 | 76.3 | 1438 | 22.95 | 5424.8 | 2723 | 2677 | 3943 | 1220 | 0.67095 | 5.425
2024-12-10 | 1:50 | Data | 0 | 33.662 | 31.853 | 169.758 | 7.64 | 160.415 | 2212.58 | 25.77 | 45.908 | 6.41 | 1.291 | 4.155 | 8359.34 | 1.445 | 97.9 | 76.3 | 1439 | 22.91 | 5433.6 | 2691 | 2661.1 | 3911.5 | 1220 | 0.67193 | 5.447
2024-12-10 | 1:50 | Data | 0 | 33.412 | 31.799 | 169.712 | 7.64 | 160.324 | 2210.77 | 25.76 | 45.998 | 6.41 | 1.296 | 4.158 | 8318.64 | 1.789 | 97.9 | 76.2 | 1437 | 23.04 | 5407.1 | 2708.8 | 2638.1 | 3911.8 | 1220.1 | 0.67381 | 5.454
2024-12-10 | 1:50 | Data | 0 | 33.642 | 32.015 | 169.712 | 7.64 | 160.324 | 2211.68 | 25.76 | 45.998 | 6.4 | 1.29 | 4.152 | 8318.64 | 1.627 | 97.9 | 76.3 | 1438 | 22.95 | 5407.1 | 2705.7 | 2592.6 | 3874.2 | 1220.1 | 0.68428 | 5.441
2024-12-10 | 1:50 | Data | 0 | 33.696 | 31.832 | 169.758 | 7.64 | 160.46 | 2211.68 | 25.76 | 45.908 | 6.41 | 1.282 | 4.152 | 8318.64 | 1.782 | 97.9 | 76.4 | 1438 | 22.95 | 5407.1 | 2705.3 | 2651 | 3917.3 | 1220.1 | 0.67375 | 5.435
2024-12-10 | 1:50 | Data | 0 | 33.898 | 31.92 | 169.984 | 7.64 | 160.55 | 2210.77 | 25.76 | 45.998 | 6.4 | 1.286 | 4.155 | 8336.72 | 1.641 | 97.9 | 76.4 | 1437 | 22.95 | 5418.9 | 2707.8 | 2651.4 | 3908 | 1220.1 | 0.67173 | 5.44
2024-12-10 | 1:50 | Data | 0 | 33.466 | 31.805 | 169.848 | 7.64 | 160.324 | 2213.49 | 25.77 | 45.908 | 6.4 | 1.282 | 4.124 | 8345.77 | 1.614 | 97.9 | 76.3 | 1439 | 22.95 | 5424.8 | 2697 | 2652.2 | 3909 | 1220.1 | 0.6731 | 5.407
2024-12-10 | 1:50 | Data | 0 | 33.419 | 31.913 | 169.712 | 7.63 | 160.324 | 2210.77 | 25.76 | 45.727 | 6.4 | 1.288 | 4.134 | 8332.2 | 1.728 | 97.9 | 76.2 | 1437 | 22.86 | 5415.9 | 2702.9 | 2655.7 | 3917.9 | 1220.1 | 0.67616 | 5.422
2024-12-10 | 1:50 | Data | 0 | 33.588 | 31.913 | 169.667 | 7.64 | 160.324 | 2208.97 | 25.76 | 45.908 | 6.41 | 1.295 | 4.142 | 8336.72 | 1.607 | 97.9 | 76.2 | 1436 | 23 | 5418.9 | 2709.8 | 2649.8 | 3915.6 | 1220.1 | 0.67481 | 5.436
2024-12-10 | 1:50 | Data | 0 | 33.554 | 31.63 | 169.667 | 7.63 | 160.324 | 2208.97 | 25.76 | 45.998 | 6.4 | 1.302 | 4.142 | 8332.2 | 1.688 | 97.9 | 76.1 | 1435 | 22.95 | 5415.9 | 2704.2 | 2683.1 | 3938.8 | 1220.1 | 0.6689 | 5.444
2024-12-10 | 1:50 | Data | 0 | 33.628 | 31.913 | 169.893 | 7.64 | 160.46 | 2208.06 | 25.76 | 45.998 | 6.4 | 1.293 | 4.141 | 8345.77 | 1.782 | 97.9 | 76.2 | 1435 | 23 | 5424.8 | 2703.7 | 2661.9 | 3921.1 | 1220.1 | 0.67165 | 5.434
2024-12-10 | 1:50 | Data | 0 | 33.864 | 32.055 | 169.938 | 7.63 | 160.505 | 2199.02 | 25.76 | 45.998 | 6.41 | 1.287 | 4.167 | 8345.77 | 1.668 | 97.9 | 76.4 | 1430 | 23 | 5424.8 | 2704.1 | 2660 | 3919.2 | 1220.1 | 0.674 | 5.454
2024-12-10 | 1:50 | Data | 0 | 33.446 | 31.853 | 169.712 | 7.64 | 160.505 | 2205.35 | 25.77 | 45.998 | 6.4 | 1.286 | 4.139 | 8345.77 | 1.519 | 97.9 | 76.3 | 1433 | 22.95 | 5424.8 | 2705.3 | 2646.2 | 3917.6 | 1220.1 | 0.67263 | 5.424
2024-12-10 | 1:50 | Data | 0 | 33.615 | 32.001 | 169.712 | 7.63 | 160.415 | 2205.35 | 25.76 | 45.908 | 6.4 | 1.288 | 4.145 | 8341.25 | 1.519 | 97.9 | 76.3 | 1434 | 23 | 5421.8 | 2692.1 | 2673.9 | 3924.8 | 1220.1 | 0.66892 | 5.434
2024-12-10 | 1:50 | Data | 0 | 33.642 | 32.001 | 169.622 | 7.64 | 160.279 | 2203.54 | 25.76 | 45.998 | 6.4 | 1.293 | 4.168 | 8368.38 | 1.485 | 97.9 | 76.3 | 1432 | 23 | 5439.4 | 2713.6 | 2674.4 | 3941.8 | 1220.1 | 0.67047 | 5.462
2024-12-10 | 1:50 | Data | 0 | 33.669 | 32.028 | 169.758 | 7.64 | 160.37 | 2201.74 | 25.76 | 45.998 | 6.4 | 1.291 | 4.155 | 8377.43 | 1.533 | 97.9 | 76.3 | 1431 | 23 | 5445.3 | 2720.5 | 2662.8 | 3933.4 | 1220.1 | 0.67549 | 5.445
2024-12-10 | 1:50 | Data | 0 | 33.858 | 31.873 | 169.848 | 7.63 | 160.46 | 2204.45 | 25.76 | 45.908 | 6.4 | 1.282 | 4.13 | 8377.43 | 1.776 | 97.9 | 76.3 | 1433 | 23 | 5445.3 | 2708.1 | 2691.1 | 3943.5 | 1220.1 | 0.67106 | 5.411
2024-12-10 | 1:50 | Data | 0 | 33.426 | 31.913 | 169.758 | 7.64 | 160.46 | 2201.74 | 25.77 | 45.998 | 6.4 | 1.288 | 4.128 | 8377.43 | 1.614 | 97.9 | 76.2 | 1432 | 23 | 5445.3 | 2724 | 2669.1 | 3936 | 1220.1 | 0.67399 | 5.415
2024-12-10 | 1:51 | Data | 0 | 33.534 | 31.805 | 169.848 | 7.64 | 160.415 | 2203.54 | 25.76 | 45.908 | 6.41 | 1.284 | 4.131 | 8332.2 | 1.614 | 97.9 | 76.3 | 1432 | 22.95 | 5415.9 | 2698.1 | 2650.6 | 3913.1 | 1220.1 | 0.67177 | 5.414
2024-12-10 | 1:51 | Data | 0 | 33.486 | 31.974 | 169.984 | 7.63 | 160.505 | 2205.35 | 25.76 | 45.998 | 6.4 | 1.282 | 4.13 | 8350.29 | 1.627 | 97.9 | 76.3 | 1433 | 23 | 5427.7 | 2706 | 2636 | 3906.9 | 1220.1 | 0.67541 | 5.412
2024-12-10 | 1:51 | Data | 0 | 33.642 | 31.974 | 169.848 | 7.63 | 160.415 | 2206.25 | 25.76 | 45.908 | 6.41 | 1.277 | 4.112 | 8345.77 | 1.668 | 97.9 | 76.3 | 1434 | 23 | 5424.8 | 2684.9 | 2656 | 3911.3 | 1220.1 | 0.66831 | 5.389
2024-12-10 | 1:51 | Data | 0 | 33.642 | 31.826 | 169.758 | 7.64 | 160.505 | 2205.35 | 25.76 | 45.998 | 6.4 | 1.284 | 4.12 | 8354.81 | 1.674 | 97.9 | 76.2 | 1434 | 22.95 | 5430.6 | 2697.7 | 2661.2 | 3921.4 | 1220.1 | 0.67035 | 5.404
2024-12-10 | 1:51 | Data | 0 | 33.439 | 31.974 | 169.667 | 7.64 | 160.37 | 2205.35 | 25.76 | 45.998 | 6.4 | 1.291 | 4.144 | 8345.77 | 1.722 | 97.9 | 76.2 | 1434 | 23 | 5424.8 | 2708.9 | 2668.8 | 3929.9 | 1220.1 | 0.67229 | 5.436
2024-12-10 | 1:51 | Data | 0 | 33.642 | 31.913 | 169.667 | 7.64 | 160.37 | 2206.25 | 25.76 | 45.908 | 6.4 | 1.294 | 4.14 | 8341.25 | 1.614 | 97.9 | 76.2 | 1433 | 23 | 5421.8 | 2698.6 | 2654.6 | 3913.7 | 1220.1 | 0.67319 | 5.433
2024-12-10 | 1:51 | Data | 0 | 33.918 | 32.042 | 169.893 | 7.64 | 160.596 | 2201.74 | 25.76 | 45.908 | 6.4 | 1.285 | 4.142 | 8345.77 | 1.519 | 97.9 | 76.3 | 1431 | 23 | 5424.8 | 2708.2 | 2665.5 | 3925.1 | 1220.1 | 0.67261 | 5.427
2024-12-10 | 1:51 | Data | 0 | 33.561 | 31.718 | 169.758 | 7.63 | 160.46 | 2197.22 | 25.76 | 45.998 | 6.4 | 1.287 | 4.153 | 8363.86 | 1.485 | 97.9 | 76.3 | 1429 | 22.95 | 5436.5 | 2694.2 | 2652.2 | 3910.6 | 1220.1 | 0.67116 | 5.441
2024-12-10 | 1:51 | Data | 0 | 33.736 | 31.859 | 169.758 | 7.64 | 160.37 | 2206.25 | 25.77 | 45.908 | 6.4 | 1.296 | 4.151 | 8350.29 | 1.647 | 97.9 | 76.2 | 1434 | 23 | 5427.7 | 2710.1 | 2659.6 | 3922.6 | 1220.1 | 0.67157 | 5.448
2024-12-10 | 1:51 | Data | 0 | 33.554 | 32.001 | 169.848 | 7.64 | 160.415 | 2205.35 | 25.76 | 45.998 | 6.41 | 1.288 | 4.125 | 8363.86 | 1.458 | 97.9 | 76.2 | 1434 | 23 | 5436.5 | 2716 | 2657.8 | 3928.6 | 1220.1 | 0.67351 | 5.412
2024-12-10 | 1:51 | Data | 0 | 33.642 | 31.812 | 169.848 | 7.64 | 160.415 | 2206.25 | 25.77 | 45.908 | 6.41 | 1.295 | 4.124 | 8345.77 | 1.789 | 97.9 | 76.1 | 1434 | 22.95 | 5424.8 | 2693.3 | 2654.5 | 3914.6 | 1220.1 | 0.67038 | 5.419
2024-12-10 | 1:51 | Data | 0 | 33.669 | 31.805 | 169.758 | 7.64 | 160.415 | 2206.25 | 25.76 | 45.998 | 6.41 | 1.291 | 4.134 | 8363.86 | 1.634 | 97.9 | 76.2 | 1433 | 23 | 5436.5 | 2704.9 | 2664.3 | 3925.7 | 1220.1 | 0.67146 | 5.424
2024-12-10 | 1:51 | Data | 0 | 33.642 | 32.028 | 169.848 | 7.64 | 160.415 | 2205.35 | 25.77 | 45.998 | 6.41 | 1.28 | 4.163 | 8386.47 | 1.614 | 97.9 | 76.5 | 1433 | 23 | 5451.2 | 2701.7 | 2667.5 | 3924.9 | 1220.1 | 0.67126 | 5.444
2024-12-10 | 1:51 | Data | 0 | 33.858 | 32.035 | 169.893 | 7.64 | 160.505 | 2206.25 | 25.75 | 45.998 | 6.4 | 1.291 | 4.176 | 8372.9 | 1.715 | 97.9 | 76.4 | 1434 | 23 | 5442.4 | 2713.9 | 2670.4 | 3932.1 | 1220.1 | 0.67288 | 5.466
2024-12-10 | 1:51 | Data | 0 | 33.642 | 32.231 | 169.758 | 7.64 | 160.415 | 2206.25 | 25.77 | 45.998 | 6.4 | 1.278 | 4.143 | 8372.9 | 1.452 | 97.9 | 76.4 | 1433 | 23 | 5442.4 | 2691.2 | 2678.4 | 3933.9 | 1220.1 | 0.67007 | 5.42
2024-12-10 | 1:51 | Data | 0 | 33.446 | 31.805 | 169.848 | 7.64 | 160.46 | 2206.25 | 25.76 | 45.908 | 6.4 | 1.293 | 4.143 | 8390.99 | 1.62 | 97.9 | 76.2 | 1434 | 22.95 | 5454.1 | 2717 | 2677.5 | 3940.7 | 1220.1 | 0.67179 | 5.436
2024-12-10 | 1:51 | Data | 0 | 33.534 | 32.109 | 169.758 | 7.64 | 160.46 | 2207.16 | 25.77 | 45.908 | 6.4 | 1.287 | 4.163 | 8345.77 | 1.472 | 97.9 | 76.4 | 1435 | 22.95 | 5424.8 | 2700.3 | 2663.5 | 3924.8 | 1220.1 | 0.6699 | 5.451
2024-12-10 | 1:52 | Data | 0 | 33.628 | 32.231 | 169.758 | 7.64 | 160.415 | 2213.49 | 25.76 | 45.998 | 6.4 | 1.285 | 4.151 | 8345.77 | 1.614 | 97.9 | 76.4 | 1439 | 22.95 | 5424.8 | 2718 | 2672 | 3928.3 | 1220.1 | 0.67033 | 5.436
2024-12-10 | 1:52 | Data | 0 | 33.615 | 31.927 | 169.712 | 7.64 | 160.415 | 2214.39 | 25.76 | 45.998 | 6.4 | 1.3 | 4.156 | 8350.29 | 1.897 | 97.9 | 76.2 | 1439 | 23 | 5427.7 | 2707.1 | 2678.3 | 3934.8 | 1220.1 | 0.6716 | 5.456
2024-12-10 | 1:52 | Data | 0 | 33.642 | 32.028 | 169.712 | 7.64 | 160.37 | 2210.77 | 25.76 | 45.818 | 6.4 | 1.3 | 4.151 | 8345.77 | 1.614 | 97.9 | 76.2 | 1436 | 22.86 | 5424.8 | 2709.4 | 2667.4 | 3927.5 | 1220.1 | 0.67471 | 5.45
2024-12-10 | 1:52 | Data | 0 | 33.527 | 32.075 | 169.758 | 7.64 | 160.46 | 2210.77 | 25.76 | 45.637 | 6.41 | 1.295 | 4.147 | 8345.77 | 1.614 | 97.9 | 76.2 | 1437 | 22.86 | 5424.8 | 2708.1 | 2656.9 | 3918.2 | 1220.1 | 0.6695 | 5.442
2024-12-10 | 1:52 | Data | 0 | 33.642 | 32.015 | 169.758 | 7.64 | 160.415 | 2208.97 | 25.77 | 45.637 | 6.41 | 1.297 | 4.142 | 8332.2 | 1.668 | 97.9 | 76.2 | 1436 | 22.86 | 5415.9 | 2698 | 2655.8 | 3918 | 1220.1 | 0.67042 | 5.439
2024-12-10 | 1:52 | Data | 0 | 33.817 | 32.082 | 169.893 | 7.64 | 160.415 | 2208.06 | 25.77 | 45.727 | 6.4 | 1.285 | 4.161 | 8363.86 | 1.715 | 97.9 | 76.4 | 1435 | 22.86 | 5436.5 | 2702.4 | 2661.8 | 3920.4 | 1220.1 | 0.66944 | 5.446
2024-12-10 | 1:52 | Data | 0 | 33.419 | 32.129 | 169.893 | 7.64 | 160.37 | 2208.97 | 25.76 | 45.727 | 6.4 | 1.284 | 4.145 | 8350.29 | 1.56 | 97.9 | 76.3 | 1435 | 22.86 | 5427.7 | 2704.1 | 2651.1 | 3919.4 | 1220.1 | 0.67161 | 5.43
2024-12-10 | 1:52 | Data | 0 | 33.48 | 31.974 | 169.848 | 7.64 | 160.415 | 2208.97 | 25.75 | 45.727 | 6.4 | 1.28 | 4.144 | 8359.34 | 1.614 | 97.9 | 76.4 | 1436 | 22.86 | 5433.6 | 2704.5 | 2659.3 | 3918.8 | 1220.2 | 0.67222 | 5.424
2024-12-10 | 1:52 | Data | 0 | 33.446 | 32.197 | 169.984 | 7.64 | 160.505 | 2208.06 | 25.76 | 45.727 | 6.4 | 1.282 | 4.146 | 8363.86 | 1.445 | 97.9 | 76.4 | 1436 | 22.86 | 5436.5 | 2704 | 2645.9 | 3911.6 | 1220.2 | 0.67269 | 5.428
2024-12-10 | 1:52 | Data | 0 | 33.696 | 31.805 | 169.893 | 7.63 | 160.415 | 2211.68 | 25.76 | 45.727 | 6.41 | 1.284 | 4.145 | 8363.86 | 1.641 | 97.9 | 76.3 | 1438 | 22.86 | 5436.5 | 2704.1 | 2660.1 | 3922.8 | 1220.2 | 0.67186 | 5.43
2024-12-10 | 1:52 | Data | 0 | 33.844 | 32.258 | 169.893 | 7.64 | 160.505 | 2203.54 | 25.76 | 45.727 | 6.4 | 1.287 | 4.138 | 8359.34 | 1.627 | 97.9 | 76.3 | 1432 | 22.86 | 5433.6 | 2707 | 2652.8 | 3918.8 | 1220.2 | 0.67361 | 5.426
2024-12-10 | 1:52 | Data | 0 | 33.419 | 31.92 | 169.848 | 7.64 | 160.37 | 2207.16 | 25.77 | 45.637 | 6.4 | 1.291 | 4.128 | 8354.81 | 1.499 | 97.9 | 76.2 | 1435 | 22.86 | 5430.6 | 2712.4 | 2660.6 | 3926.6 | 1220.2 | 0.67236 | 5.419
2024-12-10 | 1:52 | Data | 0 | 33.858 | 32.204 | 169.893 | 7.64 | 160.46 | 2210.77 | 25.76 | 45.637 | 6.4 | 1.291 | 4.134 | 8345.77 | 1.83 | 97.9 | 76.2 | 1437 | 22.82 | 5424.8 | 2716.9 | 2659.8 | 3930.5 | 1220.2 | 0.67281 | 5.425
2024-12-10 | 1:52 | Data | 0 | 33.912 | 32.042 | 169.893 | 7.64 | 160.505 | 2213.49 | 25.76 | 45.727 | 6.4 | 1.284 | 4.134 | 8345.77 | 1.749 | 97.9 | 76.3 | 1439 | 22.86 | 5424.8 | 2713.5 | 2687.8 | 3945.9 | 1220.2 | 0.67122 | 5.417
2024-12-10 | 1:52 | Data | 0 | 33.642 | 32.028 | 169.893 | 7.63 | 160.46 | 2213.49 | 25.77 | 45.727 | 6.4 | 1.284 | 4.141 | 8336.72 | 1.614 | 97.9 | 76.3 | 1439 | 22.86 | 5418.9 | 2712.4 | 2665.5 | 3930.6 | 1220.2 | 0.67161 | 5.424
2024-12-10 | 1:52 | Data | 0 | 33.871 | 32.089 | 169.893 | 7.64 | 160.505 | 2213.49 | 25.76 | 45.727 | 6.4 | 1.283 | 4.126 | 8314.11 | 1.607 | 97.9 | 76.3 | 1439 | 22.86 | 5404.2 | 2712.3 | 2669.2 | 3933.7 | 1220.2 | 0.67193 | 5.41
2024-12-10 | 1:52 | Data | 0 | 33.864 | 32.143 | 169.938 | 7.64 | 160.505 | 2216.2 | 25.76 | 45.727 | 6.41 | 1.291 | 4.134 | 8314.11 | 1.695 | 97.9 | 76.2 | 1441 | 22.82 | 5404.2 | 2711.4 | 2674.9 | 3935.5 | 1220.2 | 0.67037 | 5.424
2024-12-10 | 1:52 | Data | 0 | 33.588 | 32.251 | 169.848 | 7.64 | 160.415 | 2214.39 | 25.77 | 45.727 | 6.4 | 1.276 | 4.138 | 8323.16 | 1.593 | 97.9 | 76.4 | 1439 | 22.82 | 5410.1 | 2716.8 | 2672 | 3936.4 | 1220.2 | 0.67342 | 5.414
2024-12-10 | 1:53 | Data | 0 | 33.696 | 32.042 | 169.712 | 7.64 | 160.415 | 2213.49 | 25.77 | 45.727 | 6.4 | 1.287 | 4.124 | 8336.72 | 1.573 | 97.9 | 76.2 | 1439 | 22.86 | 5418.9 | 2704.2 | 2651.4 | 3915 | 1220.2 | 0.67344 | 5.411
2024-12-10 | 1:53 | Data | 0 | 33.669 | 31.805 | 169.848 | 7.63 | 160.415 | 2211.68 | 25.76 | 45.637 | 6.4 | 1.285 | 4.145 | 8372.9 | 1.641 | 97.9 | 76.3 | 1437 | 22.82 | 5442.4 | 2709.1 | 2659.9 | 3919 | 1220.2 | 0.67296 | 5.43
2024-12-10 | 1:53 | Data | 0 | 33.756 | 32.251 | 169.667 | 7.64 | 160.324 | 2211.68 | 25.76 | 45.637 | 6.4 | 1.288 | 4.159 | 8372.9 | 1.62 | 97.9 | 76.4 | 1438 | 22.86 | 5442.4 | 2704.6 | 2664.3 | 3926.4 | 1220.2 | 0.67232 | 5.447
2024-12-10 | 1:53 | Data | 0 | 33.486 | 32.008 | 169.486 | 7.64 | 160.189 | 2208.97 | 25.76 | 45.908 | 6.4 | 1.286 | 4.181 | 8372.9 | 1.56 | 97.9 | 76.5 | 1436 | 22.95 | 5442.4 | 2718.1 | 2693.2 | 3954.8 | 1220.2 | 0.66908 | 5.468
2024-12-10 | 1:53 | Data | 0 | 33.642 | 32.204 | 169.577 | 7.64 | 160.234 | 2208.97 | 25.76 | 45.818 | 6.41 | 1.288 | 4.156 | 8372.9 | 1.553 | 97.9 | 76.3 | 1435 | 22.91 | 5442.4 | 2724.4 | 2681.2 | 3947.4 | 1220.2 | 0.67214 | 5.444
2024-12-10 | 1:53 | Data | 0 | 33.527 | 32.028 | 169.486 | 7.64 | 160.189 | 2209.87 | 25.76 | 45.998 | 6.4 | 1.296 | 4.134 | 8345.77 | 1.6 | 97.9 | 76.1 | 1436 | 23 | 5424.8 | 2709.7 | 2681.4 | 3945 | 1220.2 | 0.67224 | 5.43
2024-12-10 | 1:53 | Data | 0 | 33.48 | 32.028 | 169.667 | 7.64 | 160.189 | 2211.68 | 25.77 | 45.998 | 6.4 | 1.3 | 4.124 | 8345.77 | 1.573 | 97.9 | 76 | 1437 | 23 | 5424.8 | 2717.6 | 2716.5 | 3962.2 | 1220.2 | 0.66813 | 5.425
2024-12-10 | 1:53 | Data | 0 | 33.412 | 32.021 | 169.396 | 7.64 | 160.099 | 2211.68 | 25.75 | 45.998 | 6.41 | 1.288 | 4.115 | 8309.59 | 1.553 | 97.9 | 76.2 | 1438 | 23 | 5401.2 | 2711.7 | 2688.3 | 3940.9 | 1220.2 | 0.66999 | 5.403
2024-12-10 | 1:53 | Data | 0 | 33.642 | 31.92 | 169.441 | 7.64 | 160.144 | 2213.49 | 25.76 | 45.998 | 6.4 | 1.282 | 4.152 | 8318.64 | 1.83 | 97.9 | 76.4 | 1439 | 23 | 5407.1 | 2692.7 | 2696.1 | 3942.8 | 1220.2 | 0.66334 | 5.432
2024-12-10 | 1:53 | Data | 0 | 33.642 | 32.204 | 169.577 | 7.64 | 160.099 | 2213.49 | 25.76 | 45.908 | 6.4 | 1.285 | 4.133 | 8350.29 | 1.728 | 97.9 | 76.3 | 1439 | 23 | 5427.7 | 2701.2 | 2675.3 | 3923 | 1220.2 | 0.66588 | 5.418
2024-12-10 | 1:53 | Data | 0 | 33.655 | 32.028 | 169.486 | 7.63 | 160.189 | 2213.49 | 25.76 | 46.089 | 6.4 | 1.297 | 4.125 | 8350.29 | 1.62 | 97.9 | 76.1 | 1439 | 23 | 5427.7 | 2705.7 | 2690.7 | 3941.1 | 1220.2 | 0.66766 | 5.422
2024-12-10 | 1:53 | Data | 0 | 33.696 | 32.028 | 169.486 | 7.64 | 160.279 | 2216.2 | 25.76 | 45.998 | 6.41 | 1.283 | 4.143 | 8345.77 | 1.533 | 97.9 | 76.3 | 1441 | 23 | 5424.8 | 2702.1 | 2667.1 | 3924.3 | 1220.2 | 0.66998 | 5.426
2024-12-10 | 1:53 | Data | 0 | 33.642 | 32.075 | 169.441 | 7.64 | 160.144 | 2216.2 | 25.76 | 45.998 | 6.4 | 1.284 | 4.149 | 8345.77 | 1.438 | 97.9 | 76.3 | 1441 | 23 | 5424.8 | 2705.9 | 2666.8 | 3926.6 | 1220.2 | 0.67196 | 5.434
2024-12-10 | 1:53 | Data | 0 | 33.648 | 32.136 | 169.577 | 7.64 | 160.234 | 2216.2 | 25.77 | 45.998 | 6.4 | 1.294 | 4.147 | 8318.64 | 1.526 | 97.9 | 76.2 | 1441 | 23 | 5407.1 | 2713.2 | 2685.9 | 3946.7 | 1220.2 | 0.66869 | 5.441
2024-12-10 | 1:53 | Data | 0 | 33.486 | 31.988 | 169.531 | 7.63 | 160.234 | 2215.29 | 25.76 | 45.998 | 6.4 | 1.297 | 4.14 | 8341.25 | 1.526 | 97.9 | 76.1 | 1440 | 22.95 | 5421.8 | 2707 | 2671.2 | 3931.8 | 1220.2 | 0.67031 | 5.437
2024-12-10 | 1:53 | Data | 0 | 33.696 | 32.028 | 169.486 | 7.63 | 160.189 | 2210.77 | 25.76 | 45.998 | 6.4 | 1.291 | 4.145 | 8314.11 | 1.614 | 97.9 | 76.3 | 1437 | 23 | 5404.2 | 2717.7 | 2674.8 | 3939.1 | 1220.2 | 0.67252 | 5.436
2024-12-10 | 1:53 | Data | 0 | 33.925 | 32.096 | 169.531 | 7.64 | 160.234 | 2207.16 | 25.76 | 45.998 | 6.41 | 1.288 | 4.126 | 8332.2 | 1.614 | 97.9 | 76.2 | 1435 | 23 | 5415.9 | 2701.7 | 2697.2 | 3942.6 | 1220.2 | 0.66751 | 5.414
2024-12-10 | 1:53 | Data | 0 | 33.871 | 32.035 | 169.531 | 7.63 | 160.144 | 2208.06 | 25.75 | 45.998 | 6.41 | 1.282 | 4.136 | 8345.77 | 1.641 | 97.9 | 76.3 | 1435 | 22.95 | 5424.8 | 2703.9 | 2725.9 | 3969.4 | 1220.2 | 0.66241 | 5.42
2024-12-10 | 1:54 | Data | 0 | 33.756 | 32.028 | 169.577 | 7.64 | 160.234 | 2206.25 | 25.76 | 45.908 | 6.4 | 1.273 | 4.139 | 8350.29 | 1.62 | 97.9 | 76.5 | 1434 | 22.95 | 5427.7 | 2709.5 | 2680.3 | 3940.9 | 1220.2 | 0.66744 | 5.412
2024-12-10 | 1:54 | Data | 0 | 33.588 | 32.089 | 169.577 | 7.63 | 160.189 | 2208.06 | 25.76 | 45.998 | 6.4 | 1.288 | 4.152 | 8350.29 | 1.701 | 97.9 | 76.3 | 1435 | 22.95 | 5427.7 | 2737.9 | 2697.6 | 3972.9 | 1220.2 | 0.66848 | 5.439
2024-12-10 | 1:54 | Data | 0 | 33.473 | 31.812 | 169.577 | 7.64 | 160.189 | 2207.16 | 25.76 | 45.998 | 6.41 | 1.291 | 4.13 | 8350.29 | 1.6 | 97.9 | 76.2 | 1435 | 22.95 | 5427.7 | 2732.2 | 2701.6 | 3971.2 | 1220.2 | 0.66883 | 5.42
2024-12-10 | 1:54 | Data | 0 | 33.979 | 31.94 | 169.531 | 7.64 | 160.189 | 2208.97 | 25.77 | 45.908 | 6.41 | 1.291 | 4.145 | 8368.38 | 1.573 | 97.9 | 76.2 | 1435 | 22.95 | 5439.4 | 2725.7 | 2681.6 | 3953.7 | 1220.2 | 0.67067 | 5.436
2024-12-10 | 1:54 | Data | 0 | 33.648 | 32.028 | 169.577 | 7.64 | 160.234 | 2208.97 | 25.76 | 46.089 | 6.4 | 1.287 | 4.132 | 8359.34 | 1.62 | 97.9 | 76.2 | 1435 | 23 | 5433.6 | 2716.9 | 2679.1 | 3942.7 | 1220.2 | 0.67121 | 5.42
2024-12-10 | 1:54 | Data | 0 | 33.743 | 32.143 | 169.577 | 7.64 | 160.234 | 2214.39 | 25.76 | 45.998 | 6.4 | 1.289 | 4.101 | 8354.81 | 1.701 | 97.9 | 76.1 | 1439 | 23 | 5430.6 | 2722.1 | 2699.5 | 3961.6 | 1220.2 | 0.66836 | 5.388
2024-12-10 | 1:54 | Data | 0 | 33.642 | 32.237 | 169.531 | 7.63 | 160.234 | 2214.39 | 25.75 | 45.998 | 6.4 | 1.288 | 4.122 | 8359.34 | 1.404 | 97.9 | 76.2 | 1439 | 23 | 5433.6 | 2718.9 | 2692.5 | 3956.3 | 1220.2 | 0.671 | 5.41
2024-12-10 | 1:54 | Data | 0 | 33.817 | 32.048 | 169.667 | 7.63 | 160.279 | 2211.68 | 25.77 | 45.998 | 6.4 | 1.29 | 4.124 | 8354.81 | 1.668 | 97.9 | 76.2 | 1438 | 23 | 5430.6 | 2740.6 | 2679.6 | 3962.1 | 1220.2 | 0.6746 | 5.413
2024-12-10 | 1:54 | Data | 0 | 33.486 | 32.015 | 169.441 | 7.63 | 160.189 | 2211.68 | 25.77 | 43.741 | 6.41 | 1.288 | 4.133 | 8345.77 | 1.445 | 98 | 76.2 | 1437 | 21.92 | 5424.8 | 2727.5 | 2679.6 | 3952 | 1220.2 | 0.67133 | 5.42
2024-12-10 | 1:54 | Data | 0 | 33.675 | 32.21 | 169.486 | 7.64 | 160.234 | 2208.06 | 25.76 | 45.998 | 6.4 | 1.294 | 4.122 | 8354.81 | 1.438 | 97.9 | 76.1 | 1435 | 22.95 | 5430.6 | 2763.1 | 2676.3 | 3983.9 | 1220.2 | 0.675 | 5.416
2024-12-10 | 1:54 | Data | 0 | 33.642 | 31.988 | 169.486 | 7.64 | 160.234 | 2208.06 | 25.76 | 45.998 | 6.4 | 1.287 | 4.13 | 8354.81 | 1.695 | 97.9 | 76.2 | 1436 | 23 | 5430.6 | 2732.5 | 2675.6 | 3954.5 | 1220.3 | 0.67223 | 5.416
2024-12-10 | 1:54 | Data | 0 | 33.594 | 31.988 | 169.531 | 7.63 | 160.234 | 2208.97 | 25.76 | 45.998 | 6.41 | 1.288 | 4.13 | 8354.81 | 1.782 | 97.9 | 76.2 | 1436 | 23 | 5430.6 | 2733 | 2692.4 | 3968.1 | 1220.3 | 0.66931 | 5.418
2024-12-10 | 1:54 | Data | 0 | 33.642 | 31.826 | 169.486 | 7.64 | 160.144 | 2208.97 | 25.76 | 45.998 | 6.41 | 1.29 | 4.123 | 8368.38 | 1.728 | 97.9 | 76.2 | 1435 | 23 | 5439.4 | 2712.3 | 2711 | 3970.7 | 1220.3 | 0.66374 | 5.412
2024-12-10 | 1:54 | Data | 0 | 33.642 | 31.988 | 169.441 | 7.64 | 160.144 | 2208.06 | 25.77 | 45.998 | 6.4 | 1.291 | 4.141 | 8372.9 | 1.782 | 97.9 | 76.2 | 1435 | 22.95 | 5442.4 | 2732.5 | 2748.9 | 4003.3 | 1220.3 | 0.66508 | 5.432
2024-12-10 | 1:54 | Data | 0 | 33.642 | 32.028 | 169.441 | 7.64 | 160.189 | 2208.97 | 25.74 | 45.998 | 6.4 | 1.289 | 4.162 | 8372.9 | 1.614 | 97.9 | 76.4 | 1435 | 22.95 | 5442.4 | 2734.1 | 2750.7 | 4005.1 | 1220.3 | 0.66573 | 5.452
2024-12-10 | 1:54 | Data | 0 | 33.419 | 32.231 | 169.531 | 7.64 | 160.099 | 2206.25 | 25.76 | 45.366 | 6.4 | 1.283 | 4.147 | 8431.69 | 1.62 | 97.9 | 76.4 | 1434 | 22.73 | 5480.6 | 2722 | 2724.2 | 3977.9 | 1220.3 | 0.66482 | 5.431
2024-12-10 | 1:54 | Data | 0 | 33.871 | 32.042 | 169.577 | 7.64 | 160.234 | 2199.93 | 25.75 | 45.908 | 6.4 | 1.289 | 4.134 | 8499.53 | 1.627 | 97.9 | 76.2 | 1430 | 22.95 | 5524.7 | 2733.1 | 2722.6 | 3987.9 | 1220.3 | 0.66644 | 5.422
2024-12-10 | 1:54 | Data | 0 | 33.446 | 31.974 | 169.486 | 7.63 | 160.189 | 2206.25 | 25.76 | 45.998 | 6.41 | 1.297 | 4.131 | 8495 | 1.614 | 97.9 | 76.1 | 1434 | 23 | 5521.8 | 2731.1 | 2693.8 | 3966.3 | 1220.3 | 0.67038 | 5.427
2024-12-10 | 1:55 | Data | 0 | 33.972 | 32.048 | 169.667 | 7.64 | 160.279 | 2208.06 | 25.74 | 45.908 | 6.4 | 1.289 | 4.157 | 8499.53 | 1.715 | 97.9 | 76.3 | 1435 | 23.04 | 5524.7 | 2725.9 | 2694.8 | 3972.5 | 1220.3 | 0.6687 | 5.446
2024-12-10 | 1:55 | Data | 0 | 33.642 | 32.035 | 169.531 | 7.64 | 160.234 | 2208.06 | 25.76 | 45.908 | 6.4 | 1.283 | 4.134 | 8499.53 | 1.593 | 97.9 | 76.3 | 1435 | 23 | 5524.7 | 2727.3 | 2694.6 | 3964 | 1220.3 | 0.67064 | 5.417
2024-12-10 | 1:55 | Data | 0 | 33.871 | 32.028 | 169.577 | 7.64 | 160.279 | 2205.35 | 25.75 | 45.908 | 6.41 | 1.287 | 4.118 | 8318.64 | 1.654 | 97.9 | 76.2 | 1434 | 22.95 | 5407.1 | 2747.3 | 2686.6 | 3969.4 | 1220.3 | 0.67538 | 5.405
2024-12-10 | 1:55 | Data | 0 | 33.534 | 32.251 | 169.531 | 7.63 | 160.189 | 2208.06 | 25.75 | 45.998 | 6.41 | 1.28 | 4.132 | 8314.11 | 1.512 | 97.9 | 76.4 | 1435 | 23 | 5404.2 | 2727.6 | 2690 | 3963.4 | 1220.3 | 0.67332 | 5.411
2024-12-10 | 1:55 | Data | 0 | 33.527 | 32.028 | 169.531 | 7.63 | 160.144 | 2208.97 | 25.75 | 45.998 | 6.41 | 1.295 | 4.141 | 8318.64 | 1.715 | 97.9 | 76.2 | 1436 | 23 | 5407.1 | 2740.6 | 2686.7 | 3966.5 | 1220.3 | 0.6731 | 5.436
2024-12-10 | 1:55 | Data | 0 | 33.453 | 31.812 | 169.35 | 7.64 | 160.099 | 2208.97 | 25.76 | 45.998 | 6.4 | 1.287 | 4.116 | 8318.64 | 1.458 | 97.9 | 76.2 | 1436 | 23 | 5407.1 | 2719.6 | 2692.4 | 3985.3 | 1220.3 | 0.67127 | 5.402
2024-12-10 | 1:55 | Data | 0 | 34.074 | 32.055 | 169.622 | 7.64 | 160.234 | 2208.97 | 25.75 | 45.908 | 6.41 | 1.291 | 4.108 | 8336.72 | 1.742 | 97.9 | 76.1 | 1436 | 23 | 5418.9 | 2728.6 | 2666.7 | 3961 | 1220.3 | 0.6703 | 5.401
2024-12-10 | 1:55 | Data | 0 | 33.54 | 32.021 | 169.531 | 7.64 | 160.234 | 2208.97 | 25.75 | 45.908 | 6.4 | 1.294 | 4.104 | 8336.72 | 1.519 | 97.9 | 76 | 1436 | 23 | 5418.9 | 2753.5 | 2699.7 | 3986.1 | 1220.3 | 0.67249 | 5.397
2024-12-10 | 1:55 | Data | 0 | 33.864 | 32.035 | 169.441 | 7.63 | 160.234 | 2211.68 | 25.75 | 45.998 | 6.4 | 1.291 | 4.11 | 8345.77 | 1.661 | 97.9 | 76.1 | 1437 | 22.95 | 5424.8 | 2735 | 2688 | 3967.4 | 1220.3 | 0.67068 | 5.399
2024-12-10 | 1:55 | Data | 0 | 33.979 | 32.197 | 169.531 | 7.64 | 160.234 | 2201.74 | 25.76 | 45.908 | 6.41 | 1.3 | 4.124 | 8336.72 | 1.506 | 97.9 | 76 | 1432 | 23 | 5418.9 | 2655.1 | 2671.1 | 3884 | 1220.3 | 0.66501 | 5.425
2024-12-10 | 1:55 | Data | 0 | 33.588 | 32.028 | 169.531 | 7.63 | 160.234 | 2211.68 | 25.76 | 45.998 | 6.41 | 1.29 | 4.132 | 8305.07 | 1.809 | 97.9 | 76.2 | 1437 | 23 | 5398.3 | 2532.9 | 2727.7 | 3904.4 | 1220.3 | 0.66335 | 5.422
2024-12-10 | 1:55 | Data | 0 | 33.844 | 32.264 | 169.486 | 7.63 | 160.189 | 2211.68 | 25.76 | 45.998 | 6.4 | 1.279 | 4.146 | 8300.55 | 1.6 | 97.9 | 76.4 | 1437 | 23 | 5395.4 | 1625.6 | 2088.5 | 2659.9 | 1220.3 | 0.60918 | 5.425
2024-12-10 | 1:55 | Data | 0 | 33.959 | 32.271 | 169.622 | 7.64 | 160.279 | 2213.49 | 25.75 | 45.908 | 6.4 | 1.286 | 4.129 | 8300.55 | 1.647 | 97.9 | 76.3 | 1439 | 22.95 | 5395.4 | 1626.8 | 2071.4 | 2646.4 | 1220.3 | 0.61229 | 5.415
2024-12-10 | 1:55 | Data | 0 | 33.925 | 32.055 | 169.441 | 7.64 | 160.234 | 2208.06 | 25.74 | 45.998 | 6.4 | 1.283 | 4.126 | 8305.07 | 1.755 | 97.9 | 76.3 | 1435 | 23 | 5398.3 | 1637.2 | 2075.2 | 2658.4 | 1220.3 | 0.61328 | 5.408
2024-12-10 | 1:55 | Data | 0 | 33.642 | 32.035 | 169.441 | 7.64 | 160.189 | 2208.97 | 25.75 | 45.998 | 6.41 | 1.289 | 4.101 | 8332.2 | 1.607 | 97.9 | 76.1 | 1436 | 23 | 5415.9 | 1634.5 | 2039.5 | 2626.6 | 1220.3 | 0.61939 | 5.39
2024-12-10 | 1:55 | Data | 0 | 33.432 | 32.109 | 169.577 | 7.64 | 160.189 | 2205.35 | 25.75 | 45.998 | 6.4 | 1.286 | 4.122 | 8336.72 | 1.404 | 97.9 | 76.2 | 1434 | 23 | 5418.9 | 1636 | 2054.6 | 2639.3 | 1220.3 | 0.61693 | 5.409
2024-12-10 | 1:55 | Data | 0 | 33.473 | 31.913 | 169.396 | 7.64 | 160.144 | 2205.35 | 25.75 | 45.998 | 6.41 | 1.287 | 4.113 | 8341.25 | 1.708 | 97.9 | 76.2 | 1434 | 22.95 | 5421.8 | 1634.3 | 2072.1 | 2651.4 | 1220.3 | 0.61398 | 5.4
2024-12-10 | 1:56 | Data | 0 | 33.588 | 32.244 | 169.577 | 7.63 | 160.144 | 2205.35 | 25.74 | 45.908 | 6.41 | 1.284 | 4.116 | 8332.2 | 1.593 | 97.9 | 76.2 | 1433 | 23 | 5415.9 | 1605.4 | 2062.7 | 2631.3 | 1220.3 | 0.60653 | 5.401
2024-12-10 | 1:56 | Data | 0 | 33.756 | 31.832 | 169.531 | 7.64 | 160.234 | 2208.06 | 25.75 | 45.908 | 6.41 | 1.287 | 4.145 | 8359.34 | 1.674 | 97.9 | 76.3 | 1436 | 23 | 5433.6 | 1647.6 | 2084.4 | 2669.5 | 1220.3 | 0.61527 | 5.432
2024-12-10 | 1:56 | Data | 0 | 33.777 | 32.035 | 169.577 | 7.64 | 160.279 | 2206.25 | 25.75 | 45.908 | 6.4 | 1.297 | 4.155 | 8359.34 | 1.512 | 97.9 | 76.2 | 1434 | 23 | 5433.6 | 1626 | 2063.6 | 2650.2 | 1220.3 | 0.6147 | 5.452
2024-12-10 | 1:56 | Data | 0 | 33.669 | 32.028 | 169.441 | 7.64 | 160.144 | 2205.35 | 25.75 | 45.998 | 6.41 | 1.289 | 4.148 | 8359.34 | 1.627 | 97.9 | 76.3 | 1433 | 23 | 5433.6 | 1650 | 2098.4 | 2684.1 | 1220.3 | 0.61135 | 5.437
2024-12-10 | 1:56 | Data | 0 | 33.615 | 32.042 | 169.441 | 7.63 | 160.144 | 2205.35 | 25.75 | 45.908 | 6.41 | 1.285 | 4.115 | 8359.34 | 1.688 | 97.9 | 76.2 | 1433 | 22.95 | 5433.6 | 1645.1 | 2114.5 | 2693.9 | 1220.3 | 0.6084 | 5.401
2024-12-10 | 1:56 | Data | 0 | 33.446 | 31.859 | 169.486 | 7.64 | 160.234 | 2206.25 | 25.74 | 45.908 | 6.41 | 1.286 | 4.13 | 8354.81 | 1.398 | 97.9 | 76.3 | 1434 | 22.95 | 5430.6 | 1642.2 | 2118.3 | 2696.3 | 1220.3 | 0.60537 | 5.417
2024-12-10 | 1:56 | Data | 0 | 33.756 | 32.082 | 169.486 | 7.63 | 160.234 | 2208.06 | 25.74 | 45.908 | 6.4 | 1.289 | 4.133 | 8350.29 | 1.62 | 97.9 | 76.2 | 1435 | 22.95 | 5427.7 | 1654.7 | 2101 | 2692.4 | 1220.3 | 0.61371 | 5.421
2024-12-10 | 1:56 | Data | 0 | 33.635 | 31.853 | 169.486 | 7.64 | 160.144 | 2208.97 | 25.75 | 45.908 | 6.4 | 1.284 | 4.128 | 8359.34 | 1.62 | 97.9 | 76.3 | 1436 | 23 | 5433.6 | 1655.4 | 2121.8 | 2704.7 | 1220.3 | 0.60944 | 5.412
2024-12-10 | 1:56 | Data | 0 | 33.615 | 32.028 | 169.531 | 7.64 | 160.099 | 2208.06 | 25.74 | 45.998 | 6.4 | 1.286 | 4.125 | 8354.81 | 1.641 | 97.9 | 76.2 | 1435 | 23 | 5430.6 | 1644 | 2101 | 2684.1 | 1220.3 | 0.61203 | 5.411
2024-12-10 | 1:56 | Data | 0 | 33.318 | 31.913 | 169.531 | 7.64 | 160.189 | 2208.97 | 25.74 | 45.998 | 6.4 | 1.288 | 4.125 | 8363.86 | 1.566 | 97.9 | 76.2 | 1435 | 23 | 5436.5 | 1630.8 | 2105.5 | 2677.6 | 1220.3 | 0.60595 | 5.413
2024-12-10 | 1:56 | Data | 0 | 33.628 | 31.913 | 169.441 | 7.64 | 160.099 | 2208.06 | 25.74 | 45.908 | 6.4 | 1.294 | 4.133 | 8359.34 | 1.553 | 97.9 | 76.2 | 1435 | 23 | 5433.6 | 1634.7 | 2102.7 | 2676.1 | 1220.3 | 0.60784 | 5.427
2024-12-10 | 1:56 | Data | 0 | 33.412 | 31.913 | 169.396 | 7.64 | 160.144 | 2210.77 | 25.75 | 45.998 | 6.41 | 1.291 | 4.14 | 8381.95 | 1.722 | 97.9 | 76.2 | 1437 | 22.95 | 5448.3 | 1650 | 2116.7 | 2699.8 | 1220.3 | 0.60877 | 5.431
2024-12-10 | 1:56 | Data | 0 | 33.473 | 31.812 | 169.486 | 7.64 | 160.144 | 2211.68 | 25.75 | 45.998 | 6.4 | 1.291 | 4.124 | 8386.47 | 1.776 | 97.9 | 76.2 | 1437 | 22.95 | 5451.2 | 1638 | 2093.3 | 2672.4 | 1220.3 | 0.61014 | 5.415
2024-12-10 | 1:56 | Data | 0 | 33.588 | 32.244 | 169.577 | 7.64 | 160.189 | 2212.58 | 25.74 | 45.998 | 6.4 | 1.288 | 4.155 | 8372.9 | 1.573 | 97.9 | 76.3 | 1439 | 23 | 5442.4 | 1649.2 | 2134.2 | 2712.1 | 1220.3 | 0.60531 | 5.442
2024-12-10 | 1:56 | Data | 0 | 33.527 | 32.001 | 169.441 | 7.64 | 160.099 | 2213.49 | 25.75 | 45.908 | 6.41 | 1.3 | 4.165 | 8359.34 | 1.627 | 97.9 | 76.2 | 1439 | 22.95 | 5433.6 | 1648.2 | 2082 | 2669.7 | 1220.3 | 0.61473 | 5.464
2024-12-10 | 1:56 | Data | 0 | 33.77 | 31.92 | 169.531 | 7.64 | 160.234 | 2213.49 | 25.74 | 45.998 | 6.41 | 1.289 | 4.154 | 8363.86 | 1.641 | 97.9 | 76.3 | 1439 | 23 | 5436.5 | 1641.8 | 2093.6 | 2674.6 | 1220.3 | 0.61014 | 5.443
2024-12-10 | 1:56 | Data | 0 | 33.432 | 31.812 | 169.396 | 7.64 | 160.144 | 2214.39 | 25.75 | 45.908 | 6.41 | 1.284 | 4.096 | 8359.34 | 1.593 | 97.9 | 76.1 | 1439 | 23 | 5433.6 | 1645.7 | 2111.4 | 2691 | 1220.3 | 0.60838 | 5.38
2024-12-10 | 1:56 | Data | 0 | 33.527 | 32.055 | 169.441 | 7.64 | 160.144 | 2213.49 | 25.74 | 45.908 | 6.41 | 1.284 | 4.11 | 8372.9 | 1.668 | 97.9 | 76.2 | 1439 | 23 | 5442.4 | 1661.8 | 2094.1 | 2688.2 | 1220.3 | 0.61555 | 5.392
2024-12-10 | 1:57 | Data | 0 | 33.615 | 31.961 | 169.441 | 7.64 | 160.099 | 2214.39 | 25.75 | 45.998 | 6.4 | 1.287 | 4.112 | 8350.29 | 1.512 | 97.9 | 76.2 | 1439 | 23 | 5427.7 | 1648 | 2108 | 2690.3 | 1220.3 | 0.60935 | 5.399
2024-12-10 | 1:57 | Data | 0 | 33.689 | 31.832 | 169.441 | 7.64 | 160.144 | 2217.1 | 25.75 | 45.998 | 6.41 | 1.283 | 4.124 | 8345.77 | 1.728 | 97.9 | 76.3 | 1441 | 23 | 5424.8 | 1611.4 | 2114.5 | 2672.3 | 1220.3 | 0.59969 | 5.407
2024-12-10 | 1:57 | Data | 0 | 33.412 | 31.913 | 169.486 | 7.64 | 160.189 | 2214.39 | 25.74 | 45.908 | 6.41 | 1.287 | 4.105 | 8354.81 | 1.607 | 97.9 | 76.1 | 1439 | 22.95 | 5430.6 | 1614.8 | 2097.8 | 2656.4 | 1220.3 | 0.6066 | 5.392
2024-12-10 | 1:57 | Data | 0 | 33.527 | 32.224 | 169.486 | 7.64 | 160.099 | 2216.2 | 25.75 | 45.908 | 6.4 | 1.282 | 4.121 | 8341.25 | 1.573 | 97.9 | 76.3 | 1441 | 22.95 | 5421.8 | 1622.1 | 2123.4 | 2688.4 | 1220.3 | 0.60341 | 5.402
2024-12-10 | 1:57 | Data | 0 | 33.642 | 31.913 | 169.35 | 7.64 | 160.099 | 2220.72 | 25.74 | 45.908 | 6.41 | 1.291 | 4.139 | 8332.2 | 1.627 | 97.9 | 76.2 | 1442 | 23 | 5415.9 | 1622.9 | 2116.4 | 2680.9 | 1220.3 | 0.60212 | 5.43
2024-12-10 | 1:57 | Data | 0 | 33.642 | 31.819 | 169.441 | 7.64 | 160.099 | 2221.62 | 25.74 | 45.998 | 6.41 | 1.285 | 4.153 | 8341.25 | 1.641 | 97.9 | 76.4 | 1444 | 23 | 5421.8 | 1623.2 | 2086.9 | 2657.6 | 1220.3 | 0.60787 | 5.439
2024-12-10 | 1:57 | Data | 0 | 33.426 | 31.913 | 169.396 | 7.64 | 160.008 | 2277.66 | 25.75 | 45.908 | 6.4 | 1.284 | 4.132 | 8318.64 | 1.62 | 98 | 76.3 | 1480 | 22.95 | 5407.1 | 1640.2 | 2067.9 | 2652.3 | 1220.3 | 0.61631 | 5.416
2024-12-10 | 1:57 | Data | 0 | 33.851 | 32.035 | 169.486 | 7.64 | 160.144 | 2277.66 | 25.75 | 45.998 | 6.4 | 1.291 | 4.121 | 8318.64 | 1.715 | 98 | 76.2 | 1480 | 23 | 5407.1 | 1613.3 | 2057.9 | 2627.5 | 1220.3 | 0.61128 | 5.412
2024-12-10 | 1:57 | Data | 0 | 33.635 | 31.826 | 169.26 | 7.64 | 160.099 | 2279.46 | 25.75 | 45.998 | 6.41 | 1.291 | 4.102 | 8314.11 | 1.782 | 98 | 76.1 | 1482 | 22.95 | 5404.2 | 1618.4 | 2073.8 | 2645.1 | 1220.3 | 0.61001 | 5.392
2024-12-10 | 1:57 | Data | 0 | 33.52 | 31.799 | 169.441 | 7.64 | 160.053 | 2276.75 | 25.74 | 45.998 | 6.4 | 1.293 | 4.124 | 8336.72 | 1.634 | 98 | 76.1 | 1480 | 23 | 5418.9 | 1618.8 | 2083.3 | 2651.4 | 1220.3 | 0.60824 | 5.418
2024-12-10 | 1:57 | Data | 0 | 33.405 | 31.826 | 169.486 | 7.64 | 160.053 | 2220.72 | 25.75 | 45.998 | 6.41 | 1.286 | 4.128 | 8332.2 | 1.701 | 97.9 | 76.3 | 1443 | 23.04 | 5415.9 | 1621.3 | 2074.3 | 2643.6 | 1220.4 | 0.61098 | 5.413
2024-12-10 | 1:57 | Data | 0 | 33.642 | 32.001 | 169.35 | 7.64 | 160.099 | 2213.49 | 25.74 | 45.908 | 6.4 | 1.28 | 4.122 | 8300.55 | 1.641 | 97.9 | 76.3 | 1439 | 22.95 | 5395.4 | 1629.7 | 2108.5 | 2676.7 | 1220.4 | 0.60367 | 5.401
2024-12-10 | 1:57 | Data | 0 | 33.588 | 31.704 | 169.305 | 7.64 | 160.099 | 2217.1 | 25.75 | 45.998 | 6.41 | 1.288 | 4.134 | 8318.64 | 1.627 | 97.9 | 76.2 | 1441 | 22.95 | 5407.1 | 1616.4 | 2099.5 | 2663.4 | 1220.4 | 0.60488 | 5.421
2024-12-10 | 1:57 | Data | 0 | 33.419 | 32.231 | 169.396 | 7.63 | 160.099 | 2216.2 | 25.74 | 46.089 | 6.4 | 1.292 | 4.143 | 8305.07 | 1.418 | 97.9 | 76.2 | 1441 | 23 | 5398.3 | 1635.6 | 2088.5 | 2666.2 | 1220.4 | 0.61025 | 5.437
2024-12-10 | 1:57 | Data | 0 | 33.642 | 31.812 | 169.35 | 7.64 | 160.099 | 2213.49 | 25.74 | 45.908 | 6.4 | 1.283 | 4.111 | 8300.55 | 1.654 | 97.9 | 76.2 | 1439 | 23 | 5395.4 | 1624.2 | 2071.3 | 2645.8 | 1220.4 | 0.61076 | 5.393
2024-12-10 | 1:57 | Data | 0 | 33.419 | 31.974 | 169.486 | 7.64 | 160.099 | 2214.39 | 25.74 | 45.908 | 6.4 | 1.273 | 4.124 | 8314.11 | 1.614 | 97.9 | 76.4 | 1439 | 22.95 | 5404.2 | 1610 | 2087.8 | 2651.1 | 1220.4 | 0.60444 | 5.397
2024-12-10 | 1:57 | Data | 0 | 33.439 | 31.974 | 169.441 | 7.63 | 160.053 | 2213.49 | 25.75 | 45.908 | 6.41 | 1.27 | 4.149 | 8318.64 | 1.56 | 97.9 | 76.6 | 1439 | 22.95 | 5407.1 | 1608.1 | 2065.3 | 2650.5 | 1220.4 | 0.61096 | 5.419
2024-12-10 | 1:57 | Data | 0 | 33.412 | 31.751 | 169.35 | 7.64 | 160.053 | 2214.39 | 25.74 | 46.089 | 6.41 | 1.28 | 4.141 | 8314.11 | 1.776 | 97.9 | 76.4 | 1439 | 23 | 5404.2 | 1622.9 | 2083.9 | 2656 | 1220.4 | 0.60853 | 5.42
2024-12-10 | 1:58 | Data | 0 | 33.358 | 32.015 | 169.441 | 7.63 | 160.099 | 2214.39 | 25.74 | 45.908 | 6.4 | 1.282 | 4.136 | 8318.64 | 1.776 | 97.9 | 76.3 | 1439 | 23 | 5407.1 | 1620.5 | 2093.4 | 2661.3 | 1220.4 | 0.60551 | 5.419
2024-12-10 | 1:58 | Data | 0 | 33.615 | 31.805 | 169.441 | 7.63 | 160.008 | 2213.49 | 25.74 | 45.908 | 6.4 | 1.286 | 4.125 | 8305.07 | 1.83 | 97.9 | 76.2 | 1439 | 23.04 | 5398.3 | 2735.6 | 3587.9 | 4556.8 | 1220.4 | 0.60415 | 5.411
2024-12-10 | 1:58 | Data | 0 | 33.54 | 31.974 | 169.35 | 7.63 | 160.053 | 2213.49 | 25.75 | 45.998 | 6.4 | 1.285 | 4.119 | 8318.64 | 1.715 | 97.9 | 76.2 | 1439 | 23 | 5407.1 | 2698.1 | 2674.2 | 3925.7 | 1220.4 | 0.66887 | 5.402
2024-12-10 | 1:58 | Data | 0 | 33.527 | 31.92 | 169.396 | 7.64 | 160.053 | 2213.49 | 25.74 | 45.908 | 6.41 | 1.283 | 4.134 | 8318.64 | 1.506 | 97.9 | 76.3 | 1439 | 23 | 5407.1 | 2702.1 | 2701.4 | 3951.6 | 1220.4 | 0.6671 | 5.416
2024-12-10 | 1:58 | Data | 0 | 33.635 | 31.826 | 169.396 | 7.63 | 160.099 | 2212.58 | 25.75 | 45.908 | 6.4 | 1.29 | 4.143 | 8318.64 | 1.566 | 97.9 | 76.3 | 1439 | 22.95 | 5407.1 | 2688.1 | 2701.2 | 3944.4 | 1220.4 | 0.66241 | 5.432
2024-12-10 | 1:58 | Data | 0 | 33.446 | 31.974 | 169.396 | 7.64 | 160.053 | 2217.1 | 25.75 | 45.908 | 6.41 | 1.286 | 4.134 | 8305.07 | 1.62 | 97.9 | 76.3 | 1441 | 22.95 | 5398.3 | 2702.9 | 2728.1 | 3967.9 | 1220.4 | 0.66267 | 5.42
2024-12-10 | 1:58 | Data | 0 | 33.297 | 31.799 | 169.305 | 7.63 | 160.008 | 2213.49 | 25.75 | 45.908 | 6.4 | 1.287 | 4.113 | 8300.55 | 1.411 | 97.9 | 76.2 | 1439 | 23 | 5395.4 | 2698.3 | 2701.6 | 3948.2 | 1220.4 | 0.66587 | 5.4
2024-12-10 | 1:58 | Data | 0 | 33.365 | 31.799 | 169.35 | 7.64 | 160.053 | 2213.49 | 25.74 | 45.998 | 6.4 | 1.284 | 4.13 | 8305.07 | 1.607 | 97.9 | 76.3 | 1439 | 22.95 | 5398.3 | 2704.6 | 2728 | 3967.5 | 1220.4 | 0.66427 | 5.413
2024-12-10 | 1:58 | Data | 0 | 33.628 | 32.028 | 169.396 | 7.64 | 160.053 | 2213.49 | 25.75 | 45.998 | 6.41 | 1.284 | 4.155 | 8318.64 | 1.614 | 97.9 | 76.4 | 1439 | 23 | 5407.1 | 2713.1 | 2716.6 | 3972.2 | 1220.4 | 0.66431 | 5.44
2024-12-10 | 1:58 | Data | 0 | 33.412 | 31.826 | 169.305 | 7.64 | 160.008 | 2210.77 | 25.75 | 45.998 | 6.4 | 1.29 | 4.146 | 8332.2 | 1.614 | 97.9 | 76.3 | 1437 | 23 | 5415.9 | 2698.4 | 2705.5 | 3950.7 | 1220.4 | 0.66572 | 5.435
2024-12-10 | 1:58 | Data | 0 | 33.588 | 31.805 | 169.441 | 7.63 | 160.053 | 2205.35 | 25.74 | 45.908 | 6.4 | 1.288 | 4.126 | 8323.16 | 1.823 | 97.9 | 76.2 | 1433 | 22.95 | 5410.1 | 2715.4 | 2706.7 | 3955.5 | 1220.4 | 0.67024 | 5.414
2024-12-10 | 1:58 | Data | 0 | 33.412 | 31.799 | 169.441 | 7.64 | 160.053 | 2206.25 | 25.75 | 45.908 | 6.41 | 1.295 | 4.126 | 8314.11 | 1.614 | 97.9 | 76.1 | 1433 | 23 | 5404.2 | 2713.2 | 2685.7 | 3941.6 | 1220.4 | 0.67097 | 5.42
2024-12-10 | 1:58 | Data | 0 | 33.419 | 32.19 | 169.441 | 7.64 | 160.099 | 2203.54 | 25.75 | 45.998 | 6.4 | 1.291 | 4.124 | 8336.72 | 1.56 | 97.9 | 76.1 | 1432 | 23 | 5418.9 | 2700.7 | 2674.8 | 3934.3 | 1220.4 | 0.66796 | 5.415
2024-12-10 | 1:58 | Data | 0 | 33.642 | 31.799 | 169.441 | 7.64 | 160.008 | 2206.25 | 25.74 | 45.998 | 6.41 | 1.285 | 4.122 | 8332.2 | 1.668 | 97.9 | 76.2 | 1435 | 23 | 5415.9 | 2721.3 | 2698.3 | 3962.5 | 1220.4 | 0.66862 | 5.406
2024-12-10 | 1:58 | Data | 0 | 33.682 | 31.805 | 169.441 | 7.64 | 160.099 | 2205.35 | 25.74 | 45.998 | 6.4 | 1.292 | 4.115 | 8345.77 | 1.668 | 97.9 | 76.1 | 1434 | 23 | 5424.8 | 2701.5 | 2693 | 3948 | 1220.4 | 0.66491 | 5.408
2024-12-10 | 1:58 | Data | 0 | 33.588 | 31.812 | 169.396 | 7.64 | 160.099 | 2206.25 | 25.75 | 45.908 | 6.4 | 1.284 | 4.125 | 8332.2 | 1.708 | 97.9 | 76.3 | 1435 | 23 | 5415.9 | 2701.3 | 2698.5 | 3949.8 | 1220.4 | 0.66563 | 5.41
2024-12-10 | 1:58 | Data | 0 | 33.817 | 31.859 | 169.441 | 7.63 | 160.144 | 2199.02 | 25.75 | 45.998 | 6.41 | 1.285 | 4.122 | 8336.72 | 1.62 | 97.9 | 76.2 | 1431 | 23 | 5418.9 | 2715.8 | 2696.4 | 3959.5 | 1220.4 | 0.66758 | 5.407
2024-12-10 | 1:58 | Data | 0 | 33.52 | 31.812 | 169.396 | 7.64 | 160.053 | 2208.97 | 25.75 | 45.908 | 6.4 | 1.282 | 4.134 | 8323.16 | 1.553 | 97.9 | 76.3 | 1435 | 22.95 | 5410.1 | 2702.8 | 2721.4 | 3967.4 | 1220.4 | 0.66181 | 5.416
2024-12-10 | 1:59 | Data | 0 | 33.412 | 32.021 | 169.35 | 7.64 | 160.008 | 2208.97 | 25.74 | 45.998 | 6.41 | 1.284 | 4.134 | 8300.55 | 1.641 | 97.9 | 76.3 | 1436 | 23 | 5395.4 | 2707.2 | 2694.6 | 3944.4 | 1220.4 | 0.66773 | 5.419
2024-12-10 | 1:59 | Data | 0 | 33.851 | 32.251 | 169.531 | 7.64 | 160.189 | 2208.97 | 25.74 | 45.908 | 6.4 | 1.28 | 4.11 | 8300.55 | 1.627 | 97.9 | 76.3 | 1436 | 22.95 | 5395.4 | 2701.7 | 2716.7 | 3957 | 1220.4 | 0.66547 | 5.39
2024-12-10 | 1:59 | Data | 0 | 33.642 | 31.907 | 169.396 | 7.64 | 160.099 | 2208.97 | 25.74 | 45.998 | 6.4 | 1.29 | 4.123 | 8300.55 | 1.627 | 97.9 | 76.2 | 1436 | 23 | 5395.4 | 2701.5 | 2737.4 | 3973.5 | 1220.4 | 0.66183 | 5.412
2024-12-10 | 1:59 | Data | 0 | 33.419 | 31.826 | 169.396 | 7.64 | 160.144 | 2208.06 | 25.75 | 45.998 | 6.4 | 1.284 | 4.144 | 8314.11 | 1.56 | 97.9 | 76.3 | 1436 | 23 | 5404.2 | 2701.8 | 2713.3 | 3955.7 | 1220.4 | 0.66471 | 5.429
2024-12-10 | 1:59 | Data | 0 | 33.216 | 31.886 | 169.35 | 7.64 | 160.099 | 2208.97 | 25.74 | 45.908 | 6.4 | 1.29 | 4.121 | 8318.64 | 1.607 | 97.9 | 76.2 | 1436 | 22.95 | 5407.1 | 2710 | 2707.1 | 3952.7 | 1220.4 | 0.66489 | 5.41
2024-12-10 | 1:59 | Data | 0 | 33.642 | 31.805 | 169.396 | 7.63 | 160.053 | 2208.06 | 25.75 | 45.908 | 6.4 | 1.292 | 4.138 | 8314.11 | 1.661 | 97.9 | 76.2 | 1435 | 23 | 5404.2 | 2702.9 | 2681.2 | 3938.9 | 1220.4 | 0.66638 | 5.43
2024-12-10 | 1:59 | Data | 0 | 33.851 | 32.089 | 169.531 | 7.63 | 160.189 | 2208.97 | 25.75 | 45.998 | 6.4 | 1.293 | 4.14 | 8323.16 | 1.614 | 97.9 | 76.2 | 1436 | 23 | 5410.1 | 2710.7 | 2695.4 | 3948.1 | 1220.4 | 0.66943 | 5.434
2024-12-10 | 1:59 | Data | 0 | 33.743 | 31.819 | 169.35 | 7.64 | 160.144 | 2206.25 | 25.74 | 46.089 | 6.4 | 1.286 | 4.12 | 8761.81 | 1.661 | 97.9 | 76.2 | 1434 | 23.04 | 5695.2 | 2689.4 | 2680.8 | 3926.2 | 1220.4 | 0.66762 | 5.406
2024-12-10 | 1:59 | Data | 0 | 33.426 | 31.805 | 169.396 | 7.64 | 160.189 | 2205.35 | 25.74 | 45.998 | 6.41 | 1.291 | 4.132 | 8400.04 | 1.6 | 97.9 | 76.2 | 1434 | 23 | 5460 | 2698.2 | 2683.2 | 3932.5 | 1220.4 | 0.66781 | 5.423
2024-12-10 | 1:59 | Data | 0 | 33.635 | 31.799 | 169.35 | 7.63 | 160.053 | 2206.25 | 25.74 | 45.908 | 6.41 | 1.286 | 4.133 | 8359.34 | 1.641 | 97.9 | 76.3 | 1434 | 22.95 | 5433.6 | 2688.4 | 2677.8 | 3925.9 | 1220.4 | 0.66691 | 5.419
2024-12-10 | 1:59 | Data | 0 | 33.635 | 31.859 | 169.441 | 7.64 | 160.099 | 2205.35 | 25.75 | 45.998 | 6.41 | 1.286 | 4.108 | 8363.86 | 1.722 | 97.9 | 76.2 | 1433 | 23 | 5436.5 | 2682.2 | 2696.1 | 3934.6 | 1220.4 | 0.66288 | 5.394
2024-12-10 | 1:59 | Data | 0 | 33.642 | 31.799 | 169.396 | 7.63 | 160.099 | 2208.06 | 25.75 | 45.998 | 6.41 | 1.3 | 4.112 | 8336.72 | 1.836 | 97.9 | 76 | 1435 | 23 | 5418.9 | 2700.5 | 2693.4 | 3939.5 | 1220.4 | 0.66737 | 5.411
2024-12-10 | 1:59 | Data | 0 | 33.419 | 32.001 | 169.396 | 7.64 | 160.099 | 2210.77 | 25.74 | 45.998 | 6.4 | 1.295 | 4.115 | 8332.2 | 1.411 | 97.9 | 76.1 | 1437 | 23 | 5415.9 | 2704.9 | 2710.2 | 3954.5 | 1220.4 | 0.66584 | 5.41
2024-12-10 | 1:59 | Data | 0 | 33.615 | 31.805 | 169.396 | 7.63 | 160.099 | 2211.68 | 25.75 | 45.908 | 6.41 | 1.287 | 4.115 | 8336.72 | 1.708 | 97.9 | 76.2 | 1438 | 22.95 | 5418.9 | 2704.4 | 2714.9 | 3959 | 1220.4 | 0.66408 | 5.402
2024-12-10 | 1:59 | Data | 0 | 33.439 | 32.116 | 169.486 | 7.63 | 160.144 | 2212.58 | 25.74 | 45.818 | 6.4 | 1.29 | 4.129 | 8332.2 | 1.573 | 97.9 | 76.2 | 1437 | 22.91 | 5415.9 | 2715.7 | 2730.8 | 3976.9 | 1220.4 | 0.66288 | 5.42
2024-12-10 | 1:59 | Data | 0 | 33.412 | 31.974 | 169.396 | 7.64 | 160.099 | 2212.58 | 25.75 | 45.998 | 6.4 | 1.297 | 4.134 | 8318.64 | 1.728 | 97.9 | 76.1 | 1438 | 23 | 5407.1 | 2700.6 | 2702.5 | 3946.4 | 1220.4 | 0.66482 | 5.43
2024-12-10 | 1:59 | Data | 0 | 33.669 | 31.94 | 169.441 | 7.64 | 160.189 | 2108.64 | 25.74 | 45.908 | 6.4 | 1.294 | 4.122 | 8318.64 | 1.526 | 97.8 | 76.1 | 1371 | 22.91 | 5407.1 | 2697.7 | 2688.6 | 3935.5 | 1220.4 | 0.67002 | 5.417
2024-12-10 | 2:00 | Data | 0 | 33.304 | 31.799 | 169.396 | 7.63 | 160.099 | 2108.64 | 25.74 | 45.637 | 6.4 | 1.294 | 4.127 | 8336.72 | 1.83 | 97.8 | 76.1 | 1371 | 22.82 | 5418.9 | 2722 | 2673 | 3939.5 | 1220.5 | 0.67322 | 5.422
2024-12-10 | 2:00 | Data | 0 | 33.797 | 32.156 | 169.531 | 7.64 | 160.189 | 2216.2 | 25.75 | 45.727 | 6.41 | 1.291 | 4.114 | 8336.72 | 1.749 | 97.9 | 76.1 | 1441 | 22.86 | 5418.9 | 2717.9 | 2688.7 | 3949.5 | 1220.5 | 0.67073 | 5.404
2024-12-10 | 2:00 | Data | 0 | 33.419 | 32.251 | 169.486 | 7.64 | 160.189 | 2213.49 | 25.74 | 45.727 | 6.41 | 1.291 | 4.122 | 8336.72 | 1.472 | 97.9 | 76.2 | 1439 | 22.86 | 5418.9 | 2701.1 | 2682.8 | 3934.1 | 1220.5 | 0.66772 | 5.411
2024-12-10 | 2:00 | Data | 0 | 33.473 | 32.015 | 169.486 | 7.64 | 160.144 | 2213.49 | 25.75 | 46.089 | 6.4 | 1.284 | 4.132 | 8363.86 | 1.573 | 97.9 | 76.3 | 1439 | 23.04 | 5436.5 | 2701.5 | 2707.6 | 3954 | 1220.5 | 0.66567 | 5.415
2024-12-10 | 2:00 | Data | 0 | 33.635 | 31.812 | 169.35 | 7.64 | 160.099 | 2213.49 | 25.74 | 45.457 | 6.4 | 1.28 | 4.141 | 8359.34 | 1.816 | 97.9 | 76.4 | 1439 | 22.73 | 5433.6 | 2712 | 2695.6 | 3948.1 | 1220.5 | 0.67036 | 5.423
2024-12-10 | 2:00 | Data | 0 | 33.75 | 31.866 | 169.486 | 7.64 | 160.144 | 2210.77 | 25.74 | 45.998 | 6.4 | 1.284 | 4.12 | 8363.86 | 1.755 | 97.9 | 76.2 | 1438 | 23.04 | 5436.5 | 2693.4 | 2702.1 | 3943.7 | 1220.5 | 0.66613 | 5.405
2024-12-10 | 2:00 | Data | 0 | 33.642 | 31.88 | 169.486 | 7.64 | 160.144 | 2210.77 | 25.75 | 45.727 | 6.41 | 1.291 | 4.132 | 8372.9 | 1.674 | 97.9 | 76.2 | 1438 | 22.82 | 5442.4 | 2712.5 | 2695.5 | 3952.1 | 1220.5 | 0.66935 | 5.421
2024-12-10 | 2:00 | Data | 0 | 33.864 | 31.873 | 169.35 | 7.64 | 160.144 | 2210.77 | 25.74 | 45.637 | 6.41 | 1.291 | 4.127 | 8377.43 | 1.668 | 97.9 | 76.2 | 1437 | 22.82 | 5445.3 | 2707.9 | 2678.9 | 3937.9 | 1220.5 | 0.66954 | 5.418
2024-12-10 | 2:00 | Data | 0 | 33.473 | 32.116 | 169.396 | 7.64 | 160.099 | 2210.77 | 25.75 | 45.727 | 6.4 | 1.291 | 4.118 | 8372.9 | 1.445 | 97.9 | 76.1 | 1437 | 22.86 | 5442.4 | 2713.1 | 2682.7 | 3938.2 | 1220.5 | 0.67163 | 5.411
2024-12-10 | 2:00 | Data | 0 | 33.311 | 31.799 | 169.35 | 7.64 | 160.099 | 2211.68 | 25.75 | 45.637 | 6.41 | 1.291 | 4.097 | 8381.95 | 1.6 | 97.9 | 76.1 | 1437 | 22.86 | 5448.3 | 2714 | 2678.5 | 3942 | 1220.5 | 0.67098 | 5.387
2024-12-10 | 2:00 | Data | 0 | 33.412 | 32.116 | 169.441 | 7.64 | 160.189 | 2208.97 | 25.74 | 46.179 | 6.4 | 1.291 | 4.106 | 8354.81 | 1.614 | 97.9 | 76.1 | 1436 | 23.09 | 5430.6 | 2713.8 | 2674.4 | 3937.9 | 1220.5 | 0.67134 | 5.397
2024-12-10 | 2:00 | Data | 0 | 33.669 | 32.015 | 169.441 | 7.64 | 160.144 | 2208.06 | 25.75 | 45.727 | 6.4 | 1.291 | 4.139 | 8336.72 | 1.404 | 97.9 | 76.2 | 1435 | 22.82 | 5418.9 | 2730.3 | 2704.2 | 3968.1 | 1220.5 | 0.67079 | 5.43
2024-12-10 | 2:00 | Data | 0 | 33.419 | 31.974 | 169.441 | 7.64 | 160.144 | 2208.06 | 25.74 | 45.727 | 6.41 | 1.285 | 4.138 | 8350.29 | 1.614 | 97.9 | 76.3 | 1436 | 22.86 | 5427.7 | 2711.6 | 2681.1 | 3951.7 | 1220.5 | 0.67052 | 5.422
2024-12-10 | 2:00 | Data | 0 | 33.642 | 31.974 | 169.441 | 7.64 | 160.144 | 2208.06 | 25.74 | 45.818 | 6.4 | 1.279 | 4.148 | 8359.34 | 1.836 | 97.9 | 76.4 | 1436 | 22.95 | 5433.6 | 2713.7 | 2686 | 3946.5 | 1220.5 | 0.66944 | 5.426
2024-12-10 | 2:00 | Data | 0 | 33.419 | 32.001 | 169.486 | 7.64 | 160.099 | 2210.77 | 25.74 | 45.818 | 6.4 | 1.291 | 4.139 | 8363.86 | 1.674 | 97.9 | 76.2 | 1437 | 22.91 | 5436.5 | 2712 | 2694.4 | 3950.7 | 1220.5 | 0.66988 | 5.43
2024-12-10 | 2:00 | Data | 0 | 33.804 | 32.035 | 169.441 | 7.64 | 160.144 | 2209.87 | 25.75 | 45.998 | 6.4 | 1.29 | 4.125 | 8359.34 | 1.654 | 97.9 | 76.2 | 1437 | 22.95 | 5433.6 | 2710.4 | 2704.2 | 3955.9 | 1220.5 | 0.66737 | 5.415
2024-12-10 | 2:00 | Data | 0 | 33.864 | 31.92 | 169.441 | 7.64 | 160.099 | 2210.77 | 25.75 | 45.998 | 6.4 | 1.286 | 4.118 | 8359.34 | 1.654 | 97.9 | 76.2 | 1438 | 23 | 5433.6 | 2718.5 | 2695 | 3953.6 | 1220.5 | 0.66965 | 5.402
2024-12-10 | 2:00 | Data | 0 | 33.858 | 32.264 | 169.577 | 7.64 | 160.189 | 2210.77 | 25.74 | 45.998 | 6.4 | 1.288 | 4.115 | 8363.86 | 1.6 | 97.9 | 76.2 | 1437 | 23 | 5436.5 | 2716.8 | 2682.3 | 3946.8 | 1220.5 | 0.66872 | 5.403
2024-12-10 | 2:01 | Data | 0 | 33.844 | 31.839 | 169.486 | 7.64 | 160.144 | 2210.77 | 25.75 | 45.998 | 6.4 | 1.284 | 4.126 | 8363.86 | 1.789 | 97.9 | 76.3 | 1438 | 23 | 5436.5 | 2698 | 2692.9 | 3941 | 1220.5 | 0.66679 | 5.411
2024-12-10 | 2:01 | Data | 0 | 34.06 | 32.251 | 169.577 | 7.64 | 160.234 | 2211.68 | 25.75 | 45.908 | 6.4 | 1.286 | 4.143 | 8381.95 | 1.742 | 97.9 | 76.3 | 1438 | 23 | 5448.3 | 2699.7 | 2684.3 | 3934.1 | 1220.5 | 0.6663 | 5.429
2024-12-10 | 2:01 | Data | 0 | 33.696 | 31.853 | 169.35 | 7.64 | 160.189 | 2210.77 | 25.75 | 45.998 | 6.4 | 1.291 | 4.132 | 8386.47 | 1.627 | 97.9 | 76.2 | 1437 | 22.95 | 5451.2 | 2713.7 | 2695.5 | 3951.8 | 1220.5 | 0.6691 | 5.423
2024-12-10 | 2:01 | Data | 0 | 33.527 | 31.853 | 169.396 | 7.63 | 160.144 | 2211.68 | 25.74 | 45.998 | 6.4 | 1.282 | 4.128 | 8390.99 | 1.695 | 97.9 | 76.3 | 1437 | 23 | 5454.1 | 2705.5 | 2688.6 | 3943.1 | 1220.5 | 0.67143 | 5.412
2024-12-10 | 2:01 | Data | 0 | 33.527 | 32.197 | 169.441 | 7.64 | 160.144 | 2211.68 | 25.74 | 45.908 | 6.4 | 1.286 | 4.147 | 8386.47 | 1.587 | 97.9 | 76.3 | 1438 | 23 | 5451.2 | 2706.4 | 2696.4 | 3945.8 | 1220.5 | 0.66827 | 5.433
2024-12-10 | 2:01 | Data | 0 | 33.48 | 31.805 | 169.441 | 7.63 | 160.144 | 2213.49 | 25.75 | 45.908 | 6.41 | 1.289 | 4.133 | 8332.2 | 1.614 | 97.9 | 76.2 | 1439 | 22.95 | 5415.9 | 2702.1 | 2690.3 | 3937 | 1220.5 | 0.66925 | 5.421
2024-12-10 | 2:01 | Data | 0 | 33.615 | 32.129 | 169.35 | 7.64 | 160.099 | 2213.49 | 25.74 | 45.998 | 6.41 | 1.289 | 4.124 | 8318.64 | 1.614 | 97.9 | 76.2 | 1439 | 22.95 | 5407.1 | 2707.2 | 2697.2 | 3951.9 | 1220.5 | 0.6674 | 5.413
2024-12-10 | 2:01 | Data | 0 | 33.642 | 32.028 | 169.441 | 7.64 | 160.144 | 2213.49 | 25.74 | 45.998 | 6.4 | 1.292 | 4.131 | 8332.2 | 1.614 | 97.9 | 76.2 | 1438 | 23.04 | 5415.9 | 2711.2 | 2705.8 | 3952.3 | 1220.5 | 0.66982 | 5.423
2024-12-10 | 2:01 | Data | 0 | 33.858 | 32.082 | 169.441 | 7.64 | 160.144 | 2216.2 | 25.74 | 45.998 | 6.41 | 1.289 | 4.132 | 8332.2 | 1.614 | 97.9 | 76.2 | 1441 | 22.95 | 5415.9 | 2711.1 | 2706.1 | 3957.1 | 1220.5 | 0.66702 | 5.42
2024-12-10 | 2:01 | Data | 0 | 33.318 | 32.015 | 169.531 | 7.64 | 160.144 | 2216.2 | 25.74 | 45.998 | 6.4 | 1.296 | 4.146 | 8372.9 | 1.418 | 97.9 | 76.2 | 1440 | 23 | 5442.4 | 2697.9 | 2722.7 | 3958.5 | 1220.5 | 0.66298 | 5.441
2024-12-10 | 2:01 | Data | 0 | 33.588 | 31.799 | 169.35 | 7.64 | 160.144 | 2216.2 | 25.75 | 45.998 | 6.4 | 1.305 | 4.107 | 8386.47 | 1.836 | 97.9 | 75.9 | 1441 | 22.95 | 5451.2 | 2702.1 | 2719.2 | 3962 | 1220.5 | 0.6636 | 5.411
2024-12-10 | 2:01 | Data | 0 | 33.682 | 31.812 | 169.486 | 7.64 | 160.144 | 2216.2 | 25.75 | 45.998 | 6.4 | 1.304 | 4.102 | 8359.34 | 1.661 | 97.9 | 75.9 | 1441 | 23.04 | 5433.6 | 2708.3 | 2724.5 | 3965.4 | 1220.5 | 0.66432 | 5.406
2024-12-10 | 2:01 | Data | 0 | 33.648 | 31.954 | 169.531 | 7.64 | 160.234 | 2216.2 | 25.74 | 45.998 | 6.4 | 1.291 | 4.115 | 8372.9 | 1.884 | 97.9 | 76.1 | 1441 | 23 | 5442.4 | 2707.4 | 2729.9 | 3970.9 | 1220.5 | 0.66323 | 5.406
2024-12-10 | 2:01 | Data | 0 | 33.642 | 31.853 | 169.531 | 7.63 | 160.099 | 2213.49 | 25.75 | 45.998 | 6.4 | 1.291 | 4.112 | 8386.47 | 1.614 | 97.9 | 76.1 | 1439 | 23 | 5451.2 | 2715.5 | 2729.8 | 3975.5 | 1220.5 | 0.6644 | 5.404
2024-12-10 | 2:01 | Data | 0 | 33.642 | 31.812 | 169.441 | 7.64 | 160.144 | 2208.06 | 25.75 | 45.908 | 6.41 | 1.293 | 4.128 | 8386.47 | 1.816 | 97.9 | 76.1 | 1436 | 23 | 5451.2 | 2694.1 | 2685.8 | 3970.2 | 1220.5 | 0.66439 | 5.42
2024-12-10 | 2:01 | Data | 0 | 33.48 | 31.907 | 169.396 | 7.64 | 160.099 | 2213.49 | 25.75 | 45.998 | 6.4 | 1.286 | 4.119 | 8386.47 | 1.418 | 97.9 | 76.2 | 1439 | 22.95 | 5451.2 | 2706.2 | 2731.6 | 3974.1 | 1220.5 | 0.66312 | 5.403
2024-12-10 | 2:01 | Data | 0 | 33.642 | 32.028 | 169.486 | 7.63 | 160.144 | 2213.49 | 25.74 | 45.908 | 6.4 | 1.297 | 4.118 | 8363.86 | 1.614 | 97.9 | 76 | 1439 | 23 | 5436.5 | 2704 | 2717.1 | 3963.6 | 1220.5 | 0.66276 | 5.415
2024-12-10 | 2:02 | Data | 0 | 33.669 | 32.231 | 169.577 | 7.63 | 160.234 | 2214.39 | 25.75 | 45.727 | 6.41 | 1.293 | 4.115 | 8350.29 | 1.506 | 97.9 | 76.1 | 1439 | 22.91 | 5427.7 | 2713.7 | 2693.4 | 3950 | 1220.5 | 0.66813 | 5.408
2024-12-10 | 2:02 | Data | 0 | 33.588 | 32.204 | 169.486 | 7.64 | 160.144 | 2213.49 | 25.74 | 45.637 | 6.41 | 1.299 | 4.124 | 8359.34 | 1.701 | 97.9 | 76 | 1438 | 22.82 | 5433.6 | 2730.7 | 2740.3 | 3990 | 1220.5 | 0.6654 | 5.422
2024-12-10 | 2:02 | Data | 0 | 33.648 | 32.028 | 169.486 | 7.63 | 160.234 | 2213.49 | 25.75 | 45.727 | 6.41 | 1.301 | 4.122 | 8332.2 | 1.445 | 97.9 | 76 | 1438 | 22.86 | 5415.9 | 2687.6 | 2725.6 | 3964 | 1220.5 | 0.6619 | 5.422
2024-12-10 | 2:02 | Data | 0 | 33.635 | 32.028 | 169.486 | 7.64 | 160.234 | 2210.77 | 25.74 | 45.637 | 6.41 | 1.3 | 4.126 | 8332.2 | 1.607 | 97.9 | 76.1 | 1438 | 22.86 | 5415.9 | 2714.7 | 2728.9 | 3973.7 | 1220.5 | 0.66602 | 5.425
2024-12-10 | 2:02 | Data | 0 | 33.642 | 31.826 | 169.396 | 7.64 | 160.099 | 2210.77 | 25.75 | 45.727 | 6.4 | 1.285 | 4.128 | 8305.07 | 1.614 | 97.9 | 76.3 | 1437 | 22.86 | 5398.3 | 2698.1 | 2741.3 | 3983.6 | 1220.6 | 0.66252 | 5.413
2024-12-10 | 2:02 | Data | 0 | 33.527 | 31.913 | 169.531 | 7.64 | 160.234 | 2208.97 | 25.75 | 45.637 | 6.4 | 1.283 | 4.143 | 8305.07 | 1.715 | 97.9 | 76.3 | 1435 | 22.82 | 5398.3 | 2710.5 | 2734.5 | 3976.2 | 1220.6 | 0.66303 | 5.426
2024-12-10 | 2:02 | Data | 0 | 33.642 | 32.028 | 169.486 | 7.64 | 160.144 | 2203.54 | 25.74 | 45.727 | 6.41 | 1.293 | 4.142 | 8291.5 | 1.627 | 97.9 | 76.2 | 1432 | 22.86 | 5389.5 | 2708.5 | 2734.1 | 3976.6 | 1220.6 | 0.66003 | 5.434
2024-12-10 | 2:02 | Data | 0 | 33.628 | 31.913 | 169.531 | 7.64 | 160.099 | 2208.06 | 25.75 | 45.818 | 6.4 | 1.296 | 4.115 | 8291.5 | 1.62 | 97.9 | 76.1 | 1436 | 22.86 | 5389.5 | 2696 | 2720.5 | 3963.3 | 1220.6 | 0.66095 | 5.411
2024-12-10 | 2:02 | Data | 0 | 33.642 | 32.028 | 169.441 | 7.64 | 160.144 | 2208.97 | 25.74 | 45.727 | 6.4 | 1.299 | 4.094 | 8305.07 | 1.614 | 97.9 | 75.9 | 1435 | 22.86 | 5398.3 | 2700.4 | 2696.2 | 3940.9 | 1220.6 | 0.66628 | 5.392
2024-12-10 | 2:02 | Data | 0 | 33.756 | 32.366 | 169.531 | 7.64 | 160.189 | 2208.06 | 25.74 | 45.727 | 6.41 | 1.287 | 4.113 | 8305.07 | 1.62 | 97.9 | 76.2 | 1435 | 22.86 | 5398.3 | 2702.9 | 2734.7 | 3972.7 | 1220.6 | 0.66203 | 5.4
2024-12-10 | 2:02 | Data | 0 | 34.074 | 32.035 | 169.577 | 7.64 | 160.189 | 2208.06 | 25.75 | 45.727 | 6.4 | 1.284 | 4.114 | 8305.07 | 1.553 | 97.9 | 76.2 | 1435 | 22.86 | 5398.3 | 2713.2 | 2734.8 | 3979.1 | 1220.6 | 0.66292 | 5.398
2024-12-10 | 2:02 | Data | 0 | 33.642 | 32.204 | 169.441 | 7.64 | 160.144 | 2208.97 | 25.74 | 45.727 | 6.41 | 1.293 | 4.131 | 8291.5 | 1.614 | 97.9 | 76.2 | 1436 | 22.86 | 5389.5 | 2723 | 2723.6 | 3973.6 | 1220.6 | 0.6657 | 5.423
2024-12-10 | 2:02 | Data | 0 | 33.642 | 31.913 | 169.486 | 7.64 | 160.144 | 2209.87 | 25.74 | 45.727 | 6.4 | 1.287 | 4.134 | 8318.64 | 1.614 | 97.9 | 76.3 | 1437 | 22.86 | 5407.1 | 2706 | 2742 | 3978.9 | 1220.6 | 0.6629 | 5.42
2024-12-10 | 2:02 | Data | 0 | 33.615 | 31.974 | 169.441 | 7.64 | 160.099 | 2211.68 | 25.74 | 45.637 | 6.41 | 1.277 | 4.136 | 8314.11 | 1.83 | 97.9 | 76.4 | 1438 | 22.86 | 5404.2 | 2711.6 | 2736 | 3975.8 | 1220.6 | 0.66131 | 5.411
2024-12-10 | 2:02 | Data | 0 | 33.588 | 32.021 | 169.486 | 7.63 | 160.144 | 2213.49 | 25.74 | 45.727 | 6.41 | 1.292 | 4.136 | 8309.59 | 1.614 | 97.9 | 76.2 | 1439 | 22.86 | 5401.2 | 2709 | 2730.4 | 3972.4 | 1220.6 | 0.66286 | 5.429
2024-12-10 | 2:02 | Data | 0 | 33.642 | 32.028 | 169.441 | 7.64 | 160.099 | 2213.49 | 25.75 | 45.727 | 6.41 | 1.299 | 4.118 | 8300.55 | 1.668 | 97.9 | 76 | 1439 | 22.86 | 5395.4 | 2720.6 | 2749.2 | 3994.1 | 1220.6 | 0.6618 | 5.418
2024-12-10 | 2:02 | Data | 0 | 33.864 | 32.042 | 169.486 | 7.64 | 160.144 | 2207.16 | 25.74 | 45.727 | 6.4 | 1.289 | 4.129 | 8305.07 | 1.782 | 97.9 | 76.2 | 1435 | 22.86 | 5398.3 | 2694.1 | 2751.3 | 3980.9 | 1220.6 | 0.65866 | 5.418
2024-12-10 | 2:02 | Data | 0 | 33.81 | 32.042 | 169.396 | 7.63 | 160.189 | 2210.77 | 25.75 | 45.727 | 6.41 | 1.283 | 4.124 | 8291.5 | 1.782 | 97.9 | 76.3 | 1437 | 22.82 | 5389.5 | 2709.8 | 2698.7 | 3952.6 | 1220.6 | 0.66432 | 5.408
2024-12-10 | 2:02 | Data | 0 | 33.891 | 32.096 | 169.486 | 7.64 | 160.234 | 2211.68 | 25.74 | 45.908 | 6.41 | 1.28 | 4.109 | 8309.59 | 1.58 | 97.9 | 76.3 | 1438 | 23 | 5401.2 | 2712.3 | 2712.8 | 3965.1 | 1220.6 | 0.66651 | 5.389
2024-12-10 | 2:03 | Data | 0 | 33.642 | 32.035 | 169.577 | 7.64 | 160.189 | 2210.77 | 25.75 | 45.637 | 6.41 | 1.294 | 4.128 | 8314.11 | 1.6 | 97.9 | 76.1 | 1436 | 22.86 | 5404.2 | 2703.4 | 2710.3 | 3955.8 | 1220.6 | 0.66575 | 5.421
2024-12-10 | 2:03 | Data | 0 | 33.77 | 31.92 | 169.531 | 7.63 | 160.234 | 2208.06 | 25.74 | 45.998 | 6.4 | 1.301 | 4.121 | 8336.72 | 1.647 | 97.9 | 76 | 1435 | 22.95 | 5418.9 | 2716.9 | 2706.2 | 3963.1 | 1220.6 | 0.66329 | 5.421
2024-12-10 | 2:03 | Data | 0 | 33.972 | 32.143 | 169.531 | 7.64 | 160.234 | 2211.68 | 25.74 | 45.998 | 6.4 | 1.293 | 4.131 | 8323.16 | 1.519 | 97.9 | 76.2 | 1438 | 23 | 5410.1 | 2709.2 | 2757.7 | 3992.8 | 1220.6 | 0.66 | 5.425
2024-12-10 | 2:03 | Data | 0 | 33.54 | 32.028 | 169.531 | 7.64 | 160.189 | 2208.97 | 25.74 | 45.998 | 6.4 | 1.293 | 4.113 | 8336.72 | 1.452 | 97.9 | 76.1 | 1436 | 23 | 5418.9 | 2701.2 | 2750.1 | 3981.7 | 1220.6 | 0.66002 | 5.407
2024-12-10 | 2:03 | Data | 0 | 33.642 | 32.251 | 169.531 | 7.64 | 160.234 | 2210.77 | 25.74 | 45.998 | 6.4 | 1.299 | 4.124 | 8336.72 | 1.519 | 97.9 | 76 | 1437 | 23 | 5418.9 | 2708.6 | 2762.4 | 3992.6 | 1220.6 | 0.66271 | 5.423
2024-12-10 | 2:03 | Data | 0 | 33.669 | 32.028 | 169.531 | 7.64 | 160.189 | 2216.2 | 25.75 | 45.727 | 6.4 | 1.293 | 4.134 | 8314.11 | 1.62 | 97.9 | 76.2 | 1441 | 22.86 | 5404.2 | 2708.6 | 2747.9 | 3986.9 | 1220.6 | 0.66005 | 5.428
2024-12-10 | 2:03 | Data | 0 | 33.642 | 32.028 | 169.396 | 7.63 | 160.189 | 2216.2 | 25.74 | 45.908 | 6.41 | 1.282 | 4.151 | 8332.2 | 1.438 | 97.9 | 76.4 | 1441 | 22.95 | 5415.9 | 2717.1 | 2726.5 | 3970.9 | 1220.6 | 0.66575 | 5.432
2024-12-10 | 2:03 | Data | 0 | 33.642 | 32.028 | 169.396 | 7.64 | 160.144 | 2216.2 | 25.75 | 45.998 | 6.41 | 1.284 | 4.122 | 8359.34 | 1.614 | 97.9 | 76.2 | 1441 | 23 | 5433.6 | 2690.7 | 2719.6 | 3951.3 | 1220.6 | 0.66244 | 5.406
2024-12-10 | 2:03 | Data | 0 | 34.074 | 31.913 | 169.531 | 7.64 | 160.279 | 2218.91 | 25.75 | 45.998 | 6.4 | 1.291 | 4.127 | 8359.34 | 1.661 | 97.9 | 76.2 | 1442 | 22.95 | 5433.6 | 2713.2 | 2725.1 | 3967.4 | 1220.6 | 0.66463 | 5.418
2024-12-10 | 2:03 | Data | 0 | 33.446 | 32.028 | 169.486 | 7.63 | 160.189 | 2216.2 | 25.73 | 45.908 | 6.41 | 1.289 | 4.115 | 8332.2 | 1.398 | 97.9 | 76.1 | 1441 | 22.95 | 5415.9 | 2712.8 | 2721.2 | 3970.2 | 1220.6 | 0.66436 | 5.403
2024-12-10 | 2:03 | Data | 0 | 33.972 | 31.873 | 169.577 | 7.64 | 160.279 | 2216.2 | 25.75 | 46.089 | 6.4 | 1.289 | 4.132 | 8332.2 | 1.782 | 97.9 | 76.2 | 1441 | 23 | 5415.9 | 2701.7 | 2692.3 | 3938.8 | 1220.6 | 0.66654 | 5.42
2024-12-10 | 2:03 | Data | 0 | 33.642 | 32.028 | 169.441 | 7.64 | 160.189 | 2217.1 | 25.75 | 45.998 | 6.41 | 1.282 | 4.143 | 8332.2 | 1.62 | 97.9 | 76.4 | 1441 | 22.91 | 5415.9 | 2713 | 2677.1 | 3937.1 | 1220.6 | 0.6716 | 5.426
2024-12-10 | 2:03 | Data | 0 | 33.486 | 32.028 | 169.531 | 7.64 | 160.189 | 2217.1 | 25.74 | 45.908 | 6.4 | 1.288 | 4.116 | 8323.16 | 1.404 | 97.9 | 76.2 | 1441 | 23 | 5410.1 | 2713.5 | 2667.4 | 3929.2 | 1220.6 | 0.67165 | 5.405
2024-12-10 | 2:03 | Data | 0 | 33.426 | 31.826 | 169.486 | 7.64 | 160.189 | 2216.2 | 25.74 | 45.908 | 6.41 | 1.285 | 4.093 | 8368.38 | 1.499 | 97.9 | 76.1 | 1441 | 22.95 | 5439.4 | 2692.6 | 2672.4 | 3918.8 | 1220.6 | 0.66824 | 5.378
2024-12-10 | 2:03 | Data | 0 | 33.446 | 31.927 | 169.531 | 7.64 | 160.234 | 2220.72 | 25.74 | 45.998 | 6.41 | 1.283 | 4.115 | 8381.95 | 1.803 | 97.9 | 76.2 | 1443 | 23 | 5448.3 | 2701.5 | 2687.9 | 3937.9 | 1220.6 | 0.66846 | 5.399
2024-12-10 | 2:03 | Data | 0 | 33.75 | 32.15 | 169.531 | 7.64 | 160.189 | 2218.91 | 25.75 | 46.089 | 6.4 | 1.285 | 4.13 | 8386.47 | 1.62 | 97.9 | 76.3 | 1443 | 22.95 | 5451.2 | 2711 | 2707.7 | 3959.9 | 1220.6 | 0.66632 | 5.415
2024-12-10 | 2:03 | Data | 0 | 33.642 | 32.028 | 169.486 | 7.64 | 160.234 | 2216.2 | 25.74 | 45.727 | 6.4 | 1.282 | 4.145 | 8381.95 | 1.614 | 97.9 | 76.4 | 1441 | 22.82 | 5448.3 | 2703.3 | 2708.5 | 3955.1 | 1220.6 | 0.66512 | 5.427
2024-12-10 | 2:04 | Data | 0 | 33.642 | 32.055 | 169.577 | 7.64 | 160.234 | 2218 | 25.75 | 45.727 | 6.4 | 1.291 | 4.155 | 8386.47 | 1.614 | 97.9 | 76.3 | 1442 | 22.91 | 5451.2 | 2702.1 | 2699.7 | 3949.5 | 1220.6 | 0.66495 | 5.447
2024-12-10 | 2:04 | Data | 0 | 33.642 | 32.204 | 169.577 | 7.64 | 160.279 | 2218.91 | 25.75 | 45.637 | 6.4 | 1.299 | 4.148 | 8381.95 | 1.614 | 97.9 | 76.2 | 1442 | 22.82 | 5448.3 | 2718 | 2752.3 | 3992.4 | 1220.6 | 0.66008 | 5.447
2024-12-10 | 2:04 | Data | 0 | 33.743 | 32.42 | 169.622 | 7.64 | 160.189 | 2218.91 | 25.75 | 45.727 | 6.4 | 1.284 | 4.122 | 8386.47 | 1.681 | 97.9 | 76.2 | 1442 | 22.86 | 5451.2 | 2705.1 | 2745.3 | 3981.2 | 1220.6 | 0.6616 | 5.407
2024-12-10 | 2:04 | Data | 0 | 33.925 | 31.832 | 169.531 | 7.64 | 160.189 | 2218.91 | 25.74 | 45.727 | 6.4 | 1.282 | 4.12 | 8386.47 | 1.627 | 97.9 | 76.3 | 1442 | 22.86 | 5451.2 | 2712.8 | 2729.7 | 3975.5 | 1220.6 | 0.66421 | 5.404
2024-12-10 | 2:04 | Data | 0 | 33.837 | 32.264 | 169.531 | 7.64 | 160.144 | 2227.95 | 25.74 | 45.637 | 6.41 | 1.299 | 4.159 | 8350.29 | 1.695 | 97.9 | 76.2 | 1448 | 22.86 | 5427.7 | 2713.5 | 2713 | 3962.9 | 1220.6 | 0.66577 | 5.458
2024-12-10 | 2:04 | Data | 0 | 33.554 | 32.028 | 169.531 | 7.64 | 160.144 | 2217.1 | 25.74 | 45.727 | 6.4 | 1.301 | 4.149 | 8345.77 | 1.6 | 97.9 | 76.1 | 1441 | 22.86 | 5424.8 | 2696.8 | 2706.4 | 3947.3 | 1220.6 | 0.66543 | 5.449
2024-12-10 | 2:04 | Data | 0 | 33.675 | 32.406 | 169.531 | 7.64 | 160.279 | 2216.2 | 25.75 | 45.998 | 6.41 | 1.295 | 4.125 | 8359.34 | 1.607 | 97.9 | 76.1 | 1441 | 23 | 5433.6 | 2690.4 | 2707.8 | 3947.6 | 1220.6 | 0.66239 | 5.421
2024-12-10 | 2:04 | Data | 0 | 33.628 | 31.913 | 169.486 | 7.63 | 160.099 | 2216.2 | 25.75 | 45.998 | 6.41 | 1.295 | 4.129 | 8359.34 | 1.836 | 97.9 | 76.1 | 1441 | 23 | 5433.6 | 2706.3 | 2694.4 | 3950.6 | 1220.7 | 0.66738 | 5.423
2024-12-10 | 2:04 | Data | 0 | 33.858 | 32.237 | 169.622 | 7.64 | 160.189 | 2214.39 | 25.75 | 45.908 | 6.4 | 1.291 | 4.115 | 8372.9 | 1.708 | 97.9 | 76.1 | 1439 | 22.95 | 5442.4 | 2710.4 | 2701.9 | 3954 | 1220.7 | 0.66733 | 5.406
2024-12-10 | 2:04 | Data | 0 | 33.601 | 32.15 | 169.486 | 7.64 | 160.189 | 2216.2 | 25.74 | 45.908 | 6.41 | 1.283 | 4.114 | 8368.38 | 1.782 | 97.9 | 76.2 | 1441 | 22.95 | 5439.4 | 2690.6 | 2689.6 | 3936 | 1220.7 | 0.66503 | 5.397
2024-12-10 | 2:04 | Data | 0 | 33.554 | 32.008 | 169.577 | 7.64 | 160.234 | 2216.2 | 25.75 | 45.998 | 6.4 | 1.285 | 4.121 | 8345.77 | 1.445 | 97.9 | 76.2 | 1441 | 23 | 5424.8 | 2702.3 | 2697.9 | 3948.5 | 1220.7 | 0.6655 | 5.405
2024-12-10 | 2:04 | Data | 0 | 33.858 | 32.042 | 169.531 | 7.64 | 160.189 | 2218.91 | 25.74 | 45.998 | 6.4 | 1.291 | 4.15 | 8350.29 | 1.722 | 97.9 | 76.3 | 1442 | 23 | 5427.7 | 2693.6 | 2697.3 | 3941.2 | 1220.7 | 0.66523 | 5.441
2024-12-10 | 2:04 | Data | 0 | 33.871 | 32.055 | 169.531 | 7.64 | 160.189 | 2221.62 | 25.75 | 45.998 | 6.4 | 1.293 | 4.118 | 8350.29 | 1.641 | 97.9 | 76.1 | 1444 | 23 | 5427.7 | 2712.4 | 2710.6 | 3964.9 | 1220.7 | 0.66641 | 5.412
2024-12-10 | 2:04 | Data | 0 | 33.777 | 32.204 | 169.577 | 7.64 | 160.234 | 2254.16 | 25.74 | 45.908 | 6.4 | 1.297 | 4.12 | 8332.2 | 1.587 | 98 | 76.1 | 1467 | 23 | 5415.9 | 2708.9 | 2722.4 | 3967 | 1220.7 | 0.66448 | 5.417
2024-12-10 | 2:04 | Data | 0 | 33.486 | 31.981 | 169.577 | 7.63 | 160.279 | 2268.62 | 25.74 | 45.998 | 6.4 | 1.288 | 4.113 | 8336.72 | 1.438 | 98 | 76.2 | 1475 | 23 | 5418.9 | 2706.6 | 2720.3 | 3965.1 | 1220.7 | 0.66399 | 5.4
2024-12-10 | 2:04 | Data | 0 | 33.527 | 32.129 | 169.396 | 7.64 | 160.189 | 2268.62 | 25.75 | 45.998 | 6.4 | 1.279 | 4.114 | 8336.72 | 1.553 | 98 | 76.3 | 1475 | 23 | 5418.9 | 2706.1 | 2735.5 | 3979.6 | 1220.7 | 0.66002 | 5.392
2024-12-10 | 2:04 | Data | 0 | 33.642 | 32.258 | 169.577 | 7.63 | 160.279 | 2268.62 | 25.74 | 45.998 | 6.4 | 1.293 | 4.122 | 8318.64 | 1.6 | 98 | 76.1 | 1475 | 22.95 | 5407.1 | 2699 | 2709.9 | 3952 | 1220.7 | 0.66378 | 5.415
2024-12-10 | 2:04 | Data | 0 | 33.642 | 32.055 | 169.577 | 7.64 | 160.189 | 2266.81 | 25.75 | 45.998 | 6.4 | 1.291 | 4.129 | 8305.07 | 1.728 | 98 | 76.2 | 1470 | 23 | 5398.3 | 2713.8 | 2702.1 | 3955.3 | 1220.7 | 0.66834 | 5.42
2024-12-10 | 2:05 | Data | 0 | 33.642 | 32.028 | 169.486 | 7.64 | 160.144 | 2215.29 | 25.75 | 45.998 | 6.4 | 1.288 | 4.139 | 8300.55 | 1.614 | 97.9 | 76.3 | 1440 | 23 | 5395.4 | 1641.7 | 2107.6 | 2683.1 | 1220.7 | 0.60861 | 5.428
2024-12-10 | 2:05 | Data | 0 | 33.615 | 32.042 | 169.622 | 7.64 | 160.144 | 2211.68 | 25.74 | 45.998 | 6.4 | 1.287 | 4.122 | 8291.5 | 1.796 | 97.9 | 76.2 | 1438 | 23 | 5389.5 | 1625.8 | 2112.3 | 2680.5 | 1220.7 | 0.60266 | 5.41
2024-12-10 | 2:05 | Data | 0 | 33.642 | 32.028 | 169.441 | 7.64 | 160.144 | 2213.49 | 25.75 | 45.908 | 6.41 | 1.289 | 4.113 | 8300.55 | 1.614 | 97.9 | 76.1 | 1439 | 23 | 5395.4 | 1632.6 | 2097.1 | 2672.1 | 1220.7 | 0.60734 | 5.401
2024-12-10 | 2:05 | Data | 0 | 33.419 | 31.974 | 169.486 | 7.64 | 160.189 | 2213.49 | 25.74 | 45.908 | 6.4 | 1.29 | 4.124 | 8305.07 | 1.607 | 97.9 | 76.2 | 1439 | 22.91 | 5398.3 | 1621.1 | 2086.2 | 2654.4 | 1220.7 | 0.60816 | 5.414
2024-12-10 | 2:05 | Data | 0 | 33.696 | 32.082 | 169.531 | 7.64 | 160.234 | 2210.77 | 25.75 | 45.908 | 6.4 | 1.291 | 4.143 | 8314.11 | 1.566 | 97.9 | 76.2 | 1438 | 23 | 5404.2 | 1624.6 | 2130.9 | 2691.9 | 1220.7 | 0.60135 | 5.435
2024-12-10 | 2:05 | Data | 0 | 33.642 | 32.264 | 169.577 | 7.64 | 160.279 | 2211.68 | 25.75 | 45.908 | 6.41 | 1.28 | 4.139 | 8318.64 | 1.607 | 97.9 | 76.4 | 1438 | 22.95 | 5407.1 | 1621.3 | 2110.1 | 2675.8 | 1220.7 | 0.60222 | 5.42
2024-12-10 | 2:05 | Data | 0 | 33.655 | 32.048 | 169.441 | 7.64 | 160.189 | 2209.87 | 25.74 | 46.089 | 6.4 | 1.279 | 4.109 | 8540.22 | 1.573 | 97.9 | 76.3 | 1437 | 23 | 5551.1 | 1646.5 | 2133.8 | 2707.8 | 1220.7 | 0.60052 | 5.387
2024-12-10 | 2:05 | Data | 0 | 33.642 | 32.123 | 169.486 | 7.64 | 160.189 | 2211.68 | 25.75 | 45.998 | 6.41 | 1.291 | 4.129 | 8535.7 | 1.668 | 97.9 | 76.2 | 1437 | 22.95 | 5548.2 | 1629.2 | 2140.7 | 2704 | 1220.7 | 0.60008 | 5.42
2024-12-10 | 2:05 | Data | 0 | 33.864 | 31.94 | 169.577 | 7.64 | 160.234 | 2209.87 | 25.74 | 45.908 | 6.4 | 1.285 | 4.143 | 8535.7 | 1.668 | 97.9 | 76.3 | 1437 | 23 | 5548.2 | 1626.7 | 2090.7 | 2661.2 | 1220.7 | 0.60856 | 5.427
2024-12-10 | 2:05 | Data | 0 | 33.642 | 32.028 | 169.441 | 7.64 | 160.144 | 2211.68 | 25.75 | 45.727 | 6.4 | 1.29 | 4.15 | 8526.66 | 1.614 | 97.9 | 76.3 | 1438 | 22.86 | 5542.3 | 1625.1 | 2096.9 | 2666.9 | 1220.7 | 0.60655 | 5.439
2024-12-10 | 2:05 | Data | 0 | 34.04 | 32.096 | 169.441 | 7.64 | 160.189 | 2210.77 | 25.75 | 45.727 | 6.4 | 1.286 | 4.151 | 8323.16 | 1.688 | 97.9 | 76.3 | 1438 | 22.82 | 5410.1 | 1614.3 | 2108.2 | 2668.9 | 1220.7 | 0.60137 | 5.438
2024-12-10 | 2:05 | Data | 0 | 33.642 | 31.974 | 169.441 | 7.64 | 160.189 | 2210.77 | 25.74 | 45.727 | 6.4 | 1.29 | 4.14 | 8318.64 | 1.668 | 97.9 | 76.2 | 1436 | 22.86 | 5407.1 | 1628.7 | 2096.2 | 2668.3 | 1220.7 | 0.60657 | 5.43
2024-12-10 | 2:05 | Data | 0 | 33.756 | 32.055 | 169.441 | 7.64 | 160.189 | 2211.68 | 25.75 | 45.727 | 6.41 | 1.287 | 4.141 | 8314.11 | 1.776 | 97.9 | 76.3 | 1438 | 22.86 | 5404.2 | 1619.9 | 2083.2 | 2652.7 | 1220.7 | 0.60809 | 5.429
2024-12-10 | 2:05 | Data | 0 | 33.655 | 31.913 | 169.577 | 7.64 | 160.189 | 2211.68 | 25.74 | 45.637 | 6.4 | 1.288 | 4.122 | 8305.07 | 1.614 | 97.9 | 76.2 | 1437 | 22.86 | 5398.3 | 1610.6 | 2077.7 | 2647.5 | 1220.7 | 0.60778 | 5.411
2024-12-10 | 2:05 | Data | 0 | 33.642 | 32.251 | 169.486 | 7.64 | 160.189 | 2210.77 | 25.75 | 45.727 | 6.4 | 1.285 | 4.12 | 8291.5 | 1.519 | 97.9 | 76.2 | 1437 | 22.86 | 5389.5 | 1620.6 | 2071 | 2644.7 | 1220.7 | 0.60982 | 5.406
2024-12-10 | 2:05 | Data | 0 | 33.871 | 32.035 | 169.622 | 7.64 | 160.279 | 2208.97 | 25.73 | 45.727 | 6.4 | 1.276 | 4.124 | 8291.5 | 1.654 | 97.9 | 76.4 | 1436 | 22.82 | 5389.5 | 1632.2 | 2084.3 | 2661.2 | 1220.7 | 0.60986 | 5.401
2024-12-10 | 2:05 | Data | 0 | 33.696 | 32.035 | 169.531 | 7.64 | 160.279 | 2208.06 | 25.74 | 45.727 | 6.4 | 1.28 | 4.141 | 8286.98 | 1.587 | 97.9 | 76.4 | 1435 | 22.86 | 5386.5 | 1622.1 | 2078.8 | 2649.2 | 1220.7 | 0.60965 | 5.421
2024-12-10 | 2:06 | Data | 0 | 33.858 | 32.143 | 169.486 | 7.64 | 160.144 | 2208.97 | 25.75 | 45.637 | 6.4 | 1.29 | 4.116 | 8286.98 | 1.614 | 97.9 | 76.1 | 1436 | 22.82 | 5386.5 | 1631.6 | 2077.1 | 2655.4 | 1220.7 | 0.61192 | 5.406
2024-12-10 | 2:06 | Data | 0 | 33.682 | 31.988 | 169.622 | 7.64 | 160.189 | 2208.06 | 25.74 | 45.727 | 6.4 | 1.285 | 4.113 | 8318.64 | 1.701 | 97.9 | 76.2 | 1435 | 22.86 | 5407.1 | 1620.4 | 2093.5 | 2661.4 | 1220.7 | 0.60584 | 5.398
2024-12-10 | 2:06 | Data | 0 | 33.642 | 32.028 | 169.441 | 7.64 | 160.099 | 2208.06 | 25.75 | 45.727 | 6.4 | 1.289 | 4.145 | 8318.64 | 1.614 | 97.9 | 76.3 | 1436 | 22.86 | 5407.1 | 1610.8 | 2081.3 | 2643.5 | 1220.7 | 0.60702 | 5.434
2024-12-10 | 2:06 | Data | 0 | 33.628 | 31.859 | 169.441 | 7.64 | 160.234 | 2208.06 | 25.74 | 45.727 | 6.4 | 1.291 | 4.136 | 8318.64 | 1.836 | 97.9 | 76.2 | 1435 | 22.82 | 5407.1 | 1625.5 | 2096.3 | 2666.9 | 1220.7 | 0.6072 | 5.427
2024-12-10 | 2:06 | Data | 0 | 33.844 | 32.264 | 169.667 | 7.64 | 160.234 | 2210.77 | 25.75 | 45.727 | 6.4 | 1.287 | 4.13 | 8309.59 | 1.6 | 97.9 | 76.2 | 1437 | 22.86 | 5401.2 | 1633.4 | 2093.9 | 2669.1 | 1220.7 | 0.60919 | 5.417
2024-12-10 | 2:06 | Data | 0 | 33.729 | 32.028 | 169.577 | 7.64 | 160.234 | 2208.97 | 25.75 | 45.637 | 6.4 | 1.277 | 4.156 | 8332.2 | 1.425 | 97.9 | 76.5 | 1435 | 22.86 | 5415.9 | 1630.2 | 2093.7 | 2666 | 1220.7 | 0.6092 | 5.432
2024-12-10 | 2:06 | Data | 0 | 33.412 | 32.021 | 169.486 | 7.63 | 160.144 | 2207.16 | 25.75 | 45.727 | 6.4 | 1.286 | 4.142 | 8336.72 | 1.506 | 97.9 | 76.3 | 1435 | 22.86 | 5418.9 | 1626.7 | 2103 | 2671 | 1220.7 | 0.60719 | 5.428
2024-12-10 | 2:06 | Data | 0 | 33.669 | 31.981 | 169.531 | 7.64 | 160.234 | 2208.06 | 25.74 | 45.727 | 6.4 | 1.288 | 4.132 | 8336.72 | 1.641 | 97.9 | 76.2 | 1436 | 22.86 | 5418.9 | 1625.8 | 2082.7 | 2652.9 | 1220.7 | 0.61089 | 5.42
2024-12-10 | 2:06 | Data | 0 | 33.628 | 32.015 | 169.441 | 7.64 | 160.189 | 2208.97 | 25.74 | 45.727 | 6.4 | 1.288 | 4.136 | 8336.72 | 1.627 | 97.9 | 76.3 | 1436 | 22.86 | 5418.9 | 1625.2 | 2088 | 2653.4 | 1220.7 | 0.60966 | 5.424
2024-12-10 | 2:06 | Data | 0 | 33.642 | 31.799 | 169.486 | 7.64 | 160.189 | 2208.06 | 25.75 | 45.818 | 6.4 | 1.297 | 4.146 | 8318.64 | 1.83 | 97.9 | 76.2 | 1436 | 22.86 | 5407.1 | 1623.5 | 2084.1 | 2655.6 | 1220.7 | 0.60652 | 5.443
2024-12-10 | 2:06 | Data | 0 | 33.432 | 32.001 | 169.441 | 7.64 | 160.144 | 2203.54 | 25.75 | 45.727 | 6.4 | 1.295 | 4.128 | 8318.64 | 1.445 | 97.9 | 76.1 | 1433 | 22.82 | 5407.1 | 1617.2 | 2070.3 | 2642.7 | 1220.7 | 0.61108 | 5.422
2024-12-10 | 2:06 | Data | 0 | 33.864 | 31.812 | 169.531 | 7.64 | 160.234 | 2208.97 | 25.75 | 45.637 | 6.4 | 1.295 | 4.119 | 8309.59 | 1.803 | 97.9 | 76.1 | 1435 | 22.82 | 5401.2 | 1612.3 | 2072 | 2640.1 | 1220.7 | 0.60903 | 5.413
2024-12-10 | 2:06 | Data | 0 | 33.925 | 32.042 | 169.531 | 7.64 | 160.279 | 2208.97 | 25.74 | 45.727 | 6.4 | 1.28 | 4.102 | 8300.55 | 1.674 | 97.9 | 76.2 | 1435 | 22.82 | 5395.4 | 1615.6 | 2061.5 | 2631.3 | 1220.7 | 0.61189 | 5.382
2024-12-10 | 2:06 | Data | 0 | 33.642 | 32.075 | 169.531 | 7.64 | 160.144 | 2208.97 | 25.75 | 45.637 | 6.41 | 1.282 | 4.124 | 8318.64 | 1.512 | 97.9 | 76.3 | 1435 | 22.86 | 5407.1 | 1620.5 | 2080.7 | 2650.1 | 1220.7 | 0.60897 | 5.405
2024-12-10 | 2:06 | Data | 0 | 33.743 | 31.853 | 169.35 | 7.64 | 160.144 | 2208.06 | 25.75 | 45.727 | 6.4 | 1.292 | 4.137 | 8332.2 | 1.755 | 97.9 | 76.2 | 1435 | 22.91 | 5415.9 | 1619.8 | 2109.2 | 2672.9 | 1220.7 | 0.60328 | 5.43
2024-12-10 | 2:06 | Data | 0 | 34.087 | 32.035 | 169.577 | 7.64 | 160.234 | 2231.56 | 25.74 | 45.727 | 6.4 | 1.287 | 4.096 | 8332.2 | 1.512 | 98 | 76.1 | 1458 | 22.86 | 5415.9 | 1633.4 | 2108.7 | 2676.9 | 1220.7 | 0.60513 | 5.383
2024-12-10 | 2:06 | Data | 0 | 33.642 | 31.826 | 169.486 | 7.64 | 160.189 | 2265.91 | 25.75 | 45.727 | 6.4 | 1.282 | 4.098 | 8336.72 | 1.56 | 98 | 76.2 | 1472 | 22.86 | 5418.9 | 1620.8 | 2097.5 | 2663.6 | 1220.7 | 0.608 | 5.38
2024-12-10 | 2:06 | Data | 0 | 33.459 | 31.974 | 169.441 | 7.64 | 160.189 | 2265.91 | 25.75 | 45.637 | 6.41 | 1.282 | 4.122 | 8684.94 | 1.445 | 98 | 76.3 | 1473 | 22.82 | 5645.2 | 1613.8 | 2086.6 | 2653.1 | 1220.7 | 0.60523 | 5.404
2024-12-10 | 2:07 | Data | 0 | 33.642 | 32.028 | 169.486 | 7.64 | 160.144 | 2265.91 | 25.75 | 45.727 | 6.4 | 1.293 | 4.163 | 8449.78 | 1.614 | 98 | 76.3 | 1473 | 22.86 | 5492.4 | 1624.1 | 2077.3 | 2652.8 | 1220.7 | 0.60999 | 5.457
2024-12-10 | 2:07 | Data | 0 | 33.642 | 32.028 | 169.531 | 7.64 | 160.189 | 2268.62 | 25.75 | 45.727 | 6.4 | 1.287 | 4.163 | 8671.37 | 1.627 | 98 | 76.4 | 1475 | 22.86 | 5636.4 | 1615.1 | 2093 | 2657.1 | 1220.7 | 0.60564 | 5.451
2024-12-10 | 2:07 | Data | 0 | 33.304 | 31.974 | 169.531 | 7.63 | 160.144 | 2213.49 | 25.75 | 45.727 | 6.4 | 1.283 | 4.14 | 8562.84 | 1.587 | 97.9 | 76.3 | 1439 | 22.82 | 5565.8 | 1624.4 | 2092.8 | 2662.8 | 1220.7 | 0.60744 | 5.423
2024-12-10 | 2:07 | Data | 0 | 33.642 | 32.136 | 169.531 | 7.64 | 160.234 | 2213.49 | 25.75 | 45.727 | 6.4 | 1.285 | 4.109 | 8454.3 | 1.614 | 97.9 | 76.2 | 1439 | 22.86 | 5495.3 | 1648.7 | 2101.4 | 2682.6 | 1220.7 | 0.61252 | 5.394
2024-12-10 | 2:07 | Data | 0 | 33.615 | 32.028 | 169.577 | 7.64 | 160.234 | 2213.49 | 25.75 | 45.727 | 6.4 | 1.297 | 4.105 | 8436.21 | 1.695 | 97.9 | 76 | 1439 | 22.86 | 5483.5 | 1630.7 | 2079.5 | 2655.2 | 1220.7 | 0.611 | 5.401
2024-12-10 | 2:07 | Data | 0 | 33.412 | 31.799 | 169.396 | 7.64 | 160.099 | 2218.91 | 25.75 | 45.727 | 6.41 | 1.283 | 4.11 | 8409.08 | 1.614 | 97.9 | 76.2 | 1442 | 22.86 | 5465.9 | 1621.6 | 2086.6 | 2655.9 | 1220.7 | 0.60762 | 5.393
2024-12-10 | 2:07 | Data | 0 | 33.743 | 32.042 | 169.486 | 7.64 | 160.189 | 2213.49 | 25.74 | 45.727 | 6.4 | 1.286 | 4.116 | 8418.13 | 1.782 | 97.9 | 76.2 | 1439 | 22.86 | 5471.8 | 1628.8 | 2076.8 | 2652.4 | 1220.7 | 0.61137 | 5.402
2024-12-10 | 2:07 | Data | 0 | 33.588 | 32.028 | 169.486 | 7.64 | 160.189 | 2213.49 | 25.74 | 45.727 | 6.4 | 1.29 | 4.143 | 8404.56 | 1.661 | 97.9 | 76.3 | 1439 | 22.86 | 5463 | 1603.2 | 2091.8 | 2648.9 | 1220.7 | 0.60178 | 5.432
2024-12-10 | 2:07 | Data | 0 | 33.473 | 31.913 | 169.531 | 7.63 | 160.189 | 2216.2 | 25.75 | 45.727 | 6.41 | 1.292 | 4.152 | 8544.75 | 1.614 | 97.9 | 76.3 | 1441 | 22.82 | 5554.1 | 1623.4 | 2084.7 | 2656.2 | 1220.7 | 0.60839 | 5.446
2024-12-10 | 2:07 | Data | 0 | 33.804 | 32.305 | 169.486 | 7.63 | 160.189 | 2214.39 | 25.75 | 45.457 | 6.41 | 1.289 | 4.127 | 8594.49 | 1.62 | 97.9 | 76.2 | 1439 | 22.73 | 5586.4 | 1625.3 | 2080.1 | 2654.1 | 1220.7 | 0.61107 | 5.416
2024-12-10 | 2:07 | Data | 0 | 33.696 | 31.812 | 169.441 | 7.64 | 160.189 | 2213.49 | 25.75 | 45.637 | 6.4 | 1.295 | 4.134 | 8336.72 | 1.688 | 97.9 | 76.1 | 1439 | 22.82 | 5418.9 | 1616.5 | 2084.1 | 2651.8 | 1220.7 | 0.61227 | 5.429
2024-12-10 | 2:07 | Data | 0 | 33.527 | 31.805 | 169.35 | 7.64 | 160.144 | 2214.39 | 25.74 | 45.457 | 6.4 | 1.296 | 4.139 | 8332.2 | 1.627 | 97.9 | 76.2 | 1439 | 22.73 | 5415.9 | 1628.5 | 2079 | 2654.4 | 1220.7 | 0.61081 | 5.435
2024-12-10 | 2:07 | Data | 0 | 33.648 | 31.805 | 169.486 | 7.64 | 160.189 | 2210.77 | 25.74 | 45.457 | 6.4 | 1.301 | 4.131 | 8332.2 | 1.701 | 97.9 | 76 | 1436 | 22.68 | 5415.9 | 1622.2 | 2087 | 2657.6 | 1220.7 | 0.60843 | 5.433
2024-12-10 | 2:07 | Data | 0 | 33.439 | 31.799 | 169.441 | 7.64 | 160.099 | 2212.58 | 25.74 | 45.637 | 6.4 | 1.295 | 4.161 | 8350.29 | 1.614 | 97.9 | 76.3 | 1438 | 22.86 | 5427.7 | 1634.9 | 2043.8 | 2630.1 | 1220.8 | 0.61892 | 5.456
2024-12-10 | 2:07 | Data | 0 | 33.588 | 32.19 | 169.531 | 7.64 | 160.189 | 2214.39 | 25.74 | 45.366 | 6.4 | 1.293 | 4.162 | 8350.29 | 1.506 | 97.9 | 76.3 | 1440 | 22.73 | 5427.7 | 1623.8 | 2070 | 2644.6 | 1220.8 | 0.61121 | 5.455
2024-12-10 | 2:07 | Data | 0 | 33.837 | 32.042 | 169.486 | 7.63 | 160.099 | 2212.58 | 25.74 | 45.727 | 6.4 | 1.294 | 4.139 | 8350.29 | 1.789 | 97.9 | 76.2 | 1439 | 22.86 | 5427.7 | 1629.5 | 2060.9 | 2641.6 | 1220.8 | 0.61364 | 5.432
2024-12-10 | 2:07 | Data | 0 | 33.756 | 31.92 | 169.486 | 7.63 | 160.234 | 2216.2 | 25.75 | 45.366 | 6.41 | 1.289 | 4.131 | 8350.29 | 1.614 | 98 | 76.2 | 1441 | 22.68 | 5427.7 | 1623.4 | 2050.9 | 2630.5 | 1220.8 | 0.61388 | 5.42
2024-12-10 | 2:07 | Data | 0 | 33.5 | 31.799 | 169.486 | 7.63 | 160.234 | 2216.2 | 25.74 | 45.727 | 6.4 | 1.272 | 4.146 | 8345.77 | 1.634 | 97.9 | 76.5 | 1441 | 22.86 | 5424.8 | 1634.9 | 2050.7 | 2637 | 1220.8 | 0.61715 | 5.419
2024-12-10 | 2:08 | Data | 0 | 33.628 | 32.028 | 169.486 | 7.64 | 160.144 | 2211.68 | 25.75 | 45.727 | 6.4 | 1.277 | 4.112 | 8354.81 | 1.809 | 97.9 | 76.3 | 1438 | 22.86 | 5430.6 | 1618.8 | 2044.9 | 2620.5 | 1220.8 | 0.60905 | 5.391
2024-12-10 | 2:08 | Data | 0 | 33.588 | 31.799 | 169.396 | 7.64 | 160.008 | 2211.68 | 25.74 | 45.727 | 6.4 | 1.287 | 4.103 | 8350.29 | 1.816 | 97.9 | 76.1 | 1437 | 22.86 | 5427.7 | 1614 | 2056 | 2627.2 | 1220.8 | 0.6127 | 5.39
2024-12-10 | 2:08 | Data | 0 | 33.864 | 31.913 | 169.486 | 7.63 | 160.189 | 2210.77 | 25.74 | 45.637 | 6.4 | 1.297 | 4.12 | 8336.72 | 1.661 | 97.9 | 76.1 | 1438 | 22.86 | 5418.9 | 1617.9 | 2058 | 2632.2 | 1220.8 | 0.6121 | 5.418
2024-12-10 | 2:08 | Data | 0 | 33.439 | 31.839 | 169.396 | 7.64 | 160.234 | 2211.68 | 25.75 | 45.637 | 6.4 | 1.291 | 4.162 | 8336.72 | 1.452 | 97.9 | 76.3 | 1437 | 22.82 | 5418.9 | 2984.5 | 3566.7 | 4717.4 | 1220.8 | 0.63192 | 5.454
2024-12-10 | 2:08 | Data | 0 | 33.412 | 32.021 | 169.35 | 7.64 | 160.099 | 2210.77 | 25.74 | 45.727 | 6.4 | 1.285 | 4.139 | 8332.2 | 1.526 | 97.9 | 76.3 | 1437 | 22.86 | 5415.9 | 2709.1 | 2675.6 | 3935.3 | 1220.8 | 0.67133 | 5.423
2024-12-10 | 2:08 | Data | 0 | 33.581 | 32.015 | 169.441 | 7.63 | 160.189 | 2210.77 | 25.74 | 45.727 | 6.4 | 1.286 | 4.118 | 8332.2 | 1.701 | 97.9 | 76.2 | 1437 | 22.86 | 5415.9 | 2736.4 | 2695.6 | 3964.1 | 1220.8 | 0.66982 | 5.402
2024-12-10 | 2:08 | Data | 0 | 33.399 | 31.799 | 169.396 | 7.64 | 160.144 | 2210.77 | 25.74 | 45.457 | 6.4 | 1.294 | 4.121 | 8359.34 | 1.641 | 97.9 | 76.1 | 1438 | 22.73 | 5433.6 | 2688.1 | 2675.3 | 3929.6 | 1220.8 | 0.66636 | 5.415
2024-12-10 | 2:08 | Data | 0 | 33.669 | 31.927 | 169.441 | 7.64 | 160.099 | 2213.49 | 25.75 | 45.727 | 6.4 | 1.294 | 4.131 | 8359.34 | 1.823 | 97.9 | 76.1 | 1439 | 22.86 | 5433.6 | 2713.1 | 2698.5 | 3955.5 | 1220.8 | 0.66686 | 5.426
2024-12-10 | 2:08 | Data | 0 | 33.844 | 31.94 | 169.622 | 7.64 | 160.144 | 2210.77 | 25.75 | 45.637 | 6.4 | 1.291 | 4.11 | 8350.29 | 1.782 | 97.9 | 76.1 | 1438 | 22.82 | 5427.7 | 2715.1 | 2661.2 | 3933 | 1220.8 | 0.66984 | 5.401
2024-12-10 | 2:08 | Data | 0 | 33.385 | 32.001 | 169.35 | 7.64 | 160.053 | 2212.58 | 25.75 | 45.727 | 6.4 | 1.289 | 4.158 | 8345.77 | 1.668 | 97.9 | 76.4 | 1439 | 22.86 | 5424.8 | 2705.8 | 2676.1 | 3938 | 1220.8 | 0.66925 | 5.446
2024-12-10 | 2:08 | Data | 0 | 33.419 | 31.799 | 169.35 | 7.64 | 160.053 | 2214.39 | 25.75 | 45.727 | 6.4 | 1.294 | 4.148 | 8363.86 | 1.614 | 97.9 | 76.2 | 1439 | 22.82 | 5436.5 | 2720 | 2669.5 | 3936 | 1220.8 | 0.67326 | 5.443
2024-12-10 | 2:08 | Data | 0 | 33.635 | 31.799 | 169.486 | 7.64 | 160.099 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.3 | 4.125 | 8350.29 | 1.661 | 97.9 | 76 | 1437 | 22.86 | 5427.7 | 2697.9 | 2701.3 | 3949.8 | 1220.8 | 0.66527 | 5.426
2024-12-10 | 2:08 | Data | 0 | 33.615 | 32.231 | 169.531 | 7.64 | 160.189 | 2211.68 | 25.72 | 45.727 | 6.4 | 1.296 | 4.133 | 8359.34 | 1.614 | 97.9 | 76.1 | 1438 | 22.86 | 5433.6 | 2691.7 | 2672.4 | 3922.8 | 1220.8 | 0.66693 | 5.429
2024-12-10 | 2:08 | Data | 0 | 33.412 | 32.069 | 169.396 | 7.64 | 160.144 | 2214.39 | 25.72 | 45.727 | 6.4 | 1.284 | 4.146 | 8359.34 | 1.512 | 97.9 | 76.4 | 1439 | 22.86 | 5433.6 | 2713.3 | 2684.9 | 3947.9 | 1220.8 | 0.66916 | 5.431
2024-12-10 | 2:08 | Data | 0 | 33.412 | 31.799 | 169.396 | 7.64 | 160.053 | 2208.97 | 25.73 | 45.727 | 6.4 | 1.291 | 4.158 | 8345.77 | 1.614 | 97.9 | 76.3 | 1435 | 22.82 | 5424.8 | 2700.6 | 2690.2 | 3944.7 | 1220.8 | 0.66677 | 5.448
2024-12-10 | 2:08 | Data | 0 | 33.554 | 31.812 | 169.486 | 7.64 | 160.189 | 2209.87 | 25.72 | 45.727 | 6.4 | 1.291 | 4.127 | 8345.77 | 1.62 | 97.9 | 76.2 | 1436 | 22.82 | 5424.8 | 2699.6 | 2670.6 | 3932.5 | 1220.8 | 0.66904 | 5.418
2024-12-10 | 2:08 | Data | 0 | 33.743 | 31.974 | 169.486 | 7.63 | 160.189 | 2211.68 | 25.71 | 45.727 | 6.4 | 1.296 | 4.119 | 8350.29 | 1.661 | 97.9 | 76.1 | 1438 | 22.86 | 5427.7 | 2702.5 | 2685.3 | 3940.5 | 1220.8 | 0.67125 | 5.414
2024-12-10 | 2:08 | Data | 0 | 33.804 | 31.832 | 169.486 | 7.64 | 160.234 | 2208.06 | 25.71 | 45.727 | 6.4 | 1.287 | 4.131 | 8345.77 | 1.809 | 97.9 | 76.2 | 1435 | 22.86 | 5424.8 | 2717.5 | 2674.3 | 3944.4 | 1220.8 | 0.67037 | 5.418
2024-12-10 | 2:09 | Data | 0 | 33.419 | 31.927 | 169.441 | 7.64 | 160.144 | 2211.68 | 25.7 | 45.818 | 6.4 | 1.286 | 4.134 | 8345.77 | 1.701 | 97.9 | 76.3 | 1437 | 22.86 | 5424.8 | 2696 | 2662.5 | 3921.4 | 1220.8 | 0.66959 | 5.42
2024-12-10 | 2:09 | Data | 0 | 33.642 | 32.028 | 169.441 | 7.64 | 160.099 | 2210.77 | 25.71 | 45.818 | 6.4 | 1.289 | 4.134 | 8363.86 | 1.614 | 97.9 | 76.2 | 1437 | 22.91 | 5436.5 | 2696.6 | 2687.8 | 3938.5 | 1220.8 | 0.66757 | 5.426
2024-12-10 | 2:09 | Data | 0 | 33.412 | 31.799 | 169.35 | 7.64 | 160.008 | 2211.68 | 25.71 | 45.637 | 6.41 | 1.282 | 4.111 | 8350.29 | 1.614 | 97.9 | 76.2 | 1438 | 22.82 | 5427.7 | 2733.5 | 2703.1 | 3967.2 | 1220.8 | 0.66897 | 5.394
2024-12-10 | 2:09 | Data | 0 | 33.635 | 32.028 | 169.441 | 7.64 | 160.189 | 2207.16 | 25.71 | 45.727 | 6.4 | 1.286 | 4.136 | 8345.77 | 1.614 | 97.9 | 76.3 | 1435 | 22.86 | 5424.8 | 2717.6 | 2699.9 | 3952.3 | 1220.8 | 0.67091 | 5.422
2024-12-10 | 2:09 | Data | 0 | 33.615 | 31.974 | 169.441 | 7.64 | 160.144 | 2204.45 | 25.72 | 45.637 | 6.4 | 1.293 | 4.131 | 8336.72 | 1.715 | 97.9 | 76.2 | 1433 | 22.82 | 5418.9 | 2690.6 | 2693.3 | 3953.4 | 1220.8 | 0.66901 | 5.424
2024-12-10 | 2:09 | Data | 0 | 33.871 | 31.873 | 169.531 | 7.64 | 160.279 | 2208.06 | 25.71 | 46.269 | 6.4 | 1.287 | 4.113 | 8336.72 | 1.681 | 97.9 | 76.2 | 1436 | 23.09 | 5418.9 | 2715 | 2733.3 | 3981 | 1220.8 | 0.66361 | 5.4
2024-12-10 | 2:09 | Data | 0 | 33.412 | 31.913 | 169.396 | 7.64 | 160.053 | 2204.45 | 25.71 | 45.727 | 6.4 | 1.285 | 4.145 | 8318.64 | 1.614 | 97.9 | 76.3 | 1432 | 22.86 | 5407.1 | 2707.5 | 2711.1 | 3957.4 | 1220.8 | 0.66666 | 5.43
2024-12-10 | 2:09 | Data | 0 | 33.642 | 31.812 | 169.531 | 7.64 | 160.144 | 2212.58 | 25.7 | 45.637 | 6.4 | 1.291 | 4.138 | 8336.72 | 1.654 | 97.9 | 76.2 | 1438 | 22.82 | 5418.9 | 2709.9 | 2704.7 | 3958.3 | 1220.8 | 0.66678 | 5.43
2024-12-10 | 2:09 | Data | 0 | 33.858 | 31.839 | 169.441 | 7.64 | 160.234 | 2210.77 | 25.72 | 45.727 | 6.4 | 1.289 | 4.149 | 8314.11 | 1.809 | 97.9 | 76.3 | 1437 | 22.82 | 5404.2 | 2728.7 | 2679.4 | 3951.5 | 1220.8 | 0.6724 | 5.438
2024-12-10 | 2:09 | Data | 0 | 33.628 | 32.028 | 169.441 | 7.64 | 160.144 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.274 | 4.143 | 8309.59 | 1.614 | 97.9 | 76.5 | 1437 | 22.82 | 5401.2 | 2705.1 | 2680.5 | 3936.3 | 1220.8 | 0.66942 | 5.417
2024-12-10 | 2:09 | Data | 0 | 33.858 | 32.028 | 169.622 | 7.64 | 160.234 | 2206.25 | 25.71 | 45.637 | 6.4 | 1.276 | 4.134 | 8314.11 | 1.668 | 97.9 | 76.4 | 1434 | 22.86 | 5404.2 | 2708.6 | 2680.7 | 3944 | 1220.8 | 0.66815 | 5.411
2024-12-10 | 2:09 | Data | 0 | 33.642 | 32.028 | 169.531 | 7.64 | 160.189 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.296 | 4.123 | 8309.59 | 1.614 | 97.9 | 76.1 | 1438 | 22.86 | 5401.2 | 2693.2 | 2695.3 | 3936.5 | 1220.8 | 0.66847 | 5.418
2024-12-10 | 2:09 | Data | 0 | 33.615 | 31.859 | 169.531 | 7.64 | 160.189 | 2208.06 | 25.71 | 45.727 | 6.4 | 1.295 | 4.122 | 8286.98 | 1.769 | 97.9 | 76.1 | 1435 | 22.86 | 5386.5 | 2703.9 | 2696.6 | 3947.2 | 1220.8 | 0.66738 | 5.416
2024-12-10 | 2:09 | Data | 0 | 33.527 | 31.974 | 169.531 | 7.64 | 160.144 | 2208.97 | 25.73 | 45.727 | 6.4 | 1.288 | 4.142 | 8273.41 | 1.506 | 97.9 | 76.3 | 1436 | 22.86 | 5377.7 | 2714 | 2700.6 | 3956.2 | 1220.8 | 0.66807 | 5.43
2024-12-10 | 2:09 | Data | 0 | 33.419 | 31.9 | 169.486 | 7.64 | 160.144 | 2216.2 | 25.72 | 45.727 | 6.4 | 1.295 | 4.124 | 8291.5 | 1.411 | 97.9 | 76.1 | 1440 | 22.86 | 5389.5 | 2713.1 | 2698.1 | 3952.1 | 1220.8 | 0.66715 | 5.42
2024-12-10 | 2:09 | Data | 0 | 33.527 | 31.805 | 169.441 | 7.64 | 160.189 | 2210.77 | 25.72 | 45.727 | 6.4 | 1.297 | 4.125 | 8300.55 | 1.62 | 97.9 | 76.1 | 1437 | 22.86 | 5395.4 | 2713.1 | 2686.5 | 3943.8 | 1220.8 | 0.66996 | 5.422
2024-12-10 | 2:09 | Data | 0 | 33.54 | 31.859 | 169.486 | 7.64 | 160.234 | 2211.68 | 25.74 | 45.637 | 6.4 | 1.295 | 4.14 | 8323.16 | 1.533 | 97.9 | 76.2 | 1437 | 22.86 | 5410.1 | 2718.6 | 2700.2 | 3960.1 | 1220.8 | 0.66744 | 5.435
2024-12-10 | 2:10 | Data | 0 | 33.527 | 32.048 | 169.396 | 7.64 | 160.234 | 2210.77 | 25.73 | 45.637 | 6.4 | 1.294 | 4.134 | 8300.55 | 1.789 | 97.9 | 76.2 | 1437 | 22.86 | 5395.4 | 2706.8 | 2697.9 | 3951.4 | 1220.8 | 0.66785 | 5.428
2024-12-10 | 2:10 | Data | 0 | 33.358 | 32.339 | 169.486 | 7.64 | 160.144 | 2210.77 | 25.73 | 45.637 | 6.4 | 1.29 | 4.152 | 8300.55 | 1.634 | 97.9 | 76.3 | 1437 | 22.86 | 5395.4 | 2739.6 | 2720.7 | 3990.8 | 1220.8 | 0.66768 | 5.439
2024-12-10 | 2:10 | Data | 0 | 33.756 | 31.805 | 169.441 | 7.64 | 160.234 | 2211.68 | 25.72 | 45.637 | 6.4 | 1.293 | 4.136 | 8314.11 | 1.668 | 97.9 | 76.2 | 1438 | 22.86 | 5404.2 | 2718.3 | 2709.2 | 3968.3 | 1220.9 | 0.66833 | 5.43
2024-12-10 | 2:10 | Data | 0 | 33.466 | 32.028 | 169.531 | 7.64 | 160.144 | 2206.25 | 25.73 | 45.637 | 6.4 | 1.289 | 4.119 | 8318.64 | 1.391 | 97.9 | 76.2 | 1434 | 22.86 | 5407.1 | 2719.9 | 2685 | 3953.1 | 1220.9 | 0.67039 | 5.408
2024-12-10 | 2:10 | Data | 0 | 33.642 | 32.143 | 169.441 | 7.64 | 160.234 | 2208.06 | 25.73 | 45.637 | 6.4 | 1.282 | 4.128 | 8314.11 | 1.614 | 97.9 | 76.3 | 1436 | 22.82 | 5404.2 | 2700.4 | 2705.8 | 3953.5 | 1220.9 | 0.6663 | 5.411
2024-12-10 | 2:10 | Data | 0 | 33.588 | 32.015 | 169.396 | 7.64 | 160.144 | 2205.35 | 25.72 | 45.727 | 6.4 | 1.291 | 4.139 | 8314.11 | 1.627 | 97.9 | 76.2 | 1434 | 22.82 | 5404.2 | 2698.6 | 2682.4 | 3936.1 | 1220.9 | 0.66865 | 5.43
2024-12-10 | 2:10 | Data | 0 | 33.527 | 31.805 | 169.396 | 7.64 | 160.189 | 2208.97 | 25.73 | 45.637 | 6.4 | 1.286 | 4.115 | 8314.11 | 1.614 | 97.9 | 76.2 | 1435 | 22.82 | 5404.2 | 2708.6 | 2674.1 | 3930.5 | 1220.9 | 0.67126 | 5.4
2024-12-10 | 2:10 | Data | 0 | 33.412 | 31.799 | 169.35 | 7.64 | 160.053 | 2205.35 | 25.72 | 45.727 | 6.4 | 1.284 | 4.14 | 8291.5 | 1.614 | 97.9 | 76.3 | 1433 | 22.86 | 5389.5 | 2716.6 | 2697.2 | 3959.5 | 1220.9 | 0.66869 | 5.424
2024-12-10 | 2:10 | Data | 0 | 33.426 | 31.907 | 169.441 | 7.64 | 160.099 | 2201.74 | 25.72 | 45.727 | 6.4 | 1.282 | 4.128 | 8291.5 | 1.506 | 97.9 | 76.3 | 1432 | 22.86 | 5389.5 | 2696.4 | 2693.5 | 3943.1 | 1220.9 | 0.66598 | 5.411
2024-12-10 | 2:10 | Data | 0 | 33.412 | 31.799 | 169.531 | 7.64 | 160.144 | 2203.54 | 25.73 | 45.637 | 6.4 | 1.283 | 4.124 | 8291.5 | 1.614 | 97.9 | 76.3 | 1431 | 22.86 | 5389.5 | 2715.2 | 2690.1 | 3954.2 | 1220.9 | 0.66568 | 5.407
2024-12-10 | 2:10 | Data | 0 | 33.588 | 32.069 | 169.577 | 7.64 | 160.189 | 2201.74 | 25.72 | 45.727 | 6.4 | 1.289 | 4.128 | 8291.5 | 1.526 | 97.9 | 76.2 | 1431 | 22.82 | 5389.5 | 2719.8 | 2702.1 | 3962.4 | 1220.9 | 0.66711 | 5.419
2024-12-10 | 2:10 | Data | 0 | 33.696 | 31.819 | 169.577 | 7.64 | 160.279 | 2201.74 | 25.73 | 45.727 | 6.41 | 1.286 | 4.101 | 8345.77 | 1.654 | 97.9 | 76.1 | 1432 | 22.82 | 5424.8 | 2694.6 | 2715.5 | 3955.2 | 1220.9 | 0.66142 | 5.387
2024-12-10 | 2:10 | Data | 0 | 33.864 | 32.028 | 169.531 | 7.63 | 160.144 | 2203.54 | 25.73 | 45.637 | 6.4 | 1.296 | 4.109 | 8350.29 | 1.715 | 97.9 | 76 | 1432 | 22.82 | 5427.7 | 2701.7 | 2726 | 3964.2 | 1220.9 | 0.66357 | 5.404
2024-12-10 | 2:10 | Data | 0 | 33.527 | 31.799 | 169.441 | 7.64 | 160.144 | 2201.74 | 25.73 | 45.727 | 6.4 | 1.291 | 4.139 | 8345.77 | 1.634 | 97.9 | 76.2 | 1431 | 22.86 | 5424.8 | 2701.6 | 2706.8 | 3955.9 | 1220.9 | 0.66454 | 5.43
2024-12-10 | 2:10 | Data | 0 | 33.912 | 32.177 | 169.622 | 7.64 | 160.279 | 2201.74 | 25.73 | 45.637 | 6.4 | 1.285 | 4.116 | 8332.2 | 1.789 | 97.9 | 76.2 | 1432 | 22.82 | 5415.9 | 2698.8 | 2693.5 | 3948.5 | 1220.9 | 0.66591 | 5.401
2024-12-10 | 2:10 | Data | 0 | 33.642 | 32.116 | 169.441 | 7.64 | 160.144 | 2199.93 | 25.72 | 45.727 | 6.4 | 1.295 | 4.118 | 8359.34 | 1.445 | 97.9 | 76.1 | 1431 | 22.86 | 5433.6 | 2705.2 | 2683.6 | 3940.3 | 1220.9 | 0.66803 | 5.411
2024-12-10 | 2:10 | Data | 0 | 33.642 | 32.136 | 169.486 | 7.64 | 160.189 | 2207.16 | 25.73 | 45.727 | 6.4 | 1.295 | 4.121 | 8363.86 | 1.641 | 97.9 | 76.1 | 1434 | 22.86 | 5436.5 | 2694.1 | 2697.9 | 3945.4 | 1220.9 | 0.66511 | 5.416
2024-12-10 | 2:10 | Data | 0 | 33.574 | 32.001 | 169.486 | 7.64 | 160.144 | 2205.35 | 25.73 | 45.727 | 6.4 | 1.291 | 4.118 | 8359.34 | 1.62 | 97.9 | 76.1 | 1434 | 22.86 | 5433.6 | 2701.1 | 2694.6 | 3947.6 | 1220.9 | 0.66755 | 5.409
2024-12-10 | 2:11 | Data | 0 | 33.756 | 32.17 | 169.622 | 7.64 | 160.279 | 2206.25 | 25.73 | 45.727 | 6.4 | 1.3 | 4.129 | 8359.34 | 1.674 | 97.9 | 76.1 | 1433 | 22.86 | 5433.6 | 2722.2 | 2686.9 | 3954.2 | 1220.9 | 0.67205 | 5.428
2024-12-10 | 2:11 | Data | 0 | 33.642 | 32.028 | 169.531 | 7.64 | 160.189 | 2203.54 | 25.72 | 45.727 | 6.4 | 1.294 | 4.136 | 8336.72 | 1.782 | 97.9 | 76.2 | 1432 | 22.86 | 5418.9 | 2682.1 | 2685.9 | 3927.7 | 1220.9 | 0.66526 | 5.429
2024-12-10 | 2:11 | Data | 0 | 33.615 | 32.197 | 169.577 | 7.64 | 160.189 | 2205.35 | 25.73 | 45.637 | 6.4 | 1.284 | 4.137 | 8345.77 | 1.614 | 97.9 | 76.3 | 1433 | 22.86 | 5424.8 | 2709.8 | 2689.3 | 3945.3 | 1220.9 | 0.67045 | 5.42
2024-12-10 | 2:11 | Data | 0 | 33.709 | 31.859 | 169.531 | 7.64 | 160.279 | 2203.54 | 25.72 | 45.818 | 6.4 | 1.291 | 4.121 | 8350.29 | 1.506 | 97.9 | 76.2 | 1431 | 22.82 | 5427.7 | 2717.6 | 2688.9 | 3953 | 1220.9 | 0.66936 | 5.411
2024-12-10 | 2:11 | Data | 0 | 33.466 | 31.974 | 169.486 | 7.64 | 160.234 | 2201.74 | 25.73 | 45.818 | 6.4 | 1.291 | 4.124 | 8345.77 | 1.506 | 97.9 | 76.2 | 1431 | 22.86 | 5424.8 | 2698.7 | 2705.6 | 3950.1 | 1220.9 | 0.66542 | 5.414
2024-12-10 | 2:11 | Data | 0 | 34.094 | 32.156 | 169.577 | 7.64 | 160.234 | 2200.83 | 25.72 | 45.727 | 6.4 | 1.294 | 4.122 | 8345.77 | 1.769 | 97.9 | 76.1 | 1431 | 22.86 | 5424.8 | 2712.3 | 2690 | 3952.4 | 1220.9 | 0.6694 | 5.416
2024-12-10 | 2:11 | Data | 0 | 33.858 | 32.035 | 169.622 | 7.64 | 160.279 | 2201.74 | 25.73 | 45.727 | 6.4 | 1.293 | 4.119 | 8336.72 | 1.776 | 97.9 | 76.1 | 1431 | 22.82 | 5418.9 | 2716.1 | 2678.7 | 3947.1 | 1220.9 | 0.66941 | 5.412
2024-12-10 | 2:11 | Data | 0 | 33.642 | 31.94 | 169.441 | 7.64 | 160.234 | 2199.93 | 25.73 | 45.727 | 6.4 | 1.29 | 4.108 | 8341.25 | 1.789 | 97.9 | 76.1 | 1430 | 22.86 | 5421.8 | 2705.1 | 2698.6 | 3946.7 | 1220.9 | 0.66865 | 5.398
2024-12-10 | 2:11 | Data | 0 | 33.588 | 32.197 | 169.531 | 7.64 | 160.234 | 2199.93 | 25.73 | 45.727 | 6.41 | 1.287 | 4.098 | 8345.77 | 1.668 | 97.9 | 76.1 | 1429 | 22.82 | 5424.8 | 2698.6 | 2689.4 | 3942.7 | 1220.9 | 0.6667 | 5.386
2024-12-10 | 2:11 | Data | 0 | 33.696 | 32.15 | 169.531 | 7.64 | 160.234 | 2199.93 | 25.72 | 45.727 | 6.4 | 1.285 | 4.115 | 8345.77 | 1.62 | 97.9 | 76.2 | 1430 | 22.86 | 5424.8 | 2709.2 | 2675.9 | 3936 | 1220.9 | 0.67011 | 5.4
2024-12-10 | 2:11 | Data | 0 | 33.871 | 32.264 | 169.667 | 7.64 | 160.279 | 2199.93 | 25.73 | 45.637 | 6.4 | 1.288 | 4.139 | 8345.77 | 1.431 | 97.9 | 76.3 | 1429 | 22.82 | 5424.8 | 2720.7 | 2675.7 | 3943.5 | 1220.9 | 0.67205 | 5.427
2024-12-10 | 2:11 | Data | 0 | 33.534 | 31.812 | 169.486 | 7.64 | 160.279 | 2203.54 | 25.72 | 45.637 | 6.4 | 1.289 | 4.129 | 8350.29 | 1.6 | 97.9 | 76.2 | 1433 | 22.86 | 5427.7 | 2724.9 | 2689.3 | 3954.6 | 1220.9 | 0.67235 | 5.418
2024-12-10 | 2:11 | Data | 0 | 33.642 | 32.021 | 169.577 | 7.64 | 160.189 | 2201.74 | 25.73 | 45.727 | 6.4 | 1.29 | 4.121 | 8345.77 | 1.627 | 97.9 | 76.2 | 1431 | 22.82 | 5424.8 | 2717.5 | 2696.4 | 3952.2 | 1220.9 | 0.6692 | 5.411
2024-12-10 | 2:11 | Data | 0 | 33.48 | 31.913 | 169.531 | 7.64 | 160.234 | 2206.25 | 25.73 | 45.637 | 6.4 | 1.286 | 4.121 | 8359.34 | 1.506 | 97.9 | 76.2 | 1434 | 22.86 | 5433.6 | 2709.9 | 2680.4 | 3939.2 | 1220.9 | 0.67009 | 5.407
2024-12-10 | 2:11 | Data | 0 | 33.871 | 32.264 | 169.531 | 7.64 | 160.234 | 2204.45 | 25.73 | 45.727 | 6.41 | 1.278 | 4.118 | 8368.38 | 1.607 | 97.9 | 76.3 | 1433 | 22.86 | 5439.4 | 2702.4 | 2681 | 3938.8 | 1220.9 | 0.6661 | 5.396
2024-12-10 | 2:11 | Data | 0 | 33.858 | 31.805 | 169.531 | 7.64 | 160.189 | 2205.35 | 25.73 | 45.727 | 6.4 | 1.291 | 4.101 | 8377.43 | 1.627 | 97.9 | 76.1 | 1433 | 22.86 | 5445.3 | 2709.9 | 2667.9 | 3937.8 | 1220.9 | 0.66967 | 5.393
2024-12-10 | 2:11 | Data | 0 | 33.675 | 32.028 | 169.531 | 7.64 | 160.324 | 2206.25 | 25.72 | 45.818 | 6.4 | 1.301 | 4.115 | 8372.9 | 1.418 | 97.9 | 76 | 1433 | 22.86 | 5442.4 | 2716.3 | 2692.7 | 3952.4 | 1220.9 | 0.66934 | 5.415
2024-12-10 | 2:12 | Data | 0 | 33.635 | 31.866 | 169.531 | 7.64 | 160.189 | 2197.22 | 25.73 | 45.727 | 6.4 | 1.295 | 4.11 | 8332.2 | 1.62 | 97.9 | 76 | 1428 | 22.86 | 5415.9 | 2705.4 | 2723.7 | 3965.6 | 1220.9 | 0.66452 | 5.405
2024-12-10 | 2:12 | Data | 0 | 33.736 | 32.406 | 169.486 | 7.64 | 160.234 | 2203.54 | 25.73 | 45.818 | 6.4 | 1.282 | 4.116 | 8336.72 | 1.627 | 97.9 | 76.2 | 1432 | 22.91 | 5418.9 | 2707 | 2694.7 | 3951.2 | 1220.9 | 0.66663 | 5.399
2024-12-10 | 2:12 | Data | 0 | 33.756 | 32.096 | 169.667 | 7.64 | 160.234 | 2199.93 | 25.72 | 45.727 | 6.4 | 1.291 | 4.132 | 8332.2 | 1.749 | 97.9 | 76.2 | 1429 | 22.86 | 5415.9 | 2733.5 | 2697.7 | 3966.4 | 1220.9 | 0.67083 | 5.424
2024-12-10 | 2:12 | Data | 0 | 33.642 | 32.251 | 169.531 | 7.64 | 160.189 | 2199.93 | 25.73 | 45.637 | 6.4 | 1.297 | 4.152 | 8332.2 | 1.391 | 97.9 | 76.2 | 1430 | 22.86 | 5415.9 | 2699.5 | 2706.5 | 3944.5 | 1220.9 | 0.66601 | 5.449
2024-12-10 | 2:12 | Data | 0 | 33.648 | 31.812 | 169.486 | 7.64 | 160.099 | 2199.93 | 25.73 | 45.727 | 6.4 | 1.291 | 4.153 | 8341.25 | 1.614 | 97.9 | 76.3 | 1431 | 22.86 | 5421.8 | 2709.9 | 2697.2 | 3956.4 | 1220.9 | 0.66597 | 5.445
2024-12-10 | 2:12 | Data | 0 | 33.615 | 32.069 | 169.531 | 7.64 | 160.234 | 2199.93 | 25.74 | 45.727 | 6.4 | 1.293 | 4.128 | 8332.2 | 1.6 | 97.9 | 76.1 | 1430 | 22.82 | 5415.9 | 2706.8 | 2686.4 | 3948.5 | 1220.9 | 0.66726 | 5.422
2024-12-10 | 2:12 | Data | 0 | 33.756 | 32.028 | 169.486 | 7.64 | 160.189 | 2199.93 | 25.73 | 45.547 | 6.4 | 1.295 | 4.127 | 8336.72 | 1.634 | 97.9 | 76.1 | 1429 | 22.73 | 5418.9 | 2698.1 | 2676 | 3929 | 1221 | 0.66844 | 5.423
2024-12-10 | 2:12 | Data | 0 | 33.864 | 31.866 | 169.577 | 7.64 | 160.189 | 2199.93 | 25.73 | 45.818 | 6.41 | 1.292 | 4.132 | 8318.64 | 1.627 | 97.9 | 76.2 | 1430 | 22.86 | 5407.1 | 2710.7 | 2669.8 | 3934.8 | 1221 | 0.67046 | 5.424
2024-12-10 | 2:12 | Data | 0 | 33.858 | 32.258 | 169.712 | 7.64 | 160.324 | 2206.25 | 25.73 | 45.818 | 6.4 | 1.291 | 4.148 | 8345.77 | 1.607 | 97.9 | 76.3 | 1434 | 22.82 | 5424.8 | 2707.2 | 2669.6 | 3934.3 | 1221 | 0.67097 | 5.439
2024-12-10 | 2:12 | Data | 0 | 33.756 | 32.251 | 169.577 | 7.64 | 160.189 | 2205.35 | 25.72 | 45.727 | 6.4 | 1.301 | 4.121 | 8363.86 | 1.607 | 97.9 | 76 | 1433 | 22.86 | 5436.5 | 2708.2 | 2680.1 | 3938.9 | 1221 | 0.66999 | 5.422
2024-12-10 | 2:12 | Data | 0 | 33.756 | 32.237 | 169.577 | 7.64 | 160.234 | 2208.97 | 25.73 | 45.727 | 6.4 | 1.276 | 4.133 | 8363.86 | 1.668 | 97.9 | 76.4 | 1435 | 22.86 | 5436.5 | 2709.7 | 2685.7 | 3944.5 | 1221 | 0.66865 | 5.408
2024-12-10 | 2:12 | Data | 0 | 33.635 | 31.94 | 169.441 | 7.64 | 160.144 | 2210.77 | 25.72 | 45.727 | 6.4 | 1.276 | 4.132 | 8359.34 | 1.789 | 97.9 | 76.4 | 1437 | 22.82 | 5433.6 | 2695.6 | 2676.8 | 3930.2 | 1221 | 0.66815 | 5.409
2024-12-10 | 2:12 | Data | 0 | 33.588 | 32.015 | 169.577 | 7.64 | 160.279 | 2208.97 | 25.73 | 45.637 | 6.4 | 1.276 | 4.119 | 8345.77 | 1.62 | 97.9 | 76.3 | 1435 | 22.86 | 5424.8 | 2706.2 | 2672.2 | 3931.6 | 1221 | 0.67084 | 5.394
2024-12-10 | 2:12 | Data | 0 | 33.642 | 32.028 | 169.486 | 7.64 | 160.234 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.277 | 4.143 | 8359.34 | 1.614 | 97.9 | 76.4 | 1438 | 22.82 | 5433.6 | 2719.2 | 2682.6 | 3944.7 | 1221 | 0.67244 | 5.42
2024-12-10 | 2:12 | Data | 0 | 33.642 | 32.028 | 169.577 | 7.64 | 160.234 | 2210.77 | 25.73 | 45.818 | 6.4 | 1.289 | 4.141 | 8359.34 | 1.526 | 97.9 | 76.3 | 1437 | 22.86 | 5433.6 | 2707.1 | 2663.3 | 3925.5 | 1221 | 0.67287 | 5.43
2024-12-10 | 2:12 | Data | 0 | 33.858 | 32.055 | 169.577 | 7.64 | 160.279 | 2211.68 | 25.73 | 45.727 | 6.4 | 1.292 | 4.153 | 8354.81 | 1.728 | 97.9 | 76.3 | 1438 | 22.86 | 5430.6 | 2728 | 2689.7 | 3961.7 | 1221 | 0.67022 | 5.444
2024-12-10 | 2:12 | Data | 0 | 33.642 | 32.028 | 169.531 | 7.64 | 160.189 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.29 | 4.123 | 8336.72 | 1.62 | 97.9 | 76.2 | 1437 | 22.86 | 5418.9 | 2715.5 | 2682.2 | 3948.9 | 1221 | 0.67152 | 5.411
2024-12-10 | 2:12 | Data | 0 | 33.858 | 32.271 | 169.712 | 7.64 | 160.279 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.282 | 4.102 | 8336.72 | 1.695 | 97.9 | 76.2 | 1437 | 22.86 | 5418.9 | 2705.5 | 2687.9 | 3942 | 1221 | 0.66905 | 5.385
2024-12-10 | 2:13 | Data | 0 | 33.804 | 32.028 | 169.531 | 7.64 | 160.189 | 2210.77 | 25.72 | 45.637 | 6.4 | 1.28 | 4.127 | 8336.72 | 1.715 | 97.9 | 76.3 | 1437 | 22.82 | 5418.9 | 2711.5 | 2692.5 | 3951 | 1221 | 0.67026 | 5.407
2024-12-10 | 2:13 | Data | 0 | 33.696 | 32.028 | 169.622 | 7.64 | 160.324 | 2211.68 | 25.73 | 45.727 | 6.4 | 1.28 | 4.13 | 8332.2 | 1.62 | 97.9 | 76.3 | 1437 | 22.86 | 5415.9 | 2708.9 | 2675.6 | 3935.9 | 1221 | 0.66931 | 5.41
2024-12-10 | 2:13 | Data | 0 | 33.675 | 32.035 | 169.622 | 7.64 | 160.324 | 2206.25 | 25.73 | 45.637 | 6.4 | 1.282 | 4.128 | 8345.77 | 1.614 | 97.9 | 76.3 | 1435 | 22.82 | 5424.8 | 2713.8 | 2679.7 | 3944.6 | 1221 | 0.67152 | 5.411
2024-12-10 | 2:13 | Data | 0 | 34.087 | 32.089 | 169.622 | 7.64 | 160.324 | 2211.68 | 25.73 | 45.727 | 6.4 | 1.284 | 4.138 | 8350.29 | 1.661 | 97.9 | 76.3 | 1437 | 22.86 | 5427.7 | 2706.6 | 2660.9 | 3930.1 | 1221 | 0.67227 | 5.422
2024-12-10 | 2:13 | Data | 0 | 33.675 | 32.055 | 169.577 | 7.64 | 160.279 | 2212.58 | 25.73 | 45.727 | 6.4 | 1.295 | 4.126 | 8359.34 | 1.593 | 97.9 | 76.1 | 1439 | 22.86 | 5433.6 | 2710.3 | 2687.7 | 3950.3 | 1221 | 0.67141 | 5.42
2024-12-10 | 2:13 | Data | 0 | 33.844 | 32.028 | 169.531 | 7.64 | 160.189 | 2213.49 | 25.72 | 45.637 | 6.4 | 1.295 | 4.104 | 8359.34 | 1.668 | 97.9 | 76 | 1439 | 22.86 | 5433.6 | 2712.1 | 2677.9 | 3942.5 | 1221 | 0.67011 | 5.398
2024-12-10 | 2:13 | Data | 0 | 33.783 | 32.028 | 169.667 | 7.64 | 160.324 | 2212.58 | 25.74 | 45.818 | 6.4 | 1.291 | 4.118 | 8377.43 | 1.526 | 97.9 | 76.1 | 1438 | 22.91 | 5445.3 | 2705.3 | 2674.1 | 3932.2 | 1221 | 0.67068 | 5.407
2024-12-10 | 2:13 | Data | 0 | 33.655 | 32.15 | 169.486 | 7.64 | 160.279 | 2213.49 | 25.72 | 45.637 | 6.4 | 1.28 | 4.141 | 8372.9 | 1.614 | 97.9 | 76.4 | 1439 | 22.82 | 5442.4 | 2716.9 | 2670.2 | 3941.5 | 1221 | 0.67098 | 5.42
2024-12-10 | 2:13 | Data | 0 | 33.446 | 32.19 | 169.577 | 7.64 | 160.234 | 2213.49 | 25.73 | 45.818 | 6.4 | 1.279 | 4.121 | 8372.9 | 1.438 | 97.9 | 76.3 | 1439 | 22.86 | 5442.4 | 2710.4 | 2660.3 | 3925 | 1221 | 0.67376 | 5.4
2024-12-10 | 2:13 | Data | 0 | 33.642 | 32.028 | 169.531 | 7.64 | 160.234 | 2214.39 | 25.73 | 45.727 | 6.4 | 1.293 | 4.125 | 8354.81 | 1.62 | 97.9 | 76.1 | 1439 | 22.86 | 5430.6 | 2717.4 | 2666.9 | 3936 | 1221 | 0.67443 | 5.419
2024-12-10 | 2:13 | Data | 0 | 33.642 | 32.251 | 169.667 | 7.64 | 160.279 | 2213.49 | 25.73 | 45.637 | 6.4 | 1.291 | 4.128 | 8345.77 | 1.553 | 97.9 | 76.2 | 1439 | 22.86 | 5424.8 | 2726.6 | 2682.2 | 3952 | 1221 | 0.67286 | 5.419
2024-12-10 | 2:13 | Data | 0 | 33.743 | 32.258 | 169.622 | 7.64 | 160.279 | 2214.39 | 25.73 | 45.186 | 6.4 | 1.301 | 4.121 | 8350.29 | 1.6 | 98 | 76 | 1439 | 22.59 | 5427.7 | 2711.4 | 2665.3 | 3934.3 | 1221 | 0.67077 | 5.422
2024-12-10 | 2:13 | Data | 0 | 33.858 | 32.035 | 169.622 | 7.64 | 160.279 | 2208.06 | 25.73 | 45.727 | 6.4 | 1.284 | 4.131 | 8345.77 | 1.836 | 97.9 | 76.3 | 1435 | 22.82 | 5424.8 | 2701 | 2659.4 | 3921 | 1221 | 0.67035 | 5.415
2024-12-10 | 2:13 | Data | 0 | 33.871 | 32.258 | 169.667 | 7.64 | 160.324 | 2213.49 | 25.73 | 45.727 | 6.4 | 1.283 | 4.119 | 8345.77 | 1.661 | 97.9 | 76.2 | 1439 | 22.86 | 5424.8 | 2700.3 | 2668.6 | 3925.5 | 1221 | 0.66972 | 5.402
2024-12-10 | 2:13 | Data | 0 | 33.642 | 32.028 | 169.577 | 7.64 | 160.279 | 2213.49 | 25.73 | 45.727 | 6.4 | 1.29 | 4.133 | 8345.77 | 1.614 | 97.9 | 76.2 | 1439 | 22.86 | 5424.8 | 2723.4 | 2673.3 | 3946.2 | 1221 | 0.67286 | 5.421
2024-12-10 | 2:13 | Data | 0 | 33.642 | 32.028 | 169.486 | 7.64 | 160.189 | 2213.49 | 25.72 | 45.727 | 6.4 | 1.282 | 4.146 | 8332.2 | 1.614 | 97.9 | 76.4 | 1439 | 22.82 | 5415.9 | 2710.4 | 2672.8 | 3931.8 | 1221 | 0.67175 | 5.428
2024-12-10 | 2:13 | Data | 0 | 33.669 | 31.805 | 169.486 | 7.64 | 160.189 | 2213.49 | 25.73 | 45.727 | 6.4 | 1.288 | 4.122 | 8332.2 | 1.715 | 97.9 | 76.2 | 1439 | 22.86 | 5415.9 | 2699.9 | 2673.5 | 3927.4 | 1221 | 0.66835 | 5.41
2024-12-10 | 2:13 | Data | 0 | 33.655 | 32.055 | 169.622 | 7.64 | 160.279 | 2211.68 | 25.73 | 45.727 | 6.4 | 1.3 | 4.136 | 8345.77 | 1.492 | 97.9 | 76.1 | 1438 | 22.82 | 5424.8 | 2709.2 | 2674.3 | 3939.3 | 1221 | 0.67143 | 5.436
2024-12-10 | 2:14 | Data | 0 | 34.087 | 32.264 | 169.712 | 7.64 | 160.37 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.296 | 4.144 | 8305.07 | 1.708 | 97.9 | 76.2 | 1436 | 22.86 | 5398.3 | 2702.9 | 2670 | 3930.7 | 1221 | 0.66981 | 5.44
2024-12-10 | 2:14 | Data | 0 | 33.642 | 31.913 | 169.486 | 7.64 | 160.189 | 2210.77 | 25.73 | 45.547 | 6.4 | 1.295 | 4.11 | 8305.07 | 1.614 | 97.9 | 76 | 1437 | 22.82 | 5398.3 | 2730.1 | 2697.5 | 3966.8 | 1221 | 0.67134 | 5.406
2024-12-10 | 2:14 | Data | 0 | 33.655 | 32.021 | 169.531 | 7.64 | 160.324 | 2210.77 | 25.72 | 45.637 | 6.4 | 1.291 | 4.13 | 8305.07 | 1.634 | 97.9 | 76.2 | 1437 | 22.82 | 5398.3 | 2695.5 | 2674.8 | 3938.3 | 1221 | 0.66878 | 5.42
2024-12-10 | 2:14 | Data | 0 | 33.412 | 32.393 | 169.531 | 7.64 | 160.189 | 2211.68 | 25.73 | 45.818 | 6.4 | 1.291 | 4.125 | 8300.55 | 1.499 | 97.9 | 76.2 | 1438 | 22.91 | 5395.4 | 2718.7 | 2682.5 | 3951.2 | 1221 | 0.67031 | 5.416
2024-12-10 | 2:14 | Data | 0 | 33.419 | 31.94 | 169.531 | 7.64 | 160.279 | 2210.77 | 25.72 | 45.727 | 6.4 | 1.301 | 4.119 | 8336.72 | 1.499 | 97.9 | 76 | 1437 | 22.91 | 5418.9 | 2716.6 | 2694.7 | 3951.9 | 1221 | 0.66947 | 5.42
2024-12-10 | 2:14 | Data | 0 | 33.642 | 32.15 | 169.486 | 7.64 | 160.234 | 2213.49 | 25.73 | 45.727 | 6.4 | 1.288 | 4.111 | 8336.72 | 1.614 | 97.9 | 76.2 | 1439 | 22.86 | 5418.9 | 2724.2 | 2654.3 | 3934.2 | 1221 | 0.67632 | 5.398
2024-12-10 | 2:14 | Data | 0 | 33.837 | 32.035 | 169.667 | 7.64 | 160.279 | 2216.2 | 25.73 | 45.727 | 6.41 | 1.279 | 4.131 | 8314.11 | 1.317 | 97.9 | 76.3 | 1441 | 22.82 | 5404.2 | 2718.7 | 2673.5 | 3942.4 | 1221 | 0.67123 | 5.411
2024-12-10 | 2:14 | Data | 0 | 33.642 | 32.028 | 169.441 | 7.64 | 160.234 | 2213.49 | 25.73 | 45.727 | 6.4 | 1.282 | 4.115 | 8305.07 | 1.614 | 97.9 | 76.3 | 1439 | 22.86 | 5398.3 | 2710 | 2699.7 | 3958.4 | 1221 | 0.66939 | 5.396
2024-12-10 | 2:14 | Data | 0 | 33.628 | 32.231 | 169.486 | 7.64 | 160.189 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.285 | 4.129 | 8305.07 | 1.56 | 97.9 | 76.3 | 1437 | 22.86 | 5398.3 | 2699.3 | 2672 | 3931.4 | 1221 | 0.67201 | 5.414
2024-12-10 | 2:14 | Data | 0 | 33.534 | 32.15 | 169.577 | 7.64 | 160.234 | 2208.97 | 25.72 | 45.818 | 6.4 | 1.289 | 4.127 | 8305.07 | 1.722 | 97.9 | 76.2 | 1436 | 22.86 | 5398.3 | 2717.7 | 2667.1 | 3935.5 | 1221 | 0.67277 | 5.416
2024-12-10 | 2:14 | Data | 0 | 33.689 | 32.028 | 169.577 | 7.64 | 160.234 | 2208.97 | 25.72 | 45.727 | 6.4 | 1.301 | 4.134 | 8300.55 | 1.627 | 97.9 | 76.1 | 1435 | 22.86 | 5395.4 | 2694 | 2671.5 | 3925.8 | 1221.1 | 0.66892 | 5.436
2024-12-10 | 2:14 | Data | 0 | 33.446 | 32.028 | 169.577 | 7.64 | 160.279 | 2209.87 | 25.73 | 45.727 | 6.4 | 1.301 | 4.153 | 8332.2 | 1.398 | 97.9 | 76.2 | 1436 | 22.86 | 5415.9 | 2690 | 2664.1 | 3918 | 1221.1 | 0.66812 | 5.454
2024-12-10 | 2:14 | Data | 0 | 33.878 | 31.873 | 169.622 | 7.64 | 160.415 | 2208.06 | 25.73 | 45.727 | 6.4 | 1.301 | 4.151 | 8332.2 | 1.614 | 97.9 | 76.1 | 1435 | 22.86 | 5415.9 | 2705.3 | 2665.5 | 3925.3 | 1221.1 | 0.67038 | 5.452
2024-12-10 | 2:14 | Data | 0 | 33.702 | 32.028 | 169.622 | 7.64 | 160.279 | 2208.06 | 25.73 | 45.637 | 6.4 | 1.294 | 4.128 | 8336.72 | 1.519 | 97.9 | 76.1 | 1435 | 22.86 | 5418.9 | 2722 | 2682.2 | 3948.7 | 1221.1 | 0.67283 | 5.421
2024-12-10 | 2:14 | Data | 0 | 33.642 | 32.237 | 169.622 | 7.64 | 160.324 | 2208.97 | 25.73 | 45.727 | 6.4 | 1.296 | 4.124 | 8323.16 | 1.641 | 97.9 | 76.1 | 1435 | 22.86 | 5410.1 | 2704.5 | 2688.1 | 3941.8 | 1221.1 | 0.6685 | 5.42
2024-12-10 | 2:14 | Data | 0 | 33.642 | 32.028 | 169.577 | 7.64 | 160.189 | 2208.06 | 25.73 | 45.727 | 6.4 | 1.292 | 4.126 | 8345.77 | 1.62 | 97.9 | 76.1 | 1436 | 22.86 | 5424.8 | 2718.2 | 2674.3 | 3944.4 | 1221.1 | 0.67127 | 5.42
2024-12-10 | 2:15 | Data | 0 | 33.864 | 32.055 | 169.531 | 7.64 | 160.234 | 2206.25 | 25.72 | 45.727 | 6.4 | 1.294 | 4.142 | 8345.77 | 1.553 | 97.9 | 76.2 | 1434 | 22.86 | 5424.8 | 2707.4 | 2683.8 | 3939.5 | 1221.1 | 0.66861 | 5.436
2024-12-10 | 2:15 | Data | 0 | 33.534 | 32.028 | 169.577 | 7.64 | 160.279 | 2206.25 | 25.73 | 45.727 | 6.4 | 1.289 | 4.144 | 8350.29 | 1.6 | 97.9 | 76.3 | 1434 | 22.86 | 5427.7 | 2696.5 | 2673.3 | 3934.6 | 1221.1 | 0.66893 | 5.434
2024-12-10 | 2:15 | Data | 0 | 33.858 | 32.055 | 169.622 | 7.64 | 160.279 | 2208.97 | 25.73 | 45.637 | 6.4 | 1.288 | 4.116 | 8350.29 | 1.728 | 97.9 | 76.2 | 1436 | 22.82 | 5427.7 | 2700.7 | 2670 | 3923.9 | 1221.1 | 0.66917 | 5.406
2024-12-10 | 2:15 | Data | 0 | 33.864 | 32.082 | 169.486 | 7.64 | 160.279 | 2208.06 | 25.73 | 45.637 | 6.4 | 1.295 | 4.112 | 8345.77 | 1.62 | 97.9 | 76.1 | 1435 | 22.86 | 5424.8 | 2716.7 | 2700.4 | 3958.9 | 1221.1 | 0.66842 | 5.407
2024-12-10 | 2:15 | Data | 0 | 33.729 | 31.947 | 169.577 | 7.64 | 160.324 | 2210.77 | 25.73 | 45.457 | 6.4 | 1.288 | 4.122 | 8336.72 | 1.526 | 97.9 | 76.2 | 1437 | 22.77 | 5418.9 | 2664.8 | 2634.6 | 3943.8 | 1221.1 | 0.67078 | 5.411
2024-12-10 | 2:15 | Data | 0 | 33.797 | 32.062 | 169.622 | 7.64 | 160.279 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.29 | 4.139 | 8336.72 | 1.688 | 97.9 | 76.2 | 1437 | 22.86 | 5418.9 | 1637 | 2074.2 | 2656.1 | 1221.1 | 0.61369 | 5.43
2024-12-10 | 2:15 | Data | 0 | 33.817 | 32.426 | 169.622 | 7.64 | 160.234 | 2210.77 | 25.74 | 45.727 | 6.4 | 1.282 | 4.13 | 8350.29 | 1.668 | 97.9 | 76.3 | 1437 | 22.86 | 5427.7 | 1616.6 | 2067.4 | 2639.5 | 1221.1 | 0.61023 | 5.411
2024-12-10 | 2:15 | Data | 0 | 33.655 | 32.028 | 169.667 | 7.64 | 160.324 | 2211.68 | 25.72 | 45.727 | 6.4 | 1.289 | 4.108 | 8332.2 | 1.614 | 97.9 | 76.1 | 1438 | 22.86 | 5415.9 | 1613.2 | 2074.5 | 2642.2 | 1221.1 | 0.60859 | 5.397
2024-12-10 | 2:15 | Data | 0 | 33.864 | 32.143 | 169.622 | 7.64 | 160.279 | 2208.97 | 25.73 | 45.637 | 6.4 | 1.289 | 4.124 | 8341.25 | 1.607 | 97.9 | 76.2 | 1436 | 22.82 | 5421.8 | 1613.7 | 2086.3 | 2650.8 | 1221.1 | 0.60612 | 5.414
2024-12-10 | 2:15 | Data | 0 | 33.588 | 32.028 | 169.531 | 7.64 | 160.279 | 2210.77 | 25.73 | 45.637 | 6.4 | 1.291 | 4.141 | 8363.86 | 1.715 | 97.9 | 76.2 | 1437 | 22.86 | 5436.5 | 1621.2 | 2101.9 | 2668.9 | 1221.1 | 0.60478 | 5.431
2024-12-10 | 2:15 | Data | 0 | 33.621 | 32.028 | 169.486 | 7.64 | 160.234 | 2212.58 | 25.73 | 45.727 | 6.4 | 1.297 | 4.145 | 8359.34 | 1.6 | 97.9 | 76.2 | 1438 | 22.91 | 5433.6 | 1620.6 | 2098.2 | 2665.6 | 1221.1 | 0.60452 | 5.442
2024-12-10 | 2:15 | Data | 0 | 33.858 | 32.156 | 169.667 | 7.64 | 160.37 | 2208.97 | 25.72 | 45.818 | 6.4 | 1.301 | 4.134 | 8363.86 | 1.715 | 97.9 | 76.1 | 1435 | 22.86 | 5436.5 | 1631.6 | 2117.6 | 2687.2 | 1221.1 | 0.60494 | 5.435
2024-12-10 | 2:15 | Data | 0 | 33.642 | 32.075 | 169.667 | 7.64 | 160.279 | 2208.06 | 25.72 | 45.727 | 6.4 | 1.289 | 4.118 | 8363.86 | 1.526 | 97.9 | 76.2 | 1435 | 22.91 | 5436.5 | 1614.1 | 2096.2 | 2659.5 | 1221.1 | 0.60376 | 5.407
2024-12-10 | 2:15 | Data | 0 | 33.972 | 31.934 | 169.577 | 7.64 | 160.324 | 2208.97 | 25.73 | 45.727 | 6.4 | 1.292 | 4.124 | 8368.38 | 1.809 | 97.9 | 76.1 | 1435 | 22.86 | 5439.4 | 1618.5 | 2110.8 | 2676.3 | 1221.1 | 0.60217 | 5.416
2024-12-10 | 2:15 | Data | 0 | 33.756 | 32.042 | 169.577 | 7.64 | 160.234 | 2208.97 | 25.73 | 45.727 | 6.4 | 1.282 | 4.116 | 8318.64 | 1.722 | 97.9 | 76.2 | 1436 | 22.86 | 5407.1 | 1628 | 2089.1 | 2661.9 | 1221.1 | 0.60862 | 5.399
2024-12-10 | 2:15 | Data | 0 | 33.446 | 32.028 | 169.531 | 7.64 | 160.234 | 2205.35 | 25.73 | 45.727 | 6.4 | 1.289 | 4.102 | 8314.11 | 1.566 | 97.9 | 76.1 | 1433 | 22.82 | 5404.2 | 1629.7 | 2072.9 | 2651 | 1221.1 | 0.61208 | 5.391
2024-12-10 | 2:16 | Data | 0 | 33.54 | 32.028 | 169.577 | 7.64 | 160.279 | 2211.68 | 25.72 | 45.637 | 6.4 | 1.297 | 4.128 | 8314.11 | 1.398 | 97.9 | 76.1 | 1438 | 22.82 | 5404.2 | 1627.9 | 2079.6 | 2655.3 | 1221.1 | 0.60978 | 5.425
2024-12-10 | 2:16 | Data | 0 | 33.419 | 32.021 | 169.577 | 7.64 | 160.234 | 2211.68 | 25.72 | 45.727 | 6.4 | 1.291 | 4.128 | 8318.64 | 1.526 | 97.9 | 76.2 | 1438 | 22.86 | 5407.1 | 1643.6 | 2098.9 | 2677.9 | 1221.1 | 0.61169 | 5.419
2024-12-10 | 2:16 | Data | 0 | 33.473 | 32.021 | 169.667 | 7.64 | 160.279 | 2210.77 | 25.72 | 45.818 | 6.4 | 1.28 | 4.123 | 8350.29 | 1.404 | 97.9 | 76.3 | 1437 | 22.86 | 5427.7 | 1626 | 2083 | 2657.1 | 1221.1 | 0.60888 | 5.402
2024-12-10 | 2:16 | Data | 0 | 33.642 | 32.015 | 169.531 | 7.64 | 160.234 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.286 | 4.113 | 8345.77 | 1.661 | 97.9 | 76.2 | 1438 | 22.82 | 5424.8 | 1642.1 | 2094.3 | 2674.3 | 1221.1 | 0.61089 | 5.399
2024-12-10 | 2:16 | Data | 0 | 33.655 | 32.028 | 169.577 | 7.64 | 160.189 | 2209.87 | 25.72 | 45.727 | 6.4 | 1.279 | 4.106 | 8345.77 | 1.607 | 97.9 | 76.3 | 1438 | 22.86 | 5424.8 | 1627.6 | 2087 | 2660 | 1221.1 | 0.60957 | 5.385
2024-12-10 | 2:16 | Data | 0 | 33.52 | 31.812 | 169.486 | 7.64 | 160.189 | 2211.68 | 25.72 | 45.637 | 6.4 | 1.283 | 4.142 | 8350.29 | 1.614 | 97.9 | 76.3 | 1437 | 22.82 | 5427.7 | 1625.1 | 2090.1 | 2660.4 | 1221.1 | 0.60904 | 5.425
2024-12-10 | 2:16 | Data | 0 | 33.642 | 32.028 | 169.486 | 7.64 | 160.234 | 2211.68 | 25.73 | 45.727 | 6.4 | 1.296 | 4.152 | 8350.29 | 1.614 | 97.9 | 76.2 | 1437 | 22.86 | 5427.7 | 1626.9 | 2081.5 | 2656.9 | 1221.1 | 0.60955 | 5.448
2024-12-10 | 2:16 | Data | 0 | 33.642 | 31.913 | 169.622 | 7.64 | 160.189 | 2210.77 | 25.73 | 45.818 | 6.4 | 1.296 | 4.114 | 8345.77 | 1.627 | 97.9 | 76 | 1436 | 22.86 | 5424.8 | 1629.4 | 2096.4 | 2667.6 | 1221.1 | 0.60841 | 5.41
2024-12-10 | 2:16 | Data | 0 | 33.54 | 32.028 | 169.531 | 7.63 | 160.189 | 2210.77 | 25.72 | 45.727 | 6.4 | 1.294 | 4.13 | 8359.34 | 1.519 | 97.9 | 76.1 | 1438 | 22.91 | 5433.6 | 1634.5 | 2104.2 | 2676 | 1221.1 | 0.60573 | 5.424
2024-12-10 | 2:16 | Data | 0 | 33.642 | 32.197 | 169.622 | 7.64 | 160.234 | 2210.77 | 25.72 | 45.727 | 6.4 | 1.299 | 4.108 | 8359.34 | 1.519 | 97.9 | 76 | 1438 | 22.86 | 5433.6 | 1631.5 | 2101 | 2674 | 1221.1 | 0.61037 | 5.407
2024-12-10 | 2:16 | Data | 0 | 34.067 | 31.92 | 169.667 | 7.64 | 160.324 | 2211.68 | 25.72 | 45.727 | 6.4 | 1.291 | 4.13 | 8291.5 | 1.803 | 97.9 | 76.2 | 1438 | 22.86 | 5389.5 | 1623.3 | 2104.9 | 2673.5 | 1221.1 | 0.60365 | 5.422
2024-12-10 | 2:16 | Data | 0 | 33.5 | 32.136 | 169.577 | 7.64 | 160.279 | 2210.77 | 25.72 | 45.727 | 6.4 | 1.285 | 4.141 | 8314.11 | 1.452 | 97.9 | 76.3 | 1437 | 22.86 | 5404.2 | 1619.9 | 2106.8 | 2670.8 | 1221.1 | 0.60383 | 5.427
2024-12-10 | 2:16 | Data | 0 | 33.642 | 32.028 | 169.531 | 7.64 | 160.234 | 2210.77 | 25.71 | 45.637 | 6.4 | 1.295 | 4.134 | 8296.02 | 1.614 | 97.9 | 76.1 | 1437 | 22.86 | 5392.4 | 1634.6 | 2082 | 2673.7 | 1221.1 | 0.60978 | 5.429
2024-12-10 | 2:16 | Data | 0 | 33.615 | 32.028 | 169.531 | 7.64 | 160.189 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.291 | 4.097 | 8300.55 | 1.614 | 97.9 | 76 | 1437 | 22.86 | 5395.4 | 1632.1 | 2104.1 | 2670.3 | 1221.1 | 0.60809 | 5.39
2024-12-10 | 2:16 | Data | 0 | 33.864 | 32.042 | 169.531 | 7.64 | 160.234 | 2209.87 | 25.72 | 45.727 | 6.4 | 1.289 | 4.118 | 8345.77 | 1.647 | 97.9 | 76.2 | 1436 | 22.86 | 5424.8 | 1630.4 | 2104.1 | 2674.4 | 1221.1 | 0.60755 | 5.406
2024-12-10 | 2:16 | Data | 0 | 33.648 | 31.988 | 169.667 | 7.64 | 160.189 | 2210.77 | 25.72 | 45.637 | 6.4 | 1.282 | 4.115 | 8345.77 | 1.654 | 97.9 | 76.3 | 1438 | 22.86 | 5424.8 | 1617.2 | 2076.8 | 2646.7 | 1221.1 | 0.60801 | 5.397
2024-12-10 | 2:16 | Data | 0 | 33.588 | 32.345 | 169.577 | 7.64 | 160.279 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.286 | 4.128 | 8363.86 | 1.614 | 97.9 | 76.2 | 1437 | 22.82 | 5436.5 | 1634.6 | 2097.1 | 2671.4 | 1221.1 | 0.6085 | 5.414
2024-12-10 | 2:16 | Data | 0 | 33.635 | 32.028 | 169.486 | 7.64 | 160.144 | 2210.77 | 25.73 | 45.637 | 6.4 | 1.303 | 4.158 | 8359.34 | 1.614 | 97.9 | 76.1 | 1437 | 22.86 | 5433.6 | 1627.3 | 2082.7 | 2657.2 | 1221.1 | 0.60923 | 5.461
2024-12-10 | 2:17 | Data | 0 | 33.756 | 32.035 | 169.531 | 7.64 | 160.234 | 2215.29 | 25.71 | 45.727 | 6.4 | 1.287 | 4.131 | 8345.77 | 1.789 | 97.9 | 76.2 | 1439 | 22.86 | 5424.8 | 1623.2 | 2084.5 | 2654.1 | 1221.1 | 0.60931 | 5.418
2024-12-10 | 2:17 | Data | 0 | 33.642 | 31.805 | 169.396 | 7.64 | 160.144 | 2209.87 | 25.72 | 45.637 | 6.4 | 1.276 | 4.114 | 8345.77 | 1.701 | 97.9 | 76.3 | 1436 | 22.86 | 5424.8 | 1623.8 | 2080.1 | 2655 | 1221.1 | 0.60802 | 5.39
2024-12-10 | 2:17 | Data | 0 | 33.743 | 31.832 | 169.486 | 7.64 | 160.279 | 2208.97 | 25.72 | 45.727 | 6.4 | 1.283 | 4.078 | 8336.72 | 1.647 | 97.9 | 76.1 | 1436 | 22.86 | 5418.9 | 1622.8 | 2096.3 | 2667 | 1221.1 | 0.60926 | 5.363
2024-12-10 | 2:17 | Data | 0 | 33.642 | 32.204 | 169.622 | 7.64 | 160.234 | 2208.06 | 25.73 | 45.727 | 6.4 | 1.292 | 4.112 | 8332.2 | 1.614 | 97.9 | 76.1 | 1435 | 22.91 | 5415.9 | 1630.1 | 2089 | 2666.6 | 1221.1 | 0.61024 | 5.404
2024-12-10 | 2:17 | Data | 0 | 33.615 | 32.251 | 169.622 | 7.63 | 160.144 | 2203.54 | 25.72 | 45.637 | 6.4 | 1.294 | 4.115 | 8309.59 | 1.634 | 97.9 | 76.1 | 1432 | 22.82 | 5401.2 | 1638.8 | 2122.2 | 2698.4 | 1221.1 | 0.60577 | 5.41
2024-12-10 | 2:17 | Data | 0 | 33.588 | 31.826 | 169.577 | 7.64 | 160.234 | 2208.06 | 25.72 | 45.727 | 6.4 | 1.288 | 4.141 | 8314.11 | 1.809 | 97.9 | 76.3 | 1435 | 22.86 | 5404.2 | 1619.3 | 2132.7 | 2690.6 | 1221.1 | 0.59953 | 5.43
2024-12-10 | 2:17 | Data | 0 | 33.642 | 32.075 | 169.577 | 7.64 | 160.279 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.282 | 4.124 | 8318.64 | 1.681 | 97.9 | 76.3 | 1438 | 22.86 | 5407.1 | 1620.7 | 2139.6 | 2700.1 | 1221.1 | 0.59699 | 5.406
2024-12-10 | 2:17 | Data | 0 | 33.648 | 31.913 | 169.577 | 7.64 | 160.234 | 2210.77 | 25.72 | 45.727 | 6.4 | 1.276 | 4.123 | 8318.64 | 1.614 | 97.9 | 76.4 | 1437 | 22.86 | 5407.1 | 1622.4 | 2107.7 | 2675.7 | 1221.1 | 0.60336 | 5.399
2024-12-10 | 2:17 | Data | 0 | 33.419 | 32.021 | 169.486 | 7.64 | 160.189 | 2210.77 | 25.73 | 45.637 | 6.4 | 1.284 | 4.126 | 8323.16 | 1.506 | 97.9 | 76.3 | 1436 | 22.86 | 5410.1 | 1629.7 | 2080.5 | 2658.1 | 1221.1 | 0.61044 | 5.411
2024-12-10 | 2:17 | Data | 0 | 33.81 | 32.028 | 169.531 | 7.64 | 160.279 | 2211.68 | 25.72 | 45.457 | 6.4 | 1.296 | 4.151 | 8318.64 | 1.634 | 97.9 | 76.2 | 1438 | 22.68 | 5407.1 | 1621.5 | 2083.4 | 2656 | 1221.1 | 0.60743 | 5.447
2024-12-10 | 2:17 | Data | 0 | 33.972 | 32.237 | 169.577 | 7.64 | 160.279 | 2210.77 | 25.71 | 45.457 | 6.4 | 1.29 | 4.139 | 8345.77 | 1.715 | 97.9 | 76.2 | 1437 | 22.73 | 5424.8 | 1642 | 2111.8 | 2689.2 | 1221.1 | 0.60805 | 5.429
2024-12-10 | 2:17 | Data | 0 | 33.743 | 32.204 | 169.622 | 7.64 | 160.279 | 2210.77 | 25.72 | 45.547 | 6.41 | 1.279 | 4.118 | 8332.2 | 1.688 | 97.9 | 76.3 | 1438 | 22.73 | 5415.9 | 1636.6 | 2093.9 | 2673 | 1221.1 | 0.6096 | 5.398
2024-12-10 | 2:17 | Data | 0 | 33.642 | 32.028 | 169.622 | 7.64 | 160.234 | 2211.68 | 25.71 | 45.457 | 6.4 | 1.289 | 4.129 | 8359.34 | 1.614 | 97.9 | 76.2 | 1437 | 22.73 | 5433.6 | 1656.2 | 2092.4 | 2679.6 | 1221.1 | 0.61252 | 5.419
2024-12-10 | 2:17 | Data | 0 | 33.844 | 32.251 | 169.622 | 7.64 | 160.234 | 2206.25 | 25.72 | 45.366 | 6.4 | 1.287 | 4.125 | 8350.29 | 1.627 | 97.9 | 76.2 | 1435 | 22.73 | 5427.7 | 1659.7 | 2132 | 2719.2 | 1221.1 | 0.60725 | 5.411
2024-12-10 | 2:17 | Data | 0 | 33.756 | 32.305 | 169.667 | 7.64 | 160.234 | 2210.77 | 25.71 | 45.366 | 6.4 | 1.294 | 4.122 | 8363.86 | 1.553 | 97.9 | 76.1 | 1438 | 22.68 | 5436.5 | 1644.6 | 2114.8 | 2692.5 | 1221.2 | 0.60789 | 5.417
2024-12-10 | 2:17 | Data | 0 | 33.669 | 32.028 | 169.486 | 7.64 | 160.144 | 2209.87 | 25.71 | 45.457 | 6.4 | 1.295 | 4.125 | 8359.34 | 1.62 | 97.9 | 76.1 | 1437 | 22.73 | 5433.6 | 1646.6 | 2114.4 | 2695 | 1221.2 | 0.60814 | 5.42
2024-12-10 | 2:17 | Data | 0 | 33.426 | 32.001 | 169.531 | 7.64 | 160.144 | 2210.77 | 25.71 | 45.457 | 6.4 | 1.293 | 4.129 | 8350.29 | 1.553 | 97.9 | 76.1 | 1437 | 22.68 | 5427.7 | 1664.2 | 2125.2 | 2715.3 | 1221.2 | 0.61004 | 5.422
2024-12-10 | 2:17 | Data | 0 | 33.635 | 32.028 | 169.622 | 7.64 | 160.234 | 2212.58 | 25.7 | 45.457 | 6.4 | 1.291 | 4.153 | 8350.29 | 1.614 | 97.9 | 76.3 | 1438 | 22.73 | 5427.7 | 1642.8 | 2094.4 | 2677 | 1221.2 | 0.61096 | 5.444
2024-12-10 | 2:18 | Data | 0 | 33.412 | 31.846 | 169.396 | 7.64 | 160.099 | 2211.68 | 25.71 | 45.457 | 6.4 | 1.289 | 4.115 | 8323.16 | 1.688 | 97.9 | 76.1 | 1438 | 22.73 | 5410.1 | 1667.6 | 2108.4 | 2702.5 | 1221.2 | 0.61419 | 5.404
2024-12-10 | 2:18 | Data | 0 | 33.851 | 31.832 | 169.486 | 7.64 | 160.279 | 2210.77 | 25.71 | 45.366 | 6.4 | 1.29 | 4.132 | 8323.16 | 1.708 | 97.9 | 76.2 | 1437 | 22.73 | 5410.1 | 1642.1 | 2095.9 | 2676.8 | 1221.2 | 0.61079 | 5.421
2024-12-10 | 2:18 | Data | 0 | 33.743 | 32.028 | 169.577 | 7.63 | 160.234 | 2209.87 | 25.71 | 45.457 | 6.4 | 1.288 | 4.138 | 8332.2 | 1.512 | 97.9 | 76.3 | 1436 | 22.73 | 5415.9 | 1662 | 2084.1 | 2680.8 | 1221.2 | 0.61307 | 5.426
2024-12-10 | 2:18 | Data | 0 | 33.628 | 32.204 | 169.577 | 7.63 | 160.189 | 2210.77 | 25.71 | 45.457 | 6.4 | 1.282 | 4.124 | 8336.72 | 1.499 | 97.9 | 76.3 | 1437 | 22.68 | 5418.9 | 1638.2 | 2091.7 | 2673.1 | 1221.2 | 0.60981 | 5.403
2024-12-10 | 2:18 | Data | 0 | 33.513 | 32.048 | 169.396 | 7.64 | 160.189 | 2210.77 | 25.71 | 45.457 | 6.4 | 1.286 | 4.096 | 8341.25 | 1.789 | 97.9 | 76.1 | 1438 | 22.73 | 5421.8 | 1647.4 | 2093.7 | 2679 | 1221.2 | 0.61229 | 5.382
2024-12-10 | 2:18 | Data | 0 | 33.642 | 32.008 | 169.531 | 7.64 | 160.099 | 2212.58 | 25.71 | 45.457 | 6.4 | 1.284 | 4.129 | 8332.2 | 1.539 | 97.9 | 76.3 | 1438 | 22.73 | 5415.9 | 2692.8 | 3603.8 | 4537.9 | 1221.2 | 0.59644 | 5.413
2024-12-10 | 2:18 | Data | 0 | 33.817 | 32.028 | 169.577 | 7.63 | 160.279 | 2211.68 | 25.71 | 45.457 | 6.4 | 1.28 | 4.133 | 8345.77 | 1.654 | 97.9 | 76.4 | 1437 | 22.68 | 5424.8 | 2735.1 | 2699.2 | 3978 | 1221.2 | 0.66979 | 5.412
2024-12-10 | 2:18 | Data | 0 | 33.412 | 31.799 | 169.35 | 7.64 | 160.099 | 2209.87 | 25.7 | 45.457 | 6.4 | 1.291 | 4.119 | 8354.81 | 1.614 | 97.9 | 76.1 | 1437 | 22.73 | 5430.6 | 2742.7 | 2711.9 | 3990.1 | 1221.2 | 0.66848 | 5.41
2024-12-10 | 2:18 | Data | 0 | 33.642 | 32.028 | 169.531 | 7.63 | 160.144 | 2203.54 | 25.72 | 45.457 | 6.4 | 1.293 | 4.129 | 8359.34 | 1.614 | 97.9 | 76.1 | 1432 | 22.68 | 5433.6 | 2726.2 | 2711 | 3980 | 1221.2 | 0.66675 | 5.422
2024-12-10 | 2:18 | Data | 0 | 33.635 | 32.028 | 169.531 | 7.63 | 160.099 | 2203.54 | 25.71 | 45.457 | 6.4 | 1.293 | 4.142 | 8359.34 | 1.614 | 97.9 | 76.2 | 1432 | 22.68 | 5433.6 | 2742.8 | 2706 | 3983.8 | 1221.2 | 0.66983 | 5.435
2024-12-10 | 2:18 | Data | 0 | 33.426 | 31.812 | 169.441 | 7.64 | 160.099 | 2208.97 | 25.73 | 45.457 | 6.4 | 1.286 | 4.148 | 8390.99 | 1.573 | 97.9 | 76.3 | 1435 | 22.77 | 5454.1 | 2671.8 | 2710.6 | 3934.2 | 1221.2 | 0.66259 | 5.434
2024-12-10 | 2:18 | Data | 0 | 33.439 | 32.163 | 169.396 | 7.64 | 160.144 | 2124.01 | 25.71 | 45.457 | 6.4 | 1.277 | 4.152 | 8386.47 | 1.553 | 97.9 | 76.5 | 1379 | 22.73 | 5451.2 | 2657 | 2700.1 | 3917 | 1221.2 | 0.66233 | 5.429
2024-12-10 | 2:18 | Data | 0 | 33.412 | 31.799 | 169.396 | 7.64 | 160.144 | 2186.37 | 25.71 | 45.727 | 6.4 | 1.283 | 4.156 | 8372.9 | 1.614 | 97.9 | 76.4 | 1424 | 22.86 | 5442.4 | 2668.5 | 2683 | 3915.2 | 1221.2 | 0.66296 | 5.44
2024-12-10 | 2:18 | Data | 0 | 33.426 | 31.799 | 169.486 | 7.63 | 160.144 | 2213.49 | 25.71 | 45.637 | 6.4 | 1.294 | 4.125 | 8372.9 | 1.526 | 97.9 | 76.1 | 1439 | 22.82 | 5442.4 | 2664.6 | 2685.9 | 3902.3 | 1221.2 | 0.66351 | 5.421
2024-12-10 | 2:18 | Data | 0 | 33.615 | 31.812 | 169.486 | 7.64 | 160.099 | 2212.58 | 25.71 | 45.457 | 6.4 | 1.288 | 4.118 | 8336.72 | 1.627 | 97.9 | 76.2 | 1438 | 22.73 | 5418.9 | 2668.2 | 2711 | 3929.3 | 1221.2 | 0.66439 | 5.406
2024-12-10 | 2:18 | Data | 0 | 33.723 | 32.129 | 169.486 | 7.64 | 160.144 | 2212.58 | 25.71 | 45.457 | 6.4 | 1.289 | 4.111 | 8318.64 | 1.722 | 97.9 | 76.1 | 1438 | 22.68 | 5407.1 | 2664.7 | 2722.8 | 3935.7 | 1221.2 | 0.66082 | 5.4
2024-12-10 | 2:18 | Data | 0 | 33.189 | 31.853 | 169.531 | 7.64 | 160.099 | 2211.68 | 25.7 | 45.637 | 6.4 | 1.288 | 4.127 | 8336.72 | 1.58 | 97.9 | 76.2 | 1438 | 22.86 | 5418.9 | 2670.1 | 2720.8 | 3935.3 | 1221.2 | 0.66259 | 5.415
2024-12-10 | 2:18 | Data | 0 | 33.567 | 31.758 | 169.486 | 7.64 | 160.234 | 2218.91 | 25.72 | 45.727 | 6.4 | 1.297 | 4.12 | 8332.2 | 1.539 | 97.9 | 76 | 1442 | 22.86 | 5415.9 | 2661.8 | 2712.9 | 3929.1 | 1221.2 | 0.66177 | 5.419
2024-12-10 | 2:19 | Data | 0 | 33.655 | 32.028 | 169.531 | 7.64 | 160.279 | 2213.49 | 25.71 | 45.727 | 6.4 | 1.299 | 4.123 | 8318.64 | 1.614 | 97.9 | 76.1 | 1439 | 22.86 | 5407.1 | 2676.1 | 2684.5 | 3918.9 | 1221.2 | 0.66516 | 5.42
2024-12-10 | 2:19 | Data | 0 | 33.682 | 31.799 | 169.531 | 7.64 | 160.189 | 2214.39 | 25.73 | 45.727 | 6.4 | 1.294 | 4.108 | 8314.11 | 1.404 | 97.9 | 76.1 | 1439 | 22.86 | 5404.2 | 2715 | 2701.7 | 3961.7 | 1221.2 | 0.66821 | 5.402
2024-12-10 | 2:19 | Data | 0 | 33.311 | 31.778 | 169.396 | 7.64 | 160.144 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.29 | 4.115 | 8314.11 | 1.492 | 97.9 | 76.1 | 1437 | 22.82 | 5404.2 | 2699.5 | 2698.4 | 3950.4 | 1221.2 | 0.66558 | 5.405
2024-12-10 | 2:19 | Data | 0 | 33.527 | 32.028 | 169.396 | 7.64 | 160.053 | 2212.58 | 25.73 | 45.637 | 6.4 | 1.283 | 4.119 | 8318.64 | 1.607 | 97.9 | 76.2 | 1439 | 22.86 | 5407.1 | 2724 | 2718.6 | 3973.5 | 1221.2 | 0.66826 | 5.402
2024-12-10 | 2:19 | Data | 0 | 33.513 | 31.603 | 169.396 | 7.64 | 160.053 | 2214.39 | 25.73 | 45.727 | 6.4 | 1.294 | 4.115 | 8359.34 | 1.728 | 97.9 | 76.1 | 1439 | 22.86 | 5433.6 | 2722.1 | 2705.3 | 3968.1 | 1221.2 | 0.66888 | 5.409
2024-12-10 | 2:19 | Data | 0 | 33.412 | 31.974 | 169.35 | 7.64 | 160.053 | 2214.39 | 25.71 | 45.727 | 6.4 | 1.284 | 4.157 | 8359.34 | 1.614 | 97.9 | 76.4 | 1439 | 22.86 | 5433.6 | 2716 | 2718 | 3973.7 | 1221.2 | 0.66617 | 5.44
2024-12-10 | 2:19 | Data | 0 | 33.412 | 31.805 | 169.35 | 7.64 | 160.099 | 2213.49 | 25.72 | 45.818 | 6.4 | 1.285 | 4.131 | 8359.34 | 1.607 | 97.9 | 76.3 | 1439 | 22.86 | 5433.6 | 2711.9 | 2705.5 | 3957.6 | 1221.2 | 0.66646 | 5.416
2024-12-10 | 2:19 | Data | 0 | 33.223 | 31.785 | 169.396 | 7.64 | 160.144 | 2211.68 | 25.71 | 45.637 | 6.4 | 1.296 | 4.134 | 8359.34 | 1.418 | 97.9 | 76.1 | 1437 | 22.82 | 5433.6 | 2720.2 | 2709.3 | 3967.9 | 1221.2 | 0.66765 | 5.43
2024-12-10 | 2:19 | Data | 0 | 33.412 | 31.9 | 169.396 | 7.64 | 160.144 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.291 | 4.118 | 8363.86 | 1.499 | 97.9 | 76.1 | 1437 | 22.86 | 5436.5 | 2709.2 | 2723.7 | 3968.7 | 1221.2 | 0.66461 | 5.409
2024-12-10 | 2:19 | Data | 0 | 33.102 | 31.751 | 169.396 | 7.64 | 160.099 | 2210.77 | 25.72 | 45.727 | 6.4 | 1.287 | 4.133 | 8359.34 | 1.593 | 97.9 | 76.3 | 1437 | 22.86 | 5433.6 | 2708.3 | 2725.8 | 3971.8 | 1221.2 | 0.66357 | 5.42
2024-12-10 | 2:19 | Data | 0 | 33.635 | 31.799 | 169.441 | 7.64 | 160.189 | 2210.77 | 25.71 | 45.727 | 6.4 | 1.287 | 4.121 | 8332.2 | 1.641 | 97.9 | 76.2 | 1437 | 22.86 | 5415.9 | 2715.2 | 2705.2 | 3964.7 | 1221.2 | 0.66557 | 5.409
2024-12-10 | 2:19 | Data | 0 | 33.412 | 31.853 | 169.35 | 7.64 | 160.144 | 2208.97 | 25.71 | 45.727 | 6.4 | 1.292 | 4.13 | 8350.29 | 1.614 | 97.9 | 76.2 | 1435 | 22.86 | 5427.7 | 2724.8 | 2705.6 | 3969.7 | 1221.2 | 0.66803 | 5.422
2024-12-10 | 2:19 | Data | 0 | 33.527 | 32.008 | 169.441 | 7.64 | 160.099 | 2208.06 | 25.71 | 45.637 | 6.4 | 1.29 | 4.126 | 8345.77 | 1.735 | 97.9 | 76.2 | 1436 | 22.82 | 5424.8 | 2718.7 | 2709 | 3968.2 | 1221.2 | 0.6684 | 5.417
2024-12-10 | 2:19 | Data | 0 | 33.5 | 32.244 | 169.531 | 7.64 | 160.099 | 2208.97 | 25.73 | 45.637 | 6.41 | 1.29 | 4.116 | 8345.77 | 1.58 | 97.9 | 76.1 | 1436 | 22.82 | 5424.8 | 2713.9 | 2690.9 | 3953.9 | 1221.2 | 0.66936 | 5.406
2024-12-10 | 2:19 | Data | 0 | 33.628 | 31.88 | 169.486 | 7.64 | 160.144 | 2205.35 | 25.73 | 45.727 | 6.4 | 1.289 | 4.103 | 8336.72 | 1.688 | 97.9 | 76.1 | 1433 | 22.86 | 5418.9 | 2723.4 | 2700.7 | 3961.1 | 1221.2 | 0.67013 | 5.393
2024-12-10 | 2:19 | Data | 0 | 33.304 | 31.684 | 169.441 | 7.64 | 160.144 | 2208.06 | 25.71 | 45.637 | 6.4 | 1.294 | 4.112 | 8345.77 | 1.6 | 97.9 | 76.1 | 1435 | 22.86 | 5424.8 | 2723.3 | 2686.9 | 3953.8 | 1221.2 | 0.672 | 5.406
2024-12-10 | 2:19 | Data | 0 | 33.243 | 31.859 | 169.396 | 7.64 | 160.053 | 2208.97 | 25.71 | 45.727 | 6.4 | 1.282 | 4.105 | 8345.77 | 1.614 | 97.9 | 76.2 | 1435 | 22.86 | 5424.8 | 2719.4 | 2695.2 | 3958.6 | 1221.2 | 0.66855 | 5.388
2024-12-10 | 2:20 | Data | 0 | 33.615 | 31.92 | 169.531 | 7.64 | 160.189 | 2208.97 | 25.7 | 45.637 | 6.4 | 1.276 | 4.105 | 8345.77 | 1.6 | 97.9 | 76.3 | 1436 | 22.82 | 5424.8 | 2725.1 | 2682.7 | 3952.1 | 1221.2 | 0.67069 | 5.382
2024-12-10 | 2:20 | Data | 0 | 33.412 | 31.974 | 169.486 | 7.64 | 160.144 | 2208.06 | 25.71 | 45.727 | 6.4 | 1.283 | 4.134 | 8345.77 | 1.438 | 97.9 | 76.3 | 1435 | 22.86 | 5424.8 | 2701.7 | 2688.5 | 3935.3 | 1221.2 | 0.66744 | 5.418
2024-12-10 | 2:20 | Data | 0 | 33.412 | 31.967 | 169.35 | 7.64 | 160.053 | 2208.97 | 25.71 | 45.727 | 6.4 | 1.282 | 4.132 | 8336.72 | 1.728 | 97.9 | 76.3 | 1436 | 22.86 | 5418.9 | 2716.3 | 2681.2 | 3944.3 | 1221.2 | 0.67187 | 5.413
2024-12-10 | 2:20 | Data | 0 | 33.358 | 31.994 | 169.396 | 7.64 | 160.144 | 2208.06 | 25.7 | 45.637 | 6.4 | 1.284 | 4.134 | 8345.77 | 1.499 | 97.9 | 76.3 | 1436 | 22.86 | 5424.8 | 2716.2 | 2710.3 | 3964.7 | 1221.2 | 0.66912 | 5.419
2024-12-10 | 2:20 | Data | 0 | 33.669 | 31.826 | 169.441 | 7.64 | 160.099 | 2208.06 | 25.71 | 43.561 | 6.4 | 1.285 | 4.101 | 8345.77 | 1.742 | 98 | 76.1 | 1436 | 21.78 | 5424.8 | 2695.2 | 2678.7 | 3932 | 1221.3 | 0.66752 | 5.386
2024-12-10 | 2:20 | Data | 0 | 33.338 | 31.569 | 169.396 | 7.64 | 160.053 | 2206.25 | 25.72 | 45.637 | 6.4 | 1.28 | 4.112 | 8350.29 | 1.627 | 97.9 | 76.2 | 1434 | 22.82 | 5427.7 | 2705.9 | 2671.9 | 3935.8 | 1221.3 | 0.67047 | 5.392
2024-12-10 | 2:20 | Data | 0 | 33.237 | 31.913 | 169.26 | 7.64 | 160.099 | 2205.35 | 25.71 | 45.727 | 6.4 | 1.286 | 4.123 | 8345.77 | 1.573 | 97.9 | 76.2 | 1433 | 22.86 | 5424.8 | 2700.5 | 2662.7 | 3924 | 1221.3 | 0.67293 | 5.409
2024-12-10 | 2:20 | Data | 0 | 33.412 | 31.994 | 169.531 | 7.64 | 160.053 | 2206.25 | 25.73 | 45.637 | 6.4 | 1.287 | 4.109 | 8323.16 | 1.452 | 97.9 | 76.1 | 1433 | 22.82 | 5410.1 | 2690.7 | 2662.3 | 3918.6 | 1221.3 | 0.672 | 5.397
2024-12-10 | 2:20 | Data | 0 | 33.399 | 31.799 | 169.305 | 7.64 | 160.053 | 2206.25 | 25.72 | 45.818 | 6.41 | 1.29 | 4.144 | 8314.11 | 1.782 | 97.9 | 76.3 | 1434 | 22.86 | 5404.2 | 2709.3 | 2652.7 | 3921 | 1221.3 | 0.67473 | 5.434
2024-12-10 | 2:20 | Data | 0 | 33.183 | 31.772 | 169.305 | 7.63 | 160.053 | 2207.16 | 25.72 | 45.637 | 6.4 | 1.287 | 4.115 | 8314.11 | 1.411 | 97.9 | 76.2 | 1434 | 22.82 | 5404.2 | 2703.2 | 2638.1 | 3902.8 | 1221.3 | 0.67615 | 5.402
2024-12-10 | 2:20 | Data | 0 | 33.183 | 31.63 | 169.396 | 7.64 | 160.008 | 2208.97 | 25.74 | 45.727 | 6.4 | 1.297 | 4.105 | 8318.64 | 1.695 | 97.9 | 76 | 1436 | 22.82 | 5407.1 | 2699.2 | 2649.8 | 3912.4 | 1221.3 | 0.67225 | 5.401
2024-12-10 | 2:20 | Data | 0 | 33.399 | 31.799 | 169.441 | 7.64 | 160.053 | 2208.06 | 25.73 | 45.637 | 6.4 | 1.293 | 4.105 | 8341.25 | 1.614 | 97.9 | 76 | 1435 | 22.86 | 5421.8 | 2690 | 2667.3 | 3917.1 | 1221.3 | 0.6696 | 5.4
2024-12-10 | 2:20 | Data | 0 | 33.527 | 31.967 | 169.441 | 7.64 | 160.144 | 2208.97 | 25.74 | 45.637 | 6.4 | 1.28 | 4.108 | 8309.59 | 1.661 | 97.9 | 76.2 | 1435 | 22.86 | 5401.2 | 2719.3 | 2660.4 | 3916.6 | 1221.3 | 0.67272 | 5.39
2024-12-10 | 2:20 | Data | 0 | 33.412 | 31.967 | 169.396 | 7.63 | 160.053 | 2208.97 | 25.74 | 45.637 | 6.4 | 1.29 | 4.095 | 8314.11 | 1.56 | 97.9 | 76 | 1436 | 22.86 | 5404.2 | 2693.5 | 2633.3 | 3904 | 1221.3 | 0.67359 | 5.384
2024-12-10 | 2:20 | Data | 0 | 33.324 | 31.886 | 169.35 | 7.64 | 160.144 | 2209.87 | 25.73 | 45.727 | 6.4 | 1.291 | 4.096 | 8336.72 | 1.701 | 97.9 | 76.1 | 1436 | 22.86 | 5418.9 | 2708.4 | 2642.7 | 3916.3 | 1221.3 | 0.67518 | 5.385
2024-12-10 | 2:20 | Data | 0 | 33.581 | 32.069 | 169.531 | 7.64 | 160.099 | 2212.58 | 25.73 | 45.727 | 6.41 | 1.283 | 4.099 | 8332.2 | 1.695 | 97.9 | 76.2 | 1438 | 22.86 | 5415.9 | 2698.1 | 2665.8 | 3920.5 | 1221.3 | 0.67231 | 5.384
2024-12-10 | 2:20 | Data | 0 | 33.412 | 31.799 | 169.26 | 7.64 | 160.099 | 2210.77 | 25.73 | 45.457 | 6.4 | 1.294 | 4.104 | 8332.2 | 1.411 | 97.9 | 76 | 1437 | 22.73 | 5415.9 | 2688.3 | 2642.9 | 3900.3 | 1221.3 | 0.67229 | 5.398
2024-12-10 | 2:20 | Data | 0 | 33.615 | 31.812 | 169.486 | 7.64 | 160.144 | 2205.35 | 25.73 | 45.727 | 6.4 | 1.288 | 4.106 | 8323.16 | 1.809 | 97.9 | 76.1 | 1434 | 22.82 | 5410.1 | 2705.4 | 2654.8 | 3920.3 | 1221.3 | 0.67356 | 5.392
2024-12-10 | 2:21 | Data | 0 | 33.412 | 31.819 | 169.305 | 7.64 | 160.008 | 2210.77 | 25.74 | 45.637 | 6.4 | 1.294 | 4.125 | 8341.25 | 1.566 | 97.9 | 76.1 | 1437 | 22.86 | 5421.8 | 2716.7 | 2644.2 | 3918.8 | 1221.3 | 0.67599 | 5.42
2024-12-10 | 2:21 | Data | 0 | 33.453 | 31.778 | 169.486 | 7.63 | 160.144 | 2211.68 | 25.73 | 45.727 | 6.4 | 1.299 | 4.134 | 8345.77 | 1.526 | 97.9 | 76.1 | 1437 | 22.86 | 5424.8 | 2704 | 2649.2 | 3914.5 | 1221.3 | 0.67201 | 5.431
2024-12-10 | 2:21 | Data | 0 | 33.412 | 31.751 | 169.35 | 7.64 | 160.099 | 2205.35 | 25.72 | 45.727 | 6.4 | 1.295 | 4.109 | 8323.16 | 1.816 | 97.9 | 76 | 1433 | 22.86 | 5410.1 | 2717.9 | 2638 | 3913.8 | 1221.3 | 0.67672 | 5.403
2024-12-10 | 2:21 | Data | 0 | 33.412 | 31.785 | 169.35 | 7.64 | 160.008 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.286 | 4.109 | 8323.16 | 1.668 | 97.9 | 76.2 | 1437 | 22.86 | 5410.1 | 2709.1 | 2662 | 3931.7 | 1221.3 | 0.67161 | 5.396
2024-12-10 | 2:21 | Data | 0 | 33.189 | 31.785 | 169.305 | 7.64 | 160.099 | 2211.68 | 25.73 | 45.637 | 6.4 | 1.284 | 4.103 | 8345.77 | 1.614 | 97.9 | 76.2 | 1438 | 22.86 | 5424.8 | 2702.3 | 2669.2 | 3927.1 | 1221.3 | 0.67018 | 5.386
2024-12-10 | 2:21 | Data | 0 | 33.459 | 31.758 | 169.441 | 7.64 | 160.053 | 2208.06 | 25.74 | 45.727 | 6.4 | 1.3 | 4.144 | 8318.64 | 1.701 | 97.9 | 76.1 | 1436 | 22.86 | 5407.1 | 2705.2 | 2654.6 | 3917.4 | 1221.3 | 0.67384 | 5.444
2024-12-10 | 2:21 | Data | 0 | 33.297 | 31.967 | 169.305 | 7.64 | 160.008 | 2208.06 | 25.72 | 45.727 | 6.4 | 1.29 | 4.114 | 8314.11 | 1.607 | 97.9 | 76.1 | 1435 | 22.82 | 5404.2 | 2703.7 | 2648.9 | 3916.4 | 1221.3 | 0.67216 | 5.403
2024-12-10 | 2:21 | Data | 0 | 33.412 | 31.846 | 169.441 | 7.64 | 160.099 | 2208.06 | 25.72 | 45.727 | 6.4 | 1.275 | 4.091 | 8323.16 | 1.681 | 97.9 | 76.2 | 1436 | 22.86 | 5410.1 | 2714.2 | 2659.2 | 3930.5 | 1221.3 | 0.67549 | 5.366
2024-12-10 | 2:21 | Data | 0 | 33.527 | 32.021 | 169.441 | 7.64 | 160.099 | 2206.25 | 25.73 | 45.637 | 6.4 | 1.282 | 4.108 | 8332.2 | 1.6 | 97.9 | 76.2 | 1434 | 22.82 | 5415.9 | 2686.6 | 2654.6 | 3906.4 | 1221.3 | 0.67026 | 5.39
2024-12-10 | 2:21 | Data | 0 | 33.412 | 31.799 | 169.486 | 7.64 | 160.144 | 2208.97 | 25.72 | 45.637 | 6.4 | 1.285 | 4.142 | 8336.72 | 1.614 | 97.9 | 76.3 | 1436 | 22.86 | 5418.9 | 2701.3 | 2652.3 | 3916.3 | 1221.3 | 0.6727 | 5.427
2024-12-10 | 2:21 | Data | 0 | 33.412 | 31.826 | 169.441 | 7.64 | 160.099 | 2208.06 | 25.73 | 45.908 | 6.4 | 1.293 | 4.123 | 8359.34 | 1.506 | 97.9 | 76.1 | 1435 | 22.91 | 5433.6 | 2706.8 | 2666.3 | 3928.6 | 1221.3 | 0.671 | 5.416
2024-12-10 | 2:21 | Data | 0 | 33.642 | 31.805 | 169.531 | 7.64 | 160.189 | 2206.25 | 25.73 | 45.637 | 6.41 | 1.29 | 4.098 | 8354.81 | 1.83 | 97.9 | 76.1 | 1433 | 22.82 | 5430.6 | 2694.3 | 2628.7 | 3895.6 | 1221.3 | 0.67312 | 5.389
2024-12-10 | 2:21 | Data | 0 | 33.426 | 31.913 | 169.396 | 7.64 | 160.053 | 2205.35 | 25.72 | 45.727 | 6.4 | 1.287 | 4.125 | 8363.86 | 1.62 | 97.9 | 76.2 | 1434 | 22.86 | 5436.5 | 2710.8 | 2635.5 | 3907.1 | 1221.3 | 0.67639 | 5.412
2024-12-10 | 2:21 | Data | 0 | 33.324 | 31.799 | 169.396 | 7.64 | 160.053 | 2205.35 | 25.73 | 45.727 | 6.4 | 1.284 | 4.11 | 8359.34 | 1.6 | 97.9 | 76.2 | 1433 | 22.86 | 5433.6 | 2706.5 | 2631.7 | 3906.1 | 1221.3 | 0.67497 | 5.395
2024-12-10 | 2:21 | Data | 0 | 33.473 | 31.799 | 169.441 | 7.64 | 160.053 | 2205.35 | 25.73 | 45.818 | 6.4 | 1.277 | 4.122 | 8372.9 | 1.62 | 97.9 | 76.3 | 1434 | 22.82 | 5442.4 | 2703.3 | 2648.4 | 3911.6 | 1221.3 | 0.67492 | 5.399
2024-12-10 | 2:21 | Data | 0 | 33.628 | 31.967 | 169.441 | 7.64 | 160.144 | 2201.74 | 25.73 | 45.727 | 6.4 | 1.282 | 4.122 | 8372.9 | 1.506 | 97.9 | 76.3 | 1431 | 22.86 | 5442.4 | 2702.6 | 2650.6 | 3911.8 | 1221.3 | 0.67493 | 5.404
2024-12-10 | 2:21 | Data | 0 | 33.243 | 31.799 | 169.396 | 7.64 | 160.099 | 2203.54 | 25.73 | 45.637 | 6.4 | 1.288 | 4.113 | 8372.9 | 1.728 | 97.9 | 76.2 | 1432 | 22.86 | 5442.4 | 2713.6 | 2667.1 | 3930.8 | 1221.3 | 0.67359 | 5.401
2024-12-10 | 2:21 | Data | 0 | 33.615 | 31.812 | 169.441 | 7.64 | 160.099 | 2205.35 | 25.73 | 45.276 | 6.4 | 1.291 | 4.136 | 8359.34 | 1.668 | 98 | 76.2 | 1433 | 22.64 | 5433.6 | 2701.7 | 2677.3 | 3931.9 | 1221.3 | 0.66887 | 5.426
2024-12-10 | 2:22 | Data | 0 | 33.439 | 31.805 | 169.396 | 7.64 | 160.144 | 2206.25 | 25.73 | 45.727 | 6.41 | 1.296 | 4.137 | 8372.9 | 1.614 | 97.9 | 76.2 | 1434 | 22.82 | 5442.4 | 2709.7 | 2695.7 | 3944.4 | 1221.3 | 0.66994 | 5.434
2024-12-10 | 2:22 | Data | 0 | 33.257 | 31.799 | 169.35 | 7.64 | 160.099 | 2206.25 | 25.73 | 45.727 | 6.4 | 1.291 | 4.105 | 8359.34 | 1.499 | 97.9 | 76.1 | 1433 | 22.86 | 5433.6 | 2708.3 | 2676.1 | 3935.2 | 1221.3 | 0.67361 | 5.395
2024-12-10 | 2:22 | Data | 0 | 33.642 | 31.826 | 169.486 | 7.64 | 160.189 | 2206.25 | 25.73 | 45.727 | 6.4 | 1.286 | 4.092 | 8354.81 | 1.789 | 97.9 | 76.1 | 1434 | 22.86 | 5430.6 | 2712.6 | 2651.1 | 3920.5 | 1221.3 | 0.67436 | 5.378
2024-12-10 | 2:22 | Data | 0 | 33.412 | 31.623 | 169.26 | 7.64 | 160.099 | 2203.54 | 25.72 | 45.637 | 6.4 | 1.291 | 4.105 | 8350.29 | 1.614 | 97.9 | 76.1 | 1431 | 22.82 | 5427.7 | 2721.5 | 2661.3 | 3932.7 | 1221.3 | 0.67525 | 5.395
2024-12-10 | 2:22 | Data | 0 | 33.426 | 31.799 | 169.396 | 7.64 | 160.053 | 2203.54 | 25.73 | 45.637 | 6.4 | 1.284 | 4.124 | 8345.77 | 1.614 | 97.9 | 76.3 | 1432 | 22.86 | 5424.8 | 2694.4 | 2647 | 3907 | 1221.3 | 0.67268 | 5.409
2024-12-10 | 2:22 | Data | 0 | 33.412 | 31.799 | 169.396 | 7.64 | 160.144 | 2203.54 | 25.73 | 45.457 | 6.4 | 1.289 | 4.138 | 8345.77 | 1.728 | 97.9 | 76.3 | 1432 | 22.73 | 5424.8 | 2692.6 | 2660.4 | 3912.9 | 1221.3 | 0.67133 | 5.427
2024-12-10 | 2:22 | Data | 0 | 33.412 | 31.934 | 169.486 | 7.64 | 160.189 | 2203.54 | 25.72 | 45.727 | 6.41 | 1.288 | 4.122 | 8345.77 | 1.533 | 97.9 | 76.2 | 1432 | 22.82 | 5424.8 | 2711 | 2641.2 | 3912.6 | 1221.3 | 0.67664 | 5.41
2024-12-10 | 2:22 | Data | 0 | 33.412 | 31.799 | 169.35 | 7.64 | 160.099 | 2206.25 | 25.73 | 45.727 | 6.4 | 1.285 | 4.116 | 8345.77 | 1.83 | 97.9 | 76.2 | 1433 | 22.86 | 5424.8 | 2709.7 | 2636.7 | 3909.1 | 1221.4 | 0.67637 | 5.401
2024-12-10 | 2:22 | Data | 0 | 33.412 | 31.907 | 169.396 | 7.64 | 160.144 | 2206.25 | 25.72 | 45.727 | 6.4 | 1.286 | 4.147 | 8345.77 | 1.411 | 97.9 | 76.3 | 1434 | 22.86 | 5424.8 | 2691.2 | 2628.2 | 3890.1 | 1221.4 | 0.67515 | 5.433
2024-12-10 | 2:22 | Data | 0 | 33.588 | 32.021 | 169.486 | 7.64 | 160.099 | 2205.35 | 25.73 | 45.547 | 6.4 | 1.29 | 4.129 | 8332.2 | 1.614 | 97.9 | 76.2 | 1434 | 22.73 | 5415.9 | 2710.4 | 2659.5 | 3924.4 | 1221.4 | 0.67283 | 5.42
2024-12-10 | 2:22 | Data | 0 | 33.851 | 31.832 | 169.486 | 7.64 | 160.189 | 2205.35 | 25.73 | 45.637 | 6.4 | 1.282 | 4.116 | 8350.29 | 1.83 | 97.9 | 76.3 | 1434 | 22.86 | 5427.7 | 2708.6 | 2649.7 | 3916.6 | 1221.4 | 0.67419 | 5.397
2024-12-10 | 2:22 | Data | 0 | 33.621 | 31.826 | 169.441 | 7.64 | 160.189 | 2207.16 | 25.73 | 45.727 | 6.4 | 1.282 | 4.105 | 8752.77 | 1.641 | 97.9 | 76.2 | 1435 | 22.86 | 5689.3 | 2698.6 | 2643.8 | 3907 | 1221.4 | 0.67341 | 5.387
2024-12-10 | 2:22 | Data | 0 | 33.439 | 31.772 | 169.305 | 7.64 | 160.099 | 2208.06 | 25.73 | 45.637 | 6.4 | 1.286 | 4.115 | 8350.29 | 1.519 | 97.9 | 76.2 | 1435 | 22.82 | 5427.7 | 2714.2 | 2651.3 | 3923 | 1221.4 | 0.67555 | 5.401
2024-12-10 | 2:22 | Data | 0 | 33.527 | 31.839 | 169.441 | 7.64 | 160.099 | 2210.77 | 25.72 | 45.818 | 6.4 | 1.285 | 4.124 | 8345.77 | 1.742 | 97.9 | 76.2 | 1437 | 22.86 | 5424.8 | 2698.3 | 2639.1 | 3899.5 | 1221.4 | 0.6751 | 5.41
2024-12-10 | 2:22 | Data | 0 | 33.615 | 31.805 | 169.531 | 7.64 | 160.234 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.28 | 4.094 | 8345.77 | 1.425 | 97.9 | 76.2 | 1437 | 22.86 | 5424.8 | 2700.8 | 2659 | 3910.6 | 1221.4 | 0.67321 | 5.373
2024-12-10 | 2:22 | Data | 0 | 33.412 | 31.799 | 169.396 | 7.64 | 160.053 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.286 | 4.119 | 8350.29 | 1.614 | 97.9 | 76.2 | 1438 | 22.82 | 5427.7 | 2710 | 2624.5 | 3902.6 | 1221.4 | 0.67843 | 5.405
2024-12-10 | 2:22 | Data | 0 | 33.662 | 31.812 | 169.577 | 7.64 | 160.144 | 2209.87 | 25.73 | 45.727 | 6.4 | 1.299 | 4.143 | 8336.72 | 1.566 | 97.9 | 76.1 | 1437 | 22.86 | 5418.9 | 2716.8 | 2640.9 | 3916.3 | 1221.4 | 0.67864 | 5.442
2024-12-10 | 2:22 | Data | 0 | 33.466 | 31.974 | 169.441 | 7.64 | 160.144 | 2211.68 | 25.73 | 45.637 | 6.39 | 1.3 | 4.12 | 8350.29 | 1.62 | 97.9 | 76 | 1438 | 22.86 | 5427.7 | 2712.4 | 2628.1 | 3905.7 | 1221.4 | 0.67802 | 5.42
2024-12-10 | 2:23 | Data | 0 | 33.527 | 32.028 | 169.531 | 7.64 | 160.234 | 2213.49 | 25.73 | 45.727 | 6.4 | 1.296 | 4.129 | 8341.25 | 1.769 | 97.9 | 76.1 | 1439 | 22.91 | 5421.8 | 2705 | 2641.6 | 3912.5 | 1221.4 | 0.67431 | 5.425
2024-12-10 | 2:23 | Data | 0 | 33.419 | 31.799 | 169.396 | 7.64 | 160.053 | 2214.39 | 25.72 | 45.727 | 6.4 | 1.291 | 4.147 | 8350.29 | 1.499 | 97.9 | 76.3 | 1439 | 22.91 | 5427.7 | 2701.3 | 2640.1 | 3902.3 | 1221.4 | 0.67365 | 5.438
2024-12-10 | 2:23 | Data | 0 | 33.48 | 31.643 | 169.441 | 7.64 | 160.189 | 2213.49 | 25.73 | 45.547 | 6.4 | 1.3 | 4.146 | 8377.43 | 1.708 | 97.9 | 76.1 | 1439 | 22.73 | 5445.3 | 2706.3 | 2633.2 | 3904.9 | 1221.4 | 0.6755 | 5.447
2024-12-10 | 2:23 | Data | 0 | 33.419 | 31.799 | 169.531 | 7.64 | 160.189 | 2213.49 | 25.72 | 45.727 | 6.4 | 1.305 | 4.099 | 8377.43 | 1.614 | 97.9 | 75.9 | 1439 | 22.86 | 5445.3 | 2694.3 | 2628.5 | 3896.4 | 1221.4 | 0.67407 | 5.402
2024-12-10 | 2:23 | Data | 0 | 33.648 | 31.826 | 169.486 | 7.64 | 160.234 | 2214.39 | 25.74 | 45.637 | 6.4 | 1.296 | 4.099 | 8390.99 | 1.735 | 97.9 | 76 | 1439 | 22.82 | 5454.1 | 2702.8 | 2650.7 | 3915.2 | 1221.4 | 0.67412 | 5.398
2024-12-10 | 2:23 | Data | 0 | 33.419 | 31.799 | 169.396 | 7.64 | 160.144 | 2212.58 | 25.72 | 45.727 | 6.4 | 1.291 | 4.137 | 8368.38 | 1.506 | 97.9 | 76.2 | 1439 | 22.86 | 5439.4 | 2686.2 | 2646.5 | 3901 | 1221.4 | 0.67172 | 5.429
2024-12-10 | 2:23 | Data | 0 | 33.412 | 31.799 | 169.396 | 7.64 | 160.099 | 2213.49 | 25.73 | 45.727 | 6.4 | 1.288 | 4.124 | 8359.34 | 1.614 | 97.9 | 76.2 | 1439 | 22.86 | 5433.6 | 2697.7 | 2646.8 | 3909.9 | 1221.4 | 0.67306 | 5.413
2024-12-10 | 2:23 | Data | 0 | 33.669 | 31.812 | 169.441 | 7.64 | 160.189 | 2214.39 | 25.72 | 45.727 | 6.4 | 1.292 | 4.125 | 8359.34 | 1.614 | 97.9 | 76.1 | 1439 | 22.86 | 5433.6 | 2698.7 | 2659.6 | 3917.1 | 1221.4 | 0.67071 | 5.419
2024-12-10 | 2:23 | Data | 0 | 33.419 | 31.799 | 169.215 | 7.64 | 160.053 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.302 | 4.134 | 8359.34 | 1.614 | 97.9 | 76 | 1437 | 22.86 | 5433.6 | 2706.8 | 2684.5 | 3939.1 | 1221.4 | 0.66883 | 5.436
2024-12-10 | 2:23 | Data | 0 | 33.405 | 31.799 | 169.441 | 7.64 | 160.099 | 2211.68 | 25.73 | 45.727 | 6.4 | 1.283 | 4.119 | 8345.77 | 1.614 | 97.9 | 76.2 | 1437 | 22.82 | 5424.8 | 2715 | 2667.5 | 3930.8 | 1221.4 | 0.67238 | 5.402
2024-12-10 | 2:23 | Data | 0 | 33.385 | 31.805 | 169.486 | 7.64 | 160.053 | 2212.58 | 25.73 | 45.727 | 6.4 | 1.28 | 4.111 | 8300.55 | 1.803 | 97.9 | 76.3 | 1438 | 22.86 | 5395.4 | 2698.5 | 2653.7 | 3915.6 | 1221.4 | 0.67274 | 5.391
2024-12-10 | 2:23 | Data | 0 | 33.642 | 31.812 | 169.396 | 7.64 | 160.144 | 2213.49 | 25.73 | 45.637 | 6.4 | 1.286 | 4.102 | 8305.07 | 1.641 | 97.9 | 76.1 | 1439 | 22.82 | 5398.3 | 2705.3 | 2642.1 | 3914.5 | 1221.4 | 0.67215 | 5.388
2024-12-10 | 2:23 | Data | 0 | 33.412 | 32.116 | 169.667 | 7.64 | 160.099 | 2214.39 | 25.72 | 45.727 | 6.4 | 1.301 | 4.096 | 8318.64 | 1.614 | 97.9 | 75.9 | 1439 | 22.86 | 5407.1 | 2688.9 | 2633.3 | 3896.1 | 1221.4 | 0.67265 | 5.397
2024-12-10 | 2:23 | Data | 0 | 33.25 | 31.974 | 169.441 | 7.64 | 160.189 | 2215.29 | 25.73 | 45.727 | 6.4 | 1.3 | 4.099 | 8318.64 | 1.566 | 97.9 | 75.9 | 1440 | 22.86 | 5407.1 | 2692.1 | 2659.6 | 3913.6 | 1221.4 | 0.67227 | 5.399
2024-12-10 | 2:23 | Data | 0 | 33.696 | 32.028 | 169.396 | 7.64 | 160.234 | 2214.39 | 25.72 | 45.727 | 6.4 | 1.292 | 4.139 | 8345.77 | 1.452 | 97.9 | 76.2 | 1439 | 22.82 | 5424.8 | 2710.6 | 2654.4 | 3924.5 | 1221.4 | 0.6731 | 5.432
2024-12-10 | 2:23 | Data | 0 | 33.837 | 32.055 | 169.486 | 7.64 | 160.234 | 2216.2 | 25.73 | 45.727 | 6.4 | 1.293 | 4.127 | 8336.72 | 1.776 | 97.9 | 76.2 | 1441 | 22.82 | 5418.9 | 2692.3 | 2643.8 | 3900.2 | 1221.4 | 0.67259 | 5.42
2024-12-10 | 2:23 | Data | 0 | 33.412 | 31.799 | 169.396 | 7.64 | 160.008 | 2216.2 | 25.73 | 45.637 | 6.4 | 1.295 | 4.148 | 8323.16 | 1.614 | 97.9 | 76.2 | 1441 | 22.82 | 5410.1 | 2719.6 | 2642.9 | 3917.2 | 1221.4 | 0.67685 | 5.442
2024-12-10 | 2:24 | Data | 0 | 33.588 | 32.028 | 169.486 | 7.64 | 160.189 | 2216.2 | 25.73 | 45.727 | 6.4 | 1.292 | 4.14 | 8332.2 | 1.695 | 97.9 | 76.2 | 1441 | 22.82 | 5415.9 | 2704 | 2635.8 | 3903.4 | 1221.4 | 0.67498 | 5.432
2024-12-10 | 2:24 | Data | 0 | 33.331 | 31.826 | 169.35 | 7.64 | 160.189 | 2215.29 | 25.73 | 45.727 | 6.4 | 1.284 | 4.109 | 8332.2 | 1.344 | 97.9 | 76.2 | 1441 | 22.91 | 5415.9 | 2693.3 | 2650.3 | 3910.6 | 1221.4 | 0.67076 | 5.393
2024-12-10 | 2:24 | Data | 0 | 33.446 | 31.805 | 169.441 | 7.64 | 160.099 | 2217.1 | 25.72 | 45.457 | 6.4 | 1.277 | 4.107 | 8318.64 | 1.614 | 97.9 | 76.3 | 1441 | 22.73 | 5407.1 | 2724.7 | 2655.9 | 3931.4 | 1221.4 | 0.67156 | 5.385
2024-12-10 | 2:24 | Data | 0 | 33.81 | 31.812 | 169.531 | 7.64 | 160.189 | 2213.49 | 25.73 | 45.457 | 6.4 | 1.295 | 4.111 | 8332.2 | 1.519 | 97.9 | 76 | 1439 | 22.73 | 5415.9 | 2715.4 | 2646 | 3914.9 | 1221.4 | 0.67657 | 5.406
2024-12-10 | 2:24 | Data | 0 | 33.513 | 31.812 | 169.35 | 7.64 | 160.189 | 2213.49 | 25.73 | 45.457 | 6.41 | 1.292 | 4.091 | 8336.72 | 1.614 | 97.9 | 76 | 1439 | 22.73 | 5418.9 | 2717.9 | 2653.2 | 3922.9 | 1221.4 | 0.67346 | 5.383
2024-12-10 | 2:24 | Data | 0 | 33.534 | 31.913 | 169.531 | 7.64 | 160.144 | 2208.97 | 25.73 | 45.637 | 6.4 | 1.284 | 4.123 | 8345.77 | 1.789 | 97.9 | 76.2 | 1436 | 22.86 | 5424.8 | 2707.8 | 2655.1 | 3919 | 1221.4 | 0.67355 | 5.407
2024-12-10 | 2:24 | Data | 0 | 33.837 | 31.94 | 169.531 | 7.64 | 160.144 | 2213.49 | 25.73 | 45.727 | 6.4 | 1.28 | 4.125 | 8345.77 | 1.668 | 97.9 | 76.3 | 1439 | 22.82 | 5424.8 | 2721.7 | 2658.5 | 3931.2 | 1221.4 | 0.67532 | 5.406
2024-12-10 | 2:24 | Data | 0 | 33.196 | 31.799 | 169.486 | 7.64 | 160.099 | 2214.39 | 25.73 | 45.457 | 6.4 | 1.282 | 4.124 | 8305.07 | 1.391 | 97.9 | 76.3 | 1439 | 22.73 | 5398.3 | 2711.8 | 2646.2 | 3916.3 | 1221.4 | 0.67521 | 5.406
2024-12-10 | 2:24 | Data | 0 | 33.419 | 31.799 | 169.486 | 7.64 | 160.189 | 2213.49 | 25.72 | 45.457 | 6.4 | 1.283 | 4.138 | 8305.07 | 1.614 | 97.9 | 76.3 | 1439 | 22.77 | 5398.3 | 2696.4 | 2641.5 | 3904.9 | 1221.4 | 0.67286 | 5.42
2024-12-10 | 2:24 | Data | 0 | 33.412 | 32.001 | 169.441 | 7.64 | 160.144 | 2213.49 | 25.72 | 45.457 | 6.41 | 1.283 | 4.143 | 8300.55 | 1.553 | 97.9 | 76.4 | 1439 | 22.73 | 5395.4 | 2699.2 | 2650.5 | 3912.3 | 1221.4 | 0.67272 | 5.424
2024-12-10 | 2:24 | Data | 0 | 33.588 | 31.913 | 169.441 | 7.64 | 160.099 | 2216.2 | 25.73 | 45.457 | 6.4 | 1.293 | 4.127 | 8305.07 | 1.749 | 98 | 76.1 | 1441 | 22.68 | 5398.3 | 2706.7 | 2681.4 | 3934.4 | 1221.5 | 0.67317 | 5.42
2024-12-10 | 2:24 | Data | 0 | 33.669 | 31.913 | 169.486 | 7.64 | 160.189 | 2216.2 | 25.73 | 45.457 | 6.4 | 1.293 | 4.122 | 8354.81 | 1.62 | 97.9 | 76.1 | 1441 | 22.68 | 5430.6 | 2694.7 | 2670.7 | 3923.6 | 1221.5 | 0.66901 | 5.415
2024-12-10 | 2:24 | Data | 0 | 33.466 | 31.799 | 169.441 | 7.64 | 160.144 | 2218 | 25.74 | 45.366 | 6.4 | 1.293 | 4.126 | 8359.34 | 1.62 | 98 | 76.1 | 1442 | 22.73 | 5433.6 | 2709.9 | 2678.3 | 3933.3 | 1221.5 | 0.67094 | 5.42
2024-12-10 | 2:24 | Data | 0 | 33.81 | 32.082 | 169.577 | 7.64 | 160.234 | 2214.39 | 25.72 | 45.727 | 6.41 | 1.293 | 4.134 | 8350.29 | 1.614 | 97.9 | 76.2 | 1439 | 22.82 | 5427.7 | 2705.7 | 2665.4 | 3931 | 1221.5 | 0.6701 | 5.427
2024-12-10 | 2:24 | Data | 0 | 33.628 | 31.853 | 169.486 | 7.64 | 160.144 | 2220.72 | 25.72 | 45.457 | 6.4 | 1.276 | 4.138 | 8354.81 | 1.553 | 98 | 76.4 | 1443 | 22.73 | 5430.6 | 2718.4 | 2664.2 | 3929 | 1221.5 | 0.67436 | 5.414
2024-12-10 | 2:24 | Data | 0 | 33.628 | 31.907 | 169.441 | 7.64 | 160.189 | 2216.2 | 25.73 | 45.366 | 6.4 | 1.282 | 4.116 | 8354.81 | 1.62 | 97.9 | 76.3 | 1441 | 22.68 | 5430.6 | 2714.8 | 2676.1 | 3925.3 | 1221.5 | 0.67204 | 5.401
2024-12-10 | 2:24 | Data | 0 | 33.385 | 31.907 | 169.486 | 7.64 | 160.189 | 2218.91 | 25.73 | 45.547 | 6.4 | 1.291 | 4.124 | 8345.77 | 1.789 | 97.9 | 76.2 | 1442 | 22.77 | 5424.8 | 2690.8 | 2677.3 | 3927.1 | 1221.5 | 0.66827 | 5.416
2024-12-10 | 2:25 | Data | 0 | 33.527 | 31.799 | 169.441 | 7.64 | 160.144 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.291 | 4.125 | 8341.25 | 1.614 | 97.9 | 76.2 | 1438 | 22.82 | 5421.8 | 2725 | 2658.2 | 3932.1 | 1221.5 | 0.67574 | 5.416
2024-12-10 | 2:25 | Data | 0 | 33.412 | 31.826 | 169.396 | 7.64 | 160.144 | 2216.2 | 25.72 | 45.457 | 6.4 | 1.289 | 4.126 | 8336.72 | 1.681 | 97.9 | 76.2 | 1441 | 22.73 | 5418.9 | 2700.7 | 2665.7 | 3924.6 | 1221.5 | 0.6718 | 5.415
2024-12-10 | 2:25 | Data | 0 | 33.412 | 31.799 | 169.486 | 7.64 | 160.144 | 2216.2 | 25.72 | 45.637 | 6.4 | 1.284 | 4.108 | 8332.2 | 1.614 | 97.9 | 76.2 | 1441 | 22.86 | 5415.9 | 2697.1 | 2680.2 | 3929.5 | 1221.5 | 0.66657 | 5.392
2024-12-10 | 2:25 | Data | 0 | 34.087 | 31.805 | 169.577 | 7.64 | 160.234 | 2213.49 | 25.72 | 45.366 | 6.4 | 1.287 | 4.124 | 8336.72 | 1.499 | 97.9 | 76.2 | 1439 | 22.73 | 5418.9 | 2706.6 | 2659.1 | 3928.9 | 1221.5 | 0.66999 | 5.409
2024-12-10 | 2:25 | Data | 0 | 33.669 | 31.799 | 169.396 | 7.64 | 160.099 | 2213.49 | 25.73 | 45.457 | 6.4 | 1.289 | 4.163 | 8332.2 | 1.62 | 97.9 | 76.4 | 1439 | 22.73 | 5415.9 | 2712.2 | 2658.8 | 3926.2 | 1221.5 | 0.67219 | 5.451
2024-12-10 | 2:25 | Data | 0 | 33.392 | 32.001 | 169.486 | 7.64 | 160.189 | 2214.39 | 25.72 | 45.457 | 6.4 | 1.282 | 4.141 | 8314.11 | 1.519 | 98 | 76.4 | 1439 | 22.73 | 5404.2 | 2704.3 | 2644.4 | 3908 | 1221.5 | 0.67293 | 5.422
2024-12-10 | 2:25 | Data | 0 | 33.264 | 31.576 | 169.486 | 7.64 | 160.189 | 2213.49 | 25.72 | 45.457 | 6.4 | 1.284 | 4.121 | 8332.2 | 1.614 | 97.9 | 76.2 | 1439 | 22.73 | 5415.9 | 2698.1 | 2661.8 | 3918.9 | 1221.5 | 0.67169 | 5.405
2024-12-10 | 2:25 | Data | 0 | 33.412 | 31.684 | 169.441 | 7.64 | 160.144 | 2213.49 | 25.73 | 45.457 | 6.4 | 1.286 | 4.109 | 8332.2 | 1.728 | 97.9 | 76.2 | 1439 | 22.73 | 5415.9 | 2710.1 | 2668.4 | 3935.1 | 1221.5 | 0.67124 | 5.395
2024-12-10 | 2:25 | Data | 0 | 33.432 | 31.799 | 169.396 | 7.64 | 160.144 | 2213.49 | 25.72 | 45.547 | 6.4 | 1.278 | 4.101 | 8332.2 | 1.62 | 97.9 | 76.2 | 1439 | 22.73 | 5415.9 | 2688.7 | 2667.3 | 3915.4 | 1221.5 | 0.66945 | 5.379
2024-12-10 | 2:25 | Data | 0 | 33.412 | 31.826 | 169.396 | 7.64 | 160.144 | 2213.49 | 25.73 | 45.457 | 6.39 | 1.29 | 4.119 | 8341.25 | 1.587 | 97.9 | 76.2 | 1439 | 22.73 | 5421.8 | 2701.2 | 2642.7 | 3910.8 | 1221.5 | 0.67418 | 5.409
2024-12-10 | 2:25 | Data | 0 | 33.439 | 31.799 | 169.35 | 7.64 | 160.144 | 2210.77 | 25.73 | 45.366 | 6.4 | 1.296 | 4.136 | 8350.29 | 1.62 | 97.9 | 76.1 | 1438 | 22.73 | 5427.7 | 2711.8 | 2652.6 | 3922.5 | 1221.5 | 0.67425 | 5.43
2024-12-10 | 2:25 | Data | 0 | 33.412 | 31.799 | 169.396 | 7.64 | 160.099 | 2209.87 | 25.73 | 45.457 | 6.4 | 1.293 | 4.151 | 8345.77 | 1.641 | 97.9 | 76.2 | 1436 | 22.68 | 5424.8 | 2689.9 | 2642.4 | 3903.6 | 1221.5 | 0.67062 | 5.444
2024-12-10 | 2:25 | Data | 0 | 33.702 | 32.082 | 169.531 | 7.64 | 160.189 | 2206.25 | 25.73 | 45.637 | 6.4 | 1.288 | 4.138 | 8350.29 | 1.715 | 97.9 | 76.3 | 1434 | 22.86 | 5427.7 | 2725 | 2642.2 | 3921.1 | 1221.5 | 0.67807 | 5.427
2024-12-10 | 2:25 | Data | 0 | 33.709 | 31.812 | 169.531 | 7.64 | 160.189 | 2206.25 | 25.72 | 45.727 | 6.4 | 1.294 | 4.137 | 8345.77 | 1.87 | 97.9 | 76.2 | 1434 | 22.86 | 5424.8 | 2689.7 | 2646.6 | 3902.9 | 1221.5 | 0.67437 | 5.432
2024-12-10 | 2:25 | Data | 0 | 33.635 | 32.123 | 169.486 | 7.64 | 160.234 | 2205.35 | 25.73 | 45.727 | 6.4 | 1.29 | 4.153 | 8345.77 | 1.668 | 97.9 | 76.3 | 1433 | 22.91 | 5424.8 | 2691.1 | 2651.3 | 3911.3 | 1221.5 | 0.67084 | 5.443
2024-12-10 | 2:25 | Data | 0 | 33.635 | 32.028 | 169.531 | 7.64 | 160.189 | 2205.35 | 25.72 | 45.637 | 6.4 | 1.29 | 4.124 | 8363.86 | 1.614 | 97.9 | 76.2 | 1433 | 22.82 | 5436.5 | 2705.4 | 2671.6 | 3938.9 | 1221.5 | 0.66962 | 5.414
2024-12-10 | 2:25 | Data | 0 | 33.588 | 31.799 | 169.441 | 7.64 | 160.099 | 2206.25 | 25.73 | 45.727 | 6.4 | 1.299 | 4.125 | 8363.86 | 1.836 | 97.9 | 76.1 | 1433 | 22.86 | 5436.5 | 2709 | 2696.9 | 3948.8 | 1221.5 | 0.67178 | 5.424
2024-12-10 | 2:26 | Data | 0 | 33.669 | 32.028 | 169.577 | 7.64 | 160.234 | 2205.35 | 25.73 | 45.637 | 6.4 | 1.293 | 4.13 | 8363.86 | 1.506 | 97.9 | 76.2 | 1434 | 22.86 | 5436.5 | 2701.6 | 2689.8 | 3941.9 | 1221.5 | 0.66808 | 5.423
2024-12-10 | 2:26 | Data | 0 | 33.844 | 32.048 | 169.577 | 7.64 | 160.234 | 2205.35 | 25.73 | 45.727 | 6.4 | 1.294 | 4.114 | 8359.34 | 1.62 | 97.9 | 76.1 | 1433 | 22.91 | 5433.6 | 2729.6 | 2658.1 | 3934.7 | 1221.5 | 0.67615 | 5.408
2024-12-10 | 2:26 | Data | 0 | 33.392 | 31.799 | 169.396 | 7.64 | 160.234 | 2206.25 | 25.73 | 45.727 | 6.4 | 1.293 | 4.132 | 8155.84 | 1.728 | 97.9 | 76.2 | 1433 | 22.82 | 5301.3 | 2720.9 | 2655.3 | 3927.1 | 1221.5 | 0.67443 | 5.425
2024-12-10 | 2:26 | Data | 0 | 33.642 | 32.028 | 169.577 | 7.64 | 160.189 | 2206.25 | 25.73 | 45.637 | 6.4 | 1.292 | 4.141 | 8146.79 | 1.62 | 97.9 | 76.2 | 1434 | 22.86 | 5295.4 | 2709.6 | 2655.9 | 3923.6 | 1221.5 | 0.67373 | 5.433
2024-12-10 | 2:26 | Data | 0 | 33.75 | 32.028 | 169.486 | 7.64 | 160.189 | 2205.35 | 25.74 | 45.727 | 6.4 | 1.288 | 4.145 | 8164.88 | 1.627 | 97.9 | 76.3 | 1433 | 22.86 | 5307.2 | 2691.7 | 2629 | 3893 | 1221.5 | 0.67635 | 5.432
2024-12-10 | 2:26 | Data | 0 | 33.837 | 32.048 | 169.622 | 7.64 | 160.279 | 2205.35 | 25.73 | 45.637 | 6.4 | 1.282 | 4.128 | 8169.4 | 1.647 | 97.9 | 76.3 | 1433 | 22.82 | 5310.1 | 2702.7 | 2626.7 | 3898.5 | 1221.5 | 0.67474 | 5.411
2024-12-10 | 2:26 | Data | 0 | 33.635 | 32.143 | 169.577 | 7.64 | 160.234 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.288 | 4.152 | 8350.29 | 1.614 | 97.9 | 76.3 | 1437 | 22.86 | 5427.7 | 2690.7 | 2627.3 | 3890.5 | 1221.5 | 0.67461 | 5.439
2024-12-10 | 2:26 | Data | 0 | 33.588 | 32.015 | 169.622 | 7.64 | 160.189 | 2206.25 | 25.72 | 45.727 | 6.4 | 1.297 | 4.134 | 8345.77 | 1.789 | 97.9 | 76.1 | 1434 | 22.86 | 5424.8 | 2681.9 | 2652.9 | 3902.1 | 1221.5 | 0.66918 | 5.431
2024-12-10 | 2:26 | Data | 0 | 33.412 | 31.812 | 169.441 | 7.64 | 160.234 | 2206.25 | 25.72 | 45.727 | 6.4 | 1.301 | 4.137 | 8336.72 | 1.762 | 97.9 | 76.1 | 1434 | 22.86 | 5418.9 | 2692.4 | 2670.5 | 3921.4 | 1221.5 | 0.66908 | 5.439
2024-12-10 | 2:26 | Data | 0 | 33.419 | 32.001 | 169.531 | 7.64 | 160.189 | 2203.54 | 25.73 | 45.727 | 6.4 | 1.287 | 4.121 | 8336.72 | 1.668 | 97.9 | 76.2 | 1431 | 22.86 | 5418.9 | 2723.3 | 2668.1 | 3939.2 | 1221.5 | 0.67144 | 5.407
2024-12-10 | 2:26 | Data | 0 | 33.439 | 31.799 | 169.396 | 7.64 | 160.099 | 2203.54 | 25.73 | 45.637 | 6.4 | 1.292 | 4.14 | 8372.9 | 1.614 | 97.9 | 76.2 | 1432 | 22.86 | 5442.4 | 2690.9 | 2664.1 | 3916.6 | 1221.5 | 0.67037 | 5.433
2024-12-10 | 2:26 | Data | 0 | 33.554 | 31.92 | 169.577 | 7.64 | 160.234 | 2201.74 | 25.73 | 45.727 | 6.4 | 1.286 | 4.124 | 8386.47 | 1.62 | 97.9 | 76.2 | 1431 | 22.86 | 5451.2 | 2694.7 | 2672.2 | 3920.3 | 1221.5 | 0.66898 | 5.411
2024-12-10 | 2:26 | Data | 0 | 33.628 | 31.913 | 169.486 | 7.64 | 160.234 | 2199.93 | 25.73 | 45.727 | 6.4 | 1.28 | 4.092 | 8386.47 | 1.614 | 97.9 | 76.2 | 1430 | 22.86 | 5451.2 | 2699.4 | 2660.6 | 3922.6 | 1221.5 | 0.67112 | 5.372
2024-12-10 | 2:26 | Data | 0 | 33.527 | 31.799 | 169.441 | 7.64 | 160.144 | 2200.83 | 25.72 | 45.727 | 6.4 | 1.288 | 4.121 | 8372.9 | 1.83 | 97.9 | 76.2 | 1431 | 22.86 | 5442.4 | 2700.6 | 2643.1 | 3906.9 | 1221.5 | 0.67662 | 5.41
2024-12-10 | 2:26 | Data | 0 | 33.473 | 32.028 | 169.577 | 7.64 | 160.279 | 2203.54 | 25.72 | 45.818 | 6.4 | 1.287 | 4.146 | 8332.2 | 1.539 | 97.9 | 76.3 | 1431 | 22.91 | 5415.9 | 2714.9 | 2647 | 3917.8 | 1221.5 | 0.6733 | 5.432
2024-12-10 | 2:26 | Data | 0 | 33.5 | 31.805 | 169.622 | 7.64 | 160.234 | 2208.97 | 25.72 | 45.637 | 6.4 | 1.293 | 4.113 | 8332.2 | 1.418 | 97.9 | 76.1 | 1435 | 22.86 | 5415.9 | 2704 | 2626 | 3898.6 | 1221.6 | 0.6743 | 5.406
2024-12-10 | 2:26 | Data | 0 | 33.642 | 31.826 | 169.441 | 7.64 | 160.189 | 2208.06 | 25.73 | 45.727 | 6.4 | 1.295 | 4.136 | 8318.64 | 1.674 | 97.9 | 76.1 | 1435 | 22.86 | 5407.1 | 2706.6 | 2637.8 | 3904.9 | 1221.6 | 0.67549 | 5.43
2024-12-10 | 2:26 | Data | 0 | 33.419 | 31.974 | 169.531 | 7.63 | 160.189 | 2208.97 | 25.73 | 45.637 | 6.4 | 1.292 | 4.14 | 8314.11 | 1.438 | 97.9 | 76.2 | 1436 | 22.86 | 5404.2 | 2703.1 | 2635.9 | 3909.8 | 1221.6 | 0.67461 | 5.433
2024-12-10 | 2:27 | Data | 0 | 33.642 | 31.826 | 169.486 | 7.64 | 160.234 | 2208.06 | 25.72 | 45.186 | 6.4 | 1.293 | 4.096 | 8359.34 | 1.674 | 98 | 76 | 1435 | 22.59 | 5433.6 | 2705.6 | 2627.9 | 3903.9 | 1221.6 | 0.67818 | 5.39
2024-12-10 | 2:27 | Data | 0 | 33.581 | 32.021 | 169.531 | 7.64 | 160.234 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.29 | 4.091 | 8354.81 | 1.708 | 97.9 | 76 | 1438 | 22.86 | 5430.6 | 2696.1 | 2654.1 | 3912.2 | 1221.6 | 0.67263 | 5.382
2024-12-10 | 2:27 | Data | 0 | 33.628 | 32.028 | 169.531 | 7.64 | 160.189 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.292 | 4.115 | 8359.34 | 1.62 | 97.9 | 76.1 | 1437 | 22.86 | 5433.6 | 2689.9 | 2641.2 | 3898.9 | 1221.6 | 0.67355 | 5.407
2024-12-10 | 2:27 | Data | 0 | 33.412 | 32.021 | 169.441 | 7.64 | 160.144 | 2210.77 | 25.73 | 45.637 | 6.4 | 1.289 | 4.133 | 8359.34 | 1.438 | 97.9 | 76.2 | 1437 | 22.82 | 5433.6 | 2695.2 | 2636.2 | 3901.5 | 1221.6 | 0.67205 | 5.42
2024-12-10 | 2:27 | Data | 0 | 33.642 | 32.021 | 169.531 | 7.64 | 160.234 | 2210.77 | 25.73 | 45.637 | 6.4 | 1.3 | 4.119 | 8341.25 | 1.627 | 97.9 | 76 | 1438 | 22.82 | 5421.8 | 2700 | 2674.2 | 3934.6 | 1221.6 | 0.66885 | 5.417
2024-12-10 | 2:27 | Data | 0 | 33.203 | 31.799 | 169.486 | 7.64 | 160.234 | 2210.77 | 25.73 | 45.637 | 6.4 | 1.29 | 4.126 | 8336.72 | 1.56 | 97.9 | 76.2 | 1437 | 22.86 | 5418.9 | 2700.7 | 2662.1 | 3917.9 | 1221.6 | 0.6726 | 5.415
2024-12-10 | 2:27 | Data | 0 | 33.628 | 31.907 | 169.486 | 7.64 | 160.234 | 2208.97 | 25.73 | 45.637 | 6.41 | 1.286 | 4.145 | 8350.29 | 1.735 | 97.9 | 76.3 | 1435 | 22.82 | 5427.7 | 2685.2 | 2675.9 | 3915 | 1221.6 | 0.66982 | 5.431
2024-12-10 | 2:27 | Data | 0 | 33.628 | 31.853 | 169.486 | 7.64 | 160.099 | 2208.06 | 25.72 | 45.637 | 6.4 | 1.287 | 4.107 | 8368.38 | 1.728 | 97.9 | 76.1 | 1436 | 22.82 | 5439.4 | 2708.7 | 2647.2 | 3915.7 | 1221.6 | 0.67498 | 5.393
2024-12-10 | 2:27 | Data | 0 | 33.419 | 31.799 | 169.441 | 7.64 | 160.189 | 2203.54 | 25.73 | 45.637 | 6.4 | 1.287 | 4.129 | 8305.07 | 1.614 | 97.9 | 76.2 | 1432 | 22.82 | 5398.3 | 2697.1 | 2671.7 | 3921.2 | 1221.6 | 0.67089 | 5.416
2024-12-10 | 2:27 | Data | 0 | 33.81 | 32.082 | 169.577 | 7.64 | 160.279 | 2213.49 | 25.72 | 45.366 | 6.4 | 1.283 | 4.134 | 8314.11 | 1.593 | 97.9 | 76.3 | 1439 | 22.73 | 5404.2 | 2690.4 | 2658.6 | 3911.1 | 1221.6 | 0.67147 | 5.418
2024-12-10 | 2:27 | Data | 0 | 33.527 | 32.021 | 169.486 | 7.64 | 160.189 | 2208.06 | 25.72 | 45.366 | 6.4 | 1.279 | 4.124 | 8305.07 | 1.593 | 97.9 | 76.3 | 1435 | 22.73 | 5398.3 | 2699.3 | 2654.5 | 3917.1 | 1221.6 | 0.67262 | 5.403
2024-12-10 | 2:27 | Data | 0 | 33.81 | 32.028 | 169.622 | 7.64 | 160.234 | 2209.87 | 25.73 | 45.366 | 6.4 | 1.289 | 4.126 | 8318.64 | 1.722 | 97.9 | 76.2 | 1436 | 22.73 | 5407.1 | 2717.1 | 2668.5 | 3925.2 | 1221.6 | 0.67122 | 5.415
2024-12-10 | 2:27 | Data | 0 | 33.439 | 32.001 | 169.577 | 7.64 | 160.234 | 2208.06 | 25.73 | 45.457 | 6.4 | 1.301 | 4.145 | 8354.81 | 1.614 | 97.9 | 76.1 | 1436 | 22.73 | 5430.6 | 2713.4 | 2652.7 | 3923.3 | 1221.6 | 0.67369 | 5.446
2024-12-10 | 2:27 | Data | 0 | 33.642 | 31.913 | 169.486 | 7.64 | 160.279 | 2208.97 | 25.74 | 45.457 | 6.4 | 1.295 | 4.134 | 8345.77 | 1.452 | 97.9 | 76.1 | 1436 | 22.73 | 5424.8 | 2711.7 | 2661.6 | 3926.1 | 1221.6 | 0.67386 | 5.43
2024-12-10 | 2:27 | Data | 0 | 33.75 | 32.055 | 169.622 | 7.64 | 160.144 | 2211.68 | 25.73 | 45.457 | 6.4 | 1.285 | 4.131 | 8345.77 | 1.722 | 97.9 | 76.3 | 1437 | 22.73 | 5424.8 | 2697.1 | 2635.7 | 3897.2 | 1221.6 | 0.67432 | 5.415
2024-12-10 | 2:27 | Data | 0 | 33.628 | 32.143 | 169.577 | 7.64 | 160.279 | 2210.77 | 25.71 | 45.457 | 6.4 | 1.288 | 4.143 | 8345.77 | 1.722 | 97.9 | 76.3 | 1438 | 22.73 | 5424.8 | 2702.5 | 2637.2 | 3901.9 | 1221.6 | 0.67498 | 5.432
2024-12-10 | 2:27 | Data | 0 | 33.642 | 31.859 | 169.486 | 7.64 | 160.189 | 2211.68 | 25.73 | 45.457 | 6.4 | 1.291 | 4.119 | 8350.29 | 1.614 | 97.9 | 76.1 | 1437 | 22.77 | 5427.7 | 2714.4 | 2621.1 | 3898.3 | 1221.6 | 0.67935 | 5.41
2024-12-10 | 2:27 | Data | 0 | 33.426 | 32.001 | 169.531 | 7.64 | 160.234 | 2211.68 | 25.73 | 45.457 | 6.4 | 1.287 | 4.124 | 8350.29 | 1.411 | 97.9 | 76.2 | 1437 | 22.73 | 5427.7 | 2705.7 | 2625.5 | 3899 | 1221.6 | 0.67738 | 5.411
2024-12-10 | 2:28 | Data | 0 | 33.837 | 32.136 | 169.531 | 7.64 | 160.279 | 2210.77 | 25.73 | 45.908 | 6.4 | 1.291 | 4.112 | 8359.34 | 1.62 | 97.9 | 76.1 | 1437 | 22.95 | 5433.6 | 2705.7 | 2623.6 | 3896.6 | 1221.6 | 0.67704 | 5.402
2024-12-10 | 2:28 | Data | 0 | 33.581 | 31.913 | 169.531 | 7.64 | 160.144 | 2211.68 | 25.72 | 45.366 | 6.4 | 1.282 | 4.137 | 8345.77 | 1.83 | 97.9 | 76.3 | 1437 | 22.68 | 5424.8 | 2701.8 | 2636.1 | 3906.6 | 1221.6 | 0.67445 | 5.419
2024-12-10 | 2:28 | Data | 0 | 33.723 | 32.204 | 169.667 | 7.64 | 160.234 | 2210.77 | 25.72 | 45.366 | 6.4 | 1.291 | 4.137 | 8368.38 | 1.512 | 97.9 | 76.2 | 1437 | 22.73 | 5439.4 | 2693.2 | 2637.5 | 3898 | 1221.6 | 0.67306 | 5.429
2024-12-10 | 2:28 | Data | 0 | 33.615 | 32.015 | 169.667 | 7.64 | 160.189 | 2210.77 | 25.73 | 45.457 | 6.4 | 1.289 | 4.14 | 8354.81 | 1.661 | 97.9 | 76.3 | 1437 | 22.68 | 5430.6 | 2703.8 | 2640.1 | 3906.6 | 1221.6 | 0.67744 | 5.429
2024-12-10 | 2:28 | Data | 0 | 33.642 | 32.028 | 169.577 | 7.64 | 160.324 | 2210.77 | 25.72 | 45.457 | 6.4 | 1.286 | 4.119 | 8341.25 | 1.614 | 97.9 | 76.2 | 1437 | 22.77 | 5421.8 | 2714.2 | 2628.1 | 3903.8 | 1221.6 | 0.67967 | 5.406
2024-12-10 | 2:28 | Data | 0 | 33.628 | 31.974 | 169.396 | 7.64 | 160.144 | 2210.77 | 25.72 | 45.457 | 6.4 | 1.282 | 4.115 | 8354.81 | 1.661 | 97.9 | 76.3 | 1437 | 22.68 | 5430.6 | 2703.7 | 2623.6 | 3902.9 | 1221.6 | 0.67775 | 5.397
2024-12-10 | 2:28 | Data | 0 | 33.756 | 32.035 | 169.667 | 7.64 | 160.279 | 2210.77 | 25.73 | 45.457 | 6.4 | 1.285 | 4.134 | 8363.86 | 1.506 | 97.9 | 76.3 | 1437 | 22.73 | 5436.5 | 2718.5 | 2621.2 | 3901.6 | 1221.6 | 0.67983 | 5.42
2024-12-10 | 2:28 | Data | 0 | 33.473 | 31.974 | 169.577 | 7.64 | 160.279 | 2210.77 | 25.73 | 45.457 | 6.4 | 1.291 | 4.125 | 8354.81 | 1.681 | 97.9 | 76.2 | 1438 | 22.73 | 5430.6 | 2688.2 | 2633.4 | 3896.2 | 1221.6 | 0.67324 | 5.417
2024-12-10 | 2:28 | Data | 0 | 33.588 | 32.028 | 169.712 | 7.64 | 160.279 | 2216.2 | 25.73 | 45.457 | 6.4 | 1.289 | 4.12 | 8359.34 | 1.809 | 97.9 | 76.2 | 1441 | 22.73 | 5433.6 | 2692.7 | 2650.8 | 3907.3 | 1221.6 | 0.67244 | 5.409
2024-12-10 | 2:28 | Data | 0 | 33.844 | 32.055 | 169.622 | 7.64 | 160.324 | 2208.06 | 25.73 | 45.457 | 6.4 | 1.291 | 4.113 | 8359.34 | 1.816 | 97.9 | 76.1 | 1435 | 22.77 | 5433.6 | 2716.1 | 2633 | 3908.9 | 1221.6 | 0.67869 | 5.404
2024-12-10 | 2:28 | Data | 0 | 33.419 | 31.913 | 169.531 | 7.64 | 160.189 | 2214.39 | 25.72 | 45.457 | 6.4 | 1.287 | 4.155 | 8336.72 | 1.614 | 97.9 | 76.4 | 1439 | 22.73 | 5418.9 | 2702.8 | 2626.7 | 3896.7 | 1221.6 | 0.67768 | 5.442
2024-12-10 | 2:28 | Data | 0 | 33.642 | 32.028 | 169.577 | 7.64 | 160.144 | 2213.49 | 25.72 | 45.457 | 6.4 | 1.299 | 4.138 | 8332.2 | 1.614 | 97.9 | 76.1 | 1439 | 22.73 | 5415.9 | 2706.4 | 2608.9 | 3884.4 | 1221.6 | 0.6794 | 5.435
2024-12-10 | 2:28 | Data | 0 | 33.419 | 31.805 | 169.486 | 7.64 | 160.189 | 2211.68 | 25.73 | 45.366 | 6.4 | 1.302 | 4.133 | 8318.64 | 1.6 | 97.9 | 76 | 1437 | 22.73 | 5407.1 | 2699.2 | 2616.1 | 3887.7 | 1221.6 | 0.67745 | 5.436
2024-12-10 | 2:28 | Data | 0 | 33.729 | 31.853 | 169.531 | 7.64 | 160.144 | 2212.58 | 25.73 | 45.366 | 6.4 | 1.301 | 4.124 | 8314.11 | 1.695 | 97.9 | 76 | 1438 | 22.68 | 5404.2 | 2698 | 2620.7 | 3889.2 | 1221.6 | 0.67648 | 5.424
2024-12-10 | 2:28 | Data | 0 | 33.756 | 32.264 | 169.622 | 7.64 | 160.324 | 2210.77 | 25.73 | 45.457 | 6.4 | 1.282 | 4.134 | 8332.2 | 1.593 | 97.9 | 76.3 | 1437 | 22.68 | 5415.9 | 2693.6 | 2641.8 | 3894 | 1221.6 | 0.67227 | 5.416
2024-12-10 | 2:28 | Data | 0 | 33.439 | 32.021 | 169.486 | 7.64 | 160.234 | 2210.77 | 25.72 | 45.457 | 6.4 | 1.295 | 4.132 | 8332.2 | 1.593 | 97.9 | 76.1 | 1438 | 22.73 | 5415.9 | 2699 | 2635.8 | 3906.6 | 1221.6 | 0.67432 | 5.427
2024-12-10 | 2:28 | Data | 0 | 33.486 | 31.826 | 169.486 | 7.64 | 160.234 | 2214.39 | 25.72 | 45.457 | 6.4 | 1.29 | 4.124 | 8332.2 | 1.458 | 97.9 | 76.2 | 1439 | 22.73 | 5415.9 | 2700.4 | 2612 | 3884.2 | 1221.6 | 0.67684 | 5.413
2024-12-10 | 2:28 | Data | 0 | 33.642 | 32.028 | 169.577 | 7.64 | 160.234 | 2216.2 | 25.72 | 45.547 | 6.4 | 1.29 | 4.127 | 8336.72 | 1.614 | 97.9 | 76.2 | 1441 | 22.77 | 5418.9 | 2704 | 2655 | 3921.5 | 1221.6 | 0.67398 | 5.415
2024-12-10 | 2:29 | Data | 0 | 33.729 | 32.129 | 169.531 | 7.64 | 160.279 | 2216.2 | 25.73 | 45.457 | 6.41 | 1.285 | 4.142 | 8318.64 | 1.6 | 97.9 | 76.3 | 1441 | 22.73 | 5407.1 | 2689.4 | 2638.9 | 3894.9 | 1221.7 | 0.67486 | 5.428
2024-12-10 | 2:29 | Data | 0 | 33.615 | 32.237 | 169.577 | 7.64 | 160.234 | 2216.2 | 25.73 | 45.457 | 6.4 | 1.279 | 4.145 | 8314.11 | 1.809 | 97.9 | 76.4 | 1440 | 22.73 | 5404.2 | 2685.6 | 2643.9 | 3892.5 | 1221.7 | 0.67275 | 5.425
2024-12-10 | 2:29 | Data | 0 | 33.648 | 32.251 | 169.577 | 7.64 | 160.279 | 2214.39 | 25.73 | 45.366 | 6.4 | 1.279 | 4.14 | 8332.2 | 1.506 | 97.9 | 76.4 | 1439 | 22.73 | 5415.9 | 2712.5 | 2648.1 | 3916.8 | 1221.7 | 0.67391 | 5.419
2024-12-10 | 2:29 | Data | 0 | 33.453 | 31.913 | 169.622 | 7.64 | 160.324 | 2216.2 | 25.73 | 45.457 | 6.4 | 1.303 | 4.132 | 8314.11 | 1.614 | 97.9 | 76 | 1441 | 22.73 | 5404.2 | 2705.2 | 2640.5 | 3903.5 | 1221.7 | 0.67459 | 5.435
2024-12-10 | 2:29 | Data | 0 | 33.419 | 32.021 | 169.486 | 7.64 | 160.189 | 2213.49 | 25.73 | 45.457 | 6.4 | 1.291 | 4.143 | 8314.11 | 1.566 | 97.9 | 76.2 | 1439 | 22.68 | 5404.2 | 2701.2 | 2627.3 | 3895.6 | 1221.7 | 0.67595 | 5.433
2024-12-10 | 2:29 | Data | 0 | 33.756 | 32.055 | 169.531 | 7.64 | 160.324 | 2213.49 | 25.72 | 45.457 | 6.4 | 1.279 | 4.131 | 8336.72 | 1.566 | 97.9 | 76.4 | 1439 | 22.73 | 5418.9 | 2717.5 | 2634 | 3908.9 | 1221.7 | 0.67758 | 5.41
2024-12-10 | 2:29 | Data | 0 | 33.588 | 32.028 | 169.622 | 7.64 | 160.234 | 2211.68 | 25.73 | 45.457 | 6.4 | 1.297 | 4.121 | 8336.72 | 1.398 | 97.9 | 76 | 1437 | 22.73 | 5418.9 | 2711.7 | 2611.4 | 3889.1 | 1221.7 | 0.67952 | 5.42
2024-12-10 | 2:29 | Data | 0 | 33.804 | 32.028 | 169.531 | 7.64 | 160.189 | 2210.77 | 25.72 | 45.457 | 6.4 | 1.305 | 4.12 | 8350.29 | 1.83 | 97.9 | 75.9 | 1437 | 22.68 | 5427.7 | 2700.4 | 2636.9 | 3896.5 | 1221.7 | 0.67663 | 5.425
2024-12-10 | 2:29 | Data | 0 | 33.642 | 32.028 | 169.486 | 7.64 | 160.189 | 2215.29 | 25.73 | 45.727 | 6.41 | 1.301 | 4.129 | 8363.86 | 1.614 | 97.9 | 76.1 | 1440 | 22.86 | 5436.5 | 2707 | 2626.1 | 3898.6 | 1221.7 | 0.67651 | 5.429
2024-12-10 | 2:29 | Data | 0 | 33.338 | 32.028 | 169.486 | 7.64 | 160.189 | 2210.77 | 25.73 | 45.457 | 6.4 | 1.291 | 4.144 | 8345.77 | 1.56 | 97.9 | 76.3 | 1438 | 22.68 | 5424.8 | 2698 | 2638.4 | 3902.6 | 1221.7 | 0.67278 | 5.434
2024-12-10 | 2:29 | Data | 0 | 33.527 | 31.812 | 169.531 | 7.64 | 160.189 | 2211.68 | 25.73 | 45.366 | 6.4 | 1.291 | 4.132 | 8359.34 | 1.776 | 97.9 | 76.2 | 1438 | 22.73 | 5433.6 | 2712.6 | 2636.4 | 3908.2 | 1221.7 | 0.67547 | 5.423
2024-12-10 | 2:29 | Data | 0 | 33.642 | 32.197 | 169.577 | 7.64 | 160.279 | 2211.68 | 25.73 | 45.547 | 6.4 | 1.287 | 4.102 | 8363.86 | 1.634 | 97.9 | 76.1 | 1437 | 22.77 | 5436.5 | 2706.6 | 2642.5 | 3908.8 | 1221.7 | 0.67524 | 5.389
2024-12-10 | 2:29 | Data | 0 | 33.797 | 32.264 | 169.486 | 7.64 | 160.234 | 2210.77 | 25.73 | 45.457 | 6.4 | 1.284 | 4.084 | 8359.34 | 1.607 | 97.9 | 76.1 | 1438 | 22.73 | 5433.6 | 2680.4 | 2630.7 | 3884.9 | 1221.7 | 0.67225 | 5.368
2024-12-10 | 2:29 | Data | 0 | 33.419 | 32.001 | 169.577 | 7.64 | 160.279 | 2210.77 | 25.72 | 45.547 | 6.4 | 1.291 | 4.129 | 8350.29 | 1.614 | 97.9 | 76.2 | 1437 | 22.77 | 5427.7 | 2710.9 | 2622.5 | 3898 | 1221.7 | 0.67965 | 5.42
2024-12-10 | 2:29 | Data | 0 | 33.844 | 32.217 | 169.622 | 7.64 | 160.234 | 2211.68 | 25.72 | 45.366 | 6.4 | 1.285 | 4.113 | 8345.77 | 1.782 | 97.9 | 76.2 | 1438 | 22.73 | 5424.8 | 2699.9 | 2625 | 3894.4 | 1221.7 | 0.67653 | 5.398
2024-12-10 | 2:29 | Data | 0 | 33.675 | 32.042 | 169.667 | 7.64 | 160.279 | 2213.49 | 25.73 | 45.457 | 6.41 | 1.288 | 4.109 | 8363.86 | 1.506 | 97.9 | 76.1 | 1439 | 22.73 | 5436.5 | 2695 | 2629.7 | 3897.2 | 1221.7 | 0.67492 | 5.397
2024-12-10 | 2:29 | Data | 0 | 33.642 | 31.866 | 169.577 | 7.64 | 160.234 | 2213.49 | 25.73 | 45.457 | 6.4 | 1.291 | 4.122 | 8350.29 | 1.566 | 97.9 | 76.2 | 1439 | 22.73 | 5427.7 | 2706.5 | 2615.3 | 3888.9 | 1221.7 | 0.678 | 5.413
2024-12-10 | 2:30 | Data | 0 | 33.534 | 31.826 | 169.531 | 7.64 | 160.279 | 2213.49 | 25.73 | 45.366 | 6.4 | 1.299 | 4.142 | 8363.86 | 1.715 | 97.9 | 76.1 | 1439 | 22.73 | 5436.5 | 2691.3 | 2610.7 | 3878.1 | 1221.7 | 0.67771 | 5.44
2024-12-10 | 2:30 | Data | 0 | 33.655 | 32.028 | 169.577 | 7.64 | 160.279 | 2214.39 | 25.73 | 45.727 | 6.4 | 1.29 | 4.128 | 8359.34 | 1.614 | 97.9 | 76.2 | 1439 | 22.86 | 5433.6 | 2714.6 | 2620.3 | 3915.2 | 1221.7 | 0.6765 | 5.418
2024-12-10 | 2:30 | Data | 0 | 33.655 | 31.853 | 169.486 | 7.64 | 160.189 | 2211.68 | 25.73 | 45.457 | 6.4 | 1.287 | 4.12 | 8359.34 | 1.728 | 97.9 | 76.2 | 1438 | 22.73 | 5433.6 | 2690 | 2619.2 | 3878 | 1221.7 | 0.67757 | 5.406
2024-12-10 | 2:30 | Data | 0 | 33.642 | 32.204 | 169.577 | 7.64 | 160.324 | 2210.77 | 25.71 | 45.727 | 6.4 | 1.28 | 4.116 | 8300.55 | 1.438 | 97.9 | 76.3 | 1437 | 22.86 | 5395.4 | 2707.2 | 2610.9 | 3891.9 | 1221.7 | 0.67899 | 5.396
2024-12-10 | 2:30 | Data | 0 | 33.871 | 32.042 | 169.667 | 7.64 | 160.37 | 2210.77 | 25.73 | 45.727 | 6.4 | 1.282 | 4.143 | 8300.55 | 1.614 | 97.9 | 76.4 | 1438 | 22.86 | 5395.4 | 2696.6 | 2625.3 | 3892.7 | 1221.7 | 0.67459 | 5.426
2024-12-10 | 2:30 | Data | 0 | 33.696 | 32.028 | 169.622 | 7.64 | 160.324 | 2210.77 | 25.72 | 45.818 | 6.4 | 1.286 | 4.133 | 8300.55 | 1.452 | 97.9 | 76.3 | 1437 | 22.86 | 5395.4 | 2692.3 | 2611.1 | 3877.9 | 1221.7 | 0.67668 | 5.42
2024-12-10 | 2:30 | Data | 0 | 33.642 | 32.021 | 169.577 | 7.64 | 160.234 | 2208.06 | 25.72 | 45.727 | 6.4 | 1.297 | 4.139 | 8296.02 | 1.627 | 97.9 | 76.1 | 1435 | 22.82 | 5392.4 | 2704.7 | 2628.2 | 3901.1 | 1221.7 | 0.67632 | 5.436
2024-12-10 | 2:30 | Data | 0 | 33.615 | 32.021 | 169.622 | 7.64 | 160.234 | 2211.68 | 25.73 | 45.637 | 6.4 | 1.295 | 4.124 | 8314.11 | 1.62 | 97.9 | 76.1 | 1437 | 22.86 | 5404.2 | 2719.3 | 2627.3 | 3905.7 | 1221.7 | 0.67936 | 5.42
2024-12-10 | 2:30 | Data | 0 | 33.527 | 32.028 | 169.531 | 7.64 | 160.144 | 2216.2 | 25.72 | 45.727 | 6.4 | 1.301 | 4.127 | 8305.07 | 1.607 | 97.9 | 76 | 1440 | 22.86 | 5398.3 | 2708.5 | 2635.8 | 3908.1 | 1221.7 | 0.6743 | 5.429
2024-12-10 | 2:30 | Data | 0 | 33.642 | 32.136 | 169.622 | 7.64 | 160.279 | 2213.49 | 25.72 | 45.908 | 6.4 | 1.301 | 4.136 | 8305.07 | 1.593 | 97.9 | 76.1 | 1439 | 22.95 | 5398.3 | 2701.8 | 2616.6 | 3888.7 | 1221.7 | 0.67661 | 5.439
2024-12-10 | 2:30 | Data | 0 | 33.635 | 32.204 | 169.486 | 7.64 | 160.234 | 2214.39 | 25.72 | 45.727 | 6.4 | 1.293 | 4.124 | 8291.5 | 1.506 | 97.9 | 76.1 | 1439 | 22.86 | 5389.5 | 2718 | 2629.3 | 3909.4 | 1221.7 | 0.6789 | 5.418
2024-12-10 | 2:30 | Data | 0 | 33.527 | 32.021 | 169.531 | 7.64 | 160.279 | 2214.39 | 25.74 | 45.637 | 6.4 | 1.287 | 4.098 | 8286.98 | 1.776 | 97.9 | 76.1 | 1439 | 22.86 | 5386.5 | 2720.5 | 2630.5 | 3913.3 | 1221.7 | 0.67758 | 5.385
2024-12-10 | 2:30 | Data | 0 | 33.925 | 32.028 | 169.667 | 7.64 | 160.324 | 2213.49 | 25.73 | 45.547 | 6.4 | 1.293 | 4.132 | 8291.5 | 1.452 | 97.9 | 76.2 | 1439 | 22.82 | 5389.5 | 2699.2 | 2630 | 3899.3 | 1221.7 | 0.67535 | 5.424
2024-12-10 | 2:30 | Data | 0 | 33.642 | 32.028 | 169.531 | 7.64 | 160.279 | 2215.29 | 25.73 | 45.727 | 6.4 | 1.299 | 4.142 | 8296.02 | 1.614 | 97.9 | 76.1 | 1440 | 22.82 | 5392.4 | 2702.5 | 2643.4 | 3909.2 | 1221.7 | 0.67329 | 5.441
2024-12-10 | 2:30 | Data | 0 | 33.696 | 32.035 | 169.531 | 7.64 | 160.189 | 2214.39 | 25.73 | 45.637 | 6.4 | 1.289 | 4.15 | 8314.11 | 1.62 | 97.9 | 76.3 | 1439 | 22.82 | 5404.2 | 2687.2 | 2633.9 | 3892.2 | 1221.7 | 0.67334 | 5.438
2024-12-10 | 2:30 | Data | 0 | 33.642 | 32.028 | 169.577 | 7.63 | 160.279 | 2214.39 | 25.71 | 45.998 | 6.4 | 1.289 | 4.131 | 8305.07 | 1.614 | 97.9 | 76.2 | 1439 | 22.95 | 5398.3 | 2683.3 | 2610.8 | 3873.1 | 1221.7 | 0.67625 | 5.42
2024-12-10 | 2:30 | Data | 0 | 33.648 | 32.028 | 169.577 | 7.64 | 160.324 | 2214.39 | 25.72 | 45.727 | 6.4 | 1.289 | 4.164 | 8300.55 | 1.614 | 97.9 | 76.4 | 1439 | 22.86 | 5395.4 | 2695.8 | 2616.6 | 3888 | 1221.7 | 0.67623 | 5.452
2024-12-10 | 2:30 | Data | 0 | 33.561 | 32.15 | 169.667 | 7.64 | 160.279 | 2213.49 | 25.72 | 45.727 | 6.4 | 1.291 | 4.145 | 8305.07 | 1.593 | 97.9 | 76.2 | 1439 | 22.86 | 5398.3 | 2697.1 | 2618.9 | 3889.2 | 1221.7 | 0.67622 | 5.437
2024-12-10 | 2:31 | Data | 0 | 34.094 | 32.062 | 169.712 | 7.64 | 160.324 | 2213.49 | 25.72 | 45.727 | 6.4 | 1.293 | 4.109 | 8309.59 | 1.755 | 97.9 | 76.1 | 1439 | 22.86 | 5401.2 | 2681.1 | 2636.6 | 3894.6 | 1221.7 | 0.67096 | 5.402
2024-12-10 | 2:31 | Data | 0 | 33.709 | 32.035 | 169.577 | 7.64 | 160.324 | 2213.49 | 25.73 | 45.727 | 6.4 | 1.291 | 4.097 | 8318.64 | 1.634 | 97.9 | 76 | 1439 | 22.86 | 5407.1 | 2705.8 | 2626 | 3899.2 | 1221.7 | 0.67679 | 5.387
2024-12-10 | 2:31 | Data | 0 | 33.81 | 32.116 | 169.622 | 7.64 | 160.234 | 2213.49 | 25.71 | 45.727 | 6.4 | 1.291 | 4.123 | 8305.07 | 1.695 | 97.9 | 76.1 | 1439 | 22.86 | 5398.3 | 1610 | 2035.9 | 2616.9 | 1221.7 | 0.61072 | 5.415
2024-12-10 | 2:31 | Data | 0 | 33.783 | 32.028 | 169.712 | 7.64 | 160.324 | 2214.39 | 25.72 | 45.818 | 6.4 | 1.299 | 4.133 | 8305.07 | 1.607 | 97.9 | 76.1 | 1439 | 22.86 | 5398.3 | 1626.8 | 2032.5 | 2615.5 | 1221.7 | 0.61826 | 5.431
2024-12-10 | 2:31 | Data | 0 | 33.426 | 32.197 | 169.667 | 7.64 | 160.324 | 2208.97 | 25.71 | 45.727 | 6.4 | 1.291 | 4.123 | 8305.07 | 1.546 | 97.9 | 76.1 | 1435 | 22.86 | 5398.3 | 1633.6 | 2025.7 | 2617.3 | 1221.7 | 0.62104 | 5.414
2024-12-10 | 2:31 | Data | 0 | 33.459 | 32.028 | 169.667 | 7.64 | 160.324 | 2213.49 | 25.73 | 45.727 | 6.4 | 1.292 | 4.142 | 8305.07 | 1.391 | 97.9 | 76.2 | 1439 | 22.86 | 5398.3 | 1626.7 | 2041.6 | 2624.6 | 1221.7 | 0.61687 | 5.433
2024-12-10 | 2:31 | Data | 0 | 33.871 | 32.251 | 169.758 | 7.64 | 160.415 | 2214.39 | 25.73 | 45.637 | 6.4 | 1.291 | 4.142 | 8305.07 | 1.715 | 97.9 | 76.2 | 1439 | 22.82 | 5398.3 | 1609.5 | 2033.3 | 2607.3 | 1221.7 | 0.61498 | 5.434
2024-12-10 | 2:31 | Data | 0 | 33.54 | 32.028 | 169.622 | 7.64 | 160.324 | 2213.49 | 25.71 | 45.727 | 6.4 | 1.296 | 4.128 | 8296.02 | 1.398 | 97.9 | 76.1 | 1438 | 22.86 | 5392.4 | 1623.7 | 2031.7 | 2608.7 | 1221.8 | 0.61903 | 5.424
2024-12-10 | 2:31 | Data | 0 | 33.642 | 32.028 | 169.531 | 7.64 | 160.279 | 2213.49 | 25.71 | 45.727 | 6.4 | 1.291 | 4.09 | 8300.55 | 1.614 | 97.9 | 76 | 1439 | 22.86 | 5395.4 | 1622.2 | 2026.6 | 2611.3 | 1221.8 | 0.61844 | 5.381
2024-12-10 | 2:31 | Data | 0 | 33.527 | 32.197 | 169.531 | 7.64 | 160.234 | 2120.39 | 25.7 | 45.727 | 6.4 | 1.29 | 4.095 | 8309.59 | 1.641 | 97.8 | 76 | 1376 | 22.86 | 5401.2 | 1621.4 | 2037.4 | 2618.5 | 1221.8 | 0.61829 | 5.384
2024-12-10 | 2:31 | Data | 0 | 33.642 | 32.028 | 169.577 | 7.64 | 160.279 | 2201.74 | 25.72 | 45.727 | 6.4 | 1.287 | 4.125 | 8336.72 | 1.614 | 97.9 | 76.2 | 1433 | 22.86 | 5418.9 | 1621.8 | 2036.3 | 2618.1 | 1221.8 | 0.61723 | 5.413
2024-12-10 | 2:31 | Data | 0 | 33.588 | 32.231 | 169.622 | 7.64 | 160.324 | 2213.49 | 25.71 | 45.727 | 6.4 | 1.288 | 4.145 | 8332.2 | 1.539 | 97.9 | 76.3 | 1439 | 22.86 | 5415.9 | 1625.7 | 2025.6 | 2611.7 | 1221.8 | 0.61968 | 5.433
2024-12-10 | 2:31 | Data | 0 | 33.986 | 31.88 | 169.531 | 7.64 | 160.324 | 2211.68 | 25.71 | 45.727 | 6.4 | 1.285 | 4.128 | 8341.25 | 1.836 | 97.9 | 76.3 | 1438 | 22.86 | 5421.8 | 1613.3 | 2035.5 | 2612.8 | 1221.8 | 0.61526 | 5.412
2024-12-10 | 2:31 | Data | 0 | 33.864 | 32.055 | 169.667 | 7.64 | 160.37 | 2210.77 | 25.71 | 45.727 | 6.4 | 1.285 | 4.138 | 8323.16 | 1.668 | 97.9 | 76.3 | 1438 | 22.86 | 5410.1 | 1616.3 | 2040.3 | 2616.7 | 1221.8 | 0.61587 | 5.424
2024-12-10 | 2:31 | Data | 0 | 33.642 | 32.028 | 169.531 | 7.64 | 160.234 | 2208.06 | 25.71 | 45.727 | 6.4 | 1.288 | 4.12 | 8318.64 | 1.728 | 97.9 | 76.2 | 1435 | 22.86 | 5407.1 | 1620.6 | 2032.7 | 2619.5 | 1221.8 | 0.61884 | 5.408
2024-12-10 | 2:31 | Data | 0 | 33.871 | 32.089 | 169.667 | 7.64 | 160.324 | 2210.77 | 25.71 | 45.637 | 6.4 | 1.288 | 4.128 | 8318.64 | 1.607 | 97.9 | 76.2 | 1438 | 22.86 | 5407.1 | 1596.2 | 2032.5 | 2599.7 | 1221.8 | 0.61117 | 5.416
2024-12-10 | 2:31 | Data | 0 | 33.527 | 31.805 | 169.577 | 7.64 | 160.279 | 2211.68 | 25.71 | 45.998 | 6.4 | 1.291 | 4.143 | 8309.59 | 1.627 | 97.9 | 76.2 | 1437 | 23 | 5401.2 | 1625.1 | 2047.7 | 2628.5 | 1221.8 | 0.6196 | 5.434
2024-12-10 | 2:31 | Data | 0 | 33.959 | 32.082 | 169.577 | 7.64 | 160.324 | 2210.77 | 25.71 | 45.727 | 6.4 | 1.295 | 4.108 | 8300.55 | 1.749 | 97.9 | 76 | 1438 | 22.82 | 5395.4 | 1632.6 | 2045.6 | 2630.8 | 1221.8 | 0.61838 | 5.403
2024-12-10 | 2:32 | Data | 0 | 33.696 | 32.251 | 169.622 | 7.64 | 160.234 | 2211.68 | 25.71 | 45.637 | 6.4 | 1.288 | 4.131 | 8268.89 | 1.587 | 97.9 | 76.2 | 1437 | 22.82 | 5374.8 | 1625.4 | 2049.7 | 2629.2 | 1221.8 | 0.61593 | 5.42
2024-12-10 | 2:32 | Data | 0 | 33.709 | 31.839 | 169.667 | 7.64 | 160.37 | 2211.68 | 25.71 | 45.727 | 6.4 | 1.286 | 4.134 | 8268.89 | 1.607 | 97.9 | 76.3 | 1438 | 22.86 | 5374.8 | 1632.4 | 2036.6 | 2623.4 | 1221.8 | 0.61992 | 5.42
2024-12-10 | 2:32 | Data | 0 | 33.669 | 32.251 | 169.622 | 7.64 | 160.37 | 2210.77 | 25.71 | 45.637 | 6.4 | 1.288 | 4.136 | 8273.41 | 1.553 | 97.9 | 76.2 | 1437 | 22.86 | 5377.7 | 1632.2 | 2048.4 | 2632.3 | 1221.8 | 0.61881 | 5.425
2024-12-10 | 2:32 | Data | 0 | 33.756 | 31.812 | 169.577 | 7.64 | 160.37 | 2210.77 | 25.71 | 45.637 | 6.4 | 1.288 | 4.145 | 8268.89 | 1.587 | 97.9 | 76.3 | 1437 | 22.86 | 5374.8 | 1635.8 | 2067.2 | 2650 | 1221.8 | 0.61421 | 5.433
2024-12-10 | 2:32 | Data | 0 | 33.642 | 32.028 | 169.577 | 7.64 | 160.234 | 2210.77 | 25.72 | 45.727 | 6.4 | 1.291 | 4.138 | 8291.5 | 1.62 | 97.9 | 76.2 | 1437 | 22.86 | 5389.5 | 1613.7 | 2056 | 2627.2 | 1221.8 | 0.61442 | 5.428
2024-12-10 | 2:32 | Data | 0 | 33.642 | 32.075 | 169.667 | 7.63 | 160.234 | 2211.68 | 25.71 | 45.637 | 6.4 | 1.301 | 4.122 | 8300.55 | 1.418 | 97.9 | 76 | 1438 | 22.82 | 5395.4 | 1629.5 | 2060.3 | 2639.5 | 1221.8 | 0.61495 | 5.422
2024-12-10 | 2:32 | Data | 0 | 33.75 | 32.116 | 169.622 | 7.64 | 160.234 | 2210.77 | 25.71 | 45.727 | 6.4 | 1.295 | 4.125 | 8300.55 | 1.566 | 97.9 | 76.1 | 1437 | 22.86 | 5395.4 | 1634.3 | 2047.6 | 2632.9 | 1221.8 | 0.61871 | 5.42
2024-12-10 | 2:32 | Data | 0 | 33.642 | 32.028 | 169.486 | 7.64 | 160.234 | 2211.68 | 25.71 | 45.637 | 6.4 | 1.289 | 4.137 | 8300.55 | 1.614 | 97.9 | 76.2 | 1437 | 22.86 | 5395.4 | 1617.7 | 2059.7 | 2632.6 | 1221.8 | 0.61216 | 5.426
2024-12-10 | 2:32 | Data | 0 | 33.642 | 32.028 | 169.486 | 7.64 | 160.234 | 2211.68 | 25.7 | 45.727 | 6.4 | 1.293 | 4.143 | 8318.64 | 1.411 | 97.9 | 76.2 | 1438 | 22.86 | 5407.1 | 1613.9 | 2079.1 | 2645.4 | 1221.8 | 0.6079 | 5.436
2024-12-10 | 2:32 | Data | 0 | 33.547 | 31.805 | 169.577 | 7.64 | 160.324 | 2210.77 | 25.72 | 45.637 | 6.4 | 1.293 | 4.098 | 8332.2 | 1.607 | 97.9 | 76 | 1438 | 22.86 | 5415.9 | 1633 | 2078.7 | 2658.8 | 1221.8 | 0.61141 | 5.392
2024-12-10 | 2:32 | Data | 0 | 33.756 | 31.947 | 169.577 | 7.64 | 160.415 | 2210.77 | 25.71 | 45.727 | 6.4 | 1.287 | 4.119 | 8336.72 | 1.566 | 97.9 | 76.2 | 1437 | 22.86 | 5418.9 | 1616.4 | 2088.1 | 2654.4 | 1221.8 | 0.60953 | 5.407
2024-12-10 | 2:32 | Data | 0 | 33.81 | 32.264 | 169.622 | 7.64 | 160.324 | 2210.77 | 25.71 | 45.727 | 6.4 | 1.291 | 4.124 | 8336.72 | 1.782 | 97.9 | 76.1 | 1437 | 22.86 | 5418.9 | 1637.7 | 2090.8 | 2668.3 | 1221.8 | 0.6126 | 5.415
2024-12-10 | 2:32 | Data | 0 | 33.858 | 32.251 | 169.577 | 7.64 | 160.279 | 2211.68 | 25.71 | 45.727 | 6.4 | 1.289 | 4.124 | 8336.72 | 1.715 | 97.9 | 76.2 | 1437 | 22.86 | 5418.9 | 1615.6 | 2059 | 2631.4 | 1221.8 | 0.61134 | 5.412
2024-12-10 | 2:32 | Data | 0 | 33.419 | 32.339 | 169.667 | 7.64 | 160.279 | 2207.16 | 25.71 | 45.547 | 6.4 | 1.282 | 4.129 | 8314.11 | 1.438 | 97.9 | 76.3 | 1435 | 22.73 | 5404.2 | 1611.1 | 2047.1 | 2618.8 | 1221.8 | 0.61237 | 5.411
2024-12-10 | 2:32 | Data | 0 | 33.412 | 32.339 | 169.577 | 7.64 | 160.324 | 2208.06 | 25.72 | 45.727 | 6.4 | 1.282 | 4.11 | 8336.72 | 1.62 | 97.9 | 76.2 | 1435 | 22.86 | 5418.9 | 1625.7 | 2059.6 | 2637.2 | 1221.8 | 0.61351 | 5.391
2024-12-10 | 2:32 | Data | 0 | 33.588 | 32.19 | 169.622 | 7.64 | 160.234 | 2210.77 | 25.71 | 45.727 | 6.4 | 1.278 | 4.133 | 8336.72 | 1.641 | 97.9 | 76.4 | 1437 | 22.86 | 5418.9 | 1624.1 | 2047.6 | 2626.5 | 1221.8 | 0.6167 | 5.411
2024-12-10 | 2:32 | Data | 0 | 33.527 | 32.028 | 169.577 | 7.63 | 160.279 | 2208.06 | 25.71 | 45.818 | 6.4 | 1.287 | 4.12 | 8318.64 | 1.708 | 97.9 | 76.2 | 1435 | 22.86 | 5407.1 | 1632.9 | 2061.6 | 2645.6 | 1221.8 | 0.61562 | 5.407
2024-12-10 | 2:32 | Data | 0 | 33.696 | 32.035 | 169.622 | 7.64 | 160.37 | 2208.97 | 25.71 | 45.637 | 6.4 | 1.292 | 4.123 | 8314.11 | 1.614 | 97.9 | 76.1 | 1435 | 22.82 | 5404.2 | 1623.5 | 2039.8 | 2621.1 | 1221.8 | 0.61762 | 5.416
2024-12-10 | 2:33 | Data | 0 | 33.669 | 32.028 | 169.486 | 7.64 | 160.279 | 2208.97 | 25.71 | 45.818 | 6.41 | 1.295 | 4.139 | 8318.64 | 1.614 | 97.9 | 76.2 | 1436 | 22.86 | 5407.1 | 1636.4 | 2034.3 | 2625.9 | 1221.8 | 0.62035 | 5.434
2024-12-10 | 2:33 | Data | 0 | 33.412 | 31.805 | 169.486 | 7.64 | 160.279 | 2208.97 | 25.72 | 45.727 | 6.4 | 1.3 | 4.172 | 8305.07 | 1.58 | 97.9 | 76.2 | 1435 | 22.86 | 5398.3 | 1624.9 | 2044.8 | 2623.7 | 1221.8 | 0.61682 | 5.472
2024-12-10 | 2:33 | Data | 0 | 33.804 | 32.055 | 169.577 | 7.64 | 160.279 | 2205.35 | 25.71 | 45.457 | 6.4 | 1.295 | 4.137 | 8332.2 | 1.587 | 97.9 | 76.2 | 1433 | 22.73 | 5415.9 | 1616.9 | 2037.5 | 2615.9 | 1221.8 | 0.61544 | 5.433
2024-12-10 | 2:33 | Data | 0 | 33.642 | 31.799 | 169.577 | 7.64 | 160.234 | 2213.49 | 25.71 | 45.727 | 6.4 | 1.295 | 4.132 | 8332.2 | 1.674 | 97.9 | 76.1 | 1439 | 22.86 | 5415.9 | 1619.6 | 2029.2 | 2609.2 | 1221.8 | 0.61956 | 5.427
2024-12-10 | 2:33 | Data | 0 | 33.25 | 31.799 | 169.441 | 7.64 | 160.189 | 2208.06 | 25.71 | 45.727 | 6.4 | 1.28 | 4.122 | 8332.2 | 1.398 | 97.9 | 76.3 | 1436 | 22.82 | 5415.9 | 1637.1 | 2026.8 | 2619.8 | 1221.8 | 0.62274 | 5.401
2024-12-10 | 2:33 | Data | 0 | 33.466 | 31.799 | 169.577 | 7.64 | 160.189 | 2201.74 | 25.72 | 45.457 | 6.4 | 1.289 | 4.141 | 8332.2 | 1.62 | 97.9 | 76.3 | 1432 | 22.73 | 5415.9 | 1623.8 | 2031.1 | 2613.2 | 1221.8 | 0.61964 | 5.43
2024-12-10 | 2:33 | Data | 0 | 33.426 | 32.021 | 169.531 | 7.63 | 160.189 | 2203.54 | 25.71 | 45.818 | 6.4 | 1.293 | 4.124 | 8345.77 | 1.519 | 97.9 | 76.1 | 1432 | 22.86 | 5424.8 | 1635.3 | 2040.2 | 2630.2 | 1221.8 | 0.61967 | 5.418
2024-12-10 | 2:33 | Data | 0 | 33.723 | 31.913 | 169.486 | 7.64 | 160.279 | 2189.08 | 25.7 | 45.457 | 6.4 | 1.289 | 4.116 | 8345.77 | 1.776 | 97.9 | 76.1 | 1423 | 22.73 | 5424.8 | 1616.2 | 2039.8 | 2615.1 | 1221.8 | 0.61778 | 5.406
2024-12-10 | 2:33 | Data | 0 | 34.013 | 31.886 | 169.577 | 7.64 | 160.324 | 2199.93 | 25.71 | 45.457 | 6.4 | 1.284 | 4.112 | 8372.9 | 1.938 | 97.9 | 76.2 | 1430 | 22.73 | 5442.4 | 1629.7 | 2029 | 2618.1 | 1221.8 | 0.61996 | 5.397
2024-12-10 | 2:33 | Data | 0 | 33.851 | 32.035 | 169.531 | 7.64 | 160.279 | 2201.74 | 25.71 | 45.457 | 6.4 | 1.282 | 4.121 | 8350.29 | 1.708 | 97.9 | 76.3 | 1431 | 22.73 | 5427.7 | 1625.6 | 2040.4 | 2622.8 | 1221.8 | 0.61721 | 5.404
2024-12-10 | 2:33 | Data | 0 | 33.473 | 31.812 | 169.577 | 7.64 | 160.279 | 2201.74 | 25.71 | 45.457 | 6.4 | 1.296 | 4.094 | 8314.11 | 1.58 | 97.9 | 76 | 1431 | 22.73 | 5404.2 | 1634.9 | 2047.5 | 2633.6 | 1221.8 | 0.61864 | 5.391
2024-12-10 | 2:33 | Data | 0 | 33.628 | 31.853 | 169.486 | 7.64 | 160.189 | 2201.74 | 25.71 | 45.457 | 6.4 | 1.292 | 4.128 | 8318.64 | 1.789 | 97.9 | 76.2 | 1432 | 22.68 | 5407.1 | 1628.3 | 2017.3 | 2604.2 | 1221.8 | 0.62221 | 5.42
2024-12-10 | 2:33 | Data | 0 | 33.756 | 31.913 | 169.622 | 7.64 | 160.279 | 2203.54 | 25.7 | 45.457 | 6.41 | 1.284 | 4.131 | 8314.11 | 1.458 | 97.9 | 76.3 | 1432 | 22.77 | 5404.2 | 1620.6 | 2029.3 | 2612.4 | 1221.8 | 0.6174 | 5.415
2024-12-10 | 2:33 | Data | 0 | 33.412 | 32.19 | 169.486 | 7.64 | 160.189 | 2203.54 | 25.71 | 45.457 | 6.4 | 1.289 | 4.121 | 8318.64 | 1.641 | 97.9 | 76.2 | 1432 | 22.73 | 5407.1 | 1619.6 | 2052.3 | 2625.3 | 1221.8 | 0.6131 | 5.41
2024-12-10 | 2:33 | Data | 0 | 33.959 | 32.143 | 169.531 | 7.64 | 160.234 | 2203.54 | 25.7 | 45.457 | 6.4 | 1.289 | 4.122 | 8318.64 | 1.695 | 97.9 | 76.2 | 1432 | 22.73 | 5407.1 | 1629.4 | 2040.7 | 2624.6 | 1221.8 | 0.61564 | 5.411
2024-12-10 | 2:33 | Data | 0 | 33.412 | 31.886 | 169.441 | 7.64 | 160.144 | 2201.74 | 25.71 | 45.547 | 6.4 | 1.29 | 4.136 | 8336.72 | 1.438 | 97.9 | 76.2 | 1431 | 22.73 | 5418.9 | 1615.1 | 2017.6 | 2598.5 | 1221.8 | 0.618 | 5.426
2024-12-10 | 2:33 | Data | 0 | 33.615 | 31.819 | 169.486 | 7.64 | 160.189 | 2204.45 | 25.71 | 45.457 | 6.4 | 1.288 | 4.137 | 8336.72 | 1.701 | 97.9 | 76.3 | 1433 | 22.73 | 5418.9 | 1626.6 | 2031 | 2615.9 | 1221.8 | 0.61787 | 5.425
2024-12-10 | 2:34 | Data | 0 | 33.669 | 32.028 | 169.622 | 7.64 | 160.324 | 2206.25 | 25.71 | 45.457 | 6.4 | 1.293 | 4.105 | 8332.2 | 1.62 | 97.9 | 76 | 1433 | 22.73 | 5415.9 | 1615.5 | 2024.7 | 2601.8 | 1221.8 | 0.61796 | 5.398
2024-12-10 | 2:34 | Data | 0 | 33.439 | 31.799 | 169.441 | 7.63 | 160.189 | 2207.16 | 25.71 | 45.366 | 6.4 | 1.282 | 4.126 | 8359.34 | 1.62 | 97.9 | 76.3 | 1435 | 22.73 | 5433.6 | 1632 | 2041.7 | 2624.9 | 1221.8 | 0.61949 | 5.408
2024-12-10 | 2:34 | Data | 0 | 33.696 | 31.859 | 169.577 | 7.64 | 160.279 | 2208.06 | 25.71 | 45.818 | 6.4 | 1.289 | 4.12 | 8359.34 | 1.587 | 97.9 | 76.2 | 1436 | 22.86 | 5433.6 | 1617.5 | 2052.2 | 2627.2 | 1221.8 | 0.61345 | 5.408
2024-12-10 | 2:34 | Data | 0 | 33.358 | 31.792 | 169.531 | 7.64 | 160.189 | 2208.97 | 25.71 | 45.547 | 6.4 | 1.288 | 4.134 | 8345.77 | 1.715 | 97.9 | 76.2 | 1436 | 22.73 | 5424.8 | 1619.5 | 2036.7 | 2615.6 | 1221.8 | 0.61789 | 5.421
2024-12-10 | 2:34 | Data | 0 | 33.419 | 31.799 | 169.486 | 7.64 | 160.189 | 2208.97 | 25.71 | 45.457 | 6.4 | 1.279 | 4.118 | 8381.95 | 1.614 | 97.9 | 76.3 | 1436 | 22.73 | 5448.3 | 1619.3 | 2041.6 | 2618.6 | 1221.8 | 0.61603 | 5.397
2024-12-10 | 2:34 | Data | 0 | 33.439 | 32.015 | 169.486 | 7.64 | 160.144 | 2207.16 | 25.71 | 45.457 | 6.41 | 1.284 | 4.13 | 8345.77 | 1.452 | 97.9 | 76.3 | 1435 | 22.68 | 5424.8 | 2620.1 | 2953.6 | 4032.2 | 1221.8 | 0.58918 | 5.414
2024-12-10 | 2:34 | Data | 0 | 33.338 | 31.805 | 169.486 | 7.64 | 160.279 | 2208.06 | 25.71 | 45.457 | 6.4 | 1.291 | 4.128 | 8345.77 | 1.418 | 97.9 | 76.2 | 1435 | 22.73 | 5424.8 | 2705.3 | 2663.8 | 3925 | 1221.8 | 0.67053 | 5.419
2024-12-10 | 2:34 | Data | 0 | 33.858 | 32.035 | 169.622 | 7.64 | 160.324 | 2208.97 | 25.71 | 45.457 | 6.4 | 1.291 | 4.106 | 8332.2 | 1.695 | 97.9 | 76.1 | 1435 | 22.73 | 5415.9 | 2697.3 | 2653.7 | 3914.3 | 1221.8 | 0.67208 | 5.397
2024-12-10 | 2:34 | Data | 0 | 33.831 | 32.028 | 169.486 | 7.63 | 160.189 | 2208.97 | 25.71 | 45.457 | 6.41 | 1.292 | 4.104 | 8359.34 | 1.715 | 97.9 | 76.1 | 1436 | 22.77 | 5433.6 | 2691.3 | 2655.4 | 3915 | 1221.8 | 0.67067 | 5.397
2024-12-10 | 2:34 | Data | 0 | 33.311 | 31.691 | 169.441 | 7.64 | 160.189 | 2214.39 | 25.71 | 45.366 | 6.4 | 1.279 | 4.128 | 8345.77 | 1.647 | 98 | 76.4 | 1439 | 22.73 | 5424.8 | 2695.9 | 2622.5 | 3888.6 | 1221.8 | 0.67314 | 5.408
2024-12-10 | 2:34 | Data | 0 | 33.797 | 32.055 | 169.667 | 7.64 | 160.189 | 2211.68 | 25.72 | 45.457 | 6.4 | 1.289 | 4.126 | 8332.2 | 1.701 | 97.9 | 76.2 | 1437 | 22.73 | 5415.9 | 2691 | 2626.4 | 3887.1 | 1221.8 | 0.67566 | 5.414
2024-12-10 | 2:34 | Data | 0 | 33.257 | 31.799 | 169.396 | 7.64 | 160.189 | 2214.39 | 25.71 | 45.366 | 6.4 | 1.288 | 4.116 | 8345.77 | 1.404 | 98 | 76.2 | 1439 | 22.73 | 5424.8 | 2698.4 | 2649 | 3909.9 | 1221.8 | 0.67228 | 5.405
2024-12-10 | 2:34 | Data | 0 | 33.743 | 32.028 | 169.486 | 7.63 | 160.234 | 2213.49 | 25.7 | 45.457 | 6.4 | 1.28 | 4.128 | 8336.72 | 1.782 | 97.9 | 76.3 | 1439 | 22.77 | 5418.9 | 2697 | 2646.3 | 3909 | 1221.8 | 0.67267 | 5.409
2024-12-10 | 2:34 | Data | 0 | 33.642 | 32.028 | 169.531 | 7.64 | 160.189 | 2213.49 | 25.71 | 45.457 | 6.4 | 1.279 | 4.126 | 8314.11 | 1.728 | 98 | 76.3 | 1439 | 22.73 | 5404.2 | 2700.8 | 2635.8 | 3896.4 | 1221.8 | 0.67704 | 5.405
2024-12-10 | 2:34 | Data | 0 | 33.635 | 31.812 | 169.441 | 7.64 | 160.234 | 2213.49 | 25.71 | 45.366 | 6.4 | 1.295 | 4.109 | 8318.64 | 1.701 | 97.9 | 76 | 1439 | 22.68 | 5407.1 | 2689.3 | 2623.4 | 3888.6 | 1221.9 | 0.6749 | 5.405
2024-12-10 | 2:34 | Data | 0 | 33.642 | 31.853 | 169.441 | 7.64 | 160.189 | 2213.49 | 25.71 | 45.457 | 6.4 | 1.291 | 4.104 | 8314.11 | 1.62 | 97.9 | 76.1 | 1439 | 22.73 | 5404.2 | 2700.1 | 2647.6 | 3909.2 | 1221.9 | 0.67425 | 5.395
2024-12-10 | 2:34 | Data | 0 | 33.419 | 32.015 | 169.577 | 7.64 | 160.189 | 2205.35 | 25.68 | 45.457 | 6.4 | 1.284 | 4.115 | 8318.64 | 1.411 | 97.9 | 76.2 | 1434 | 22.73 | 5407.1 | 2691.8 | 2649.4 | 3906.6 | 1221.9 | 0.67302 | 5.4
2024-12-10 | 2:34 | Data | 0 | 33.426 | 31.799 | 169.441 | 7.64 | 160.234 | 2213.49 | 25.69 | 45.457 | 6.4 | 1.29 | 4.115 | 8318.64 | 1.614 | 97.9 | 76.1 | 1438 | 22.73 | 5407.1 | 2703.3 | 2665.2 | 3928.3 | 1221.9 | 0.67182 | 5.406
2024-12-10 | 2:35 | Data | 0 | 33.54 | 31.974 | 169.531 | 7.64 | 160.189 | 2208.06 | 25.7 | 45.457 | 6.4 | 1.288 | 4.129 | 8323.16 | 1.627 | 97.9 | 76.2 | 1435 | 22.77 | 5410.1 | 2691.5 | 2660.8 | 3919.5 | 1221.9 | 0.66958 | 5.417
2024-12-10 | 2:35 | Data | 0 | 33.81 | 32.028 | 169.531 | 7.64 | 160.279 | 2208.97 | 25.69 | 45.457 | 6.4 | 1.293 | 4.14 | 8314.11 | 1.809 | 97.9 | 76.2 | 1435 | 22.73 | 5404.2 | 2705.6 | 2641 | 3906.1 | 1221.9 | 0.6746 | 5.434
2024-12-10 | 2:35 | Data | 0 | 33.412 | 32.028 | 169.486 | 7.64 | 160.189 | 2208.97 | 25.69 | 45.457 | 6.4 | 1.287 | 4.133 | 8318.64 | 1.593 | 97.9 | 76.3 | 1436 | 22.73 | 5407.1 | 2687.1 | 2642.8 | 3898.5 | 1221.9 | 0.67003 | 5.42
2024-12-10 | 2:35 | Data | 0 | 33.581 | 32.244 | 169.486 | 7.64 | 160.189 | 2210.77 | 25.7 | 45.366 | 6.4 | 1.285 | 4.139 | 8336.72 | 1.708 | 97.9 | 76.3 | 1437 | 22.68 | 5418.9 | 2702.3 | 2661.2 | 3917.8 | 1221.9 | 0.67392 | 5.425
2024-12-10 | 2:35 | Data | 0 | 33.419 | 32.021 | 169.486 | 7.64 | 160.189 | 2210.77 | 25.69 | 45.457 | 6.4 | 1.285 | 4.11 | 8323.16 | 1.6 | 97.9 | 76.2 | 1437 | 22.73 | 5410.1 | 2705.4 | 2639.6 | 3904.1 | 1221.9 | 0.67365 | 5.394
2024-12-10 | 2:35 | Data | 0 | 33.858 | 32.035 | 169.577 | 7.64 | 160.234 | 2211.68 | 25.7 | 45.457 | 6.4 | 1.291 | 4.121 | 8332.2 | 1.634 | 97.9 | 76.2 | 1438 | 22.73 | 5415.9 | 2695.2 | 2628.8 | 3891.4 | 1221.9 | 0.67492 | 5.411
2024-12-10 | 2:35 | Data | 0 | 33.594 | 31.711 | 169.486 | 7.64 | 160.234 | 2211.68 | 25.69 | 45.457 | 6.4 | 1.293 | 4.112 | 8323.16 | 1.728 | 97.9 | 76.1 | 1438 | 22.73 | 5410.1 | 2687.2 | 2663.7 | 3911.5 | 1221.9 | 0.67073 | 5.404
2024-12-10 | 2:35 | Data | 0 | 33.628 | 31.853 | 169.531 | 7.64 | 160.189 | 2208.97 | 25.7 | 45.457 | 6.4 | 1.282 | 4.102 | 8296.02 | 1.614 | 97.9 | 76.2 | 1435 | 22.77 | 5392.4 | 2702.8 | 2624.4 | 3892.6 | 1221.9 | 0.67679 | 5.383
2024-12-10 | 2:35 | Data | 0 | 33.615 | 32.001 | 169.577 | 7.63 | 160.144 | 2208.97 | 25.69 | 45.637 | 6.4 | 1.291 | 4.128 | 8286.98 | 1.654 | 97.9 | 76.2 | 1436 | 22.82 | 5386.5 | 2706.2 | 2625.1 | 3898.4 | 1221.9 | 0.67432 | 5.42
2024-12-10 | 2:35 | Data | 0 | 33.439 | 31.643 | 169.531 | 7.64 | 160.234 | 2208.06 | 25.69 | 45.457 | 6.4 | 1.301 | 4.123 | 8734.68 | 1.593 | 97.9 | 76 | 1435 | 22.73 | 5677.5 | 2710.2 | 2620.2 | 3898.6 | 1221.9 | 0.67789 | 5.424
2024-12-10 | 2:35 | Data | 0 | 33.615 | 31.913 | 169.486 | 7.64 | 160.144 | 2208.97 | 25.69 | 45.366 | 6.4 | 1.29 | 4.105 | 8273.41 | 1.823 | 97.9 | 76.1 | 1436 | 22.68 | 5377.7 | 2700 | 2640.3 | 3908.4 | 1221.9 | 0.673 | 5.394
2024-12-10 | 2:35 | Data | 0 | 33.419 | 31.974 | 169.441 | 7.64 | 160.144 | 2208.97 | 25.69 | 45.547 | 6.4 | 1.28 | 4.118 | 8273.41 | 1.641 | 97.9 | 76.3 | 1435 | 22.73 | 5377.7 | 2701.5 | 2642 | 3912.1 | 1221.9 | 0.67268 | 5.398
2024-12-10 | 2:35 | Data | 0 | 33.527 | 32.339 | 169.577 | 7.64 | 160.279 | 2208.97 | 25.69 | 45.457 | 6.4 | 1.285 | 4.128 | 8282.46 | 1.566 | 97.9 | 76.3 | 1435 | 22.73 | 5383.6 | 2693.7 | 2647 | 3901.4 | 1221.9 | 0.67392 | 5.412
2024-12-10 | 2:35 | Data | 0 | 33.419 | 31.799 | 169.486 | 7.64 | 160.189 | 2208.06 | 25.68 | 45.727 | 6.4 | 1.288 | 4.126 | 8300.55 | 1.782 | 97.9 | 76.2 | 1436 | 22.86 | 5395.4 | 2700.3 | 2638.1 | 3903.5 | 1221.9 | 0.67386 | 5.414
2024-12-10 | 2:35 | Data | 0 | 33.419 | 32.021 | 169.577 | 7.64 | 160.279 | 2208.97 | 25.71 | 45.457 | 6.4 | 1.299 | 4.151 | 8305.07 | 1.593 | 97.9 | 76.2 | 1435 | 22.68 | 5398.3 | 2703.3 | 2652 | 3915.1 | 1221.9 | 0.67335 | 5.449
2024-12-10 | 2:35 | Data | 0 | 33.216 | 31.799 | 169.441 | 7.64 | 160.189 | 2208.06 | 25.71 | 45.366 | 6.4 | 1.301 | 4.115 | 8318.64 | 1.506 | 97.9 | 76 | 1435 | 22.73 | 5407.1 | 2723.2 | 2636.1 | 3917.2 | 1221.9 | 0.67763 | 5.416
2024-12-10 | 2:35 | Data | 0 | 33.426 | 31.799 | 169.441 | 7.64 | 160.189 | 2207.16 | 25.7 | 45.366 | 6.4 | 1.294 | 4.142 | 8314.11 | 1.614 | 97.9 | 76.2 | 1435 | 22.73 | 5404.2 | 2692 | 2656.8 | 3915.3 | 1221.9 | 0.67131 | 5.434
2024-12-10 | 2:36 | Data | 0 | 33.426 | 31.826 | 169.531 | 7.64 | 160.189 | 2208.06 | 25.71 | 45.366 | 6.41 | 1.294 | 4.126 | 8318.64 | 1.627 | 97.9 | 76.1 | 1435 | 22.73 | 5407.1 | 2705.5 | 2643.9 | 3911.2 | 1221.9 | 0.67321 | 5.421
2024-12-10 | 2:36 | Data | 0 | 33.439 | 31.913 | 169.531 | 7.64 | 160.189 | 2208.97 | 25.71 | 45.457 | 6.4 | 1.286 | 4.096 | 8336.72 | 1.566 | 97.9 | 76.1 | 1436 | 22.73 | 5418.9 | 2681.5 | 2636.1 | 3887.2 | 1221.9 | 0.6719 | 5.382
2024-12-10 | 2:36 | Data | 0 | 33.466 | 32.116 | 169.486 | 7.64 | 160.234 | 2208.97 | 25.72 | 45.457 | 6.4 | 1.293 | 4.098 | 8300.55 | 1.445 | 97.9 | 76 | 1435 | 22.73 | 5395.4 | 2703.2 | 2628.2 | 3903.9 | 1221.9 | 0.67424 | 5.392
2024-12-10 | 2:36 | Data | 0 | 33.412 | 32.021 | 169.531 | 7.64 | 160.279 | 2208.97 | 25.71 | 45.457 | 6.4 | 1.288 | 4.105 | 8305.07 | 1.573 | 97.9 | 76.1 | 1436 | 22.73 | 5398.3 | 2696.4 | 2642.2 | 3906.2 | 1221.9 | 0.67247 | 5.392
2024-12-10 | 2:36 | Data | 0 | 33.48 | 31.63 | 169.486 | 7.64 | 160.279 | 2208.97 | 25.71 | 45.457 | 6.4 | 1.293 | 4.096 | 8305.07 | 1.411 | 97.9 | 76 | 1435 | 22.68 | 5398.3 | 2710.4 | 2652.4 | 3929 | 1221.9 | 0.6744 | 5.388
2024-12-10 | 2:36 | Data | 0 | 33.669 | 31.981 | 169.577 | 7.64 | 160.279 | 2203.54 | 25.71 | 45.457 | 6.4 | 1.303 | 4.104 | 8305.07 | 1.445 | 97.9 | 75.9 | 1432 | 22.68 | 5398.3 | 2715.1 | 2642.4 | 3915.7 | 1221.9 | 0.67715 | 5.407
2024-12-10 | 2:36 | Data | 0 | 33.993 | 32.534 | 161.751 | 7.64 | 153.139 | 2203.54 | 25.71 | 45.457 | 6.4 | 1.29 | 4.074 | 8336.72 | 1.425 | 97.9 | 76 | 1432 | 22.73 | 5418.9 | 2659.2 | 2601.6 | 3850.3 | 1221.9 | 0.67362 | 5.363
2024-12-10 | 2:36 | Data | 0 | 34.134 | 32.94 | 153.429 | 7.64 | 145.456 | 2208.97 | 25.7 | 45.276 | 6.4 | 1.269 | 3.927 | 8341.25 | 1.357 | 98 | 75.6 | 1435 | 22.59 | 5421.8 | 2572.3 | 2556 | 3767.7 | 1221.9 | 0.66481 | 5.196
2024-12-10 | 2:36 | Data | 0 | 34.735 | 33.25 | 147.006 | 7.64 | 139.49 | 2211.68 | 25.7 | 45.186 | 6.4 | 1.241 | 3.756 | 8363.86 | 1.458 | 98 | 75.2 | 1438 | 22.59 | 5436.5 | 2525.1 | 2515.2 | 3700.7 | 1221.9 | 0.66662 | 4.998
2024-12-10 | 2:36 | Data | 0 | 34.796 | 33.527 | 141.532 | 7.64 | 134.609 | 2210.77 | 25.71 | 45.005 | 6.4 | 1.216 | 3.613 | 8345.77 | 1.154 | 98 | 74.8 | 1438 | 22.59 | 5424.8 | 2448.6 | 2471.3 | 3625.7 | 1221.9 | 0.65823 | 4.828
2024-12-10 | 2:36 | Data | 0 | 34.972 | 33.756 | 137.235 | 7.64 | 130.542 | 2211.68 | 25.71 | 45.366 | 6.4 | 1.195 | 3.466 | 8332.2 | 1.148 | 97.9 | 74.4 | 1437 | 22.73 | 5415.9 | 2428.1 | 2447.2 | 3593.5 | 1221.9 | 0.65686 | 4.662
2024-12-10 | 2:36 | Data | 0 | 35.073 | 33.878 | 134.069 | 7.64 | 127.649 | 2218 | 25.71 | 45.998 | 6.41 | 1.181 | 3.366 | 8318.64 | 1.168 | 97.9 | 74 | 1442 | 23 | 5407.1 | 2404 | 2430.3 | 3568.6 | 1221.9 | 0.65755 | 4.547
2024-12-10 | 2:36 | Data | 0 | 35.228 | 33.986 | 131.762 | 7.64 | 125.435 | 2218.91 | 25.71 | 46.45 | 6.41 | 1.163 | 3.293 | 8300.55 | 1.141 | 97.9 | 73.9 | 1442 | 23.22 | 5395.4 | 2385.3 | 2427 | 3549.1 | 1221.9 | 0.65595 | 4.458
2024-12-10 | 2:36 | Data | 0 | 35.228 | 34.195 | 129.455 | 7.64 | 123.401 | 2215.29 | 25.71 | 47.262 | 6.41 | 1.153 | 3.253 | 8264.37 | 1.026 | 97.9 | 73.8 | 1440 | 23.63 | 5371.8 | 2368.6 | 2416.3 | 3528.7 | 1221.9 | 0.65233 | 4.406
2024-12-10 | 2:36 | Data | 0 | 35.039 | 34.324 | 127.691 | 7.64 | 121.729 | 2218.91 | 25.71 | 47.984 | 6.42 | 1.148 | 3.2 | 8264.37 | 0.891 | 97.8 | 73.6 | 1443 | 23.99 | 5371.8 | 2366.9 | 2396.5 | 3518.3 | 1221.9 | 0.65592 | 4.348
2024-12-10 | 2:36 | Data | 0 | 35.37 | 34.337 | 126.244 | 7.64 | 120.373 | 2222.52 | 25.73 | 48.707 | 6.43 | 1.135 | 3.149 | 8219.15 | 1.134 | 97.8 | 73.5 | 1445 | 24.35 | 5342.4 | 2352.3 | 2387.9 | 3493.2 | 1221.9 | 0.65378 | 4.284
2024-12-10 | 2:36 | Data | 0 | 35.37 | 34.452 | 125.113 | 7.64 | 119.379 | 2221.62 | 25.73 | 49.519 | 6.44 | 1.134 | 3.106 | 8173.92 | 1.1 | 97.8 | 73.3 | 1445 | 24.76 | 5313.1 | 2344.9 | 2372.4 | 3487.5 | 1221.9 | 0.65295 | 4.24
2024-12-10 | 2:36 | Data | 0 | 35.269 | 34.56 | 124.435 | 7.64 | 118.656 | 2222.52 | 25.73 | 50.151 | 6.44 | 1.136 | 3.103 | 8124.18 | 0.716 | 97.7 | 73.2 | 1445 | 25.03 | 5280.7 | 2334.5 | 2351.4 | 3459.3 | 1221.9 | 0.65164 | 4.238
2024-12-10 | 2:37 | Data | 0 | 35.593 | 34.465 | 123.666 | 7.64 | 117.933 | 2222.52 | 25.72 | 50.603 | 6.45 | 1.135 | 3.089 | 8074.44 | 0.925 | 97.7 | 73.1 | 1444 | 25.35 | 5248.4 | 2322 | 2371.8 | 3469.7 | 1221.9 | 0.65274 | 4.224
2024-12-10 | 2:37 | Data | 0 | 35.485 | 34.391 | 123.349 | 7.64 | 117.616 | 2222.52 | 25.75 | 51.325 | 6.46 | 1.124 | 3.069 | 8042.78 | 0.864 | 97.7 | 73.2 | 1445 | 25.62 | 5227.8 | 2307 | 2370 | 3458.1 | 1221.9 | 0.65128 | 4.193
2024-12-10 | 2:37 | Data | 0 | 35.262 | 34.56 | 123.213 | 7.64 | 117.526 | 2222.52 | 25.74 | 51.686 | 6.46 | 1.122 | 3.073 | 7997.56 | 0.837 | 97.7 | 73.3 | 1445 | 25.89 | 5198.4 | 2326.9 | 2365.4 | 3465.8 | 1222 | 0.65636 | 4.194
2024-12-10 | 2:37 | Data | 0 | 35.485 | 34.351 | 123.304 | 7.64 | 117.526 | 2222.52 | 25.74 | 52.408 | 6.47 | 1.135 | 3.054 | 7956.86 | 0.945 | 97.6 | 72.9 | 1445 | 26.2 | 5172 | 2330.5 | 2369.4 | 3475.6 | 1222 | 0.65406 | 4.189
2024-12-10 | 2:37 | Data | 0 | 35.471 | 34.364 | 123.213 | 7.64 | 117.526 | 2225.23 | 25.74 | 52.86 | 6.47 | 1.126 | 3.054 | 7943.29 | 0.918 | 97.6 | 73.1 | 1446 | 26.43 | 5163.1 | 2315.2 | 2359.1 | 3454.2 | 1222 | 0.65218 | 4.18
2024-12-10 | 2:37 | Data | 0 | 35.255 | 34.553 | 123.168 | 7.64 | 117.481 | 2218.91 | 25.75 | 53.401 | 6.48 | 1.124 | 3.059 | 7920.68 | 0.857 | 97.6 | 73.1 | 1442 | 26.7 | 5148.4 | 2314.2 | 2367.6 | 3456.5 | 1222 | 0.65211 | 4.183
2024-12-10 | 2:37 | Data | 0 | 35.282 | 34.459 | 123.213 | 7.64 | 117.526 | 2218.91 | 25.75 | 53.672 | 6.48 | 1.129 | 3.065 | 7875.46 | 0.911 | 97.6 | 73.1 | 1443 | 26.84 | 5119 | 2327.8 | 2359.7 | 3465.7 | 1222 | 0.65361 | 4.193
2024-12-10 | 2:37 | Data | 0 | 35.485 | 34.567 | 123.123 | 7.64 | 117.436 | 2220.72 | 25.74 | 54.033 | 6.48 | 1.122 | 3.081 | 7852.85 | 0.918 | 97.6 | 73.3 | 1443 | 26.97 | 5104.3 | 2321.8 | 2378.2 | 3471.7 | 1222 | 0.65377 | 4.203
2024-12-10 | 2:37 | Data | 0 | 35.654 | 34.567 | 122.897 | 7.64 | 117.165 | 2218.91 | 25.74 | 54.214 | 6.49 | 1.132 | 3.053 | 7807.62 | 0.938 | 97.6 | 72.9 | 1442 | 27.11 | 5075 | 2325.4 | 2377 | 3475.4 | 1222 | 0.65329 | 4.184
2024-12-10 | 2:37 | Data | 0 | 35.269 | 34.337 | 122.851 | 7.64 | 117.165 | 2220.72 | 25.75 | 54.214 | 6.49 | 1.122 | 3.053 | 7789.54 | 0.911 | 97.6 | 73.1 | 1442 | 27.15 | 5063.2 | 2298.5 | 2373.6 | 3455.3 | 1222 | 0.64884 | 4.175
2024-12-10 | 2:37 | Data | 0 | 35.37 | 34.452 | 122.851 | 7.64 | 117.21 | 2216.2 | 25.75 | 54.485 | 6.49 | 1.122 | 3.046 | 7753.36 | 0.925 | 97.5 | 73.1 | 1441 | 27.24 | 5039.7 | 2331.2 | 2338.3 | 3447.5 | 1222 | 0.65834 | 4.168
2024-12-10 | 2:37 | Data | 0 | 35.532 | 34.567 | 122.806 | 7.64 | 117.165 | 2216.2 | 25.75 | 54.485 | 6.49 | 1.126 | 3.053 | 7744.31 | 0.932 | 97.5 | 73 | 1441 | 27.24 | 5033.8 | 2317.4 | 2358.8 | 3455.9 | 1222 | 0.6536 | 4.18
2024-12-10 | 2:37 | Data | 0 | 35.471 | 34.553 | 122.897 | 7.64 | 117.165 | 2216.2 | 25.74 | 54.485 | 6.49 | 1.128 | 3.065 | 7726.22 | 0.965 | 97.5 | 73.1 | 1441 | 27.24 | 5022 | 2309.1 | 2365.5 | 3457.5 | 1222 | 0.65348 | 4.193
2024-12-10 | 2:37 | Data | 0 | 35.593 | 34.567 | 122.851 | 7.64 | 117.165 | 2216.2 | 25.75 | 54.846 | 6.48 | 1.125 | 3.068 | 7699.09 | 1.134 | 97.5 | 73.2 | 1441 | 27.38 | 5004.4 | 2306.2 | 2361 | 3448.5 | 1222 | 0.65265 | 4.194
2024-12-10 | 2:37 | Data | 0 | 35.485 | 34.681 | 122.851 | 7.64 | 117.21 | 2216.2 | 25.75 | 54.756 | 6.5 | 1.126 | 3.04 | 7690.05 | 0.918 | 97.5 | 73 | 1441 | 27.42 | 4998.5 | 2320.6 | 2359.4 | 3467 | 1222 | 0.65277 | 4.166
2024-12-10 | 2:37 | Data | 0 | 35.586 | 34.783 | 122.942 | 7.64 | 117.165 | 2216.2 | 25.74 | 54.846 | 6.49 | 1.121 | 3.075 | 7671.96 | 0.918 | 97.5 | 73.3 | 1441 | 27.42 | 4986.8 | 2303.4 | 2358.1 | 3443.7 | 1222 | 0.65321 | 4.195
2024-12-10 | 2:37 | Data | 0 | 35.512 | 34.681 | 122.942 | 7.64 | 117.255 | 2217.1 | 25.76 | 54.756 | 6.49 | 1.13 | 3.063 | 7653.87 | 0.932 | 97.5 | 73.1 | 1441 | 27.42 | 4975 | 2306 | 2391.3 | 3465.4 | 1222 | 0.64946 | 4.193
2024-12-10 | 2:37 | Data | 0 | 35.478 | 34.344 | 122.851 | 7.64 | 117.21 | 2212.58 | 25.75 | 54.846 | 6.5 | 1.132 | 3.045 | 7644.82 | 0.959 | 97.5 | 72.9 | 1438 | 27.42 | 4969.1 | 2317 | 2364.8 | 3458.4 | 1222 | 0.65436 | 4.177
2024-12-10 | 2:38 | Data | 0 | 35.431 | 34.735 | 122.897 | 7.64 | 117.165 | 2210.77 | 25.77 | 54.756 | 6.49 | 1.129 | 3.074 | 7644.82 | 0.945 | 97.5 | 73.1 | 1438 | 27.38 | 4969.1 | 2283.7 | 2374.1 | 3441.5 | 1222 | 0.64811 | 4.203
2024-12-10 | 2:38 | Data | 0 | 35.6 | 34.567 | 122.399 | 7.64 | 116.713 | 2211.68 | 25.76 | 54.846 | 6.49 | 1.13 | 3.086 | 7635.78 | 1.087 | 97.5 | 73.2 | 1437 | 27.38 | 4963.3 | 2311.9 | 2343.3 | 3440.1 | 1222 | 0.65574 | 4.218
2024-12-10 | 2:38 | Data | 0 | 35.687 | 34.796 | 122.263 | 7.64 | 116.532 | 2210.77 | 25.76 | 54.846 | 6.49 | 1.115 | 3.054 | 7617.69 | 0.911 | 97.5 | 73.3 | 1437 | 27.42 | 4951.5 | 2317.1 | 2353.4 | 3450.5 | 1222 | 0.65605 | 4.17
2024-12-10 | 2:38 | Data | 0 | 35.714 | 34.573 | 122.263 | 7.64 | 116.622 | 2211.68 | 25.75 | 54.846 | 6.49 | 1.113 | 3.048 | 7613.17 | 1.121 | 97.5 | 73.2 | 1438 | 27.42 | 4948.6 | 2319.5 | 2379.3 | 3468.1 | 1222 | 0.65465 | 4.162
2024-12-10 | 2:38 | Data | 0 | 35.431 | 34.567 | 122.173 | 7.64 | 116.532 | 2214.39 | 25.76 | 54.846 | 6.49 | 1.116 | 3.053 | 7613.17 | 0.891 | 97.5 | 73.2 | 1441 | 27.38 | 4948.6 | 2320.6 | 2386.6 | 3468.9 | 1222 | 0.65408 | 4.169
2024-12-10 | 2:38 | Data | 0 | 35.512 | 34.567 | 122.128 | 7.64 | 116.532 | 2216.2 | 25.75 | 54.575 | 6.49 | 1.125 | 3.051 | 7599.6 | 0.925 | 97.5 | 73.1 | 1441 | 27.24 | 4939.7 | 2298.7 | 2354.6 | 3446.3 | 1222 | 0.64862 | 4.175
2024-12-10 | 2:38 | Data | 0 | 35.917 | 34.621 | 122.263 | 7.64 | 116.622 | 2216.2 | 25.74 | 54.756 | 6.49 | 1.116 | 3.053 | 7599.6 | 1.08 | 97.5 | 73.2 | 1441 | 27.38 | 4939.7 | 2304.2 | 2347.8 | 3437.9 | 1222 | 0.6527 | 4.169
2024-12-10 | 2:38 | Data | 0 | 35.654 | 34.621 | 122.173 | 7.64 | 116.487 | 2213.49 | 25.75 | 54.846 | 6.49 | 1.126 | 3.045 | 7590.56 | 0.722 | 97.5 | 73 | 1439 | 27.38 | 4933.9 | 2307.7 | 2379.1 | 3453.8 | 1222 | 0.64619 | 4.173
2024-12-10 | 2:38 | Data | 0 | 35.485 | 34.567 | 122.173 | 7.64 | 116.532 | 2218.91 | 25.76 | 54.665 | 6.49 | 1.122 | 3.041 | 7590.56 | 0.918 | 97.5 | 73 | 1442 | 27.33 | 4933.9 | 2297.8 | 2346.4 | 3436.1 | 1222 | 0.65235 | 4.165
2024-12-10 | 2:38 | Data | 0 | 35.485 | 34.567 | 122.218 | 7.64 | 116.532 | 2216.2 | 25.75 | 54.846 | 6.49 | 1.126 | 3.048 | 7581.51 | 0.918 | 97.5 | 73 | 1441 | 27.42 | 4928 | 2320.1 | 2345.9 | 3442 | 1222 | 0.65875 | 4.173
2024-12-10 | 2:38 | Data | 0 | 35.289 | 34.762 | 122.128 | 7.64 | 116.487 | 2216.2 | 25.76 | 54.756 | 6.49 | 1.133 | 3.05 | 7576.99 | 0.905 | 97.5 | 72.9 | 1441 | 27.42 | 4925 | 2296.4 | 2358.5 | 3442.3 | 1222 | 0.65082 | 4.184
2024-12-10 | 2:38 | Data | 0 | 35.654 | 34.654 | 122.218 | 7.64 | 116.532 | 2216.2 | 25.74 | 54.846 | 6.49 | 1.126 | 3.043 | 7576.99 | 0.999 | 97.5 | 73 | 1441 | 27.42 | 4925 | 2308.3 | 2335.7 | 3432 | 1222 | 0.65668 | 4.169
2024-12-10 | 2:38 | Data | 0 | 35.269 | 34.567 | 122.173 | 7.64 | 116.532 | 2218.91 | 25.76 | 54.756 | 6.49 | 1.121 | 3.044 | 7567.95 | 0.891 | 97.5 | 73.1 | 1442 | 27.42 | 4919.2 | 2294.6 | 2342.6 | 3424.1 | 1222 | 0.65069 | 4.164
2024-12-10 | 2:38 | Data | 0 | 35.485 | 34.567 | 122.218 | 7.64 | 116.532 | 2218.91 | 25.77 | 54.756 | 6.49 | 1.125 | 3.041 | 7563.42 | 0.918 | 97.5 | 73 | 1442 | 27.33 | 4916.2 | 2317 | 2345.9 | 3443.4 | 1222 | 0.65484 | 4.166
2024-12-10 | 2:38 | Data | 0 | 35.505 | 34.357 | 122.128 | 7.64 | 116.577 | 2222.52 | 25.77 | 54.756 | 6.49 | 1.13 | 3.06 | 7563.42 | 0.972 | 97.5 | 73.1 | 1445 | 27.38 | 4916.2 | 2297.2 | 2342.8 | 3431.4 | 1222 | 0.65221 | 4.189
2024-12-10 | 2:38 | Data | 0 | 35.573 | 34.567 | 122.218 | 7.64 | 116.532 | 2222.52 | 25.76 | 54.756 | 6.49 | 1.125 | 3.035 | 7572.47 | 0.932 | 97.5 | 73 | 1445 | 27.38 | 4922.1 | 2301.6 | 2373.7 | 3455.7 | 1222 | 0.65055 | 4.16
2024-12-10 | 2:38 | Data | 0 | 35.708 | 34.681 | 122.173 | 7.64 | 116.577 | 2218.91 | 25.76 | 54.846 | 6.49 | 1.115 | 3.033 | 7558.9 | 0.925 | 97.5 | 73.1 | 1442 | 27.38 | 4913.3 | 2314.4 | 2363.8 | 3454.7 | 1222 | 0.654 | 4.148
2024-12-10 | 2:38 | Data | 0 | 35.6 | 34.567 | 122.263 | 7.64 | 116.532 | 2218.91 | 25.75 | 54.846 | 6.49 | 1.127 | 3.043 | 7563.42 | 1.019 | 97.5 | 73 | 1442 | 27.38 | 4916.2 | 2305.8 | 2350.1 | 3441.3 | 1222 | 0.65362 | 4.17
2024-12-10 | 2:39 | Data | 0 | 35.485 | 34.567 | 122.218 | 7.64 | 116.532 | 2218.91 | 25.76 | 54.756 | 6.49 | 1.132 | 3.047 | 7567.95 | 0.83 | 97.5 | 72.9 | 1442 | 27.38 | 4919.2 | 2303.8 | 2341 | 3438.4 | 1222 | 0.65511 | 4.18
2024-12-10 | 2:39 | Data | 0 | 35.498 | 34.675 | 122.218 | 7.64 | 116.532 | 2221.62 | 25.75 | 54.756 | 6.49 | 1.13 | 3.046 | 7545.34 | 0.898 | 97.5 | 73 | 1444 | 27.38 | 4904.5 | 2311 | 2330.5 | 3432.2 | 1222 | 0.65758 | 4.177
2024-12-10 | 2:39 | Data | 0 | 35.485 | 34.607 | 122.218 | 7.64 | 116.532 | 2221.62 | 25.75 | 54.756 | 6.49 | 1.131 | 3.052 | 7549.86 | 0.83 | 97.5 | 73 | 1443 | 27.38 | 4907.4 | 2312.1 | 2343.5 | 3447.2 | 1222 | 0.65365 | 4.182
2024-12-10 | 2:39 | Data | 0 | 35.377 | 34.681 | 122.218 | 7.64 | 116.487 | 2227.95 | 25.76 | 54.846 | 6.49 | 1.128 | 3.045 | 7531.77 | 1.026 | 97.5 | 73 | 1448 | 27.38 | 4895.6 | 2322.9 | 2340.7 | 3446.9 | 1222 | 0.65839 | 4.173
2024-12-10 | 2:39 | Data | 0 | 35.708 | 34.567 | 122.218 | 7.64 | 116.577 | 2225.23 | 25.76 | 54.756 | 6.49 | 1.119 | 3.046 | 7531.77 | 0.945 | 97.5 | 73.1 | 1446 | 27.38 | 4895.6 | 2327.6 | 2360.6 | 3457.6 | 1222 | 0.65829 | 4.165
2024-12-10 | 2:39 | Data | 0 | 35.269 | 34.567 | 122.173 | 7.64 | 116.487 | 2225.23 | 25.75 | 54.846 | 6.49 | 1.127 | 3.054 | 7576.99 | 0.864 | 97.5 | 73 | 1446 | 27.42 | 4925 | 2309.4 | 2324.5 | 3429.6 | 1222 | 0.65481 | 4.182
2024-12-10 | 2:39 | Data | 0 | 35.485 | 34.567 | 122.218 | 7.64 | 116.487 | 2225.23 | 25.75 | 54.485 | 6.49 | 1.126 | 3.063 | 7531.77 | 0.918 | 97.6 | 73.1 | 1446 | 27.29 | 4895.6 | 2303.7 | 2354.6 | 3445.5 | 1222 | 0.65282 | 4.189
2024-12-10 | 2:39 | Data | 0 | 35.701 | 34.789 | 122.173 | 7.64 | 116.532 | 2220.72 | 25.77 | 54.485 | 6.49 | 1.124 | 3.047 | 7536.29 | 0.932 | 97.6 | 73.1 | 1442 | 27.24 | 4898.6 | 2301.5 | 2339 | 3434.1 | 1222 | 0.65487 | 4.172
2024-12-10 | 2:39 | Data | 0 | 35.714 | 34.681 | 122.218 | 7.63 | 116.577 | 2218.91 | 25.76 | 54.485 | 6.49 | 1.131 | 3.051 | 7531.77 | 0.918 | 97.5 | 72.9 | 1442 | 27.29 | 4895.6 | 2292.5 | 2350.2 | 3434.5 | 1222 | 0.65087 | 4.182
2024-12-10 | 2:39 | Data | 0 | 35.539 | 34.573 | 122.173 | 7.64 | 116.577 | 2218.91 | 25.75 | 54.575 | 6.49 | 1.138 | 3.046 | 7531.77 | 0.918 | 97.5 | 72.8 | 1442 | 27.29 | 4895.6 | 2310.9 | 2354.2 | 3447.7 | 1222 | 0.65495 | 4.186
2024-12-10 | 2:39 | Data | 0 | 35.485 | 34.465 | 122.173 | 7.64 | 116.532 | 2221.62 | 25.75 | 54.575 | 6.49 | 1.131 | 3.042 | 7527.25 | 1.033 | 97.5 | 72.9 | 1445 | 27.29 | 4892.7 | 2310.1 | 2345.9 | 3440.1 | 1222 | 0.65727 | 4.173
2024-12-10 | 2:39 | Data | 0 | 35.485 | 34.897 | 122.263 | 7.64 | 116.532 | 2222.52 | 25.77 | 54.485 | 6.49 | 1.118 | 3.041 | 7549.86 | 0.79 | 97.5 | 73.1 | 1445 | 27.24 | 4907.4 | 1250.9 | 1694.3 | 2114.3 | 1222 | 0.58746 | 4.16
2024-12-10 | 2:39 | Data | 0 | 35.539 | 34.573 | 122.263 | 7.64 | 116.622 | 2220.72 | 25.77 | 54.575 | 6.5 | 1.125 | 3.039 | 7549.86 | 0.918 | 97.5 | 73 | 1443 | 27.24 | 4907.4 | 1214.6 | 1690.9 | 2100.9 | 1222.1 | 0.57836 | 4.163
2024-12-10 | 2:39 | Data | 0 | 35.714 | 34.594 | 122.218 | 7.64 | 116.532 | 2218.91 | 25.76 | 54.575 | 6.49 | 1.121 | 3.041 | 7708.14 | 0.918 | 97.5 | 73.1 | 1442 | 27.29 | 5010.3 | 1217.6 | 1692.4 | 2106.5 | 1222.1 | 0.57707 | 4.162
2024-12-10 | 2:39 | Data | 0 | 35.539 | 34.567 | 122.263 | 7.64 | 116.532 | 2218.91 | 25.76 | 54.485 | 6.49 | 1.127 | 3.051 | 7717.18 | 0.709 | 97.5 | 73 | 1442 | 27.29 | 5016.2 | 1235 | 1709.9 | 2130.7 | 1222.1 | 0.57877 | 4.18
2024-12-10 | 2:39 | Data | 0 | 35.708 | 34.796 | 122.263 | 7.64 | 116.622 | 2222.52 | 25.76 | 54.575 | 6.49 | 1.128 | 3.042 | 7717.18 | 0.918 | 97.5 | 73 | 1445 | 27.24 | 5016.2 | 1236.7 | 1721.3 | 2135.9 | 1222.1 | 0.57818 | 4.169
2024-12-10 | 2:39 | Data | 0 | 35.539 | 34.573 | 122.263 | 7.64 | 116.532 | 2218.91 | 25.76 | 54.485 | 6.49 | 1.124 | 3.057 | 7717.18 | 0.918 | 97.5 | 73.1 | 1443 | 27.24 | 5016.2 | 1227.5 | 1722.3 | 2137.1 | 1222.1 | 0.57266 | 4.18
2024-12-10 | 2:40 | Data | 0 | 35.512 | 34.681 | 122.218 | 7.64 | 116.532 | 2217.1 | 25.75 | 54.575 | 6.49 | 1.126 | 3.053 | 7531.77 | 0.695 | 97.5 | 73 | 1441 | 27.29 | 4895.6 | 1242.8 | 1708 | 2130.1 | 1222.1 | 0.58318 | 4.179
2024-12-10 | 2:40 | Data | 0 | 35.546 | 34.58 | 122.218 | 7.64 | 116.622 | 2215.29 | 25.75 | 54.485 | 6.49 | 1.133 | 3.051 | 7531.77 | 0.817 | 97.5 | 72.9 | 1440 | 27.29 | 4895.6 | 1250.2 | 1712.5 | 2143.5 | 1222.1 | 0.58712 | 4.184
2024-12-10 | 2:40 | Data | 0 | 35.714 | 34.681 | 122.309 | 7.64 | 116.577 | 2216.2 | 25.74 | 54.485 | 6.49 | 1.127 | 3.03 | 7531.77 | 0.702 | 97.5 | 72.9 | 1441 | 27.29 | 4895.6 | 1228.2 | 1707.6 | 2124.3 | 1222.1 | 0.57653 | 4.158
2024-12-10 | 2:40 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.532 | 2217.1 | 25.74 | 54.394 | 6.49 | 1.131 | 3.055 | 7531.77 | 0.918 | 97.5 | 73 | 1441 | 27.15 | 4895.6 | 1249.6 | 1697 | 2126.8 | 1222.1 | 0.58622 | 4.187
2024-12-10 | 2:40 | Data | 0 | 35.282 | 34.513 | 122.128 | 7.64 | 116.487 | 2217.1 | 25.75 | 54.304 | 6.49 | 1.12 | 3.057 | 7563.42 | 0.803 | 97.6 | 73.2 | 1441 | 27.11 | 4916.2 | 1234 | 1709.5 | 2130.2 | 1222.1 | 0.57884 | 4.178
2024-12-10 | 2:40 | Data | 0 | 35.485 | 34.681 | 122.218 | 7.64 | 116.532 | 2216.2 | 25.74 | 54.214 | 6.48 | 1.126 | 3.052 | 7567.95 | 0.918 | 97.5 | 73 | 1441 | 27.15 | 4919.2 | 1247.8 | 1717.9 | 2144.4 | 1222.1 | 0.58158 | 4.178
2024-12-10 | 2:40 | Data | 0 | 35.66 | 34.573 | 122.173 | 7.64 | 116.577 | 2213.49 | 25.75 | 54.304 | 6.49 | 1.124 | 3.033 | 7549.86 | 0.999 | 97.5 | 73 | 1439 | 27.15 | 4907.4 | 1244.6 | 1687.5 | 2114.9 | 1222.1 | 0.58689 | 4.157
2024-12-10 | 2:40 | Data | 0 | 35.498 | 34.573 | 122.263 | 7.64 | 116.577 | 2214.39 | 25.74 | 54.214 | 6.49 | 1.121 | 3.028 | 7549.86 | 0.905 | 97.6 | 73 | 1439 | 27.11 | 4907.4 | 1241.9 | 1690.5 | 2115.7 | 1222.1 | 0.58554 | 4.149
2024-12-10 | 2:40 | Data | 0 | 35.714 | 34.573 | 122.263 | 7.64 | 116.577 | 2210.77 | 25.74 | 54.304 | 6.49 | 1.118 | 3.031 | 7531.77 | 0.932 | 97.5 | 73.1 | 1437 | 27.15 | 4895.6 | 1230 | 1716.6 | 2131.5 | 1222.1 | 0.57603 | 4.147
2024-12-10 | 2:40 | Data | 0 | 35.485 | 34.654 | 122.218 | 7.64 | 116.622 | 2211.68 | 25.74 | 54.485 | 6.49 | 1.124 | 3.054 | 7527.25 | 0.83 | 97.5 | 73.1 | 1437 | 27.29 | 4892.7 | 1245 | 1709.5 | 2136.6 | 1222.1 | 0.58159 | 4.176
2024-12-10 | 2:40 | Data | 0 | 35.485 | 34.567 | 122.218 | 7.64 | 116.487 | 2206.25 | 25.75 | 54.485 | 6.49 | 1.112 | 3.043 | 7549.86 | 0.918 | 97.5 | 73.2 | 1433 | 27.29 | 4907.4 | 1252.8 | 1716.9 | 2143.5 | 1222.1 | 0.58511 | 4.154
2024-12-10 | 2:40 | Data | 0 | 35.485 | 34.567 | 122.173 | 7.64 | 116.532 | 2210.77 | 25.74 | 54.304 | 6.49 | 1.109 | 3.026 | 7549.86 | 0.918 | 97.5 | 73.2 | 1437 | 27.15 | 4907.4 | 1240.5 | 1716.1 | 2138.5 | 1222.1 | 0.58053 | 4.136
2024-12-10 | 2:40 | Data | 0 | 35.714 | 34.796 | 122.309 | 7.64 | 116.577 | 2210.77 | 25.74 | 54.485 | 6.49 | 1.122 | 3.054 | 7558.9 | 0.918 | 97.5 | 73.1 | 1437 | 27.29 | 4913.3 | 1270.1 | 1718.1 | 2156.2 | 1222.1 | 0.58985 | 4.176
2024-12-10 | 2:40 | Data | 0 | 35.6 | 34.789 | 122.263 | 7.64 | 116.487 | 2210.77 | 25.74 | 54.485 | 6.49 | 1.122 | 3.038 | 7549.86 | 0.898 | 97.5 | 73 | 1436 | 27.29 | 4907.4 | 1254.8 | 1713.3 | 2142.5 | 1222.1 | 0.58485 | 4.16
2024-12-10 | 2:40 | Data | 0 | 35.485 | 34.567 | 122.263 | 7.64 | 116.532 | 2210.77 | 25.75 | 54.575 | 6.49 | 1.127 | 3.045 | 7545.34 | 0.918 | 97.5 | 73 | 1437 | 27.24 | 4904.5 | 1254.5 | 1705.2 | 2139.3 | 1222.1 | 0.58584 | 4.172
2024-12-10 | 2:40 | Data | 0 | 35.6 | 34.681 | 122.309 | 7.64 | 116.577 | 2211.68 | 25.75 | 54.575 | 6.49 | 1.131 | 3.058 | 7531.77 | 0.898 | 97.5 | 73 | 1437 | 27.24 | 4895.6 | 1243.9 | 1705.2 | 2144.2 | 1222.1 | 0.58169 | 4.189
2024-12-10 | 2:40 | Data | 0 | 35.573 | 34.452 | 122.218 | 7.64 | 116.577 | 2209.87 | 25.75 | 54.394 | 6.49 | 1.121 | 3.056 | 7531.77 | 0.911 | 97.5 | 73.2 | 1436 | 27.24 | 4895.6 | 1251.8 | 1709.9 | 2138.9 | 1222.1 | 0.58564 | 4.177
2024-12-10 | 2:40 | Data | 0 | 35.485 | 34.769 | 122.263 | 7.64 | 116.532 | 2216.2 | 25.75 | 54.485 | 6.49 | 1.126 | 3.05 | 7518.2 | 0.83 | 97.5 | 73 | 1441 | 27.24 | 4886.8 | 1265.2 | 1724.7 | 2161.7 | 1222.1 | 0.58554 | 4.176
2024-12-10 | 2:41 | Data | 0 | 35.485 | 34.567 | 122.218 | 7.64 | 116.532 | 2213.49 | 25.75 | 54.304 | 6.49 | 1.125 | 3.031 | 7518.2 | 0.918 | 97.5 | 72.9 | 1438 | 27.2 | 4886.8 | 1244.7 | 1706.9 | 2132.6 | 1222.1 | 0.5833 | 4.157
2024-12-10 | 2:41 | Data | 0 | 35.485 | 34.567 | 122.218 | 7.64 | 116.532 | 2213.49 | 25.74 | 54.485 | 6.49 | 1.122 | 3.028 | 7509.16 | 0.911 | 97.5 | 73 | 1439 | 27.24 | 4881 | 1257.4 | 1696.4 | 2132.4 | 1222.1 | 0.58865 | 4.151
2024-12-10 | 2:41 | Data | 0 | 35.66 | 34.675 | 122.263 | 7.64 | 116.532 | 2213.49 | 25.75 | 54.485 | 6.49 | 1.127 | 3.036 | 7504.64 | 0.905 | 97.5 | 72.9 | 1439 | 27.29 | 4878 | 1242.4 | 1716.9 | 2141.8 | 1222.1 | 0.57958 | 4.163
2024-12-10 | 2:41 | Data | 0 | 35.485 | 34.567 | 122.218 | 7.64 | 116.487 | 2217.1 | 25.74 | 54.575 | 6.49 | 1.127 | 3.054 | 7518.2 | 0.918 | 97.5 | 73 | 1441 | 27.29 | 4886.8 | 1240.3 | 1736.3 | 2144.3 | 1222.1 | 0.57651 | 4.18
2024-12-10 | 2:41 | Data | 0 | 35.282 | 34.567 | 122.218 | 7.64 | 116.487 | 2218.91 | 25.74 | 54.575 | 6.48 | 1.121 | 3.055 | 7531.77 | 0.81 | 97.5 | 73.2 | 1442 | 27.29 | 4895.6 | 1263.6 | 1723.4 | 2158.3 | 1222.1 | 0.58592 | 4.176
2024-12-10 | 2:41 | Data | 0 | 35.316 | 34.344 | 122.128 | 7.64 | 116.487 | 2218.91 | 25.75 | 54.575 | 6.49 | 1.127 | 3.039 | 7518.2 | 0.911 | 97.5 | 73 | 1442 | 27.24 | 4886.8 | 1241.5 | 1723.6 | 2144.7 | 1222.1 | 0.57855 | 4.166
2024-12-10 | 2:41 | Data | 0 | 35.485 | 34.735 | 122.218 | 7.64 | 116.577 | 2218.91 | 25.74 | 54.485 | 6.49 | 1.125 | 3.045 | 7522.72 | 0.972 | 97.5 | 73 | 1443 | 27.2 | 4889.8 | 1255.4 | 1736.9 | 2164.5 | 1222.1 | 0.57866 | 4.17
2024-12-10 | 2:41 | Data | 0 | 35.498 | 34.567 | 122.218 | 7.64 | 116.532 | 2218.91 | 25.74 | 54.485 | 6.49 | 1.118 | 3.053 | 7504.64 | 0.803 | 97.5 | 73.2 | 1443 | 27.29 | 4878 | 1264 | 1739.1 | 2168.2 | 1222.1 | 0.5811 | 4.17
2024-12-10 | 2:41 | Data | 0 | 35.458 | 34.567 | 122.173 | 7.64 | 116.487 | 2216.2 | 25.74 | 54.033 | 6.49 | 1.122 | 3.057 | 7522.72 | 0.918 | 97.6 | 73.1 | 1441 | 27.02 | 4889.8 | 1247.5 | 1740.1 | 2161.4 | 1222.1 | 0.57586 | 4.181
2024-12-10 | 2:41 | Data | 0 | 35.485 | 34.567 | 122.128 | 7.64 | 116.396 | 2213.49 | 25.75 | 54.575 | 6.49 | 1.131 | 3.052 | 7531.77 | 0.918 | 97.5 | 73 | 1439 | 27.29 | 4895.6 | 1236.1 | 1722.3 | 2147.7 | 1222.1 | 0.58075 | 4.182
2024-12-10 | 2:41 | Data | 0 | 35.714 | 34.371 | 122.218 | 7.64 | 116.532 | 2222.52 | 25.74 | 54.575 | 6.49 | 1.136 | 3.039 | 7513.68 | 0.972 | 97.5 | 72.8 | 1445 | 27.29 | 4883.9 | 1237.9 | 1732.1 | 2146.7 | 1222.1 | 0.57559 | 4.176
2024-12-10 | 2:41 | Data | 0 | 35.262 | 34.391 | 122.083 | 7.64 | 116.441 | 2217.1 | 25.75 | 54.575 | 6.49 | 1.13 | 3.045 | 7531.77 | 0.871 | 97.5 | 72.9 | 1441 | 27.24 | 4895.6 | 1246.7 | 1721.7 | 2141.9 | 1222.1 | 0.57599 | 4.175
2024-12-10 | 2:41 | Data | 0 | 35.255 | 34.722 | 122.128 | 7.64 | 116.487 | 2216.2 | 25.75 | 54.575 | 6.49 | 1.124 | 3.051 | 7518.2 | 0.918 | 97.5 | 73.1 | 1441 | 27.29 | 4886.8 | 1223.8 | 1709.7 | 2123.5 | 1222.1 | 0.57683 | 4.177
2024-12-10 | 2:41 | Data | 0 | 35.485 | 34.567 | 122.128 | 7.64 | 116.487 | 2218.91 | 25.74 | 54.214 | 6.49 | 1.125 | 3.043 | 7531.77 | 0.918 | 97.6 | 73 | 1442 | 27.11 | 4895.6 | 1245.5 | 1715.9 | 2138.6 | 1222.1 | 0.58091 | 4.169
2024-12-10 | 2:41 | Data | 0 | 35.282 | 34.553 | 122.218 | 7.64 | 116.441 | 2221.62 | 25.74 | 54.485 | 6.49 | 1.135 | 3.051 | 7518.2 | 0.716 | 97.5 | 72.9 | 1444 | 27.29 | 4886.8 | 1238.7 | 1726.9 | 2142.6 | 1222.1 | 0.57828 | 4.185
2024-12-10 | 2:41 | Data | 0 | 35.714 | 34.6 | 122.263 | 7.64 | 116.577 | 2220.72 | 25.74 | 54.485 | 6.49 | 1.131 | 3.051 | 7531.77 | 0.972 | 97.5 | 73 | 1443 | 27.24 | 4895.6 | 1233.5 | 1702.9 | 2123.4 | 1222.1 | 0.58125 | 4.181
2024-12-10 | 2:41 | Data | 0 | 35.255 | 34.337 | 122.128 | 7.64 | 116.441 | 2220.72 | 25.75 | 54.485 | 6.49 | 1.121 | 3.055 | 7549.86 | 1.094 | 97.5 | 73.2 | 1442 | 27.24 | 4907.4 | 1243.1 | 1709.5 | 2133 | 1222.1 | 0.58132 | 4.176
2024-12-10 | 2:41 | Data | 0 | 35.485 | 34.344 | 122.218 | 7.64 | 116.487 | 2220.72 | 25.75 | 54.485 | 6.49 | 1.121 | 3.047 | 7527.25 | 0.945 | 97.5 | 73.1 | 1443 | 27.24 | 4892.7 | 1248.3 | 1709.5 | 2133.9 | 1222.1 | 0.58549 | 4.168
2024-12-10 | 2:42 | Data | 0 | 35.485 | 34.567 | 122.128 | 7.64 | 116.487 | 2218 | 25.74 | 54.485 | 6.49 | 1.124 | 3.048 | 7531.77 | 0.918 | 97.5 | 73.1 | 1442 | 27.24 | 4895.6 | 1226.1 | 1696.7 | 2113.8 | 1222.1 | 0.57847 | 4.171
2024-12-10 | 2:42 | Data | 0 | 35.491 | 34.459 | 122.128 | 7.64 | 116.487 | 2225.23 | 25.75 | 54.575 | 6.49 | 1.122 | 3.046 | 7549.86 | 0.932 | 97.5 | 73.1 | 1446 | 27.29 | 4907.4 | 1262.1 | 1724.9 | 2154.3 | 1222.1 | 0.58518 | 4.17
2024-12-10 | 2:42 | Data | 0 | 35.309 | 34.567 | 122.128 | 7.64 | 116.487 | 2225.23 | 25.75 | 54.485 | 6.49 | 1.121 | 3.048 | 7549.86 | 0.871 | 97.5 | 73.1 | 1446 | 27.24 | 4907.4 | 1246.8 | 1701.9 | 2132.2 | 1222.1 | 0.57988 | 4.168
2024-12-10 | 2:42 | Data | 0 | 35.485 | 34.567 | 122.263 | 7.64 | 116.487 | 2223.43 | 25.74 | 54.485 | 6.49 | 1.131 | 3.059 | 7558.9 | 0.716 | 97.5 | 73 | 1445 | 27.24 | 4913.3 | 1253 | 1703.9 | 2133.8 | 1222.1 | 0.5864 | 4.189
2024-12-10 | 2:42 | Data | 0 | 35.37 | 34.567 | 122.083 | 7.64 | 116.396 | 2218 | 25.74 | 54.575 | 6.49 | 1.121 | 3.044 | 7558.9 | 0.743 | 97.5 | 73.1 | 1442 | 27.29 | 4913.3 | 1259 | 1700.2 | 2135.2 | 1222.1 | 0.58821 | 4.164
2024-12-10 | 2:42 | Data | 0 | 35.289 | 34.54 | 122.218 | 7.64 | 116.532 | 2213.49 | 25.74 | 54.575 | 6.49 | 1.122 | 3.054 | 7563.42 | 0.999 | 97.5 | 73.1 | 1439 | 27.29 | 4916.2 | 1260 | 1714.3 | 2145.3 | 1222.1 | 0.58582 | 4.176
2024-12-10 | 2:42 | Data | 0 | 35.431 | 34.567 | 122.128 | 7.64 | 116.396 | 2218.91 | 25.74 | 54.575 | 6.49 | 1.121 | 3.031 | 7572.47 | 1.08 | 97.5 | 73 | 1442 | 27.29 | 4922.1 | 1260.9 | 1719.4 | 2150.7 | 1222.1 | 0.58396 | 4.152
2024-12-10 | 2:42 | Data | 0 | 35.269 | 34.459 | 122.083 | 7.64 | 116.441 | 2216.2 | 25.75 | 54.485 | 6.49 | 1.124 | 3.037 | 7549.86 | 0.797 | 97.5 | 73 | 1441 | 27.29 | 4907.4 | 1253.9 | 1738.8 | 2161.6 | 1222.1 | 0.58083 | 4.162
2024-12-10 | 2:42 | Data | 0 | 35.471 | 34.391 | 122.173 | 7.64 | 116.396 | 2216.2 | 25.75 | 54.485 | 6.49 | 1.127 | 3.057 | 7563.42 | 0.918 | 97.5 | 73.1 | 1441 | 27.24 | 4916.2 | 1257.5 | 1715.3 | 2149.6 | 1222.1 | 0.5831 | 4.183
2024-12-10 | 2:42 | Data | 0 | 35.593 | 34.371 | 122.263 | 7.64 | 116.532 | 2216.2 | 25.75 | 54.575 | 6.49 | 1.127 | 3.053 | 7581.51 | 0.918 | 97.5 | 73.1 | 1440 | 27.29 | 4928 | 1258.4 | 1716.3 | 2144.6 | 1222.1 | 0.58665 | 4.179
2024-12-10 | 2:42 | Data | 0 | 35.282 | 34.452 | 122.173 | 7.64 | 116.487 | 2212.58 | 25.75 | 54.485 | 6.49 | 1.118 | 3.044 | 7572.47 | 0.918 | 97.5 | 73.1 | 1439 | 27.24 | 4922.1 | 1261 | 1728.6 | 2158.8 | 1222.1 | 0.58235 | 4.161
2024-12-10 | 2:42 | Data | 0 | 35.262 | 34.553 | 122.218 | 7.65 | 116.487 | 2218 | 25.74 | 54.575 | 6.49 | 1.124 | 3.046 | 7604.12 | 0.918 | 97.5 | 73 | 1442 | 27.24 | 4942.7 | 1262.3 | 1729.6 | 2161.2 | 1222.1 | 0.5828 | 4.17
2024-12-10 | 2:42 | Data | 0 | 35.485 | 34.783 | 122.263 | 7.64 | 116.532 | 2218.91 | 25.75 | 54.485 | 6.49 | 1.119 | 3.06 | 7563.42 | 0.884 | 97.5 | 73.2 | 1443 | 27.24 | 4916.2 | 1249.4 | 1700.1 | 2132.3 | 1222.1 | 0.58589 | 4.179
2024-12-10 | 2:42 | Data | 0 | 35.485 | 34.391 | 122.128 | 7.64 | 116.487 | 2216.2 | 25.74 | 54.575 | 6.48 | 1.122 | 3.045 | 7576.99 | 1.033 | 97.5 | 73.1 | 1441 | 27.24 | 4925 | 1264.4 | 1725.3 | 2151.3 | 1222.1 | 0.58272 | 4.167
2024-12-10 | 2:42 | Data | 0 | 35.478 | 34.567 | 122.128 | 7.64 | 116.487 | 2218 | 25.74 | 54.485 | 6.49 | 1.12 | 3.053 | 7576.99 | 0.918 | 97.5 | 73.2 | 1442 | 27.24 | 4925 | 1263.9 | 1726 | 2154.2 | 1222.1 | 0.58652 | 4.171
2024-12-10 | 2:42 | Data | 0 | 35.262 | 34.384 | 122.173 | 7.64 | 116.441 | 2220.72 | 25.74 | 54.485 | 6.48 | 1.127 | 3.045 | 7558.9 | 0.992 | 97.5 | 73 | 1443 | 27.24 | 4913.3 | 1229.1 | 1694.2 | 2114.9 | 1222.1 | 0.58034 | 4.17
2024-12-10 | 2:42 | Data | 0 | 35.485 | 34.681 | 122.309 | 7.64 | 116.532 | 2216.2 | 25.75 | 54.575 | 6.49 | 1.128 | 3.03 | 7563.42 | 0.918 | 97.5 | 72.9 | 1440 | 27.29 | 4916.2 | 1256.5 | 1718.7 | 2148.9 | 1222.1 | 0.5837 | 4.157
2024-12-10 | 2:42 | Data | 0 | 35.269 | 34.513 | 122.128 | 7.64 | 116.487 | 2213.49 | 25.75 | 54.575 | 6.48 | 1.126 | 3.035 | 7558.9 | 0.918 | 97.5 | 73 | 1439 | 27.29 | 4913.3 | 1245.8 | 1723.7 | 2146.9 | 1222.1 | 0.58022 | 4.16
2024-12-10 | 2:43 | Data | 0 | 35.431 | 34.769 | 122.218 | 7.64 | 116.441 | 2218.91 | 25.74 | 54.575 | 6.48 | 1.133 | 3.035 | 7572.47 | 0.891 | 97.5 | 72.8 | 1442 | 27.29 | 4922.1 | 1227.3 | 1716.5 | 2130.5 | 1222.1 | 0.574 | 4.168
2024-12-10 | 2:43 | Data | 0 | 35.485 | 34.654 | 122.263 | 7.64 | 116.487 | 2213.49 | 25.74 | 54.575 | 6.48 | 1.131 | 3.042 | 7558.9 | 0.918 | 97.5 | 72.9 | 1439 | 27.24 | 4913.3 | 1217.5 | 1727.2 | 2130.3 | 1222.1 | 0.5729 | 4.173
2024-12-10 | 2:43 | Data | 0 | 35.471 | 34.587 | 122.128 | 7.64 | 116.441 | 2218.91 | 25.74 | 54.485 | 6.49 | 1.131 | 3.054 | 7563.42 | 0.945 | 97.5 | 73 | 1442 | 27.24 | 4916.2 | 1217.8 | 1721.4 | 2117.3 | 1222.1 | 0.57722 | 4.185
2024-12-10 | 2:43 | Data | 0 | 35.161 | 34.337 | 122.128 | 7.64 | 116.487 | 2215.29 | 25.75 | 54.756 | 6.48 | 1.128 | 3.051 | 7554.38 | 0.878 | 97.5 | 73 | 1441 | 27.42 | 4910.3 | 1221.5 | 1716.3 | 2129.7 | 1222.1 | 0.57402 | 4.179
2024-12-10 | 2:43 | Data | 0 | 35.269 | 34.567 | 122.173 | 7.64 | 116.487 | 2218.91 | 25.75 | 54.485 | 6.48 | 1.121 | 3.059 | 7549.86 | 0.81 | 97.5 | 73.2 | 1442 | 27.24 | 4907.4 | 1209.5 | 1713.6 | 2119.2 | 1222.1 | 0.56998 | 4.18
2024-12-10 | 2:43 | Data | 0 | 35.6 | 34.594 | 122.263 | 7.64 | 116.532 | 2221.62 | 25.74 | 54.575 | 6.49 | 1.114 | 3.06 | 7549.86 | 0.911 | 97.5 | 73.3 | 1444 | 27.24 | 4907.4 | 1236.2 | 1728.4 | 2145.8 | 1222.1 | 0.57559 | 4.174
2024-12-10 | 2:43 | Data | 0 | 35.269 | 34.452 | 122.037 | 7.64 | 116.396 | 2225.23 | 25.75 | 54.575 | 6.49 | 1.115 | 3.051 | 7531.77 | 0.749 | 97.5 | 73.2 | 1446 | 27.29 | 4895.6 | 1220.6 | 1705.2 | 2116.9 | 1222.1 | 0.57834 | 4.166
2024-12-10 | 2:43 | Data | 0 | 35.478 | 34.513 | 122.037 | 7.64 | 116.351 | 2225.23 | 25.74 | 54.575 | 6.49 | 1.12 | 3.047 | 7536.29 | 0.817 | 97.5 | 73.1 | 1447 | 27.29 | 4898.6 | 1207.3 | 1719.7 | 2121 | 1222.1 | 0.5694 | 4.167
2024-12-10 | 2:43 | Data | 0 | 35.397 | 34.344 | 122.128 | 7.64 | 116.487 | 2225.23 | 25.75 | 54.485 | 6.49 | 1.115 | 3.056 | 6984.58 | 0.824 | 97.5 | 73.3 | 1446 | 27.29 | 4540 | 1377.6 | 2235.2 | 2661.7 | 1222.1 | 0.55286 | 4.17
2024-12-10 | 2:43 | Data | 0 | 35.269 | 34.344 | 122.083 | 7.64 | 116.441 | 2223.43 | 25.74 | 54.575 | 6.48 | 1.121 | 3.056 | 7337.31 | 0.905 | 97.6 | 73.2 | 1445 | 27.24 | 4769.3 | 2306.1 | 2365 | 3456.5 | 1222.1 | 0.64963 | 4.178
2024-12-10 | 2:43 | Data | 0 | 35.458 | 34.567 | 122.173 | 7.64 | 116.441 | 2221.62 | 25.74 | 54.485 | 6.49 | 1.124 | 3.068 | 7355.4 | 0.905 | 97.5 | 73.2 | 1445 | 27.24 | 4781 | 2326 | 2382.1 | 3474.2 | 1222.1 | 0.65489 | 4.192
2024-12-10 | 2:43 | Data | 0 | 35.255 | 34.337 | 122.173 | 7.64 | 116.351 | 2221.62 | 25.75 | 54.485 | 6.49 | 1.122 | 3.062 | 7350.88 | 0.945 | 97.5 | 73.2 | 1445 | 27.24 | 4778.1 | 2284.5 | 2356.9 | 3441.4 | 1222.1 | 0.6478 | 4.184
2024-12-10 | 2:43 | Data | 0 | 35.37 | 34.567 | 122.083 | 7.64 | 116.441 | 2218.91 | 25.74 | 54.575 | 6.48 | 1.121 | 3.06 | 7671.96 | 0.905 | 97.5 | 73.2 | 1443 | 27.29 | 4986.8 | 2295.4 | 2372.1 | 3457 | 1222.1 | 0.64434 | 4.181
2024-12-10 | 2:43 | Data | 0 | 35.255 | 34.513 | 122.083 | 7.64 | 116.396 | 2221.62 | 25.74 | 54.575 | 6.49 | 1.121 | 3.063 | 7671.96 | 0.918 | 97.5 | 73.2 | 1444 | 27.29 | 4986.8 | 2319.7 | 2355.8 | 3454.9 | 1222.1 | 0.65466 | 4.185
2024-12-10 | 2:43 | Data | 0 | 35.485 | 34.567 | 122.263 | 7.64 | 116.487 | 2216.2 | 25.75 | 54.485 | 6.48 | 1.126 | 3.042 | 7658.39 | 0.918 | 97.5 | 73 | 1441 | 27.24 | 4978 | 2307.5 | 2366.1 | 3455 | 1222.1 | 0.65262 | 4.167
2024-12-10 | 2:43 | Data | 0 | 35.431 | 34.567 | 122.263 | 7.65 | 116.532 | 2222.52 | 25.75 | 54.575 | 6.49 | 1.114 | 3.041 | 7640.3 | 0.911 | 97.5 | 73.2 | 1445 | 27.29 | 4966.2 | 2302.7 | 2359.5 | 3449.3 | 1222.1 | 0.65262 | 4.156
2024-12-10 | 2:43 | Data | 0 | 35.282 | 34.54 | 122.037 | 7.64 | 116.441 | 2222.52 | 25.76 | 54.575 | 6.49 | 1.126 | 3.043 | 7658.39 | 0.722 | 97.5 | 73 | 1445 | 27.29 | 4978 | 2300.9 | 2361.2 | 3446.5 | 1222.1 | 0.65159 | 4.17
2024-12-10 | 2:44 | Data | 0 | 35.255 | 34.54 | 122.083 | 7.64 | 116.441 | 2218.91 | 25.74 | 54.575 | 6.49 | 1.131 | 3.027 | 7653.87 | 0.743 | 97.5 | 72.8 | 1442 | 27.29 | 4975 | 2300 | 2376.1 | 3460.4 | 1222.1 | 0.64671 | 4.158
2024-12-10 | 2:44 | Data | 0 | 35.37 | 34.56 | 122.173 | 7.64 | 116.487 | 2218.91 | 25.75 | 54.485 | 6.48 | 1.129 | 3.061 | 7640.3 | 0.918 | 97.5 | 73.1 | 1442 | 27.29 | 4966.2 | 2296.2 | 2361.2 | 3443.5 | 1222.2 | 0.6494 | 4.189
2024-12-10 | 2:44 | Data | 0 | 35.593 | 34.567 | 122.128 | 7.64 | 116.441 | 2217.1 | 25.75 | 54.485 | 6.48 | 1.124 | 3.054 | 7635.78 | 0.824 | 97.5 | 73.1 | 1441 | 27.24 | 4963.3 | 2302.4 | 2368.5 | 3459.8 | 1222.2 | 0.64886 | 4.178
2024-12-10 | 2:44 | Data | 0 | 35.37 | 34.553 | 122.037 | 7.64 | 116.396 | 2216.2 | 25.74 | 54.575 | 6.48 | 1.126 | 3.057 | 7635.78 | 0.918 | 97.5 | 73.1 | 1441 | 27.29 | 4963.3 | 2307.2 | 2366.8 | 3459 | 1222.2 | 0.65005 | 4.183
2024-12-10 | 2:44 | Data | 0 | 35.309 | 34.567 | 122.173 | 7.64 | 116.396 | 2217.1 | 25.73 | 54.485 | 6.49 | 1.124 | 3.046 | 7613.17 | 0.878 | 97.5 | 73 | 1441 | 27.29 | 4948.6 | 2317.1 | 2354.1 | 3448.5 | 1222.2 | 0.654 | 4.17
2024-12-10 | 2:44 | Data | 0 | 35.498 | 34.567 | 122.128 | 7.64 | 116.532 | 2213.49 | 25.72 | 54.575 | 6.49 | 1.12 | 3.047 | 7617.69 | 0.918 | 97.5 | 73.1 | 1439 | 27.24 | 4951.5 | 2308.4 | 2367.8 | 3462.6 | 1222.2 | 0.65131 | 4.166
2024-12-10 | 2:44 | Data | 0 | 35.478 | 34.567 | 122.128 | 7.64 | 116.487 | 2208.97 | 25.73 | 54.485 | 6.49 | 1.128 | 3.045 | 7590.56 | 0.918 | 97.5 | 73 | 1436 | 27.29 | 4933.9 | 2310.1 | 2356.6 | 3454.7 | 1222.2 | 0.65248 | 4.173
2024-12-10 | 2:44 | Data | 0 | 35.471 | 34.54 | 122.083 | 7.64 | 116.441 | 2214.39 | 25.72 | 54.485 | 6.48 | 1.124 | 3.045 | 7586.04 | 0.797 | 97.5 | 73 | 1439 | 27.24 | 4930.9 | 2301.4 | 2367.9 | 3453.9 | 1222.2 | 0.65014 | 4.169
2024-12-10 | 2:44 | Data | 0 | 35.485 | 34.364 | 122.218 | 7.64 | 116.487 | 2210.77 | 25.73 | 54.575 | 6.49 | 1.136 | 3.063 | 7563.42 | 0.918 | 97.5 | 72.9 | 1437 | 27.29 | 4916.2 | 2304.3 | 2334.7 | 3431.8 | 1222.2 | 0.65314 | 4.199
2024-12-10 | 2:44 | Data | 0 | 35.255 | 34.56 | 122.083 | 7.64 | 116.441 | 2208.97 | 25.73 | 54.485 | 6.49 | 1.13 | 3.046 | 7576.99 | 0.716 | 97.5 | 72.9 | 1435 | 27.29 | 4925 | 2293.4 | 2360.5 | 3442.8 | 1222.2 | 0.64851 | 4.176
2024-12-10 | 2:44 | Data | 0 | 35.485 | 34.681 | 122.218 | 7.64 | 116.532 | 2208.06 | 25.72 | 54.124 | 6.49 | 1.121 | 3.054 | 7563.42 | 0.918 | 97.5 | 73.2 | 1435 | 27.11 | 4916.2 | 2304 | 2354.5 | 3447.5 | 1222.2 | 0.65317 | 4.174
2024-12-10 | 2:44 | Data | 0 | 35.485 | 34.567 | 122.173 | 7.64 | 116.487 | 2208.97 | 25.73 | 54.575 | 6.48 | 1.126 | 3.043 | 7549.86 | 0.918 | 97.5 | 73 | 1436 | 27.24 | 4907.4 | 2309.8 | 2332.8 | 3436.3 | 1222.2 | 0.6554 | 4.169
2024-12-10 | 2:44 | Data | 0 | 35.262 | 34.452 | 122.218 | 7.64 | 116.487 | 2208.06 | 25.73 | 54.575 | 6.49 | 1.131 | 3.059 | 7549.86 | 0.925 | 97.5 | 73 | 1436 | 27.29 | 4907.4 | 2306.9 | 2364.2 | 3458.3 | 1222.2 | 0.64804 | 4.19
2024-12-10 | 2:44 | Data | 0 | 35.485 | 34.567 | 122.128 | 7.64 | 116.487 | 2212.58 | 25.73 | 54.665 | 6.49 | 1.13 | 3.052 | 7549.86 | 0.918 | 97.5 | 73 | 1439 | 27.29 | 4907.4 | 2304.8 | 2383.1 | 3462.5 | 1222.2 | 0.65058 | 4.183
2024-12-10 | 2:44 | Data | 0 | 35.255 | 34.756 | 122.037 | 7.63 | 116.396 | 2213.49 | 25.73 | 54.485 | 6.49 | 1.132 | 3.046 | 7536.29 | 0.749 | 97.5 | 72.9 | 1439 | 27.24 | 4898.6 | 2314.2 | 2366 | 3458.7 | 1222.2 | 0.65055 | 4.178
2024-12-10 | 2:44 | Data | 0 | 35.458 | 34.769 | 122.128 | 7.64 | 116.441 | 2213.49 | 25.73 | 54.575 | 6.49 | 1.128 | 3.064 | 7549.86 | 0.918 | 97.5 | 73.1 | 1439 | 27.29 | 4907.4 | 2319.4 | 2353.7 | 3448.7 | 1222.2 | 0.65877 | 4.192
2024-12-10 | 2:44 | Data | 0 | 35.485 | 34.344 | 122.218 | 7.64 | 116.487 | 2213.49 | 25.75 | 54.575 | 6.49 | 1.126 | 3.054 | 7549.86 | 0.945 | 97.5 | 73.1 | 1439 | 27.24 | 4907.4 | 2325.1 | 2347.8 | 3451.7 | 1222.2 | 0.65537 | 4.18
2024-12-10 | 2:44 | Data | 0 | 35.309 | 34.553 | 122.128 | 7.64 | 116.487 | 2213.49 | 25.72 | 54.485 | 6.49 | 1.124 | 3.058 | 7545.34 | 0.905 | 97.5 | 73.1 | 1439 | 27.24 | 4904.5 | 2290.9 | 2345.7 | 3434.8 | 1222.2 | 0.654 | 4.181
2024-12-10 | 2:45 | Data | 0 | 35.282 | 34.459 | 122.128 | 7.64 | 116.441 | 2216.2 | 25.73 | 54.575 | 6.49 | 1.127 | 3.059 | 7536.29 | 0.803 | 97.5 | 73.1 | 1441 | 27.29 | 4898.6 | 2307.2 | 2374.4 | 3462 | 1222.2 | 0.65038 | 4.185
2024-12-10 | 2:45 | Data | 0 | 35.37 | 34.54 | 122.173 | 7.65 | 116.487 | 2216.2 | 25.73 | 54.485 | 6.49 | 1.125 | 3.056 | 7554.38 | 0.749 | 97.5 | 73.1 | 1441 | 27.24 | 4910.3 | 2316.8 | 2373.8 | 3465.2 | 1222.2 | 0.65327 | 4.181
2024-12-10 | 2:45 | Data | 0 | 35.6 | 34.398 | 122.218 | 7.64 | 116.577 | 2216.2 | 25.75 | 54.575 | 6.49 | 1.117 | 3.046 | 7549.86 | 0.952 | 97.5 | 73.2 | 1441 | 27.29 | 4907.4 | 2322.2 | 2358.9 | 3455.5 | 1222.2 | 0.65642 | 4.164
2024-12-10 | 2:45 | Data | 0 | 35.485 | 34.344 | 122.173 | 7.64 | 116.487 | 2213.49 | 25.74 | 54.485 | 6.49 | 1.112 | 3.045 | 7554.38 | 1.006 | 97.5 | 73.3 | 1439 | 27.29 | 4910.3 | 2313.4 | 2368.4 | 3464.9 | 1222.2 | 0.65025 | 4.158
2024-12-10 | 2:45 | Data | 0 | 35.262 | 34.513 | 122.128 | 7.64 | 116.487 | 2210.77 | 25.74 | 54.304 | 6.49 | 1.115 | 3.033 | 7549.86 | 0.743 | 97.5 | 73.1 | 1438 | 27.2 | 4907.4 | 2301.9 | 2351.6 | 3449.4 | 1222.2 | 0.65111 | 4.147
2024-12-10 | 2:45 | Data | 0 | 35.586 | 34.789 | 122.218 | 7.64 | 116.441 | 2213.49 | 25.74 | 54.304 | 6.49 | 1.122 | 3.03 | 7531.77 | 0.709 | 97.5 | 73 | 1439 | 27.15 | 4895.6 | 2321 | 2368 | 3466.4 | 1222.2 | 0.65255 | 4.152
2024-12-10 | 2:45 | Data | 0 | 35.471 | 34.681 | 122.218 | 7.64 | 116.487 | 2213.49 | 25.74 | 54.304 | 6.48 | 1.128 | 3.047 | 7531.77 | 0.911 | 97.5 | 73 | 1439 | 27.15 | 4895.6 | 2305.4 | 2376.2 | 3458.3 | 1222.2 | 0.64972 | 4.174
2024-12-10 | 2:45 | Data | 0 | 35.316 | 34.567 | 122.263 | 7.64 | 116.487 | 2214.39 | 25.75 | 54.485 | 6.48 | 1.128 | 3.054 | 7531.77 | 0.898 | 97.5 | 73 | 1439 | 27.24 | 4895.6 | 2325.1 | 2379.3 | 3470.6 | 1222.2 | 0.65568 | 4.183
2024-12-10 | 2:45 | Data | 0 | 35.485 | 34.567 | 122.173 | 7.64 | 116.487 | 2213.49 | 25.75 | 54.394 | 6.48 | 1.122 | 3.041 | 7536.29 | 0.918 | 97.5 | 73 | 1439 | 27.15 | 4898.6 | 2319.3 | 2374.5 | 3471.1 | 1222.2 | 0.65346 | 4.163
2024-12-10 | 2:45 | Data | 0 | 35.478 | 34.567 | 122.218 | 7.64 | 116.532 | 2213.49 | 25.75 | 54.304 | 6.49 | 1.124 | 3.06 | 7549.86 | 0.918 | 97.5 | 73.1 | 1439 | 27.2 | 4907.4 | 2319.7 | 2365.6 | 3462.3 | 1222.2 | 0.65229 | 4.184
2024-12-10 | 2:45 | Data | 0 | 35.309 | 34.681 | 122.173 | 7.64 | 116.487 | 2215.29 | 25.75 | 54.575 | 6.49 | 1.127 | 3.057 | 7527.25 | 0.898 | 97.5 | 73.1 | 1439 | 27.24 | 4892.7 | 2311.8 | 2378.8 | 3468.7 | 1222.2 | 0.65184 | 4.183
2024-12-10 | 2:45 | Data | 0 | 35.485 | 34.567 | 122.128 | 7.64 | 116.487 | 2217.1 | 25.74 | 54.485 | 6.48 | 1.127 | 3.056 | 7549.86 | 0.918 | 97.5 | 73.1 | 1442 | 27.29 | 4907.4 | 2331.8 | 2354 | 3460.8 | 1222.2 | 0.65911 | 4.182
2024-12-10 | 2:45 | Data | 0 | 35.498 | 34.567 | 122.263 | 7.64 | 116.532 | 2218 | 25.75 | 54.304 | 6.49 | 1.118 | 3.046 | 7522.72 | 0.918 | 97.6 | 73.2 | 1442 | 27.15 | 4889.8 | 2324.1 | 2371.3 | 3467 | 1222.2 | 0.65292 | 4.165
2024-12-10 | 2:45 | Data | 0 | 35.485 | 34.567 | 122.173 | 7.64 | 116.487 | 2220.72 | 25.74 | 54.485 | 6.48 | 1.114 | 3.04 | 7545.34 | 0.918 | 97.5 | 73.2 | 1442 | 27.29 | 4904.5 | 2311.5 | 2334.3 | 3436.7 | 1222.2 | 0.6548 | 4.154
2024-12-10 | 2:45 | Data | 0 | 35.485 | 34.594 | 122.218 | 7.64 | 116.487 | 2218 | 25.75 | 54.485 | 6.49 | 1.127 | 3.061 | 7531.77 | 0.817 | 97.5 | 73.1 | 1442 | 27.24 | 4895.6 | 2323.3 | 2351.6 | 3449.3 | 1222.2 | 0.65345 | 4.189
2024-12-10 | 2:45 | Data | 0 | 35.714 | 34.594 | 122.263 | 7.64 | 116.577 | 2218.91 | 25.75 | 54.214 | 6.48 | 1.124 | 3.072 | 7549.86 | 0.891 | 97.6 | 73.2 | 1443 | 27.11 | 4907.4 | 2321.7 | 2353.2 | 3457.3 | 1222.2 | 0.65602 | 4.194
2024-12-10 | 2:45 | Data | 0 | 35.6 | 34.567 | 122.218 | 7.64 | 116.532 | 2216.2 | 25.74 | 54.485 | 6.48 | 1.121 | 3.042 | 7531.77 | 0.932 | 97.5 | 73.1 | 1441 | 27.33 | 4895.6 | 2319.8 | 2344.4 | 3447.5 | 1222.2 | 0.65894 | 4.162
2024-12-10 | 2:45 | Data | 0 | 35.498 | 34.357 | 122.218 | 7.64 | 116.487 | 2216.2 | 25.74 | 54.304 | 6.48 | 1.125 | 3.065 | 7522.72 | 0.925 | 97.5 | 73.2 | 1441 | 27.15 | 4889.8 | 2297.7 | 2365.7 | 3450.8 | 1222.2 | 0.64858 | 4.19
2024-12-10 | 2:46 | Data | 0 | 35.485 | 34.567 | 122.218 | 7.65 | 116.532 | 2216.2 | 25.74 | 54.575 | 6.49 | 1.127 | 3.053 | 7522.72 | 0.918 | 97.5 | 73 | 1441 | 27.29 | 4889.8 | 2287.6 | 2382.1 | 3452.2 | 1222.2 | 0.64944 | 4.179
2024-12-10 | 2:46 | Data | 0 | 35.512 | 34.567 | 122.128 | 7.64 | 116.577 | 2216.2 | 25.75 | 54.575 | 6.49 | 1.128 | 3.027 | 7504.64 | 0.918 | 97.5 | 72.9 | 1441 | 27.29 | 4878 | 2298.8 | 2368 | 3450.2 | 1222.2 | 0.65442 | 4.154
2024-12-10 | 2:46 | Data | 0 | 35.708 | 34.567 | 122.218 | 7.64 | 116.532 | 2216.2 | 25.75 | 54.304 | 6.48 | 1.126 | 3.062 | 7504.64 | 0.972 | 97.6 | 73.1 | 1441 | 27.15 | 4878 | 2306 | 2366.1 | 3458 | 1222.2 | 0.6523 | 4.188
2024-12-10 | 2:46 | Data | 0 | 35.708 | 34.776 | 122.218 | 7.64 | 116.532 | 2213.49 | 25.74 | 54.575 | 6.48 | 1.128 | 3.063 | 7522.72 | 0.938 | 97.5 | 73.1 | 1439 | 27.29 | 4889.8 | 2305.3 | 2360.4 | 3448.3 | 1222.2 | 0.65262 | 4.19
2024-12-10 | 2:46 | Data | 0 | 35.512 | 34.594 | 122.218 | 7.64 | 116.487 | 2211.68 | 25.74 | 54.485 | 6.48 | 1.131 | 3.036 | 7527.25 | 0.824 | 97.5 | 72.9 | 1437 | 27.24 | 4892.7 | 2301.1 | 2383.6 | 3462.7 | 1222.2 | 0.6479 | 4.167
2024-12-10 | 2:46 | Data | 0 | 35.37 | 34.513 | 122.083 | 7.64 | 116.532 | 2214.39 | 25.75 | 54.575 | 6.49 | 1.131 | 3.042 | 7518.2 | 0.972 | 97.5 | 72.9 | 1439 | 27.29 | 4886.8 | 2310.6 | 2365.8 | 3462.7 | 1222.2 | 0.64968 | 4.173
2024-12-10 | 2:46 | Data | 0 | 35.485 | 34.573 | 122.263 | 7.64 | 116.532 | 2216.2 | 25.75 | 54.575 | 6.49 | 1.128 | 3.038 | 7518.2 | 0.891 | 97.5 | 72.9 | 1441 | 27.29 | 4886.8 | 2319.6 | 2343.1 | 3449.9 | 1222.2 | 0.65598 | 4.167
2024-12-10 | 2:46 | Data | 0 | 35.573 | 34.614 | 122.218 | 7.64 | 116.532 | 2214.39 | 25.75 | 54.485 | 6.48 | 1.121 | 3.046 | 7522.72 | 0.756 | 97.5 | 73.1 | 1439 | 27.24 | 4889.8 | 2300.5 | 2358.6 | 3447.3 | 1222.2 | 0.64952 | 4.168
2024-12-10 | 2:46 | Data | 0 | 35.6 | 34.573 | 122.218 | 7.64 | 116.532 | 2213.49 | 25.74 | 54.575 | 6.49 | 1.117 | 3.058 | 7531.77 | 0.905 | 97.5 | 73.3 | 1439 | 27.24 | 4895.6 | 2316.1 | 2372.8 | 3463.6 | 1222.2 | 0.65095 | 4.176
2024-12-10 | 2:46 | Data | 0 | 35.262 | 34.513 | 122.263 | 7.64 | 116.487 | 2213.49 | 25.75 | 54.124 | 6.48 | 1.127 | 3.054 | 7531.77 | 0.918 | 97.6 | 73 | 1439 | 27.06 | 4895.6 | 2303.4 | 2346.5 | 3460.6 | 1222.2 | 0.65801 | 4.18
2024-12-10 | 2:46 | Data | 0 | 35.485 | 34.796 | 122.218 | 7.64 | 116.532 | 2213.49 | 25.74 | 54.575 | 6.48 | 1.129 | 3.062 | 7531.77 | 0.905 | 97.5 | 73.1 | 1439 | 27.24 | 4895.6 | 2295.4 | 2364.3 | 3449.1 | 1222.2 | 0.65185 | 4.19
2024-12-10 | 2:46 | Data | 0 | 35.431 | 34.567 | 122.173 | 7.64 | 116.532 | 2213.49 | 25.74 | 54.575 | 6.48 | 1.127 | 3.056 | 7567.95 | 0.891 | 97.5 | 73.1 | 1439 | 27.29 | 4919.2 | 2292.1 | 2345 | 3434.2 | 1222.3 | 0.64921 | 4.183
2024-12-10 | 2:46 | Data | 0 | 35.586 | 34.567 | 122.218 | 7.64 | 116.532 | 2222.52 | 25.75 | 54.575 | 6.49 | 1.13 | 3.063 | 7911.64 | 0.945 | 97.5 | 73 | 1445 | 27.24 | 5142.6 | 2307.7 | 2353.4 | 3440 | 1222.3 | 0.65517 | 4.191
2024-12-10 | 2:46 | Data | 0 | 35.498 | 34.567 | 122.173 | 7.64 | 116.532 | 2210.77 | 25.74 | 54.575 | 6.49 | 1.127 | 3.052 | 7522.72 | 0.918 | 97.5 | 73.1 | 1437 | 27.29 | 4889.8 | 2298.8 | 2362.3 | 3447.3 | 1222.3 | 0.64972 | 4.179
2024-12-10 | 2:46 | Data | 0 | 35.485 | 34.58 | 122.218 | 7.64 | 116.577 | 2214.39 | 25.74 | 54.485 | 6.49 | 1.126 | 3.07 | 7531.77 | 0.905 | 97.5 | 73.2 | 1439 | 27.24 | 4895.6 | 2322.2 | 2358.5 | 3457.1 | 1222.3 | 0.65663 | 4.196
2024-12-10 | 2:46 | Data | 0 | 35.505 | 34.567 | 122.218 | 7.64 | 116.577 | 2214.39 | 25.74 | 57.374 | 6.48 | 1.122 | 3.061 | 7518.2 | 0.749 | 97.4 | 73.2 | 1439 | 28.69 | 4886.8 | 2304.9 | 2348.9 | 3443 | 1222.3 | 0.6507 | 4.182
2024-12-10 | 2:46 | Data | 0 | 35.478 | 34.783 | 122.218 | 7.65 | 116.532 | 2213.49 | 25.75 | 54.575 | 6.48 | 1.129 | 3.042 | 7531.77 | 0.716 | 97.5 | 72.9 | 1438 | 27.29 | 4895.6 | 2295.3 | 2379.4 | 3464.3 | 1222.3 | 0.64574 | 4.17
2024-12-10 | 2:46 | Data | 0 | 35.802 | 34.627 | 122.354 | 7.64 | 116.622 | 2213.49 | 25.74 | 54.575 | 6.49 | 1.122 | 3.048 | 7531.77 | 0.959 | 97.5 | 73.1 | 1439 | 27.24 | 4895.6 | 2306.9 | 2369.4 | 3456.9 | 1222.3 | 0.65071 | 4.17
2024-12-10 | 2:47 | Data | 0 | 35.485 | 34.567 | 122.263 | 7.64 | 116.532 | 2215.29 | 25.75 | 54.485 | 6.48 | 1.132 | 3.048 | 7513.68 | 0.918 | 97.5 | 72.9 | 1441 | 27.24 | 4883.9 | 2331.5 | 2342.8 | 3450.5 | 1222.3 | 0.6587 | 4.18
2024-12-10 | 2:47 | Data | 0 | 35.491 | 34.742 | 122.263 | 7.64 | 116.577 | 2214.39 | 25.74 | 54.575 | 6.48 | 1.128 | 3.051 | 7531.77 | 0.918 | 97.5 | 73 | 1439 | 27.24 | 4895.6 | 2311.3 | 2360 | 3452.7 | 1222.3 | 0.65153 | 4.179
2024-12-10 | 2:47 | Data | 0 | 35.714 | 34.594 | 122.263 | 7.64 | 116.577 | 2214.39 | 25.74 | 54.485 | 6.48 | 1.121 | 3.05 | 7518.2 | 0.918 | 97.5 | 73.1 | 1439 | 27.24 | 4886.8 | 2309.3 | 2355.2 | 3442.8 | 1222.3 | 0.65477 | 4.171
2024-12-10 | 2:47 | Data | 0 | 35.512 | 34.573 | 122.309 | 7.64 | 116.622 | 2213.49 | 25.75 | 54.575 | 6.48 | 1.127 | 3.06 | 7518.2 | 0.736 | 97.5 | 73.1 | 1439 | 27.29 | 4886.8 | 2294.5 | 2372 | 3451.1 | 1222.3 | 0.64925 | 4.187
2024-12-10 | 2:47 | Data | 0 | 35.654 | 34.796 | 122.173 | 7.64 | 116.532 | 2213.49 | 25.74 | 54.485 | 6.49 | 1.127 | 3.083 | 7527.25 | 0.918 | 97.5 | 73.2 | 1439 | 27.29 | 4892.7 | 2314.2 | 2357.2 | 3448.2 | 1222.3 | 0.65545 | 4.21
2024-12-10 | 2:47 | Data | 0 | 35.485 | 34.607 | 121.992 | 7.64 | 116.306 | 2212.58 | 25.74 | 54.485 | 6.48 | 1.122 | 3.047 | 7518.2 | 0.918 | 97.5 | 73.1 | 1439 | 27.24 | 4886.8 | 2320.3 | 2358.1 | 3456.1 | 1222.3 | 0.65463 | 4.17
2024-12-10 | 2:47 | Data | 0 | 35.701 | 34.769 | 122.037 | 7.64 | 116.351 | 2217.1 | 25.75 | 54.485 | 6.48 | 1.128 | 3.035 | 7504.64 | 0.972 | 97.5 | 72.9 | 1441 | 27.24 | 4878 | 2331.6 | 2343.1 | 3456 | 1222.3 | 0.6571 | 4.163
2024-12-10 | 2:47 | Data | 0 | 35.539 | 34.567 | 121.947 | 7.64 | 116.306 | 2216.2 | 25.75 | 54.575 | 6.48 | 1.119 | 3.043 | 7504.64 | 0.925 | 97.5 | 73.1 | 1440 | 27.29 | 4878 | 2318.9 | 2353.7 | 3450.6 | 1222.3 | 0.65526 | 4.161
2024-12-10 | 2:47 | Data | 0 | 35.498 | 34.573 | 122.037 | 7.64 | 116.306 | 2216.2 | 25.74 | 54.575 | 6.48 | 1.116 | 3.037 | 7504.64 | 0.911 | 97.5 | 73.1 | 1441 | 27.29 | 4878 | 2302 | 2347.7 | 3444.4 | 1222.3 | 0.65048 | 4.153
2024-12-10 | 2:47 | Data | 0 | 35.6 | 34.789 | 122.083 | 7.64 | 116.396 | 2214.39 | 25.74 | 51.596 | 6.48 | 1.118 | 3.033 | 7500.11 | 0.891 | 97.7 | 73.1 | 1439 | 25.8 | 4875.1 | 2304.7 | 2350.3 | 3446.8 | 1222.3 | 0.6545 | 4.151
2024-12-10 | 2:47 | Data | 0 | 35.627 | 34.681 | 122.037 | 7.64 | 116.441 | 2221.62 | 25.75 | 53.943 | 6.49 | 1.128 | 3.029 | 7518.2 | 0.911 | 97.6 | 72.9 | 1444 | 26.97 | 4886.8 | 2299 | 2338.5 | 3425.7 | 1222.3 | 0.6548 | 4.158
2024-12-10 | 2:47 | Data | 0 | 35.714 | 34.621 | 122.083 | 7.64 | 116.441 | 2221.62 | 25.75 | 53.943 | 6.49 | 1.125 | 3.03 | 7504.64 | 0.918 | 97.6 | 72.9 | 1445 | 27.02 | 4878 | 2288.1 | 2370.5 | 3448.8 | 1222.3 | 0.64815 | 4.155
2024-12-10 | 2:47 | Data | 0 | 35.498 | 34.567 | 121.992 | 7.64 | 116.351 | 2222.52 | 25.74 | 54.033 | 6.49 | 1.124 | 3.044 | 7504.64 | 0.918 | 97.6 | 73 | 1445 | 27.02 | 4878 | 2300.5 | 2353.3 | 3437.2 | 1222.3 | 0.65334 | 4.168
2024-12-10 | 2:47 | Data | 0 | 35.714 | 34.796 | 122.128 | 7.64 | 116.396 | 2222.52 | 25.75 | 54.033 | 6.49 | 1.131 | 3.038 | 7491.07 | 0.918 | 97.6 | 72.9 | 1445 | 27.02 | 4869.2 | 2312.3 | 2371.1 | 3463.1 | 1222.3 | 0.65038 | 4.17
2024-12-10 | 2:47 | Data | 0 | 35.498 | 34.567 | 122.037 | 7.64 | 116.396 | 2218.91 | 25.75 | 54.485 | 6.48 | 1.125 | 3.035 | 7504.64 | 0.918 | 97.5 | 73 | 1443 | 27.24 | 4878 | 2307.2 | 2365.9 | 3457 | 1222.3 | 0.64907 | 4.161
2024-12-10 | 2:47 | Data | 0 | 35.485 | 34.594 | 122.037 | 7.64 | 116.396 | 2222.52 | 25.75 | 54.575 | 6.48 | 1.124 | 3.045 | 7500.11 | 0.857 | 97.5 | 73 | 1445 | 27.24 | 4875.1 | 1228.4 | 1705.3 | 2121 | 1222.3 | 0.57927 | 4.169
2024-12-10 | 2:47 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.351 | 2222.52 | 25.75 | 54.485 | 6.48 | 1.122 | 3.063 | 7504.64 | 0.911 | 97.5 | 73.2 | 1445 | 27.24 | 4878 | 1229 | 1704.9 | 2125.1 | 1222.3 | 0.58001 | 4.185
2024-12-10 | 2:48 | Data | 0 | 35.539 | 34.573 | 121.992 | 7.64 | 116.396 | 2224.33 | 25.74 | 54.575 | 6.48 | 1.121 | 3.039 | 7504.64 | 0.918 | 97.6 | 73.1 | 1446 | 27.29 | 4878 | 1229.4 | 1692.8 | 2110.2 | 1222.3 | 0.58131 | 4.16
2024-12-10 | 2:48 | Data | 0 | 35.491 | 34.681 | 122.083 | 7.64 | 116.351 | 2222.52 | 25.74 | 54.575 | 6.49 | 1.118 | 3.054 | 7491.07 | 0.918 | 97.5 | 73.2 | 1445 | 27.29 | 4869.2 | 1214.4 | 1719.3 | 2122.3 | 1222.3 | 0.57708 | 4.171
2024-12-10 | 2:48 | Data | 0 | 35.708 | 34.621 | 122.037 | 7.65 | 116.396 | 2218.91 | 25.74 | 54.575 | 6.48 | 1.129 | 3.055 | 7509.16 | 0.81 | 97.5 | 73 | 1442 | 27.29 | 4881 | 1231.5 | 1702.2 | 2121.9 | 1222.3 | 0.58064 | 4.184
2024-12-10 | 2:48 | Data | 0 | 35.714 | 34.681 | 122.083 | 7.64 | 116.396 | 2218.91 | 25.75 | 54.575 | 6.48 | 1.127 | 3.062 | 7509.16 | 0.918 | 97.5 | 73.1 | 1443 | 27.29 | 4881 | 1224.2 | 1674.7 | 2110.6 | 1222.3 | 0.58246 | 4.189
2024-12-10 | 2:48 | Data | 0 | 35.708 | 34.776 | 121.992 | 7.64 | 116.396 | 2216.2 | 25.74 | 54.485 | 6.48 | 1.128 | 3.051 | 7509.16 | 0.871 | 97.5 | 73 | 1441 | 27.29 | 4881 | 1234.1 | 1719.4 | 2138.5 | 1222.3 | 0.57762 | 4.179
2024-12-10 | 2:48 | Data | 0 | 35.714 | 34.789 | 122.128 | 7.64 | 116.441 | 2218 | 25.74 | 54.575 | 6.49 | 1.127 | 3.046 | 7504.64 | 0.925 | 97.5 | 73 | 1442 | 27.29 | 4878 | 1217.6 | 1692.4 | 2105.4 | 1222.3 | 0.57648 | 4.174
2024-12-10 | 2:48 | Data | 0 | 35.708 | 34.796 | 122.037 | 7.64 | 116.351 | 2222.52 | 25.74 | 54.575 | 6.48 | 1.124 | 3.045 | 7500.11 | 0.918 | 97.5 | 73.1 | 1445 | 27.24 | 4875.1 | 1232.1 | 1694.4 | 2114.2 | 1222.3 | 0.58063 | 4.168
2024-12-10 | 2:48 | Data | 0 | 35.485 | 34.681 | 122.083 | 7.65 | 116.441 | 2222.52 | 25.75 | 54.575 | 6.48 | 1.118 | 3.052 | 7509.16 | 0.925 | 97.5 | 73.2 | 1444 | 27.29 | 4881 | 1248.6 | 1695.1 | 2123.9 | 1222.3 | 0.58704 | 4.168
2024-12-10 | 2:48 | Data | 0 | 35.485 | 34.742 | 122.037 | 7.64 | 116.351 | 2269.52 | 25.75 | 54.485 | 6.48 | 1.113 | 3.061 | 7504.64 | 0.979 | 97.6 | 73.3 | 1475 | 27.29 | 4878 | 1234.2 | 1701.1 | 2121.2 | 1222.3 | 0.5811 | 4.174
2024-12-10 | 2:48 | Data | 0 | 35.546 | 34.567 | 122.037 | 7.64 | 116.351 | 2275.85 | 25.74 | 54.485 | 6.48 | 1.117 | 3.042 | 7518.2 | 0.925 | 97.6 | 73.1 | 1479 | 27.29 | 4886.8 | 1212.4 | 1704 | 2110.5 | 1222.3 | 0.57426 | 4.159
2024-12-10 | 2:48 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.396 | 2274.95 | 25.75 | 54.575 | 6.49 | 1.124 | 3.055 | 7518.2 | 0.918 | 97.6 | 73.1 | 1479 | 27.29 | 4886.8 | 1232.7 | 1715.1 | 2132 | 1222.3 | 0.58271 | 4.18
2024-12-10 | 2:48 | Data | 0 | 35.458 | 34.789 | 122.083 | 7.65 | 116.396 | 2271.33 | 25.73 | 54.394 | 6.48 | 1.12 | 3.057 | 7518.2 | 0.911 | 97.6 | 73.2 | 1476 | 27.24 | 4886.8 | 1237.2 | 1696.1 | 2118.6 | 1222.3 | 0.58184 | 4.178
2024-12-10 | 2:48 | Data | 0 | 35.6 | 34.573 | 122.128 | 7.64 | 116.441 | 2221.62 | 25.73 | 54.485 | 6.48 | 1.116 | 3.043 | 7518.2 | 0.932 | 97.5 | 73.2 | 1445 | 27.29 | 4886.8 | 1216.1 | 1697.4 | 2106.4 | 1222.3 | 0.58087 | 4.159
2024-12-10 | 2:48 | Data | 0 | 35.708 | 34.573 | 122.037 | 7.64 | 116.396 | 2223.43 | 25.73 | 54.485 | 6.48 | 1.127 | 3.034 | 7509.16 | 0.918 | 97.5 | 72.9 | 1445 | 27.24 | 4881 | 1218.1 | 1698.1 | 2107.5 | 1222.3 | 0.578 | 4.161
2024-12-10 | 2:48 | Data | 0 | 35.6 | 34.621 | 121.992 | 7.64 | 116.396 | 2220.72 | 25.73 | 54.575 | 6.48 | 1.127 | 3.053 | 7509.16 | 0.81 | 97.5 | 73 | 1443 | 27.29 | 4881 | 1228.1 | 1711.3 | 2124.2 | 1222.3 | 0.57757 | 4.18
2024-12-10 | 2:48 | Data | 0 | 35.485 | 34.668 | 122.083 | 7.64 | 116.306 | 2221.62 | 25.73 | 54.846 | 6.48 | 1.135 | 3.04 | 7518.2 | 0.918 | 97.5 | 72.8 | 1444 | 27.38 | 4886.8 | 1235.7 | 1691.7 | 2112.2 | 1222.3 | 0.58382 | 4.174
2024-12-10 | 2:48 | Data | 0 | 35.6 | 34.789 | 121.992 | 7.64 | 116.351 | 2222.52 | 25.73 | 54.485 | 6.48 | 1.131 | 3.028 | 7509.16 | 0.878 | 97.5 | 72.8 | 1445 | 27.29 | 4881 | 1217.1 | 1724 | 2128.7 | 1222.3 | 0.57203 | 4.16
2024-12-10 | 2:48 | Data | 0 | 35.491 | 34.573 | 122.037 | 7.64 | 116.351 | 2224.33 | 25.74 | 54.575 | 6.48 | 1.121 | 3.055 | 7504.64 | 0.911 | 97.5 | 73.2 | 1446 | 27.33 | 4878 | 1212.3 | 1690.9 | 2102.8 | 1222.3 | 0.57696 | 4.177
2024-12-10 | 2:49 | Data | 0 | 35.6 | 34.789 | 122.083 | 7.64 | 116.351 | 2222.52 | 25.73 | 54.485 | 6.48 | 1.112 | 3.062 | 7504.64 | 0.911 | 97.5 | 73.3 | 1445 | 27.24 | 4878 | 1213.1 | 1719.8 | 2124.2 | 1222.3 | 0.57148 | 4.174
2024-12-10 | 2:49 | Data | 0 | 35.485 | 34.567 | 121.947 | 7.64 | 116.306 | 2222.52 | 25.75 | 54.485 | 6.48 | 1.122 | 3.045 | 7500.11 | 0.918 | 97.5 | 73.1 | 1445 | 27.24 | 4875.1 | 1231.2 | 1695.1 | 2115 | 1222.3 | 0.58142 | 4.166
2024-12-10 | 2:49 | Data | 0 | 35.485 | 34.567 | 121.947 | 7.64 | 116.306 | 2221.62 | 25.74 | 54.485 | 6.48 | 1.127 | 3.048 | 7486.55 | 0.918 | 97.5 | 73 | 1445 | 27.24 | 4866.3 | 1204.3 | 1695.7 | 2098.1 | 1222.3 | 0.57332 | 4.176
2024-12-10 | 2:49 | Data | 0 | 35.701 | 34.796 | 122.037 | 7.64 | 116.351 | 2224.33 | 25.72 | 54.575 | 6.48 | 1.124 | 3.041 | 7468.46 | 0.743 | 97.5 | 73 | 1446 | 27.29 | 4854.5 | 1217.9 | 1682.6 | 2093.6 | 1222.3 | 0.57986 | 4.165
2024-12-10 | 2:49 | Data | 0 | 35.6 | 34.465 | 122.037 | 7.64 | 116.351 | 2225.23 | 25.72 | 54.485 | 6.48 | 1.124 | 3.048 | 7482.02 | 1.067 | 97.5 | 73.1 | 1446 | 27.24 | 4863.3 | 1219.1 | 1693.7 | 2105.6 | 1222.3 | 0.57773 | 4.172
2024-12-10 | 2:49 | Data | 0 | 35.478 | 34.567 | 121.992 | 7.64 | 116.261 | 2227.95 | 25.73 | 54.485 | 6.48 | 1.125 | 3.041 | 7482.02 | 0.918 | 97.6 | 73 | 1448 | 27.24 | 4863.3 | 1219.2 | 1702.2 | 2112.8 | 1222.3 | 0.57696 | 4.167
2024-12-10 | 2:49 | Data | 0 | 35.714 | 34.567 | 122.083 | 7.64 | 116.396 | 2224.33 | 25.73 | 54.575 | 6.48 | 1.125 | 3.057 | 7491.07 | 0.925 | 97.5 | 73.1 | 1446 | 27.29 | 4869.2 | 1227 | 1717.5 | 2132.7 | 1222.3 | 0.57354 | 4.182
2024-12-10 | 2:49 | Data | 0 | 35.485 | 34.769 | 121.992 | 7.64 | 116.306 | 2234.27 | 25.72 | 54.575 | 6.48 | 1.119 | 3.059 | 7491.07 | 0.743 | 97.6 | 73.2 | 1453 | 27.29 | 4869.2 | 1233.4 | 1728.2 | 2143.5 | 1222.3 | 0.57511 | 4.178
2024-12-10 | 2:49 | Data | 0 | 35.701 | 34.58 | 121.992 | 7.64 | 116.396 | 2226.14 | 25.73 | 54.575 | 6.48 | 1.121 | 3.053 | 7495.59 | 0.959 | 97.5 | 73.1 | 1447 | 27.29 | 4872.1 | 1226.7 | 1704 | 2122.2 | 1222.3 | 0.57625 | 4.173
2024-12-10 | 2:49 | Data | 0 | 35.6 | 34.681 | 122.037 | 7.64 | 116.351 | 2225.23 | 25.72 | 54.485 | 6.48 | 1.118 | 3.05 | 7495.59 | 0.945 | 97.5 | 73.2 | 1446 | 27.29 | 4872.1 | 1235.4 | 1729.9 | 2148.1 | 1222.3 | 0.57327 | 4.169
2024-12-10 | 2:49 | Data | 0 | 35.498 | 34.567 | 121.992 | 7.64 | 116.306 | 2227.95 | 25.73 | 54.485 | 6.48 | 1.119 | 3.04 | 7504.64 | 0.918 | 97.6 | 73.1 | 1448 | 27.24 | 4878 | 1235.6 | 1709.2 | 2129.6 | 1222.3 | 0.57887 | 4.16
2024-12-10 | 2:49 | Data | 0 | 35.485 | 34.58 | 122.083 | 7.64 | 116.351 | 2224.33 | 25.73 | 54.575 | 6.48 | 1.121 | 3.062 | 7504.64 | 0.986 | 97.6 | 73.2 | 1446 | 27.29 | 4878 | 1226.5 | 1720.2 | 2133.3 | 1222.3 | 0.57441 | 4.182
2024-12-10 | 2:49 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2225.23 | 25.72 | 54.485 | 6.48 | 1.121 | 3.059 | 7671.96 | 0.918 | 97.5 | 73.2 | 1446 | 27.29 | 4986.8 | 1229 | 1703.9 | 2116.9 | 1222.3 | 0.58029 | 4.181
2024-12-10 | 2:49 | Data | 0 | 35.485 | 34.567 | 121.902 | 7.65 | 116.306 | 2226.14 | 25.73 | 54.575 | 6.48 | 1.126 | 3.051 | 7662.91 | 0.918 | 97.6 | 73 | 1447 | 27.29 | 4980.9 | 1223.5 | 1696.6 | 2112.4 | 1222.3 | 0.57358 | 4.178
2024-12-10 | 2:49 | Data | 0 | 35.485 | 34.567 | 121.902 | 7.64 | 116.261 | 2227.95 | 25.73 | 54.575 | 6.48 | 1.125 | 3.065 | 7658.39 | 0.749 | 97.6 | 73.2 | 1448 | 27.24 | 4978 | 1214.3 | 1692.6 | 2110 | 1222.3 | 0.57751 | 4.192
2024-12-10 | 2:49 | Data | 0 | 35.485 | 34.607 | 121.992 | 7.64 | 116.306 | 2224.33 | 25.72 | 54.575 | 6.48 | 1.125 | 3.048 | 7662.91 | 0.878 | 97.5 | 73.1 | 1445 | 27.29 | 4980.9 | 1222.3 | 1694.7 | 2106.8 | 1222.3 | 0.57266 | 4.172
2024-12-10 | 2:49 | Data | 0 | 35.485 | 34.742 | 122.037 | 7.64 | 116.306 | 2213.49 | 25.72 | 54.575 | 6.48 | 1.112 | 3.035 | 7477.5 | 0.803 | 97.5 | 73.2 | 1439 | 27.29 | 4860.4 | 1224.9 | 1716 | 2125.8 | 1222.3 | 0.57619 | 4.149
2024-12-10 | 2:49 | Data | 0 | 35.701 | 34.796 | 122.037 | 7.64 | 116.351 | 2220.72 | 25.72 | 54.575 | 6.48 | 1.118 | 3.036 | 7495.59 | 0.925 | 97.5 | 73.1 | 1442 | 27.24 | 4872.1 | 1227.5 | 1718.8 | 2131.6 | 1222.3 | 0.5748 | 4.154
2024-12-10 | 2:50 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.261 | 2220.72 | 25.73 | 54.575 | 6.48 | 1.122 | 3.042 | 7491.07 | 0.972 | 97.5 | 73 | 1442 | 27.29 | 4869.2 | 1220.5 | 1709.9 | 2121.7 | 1222.3 | 0.57438 | 4.164
2024-12-10 | 2:50 | Data | 0 | 35.485 | 34.553 | 121.992 | 7.65 | 116.306 | 2218.91 | 25.73 | 54.575 | 6.48 | 1.116 | 3.044 | 7486.55 | 0.932 | 97.5 | 73.2 | 1442 | 27.33 | 4866.3 | 1219.5 | 1703.7 | 2112.5 | 1222.3 | 0.57653 | 4.159
2024-12-10 | 2:50 | Data | 0 | 35.539 | 34.452 | 121.947 | 7.64 | 116.351 | 2217.1 | 25.72 | 54.575 | 6.48 | 1.121 | 3.037 | 7527.25 | 0.722 | 97.5 | 73 | 1441 | 27.29 | 4892.7 | 1212 | 1711.1 | 2116 | 1222.3 | 0.57327 | 4.159
2024-12-10 | 2:50 | Data | 0 | 35.262 | 34.567 | 121.992 | 7.64 | 116.261 | 2216.2 | 25.73 | 54.575 | 6.49 | 1.128 | 3.038 | 7509.16 | 0.695 | 97.5 | 72.9 | 1441 | 27.24 | 4881 | 1229 | 1721.4 | 2136.9 | 1222.3 | 0.57386 | 4.166
2024-12-10 | 2:50 | Data | 0 | 35.316 | 34.567 | 121.992 | 7.64 | 116.351 | 2210.77 | 25.72 | 54.394 | 6.48 | 1.128 | 3.042 | 7495.59 | 0.81 | 97.5 | 72.9 | 1438 | 27.24 | 4872.1 | 1234.7 | 1701.5 | 2121.3 | 1222.3 | 0.58178 | 4.17
2024-12-10 | 2:50 | Data | 0 | 35.593 | 34.58 | 121.947 | 7.65 | 116.306 | 2222.52 | 25.74 | 54.485 | 6.48 | 1.122 | 3.037 | 7491.07 | 0.918 | 97.5 | 73 | 1445 | 27.24 | 4869.2 | 1224.2 | 1698.4 | 2110.5 | 1222.3 | 0.57702 | 4.16
2024-12-10 | 2:50 | Data | 0 | 35.586 | 34.567 | 121.992 | 7.64 | 116.351 | 2222.52 | 25.73 | 54.575 | 6.48 | 1.124 | 3.042 | 7495.59 | 0.81 | 97.5 | 73 | 1445 | 27.29 | 4872.1 | 1219.1 | 1705.5 | 2114.6 | 1222.3 | 0.57704 | 4.167
2024-12-10 | 2:50 | Data | 0 | 35.485 | 34.573 | 121.947 | 7.64 | 116.306 | 2215.29 | 25.72 | 54.575 | 6.48 | 1.124 | 3.04 | 7491.07 | 0.891 | 97.5 | 73 | 1441 | 27.29 | 4869.2 | 1241.9 | 1725.5 | 2143.3 | 1222.3 | 0.57848 | 4.163
2024-12-10 | 2:50 | Data | 0 | 35.262 | 34.56 | 121.902 | 7.64 | 116.261 | 2218.91 | 25.73 | 54.575 | 6.48 | 1.122 | 3.043 | 7495.59 | 0.817 | 97.5 | 73.1 | 1443 | 27.29 | 4872.1 | 1226.1 | 1717.1 | 2129.7 | 1222.4 | 0.57289 | 4.164
2024-12-10 | 2:50 | Data | 0 | 35.485 | 34.573 | 121.992 | 7.64 | 116.306 | 2218.91 | 25.73 | 54.485 | 6.48 | 1.122 | 3.048 | 7495.59 | 0.905 | 97.5 | 73.1 | 1443 | 27.24 | 4872.1 | 1225.3 | 1707.9 | 2120.5 | 1222.4 | 0.57286 | 4.17
2024-12-10 | 2:50 | Data | 0 | 35.458 | 34.567 | 121.992 | 7.64 | 116.351 | 2222.52 | 25.73 | 54.575 | 6.49 | 1.119 | 3.042 | 7482.02 | 0.911 | 97.5 | 73.1 | 1444 | 27.29 | 4863.3 | 1209.1 | 1701.5 | 2106.6 | 1222.4 | 0.57367 | 4.161
2024-12-10 | 2:50 | Data | 0 | 35.323 | 34.56 | 121.992 | 7.64 | 116.351 | 2227.95 | 25.73 | 54.485 | 6.49 | 1.122 | 3.037 | 7491.07 | 0.83 | 97.6 | 73 | 1448 | 27.24 | 4869.2 | 1216.2 | 1727.8 | 2135.4 | 1222.4 | 0.56953 | 4.16
2024-12-10 | 2:50 | Data | 0 | 35.708 | 34.621 | 121.992 | 7.64 | 116.261 | 2230.66 | 25.73 | 54.485 | 6.48 | 1.128 | 3.047 | 7500.11 | 0.857 | 97.6 | 73 | 1450 | 27.29 | 4875.1 | 1239.9 | 1745.3 | 2158.7 | 1222.4 | 0.57496 | 4.174
2024-12-10 | 2:50 | Data | 0 | 35.586 | 34.58 | 121.947 | 7.64 | 116.306 | 2227.95 | 25.73 | 54.485 | 6.48 | 1.119 | 3.052 | 7491.07 | 1.026 | 97.6 | 73.2 | 1448 | 27.29 | 4869.2 | 1212.2 | 1728.7 | 2131.8 | 1222.4 | 0.56774 | 4.17
2024-12-10 | 2:50 | Data | 0 | 35.478 | 34.526 | 122.037 | 7.64 | 116.306 | 2227.95 | 25.72 | 54.575 | 6.48 | 1.117 | 3.051 | 7504.64 | 0.918 | 97.6 | 73.2 | 1448 | 27.24 | 4878 | 1232.1 | 1755.7 | 2163.7 | 1222.4 | 0.5688 | 4.167
2024-12-10 | 2:50 | Data | 0 | 35.478 | 34.735 | 121.902 | 7.64 | 116.351 | 2227.95 | 25.73 | 54.575 | 6.48 | 1.121 | 3.043 | 7509.16 | 0.803 | 97.5 | 73.1 | 1448 | 27.29 | 4881 | 1220.7 | 1743 | 2146.6 | 1222.4 | 0.56593 | 4.163
2024-12-10 | 2:50 | Data | 0 | 35.269 | 34.546 | 121.947 | 7.64 | 116.215 | 2230.66 | 25.73 | 54.485 | 6.48 | 1.132 | 3.046 | 7504.64 | 0.736 | 97.6 | 72.9 | 1450 | 27.24 | 4878 | 1222 | 1742.4 | 2153.4 | 1222.4 | 0.57711 | 4.178
2024-12-10 | 2:50 | Data | 0 | 35.316 | 34.567 | 122.037 | 7.64 | 116.306 | 2227.04 | 25.72 | 54.485 | 6.48 | 1.13 | 3.041 | 7513.68 | 0.864 | 97.6 | 72.9 | 1448 | 27.24 | 4883.9 | 1226.9 | 1732.1 | 2142.6 | 1222.4 | 0.57297 | 4.17
2024-12-10 | 2:51 | Data | 0 | 35.309 | 34.54 | 121.856 | 7.64 | 116.261 | 2227.95 | 25.73 | 54.485 | 6.48 | 1.121 | 3.035 | 7504.64 | 0.871 | 97.6 | 73 | 1448 | 27.24 | 4878 | 1237.4 | 1730.7 | 2146.7 | 1222.4 | 0.57639 | 4.157
2024-12-10 | 2:51 | Data | 0 | 35.255 | 34.513 | 121.947 | 7.64 | 116.17 | 2235.18 | 25.73 | 54.575 | 6.48 | 1.108 | 3.037 | 7504.64 | 0.918 | 97.6 | 73.3 | 1453 | 27.29 | 4878 | 1234.2 | 1731.4 | 2143.8 | 1222.4 | 0.57455 | 4.145
2024-12-10 | 2:51 | Data | 0 | 35.485 | 34.391 | 121.947 | 7.64 | 116.261 | 2235.18 | 25.73 | 54.575 | 6.48 | 1.121 | 3.036 | 7495.59 | 0.83 | 97.6 | 73 | 1453 | 27.24 | 4872.1 | 1220.1 | 1715.2 | 2122.8 | 1222.4 | 0.57384 | 4.158
2024-12-10 | 2:51 | Data | 0 | 35.593 | 34.573 | 121.947 | 7.64 | 116.306 | 2235.18 | 25.72 | 54.485 | 6.48 | 1.122 | 3.026 | 7504.64 | 0.824 | 97.6 | 72.9 | 1453 | 27.24 | 4878 | 1210.9 | 1724.4 | 2124.5 | 1222.4 | 0.57097 | 4.149
2024-12-10 | 2:51 | Data | 0 | 35.262 | 34.357 | 121.902 | 7.64 | 116.215 | 2229.75 | 25.73 | 54.575 | 6.49 | 1.118 | 3.044 | 7504.64 | 0.743 | 97.6 | 73.1 | 1449 | 27.29 | 4878 | 1224.2 | 1729.3 | 2137.4 | 1222.4 | 0.57154 | 4.161
2024-12-10 | 2:51 | Data | 0 | 35.282 | 34.337 | 121.856 | 7.64 | 116.17 | 2229.75 | 25.73 | 54.485 | 6.48 | 1.124 | 3.051 | 7491.07 | 0.925 | 97.6 | 73.1 | 1449 | 27.29 | 4869.2 | 1234.9 | 1721.2 | 2134.9 | 1222.4 | 0.5779 | 4.175
2024-12-10 | 2:51 | Data | 0 | 35.485 | 34.398 | 121.902 | 7.64 | 116.351 | 2232.47 | 25.72 | 54.575 | 6.48 | 1.121 | 3.047 | 7522.72 | 0.918 | 97.6 | 73.1 | 1451 | 27.24 | 4889.8 | 1218.3 | 1697.1 | 2109.3 | 1222.4 | 0.57465 | 4.169
2024-12-10 | 2:51 | Data | 0 | 35.485 | 34.567 | 121.947 | 7.64 | 116.261 | 2230.66 | 25.73 | 54.575 | 6.48 | 1.121 | 3.056 | 7518.2 | 0.918 | 97.6 | 73.2 | 1450 | 27.24 | 4886.8 | 1223 | 1744.4 | 2140.7 | 1222.4 | 0.57341 | 4.177
2024-12-10 | 2:51 | Data | 0 | 35.383 | 34.546 | 121.992 | 7.64 | 116.306 | 2230.66 | 25.73 | 54.575 | 6.48 | 1.131 | 3.027 | 7531.77 | 0.864 | 97.6 | 72.8 | 1450 | 27.29 | 4895.6 | 1219.2 | 1716 | 2125.8 | 1222.4 | 0.57391 | 4.16
2024-12-10 | 2:51 | Data | 0 | 35.37 | 34.519 | 121.902 | 7.64 | 116.215 | 2229.75 | 25.73 | 54.575 | 6.48 | 1.138 | 3.033 | 7531.77 | 0.925 | 97.6 | 72.7 | 1449 | 27.24 | 4895.6 | 1200.3 | 1734.6 | 2130.6 | 1222.4 | 0.56354 | 4.17
2024-12-10 | 2:51 | Data | 0 | 35.498 | 34.364 | 121.947 | 7.64 | 116.261 | 2230.66 | 25.72 | 54.485 | 6.48 | 1.129 | 3.037 | 7531.77 | 0.918 | 97.6 | 72.9 | 1449 | 27.29 | 4895.6 | 1213.7 | 1715.2 | 2118.6 | 1222.4 | 0.57221 | 4.167
2024-12-10 | 2:51 | Data | 0 | 35.431 | 34.567 | 121.856 | 7.64 | 116.215 | 2227.04 | 25.73 | 54.575 | 6.48 | 1.124 | 3.053 | 7527.25 | 0.911 | 97.5 | 73.1 | 1448 | 27.29 | 4892.7 | 1208.7 | 1704.5 | 2109.4 | 1222.4 | 0.57148 | 4.177
2024-12-10 | 2:51 | Data | 0 | 35.282 | 34.513 | 121.947 | 7.64 | 116.261 | 2231.56 | 25.73 | 54.485 | 6.48 | 1.121 | 3.048 | 7549.86 | 0.803 | 97.6 | 73.1 | 1451 | 27.24 | 4907.4 | 1216 | 1716.3 | 2125.8 | 1222.4 | 0.57182 | 4.17
2024-12-10 | 2:51 | Data | 0 | 35.485 | 34.567 | 121.856 | 7.64 | 116.306 | 2226.14 | 25.73 | 54.575 | 6.48 | 1.121 | 3.041 | 7527.25 | 0.918 | 97.6 | 73.1 | 1447 | 27.24 | 4892.7 | 1232.2 | 1727.8 | 2141.1 | 1222.4 | 0.57606 | 4.162
2024-12-10 | 2:51 | Data | 0 | 35.269 | 34.452 | 121.947 | 7.64 | 116.306 | 2225.23 | 25.73 | 54.936 | 6.48 | 1.121 | 3.035 | 7522.72 | 0.918 | 97.5 | 73 | 1446 | 27.42 | 4889.8 | 1246.6 | 1715.3 | 2140.4 | 1222.4 | 0.57618 | 4.155
2024-12-10 | 2:51 | Data | 0 | 35.478 | 34.398 | 121.947 | 7.64 | 116.261 | 2222.52 | 25.73 | 54.485 | 6.48 | 1.133 | 3.039 | 7531.77 | 0.911 | 97.5 | 72.8 | 1445 | 27.29 | 4895.6 | 1233.3 | 1710.3 | 2129.6 | 1222.4 | 0.57805 | 4.172
2024-12-10 | 2:51 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.261 | 2222.52 | 25.73 | 54.485 | 6.48 | 1.131 | 3.059 | 7504.64 | 0.918 | 97.5 | 73 | 1445 | 27.29 | 4878 | 1237 | 1733.9 | 2149.8 | 1222.4 | 0.57475 | 4.19
2024-12-10 | 2:52 | Data | 0 | 35.471 | 34.526 | 121.902 | 7.64 | 116.261 | 2222.52 | 25.73 | 54.846 | 6.48 | 1.132 | 3.021 | 7513.68 | 1.087 | 97.5 | 72.7 | 1445 | 27.42 | 4883.9 | 1243.1 | 1713.3 | 2133.4 | 1222.4 | 0.58392 | 4.154
2024-12-10 | 2:52 | Data | 0 | 35.485 | 34.452 | 121.947 | 7.65 | 116.306 | 2221.62 | 25.72 | 54.575 | 6.48 | 1.131 | 3.03 | 7518.2 | 0.803 | 97.5 | 72.8 | 1444 | 27.24 | 4886.8 | 1238 | 1718 | 2135.6 | 1222.4 | 0.57855 | 4.16
2024-12-10 | 2:52 | Data | 0 | 35.383 | 34.56 | 122.037 | 7.64 | 116.261 | 2221.62 | 25.73 | 54.575 | 6.48 | 1.134 | 3.031 | 7527.25 | 0.905 | 97.5 | 72.8 | 1444 | 27.24 | 4892.7 | 1224.4 | 1728.2 | 2136.6 | 1222.4 | 0.57474 | 4.165
2024-12-10 | 2:52 | Data | 0 | 35.485 | 34.344 | 121.856 | 7.64 | 116.261 | 2227.04 | 25.72 | 54.575 | 6.48 | 1.133 | 3.028 | 7518.2 | 0.932 | 97.6 | 72.8 | 1448 | 27.24 | 4886.8 | 1233 | 1711.4 | 2130 | 1222.4 | 0.57808 | 4.161
2024-12-10 | 2:52 | Data | 0 | 35.431 | 34.567 | 121.902 | 7.64 | 116.215 | 2343.64 | 25.72 | 54.575 | 6.48 | 1.128 | 3.036 | 7346.36 | 0.911 | 97.7 | 72.9 | 1523 | 27.29 | 4775.1 | 1213.1 | 1703 | 2112 | 1222.4 | 0.57334 | 4.164
2024-12-10 | 2:52 | Data | 0 | 35.282 | 34.567 | 121.992 | 7.64 | 116.306 | 2223.43 | 25.73 | 54.575 | 6.48 | 1.13 | 3.048 | 7341.83 | 0.817 | 97.5 | 73 | 1445 | 27.29 | 4772.2 | 1226.2 | 1727.7 | 2136.5 | 1222.4 | 0.57407 | 4.178
2024-12-10 | 2:52 | Data | 0 | 35.478 | 34.567 | 121.902 | 7.64 | 116.261 | 2217.1 | 25.73 | 54.575 | 6.48 | 1.131 | 3.05 | 7346.36 | 0.918 | 97.5 | 72.9 | 1441 | 27.29 | 4775.1 | 2428.2 | 2608.6 | 3729.8 | 1222.4 | 0.6477 | 4.181
2024-12-10 | 2:52 | Data | 0 | 35.593 | 34.452 | 122.083 | 7.64 | 116.306 | 2218 | 25.73 | 54.756 | 6.48 | 1.13 | 3.022 | 7350.88 | 0.81 | 97.5 | 72.8 | 1442 | 27.38 | 4778.1 | 2305 | 2380 | 3475.1 | 1222.4 | 0.65079 | 4.153
2024-12-10 | 2:52 | Data | 0 | 35.485 | 34.567 | 121.902 | 7.64 | 116.261 | 2224.33 | 25.73 | 54.485 | 6.48 | 1.122 | 3.041 | 7522.72 | 0.743 | 97.6 | 73 | 1446 | 27.24 | 4889.8 | 2312.4 | 2367.7 | 3460.5 | 1222.4 | 0.65355 | 4.162
2024-12-10 | 2:52 | Data | 0 | 35.478 | 34.553 | 121.902 | 7.64 | 116.215 | 2218.91 | 25.73 | 54.485 | 6.48 | 1.113 | 3.037 | 7536.29 | 0.938 | 97.5 | 73.2 | 1442 | 27.29 | 4898.6 | 2294.6 | 2382.2 | 3458.9 | 1222.4 | 0.6516 | 4.151
2024-12-10 | 2:52 | Data | 0 | 35.478 | 34.661 | 121.992 | 7.64 | 116.261 | 2218.91 | 25.73 | 54.575 | 6.48 | 1.128 | 3.039 | 7549.86 | 0.824 | 97.5 | 72.9 | 1442 | 27.29 | 4907.4 | 2302.1 | 2372.7 | 3459.7 | 1222.4 | 0.64824 | 4.168
2024-12-10 | 2:52 | Data | 0 | 35.255 | 34.459 | 121.856 | 7.64 | 116.215 | 2218.91 | 25.72 | 54.575 | 6.48 | 1.131 | 3.037 | 7522.72 | 0.972 | 97.5 | 72.9 | 1442 | 27.24 | 4889.8 | 2292.9 | 2384.9 | 3457.7 | 1222.4 | 0.64805 | 4.169
2024-12-10 | 2:52 | Data | 0 | 35.485 | 34.364 | 121.947 | 7.64 | 116.215 | 2218.91 | 25.72 | 54.756 | 6.48 | 1.131 | 3.053 | 7549.86 | 1.033 | 97.5 | 73 | 1442 | 27.29 | 4907.4 | 2309.9 | 2381.3 | 3469 | 1222.4 | 0.65026 | 4.183
2024-12-10 | 2:52 | Data | 0 | 35.262 | 34.344 | 121.992 | 7.64 | 116.215 | 2218.91 | 25.72 | 54.394 | 6.48 | 1.127 | 3.051 | 7518.2 | 0.911 | 97.5 | 73 | 1442 | 27.24 | 4886.8 | 2299.7 | 2376.1 | 3459 | 1222.4 | 0.64881 | 4.178
2024-12-10 | 2:52 | Data | 0 | 35.282 | 34.567 | 121.811 | 7.64 | 116.261 | 2216.2 | 25.72 | 54.575 | 6.48 | 1.119 | 3.047 | 7513.68 | 0.817 | 97.5 | 73.1 | 1441 | 27.29 | 4883.9 | 2292.2 | 2385.6 | 3462.7 | 1222.4 | 0.64477 | 4.167
2024-12-10 | 2:52 | Data | 0 | 35.478 | 34.567 | 121.992 | 7.64 | 116.306 | 2216.2 | 25.71 | 54.665 | 6.48 | 1.117 | 3.045 | 7522.72 | 0.918 | 97.5 | 73.2 | 1441 | 27.33 | 4889.8 | 2321.2 | 2384.2 | 3476.8 | 1222.4 | 0.65308 | 4.161
2024-12-10 | 2:52 | Data | 0 | 35.478 | 34.391 | 121.992 | 7.64 | 116.261 | 2217.1 | 25.7 | 54.575 | 6.48 | 1.119 | 3.033 | 7513.68 | 0.918 | 97.5 | 73 | 1441 | 27.29 | 4883.9 | 2329.9 | 2382.7 | 3478.8 | 1222.4 | 0.65398 | 4.15
2024-12-10 | 2:52 | Data | 0 | 35.444 | 34.567 | 121.992 | 7.64 | 116.261 | 2221.62 | 25.71 | 54.575 | 6.48 | 1.119 | 3.03 | 7522.72 | 0.898 | 97.5 | 73 | 1443 | 27.29 | 4889.8 | 2302.9 | 2367.1 | 3455 | 1222.4 | 0.64999 | 4.149
2024-12-10 | 2:53 | Data | 0 | 35.708 | 34.459 | 121.947 | 7.64 | 116.306 | 2218.91 | 25.7 | 54.485 | 6.48 | 1.121 | 3.043 | 7518.2 | 0.945 | 97.5 | 73.1 | 1442 | 27.29 | 4886.8 | 2302.5 | 2395.2 | 3473.4 | 1222.4 | 0.64554 | 4.163
2024-12-10 | 2:53 | Data | 0 | 35.289 | 34.567 | 121.947 | 7.64 | 116.215 | 2222.52 | 25.72 | 54.575 | 6.48 | 1.119 | 3.043 | 7513.68 | 0.864 | 97.5 | 73.1 | 1444 | 27.29 | 4883.9 | 2307.3 | 2366.9 | 3459.6 | 1222.4 | 0.65251 | 4.162
2024-12-10 | 2:53 | Data | 0 | 35.485 | 34.567 | 121.902 | 7.64 | 116.261 | 2224.33 | 25.71 | 54.575 | 6.48 | 1.127 | 3.03 | 7513.68 | 0.918 | 97.6 | 72.9 | 1446 | 27.24 | 4883.9 | 2316.7 | 2369.8 | 3465.1 | 1222.4 | 0.65039 | 4.158
2024-12-10 | 2:53 | Data | 0 | 35.539 | 34.452 | 122.083 | 7.64 | 116.261 | 2222.52 | 25.71 | 54.485 | 6.48 | 1.133 | 3.055 | 7500.11 | 0.945 | 97.5 | 72.9 | 1445 | 27.29 | 4875.1 | 2305.8 | 2362.3 | 3452.7 | 1222.4 | 0.65148 | 4.189
2024-12-10 | 2:53 | Data | 0 | 35.458 | 34.681 | 122.083 | 7.64 | 116.306 | 2222.52 | 25.71 | 54.575 | 6.48 | 1.121 | 3.056 | 7495.59 | 1.033 | 97.5 | 73.2 | 1445 | 27.29 | 4872.1 | 2306.1 | 2384.7 | 3466.1 | 1222.4 | 0.64752 | 4.177
2024-12-10 | 2:53 | Data | 0 | 35.37 | 34.567 | 122.037 | 7.64 | 116.261 | 2222.52 | 25.7 | 54.575 | 6.48 | 1.124 | 3.035 | 7509.16 | 0.898 | 97.5 | 73 | 1445 | 27.29 | 4881 | 2313.8 | 2379.6 | 3468 | 1222.4 | 0.651 | 4.159
2024-12-10 | 2:53 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.306 | 2224.33 | 25.71 | 54.575 | 6.48 | 1.127 | 3.037 | 7518.2 | 0.918 | 97.5 | 72.9 | 1446 | 27.29 | 4886.8 | 2309.1 | 2369.8 | 3458.3 | 1222.4 | 0.65144 | 4.164
2024-12-10 | 2:53 | Data | 0 | 35.478 | 34.681 | 122.037 | 7.64 | 116.261 | 2222.52 | 25.71 | 54.485 | 6.48 | 1.12 | 3.05 | 7522.72 | 0.918 | 97.5 | 73.1 | 1445 | 27.24 | 4889.8 | 2308.3 | 2373.2 | 3460 | 1222.4 | 0.6523 | 4.168
2024-12-10 | 2:53 | Data | 0 | 35.316 | 34.56 | 121.902 | 7.64 | 116.261 | 2222.52 | 25.71 | 54.575 | 6.48 | 1.121 | 3.052 | 7509.16 | 0.891 | 97.5 | 73.1 | 1444 | 27.24 | 4881 | 2303.5 | 2383.9 | 3459.1 | 1222.4 | 0.6495 | 4.173
2024-12-10 | 2:53 | Data | 0 | 35.37 | 34.567 | 121.992 | 7.64 | 116.306 | 2223.43 | 25.72 | 54.575 | 6.48 | 1.129 | 3.038 | 7504.64 | 0.864 | 97.5 | 72.9 | 1445 | 27.29 | 4878 | 2290.5 | 2382.5 | 3457.6 | 1222.4 | 0.64754 | 4.168
2024-12-10 | 2:53 | Data | 0 | 35.532 | 34.567 | 121.992 | 7.64 | 116.306 | 2218.91 | 25.71 | 54.485 | 6.48 | 1.119 | 3.028 | 7522.72 | 0.749 | 97.5 | 73 | 1442 | 27.24 | 4889.8 | 2302 | 2383.3 | 3461.3 | 1222.4 | 0.64924 | 4.148
2024-12-10 | 2:53 | Data | 0 | 35.262 | 34.56 | 121.856 | 7.64 | 116.215 | 2216.2 | 25.71 | 54.575 | 6.48 | 1.121 | 3.039 | 7504.64 | 0.716 | 97.5 | 73.1 | 1441 | 27.29 | 4878 | 2307.7 | 2363.6 | 3452.4 | 1222.4 | 0.65262 | 4.16
2024-12-10 | 2:53 | Data | 0 | 35.674 | 34.796 | 122.037 | 7.64 | 116.261 | 2217.1 | 25.71 | 54.485 | 6.48 | 1.124 | 3.062 | 7518.2 | 0.911 | 97.5 | 73.2 | 1441 | 27.29 | 4886.8 | 2310.4 | 2359.1 | 3449.7 | 1222.4 | 0.65427 | 4.184
2024-12-10 | 2:53 | Data | 0 | 35.269 | 34.567 | 121.947 | 7.64 | 116.261 | 2216.2 | 25.71 | 54.575 | 6.48 | 1.131 | 3.054 | 7518.2 | 0.905 | 97.5 | 73 | 1440 | 27.29 | 4886.8 | 2298.2 | 2354.2 | 3438 | 1222.4 | 0.65098 | 4.185
2024-12-10 | 2:53 | Data | 0 | 35.431 | 34.452 | 121.902 | 7.64 | 116.215 | 2213.49 | 25.71 | 54.485 | 6.48 | 1.13 | 3.026 | 7518.2 | 1.114 | 97.5 | 72.8 | 1439 | 27.24 | 4886.8 | 2301.6 | 2354 | 3441.3 | 1222.4 | 0.6478 | 4.154
2024-12-10 | 2:53 | Data | 0 | 35.512 | 34.371 | 121.947 | 7.64 | 116.261 | 2214.39 | 25.71 | 54.575 | 6.48 | 1.127 | 3.016 | 7531.77 | 1.04 | 97.5 | 72.8 | 1439 | 27.24 | 4895.6 | 2301.4 | 2353.6 | 3442.4 | 1222.4 | 0.64651 | 4.142
2024-12-10 | 2:53 | Data | 0 | 35.539 | 34.567 | 121.992 | 7.64 | 116.261 | 2214.39 | 25.71 | 54.485 | 6.48 | 1.125 | 3.038 | 7549.86 | 0.945 | 97.5 | 73 | 1439 | 27.24 | 4907.4 | 2300.8 | 2356.3 | 3447 | 1222.4 | 0.65137 | 4.163
2024-12-10 | 2:54 | Data | 0 | 35.498 | 34.398 | 121.902 | 7.64 | 116.215 | 2218.91 | 25.72 | 54.394 | 6.48 | 1.13 | 3.04 | 7527.25 | 0.918 | 97.5 | 72.9 | 1443 | 27.29 | 4892.7 | 2322.8 | 2349.2 | 3453.6 | 1222.5 | 0.65652 | 4.17
2024-12-10 | 2:54 | Data | 0 | 35.458 | 34.681 | 122.037 | 7.64 | 116.306 | 2222.52 | 25.71 | 54.575 | 6.48 | 1.121 | 3.035 | 7549.86 | 1.019 | 97.5 | 73 | 1444 | 27.29 | 4907.4 | 2305.4 | 2362.6 | 3451.1 | 1222.5 | 0.65301 | 4.157
2024-12-10 | 2:54 | Data | 0 | 35.289 | 34.567 | 121.992 | 7.64 | 116.351 | 2221.62 | 25.71 | 54.485 | 6.48 | 1.136 | 3.031 | 7549.86 | 0.905 | 97.5 | 72.7 | 1445 | 27.24 | 4907.4 | 2312 | 2355.8 | 3453.5 | 1222.5 | 0.65394 | 4.167
2024-12-10 | 2:54 | Data | 0 | 35.485 | 34.567 | 121.902 | 7.64 | 116.215 | 2221.62 | 25.7 | 54.575 | 6.48 | 1.12 | 3.046 | 7531.77 | 0.878 | 97.5 | 73.1 | 1445 | 27.24 | 4895.6 | 2312.4 | 2332.7 | 3437 | 1222.5 | 0.6549 | 4.165
2024-12-10 | 2:54 | Data | 0 | 35.708 | 34.668 | 122.083 | 7.64 | 116.396 | 2221.62 | 25.71 | 54.575 | 6.48 | 1.116 | 3.042 | 7531.77 | 0.844 | 97.5 | 73.2 | 1445 | 27.29 | 4895.6 | 2324.6 | 2348.1 | 3456 | 1222.5 | 0.65743 | 4.158
2024-12-10 | 2:54 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.306 | 2216.2 | 25.71 | 54.485 | 6.48 | 1.125 | 3.041 | 7522.72 | 0.918 | 97.5 | 73 | 1441 | 27.29 | 4889.8 | 2308.8 | 2351.1 | 3449.6 | 1222.5 | 0.65074 | 4.166
2024-12-10 | 2:54 | Data | 0 | 35.478 | 34.567 | 121.947 | 7.64 | 116.306 | 2117.68 | 25.71 | 54.575 | 6.48 | 1.122 | 3.042 | 7518.2 | 0.918 | 97.4 | 73 | 1376 | 27.29 | 4886.8 | 2311.9 | 2366.3 | 3449.6 | 1222.5 | 0.64953 | 4.163
2024-12-10 | 2:54 | Data | 0 | 35.687 | 34.58 | 121.992 | 7.64 | 116.351 | 2217.1 | 25.71 | 54.485 | 6.48 | 1.121 | 3.038 | 7518.2 | 0.925 | 97.5 | 73 | 1441 | 27.24 | 4886.8 | 2299.2 | 2366.4 | 3450.4 | 1222.5 | 0.65097 | 4.16
2024-12-10 | 2:54 | Data | 0 | 35.485 | 34.567 | 121.902 | 7.64 | 116.215 | 2218.91 | 25.71 | 54.575 | 6.48 | 1.118 | 3.048 | 7522.72 | 0.918 | 97.5 | 73.2 | 1442 | 27.24 | 4889.8 | 2301.8 | 2344.8 | 3435.2 | 1222.5 | 0.65469 | 4.168
2024-12-10 | 2:54 | Data | 0 | 35.64 | 34.567 | 121.947 | 7.64 | 116.306 | 2220.72 | 25.72 | 54.575 | 6.48 | 1.124 | 3.054 | 7531.77 | 0.83 | 97.5 | 73.1 | 1442 | 27.29 | 4895.6 | 2307.8 | 2352.1 | 3438.5 | 1222.5 | 0.65425 | 4.179
2024-12-10 | 2:54 | Data | 0 | 35.485 | 34.567 | 121.947 | 7.64 | 116.261 | 2218.91 | 25.71 | 54.485 | 6.48 | 1.122 | 3.055 | 7518.2 | 0.918 | 97.5 | 73.1 | 1442 | 27.24 | 4886.8 | 2300.5 | 2354.7 | 3439.2 | 1222.5 | 0.65233 | 4.178
2024-12-10 | 2:54 | Data | 0 | 35.316 | 34.681 | 122.037 | 7.64 | 116.261 | 2223.43 | 25.71 | 54.485 | 6.48 | 1.115 | 3.054 | 7522.72 | 1.026 | 97.5 | 73.3 | 1445 | 27.29 | 4889.8 | 2315.8 | 2378.5 | 3465.9 | 1222.5 | 0.65621 | 4.169
2024-12-10 | 2:54 | Data | 0 | 35.491 | 34.567 | 121.947 | 7.64 | 116.306 | 2218.91 | 25.71 | 54.485 | 6.48 | 1.117 | 3.038 | 7527.25 | 0.749 | 97.5 | 73.1 | 1442 | 27.24 | 4892.7 | 2300.9 | 2361.4 | 3446.7 | 1222.5 | 0.65046 | 4.155
2024-12-10 | 2:54 | Data | 0 | 35.431 | 34.789 | 121.992 | 7.64 | 116.306 | 2216.2 | 25.71 | 54.485 | 6.48 | 1.121 | 3.051 | 7513.68 | 0.891 | 97.5 | 73.1 | 1440 | 27.24 | 4883.9 | 2317.1 | 2344 | 3451.9 | 1222.5 | 0.65323 | 4.172
2024-12-10 | 2:54 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.261 | 2216.2 | 25.71 | 54.485 | 6.48 | 1.124 | 3.059 | 7531.77 | 0.918 | 97.5 | 73.1 | 1441 | 27.24 | 4895.6 | 2305.2 | 2367.1 | 3452.7 | 1222.5 | 0.65037 | 4.183
2024-12-10 | 2:54 | Data | 0 | 35.458 | 34.567 | 121.992 | 7.65 | 116.306 | 2216.2 | 25.71 | 54.665 | 6.48 | 1.116 | 3.034 | 7513.68 | 0.905 | 97.5 | 73.1 | 1441 | 27.29 | 4883.9 | 2300.1 | 2354 | 3442.1 | 1222.5 | 0.64939 | 4.15
2024-12-10 | 2:54 | Data | 0 | 35.471 | 34.789 | 121.902 | 7.64 | 116.261 | 2214.39 | 25.71 | 54.485 | 6.49 | 1.119 | 3.042 | 7527.25 | 0.898 | 97.5 | 73.1 | 1439 | 27.29 | 4892.7 | 2308.5 | 2377.7 | 3464.1 | 1222.5 | 0.65043 | 4.161
2024-12-10 | 2:54 | Data | 0 | 35.485 | 34.567 | 121.902 | 7.64 | 116.261 | 2213.49 | 25.72 | 54.575 | 6.48 | 1.122 | 3.051 | 7549.86 | 0.83 | 97.5 | 73.1 | 1439 | 27.24 | 4907.4 | 2310.8 | 2371.6 | 3455.3 | 1222.5 | 0.65169 | 4.173
2024-12-10 | 2:54 | Data | 0 | 35.708 | 34.621 | 122.037 | 7.64 | 116.306 | 2216.2 | 25.72 | 54.575 | 6.48 | 1.126 | 3.046 | 7531.77 | 0.925 | 97.5 | 73 | 1441 | 27.29 | 4895.6 | 2299.2 | 2356.6 | 3441 | 1222.5 | 0.65221 | 4.172
2024-12-10 | 2:55 | Data | 0 | 35.275 | 34.526 | 121.947 | 7.64 | 116.396 | 2213.49 | 25.72 | 54.485 | 6.48 | 1.134 | 3.045 | 7545.34 | 0.736 | 97.5 | 72.9 | 1439 | 27.24 | 4904.5 | 2291.8 | 2367.1 | 3445.5 | 1222.5 | 0.64984 | 4.179
2024-12-10 | 2:55 | Data | 0 | 35.593 | 34.567 | 122.037 | 7.64 | 116.351 | 2210.77 | 25.71 | 54.575 | 6.48 | 1.129 | 3.045 | 7531.77 | 0.959 | 97.5 | 73 | 1438 | 27.24 | 4895.6 | 2301.2 | 2364.1 | 3443.4 | 1222.5 | 0.6548 | 4.174
2024-12-10 | 2:55 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.261 | 2210.77 | 25.71 | 54.575 | 6.48 | 1.124 | 3.046 | 7527.25 | 0.918 | 97.5 | 73 | 1437 | 27.29 | 4892.7 | 2309.2 | 2362.5 | 3453.5 | 1222.5 | 0.65133 | 4.17
2024-12-10 | 2:55 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.306 | 2211.68 | 25.7 | 54.485 | 6.48 | 1.127 | 3.054 | 7554.38 | 0.918 | 97.5 | 73 | 1438 | 27.24 | 4910.3 | 2312.6 | 2352.7 | 3446.3 | 1222.5 | 0.6557 | 4.18
2024-12-10 | 2:55 | Data | 0 | 35.512 | 34.567 | 121.992 | 7.64 | 116.306 | 2210.77 | 25.71 | 54.575 | 6.48 | 1.126 | 3.036 | 7558.9 | 0.81 | 97.5 | 72.9 | 1438 | 27.29 | 4913.3 | 2314.9 | 2335.8 | 3436.2 | 1222.5 | 0.65775 | 4.162
2024-12-10 | 2:55 | Data | 0 | 35.66 | 34.621 | 122.037 | 7.64 | 116.351 | 2208.97 | 25.71 | 54.485 | 6.48 | 1.124 | 3.037 | 7563.42 | 1.087 | 97.5 | 73 | 1436 | 27.24 | 4916.2 | 2317.6 | 2341.8 | 3444.7 | 1222.5 | 0.65497 | 4.161
2024-12-10 | 2:55 | Data | 0 | 35.512 | 34.452 | 122.083 | 7.64 | 116.351 | 2208.06 | 25.71 | 54.575 | 6.48 | 1.124 | 3.051 | 7572.47 | 1.033 | 97.5 | 73.1 | 1435 | 27.29 | 4922.1 | 2290.4 | 2352.6 | 3433.6 | 1222.5 | 0.65033 | 4.175
2024-12-10 | 2:55 | Data | 0 | 35.667 | 34.796 | 122.083 | 7.64 | 116.351 | 2204.45 | 25.71 | 54.485 | 6.48 | 1.124 | 3.04 | 7567.95 | 0.911 | 97.5 | 73 | 1433 | 27.24 | 4919.2 | 2304.4 | 2357.6 | 3447.5 | 1222.5 | 0.65344 | 4.163
2024-12-10 | 2:55 | Data | 0 | 35.721 | 34.796 | 122.083 | 7.65 | 116.351 | 2208.06 | 25.71 | 54.575 | 6.48 | 1.135 | 3.05 | 7563.42 | 0.716 | 97.5 | 72.9 | 1436 | 27.29 | 4916.2 | 2309.4 | 2345.2 | 3445.5 | 1222.5 | 0.65539 | 4.185
2024-12-10 | 2:55 | Data | 0 | 35.289 | 34.567 | 121.947 | 7.64 | 116.306 | 2208.97 | 25.71 | 54.575 | 6.48 | 1.134 | 3.051 | 7563.42 | 0.695 | 97.5 | 72.9 | 1436 | 27.29 | 4916.2 | 2310.9 | 2365.1 | 3455.6 | 1222.5 | 0.65379 | 4.185
2024-12-10 | 2:55 | Data | 0 | 35.714 | 34.573 | 121.947 | 7.64 | 116.396 | 2211.68 | 25.7 | 54.575 | 6.48 | 1.124 | 3.054 | 7549.86 | 0.749 | 97.5 | 73.1 | 1437 | 27.29 | 4907.4 | 2300.9 | 2355.1 | 3441.8 | 1222.5 | 0.65119 | 4.178
2024-12-10 | 2:55 | Data | 0 | 35.37 | 34.567 | 121.947 | 7.64 | 116.306 | 2210.77 | 25.71 | 54.485 | 6.48 | 1.124 | 3.058 | 7549.86 | 0.716 | 97.5 | 73.1 | 1438 | 27.24 | 4907.4 | 2314 | 2352.9 | 3443.4 | 1222.5 | 0.65423 | 4.182
2024-12-10 | 2:55 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.65 | 116.351 | 2210.77 | 25.74 | 54.575 | 6.48 | 1.125 | 3.062 | 7531.77 | 0.918 | 97.5 | 73.1 | 1437 | 27.24 | 4895.6 | 2308.6 | 2328.8 | 3434.5 | 1222.5 | 0.65543 | 4.187
2024-12-10 | 2:55 | Data | 0 | 35.262 | 34.621 | 122.037 | 7.64 | 116.306 | 2210.77 | 25.72 | 54.485 | 6.48 | 1.126 | 3.059 | 7536.29 | 0.911 | 97.5 | 73.1 | 1437 | 27.29 | 4898.6 | 2274.8 | 2361.9 | 3426.2 | 1222.5 | 0.64539 | 4.184
2024-12-10 | 2:55 | Data | 0 | 35.485 | 34.567 | 121.947 | 7.64 | 116.306 | 2208.06 | 25.71 | 54.575 | 6.48 | 1.115 | 3.043 | 7536.29 | 0.918 | 97.5 | 73.2 | 1436 | 27.29 | 4898.6 | 2315.1 | 2353.8 | 3442.4 | 1222.5 | 0.65959 | 4.159
2024-12-10 | 2:55 | Data | 0 | 35.485 | 34.627 | 122.037 | 7.64 | 116.351 | 2211.68 | 25.71 | 54.485 | 6.48 | 1.122 | 3.043 | 7531.77 | 0.918 | 97.5 | 73.1 | 1438 | 27.24 | 4895.6 | 2299.9 | 2332.1 | 3424.4 | 1222.5 | 0.65472 | 4.165
2024-12-10 | 2:55 | Data | 0 | 35.6 | 34.776 | 122.083 | 7.64 | 116.306 | 2211.68 | 25.71 | 54.485 | 6.48 | 1.13 | 3.046 | 7518.2 | 0.837 | 97.5 | 72.9 | 1437 | 27.24 | 4886.8 | 2303.8 | 2371.5 | 3456.3 | 1222.5 | 0.65193 | 4.177
2024-12-10 | 2:56 | Data | 0 | 35.512 | 34.567 | 121.947 | 7.64 | 116.306 | 2213.49 | 25.72 | 54.485 | 6.48 | 1.13 | 3.05 | 7522.72 | 0.925 | 97.5 | 73 | 1439 | 27.24 | 4889.8 | 2304.6 | 2358.9 | 3446.9 | 1222.5 | 0.65088 | 4.18
2024-12-10 | 2:56 | Data | 0 | 35.6 | 34.573 | 121.992 | 7.64 | 116.351 | 2211.68 | 25.72 | 54.575 | 6.48 | 1.131 | 3.055 | 7513.68 | 0.918 | 97.5 | 73 | 1438 | 27.29 | 4883.9 | 2307.7 | 2345.9 | 3439.7 | 1222.5 | 0.65697 | 4.188
2024-12-10 | 2:56 | Data | 0 | 35.654 | 34.796 | 122.083 | 7.64 | 116.351 | 2213.49 | 25.71 | 54.575 | 6.48 | 1.128 | 3.05 | 7518.2 | 1.026 | 97.5 | 73 | 1439 | 27.24 | 4886.8 | 2302.2 | 2351.2 | 3442 | 1222.5 | 0.65262 | 4.178
2024-12-10 | 2:56 | Data | 0 | 35.714 | 34.621 | 122.083 | 7.64 | 116.441 | 2208.06 | 25.71 | 54.485 | 6.48 | 1.119 | 3.058 | 7509.16 | 0.918 | 97.5 | 73.2 | 1436 | 27.29 | 4881 | 2298.9 | 2359.5 | 3445 | 1222.5 | 0.65165 | 4.177
2024-12-10 | 2:56 | Data | 0 | 35.687 | 34.769 | 121.992 | 7.64 | 116.351 | 2210.77 | 25.72 | 54.485 | 6.48 | 1.124 | 3.058 | 7509.16 | 0.959 | 97.5 | 73.1 | 1437 | 27.24 | 4881 | 2298.2 | 2359.2 | 3441.3 | 1222.5 | 0.65244 | 4.181
2024-12-10 | 2:56 | Data | 0 | 35.6 | 34.567 | 122.083 | 7.64 | 116.351 | 2210.77 | 25.73 | 54.575 | 6.49 | 1.127 | 3.055 | 7504.64 | 0.932 | 97.5 | 73.1 | 1437 | 27.29 | 4878 | 2307.8 | 2335.9 | 3436 | 1222.5 | 0.65467 | 4.182
2024-12-10 | 2:56 | Data | 0 | 35.539 | 34.573 | 122.083 | 7.64 | 116.396 | 2211.68 | 25.71 | 54.575 | 6.48 | 1.122 | 3.051 | 7518.2 | 0.891 | 97.5 | 73.1 | 1437 | 27.29 | 4886.8 | 2293.7 | 2362.5 | 3441.3 | 1222.5 | 0.64914 | 4.173
2024-12-10 | 2:56 | Data | 0 | 35.593 | 34.769 | 121.992 | 7.64 | 116.351 | 2210.77 | 25.7 | 54.575 | 6.47 | 1.12 | 3.059 | 7504.64 | 0.77 | 97.5 | 73.2 | 1437 | 27.24 | 4878 | 2293.7 | 2358.9 | 3446.9 | 1222.5 | 0.65709 | 4.178
2024-12-10 | 2:56 | Data | 0 | 35.269 | 34.567 | 122.083 | 7.64 | 116.396 | 2210.77 | 25.73 | 54.485 | 6.48 | 1.117 | 3.053 | 7518.2 | 0.891 | 97.5 | 73.2 | 1437 | 27.24 | 4886.8 | 2313.7 | 2336.2 | 3436.7 | 1222.5 | 0.65485 | 4.17
2024-12-10 | 2:56 | Data | 0 | 35.485 | 34.675 | 122.037 | 7.64 | 116.396 | 2213.49 | 25.73 | 54.575 | 6.48 | 1.126 | 3.037 | 7504.64 | 0.702 | 97.5 | 72.9 | 1439 | 27.24 | 4878 | 2289.2 | 2339.6 | 3424.8 | 1222.5 | 0.65236 | 4.164
2024-12-10 | 2:56 | Data | 0 | 35.6 | 34.783 | 122.037 | 7.64 | 116.351 | 2213.49 | 25.73 | 54.485 | 6.48 | 1.125 | 3.025 | 7513.68 | 0.932 | 97.5 | 72.9 | 1439 | 27.24 | 4883.9 | 2310.1 | 2348 | 3445.1 | 1222.6 | 0.65494 | 4.15
2024-12-10 | 2:56 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.351 | 2213.49 | 25.71 | 54.485 | 6.48 | 1.126 | 3.053 | 7549.86 | 0.918 | 97.5 | 73.1 | 1439 | 27.24 | 4907.4 | 2325.2 | 2351.8 | 3449.1 | 1222.6 | 0.65981 | 4.179
2024-12-10 | 2:56 | Data | 0 | 35.701 | 34.796 | 122.128 | 7.64 | 116.441 | 2214.39 | 25.73 | 54.575 | 6.48 | 1.13 | 3.035 | 7518.2 | 0.925 | 97.5 | 72.9 | 1439 | 27.24 | 4886.8 | 2290.9 | 2349.8 | 3431.6 | 1222.6 | 0.65198 | 4.165
2024-12-10 | 2:56 | Data | 0 | 35.512 | 34.783 | 122.128 | 7.64 | 116.441 | 2213.49 | 25.72 | 54.575 | 6.48 | 1.121 | 3.043 | 7531.77 | 0.749 | 97.5 | 73.1 | 1439 | 27.29 | 4895.6 | 1212 | 1675.1 | 2089.7 | 1222.6 | 0.5784 | 4.162
2024-12-10 | 2:56 | Data | 0 | 35.714 | 34.573 | 122.128 | 7.64 | 116.351 | 2211.68 | 25.72 | 54.575 | 6.48 | 1.128 | 3.041 | 7536.29 | 0.898 | 97.5 | 72.9 | 1438 | 27.29 | 4898.6 | 1226 | 1697.8 | 2115.6 | 1222.6 | 0.58094 | 4.168
2024-12-10 | 2:56 | Data | 0 | 35.491 | 34.796 | 122.037 | 7.64 | 116.351 | 2211.68 | 25.72 | 54.485 | 6.48 | 1.125 | 3.044 | 7531.77 | 0.803 | 97.5 | 73 | 1438 | 27.29 | 4895.6 | 1229.8 | 1687.2 | 2105.7 | 1222.6 | 0.58364 | 4.168
2024-12-10 | 2:56 | Data | 0 | 35.687 | 34.621 | 122.083 | 7.64 | 116.396 | 2210.77 | 25.71 | 54.485 | 6.48 | 1.118 | 3.04 | 7558.9 | 0.918 | 97.5 | 73.1 | 1436 | 27.24 | 4913.3 | 1207 | 1703 | 2107.1 | 1222.6 | 0.57344 | 4.158
2024-12-10 | 2:56 | Data | 0 | 35.6 | 34.573 | 122.037 | 7.64 | 116.396 | 2213.49 | 25.71 | 54.485 | 6.48 | 1.121 | 3.042 | 7572.47 | 0.938 | 97.5 | 73.1 | 1439 | 27.24 | 4922.1 | 1219.5 | 1721.5 | 2141.8 | 1222.6 | 0.57151 | 4.162
2024-12-10 | 2:57 | Data | 0 | 35.485 | 34.783 | 122.037 | 7.64 | 116.396 | 2208.06 | 25.71 | 54.575 | 6.48 | 1.125 | 3.057 | 7563.42 | 0.83 | 97.5 | 73.1 | 1436 | 27.29 | 4916.2 | 1231.8 | 1707.8 | 2123 | 1222.6 | 0.58015 | 4.182
2024-12-10 | 2:57 | Data | 0 | 35.6 | 34.789 | 121.992 | 7.64 | 116.306 | 2211.68 | 25.71 | 54.485 | 6.48 | 1.121 | 3.042 | 7567.95 | 0.905 | 97.5 | 73.1 | 1438 | 27.29 | 4919.2 | 1229.8 | 1694.3 | 2111.5 | 1222.6 | 0.5798 | 4.163
2024-12-10 | 2:57 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2208.06 | 25.71 | 54.575 | 6.48 | 1.128 | 3.036 | 7558.9 | 0.918 | 97.5 | 72.9 | 1435 | 27.29 | 4913.3 | 1222.2 | 1704.1 | 2115 | 1222.6 | 0.57732 | 4.163
2024-12-10 | 2:57 | Data | 0 | 35.485 | 34.783 | 122.128 | 7.64 | 116.396 | 2208.97 | 25.71 | 54.485 | 6.48 | 1.131 | 3.056 | 7563.42 | 0.743 | 97.5 | 73 | 1436 | 27.24 | 4916.2 | 1224.6 | 1708.8 | 2120.3 | 1222.6 | 0.57682 | 4.187
2024-12-10 | 2:57 | Data | 0 | 35.498 | 34.742 | 122.128 | 7.64 | 116.351 | 2206.25 | 25.71 | 54.485 | 6.48 | 1.13 | 3.04 | 7572.47 | 0.857 | 97.5 | 72.9 | 1435 | 27.24 | 4922.1 | 1226.2 | 1696.8 | 2113.3 | 1222.6 | 0.57942 | 4.17
2024-12-10 | 2:57 | Data | 0 | 35.491 | 34.567 | 121.992 | 7.64 | 116.351 | 2210.77 | 25.71 | 54.575 | 6.48 | 1.121 | 3.048 | 7558.9 | 0.918 | 97.5 | 73.1 | 1437 | 27.29 | 4913.3 | 1223.4 | 1691.3 | 2103.5 | 1222.6 | 0.5784 | 4.171
2024-12-10 | 2:57 | Data | 0 | 35.485 | 34.742 | 121.992 | 7.64 | 116.351 | 2211.68 | 25.72 | 54.575 | 6.48 | 1.112 | 3.048 | 7558.9 | 0.743 | 97.5 | 73.3 | 1437 | 27.29 | 4913.3 | 1229.7 | 1704.9 | 2122.3 | 1222.6 | 0.57845 | 4.161
2024-12-10 | 2:57 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.306 | 2211.68 | 25.71 | 54.575 | 6.47 | 1.113 | 3.035 | 7554.38 | 0.918 | 97.5 | 73.2 | 1438 | 27.29 | 4910.3 | 1234.2 | 1694.9 | 2115.4 | 1222.6 | 0.58313 | 4.148
2024-12-10 | 2:57 | Data | 0 | 35.491 | 34.567 | 122.037 | 7.64 | 116.351 | 2210.77 | 25.71 | 54.575 | 6.48 | 1.117 | 3.044 | 7549.86 | 0.918 | 97.5 | 73.2 | 1437 | 27.29 | 4907.4 | 1218.8 | 1702.7 | 2115.1 | 1222.6 | 0.57571 | 4.161
2024-12-10 | 2:57 | Data | 0 | 35.66 | 34.567 | 122.037 | 7.64 | 116.351 | 2211.68 | 25.71 | 54.485 | 6.48 | 1.129 | 3.051 | 7558.9 | 0.932 | 97.5 | 73 | 1438 | 27.24 | 4913.3 | 1226.7 | 1702.2 | 2117.9 | 1222.6 | 0.5777 | 4.179
2024-12-10 | 2:57 | Data | 0 | 35.329 | 34.567 | 122.083 | 7.64 | 116.396 | 2210.77 | 25.71 | 54.575 | 6.48 | 1.121 | 3.057 | 7549.86 | 0.709 | 97.5 | 73.2 | 1437 | 27.29 | 4907.4 | 1212.1 | 1668.5 | 2081.7 | 1222.6 | 0.58089 | 4.179
2024-12-10 | 2:57 | Data | 0 | 35.485 | 34.783 | 122.037 | 7.64 | 116.351 | 2211.68 | 25.71 | 54.485 | 6.48 | 1.125 | 3.051 | 7531.77 | 0.803 | 97.5 | 73.1 | 1438 | 27.29 | 4895.6 | 1229.4 | 1711.3 | 2125.9 | 1222.6 | 0.57737 | 4.176
2024-12-10 | 2:57 | Data | 0 | 35.924 | 34.695 | 122.128 | 7.64 | 116.487 | 2211.68 | 25.7 | 54.485 | 6.48 | 1.126 | 3.03 | 7531.77 | 0.972 | 97.5 | 72.9 | 1438 | 27.29 | 4895.6 | 1229.7 | 1703.9 | 2120.8 | 1222.6 | 0.57806 | 4.157
2024-12-10 | 2:57 | Data | 0 | 35.485 | 34.742 | 121.992 | 7.64 | 116.351 | 2211.68 | 25.71 | 54.575 | 6.48 | 1.127 | 3.047 | 7531.77 | 0.918 | 97.5 | 73 | 1437 | 27.29 | 4895.6 | 1211.9 | 1687.6 | 2095.5 | 1222.6 | 0.57443 | 4.175
2024-12-10 | 2:57 | Data | 0 | 35.687 | 34.796 | 122.083 | 7.64 | 116.396 | 2210.77 | 25.71 | 54.575 | 6.48 | 1.12 | 3.042 | 7531.77 | 0.911 | 97.5 | 73.1 | 1437 | 27.24 | 4895.6 | 1238.1 | 1707.4 | 2120.8 | 1222.6 | 0.57982 | 4.161
2024-12-10 | 2:57 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2210.77 | 25.72 | 54.575 | 6.48 | 1.121 | 3.034 | 7549.86 | 0.945 | 97.5 | 73 | 1437 | 27.29 | 4907.4 | 1215.6 | 1694.7 | 2104.7 | 1222.6 | 0.57506 | 4.153
2024-12-10 | 2:57 | Data | 0 | 35.485 | 34.398 | 122.037 | 7.64 | 116.351 | 2218.91 | 25.72 | 54.575 | 6.48 | 1.121 | 3.039 | 7536.29 | 1.033 | 97.5 | 73 | 1442 | 27.29 | 4898.6 | 1223.7 | 1689.7 | 2105.2 | 1222.6 | 0.57946 | 4.161
2024-12-10 | 2:57 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2218 | 25.71 | 54.575 | 6.48 | 1.13 | 3.027 | 7536.29 | 0.905 | 97.5 | 72.8 | 1442 | 27.29 | 4898.6 | 1223.2 | 1703.5 | 2111.1 | 1222.6 | 0.57974 | 4.157
2024-12-10 | 2:58 | Data | 0 | 35.66 | 34.789 | 122.037 | 7.64 | 116.306 | 2213.49 | 25.71 | 54.485 | 6.48 | 1.121 | 3.035 | 7934.25 | 0.911 | 97.5 | 73 | 1439 | 27.29 | 5157.3 | 1218.4 | 1693.8 | 2106.5 | 1222.6 | 0.57633 | 4.157
2024-12-10 | 2:58 | Data | 0 | 35.539 | 34.668 | 122.037 | 7.64 | 116.351 | 2211.68 | 25.71 | 54.485 | 6.48 | 1.118 | 3.052 | 7536.29 | 0.824 | 97.5 | 73.2 | 1437 | 27.29 | 4898.6 | 1222.2 | 1690.7 | 2103.7 | 1222.6 | 0.58177 | 4.17
2024-12-10 | 2:58 | Data | 0 | 35.66 | 34.594 | 121.992 | 7.64 | 116.396 | 2208.97 | 25.71 | 54.214 | 6.48 | 1.119 | 3.026 | 7536.29 | 0.918 | 97.5 | 73 | 1436 | 27.15 | 4898.6 | 1239.6 | 1700.8 | 2123.4 | 1222.6 | 0.58358 | 4.145
2024-12-10 | 2:58 | Data | 0 | 35.546 | 34.567 | 121.947 | 7.64 | 116.306 | 2214.39 | 25.71 | 54.485 | 6.48 | 1.121 | 3.035 | 7549.86 | 0.925 | 97.5 | 73 | 1439 | 27.29 | 4907.4 | 1228.9 | 1701 | 2115.6 | 1222.6 | 0.58261 | 4.155
2024-12-10 | 2:58 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.351 | 2210.77 | 25.71 | 54.575 | 6.47 | 1.124 | 3.045 | 7527.25 | 0.918 | 97.5 | 73 | 1437 | 27.24 | 4892.7 | 1234.2 | 1699.5 | 2123.8 | 1222.6 | 0.57871 | 4.17
2024-12-10 | 2:58 | Data | 0 | 35.262 | 34.567 | 121.992 | 7.64 | 116.306 | 2213.49 | 25.71 | 54.575 | 6.48 | 1.119 | 3.038 | 7536.29 | 0.81 | 97.5 | 73.1 | 1439 | 27.29 | 4898.6 | 1230.7 | 1688.7 | 2106.8 | 1222.6 | 0.58395 | 4.156
2024-12-10 | 2:58 | Data | 0 | 35.485 | 34.398 | 121.947 | 7.64 | 116.351 | 2214.39 | 25.71 | 54.485 | 6.48 | 1.117 | 3.039 | 7549.86 | 1.033 | 97.5 | 73.1 | 1439 | 27.24 | 4907.4 | 1227.8 | 1699.8 | 2103.4 | 1222.6 | 0.58164 | 4.155
2024-12-10 | 2:58 | Data | 0 | 35.485 | 34.567 | 121.947 | 7.64 | 116.261 | 2216.2 | 25.71 | 54.485 | 6.48 | 1.121 | 3.039 | 7536.29 | 0.918 | 97.5 | 73.1 | 1441 | 27.29 | 4898.6 | 1207 | 1699.7 | 2105.5 | 1222.6 | 0.57109 | 4.159
2024-12-10 | 2:58 | Data | 0 | 35.586 | 34.654 | 122.083 | 7.64 | 116.351 | 2218.91 | 25.71 | 54.575 | 6.48 | 1.132 | 3.048 | 7531.77 | 0.756 | 97.5 | 72.9 | 1442 | 27.29 | 4895.6 | 1215.3 | 1709.6 | 2118.3 | 1222.6 | 0.57135 | 4.182
2024-12-10 | 2:58 | Data | 0 | 35.485 | 34.567 | 121.902 | 7.64 | 116.351 | 2222.52 | 25.71 | 54.575 | 6.48 | 1.126 | 3.036 | 7518.2 | 0.918 | 97.5 | 73 | 1445 | 27.24 | 4886.8 | 1210.6 | 1689.6 | 2099.6 | 1222.6 | 0.57478 | 4.161
2024-12-10 | 2:58 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.306 | 2225.23 | 25.71 | 54.485 | 6.47 | 1.13 | 3.027 | 7518.2 | 0.918 | 97.5 | 72.8 | 1446 | 27.29 | 4886.8 | 1231.6 | 1713.3 | 2128.4 | 1222.6 | 0.57789 | 4.158
2024-12-10 | 2:58 | Data | 0 | 35.498 | 34.567 | 121.992 | 7.64 | 116.441 | 2227.95 | 25.71 | 54.575 | 6.48 | 1.128 | 3.028 | 7518.2 | 0.722 | 97.6 | 72.9 | 1448 | 27.29 | 4886.8 | 1216 | 1696 | 2104.4 | 1222.6 | 0.57725 | 4.156
2024-12-10 | 2:58 | Data | 0 | 35.485 | 34.58 | 122.083 | 7.64 | 116.306 | 2227.04 | 25.71 | 54.485 | 6.48 | 1.118 | 3.038 | 7518.2 | 0.891 | 97.6 | 73.1 | 1448 | 27.24 | 4886.8 | 1224.7 | 1718.5 | 2127.3 | 1222.6 | 0.57523 | 4.157
2024-12-10 | 2:58 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.351 | 2225.23 | 25.71 | 54.575 | 6.48 | 1.112 | 3.034 | 7518.2 | 0.918 | 97.6 | 73.2 | 1446 | 27.24 | 4886.8 | 1238 | 1704 | 2120.7 | 1222.6 | 0.57897 | 4.146
2024-12-10 | 2:58 | Data | 0 | 35.532 | 34.567 | 121.992 | 7.64 | 116.306 | 2225.23 | 25.71 | 54.575 | 6.48 | 1.121 | 3.042 | 7518.2 | 0.817 | 97.6 | 73 | 1446 | 27.24 | 4886.8 | 1219.6 | 1711.4 | 2117.8 | 1222.6 | 0.57595 | 4.164
2024-12-10 | 2:58 | Data | 0 | 35.397 | 34.567 | 121.992 | 7.64 | 116.351 | 2225.23 | 25.71 | 54.575 | 6.48 | 1.136 | 3.034 | 7513.68 | 0.722 | 97.5 | 72.8 | 1446 | 27.24 | 4883.9 | 1216.6 | 1697.4 | 2106.1 | 1222.6 | 0.57663 | 4.17
2024-12-10 | 2:58 | Data | 0 | 35.654 | 34.789 | 122.173 | 7.64 | 116.396 | 2225.23 | 25.71 | 54.485 | 6.48 | 1.121 | 3.035 | 7504.64 | 0.918 | 97.5 | 73 | 1446 | 27.24 | 4878 | 1233.6 | 1724.7 | 2136.2 | 1222.6 | 0.57951 | 4.156
2024-12-10 | 2:58 | Data | 0 | 35.512 | 34.573 | 122.037 | 7.64 | 116.351 | 2222.52 | 25.72 | 54.575 | 6.48 | 1.122 | 3.026 | 7518.2 | 0.857 | 97.5 | 73 | 1445 | 27.24 | 4886.8 | 1231.8 | 1700.6 | 2117.7 | 1222.6 | 0.58111 | 4.148
2024-12-10 | 2:59 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2226.14 | 25.71 | 54.575 | 6.48 | 1.124 | 3.052 | 7518.2 | 0.918 | 97.6 | 73.1 | 1447 | 27.24 | 4886.8 | 1203.7 | 1699.3 | 2118.4 | 1222.6 | 0.57656 | 4.176
2024-12-10 | 2:59 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.351 | 2226.14 | 25.71 | 54.485 | 6.48 | 1.122 | 3.045 | 7518.2 | 0.918 | 97.6 | 73.1 | 1446 | 27.24 | 4886.8 | 1234.5 | 1712.6 | 2129.1 | 1222.6 | 0.58011 | 4.166
2024-12-10 | 2:59 | Data | 0 | 35.431 | 34.567 | 121.992 | 7.64 | 116.306 | 2225.23 | 25.71 | 54.575 | 6.48 | 1.13 | 3.056 | 7536.29 | 0.911 | 97.6 | 73 | 1446 | 27.24 | 4898.6 | 1229.6 | 1697.1 | 2115.2 | 1222.6 | 0.58061 | 4.186
2024-12-10 | 2:59 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.306 | 2226.14 | 25.71 | 54.575 | 6.48 | 1.125 | 3.053 | 7531.77 | 0.918 | 97.5 | 73.1 | 1448 | 27.29 | 4895.6 | 1217.4 | 1715.5 | 2121.7 | 1222.6 | 0.57305 | 4.178
2024-12-10 | 2:59 | Data | 0 | 35.485 | 34.567 | 121.947 | 7.64 | 116.261 | 2227.95 | 25.71 | 54.575 | 6.48 | 1.122 | 3.034 | 7531.77 | 0.918 | 97.6 | 73 | 1449 | 27.29 | 4895.6 | 1208.8 | 1717.5 | 2118.4 | 1222.6 | 0.56991 | 4.156
2024-12-10 | 2:59 | Data | 0 | 35.431 | 34.668 | 121.992 | 7.64 | 116.306 | 2227.95 | 25.71 | 54.575 | 6.48 | 1.122 | 3.035 | 7518.2 | 0.891 | 97.6 | 73 | 1448 | 27.29 | 4886.8 | 1223.8 | 1701.7 | 2117.1 | 1222.6 | 0.58674 | 4.159
2024-12-10 | 2:59 | Data | 0 | 35.323 | 34.567 | 121.992 | 7.64 | 116.351 | 2230.66 | 25.71 | 54.485 | 6.48 | 1.12 | 3.056 | 7531.77 | 0.878 | 97.6 | 73.2 | 1450 | 27.29 | 4895.6 | 1227.9 | 1711.4 | 2123.6 | 1222.6 | 0.57698 | 4.176
2024-12-10 | 2:59 | Data | 0 | 35.687 | 34.58 | 122.083 | 7.64 | 116.396 | 2228.85 | 25.71 | 54.394 | 6.48 | 1.121 | 3.063 | 7513.68 | 1.114 | 97.6 | 73.2 | 1448 | 27.24 | 4883.9 | 1234.7 | 1717.9 | 2133.9 | 1222.6 | 0.57671 | 4.185
2024-12-10 | 2:59 | Data | 0 | 35.262 | 34.567 | 121.992 | 7.64 | 116.306 | 2227.04 | 25.71 | 54.575 | 6.48 | 1.126 | 3.071 | 7531.77 | 1.006 | 97.5 | 73.2 | 1448 | 27.29 | 4895.6 | 1222.5 | 1718.1 | 2128.1 | 1222.6 | 0.57352 | 4.197
2024-12-10 | 2:59 | Data | 0 | 35.6 | 34.398 | 121.992 | 7.64 | 116.351 | 2229.75 | 25.71 | 54.485 | 6.48 | 1.117 | 3.051 | 7531.77 | 0.884 | 97.6 | 73.2 | 1450 | 27.24 | 4895.6 | 1211.2 | 1718.7 | 2120.4 | 1222.6 | 0.57083 | 4.169
2024-12-10 | 2:59 | Data | 0 | 35.397 | 34.513 | 121.992 | 7.64 | 116.396 | 2230.66 | 25.7 | 54.485 | 6.48 | 1.121 | 3.042 | 7531.77 | 0.83 | 97.6 | 73.1 | 1450 | 27.29 | 4895.6 | 1223.3 | 1726.9 | 2135 | 1222.6 | 0.57241 | 4.162
2024-12-10 | 2:59 | Data | 0 | 35.478 | 34.567 | 122.037 | 7.64 | 116.306 | 2230.66 | 25.71 | 54.575 | 6.48 | 1.116 | 3.031 | 7902.59 | 0.803 | 97.5 | 73.1 | 1450 | 27.29 | 5136.7 | 1227.7 | 1724.9 | 2134.8 | 1222.6 | 0.57358 | 4.147
2024-12-10 | 2:59 | Data | 0 | 35.431 | 34.567 | 121.902 | 7.64 | 116.306 | 2227.95 | 25.71 | 54.485 | 6.48 | 1.116 | 3.054 | 7898.07 | 0.891 | 97.6 | 73.2 | 1448 | 27.29 | 5133.7 | 1252.9 | 1717.2 | 2142.5 | 1222.6 | 0.58392 | 4.171
2024-12-10 | 2:59 | Data | 0 | 35.485 | 34.58 | 121.947 | 7.64 | 116.351 | 2225.23 | 25.72 | 54.575 | 6.48 | 1.13 | 3.038 | 7879.98 | 0.864 | 97.5 | 72.9 | 1446 | 27.29 | 5122 | 1229 | 1728 | 2138.2 | 1222.6 | 0.57435 | 4.168
2024-12-10 | 2:59 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2225.23 | 25.71 | 54.485 | 6.48 | 1.121 | 3.034 | 7518.2 | 0.918 | 97.6 | 73 | 1446 | 27.24 | 4886.8 | 1242.8 | 1749.1 | 2162.2 | 1222.6 | 0.57372 | 4.155
2024-12-10 | 2:59 | Data | 0 | 35.458 | 34.789 | 122.037 | 7.64 | 116.306 | 2211.68 | 25.71 | 54.485 | 6.48 | 1.12 | 3.022 | 7522.72 | 0.891 | 97.5 | 73 | 1437 | 27.29 | 4889.8 | 1234.9 | 1712.7 | 2130.1 | 1222.6 | 0.5781 | 4.142
2024-12-10 | 2:59 | Data | 0 | 35.471 | 34.567 | 121.992 | 7.64 | 116.351 | 2221.62 | 25.71 | 54.485 | 6.48 | 1.121 | 3.026 | 7518.2 | 0.918 | 97.5 | 73 | 1445 | 27.24 | 4886.8 | 1242.8 | 1708.7 | 2125.4 | 1222.6 | 0.58132 | 4.147
2024-12-10 | 3:00 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.306 | 2222.52 | 25.71 | 54.575 | 6.48 | 1.122 | 3.02 | 7518.2 | 0.918 | 97.5 | 72.9 | 1445 | 27.24 | 4886.8 | 1222.3 | 1712.3 | 2126.4 | 1222.6 | 0.57823 | 4.142
2024-12-10 | 3:00 | Data | 0 | 35.498 | 34.351 | 122.037 | 7.64 | 116.351 | 2218.91 | 25.71 | 54.575 | 6.48 | 1.124 | 3.017 | 7522.72 | 0.945 | 97.5 | 72.8 | 1442 | 27.29 | 4889.8 | 1216.2 | 1706.5 | 2121.7 | 1222.6 | 0.57766 | 4.142
2024-12-10 | 3:00 | Data | 0 | 35.485 | 34.567 | 121.947 | 7.64 | 116.351 | 2218.91 | 25.72 | 54.575 | 6.48 | 1.124 | 3.035 | 7518.2 | 0.918 | 97.5 | 73 | 1442 | 27.24 | 4886.8 | 1207.9 | 1722.4 | 2126.7 | 1222.6 | 0.56729 | 4.159
2024-12-10 | 3:00 | Data | 0 | 35.485 | 34.567 | 121.947 | 7.64 | 116.306 | 2222.52 | 25.71 | 54.575 | 6.47 | 1.119 | 3.054 | 7504.64 | 0.918 | 97.5 | 73.2 | 1444 | 27.24 | 4878 | 1210.8 | 1736.9 | 2140.2 | 1222.6 | 0.56386 | 4.172
2024-12-10 | 3:00 | Data | 0 | 35.485 | 34.479 | 121.947 | 7.64 | 116.306 | 2218.91 | 25.71 | 54.485 | 6.48 | 1.121 | 3.047 | 7518.2 | 1.033 | 97.5 | 73.1 | 1442 | 27.29 | 4886.8 | 1206 | 1736.3 | 2135.7 | 1222.6 | 0.56725 | 4.169
2024-12-10 | 3:00 | Data | 0 | 35.262 | 34.344 | 121.856 | 7.64 | 116.261 | 2215.29 | 25.71 | 54.665 | 6.48 | 1.115 | 3.035 | 7509.16 | 0.891 | 97.5 | 73.1 | 1441 | 27.24 | 4881 | 1227.5 | 1731.4 | 2143.7 | 1222.6 | 0.57081 | 4.151
2024-12-10 | 3:00 | Data | 0 | 35.255 | 34.344 | 121.856 | 7.64 | 116.261 | 2222.52 | 25.71 | 54.575 | 6.47 | 1.119 | 3.034 | 7504.64 | 1.094 | 97.5 | 73.1 | 1444 | 27.24 | 4878 | 1223.6 | 1734.8 | 2134 | 1222.6 | 0.56963 | 4.152
2024-12-10 | 3:00 | Data | 0 | 35.262 | 34.452 | 121.947 | 7.64 | 116.215 | 2222.52 | 25.71 | 54.575 | 6.48 | 1.121 | 3.054 | 7504.64 | 0.918 | 97.5 | 73.2 | 1445 | 27.24 | 4878 | 1220.1 | 1712.9 | 2123.8 | 1222.6 | 0.57183 | 4.175
2024-12-10 | 3:00 | Data | 0 | 35.485 | 34.567 | 121.947 | 7.64 | 116.261 | 2222.52 | 25.71 | 54.485 | 6.48 | 1.126 | 3.038 | 7509.16 | 0.918 | 97.5 | 73 | 1444 | 27.24 | 4881 | 1220 | 1707.2 | 2112.6 | 1222.6 | 0.57123 | 4.163
2024-12-10 | 3:00 | Data | 0 | 35.458 | 34.567 | 121.947 | 7.64 | 116.306 | 2222.52 | 25.71 | 54.575 | 6.48 | 1.122 | 3.035 | 7500.11 | 0.918 | 97.5 | 73 | 1445 | 27.24 | 4875.1 | 1223.5 | 1722.3 | 2133.1 | 1222.6 | 0.57245 | 4.158
2024-12-10 | 3:00 | Data | 0 | 35.485 | 34.364 | 121.856 | 7.64 | 116.306 | 2224.33 | 25.71 | 54.485 | 6.47 | 1.118 | 3.056 | 7482.02 | 0.918 | 97.5 | 73.2 | 1446 | 27.24 | 4863.3 | 1237.6 | 1738.4 | 2157.6 | 1222.6 | 0.57208 | 4.174
2024-12-10 | 3:00 | Data | 0 | 35.485 | 34.479 | 121.947 | 7.64 | 116.261 | 2224.33 | 25.72 | 54.575 | 6.48 | 1.121 | 3.034 | 7477.5 | 0.979 | 97.5 | 73 | 1446 | 27.29 | 4860.4 | 1227.7 | 1716.7 | 2131.4 | 1222.6 | 0.57642 | 4.155
2024-12-10 | 3:00 | Data | 0 | 35.262 | 34.344 | 121.947 | 7.64 | 116.261 | 2123.1 | 25.71 | 54.485 | 6.47 | 1.122 | 3.05 | 7477.5 | 1.026 | 97.4 | 73.1 | 1379 | 27.29 | 4860.4 | 1233.3 | 1700.3 | 2119.5 | 1222.6 | 0.58167 | 4.172
2024-12-10 | 3:00 | Data | 0 | 35.478 | 34.344 | 121.947 | 7.64 | 116.351 | 2218 | 25.71 | 54.665 | 6.47 | 1.121 | 3.054 | 7482.02 | 1.019 | 97.5 | 73.2 | 1442 | 27.33 | 4863.3 | 1221.7 | 1701.8 | 2114.3 | 1222.6 | 0.57799 | 4.175
2024-12-10 | 3:00 | Data | 0 | 35.269 | 34.337 | 121.947 | 7.64 | 116.261 | 2230.66 | 25.72 | 54.575 | 6.48 | 1.128 | 3.045 | 7477.5 | 0.911 | 97.6 | 73 | 1450 | 27.29 | 4860.4 | 1218.4 | 1697.3 | 2111.2 | 1222.6 | 0.57578 | 4.174
2024-12-10 | 3:00 | Data | 0 | 35.262 | 34.56 | 121.902 | 7.64 | 116.306 | 2227.95 | 25.71 | 54.485 | 6.48 | 1.116 | 3.056 | 7491.07 | 0.871 | 97.6 | 73.3 | 1448 | 27.24 | 4869.2 | 1217.7 | 1716.7 | 2122.4 | 1222.6 | 0.573 | 4.172
2024-12-10 | 3:00 | Data | 0 | 35.356 | 34.553 | 121.992 | 7.64 | 116.215 | 2227.95 | 25.72 | 54.485 | 6.48 | 1.126 | 3.035 | 7495.59 | 0.999 | 97.6 | 72.9 | 1448 | 27.29 | 4872.1 | 1220.9 | 1727.9 | 2132.4 | 1222.6 | 0.57257 | 4.161
2024-12-10 | 3:00 | Data | 0 | 35.431 | 34.567 | 121.947 | 7.64 | 116.261 | 2225.23 | 25.72 | 54.485 | 6.48 | 1.127 | 3.008 | 7495.59 | 0.905 | 97.6 | 72.7 | 1446 | 27.24 | 4872.1 | 1214.9 | 1720.9 | 2124.3 | 1222.6 | 0.57149 | 4.135
2024-12-10 | 3:01 | Data | 0 | 35.37 | 34.513 | 121.992 | 7.64 | 116.261 | 2222.52 | 25.71 | 54.304 | 6.48 | 1.132 | 3.026 | 7491.07 | 1.006 | 97.6 | 72.8 | 1445 | 27.15 | 4869.2 | 1214.1 | 1718.5 | 2122.4 | 1222.6 | 0.57158 | 4.157
2024-12-10 | 3:01 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.261 | 2223.43 | 25.71 | 54.304 | 6.48 | 1.126 | 3.061 | 7468.46 | 0.918 | 97.6 | 73.1 | 1445 | 27.11 | 4854.5 | 1216.1 | 1723.5 | 2127.5 | 1222.6 | 0.57194 | 4.187
2024-12-10 | 3:01 | Data | 0 | 35.485 | 34.391 | 121.992 | 7.64 | 116.261 | 2222.52 | 25.7 | 54.575 | 6.48 | 1.128 | 3.047 | 7133.81 | 1.033 | 97.5 | 73 | 1445 | 27.24 | 4637 | 1218 | 1722 | 2129.9 | 1222.6 | 0.57318 | 4.174
2024-12-10 | 3:01 | Data | 0 | 35.485 | 34.567 | 121.902 | 7.64 | 116.215 | 2221.62 | 25.71 | 54.575 | 6.48 | 1.126 | 3.058 | 7504.64 | 0.743 | 97.5 | 73.1 | 1443 | 27.29 | 4878 | 1221 | 1707.9 | 2120.1 | 1222.6 | 0.57413 | 4.183
2024-12-10 | 3:01 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.306 | 2224.33 | 25.71 | 54.575 | 6.47 | 1.126 | 3.063 | 7504.64 | 0.918 | 97.5 | 73.1 | 1446 | 27.29 | 4878 | 2301.6 | 2399.2 | 3479.3 | 1222.7 | 0.64715 | 4.189
2024-12-10 | 3:01 | Data | 0 | 35.471 | 34.351 | 121.947 | 7.64 | 116.215 | 2218 | 25.71 | 54.485 | 6.48 | 1.12 | 3.036 | 7518.2 | 1.094 | 97.5 | 73.1 | 1441 | 27.24 | 4886.8 | 2312.4 | 2391.3 | 3478.8 | 1222.7 | 0.6465 | 4.157
2024-12-10 | 3:01 | Data | 0 | 35.498 | 34.567 | 121.992 | 7.64 | 116.306 | 2220.72 | 25.71 | 54.485 | 6.47 | 1.126 | 3.02 | 7518.2 | 0.918 | 97.5 | 72.8 | 1443 | 27.24 | 4886.8 | 2288.2 | 2387.2 | 3454.9 | 1222.7 | 0.6473 | 4.146
2024-12-10 | 3:01 | Data | 0 | 35.289 | 34.344 | 121.992 | 7.64 | 116.261 | 2220.72 | 25.71 | 54.304 | 6.48 | 1.126 | 3.039 | 7518.2 | 0.905 | 97.6 | 73 | 1442 | 27.15 | 4886.8 | 2303.9 | 2395.7 | 3474.7 | 1222.7 | 0.64666 | 4.165
2024-12-10 | 3:01 | Data | 0 | 35.309 | 34.553 | 121.947 | 7.64 | 116.261 | 2220.72 | 25.71 | 54.304 | 6.48 | 1.13 | 3.03 | 7522.72 | 0.918 | 97.6 | 72.9 | 1442 | 27.15 | 4889.8 | 2298.6 | 2387.3 | 3465.4 | 1222.7 | 0.64926 | 4.16
2024-12-10 | 3:01 | Data | 0 | 35.262 | 34.513 | 121.947 | 7.64 | 116.261 | 2220.72 | 25.7 | 54.304 | 6.48 | 1.131 | 3.033 | 7527.25 | 0.911 | 97.6 | 72.9 | 1442 | 27.15 | 4892.7 | 2323.5 | 2379.5 | 3471.6 | 1222.7 | 0.65345 | 4.164
2024-12-10 | 3:01 | Data | 0 | 35.431 | 34.567 | 121.947 | 7.64 | 116.215 | 2218 | 25.71 | 54.304 | 6.48 | 1.116 | 3.043 | 7518.2 | 0.918 | 97.6 | 73.2 | 1442 | 27.11 | 4886.8 | 2291.2 | 2380.1 | 3459 | 1222.7 | 0.64417 | 4.159
2024-12-10 | 3:01 | Data | 0 | 35.255 | 34.513 | 121.856 | 7.64 | 116.261 | 2218.91 | 25.72 | 54.214 | 6.48 | 1.118 | 3.037 | 7527.25 | 0.918 | 97.6 | 73.1 | 1442 | 27.06 | 4892.7 | 2306.1 | 2370.7 | 3462.6 | 1222.7 | 0.65018 | 4.155
2024-12-10 | 3:01 | Data | 0 | 35.485 | 34.54 | 121.947 | 7.64 | 116.261 | 2217.1 | 25.71 | 54.033 | 6.47 | 1.126 | 3.042 | 7522.72 | 1.026 | 97.6 | 73 | 1442 | 27.02 | 4889.8 | 2305.4 | 2400.4 | 3479.9 | 1222.7 | 0.64676 | 4.169
2024-12-10 | 3:01 | Data | 0 | 35.255 | 34.513 | 121.902 | 7.65 | 116.261 | 2214.39 | 25.7 | 54.485 | 6.48 | 1.121 | 3.033 | 7513.68 | 0.918 | 97.5 | 73 | 1439 | 27.24 | 4883.9 | 2296.5 | 2401.5 | 3467.6 | 1222.7 | 0.64509 | 4.154
2024-12-10 | 3:01 | Data | 0 | 35.262 | 34.553 | 121.856 | 7.64 | 116.215 | 2218.91 | 25.69 | 54.575 | 6.48 | 1.121 | 3.047 | 7518.2 | 0.891 | 97.5 | 73.1 | 1443 | 27.29 | 4886.8 | 2282.9 | 2381.8 | 3457.2 | 1222.7 | 0.64381 | 4.168
2024-12-10 | 3:01 | Data | 0 | 35.431 | 34.567 | 121.992 | 7.64 | 116.261 | 2220.72 | 25.69 | 54.575 | 6.47 | 1.125 | 3.036 | 7518.2 | 1.019 | 97.5 | 73 | 1442 | 27.24 | 4886.8 | 2308.6 | 2378.5 | 3468.4 | 1222.7 | 0.64929 | 4.161
2024-12-10 | 3:01 | Data | 0 | 35.694 | 34.567 | 121.947 | 7.64 | 116.306 | 2218.91 | 25.67 | 54.575 | 6.47 | 1.127 | 3.031 | 7545.34 | 0.824 | 97.5 | 72.9 | 1443 | 27.24 | 4904.5 | 2297.2 | 2396.4 | 3471.2 | 1222.7 | 0.64529 | 4.158
2024-12-10 | 3:01 | Data | 0 | 35.431 | 34.567 | 121.992 | 7.64 | 116.306 | 2216.2 | 25.68 | 54.575 | 6.48 | 1.131 | 3.062 | 7531.77 | 0.891 | 97.5 | 73 | 1441 | 27.29 | 4895.6 | 2313.4 | 2384.5 | 3472.2 | 1222.7 | 0.65147 | 4.193
2024-12-10 | 3:02 | Data | 0 | 35.478 | 34.567 | 121.902 | 7.64 | 116.261 | 2218 | 25.67 | 54.214 | 6.47 | 1.129 | 3.067 | 7531.77 | 0.918 | 97.6 | 73.1 | 1442 | 27.15 | 4895.6 | 2318.8 | 2369.6 | 3467 | 1222.7 | 0.65062 | 4.197
2024-12-10 | 3:02 | Data | 0 | 35.383 | 34.567 | 121.992 | 7.64 | 116.351 | 2218.91 | 25.68 | 54.485 | 6.47 | 1.131 | 3.043 | 7549.86 | 0.878 | 97.5 | 72.9 | 1442 | 27.24 | 4907.4 | 2316.1 | 2384 | 3473.3 | 1222.7 | 0.65038 | 4.173
2024-12-10 | 3:02 | Data | 0 | 35.593 | 34.573 | 121.992 | 7.64 | 116.261 | 2213.49 | 25.68 | 54.575 | 6.47 | 1.121 | 3.028 | 7549.86 | 0.918 | 97.5 | 73 | 1439 | 27.29 | 4907.4 | 2307.5 | 2377.9 | 3460.4 | 1222.7 | 0.64945 | 4.15
2024-12-10 | 3:02 | Data | 0 | 35.471 | 34.567 | 121.947 | 7.64 | 116.306 | 2221.62 | 25.67 | 54.575 | 6.48 | 1.124 | 3.043 | 7558.9 | 0.918 | 97.5 | 73 | 1444 | 27.24 | 4913.3 | 2311.6 | 2377.2 | 3464.8 | 1222.7 | 0.64962 | 4.166
2024-12-10 | 3:02 | Data | 0 | 35.262 | 34.681 | 122.037 | 7.64 | 116.351 | 2222.52 | 25.67 | 54.665 | 6.47 | 1.126 | 3.041 | 7545.34 | 0.776 | 97.5 | 73 | 1444 | 27.29 | 4904.5 | 2309.4 | 2375.9 | 3458.2 | 1222.7 | 0.65078 | 4.167
2024-12-10 | 3:02 | Data | 0 | 35.282 | 34.54 | 122.037 | 7.64 | 116.306 | 2222.52 | 25.67 | 54.485 | 6.47 | 1.127 | 3.045 | 7554.38 | 0.722 | 97.5 | 73 | 1444 | 27.24 | 4910.3 | 2308.2 | 2356.5 | 3454 | 1222.7 | 0.65053 | 4.171
2024-12-10 | 3:02 | Data | 0 | 35.255 | 34.567 | 121.902 | 7.64 | 116.306 | 2225.23 | 25.69 | 54.485 | 6.47 | 1.122 | 3.035 | 7567.95 | 0.749 | 97.6 | 73 | 1446 | 27.24 | 4919.2 | 2302.7 | 2365.9 | 3451 | 1222.7 | 0.65152 | 4.157
2024-12-10 | 3:02 | Data | 0 | 35.255 | 34.56 | 121.902 | 7.64 | 116.261 | 2225.23 | 25.68 | 54.485 | 6.48 | 1.121 | 3.045 | 7545.34 | 0.898 | 97.6 | 73.1 | 1446 | 27.29 | 4904.5 | 2303.7 | 2388.7 | 3467.7 | 1222.7 | 0.64779 | 4.165
2024-12-10 | 3:02 | Data | 0 | 35.397 | 34.357 | 121.947 | 7.64 | 116.351 | 2227.95 | 25.69 | 54.575 | 6.47 | 1.129 | 3.04 | 7549.86 | 0.918 | 97.6 | 72.9 | 1448 | 27.29 | 4907.4 | 2302.7 | 2367.6 | 3457.7 | 1222.7 | 0.64963 | 4.168
2024-12-10 | 3:02 | Data | 0 | 35.262 | 34.452 | 121.902 | 7.64 | 116.306 | 2227.95 | 25.69 | 54.485 | 6.48 | 1.126 | 3.057 | 7549.86 | 0.918 | 97.6 | 73.1 | 1448 | 27.29 | 4907.4 | 2311.9 | 2382.1 | 3470.3 | 1222.7 | 0.64916 | 4.183
2024-12-10 | 3:02 | Data | 0 | 35.485 | 34.351 | 121.992 | 7.64 | 116.261 | 2227.95 | 25.7 | 54.485 | 6.47 | 1.133 | 3.039 | 7536.29 | 1.094 | 97.6 | 72.8 | 1448 | 27.24 | 4898.6 | 2293.9 | 2370.4 | 3445.9 | 1222.7 | 0.64908 | 4.172
2024-12-10 | 3:02 | Data | 0 | 35.458 | 34.567 | 121.947 | 7.64 | 116.306 | 2227.95 | 25.69 | 54.485 | 6.47 | 1.126 | 3.033 | 7558.9 | 0.905 | 97.5 | 72.9 | 1448 | 27.29 | 4913.3 | 2315.2 | 2384.7 | 3469.3 | 1222.7 | 0.64959 | 4.16
2024-12-10 | 3:02 | Data | 0 | 35.262 | 34.452 | 121.947 | 7.64 | 116.306 | 2227.95 | 25.69 | 54.485 | 6.47 | 1.128 | 3.034 | 7531.77 | 0.918 | 97.6 | 72.9 | 1448 | 27.29 | 4895.6 | 2292.8 | 2367.3 | 3440.8 | 1222.7 | 0.65021 | 4.162
2024-12-10 | 3:02 | Data | 0 | 35.478 | 34.465 | 121.992 | 7.64 | 116.306 | 2227.95 | 25.69 | 54.575 | 6.48 | 1.118 | 3.031 | 7545.34 | 0.945 | 97.6 | 73.1 | 1448 | 27.29 | 4904.5 | 2313.2 | 2363 | 3461.7 | 1222.7 | 0.64973 | 4.149
2024-12-10 | 3:02 | Data | 0 | 35.708 | 34.58 | 122.083 | 7.64 | 116.441 | 2229.75 | 25.69 | 54.485 | 6.48 | 1.117 | 3.046 | 7549.86 | 0.803 | 97.6 | 73.2 | 1449 | 27.24 | 4907.4 | 2297 | 2381.2 | 3454.9 | 1222.7 | 0.64661 | 4.162
2024-12-10 | 3:02 | Data | 0 | 35.37 | 34.567 | 121.992 | 7.64 | 116.306 | 2229.75 | 25.7 | 54.485 | 6.48 | 1.12 | 3.029 | 7549.86 | 0.878 | 97.6 | 73 | 1450 | 27.24 | 4907.4 | 2308.1 | 2385.3 | 3463.6 | 1222.7 | 0.65263 | 4.15
2024-12-10 | 3:02 | Data | 0 | 35.316 | 34.567 | 121.992 | 7.64 | 116.351 | 2229.75 | 25.7 | 54.575 | 6.48 | 1.125 | 3.033 | 7549.86 | 0.81 | 97.6 | 72.9 | 1449 | 27.29 | 4907.4 | 2290.1 | 2363.3 | 3444.1 | 1222.7 | 0.6479 | 4.158
2024-12-10 | 3:02 | Data | 0 | 35.309 | 34.553 | 121.992 | 7.64 | 116.306 | 2230.66 | 25.69 | 54.575 | 6.48 | 1.117 | 3.035 | 7549.86 | 0.83 | 97.6 | 73.1 | 1449 | 27.29 | 4907.4 | 2293.9 | 2384.8 | 3463.1 | 1222.7 | 0.64681 | 4.152
2024-12-10 | 3:03 | Data | 0 | 35.444 | 34.567 | 121.992 | 7.64 | 116.306 | 2229.75 | 25.7 | 54.575 | 6.47 | 1.111 | 3.054 | 7536.29 | 0.905 | 97.6 | 73.3 | 1449 | 27.29 | 4898.6 | 2323.2 | 2363.6 | 3470.9 | 1222.7 | 0.65308 | 4.165
2024-12-10 | 3:03 | Data | 0 | 35.498 | 34.567 | 121.947 | 7.64 | 116.351 | 2230.66 | 25.69 | 54.575 | 6.47 | 1.119 | 3.045 | 7513.68 | 0.918 | 97.6 | 73.1 | 1450 | 27.24 | 4883.9 | 2343.4 | 2377.2 | 3486.7 | 1222.7 | 0.65507 | 4.163
2024-12-10 | 3:03 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.306 | 2229.75 | 25.69 | 54.485 | 6.48 | 1.121 | 3.045 | 7504.64 | 0.918 | 97.6 | 73.1 | 1450 | 27.29 | 4878 | 2310.8 | 2372.3 | 3468 | 1222.7 | 0.65022 | 4.167
2024-12-10 | 3:03 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.351 | 2228.85 | 25.71 | 54.575 | 6.48 | 1.121 | 3.059 | 7504.64 | 0.918 | 97.6 | 73.2 | 1449 | 27.24 | 4878 | 2327.2 | 2339.3 | 3450.2 | 1222.7 | 0.65686 | 4.18
2024-12-10 | 3:03 | Data | 0 | 35.37 | 34.567 | 122.083 | 7.64 | 116.351 | 2228.85 | 25.69 | 54.485 | 6.47 | 1.124 | 3.035 | 7518.2 | 0.905 | 97.6 | 73 | 1448 | 27.24 | 4886.8 | 2327.9 | 2376.2 | 3476.1 | 1222.7 | 0.65388 | 4.159
2024-12-10 | 3:03 | Data | 0 | 35.485 | 34.56 | 121.992 | 7.65 | 116.306 | 2227.95 | 25.69 | 54.575 | 6.48 | 1.117 | 3.035 | 7504.64 | 0.925 | 97.6 | 73.1 | 1448 | 27.29 | 4878 | 2339.9 | 2379.6 | 3489.6 | 1222.7 | 0.65231 | 4.151
2024-12-10 | 3:03 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2227.95 | 25.7 | 54.485 | 6.48 | 1.124 | 3.064 | 7518.2 | 0.918 | 97.6 | 73.2 | 1448 | 27.29 | 4886.8 | 2325.4 | 2374.9 | 3470.7 | 1222.7 | 0.65359 | 4.189
2024-12-10 | 3:03 | Data | 0 | 35.444 | 34.567 | 122.083 | 7.64 | 116.396 | 2227.95 | 25.69 | 54.485 | 6.48 | 1.121 | 3.042 | 7518.2 | 0.905 | 97.5 | 73.1 | 1448 | 27.29 | 4886.8 | 2320.9 | 2353.9 | 3455.2 | 1222.7 | 0.65524 | 4.163
2024-12-10 | 3:03 | Data | 0 | 35.316 | 34.519 | 122.037 | 7.65 | 116.351 | 2227.04 | 25.7 | 54.575 | 6.48 | 1.129 | 3.022 | 7518.2 | 0.803 | 97.6 | 72.8 | 1448 | 27.29 | 4886.8 | 2319.4 | 2361.5 | 3462.2 | 1222.7 | 0.65297 | 4.151
2024-12-10 | 3:03 | Data | 0 | 35.458 | 34.661 | 121.992 | 7.64 | 116.396 | 2224.33 | 25.69 | 54.485 | 6.48 | 1.127 | 3.021 | 7522.72 | 0.986 | 97.6 | 72.8 | 1446 | 27.24 | 4889.8 | 2343 | 2367.7 | 3484.1 | 1222.7 | 0.65547 | 4.147
2024-12-10 | 3:03 | Data | 0 | 35.37 | 34.567 | 122.083 | 7.64 | 116.306 | 2225.23 | 25.7 | 54.485 | 6.48 | 1.131 | 3.029 | 7513.68 | 0.878 | 97.5 | 72.8 | 1446 | 27.24 | 4883.9 | 2320.9 | 2369.2 | 3472.3 | 1222.7 | 0.65251 | 4.159
2024-12-10 | 3:03 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.306 | 2227.95 | 25.71 | 54.575 | 6.47 | 1.13 | 3.039 | 7513.68 | 0.918 | 97.6 | 72.9 | 1448 | 27.24 | 4883.9 | 2311.1 | 2374.6 | 3466.2 | 1222.7 | 0.65002 | 4.169
2024-12-10 | 3:03 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.306 | 2227.95 | 25.7 | 54.485 | 6.48 | 1.119 | 3.028 | 7536.29 | 0.918 | 97.6 | 73 | 1448 | 27.29 | 4898.6 | 2344.8 | 2386.3 | 3480.4 | 1222.7 | 0.65249 | 4.145
2024-12-10 | 3:03 | Data | 0 | 35.586 | 34.472 | 121.947 | 7.64 | 116.351 | 2224.33 | 25.71 | 54.575 | 6.48 | 1.117 | 3.046 | 7518.2 | 1.073 | 97.6 | 73.2 | 1446 | 27.24 | 4886.8 | 2339.3 | 2378.4 | 3491.1 | 1222.7 | 0.65311 | 4.162
2024-12-10 | 3:03 | Data | 0 | 35.485 | 34.567 | 121.947 | 7.64 | 116.306 | 2221.62 | 25.71 | 54.575 | 6.47 | 1.124 | 3.045 | 7536.29 | 0.918 | 97.5 | 73 | 1445 | 27.24 | 4898.6 | 2326 | 2358.7 | 3466.6 | 1222.7 | 0.65335 | 4.17
2024-12-10 | 3:03 | Data | 0 | 35.262 | 34.567 | 121.992 | 7.64 | 116.306 | 2221.62 | 25.71 | 54.575 | 6.48 | 1.125 | 3.034 | 7531.77 | 0.891 | 97.5 | 73 | 1444 | 27.29 | 4895.6 | 2333.9 | 2364.7 | 3486.3 | 1222.8 | 0.65334 | 4.158
2024-12-10 | 3:03 | Data | 0 | 35.491 | 34.567 | 122.037 | 7.64 | 116.306 | 2222.52 | 25.71 | 54.485 | 6.48 | 1.117 | 3.024 | 7549.86 | 0.918 | 97.5 | 73 | 1445 | 27.29 | 4907.4 | 2330 | 2364.9 | 3475.5 | 1222.8 | 0.65018 | 4.141
2024-12-10 | 3:04 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.306 | 2218.91 | 25.69 | 54.575 | 6.48 | 1.114 | 3.04 | 7527.25 | 0.918 | 97.5 | 73.2 | 1442 | 27.29 | 4892.7 | 2340.1 | 2367.8 | 3478 | 1222.8 | 0.65521 | 4.153
2024-12-10 | 3:04 | Data | 0 | 35.654 | 34.58 | 122.037 | 7.64 | 116.351 | 2216.2 | 25.7 | 54.575 | 6.47 | 1.131 | 3.04 | 7522.72 | 0.999 | 97.5 | 72.9 | 1441 | 27.29 | 4889.8 | 2336.3 | 2389.8 | 3493.7 | 1222.8 | 0.65204 | 4.17
2024-12-10 | 3:04 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.306 | 2213.49 | 25.71 | 54.485 | 6.48 | 1.116 | 3.034 | 7527.25 | 0.918 | 97.5 | 73.1 | 1439 | 27.24 | 4892.7 | 2319.2 | 2380.4 | 3474.8 | 1222.8 | 0.65077 | 4.149
2024-12-10 | 3:04 | Data | 0 | 35.654 | 34.567 | 121.947 | 7.64 | 116.306 | 2210.77 | 25.7 | 54.485 | 6.47 | 1.121 | 3.033 | 7522.72 | 0.938 | 97.5 | 73 | 1437 | 27.29 | 4889.8 | 2331.4 | 2366.2 | 3474.3 | 1222.8 | 0.65405 | 4.154
2024-12-10 | 3:04 | Data | 0 | 35.593 | 34.567 | 122.037 | 7.64 | 116.396 | 2208.06 | 25.69 | 54.575 | 6.47 | 1.129 | 3.015 | 7531.77 | 0.932 | 97.5 | 72.8 | 1435 | 27.29 | 4895.6 | 2335.2 | 2355.5 | 3468 | 1222.8 | 0.65616 | 4.143
2024-12-10 | 3:04 | Data | 0 | 35.269 | 34.567 | 121.992 | 7.64 | 116.306 | 2208.06 | 25.69 | 54.485 | 6.47 | 1.124 | 3.005 | 7522.72 | 0.81 | 97.5 | 72.8 | 1435 | 27.24 | 4889.8 | 2329.8 | 2377.6 | 3481.9 | 1222.8 | 0.65222 | 4.129
2024-12-10 | 3:04 | Data | 0 | 35.275 | 34.668 | 121.992 | 7.64 | 116.306 | 2208.06 | 25.7 | 54.575 | 6.48 | 1.126 | 3.029 | 7518.2 | 0.722 | 97.5 | 72.9 | 1436 | 27.24 | 4886.8 | 2324.6 | 2372.3 | 3473.2 | 1222.8 | 0.65336 | 4.154
2024-12-10 | 3:04 | Data | 0 | 35.289 | 34.513 | 121.992 | 7.64 | 116.351 | 2211.68 | 25.7 | 54.575 | 6.48 | 1.131 | 3.034 | 7513.68 | 0.803 | 97.5 | 72.9 | 1438 | 27.29 | 4883.9 | 2326.6 | 2381.7 | 3484.5 | 1222.8 | 0.65276 | 4.163
2024-12-10 | 3:04 | Data | 0 | 35.485 | 34.391 | 121.947 | 7.63 | 116.351 | 2210.77 | 25.7 | 54.575 | 6.48 | 1.129 | 3.04 | 7518.2 | 1.033 | 97.5 | 72.9 | 1437 | 27.29 | 4886.8 | 2323.4 | 2383.8 | 3487.3 | 1222.8 | 0.65395 | 4.17
2024-12-10 | 3:04 | Data | 0 | 35.714 | 34.479 | 121.992 | 7.64 | 116.396 | 2210.77 | 25.69 | 54.124 | 6.48 | 1.126 | 3.035 | 7527.25 | 0.891 | 97.6 | 72.9 | 1437 | 27.06 | 4892.7 | 2346.4 | 2375.3 | 3492.6 | 1222.8 | 0.65404 | 4.161
2024-12-10 | 3:04 | Data | 0 | 35.6 | 34.357 | 121.992 | 7.64 | 116.396 | 2210.77 | 25.7 | 54.485 | 6.47 | 1.121 | 3.034 | 7531.77 | 1.1 | 97.5 | 73 | 1438 | 27.29 | 4895.6 | 2255.4 | 2359.5 | 3410.1 | 1222.8 | 0.64885 | 4.154
2024-12-10 | 3:04 | Data | 0 | 35.586 | 34.567 | 122.037 | 7.64 | 116.306 | 2210.77 | 25.7 | 54.485 | 6.48 | 1.126 | 3.033 | 7531.77 | 1.114 | 97.5 | 72.9 | 1437 | 27.24 | 4895.6 | 2248.7 | 2336.9 | 3395.7 | 1222.8 | 0.6461 | 4.159
2024-12-10 | 3:04 | Data | 0 | 35.6 | 34.567 | 122.037 | 7.64 | 116.396 | 2210.77 | 25.69 | 54.575 | 6.48 | 1.121 | 3.01 | 7531.77 | 0.959 | 97.5 | 72.9 | 1437 | 27.29 | 4895.6 | 2269.1 | 2349.3 | 3412.9 | 1222.8 | 0.64859 | 4.131
2024-12-10 | 3:04 | Data | 0 | 35.37 | 34.762 | 121.947 | 7.64 | 116.306 | 2212.58 | 25.7 | 54.575 | 6.48 | 1.124 | 3.035 | 7518.2 | 0.864 | 97.5 | 73 | 1438 | 27.29 | 4886.8 | 2260.9 | 2369.2 | 3421 | 1222.8 | 0.64602 | 4.16
2024-12-10 | 3:04 | Data | 0 | 35.485 | 34.567 | 121.947 | 7.64 | 116.261 | 2208.97 | 25.71 | 54.485 | 6.48 | 1.127 | 3.018 | 7518.2 | 0.918 | 97.5 | 72.8 | 1436 | 27.24 | 4886.8 | 2252.8 | 2367.8 | 3410.4 | 1222.8 | 0.64451 | 4.144
2024-12-10 | 3:04 | Data | 0 | 35.269 | 34.567 | 122.037 | 7.64 | 116.306 | 2210.77 | 25.7 | 54.485 | 6.48 | 1.121 | 3.027 | 7531.77 | 0.891 | 97.5 | 73 | 1438 | 27.29 | 4895.6 | 2267.8 | 2379 | 3427.6 | 1222.8 | 0.64835 | 4.147
2024-12-10 | 3:04 | Data | 0 | 35.694 | 34.681 | 122.083 | 7.64 | 116.351 | 2211.68 | 25.7 | 54.575 | 6.47 | 1.121 | 3.051 | 7518.2 | 0.918 | 97.5 | 73.1 | 1438 | 27.29 | 4886.8 | 2265.7 | 2372.6 | 3423.6 | 1222.8 | 0.64551 | 4.172
2024-12-10 | 3:04 | Data | 0 | 35.573 | 34.567 | 121.992 | 7.65 | 116.306 | 2216.2 | 25.69 | 54.575 | 6.48 | 1.121 | 3.055 | 7527.25 | 1.006 | 97.5 | 73.2 | 1441 | 27.33 | 4892.7 | 2250.2 | 2338.4 | 3393.1 | 1222.8 | 0.64574 | 4.176
2024-12-10 | 3:05 | Data | 0 | 35.262 | 34.553 | 121.947 | 7.64 | 116.261 | 2216.2 | 25.7 | 54.485 | 6.47 | 1.127 | 3.038 | 7518.2 | 0.878 | 97.5 | 72.9 | 1441 | 27.24 | 4886.8 | 2261.3 | 2372.8 | 3423.4 | 1222.8 | 0.64298 | 4.165
2024-12-10 | 3:05 | Data | 0 | 35.282 | 34.546 | 121.947 | 7.64 | 116.261 | 2218.91 | 25.7 | 54.485 | 6.47 | 1.128 | 3.036 | 7527.25 | 0.783 | 97.5 | 72.9 | 1442 | 27.24 | 4892.7 | 2306.5 | 2381.9 | 3467.7 | 1222.8 | 0.6464 | 4.164
2024-12-10 | 3:05 | Data | 0 | 35.255 | 34.54 | 122.083 | 7.64 | 116.306 | 2218 | 25.69 | 54.575 | 6.48 | 1.129 | 3.033 | 7531.77 | 0.918 | 97.5 | 72.9 | 1442 | 27.29 | 4895.6 | 2316.5 | 2384.1 | 3471.5 | 1222.8 | 0.65165 | 4.161
2024-12-10 | 3:05 | Data | 0 | 35.383 | 34.567 | 121.992 | 7.64 | 116.351 | 2216.2 | 25.69 | 54.485 | 6.48 | 1.132 | 3.048 | 7536.29 | 0.722 | 97.5 | 72.9 | 1441 | 27.24 | 4898.6 | 2298 | 2364.4 | 3450.4 | 1222.8 | 0.64615 | 4.18
2024-12-10 | 3:05 | Data | 0 | 35.431 | 34.567 | 122.083 | 7.64 | 116.351 | 2218.91 | 25.69 | 54.485 | 6.47 | 1.131 | 3.056 | 7518.2 | 0.911 | 97.5 | 73 | 1442 | 27.29 | 4886.8 | 2317.5 | 2359 | 3461 | 1222.8 | 0.65286 | 4.188
2024-12-10 | 3:05 | Data | 0 | 35.269 | 34.54 | 121.947 | 7.64 | 116.306 | 2222.52 | 25.7 | 54.575 | 6.48 | 1.127 | 3.056 | 7522.72 | 0.749 | 97.5 | 73.1 | 1445 | 27.29 | 4889.8 | 2315.9 | 2375.2 | 3468.2 | 1222.8 | 0.64964 | 4.183
2024-12-10 | 3:05 | Data | 0 | 35.37 | 34.344 | 121.902 | 7.64 | 116.261 | 2225.23 | 25.7 | 54.033 | 6.48 | 1.124 | 3.046 | 7504.64 | 0.918 | 97.6 | 73 | 1446 | 27.02 | 4878 | 2297.3 | 2353.1 | 3450.3 | 1222.8 | 0.6522 | 4.17
2024-12-10 | 3:05 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.306 | 2227.95 | 25.69 | 54.575 | 6.47 | 1.127 | 3.048 | 7504.64 | 0.918 | 97.5 | 73 | 1448 | 27.29 | 4878 | 2316.3 | 2390 | 3480.8 | 1222.8 | 0.65012 | 4.175
2024-12-10 | 3:05 | Data | 0 | 35.485 | 34.567 | 121.947 | 7.64 | 116.306 | 2227.04 | 25.7 | 54.394 | 6.48 | 1.121 | 3.042 | 7513.68 | 0.918 | 97.6 | 73.1 | 1448 | 27.24 | 4883.9 | 2305.2 | 2345.5 | 3446.4 | 1222.8 | 0.65229 | 4.162
2024-12-10 | 3:05 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.306 | 2225.23 | 25.69 | 54.485 | 6.48 | 1.131 | 3.037 | 7518.2 | 0.918 | 97.6 | 72.9 | 1446 | 27.24 | 4886.8 | 2310.1 | 2351.7 | 3446.3 | 1222.8 | 0.65417 | 4.167
2024-12-10 | 3:05 | Data | 0 | 35.282 | 34.351 | 121.992 | 7.64 | 116.261 | 2216.2 | 25.7 | 54.575 | 6.48 | 1.126 | 3.019 | 7513.68 | 1.013 | 97.5 | 72.8 | 1440 | 27.29 | 4883.9 | 2325.2 | 2360.2 | 3467.6 | 1222.8 | 0.64897 | 4.145
2024-12-10 | 3:05 | Data | 0 | 35.485 | 34.567 | 121.902 | 7.64 | 116.261 | 2225.23 | 25.69 | 54.575 | 6.47 | 1.121 | 3.03 | 7522.72 | 0.918 | 97.5 | 73 | 1446 | 27.24 | 4889.8 | 2316.1 | 2362.7 | 3464.2 | 1222.8 | 0.65215 | 4.151
2024-12-10 | 3:05 | Data | 0 | 35.269 | 34.567 | 122.037 | 7.64 | 116.306 | 2220.72 | 25.69 | 54.485 | 6.47 | 1.127 | 3.035 | 7531.77 | 0.81 | 97.5 | 72.9 | 1443 | 27.29 | 4895.6 | 2303.3 | 2378.3 | 3461.8 | 1222.8 | 0.64874 | 4.161
2024-12-10 | 3:05 | Data | 0 | 35.262 | 34.776 | 121.992 | 7.64 | 116.351 | 2222.52 | 25.69 | 54.485 | 6.47 | 1.129 | 3.042 | 7531.77 | 0.918 | 97.5 | 72.9 | 1445 | 27.2 | 4895.6 | 2309.3 | 2366.2 | 3457.1 | 1222.8 | 0.65046 | 4.17
2024-12-10 | 3:05 | Data | 0 | 35.478 | 34.567 | 122.037 | 7.64 | 116.351 | 2226.14 | 25.7 | 54.575 | 6.48 | 1.122 | 3.029 | 7531.77 | 0.83 | 97.6 | 73 | 1446 | 27.24 | 4895.6 | 2302.9 | 2368.1 | 3460.1 | 1222.8 | 0.64714 | 4.151
2024-12-10 | 3:05 | Data | 0 | 35.485 | 34.769 | 121.992 | 7.64 | 116.306 | 2225.23 | 25.69 | 54.575 | 6.48 | 1.117 | 3.035 | 7545.34 | 0.81 | 97.5 | 73.1 | 1447 | 27.29 | 4904.5 | 2314.1 | 2368.9 | 3464 | 1222.8 | 0.65075 | 4.151
2024-12-10 | 3:05 | Data | 0 | 35.458 | 34.567 | 121.992 | 7.64 | 116.215 | 2220.72 | 25.68 | 54.575 | 6.47 | 1.122 | 3.03 | 7531.77 | 0.911 | 97.5 | 73 | 1444 | 27.29 | 4895.6 | 2301 | 2373.1 | 3464.2 | 1222.8 | 0.64718 | 4.153
2024-12-10 | 3:05 | Data | 0 | 35.269 | 34.357 | 121.902 | 7.64 | 116.306 | 2222.52 | 25.69 | 54.485 | 6.47 | 1.132 | 3.041 | 7545.34 | 0.905 | 97.5 | 72.9 | 1445 | 27.24 | 4904.5 | 2326.4 | 2372.5 | 3475.1 | 1222.8 | 0.65146 | 4.174
2024-12-10 | 3:06 | Data | 0 | 35.485 | 34.479 | 121.856 | 7.64 | 116.261 | 2220.72 | 25.7 | 54.485 | 6.48 | 1.12 | 3.05 | 7531.77 | 0.857 | 97.5 | 73.2 | 1442 | 27.29 | 4895.6 | 2307 | 2341.4 | 3451.5 | 1222.8 | 0.65492 | 4.167
2024-12-10 | 3:06 | Data | 0 | 35.485 | 34.351 | 122.037 | 7.64 | 116.351 | 2208.06 | 25.7 | 54.485 | 6.47 | 1.112 | 3.031 | 7549.86 | 0.918 | 97.5 | 73.2 | 1435 | 27.29 | 4907.4 | 2308.1 | 2350.1 | 3444.5 | 1222.8 | 0.65436 | 4.142
2024-12-10 | 3:06 | Data | 0 | 35.309 | 34.54 | 121.902 | 7.64 | 116.261 | 2216.2 | 25.69 | 54.485 | 6.48 | 1.117 | 3.031 | 7518.2 | 0.756 | 97.5 | 73.1 | 1441 | 27.29 | 4886.8 | 2303.4 | 2343.2 | 3432.2 | 1222.8 | 0.65518 | 4.15
2024-12-10 | 3:06 | Data | 0 | 35.255 | 34.452 | 121.902 | 7.64 | 116.261 | 2211.68 | 25.69 | 54.485 | 6.48 | 1.128 | 3.037 | 7518.2 | 0.803 | 97.5 | 72.9 | 1438 | 27.29 | 4886.8 | 2306.1 | 2370.4 | 3449.4 | 1222.8 | 0.6534 | 4.164
2024-12-10 | 3:06 | Data | 0 | 35.471 | 34.344 | 121.947 | 7.64 | 116.215 | 2213.49 | 25.7 | 54.485 | 6.47 | 1.126 | 3.024 | 7531.77 | 0.965 | 97.5 | 72.9 | 1439 | 27.29 | 4895.6 | 2305.2 | 2375.8 | 3463.1 | 1222.8 | 0.65168 | 4.15
2024-12-10 | 3:06 | Data | 0 | 35.485 | 34.391 | 121.902 | 7.64 | 116.261 | 2214.39 | 25.69 | 54.575 | 6.47 | 1.122 | 3.038 | 7531.77 | 0.918 | 97.5 | 73 | 1439 | 27.29 | 4895.6 | 2318.2 | 2368.3 | 3453.8 | 1222.8 | 0.65214 | 4.161
2024-12-10 | 3:06 | Data | 0 | 35.532 | 34.364 | 121.947 | 7.64 | 116.306 | 2213.49 | 25.7 | 54.214 | 6.48 | 1.121 | 3.04 | 7513.68 | 0.938 | 97.5 | 73.1 | 1439 | 27.15 | 4883.9 | 2292.3 | 2362.4 | 3440.2 | 1222.8 | 0.64875 | 4.161
2024-12-10 | 3:06 | Data | 0 | 35.485 | 34.567 | 122.128 | 7.64 | 116.306 | 2214.39 | 25.71 | 54.214 | 6.47 | 1.127 | 3.037 | 7518.2 | 0.918 | 97.6 | 72.9 | 1439 | 27.11 | 4886.8 | 2309.5 | 2381.4 | 3469 | 1222.8 | 0.64931 | 4.164
2024-12-10 | 3:06 | Data | 0 | 35.37 | 34.513 | 122.037 | 7.64 | 116.351 | 2212.58 | 25.71 | 54.304 | 6.47 | 1.13 | 3.048 | 7549.86 | 0.749 | 97.6 | 73 | 1439 | 27.15 | 4907.4 | 2291 | 2367.8 | 3446.7 | 1222.9 | 0.64689 | 4.178
2024-12-10 | 3:06 | Data | 0 | 35.471 | 34.337 | 121.856 | 7.64 | 116.261 | 2213.49 | 25.71 | 54.665 | 6.48 | 1.122 | 3.034 | 7536.29 | 1.013 | 97.5 | 73 | 1439 | 27.33 | 4898.6 | 2296.2 | 2376.3 | 3459.7 | 1222.9 | 0.64811 | 4.156
2024-12-10 | 3:06 | Data | 0 | 35.262 | 34.351 | 121.947 | 7.64 | 116.306 | 2216.2 | 25.7 | 54.394 | 6.48 | 1.115 | 3.039 | 7549.86 | 0.857 | 97.5 | 73.2 | 1441 | 27.2 | 4907.4 | 2295.3 | 2354.6 | 3442.9 | 1222.9 | 0.65184 | 4.154
2024-12-10 | 3:06 | Data | 0 | 35.37 | 34.567 | 121.947 | 7.64 | 116.306 | 2218.91 | 25.71 | 54.575 | 6.48 | 1.12 | 3.023 | 7549.86 | 0.891 | 97.5 | 73 | 1442 | 27.29 | 4907.4 | 2307.4 | 2350.8 | 3446.4 | 1222.9 | 0.6519 | 4.143
2024-12-10 | 3:06 | Data | 0 | 35.512 | 34.398 | 121.992 | 7.64 | 116.351 | 2218.91 | 25.71 | 54.304 | 6.47 | 1.126 | 3.04 | 7549.86 | 0.979 | 97.6 | 73 | 1442 | 27.15 | 4907.4 | 2301.4 | 2358.9 | 3443.9 | 1222.9 | 0.65219 | 4.166
2024-12-10 | 3:06 | Data | 0 | 35.654 | 34.58 | 122.037 | 7.64 | 116.396 | 2216.2 | 25.71 | 54.304 | 6.47 | 1.124 | 3.048 | 7549.86 | 0.918 | 97.6 | 73.1 | 1441 | 27.15 | 4907.4 | 2314.3 | 2373.5 | 3464.1 | 1222.9 | 0.65212 | 4.171
2024-12-10 | 3:06 | Data | 0 | 35.458 | 34.735 | 122.083 | 7.64 | 116.306 | 2218.91 | 25.71 | 54.394 | 6.47 | 1.126 | 3.035 | 7549.86 | 1.033 | 97.5 | 72.9 | 1442 | 27.2 | 4907.4 | 2311.8 | 2362.2 | 3455.9 | 1222.9 | 0.64995 | 4.161
2024-12-10 | 3:06 | Data | 0 | 35.485 | 34.567 | 121.947 | 7.64 | 116.261 | 2218.91 | 25.71 | 54.033 | 6.48 | 1.12 | 3.05 | 7522.72 | 0.945 | 97.6 | 73.2 | 1442 | 27.06 | 4889.8 | 2286.1 | 2369.5 | 3449.4 | 1222.9 | 0.64733 | 4.17
2024-12-10 | 3:06 | Data | 0 | 35.485 | 34.58 | 122.037 | 7.64 | 116.351 | 2215.29 | 25.71 | 54.485 | 6.47 | 1.115 | 3.052 | 7545.34 | 0.891 | 97.5 | 73.3 | 1439 | 27.29 | 4904.5 | 2295.2 | 2353.2 | 3437.4 | 1222.9 | 0.65209 | 4.167
2024-12-10 | 3:07 | Data | 0 | 35.525 | 34.371 | 121.947 | 7.64 | 116.351 | 2213.49 | 25.71 | 54.485 | 6.47 | 1.119 | 3.044 | 7531.77 | 0.905 | 97.5 | 73.1 | 1439 | 27.24 | 4895.6 | 2325.3 | 2372.2 | 3464.3 | 1222.9 | 0.65501 | 4.162
2024-12-10 | 3:07 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2216.2 | 25.71 | 54.575 | 6.47 | 1.13 | 3.064 | 7531.77 | 0.918 | 97.5 | 73.1 | 1441 | 27.24 | 4895.6 | 2298.3 | 2353.1 | 3441.5 | 1222.9 | 0.65084 | 4.194
2024-12-10 | 3:07 | Data | 0 | 35.309 | 34.398 | 121.947 | 7.64 | 116.306 | 2216.2 | 25.71 | 54.214 | 6.48 | 1.131 | 3.025 | 7558.9 | 0.716 | 97.5 | 72.8 | 1441 | 27.15 | 4913.3 | 2309.3 | 2328.8 | 3427.5 | 1222.9 | 0.6574 | 4.155
2024-12-10 | 3:07 | Data | 0 | 35.485 | 34.56 | 121.902 | 7.64 | 116.306 | 2217.1 | 25.71 | 54.304 | 6.47 | 1.127 | 3.036 | 7549.86 | 0.932 | 97.6 | 72.9 | 1441 | 27.15 | 4907.4 | 2305.1 | 2341.6 | 3437.1 | 1222.9 | 0.65496 | 4.164
2024-12-10 | 3:07 | Data | 0 | 35.255 | 34.54 | 121.947 | 7.64 | 116.261 | 2221.62 | 25.71 | 54.485 | 6.47 | 1.125 | 3.051 | 7563.42 | 0.803 | 97.5 | 73.1 | 1445 | 27.29 | 4916.2 | 2297.6 | 2333 | 3425.9 | 1222.9 | 0.65475 | 4.176
2024-12-10 | 3:07 | Data | 0 | 35.269 | 34.567 | 121.947 | 7.64 | 116.261 | 2228.85 | 25.7 | 54.575 | 6.48 | 1.113 | 3.044 | 7563.42 | 0.689 | 97.6 | 73.2 | 1449 | 27.24 | 4916.2 | 2300.8 | 2355 | 3448.5 | 1222.9 | 0.65428 | 4.158
2024-12-10 | 3:07 | Data | 0 | 35.431 | 34.776 | 121.992 | 7.64 | 116.306 | 2230.66 | 25.71 | 54.575 | 6.47 | 1.114 | 3.047 | 7563.42 | 0.871 | 97.6 | 73.2 | 1449 | 27.33 | 4916.2 | 2310.5 | 2344.7 | 3441.2 | 1222.9 | 0.65585 | 4.161
2024-12-10 | 3:07 | Data | 0 | 35.485 | 34.735 | 121.992 | 7.64 | 116.261 | 2230.66 | 25.71 | 54.485 | 6.47 | 1.121 | 3.035 | 7576.99 | 0.918 | 97.6 | 73 | 1449 | 27.24 | 4925 | 2310.7 | 2364 | 3457.6 | 1222.9 | 0.6513 | 4.157
2024-12-10 | 3:07 | Data | 0 | 35.485 | 34.351 | 121.947 | 7.64 | 116.306 | 2230.66 | 25.71 | 54.575 | 6.47 | 1.127 | 3.026 | 7576.99 | 0.864 | 97.6 | 72.8 | 1449 | 27.24 | 4925 | 2298.4 | 2342.7 | 3435.8 | 1222.9 | 0.65226 | 4.153
2024-12-10 | 3:07 | Data | 0 | 35.654 | 34.621 | 122.128 | 7.64 | 116.351 | 2233.37 | 25.71 | 54.575 | 6.47 | 1.126 | 3.044 | 7581.51 | 0.972 | 97.6 | 73 | 1451 | 27.24 | 4928 | 2298.4 | 2351.6 | 3437.5 | 1222.9 | 0.6519 | 4.17
2024-12-10 | 3:07 | Data | 0 | 35.269 | 34.513 | 121.992 | 7.64 | 116.261 | 2236.08 | 25.71 | 54.846 | 6.47 | 1.117 | 3.043 | 7563.42 | 0.911 | 97.6 | 73.1 | 1453 | 27.38 | 4916.2 | 2299 | 2339.6 | 3434.4 | 1222.9 | 0.6495 | 4.16
2024-12-10 | 3:07 | Data | 0 | 35.478 | 34.567 | 121.992 | 7.64 | 116.396 | 2235.18 | 25.71 | 54.575 | 6.47 | 1.125 | 3.038 | 7563.42 | 0.918 | 97.6 | 73 | 1453 | 27.24 | 4916.2 | 2310.3 | 2363 | 3453.6 | 1222.9 | 0.65342 | 4.163
2024-12-10 | 3:07 | Data | 0 | 35.289 | 34.54 | 121.992 | 7.64 | 116.351 | 2235.18 | 25.7 | 54.756 | 6.47 | 1.128 | 3.04 | 7549.86 | 0.81 | 97.6 | 72.9 | 1453 | 27.38 | 4907.4 | 2308 | 2359.7 | 3446.5 | 1222.9 | 0.65467 | 4.168
2024-12-10 | 3:07 | Data | 0 | 35.262 | 34.54 | 121.992 | 7.64 | 116.351 | 2233.37 | 25.71 | 54.485 | 6.47 | 1.13 | 3.052 | 7554.38 | 0.803 | 97.6 | 73 | 1452 | 27.24 | 4910.3 | 2308.1 | 2345.5 | 3442.4 | 1222.9 | 0.65418 | 4.181
2024-12-10 | 3:07 | Data | 0 | 35.586 | 34.567 | 121.947 | 7.64 | 116.306 | 2229.75 | 25.71 | 54.575 | 6.47 | 1.115 | 3.051 | 7563.42 | 0.817 | 97.6 | 73.2 | 1449 | 27.24 | 4916.2 | 2295.4 | 2366.4 | 3449.6 | 1222.9 | 0.65147 | 4.166
2024-12-10 | 3:07 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.396 | 2229.75 | 25.7 | 54.575 | 6.47 | 1.121 | 3.041 | 7549.86 | 0.911 | 97.6 | 73.1 | 1449 | 27.24 | 4907.4 | 2306.6 | 2362.5 | 3444.3 | 1222.9 | 0.654 | 4.162
2024-12-10 | 3:07 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.306 | 2230.66 | 25.72 | 54.485 | 6.47 | 1.121 | 3.034 | 7567.95 | 0.918 | 97.6 | 73 | 1449 | 27.29 | 4919.2 | 2296.1 | 2354.9 | 3433.9 | 1222.9 | 0.65152 | 4.154
2024-12-10 | 3:07 | Data | 0 | 35.316 | 34.364 | 121.992 | 7.64 | 116.396 | 2227.95 | 25.71 | 54.485 | 6.47 | 1.122 | 3.038 | 7558.9 | 0.945 | 97.6 | 73 | 1448 | 27.24 | 4913.3 | 2310 | 2353.2 | 3444.3 | 1222.9 | 0.64778 | 4.16
2024-12-10 | 3:08 | Data | 0 | 35.687 | 34.567 | 121.947 | 7.64 | 116.351 | 2227.04 | 25.71 | 54.485 | 6.47 | 1.121 | 3.021 | 7545.34 | 1.026 | 97.5 | 72.9 | 1448 | 27.24 | 4904.5 | 2298 | 2346.3 | 3441.2 | 1222.9 | 0.65196 | 4.142
2024-12-10 | 3:08 | Data | 0 | 35.478 | 34.567 | 122.037 | 7.64 | 116.351 | 2227.04 | 25.71 | 54.485 | 6.47 | 1.116 | 3.045 | 7531.77 | 0.918 | 97.6 | 73.2 | 1448 | 27.29 | 4895.6 | 2313.9 | 2366.3 | 3456.2 | 1222.9 | 0.65373 | 4.16
2024-12-10 | 3:08 | Data | 0 | 35.458 | 34.567 | 121.992 | 7.65 | 116.306 | 2227.95 | 25.71 | 54.575 | 6.47 | 1.121 | 3.067 | 7531.77 | 0.911 | 97.5 | 73.2 | 1448 | 27.29 | 4895.6 | 2293.6 | 2345.4 | 3434 | 1222.9 | 0.65189 | 4.189
2024-12-10 | 3:08 | Data | 0 | 35.485 | 34.567 | 121.902 | 7.64 | 116.351 | 2233.37 | 25.71 | 54.394 | 6.47 | 1.121 | 3.035 | 7549.86 | 0.918 | 97.6 | 73 | 1451 | 27.24 | 4907.4 | 2301.3 | 2346.2 | 3438.8 | 1222.9 | 0.65147 | 4.158
2024-12-10 | 3:08 | Data | 0 | 35.518 | 34.567 | 121.992 | 7.64 | 116.396 | 2232.47 | 25.7 | 54.485 | 6.47 | 1.128 | 3.029 | 7373.49 | 0.925 | 97.6 | 72.9 | 1452 | 27.24 | 4792.8 | 2310.3 | 2347.8 | 3446.4 | 1222.9 | 0.65404 | 4.155
2024-12-10 | 3:08 | Data | 0 | 35.437 | 34.783 | 122.037 | 7.64 | 116.396 | 2233.37 | 25.72 | 54.575 | 6.47 | 1.12 | 3.035 | 7341.83 | 0.817 | 97.6 | 73.1 | 1451 | 27.29 | 4772.2 | 2312.2 | 2345.3 | 3448.2 | 1222.9 | 0.65248 | 4.155
2024-12-10 | 3:08 | Data | 0 | 35.491 | 34.621 | 122.037 | 7.64 | 116.441 | 2232.47 | 25.71 | 54.485 | 6.47 | 1.116 | 3.028 | 7337.31 | 0.925 | 97.6 | 73.1 | 1451 | 27.24 | 4769.3 | 2289 | 2357.6 | 3432.1 | 1222.9 | 0.6503 | 4.144
2024-12-10 | 3:08 | Data | 0 | 35.269 | 34.546 | 121.947 | 7.64 | 116.351 | 2227.95 | 25.71 | 54.214 | 6.47 | 1.122 | 3.026 | 7337.31 | 0.911 | 97.6 | 72.9 | 1448 | 27.15 | 4769.3 | 2304.1 | 2337.1 | 3431.7 | 1222.9 | 0.65673 | 4.149
2024-12-10 | 3:08 | Data | 0 | 35.687 | 34.567 | 121.992 | 7.64 | 116.396 | 2227.95 | 25.71 | 54.846 | 6.47 | 1.131 | 3.035 | 7513.68 | 0.972 | 97.5 | 72.9 | 1448 | 27.38 | 4883.9 | 2318.6 | 2338.7 | 3437.2 | 1222.9 | 0.65663 | 4.165
2024-12-10 | 3:08 | Data | 0 | 35.701 | 34.621 | 122.083 | 7.64 | 116.351 | 2227.95 | 25.71 | 54.485 | 6.48 | 1.126 | 3.016 | 7531.77 | 0.911 | 97.6 | 72.8 | 1448 | 27.24 | 4895.6 | 2323.8 | 2337.3 | 3441.3 | 1222.9 | 0.6586 | 4.142
2024-12-10 | 3:08 | Data | 0 | 35.6 | 34.573 | 122.128 | 7.64 | 116.396 | 2225.23 | 25.71 | 54.575 | 6.47 | 1.115 | 3.026 | 7513.68 | 0.749 | 97.5 | 73.1 | 1446 | 27.24 | 4883.9 | 2299.1 | 2332.7 | 3426.5 | 1222.9 | 0.65425 | 4.141
2024-12-10 | 3:08 | Data | 0 | 35.532 | 34.587 | 121.992 | 7.64 | 116.396 | 2222.52 | 25.71 | 54.485 | 6.47 | 1.121 | 3.067 | 7536.29 | 0.911 | 97.5 | 73.2 | 1445 | 27.24 | 4898.6 | 2311.9 | 2338.2 | 3443.7 | 1222.9 | 0.65414 | 4.188
2024-12-10 | 3:08 | Data | 0 | 35.687 | 34.621 | 122.128 | 7.64 | 116.441 | 2218 | 25.71 | 54.575 | 6.47 | 1.121 | 3.044 | 7536.29 | 1.026 | 97.5 | 73.1 | 1442 | 27.24 | 4898.6 | 2328.9 | 2350.1 | 3452.3 | 1222.9 | 0.65764 | 4.164
2024-12-10 | 3:08 | Data | 0 | 35.512 | 34.6 | 122.083 | 7.64 | 116.396 | 2222.52 | 25.71 | 54.485 | 6.47 | 1.13 | 3.028 | 7554.38 | 0.79 | 97.5 | 72.8 | 1445 | 27.2 | 4910.3 | 2293.2 | 2347.8 | 3435 | 1222.9 | 0.6527 | 4.159
2024-12-10 | 3:08 | Data | 0 | 35.573 | 34.594 | 122.037 | 7.64 | 116.396 | 2222.52 | 25.7 | 54.575 | 6.47 | 1.132 | 3.042 | 7527.25 | 0.851 | 97.5 | 72.9 | 1445 | 27.29 | 4892.7 | 2294.3 | 2356.7 | 3436.1 | 1222.9 | 0.65238 | 4.173
2024-12-10 | 3:08 | Data | 0 | 35.654 | 34.479 | 122.037 | 7.64 | 116.351 | 2225.23 | 25.71 | 54.575 | 6.48 | 1.12 | 3.037 | 7531.77 | 1.114 | 97.5 | 73.1 | 1446 | 27.29 | 4895.6 | 2300.9 | 2360.4 | 3442.9 | 1222.9 | 0.65339 | 4.156
2024-12-10 | 3:08 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2224.33 | 25.71 | 54.575 | 6.47 | 1.125 | 3.036 | 7549.86 | 0.918 | 97.6 | 73 | 1446 | 27.24 | 4907.4 | 2317.8 | 2355.4 | 3452.5 | 1222.9 | 0.65403 | 4.161
2024-12-10 | 3:08 | Data | 0 | 35.485 | 34.58 | 122.037 | 7.64 | 116.396 | 2225.23 | 25.71 | 54.575 | 6.47 | 1.124 | 3.046 | 7558.9 | 0.83 | 97.6 | 73 | 1446 | 27.29 | 4913.3 | 2297.7 | 2353.9 | 3438.5 | 1222.9 | 0.65172 | 4.17
2024-12-10 | 3:09 | Data | 0 | 35.593 | 34.573 | 122.037 | 7.64 | 116.396 | 2227.95 | 25.72 | 54.485 | 6.48 | 1.111 | 3.039 | 7549.86 | 0.925 | 97.6 | 73.2 | 1448 | 27.24 | 4907.4 | 2288.4 | 2350 | 3431.3 | 1222.9 | 0.64921 | 4.149
2024-12-10 | 3:09 | Data | 0 | 35.485 | 34.594 | 122.083 | 7.64 | 116.351 | 2227.95 | 25.71 | 54.575 | 6.47 | 1.113 | 3.058 | 7549.86 | 0.716 | 97.6 | 73.3 | 1448 | 27.24 | 4907.4 | 2304.7 | 2360.6 | 3445.8 | 1223 | 0.65256 | 4.17
2024-12-10 | 3:09 | Data | 0 | 35.485 | 34.742 | 122.037 | 7.64 | 116.351 | 2227.95 | 25.71 | 54.485 | 6.47 | 1.121 | 3.056 | 7531.77 | 0.803 | 97.6 | 73.2 | 1448 | 27.24 | 4895.6 | 2312.4 | 2356.6 | 3448.2 | 1223 | 0.65463 | 4.178
2024-12-10 | 3:09 | Data | 0 | 35.485 | 34.567 | 121.947 | 7.64 | 116.351 | 2230.66 | 25.71 | 54.575 | 6.47 | 1.129 | 3.042 | 7518.2 | 0.918 | 97.6 | 72.9 | 1450 | 27.29 | 4886.8 | 2300.7 | 2359.9 | 3450 | 1223 | 0.65125 | 4.17
2024-12-10 | 3:09 | Data | 0 | 35.485 | 34.742 | 121.947 | 7.64 | 116.396 | 2230.66 | 25.71 | 54.575 | 6.47 | 1.125 | 3.021 | 7527.25 | 0.918 | 97.6 | 72.9 | 1450 | 27.29 | 4892.7 | 2317.7 | 2368.8 | 3465.6 | 1223 | 0.65406 | 4.147
2024-12-10 | 3:09 | Data | 0 | 35.485 | 34.789 | 122.083 | 7.64 | 116.351 | 2234.27 | 25.71 | 54.575 | 6.47 | 1.12 | 3.037 | 7522.72 | 0.898 | 97.6 | 73.1 | 1452 | 27.24 | 4889.8 | 2313.9 | 2366.9 | 3456.9 | 1223 | 0.65313 | 4.157
2024-12-10 | 3:09 | Data | 0 | 35.458 | 34.769 | 122.037 | 7.64 | 116.351 | 2227.04 | 25.71 | 54.485 | 6.47 | 1.12 | 3.035 | 7518.2 | 0.878 | 97.5 | 73.1 | 1447 | 27.29 | 4886.8 | 2304.7 | 2351.2 | 3441.7 | 1223 | 0.65355 | 4.153
2024-12-10 | 3:09 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.396 | 2227.04 | 25.71 | 54.485 | 6.47 | 1.125 | 3.039 | 7495.59 | 0.918 | 97.6 | 73 | 1448 | 27.24 | 4872.1 | 2312.1 | 2361.7 | 3458.6 | 1223 | 0.65207 | 4.164
2024-12-10 | 3:09 | Data | 0 | 35.485 | 34.769 | 122.083 | 7.64 | 116.396 | 2227.95 | 25.71 | 54.485 | 6.48 | 1.119 | 3.05 | 7504.64 | 0.891 | 97.6 | 73.1 | 1448 | 27.24 | 4878 | 2312.6 | 2352 | 3442.1 | 1223 | 0.65589 | 4.17
2024-12-10 | 3:09 | Data | 0 | 35.485 | 34.789 | 122.037 | 7.64 | 116.351 | 2227.04 | 25.72 | 54.846 | 6.47 | 1.131 | 3.042 | 7513.68 | 0.871 | 97.5 | 72.9 | 1448 | 27.42 | 4883.9 | 2300.9 | 2356.8 | 3443.4 | 1223 | 0.65156 | 4.172
2024-12-10 | 3:09 | Data | 0 | 35.654 | 34.796 | 122.083 | 7.64 | 116.396 | 2227.95 | 25.71 | 54.575 | 6.47 | 1.121 | 3.028 | 7518.2 | 0.911 | 97.6 | 73 | 1448 | 27.29 | 4886.8 | 2320.6 | 2361.4 | 3456.8 | 1223 | 0.65521 | 4.148
2024-12-10 | 3:09 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.396 | 2232.47 | 25.71 | 54.575 | 6.47 | 1.128 | 3.027 | 7531.77 | 0.918 | 97.6 | 72.9 | 1451 | 27.24 | 4895.6 | 2295.8 | 2346.9 | 3437.5 | 1223 | 0.65275 | 4.156
2024-12-10 | 3:09 | Data | 0 | 35.714 | 34.796 | 122.128 | 7.64 | 116.441 | 2230.66 | 25.71 | 54.485 | 6.47 | 1.124 | 3.042 | 7549.86 | 0.918 | 97.6 | 73 | 1450 | 27.24 | 4907.4 | 2319.5 | 2343.6 | 3445 | 1223 | 0.65773 | 4.166
2024-12-10 | 3:09 | Data | 0 | 35.708 | 34.567 | 122.037 | 7.64 | 116.441 | 2227.04 | 25.71 | 54.485 | 6.47 | 1.122 | 3.048 | 7531.77 | 0.959 | 97.6 | 73.1 | 1448 | 27.29 | 4895.6 | 2313 | 2349.7 | 3445.4 | 1223 | 0.65589 | 4.172
2024-12-10 | 3:09 | Data | 0 | 35.654 | 34.796 | 122.173 | 7.64 | 116.441 | 2232.47 | 25.71 | 54.575 | 6.47 | 1.12 | 3.046 | 7531.77 | 0.891 | 97.6 | 73.1 | 1452 | 27.29 | 4895.6 | 2310.8 | 2334.9 | 3433.4 | 1223 | 0.65661 | 4.167
2024-12-10 | 3:09 | Data | 0 | 35.539 | 34.796 | 122.128 | 7.64 | 116.441 | 2230.66 | 25.71 | 54.575 | 6.47 | 1.127 | 3.055 | 7527.25 | 0.716 | 97.6 | 73.1 | 1449 | 27.24 | 4892.7 | 2318.9 | 2382.5 | 3470.3 | 1223 | 0.65196 | 4.182
2024-12-10 | 3:09 | Data | 0 | 35.512 | 34.567 | 122.128 | 7.64 | 116.351 | 2229.75 | 25.71 | 54.485 | 6.47 | 1.127 | 3.054 | 7531.77 | 0.925 | 97.6 | 73 | 1450 | 27.29 | 4895.6 | 2289.1 | 2375.1 | 3448.1 | 1223 | 0.65026 | 4.18
2024-12-10 | 3:10 | Data | 0 | 35.654 | 34.789 | 122.128 | 7.64 | 116.396 | 2235.18 | 25.71 | 54.485 | 6.47 | 1.121 | 3.052 | 7549.86 | 1.019 | 97.6 | 73.1 | 1453 | 27.24 | 4907.4 | 2316.8 | 2356.9 | 3450.9 | 1223 | 0.65453 | 4.172
2024-12-10 | 3:10 | Data | 0 | 35.498 | 34.594 | 122.083 | 7.64 | 116.441 | 2230.66 | 25.71 | 54.214 | 6.47 | 1.119 | 3.046 | 7549.86 | 0.864 | 97.6 | 73.1 | 1450 | 27.11 | 4907.4 | 2298.1 | 2339.2 | 3426.4 | 1223 | 0.65365 | 4.165
2024-12-10 | 3:10 | Data | 0 | 35.627 | 34.796 | 122.128 | 7.64 | 116.396 | 2238.79 | 25.72 | 54.485 | 6.47 | 1.126 | 3.046 | 7549.86 | 0.905 | 97.6 | 73 | 1454 | 27.24 | 4907.4 | 2309.4 | 2338.7 | 3435.8 | 1223 | 0.6544 | 4.173
2024-12-10 | 3:10 | Data | 0 | 35.485 | 34.594 | 122.037 | 7.64 | 116.396 | 2233.37 | 25.71 | 54.485 | 6.47 | 1.129 | 3.045 | 7513.68 | 0.803 | 97.6 | 73 | 1452 | 27.29 | 4883.9 | 1242.6 | 1716.7 | 2136.6 | 1223 | 0.58148 | 4.173
2024-12-10 | 3:10 | Data | 0 | 35.701 | 34.769 | 122.083 | 7.64 | 116.396 | 2228.85 | 25.71 | 54.575 | 6.47 | 1.132 | 3.037 | 7522.72 | 1.019 | 97.6 | 72.8 | 1449 | 27.29 | 4889.8 | 1214.5 | 1695.2 | 2103.7 | 1223 | 0.57718 | 4.17
2024-12-10 | 3:10 | Data | 0 | 35.539 | 34.796 | 122.083 | 7.64 | 116.441 | 2230.66 | 25.71 | 54.485 | 6.47 | 1.119 | 3.037 | 7929.72 | 0.722 | 97.6 | 73.1 | 1450 | 27.24 | 5154.3 | 1227.8 | 1697.6 | 2116.3 | 1223 | 0.58065 | 4.158
2024-12-10 | 3:10 | Data | 0 | 35.539 | 34.567 | 122.083 | 7.64 | 116.441 | 2229.75 | 25.71 | 54.665 | 6.47 | 1.121 | 3.056 | 7509.16 | 0.932 | 97.6 | 73.2 | 1449 | 27.29 | 4881 | 1227.4 | 1711.6 | 2121.7 | 1223 | 0.578 | 4.177
2024-12-10 | 3:10 | Data | 0 | 35.687 | 34.681 | 122.083 | 7.65 | 116.441 | 2235.18 | 25.71 | 54.575 | 6.47 | 1.131 | 3.051 | 7504.64 | 0.803 | 97.6 | 73 | 1452 | 27.29 | 4878 | 1213.4 | 1706.5 | 2112.4 | 1223 | 0.57391 | 4.181
2024-12-10 | 3:10 | Data | 0 | 35.701 | 34.796 | 122.128 | 7.64 | 116.351 | 2230.66 | 25.71 | 54.485 | 6.47 | 1.127 | 3.057 | 7509.16 | 0.743 | 97.6 | 73.1 | 1450 | 27.29 | 4881 | 1219.1 | 1678.3 | 2091.7 | 1223 | 0.58294 | 4.184
2024-12-10 | 3:10 | Data | 0 | 35.6 | 34.783 | 122.037 | 7.64 | 116.396 | 2232.47 | 25.71 | 54.575 | 6.47 | 1.128 | 3.05 | 7504.64 | 0.918 | 97.6 | 73 | 1452 | 27.24 | 4878 | 1229.1 | 1721.4 | 2133.7 | 1223 | 0.57711 | 4.178
2024-12-10 | 3:10 | Data | 0 | 35.505 | 34.783 | 122.128 | 7.64 | 116.396 | 2234.27 | 25.72 | 54.485 | 6.47 | 1.119 | 3.029 | 7522.72 | 0.743 | 97.6 | 73 | 1452 | 27.29 | 4889.8 | 1228.3 | 1711.8 | 2123 | 1223 | 0.58287 | 4.148
2024-12-10 | 3:10 | Data | 0 | 35.701 | 34.567 | 122.083 | 7.64 | 116.396 | 2230.66 | 25.71 | 54.485 | 6.47 | 1.131 | 3.029 | 7518.2 | 0.959 | 97.6 | 72.8 | 1449 | 27.24 | 4886.8 | 1221.6 | 1707.3 | 2117.5 | 1223 | 0.57586 | 4.16
2024-12-10 | 3:10 | Data | 0 | 35.714 | 34.573 | 122.173 | 7.64 | 116.396 | 2236.08 | 25.71 | 54.485 | 6.47 | 1.127 | 3.036 | 7504.64 | 0.959 | 97.6 | 72.9 | 1453 | 27.24 | 4878 | 1209.4 | 1698.5 | 2106.7 | 1223 | 0.57346 | 4.163
2024-12-10 | 3:10 | Data | 0 | 35.6 | 34.796 | 122.128 | 7.65 | 116.441 | 2236.08 | 25.71 | 54.575 | 6.47 | 1.13 | 3.025 | 7531.77 | 0.911 | 97.6 | 72.8 | 1453 | 27.24 | 4895.6 | 1220.7 | 1721 | 2130.2 | 1223 | 0.56805 | 4.154
2024-12-10 | 3:10 | Data | 0 | 35.586 | 34.654 | 122.037 | 7.64 | 116.396 | 2236.08 | 25.71 | 54.485 | 6.47 | 1.127 | 3.009 | 7522.72 | 0.938 | 97.6 | 72.8 | 1453 | 27.24 | 4889.8 | 1225.9 | 1710.3 | 2121.6 | 1223 | 0.57918 | 4.136
2024-12-10 | 3:10 | Data | 0 | 35.654 | 34.789 | 122.128 | 7.65 | 116.351 | 2233.37 | 25.71 | 54.485 | 6.47 | 1.122 | 3.013 | 7518.2 | 0.911 | 97.6 | 72.9 | 1452 | 27.29 | 4886.8 | 1219.1 | 1691.4 | 2103.1 | 1223 | 0.57771 | 4.135
2024-12-10 | 3:10 | Data | 0 | 35.485 | 34.695 | 122.037 | 7.64 | 116.396 | 2238.79 | 25.71 | 54.394 | 6.47 | 1.119 | 3.042 | 7518.2 | 1.073 | 97.6 | 73.1 | 1454 | 27.29 | 4886.8 | 1223.9 | 1688.7 | 2104.4 | 1223 | 0.58108 | 4.161
2024-12-10 | 3:10 | Data | 0 | 35.6 | 34.789 | 122.037 | 7.64 | 116.396 | 2233.37 | 25.71 | 54.033 | 6.48 | 1.122 | 3.056 | 7518.2 | 0.959 | 97.6 | 73.1 | 1452 | 27.02 | 4886.8 | 1219.3 | 1707.2 | 2116.9 | 1223 | 0.57868 | 4.179
2024-12-10 | 3:11 | Data | 0 | 35.512 | 34.567 | 122.083 | 7.64 | 116.441 | 2232.47 | 25.71 | 54.485 | 6.47 | 1.122 | 3.054 | 7509.16 | 0.918 | 97.6 | 73.1 | 1451 | 27.29 | 4881 | 1226.4 | 1702 | 2116.2 | 1223 | 0.57818 | 4.178
2024-12-10 | 3:11 | Data | 0 | 35.498 | 34.573 | 122.128 | 7.64 | 116.396 | 2230.66 | 25.71 | 54.575 | 6.47 | 1.129 | 3.059 | 7500.11 | 0.911 | 97.6 | 73 | 1450 | 27.29 | 4875.1 | 1238.3 | 1693.7 | 2119.2 | 1223 | 0.58334 | 4.188
2024-12-10 | 3:11 | Data | 0 | 35.701 | 34.688 | 122.128 | 7.64 | 116.396 | 2230.66 | 25.71 | 54.575 | 6.47 | 1.121 | 3.069 | 7504.64 | 1.121 | 97.6 | 73.3 | 1450 | 27.24 | 4878 | 1239.5 | 1690 | 2113.5 | 1223 | 0.58614 | 4.189
2024-12-10 | 3:11 | Data | 0 | 35.701 | 34.688 | 122.173 | 7.64 | 116.441 | 2230.66 | 25.71 | 54.575 | 6.47 | 1.118 | 3.031 | 7491.07 | 0.979 | 97.6 | 73.1 | 1449 | 27.24 | 4869.2 | 1244.7 | 1694.8 | 2118.7 | 1223 | 0.58733 | 4.148
2024-12-10 | 3:11 | Data | 0 | 35.539 | 34.594 | 122.083 | 7.64 | 116.396 | 2227.95 | 25.71 | 54.485 | 6.47 | 1.121 | 3.044 | 7509.16 | 0.871 | 97.6 | 73.1 | 1448 | 27.24 | 4881 | 1214.8 | 1676.1 | 2085.3 | 1223 | 0.57719 | 4.165
2024-12-10 | 3:11 | Data | 0 | 35.593 | 34.796 | 122.083 | 7.64 | 116.441 | 2228.85 | 25.71 | 54.485 | 6.47 | 1.122 | 3.04 | 7518.2 | 0.918 | 97.6 | 73 | 1449 | 27.29 | 4886.8 | 1234.2 | 1705.1 | 2123.8 | 1223 | 0.58301 | 4.164
2024-12-10 | 3:11 | Data | 0 | 35.573 | 34.567 | 122.083 | 7.65 | 116.441 | 2232.47 | 25.71 | 54.575 | 6.47 | 1.129 | 3.05 | 7504.64 | 0.938 | 97.6 | 73 | 1451 | 27.29 | 4878 | 1222.7 | 1704.2 | 2115.2 | 1223 | 0.57776 | 4.18
2024-12-10 | 3:11 | Data | 0 | 35.6 | 34.789 | 122.128 | 7.64 | 116.396 | 2230.66 | 25.71 | 54.485 | 6.47 | 1.126 | 3.064 | 7504.64 | 0.918 | 97.6 | 73.1 | 1450 | 27.29 | 4878 | 1224.8 | 1701.5 | 2114.5 | 1223 | 0.57945 | 4.19
2024-12-10 | 3:11 | Data | 0 | 35.728 | 34.594 | 122.173 | 7.64 | 116.396 | 2231.56 | 25.71 | 54.485 | 6.47 | 1.121 | 3.046 | 7522.72 | 1.04 | 97.6 | 73.1 | 1451 | 27.29 | 4889.8 | 1229.2 | 1690.3 | 2108.7 | 1223 | 0.58318 | 4.168
2024-12-10 | 3:11 | Data | 0 | 35.539 | 34.573 | 122.128 | 7.64 | 116.306 | 2233.37 | 25.71 | 54.575 | 6.47 | 1.131 | 3.029 | 7500.11 | 0.918 | 97.6 | 72.8 | 1451 | 27.29 | 4875.1 | 1221.5 | 1678.7 | 2097.3 | 1223 | 0.58155 | 4.159
2024-12-10 | 3:11 | Data | 0 | 35.458 | 34.742 | 122.083 | 7.64 | 116.351 | 2231.56 | 25.71 | 54.485 | 6.47 | 1.127 | 3.037 | 7500.11 | 0.905 | 97.6 | 72.9 | 1451 | 27.29 | 4875.1 | 1218.2 | 1699.1 | 2112.3 | 1223 | 0.57557 | 4.164
2024-12-10 | 3:11 | Data | 0 | 35.491 | 34.567 | 122.037 | 7.64 | 116.351 | 2233.37 | 25.71 | 54.485 | 6.47 | 1.124 | 3.047 | 7504.64 | 0.918 | 97.6 | 73.1 | 1452 | 27.29 | 4878 | 1233.8 | 1706.6 | 2128.8 | 1223 | 0.57809 | 4.171
2024-12-10 | 3:11 | Data | 0 | 35.755 | 34.594 | 122.128 | 7.64 | 116.441 | 2230.66 | 25.71 | 54.485 | 6.47 | 1.118 | 3.057 | 7504.64 | 0.898 | 97.6 | 73.2 | 1449 | 27.24 | 4878 | 1218.1 | 1687.5 | 2100.9 | 1223 | 0.58029 | 4.176
2024-12-10 | 3:11 | Data | 0 | 35.37 | 34.567 | 121.992 | 7.64 | 116.396 | 2235.18 | 25.71 | 54.304 | 6.48 | 1.122 | 3.054 | 7504.64 | 0.749 | 97.6 | 73.1 | 1453 | 27.15 | 4878 | 1194.4 | 1707.7 | 2110.3 | 1223 | 0.56736 | 4.176
2024-12-10 | 3:11 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.351 | 2227.95 | 25.71 | 54.304 | 6.47 | 1.128 | 3.053 | 7504.64 | 0.918 | 97.6 | 73 | 1448 | 27.15 | 4878 | 1221.2 | 1689.1 | 2102.9 | 1223 | 0.58233 | 4.18
2024-12-10 | 3:11 | Data | 0 | 35.714 | 34.58 | 122.173 | 7.64 | 116.487 | 2229.75 | 25.71 | 54.304 | 6.47 | 1.129 | 3.036 | 7504.64 | 0.945 | 97.6 | 72.9 | 1449 | 27.15 | 4878 | 1223.7 | 1696.1 | 2112.2 | 1223 | 0.57952 | 4.166
2024-12-10 | 3:11 | Data | 0 | 35.714 | 34.621 | 122.083 | 7.64 | 116.441 | 2227.95 | 25.71 | 54.485 | 6.47 | 1.124 | 3.052 | 7509.16 | 1.033 | 97.6 | 73.1 | 1448 | 27.2 | 4881 | 1228.8 | 1708.1 | 2121.2 | 1223 | 0.57649 | 4.173
2024-12-10 | 3:11 | Data | 0 | 35.458 | 34.567 | 122.037 | 7.64 | 116.351 | 2227.95 | 25.71 | 54.304 | 6.47 | 1.129 | 3.05 | 7518.2 | 0.911 | 97.6 | 73 | 1448 | 27.11 | 4886.8 | 1229.1 | 1688.5 | 2108.8 | 1223 | 0.5836 | 4.179
2024-12-10 | 3:12 | Data | 0 | 35.498 | 34.567 | 122.037 | 7.64 | 116.396 | 2227.95 | 25.71 | 54.214 | 6.47 | 1.128 | 3.05 | 7509.16 | 0.925 | 97.6 | 73 | 1448 | 27.11 | 4881 | 1227.6 | 1684.1 | 2104.6 | 1223 | 0.58227 | 4.179
2024-12-10 | 3:12 | Data | 0 | 35.485 | 34.634 | 121.992 | 7.64 | 116.396 | 2222.52 | 25.71 | 54.665 | 6.47 | 1.119 | 3.044 | 7518.2 | 1.006 | 97.5 | 73.1 | 1445 | 27.29 | 4886.8 | 1216.2 | 1701.4 | 2110.1 | 1223 | 0.57622 | 4.161
2024-12-10 | 3:12 | Data | 0 | 35.262 | 34.56 | 122.037 | 7.65 | 116.306 | 2227.95 | 25.71 | 54.394 | 6.47 | 1.129 | 3.045 | 7513.68 | 0.824 | 97.6 | 73 | 1448 | 27.2 | 4883.9 | 1222.6 | 1709.5 | 2122.7 | 1223 | 0.57546 | 4.173
2024-12-10 | 3:12 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2226.14 | 25.71 | 54.394 | 6.47 | 1.126 | 3.045 | 7495.59 | 0.918 | 97.6 | 73 | 1447 | 27.15 | 4872.1 | 1220.1 | 1704.4 | 2115.5 | 1223 | 0.57871 | 4.171
2024-12-10 | 3:12 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2116.78 | 25.71 | 54.575 | 6.48 | 1.128 | 3.05 | 7500.11 | 0.918 | 97.4 | 73 | 1376 | 27.29 | 4875.1 | 1234.9 | 1692.5 | 2113.4 | 1223 | 0.58342 | 4.178
2024-12-10 | 3:12 | Data | 0 | 35.316 | 34.567 | 122.037 | 7.64 | 116.306 | 2227.04 | 25.71 | 54.575 | 6.47 | 1.13 | 3.038 | 7491.07 | 0.898 | 97.5 | 72.9 | 1448 | 27.24 | 4869.2 | 1227.7 | 1696.8 | 2109.4 | 1223 | 0.58176 | 4.168
2024-12-10 | 3:12 | Data | 0 | 35.485 | 34.594 | 121.992 | 7.64 | 116.351 | 2227.95 | 25.71 | 54.033 | 6.47 | 1.131 | 3.034 | 7477.5 | 0.871 | 97.6 | 72.8 | 1448 | 27.02 | 4860.4 | 1219.9 | 1678.8 | 2096.7 | 1223 | 0.5804 | 4.167
2024-12-10 | 3:12 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.306 | 2227.95 | 25.71 | 53.943 | 6.47 | 1.134 | 3.052 | 7509.16 | 0.918 | 97.6 | 72.9 | 1448 | 26.97 | 4881 | 1227.2 | 1695.5 | 2111.6 | 1223 | 0.58267 | 4.186
2024-12-10 | 3:12 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.261 | 2227.95 | 25.71 | 54.485 | 6.47 | 1.12 | 3.045 | 7504.64 | 0.918 | 97.6 | 73.1 | 1448 | 27.29 | 4878 | 1216.7 | 1682.8 | 2109.4 | 1223 | 0.58128 | 4.165
2024-12-10 | 3:12 | Data | 0 | 35.539 | 34.567 | 121.992 | 7.64 | 116.396 | 2227.04 | 25.71 | 54.394 | 6.47 | 1.121 | 3.036 | 7509.16 | 0.756 | 97.6 | 73 | 1448 | 27.15 | 4881 | 1219.7 | 1684 | 2099.4 | 1223 | 0.58331 | 4.158
2024-12-10 | 3:12 | Data | 0 | 35.377 | 34.681 | 121.992 | 7.64 | 116.396 | 2227.95 | 25.71 | 54.304 | 6.47 | 1.121 | 3.05 | 7509.16 | 0.905 | 97.6 | 73.1 | 1448 | 27.15 | 4881 | 1227.7 | 1699.3 | 2120.7 | 1223 | 0.58204 | 4.171
2024-12-10 | 3:12 | Data | 0 | 35.262 | 34.553 | 121.947 | 7.64 | 116.306 | 2227.04 | 25.71 | 54.485 | 6.47 | 1.133 | 3.048 | 7491.07 | 0.952 | 97.6 | 72.9 | 1447 | 27.24 | 4869.2 | 1232.8 | 1695.7 | 2115.7 | 1223 | 0.58258 | 4.181
2024-12-10 | 3:12 | Data | 0 | 35.485 | 34.58 | 122.037 | 7.64 | 116.351 | 2230.66 | 25.72 | 54.214 | 6.47 | 1.13 | 3.048 | 7491.07 | 0.905 | 97.6 | 73 | 1450 | 27.15 | 4869.2 | 1213.6 | 1689.3 | 2098.2 | 1223 | 0.5791 | 4.178
2024-12-10 | 3:12 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.306 | 2224.33 | 25.71 | 54.214 | 6.47 | 1.118 | 3.053 | 7495.59 | 0.918 | 97.6 | 73.2 | 1446 | 27.11 | 4872.1 | 1217.1 | 1684.8 | 2098.4 | 1223 | 0.57914 | 4.17
2024-12-10 | 3:12 | Data | 0 | 35.654 | 34.567 | 122.128 | 7.64 | 116.396 | 2222.52 | 25.71 | 54.214 | 6.47 | 1.12 | 3.023 | 7495.59 | 0.959 | 97.6 | 73 | 1445 | 27.15 | 4872.1 | 1215.6 | 1693.4 | 2101.7 | 1223 | 0.57973 | 4.142
2024-12-10 | 3:12 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.351 | 2222.52 | 25.71 | 54.214 | 6.47 | 1.121 | 3.063 | 7504.64 | 0.918 | 97.6 | 73.2 | 1445 | 27.11 | 4878 | 1214.9 | 1690 | 2100.2 | 1223 | 0.57872 | 4.184
2024-12-10 | 3:12 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2218.91 | 25.71 | 54.485 | 6.47 | 1.127 | 3.063 | 7477.5 | 0.716 | 97.5 | 73.1 | 1442 | 27.29 | 4860.4 | 1224.2 | 1652 | 2076.6 | 1223 | 0.58873 | 4.189
2024-12-10 | 3:12 | Data | 0 | 35.708 | 34.594 | 122.083 | 7.64 | 116.351 | 2218.91 | 25.71 | 54.304 | 6.47 | 1.127 | 3.043 | 7482.02 | 0.918 | 97.6 | 73 | 1443 | 27.11 | 4863.3 | 1217.4 | 1686.4 | 2100.2 | 1223.1 | 0.57998 | 4.168
2024-12-10 | 3:13 | Data | 0 | 35.708 | 34.681 | 122.128 | 7.64 | 116.351 | 2218.91 | 25.71 | 54.304 | 6.47 | 1.129 | 3.059 | 7482.02 | 0.918 | 97.6 | 73 | 1442 | 27.15 | 4863.3 | 1206.7 | 1672.4 | 2081.4 | 1223.1 | 0.57842 | 4.188
2024-12-10 | 3:13 | Data | 0 | 35.687 | 34.567 | 122.083 | 7.64 | 116.441 | 2216.2 | 25.71 | 54.575 | 6.47 | 1.135 | 3.024 | 7477.5 | 0.972 | 97.5 | 72.7 | 1441 | 27.24 | 4860.4 | 1209.6 | 1663 | 2073.7 | 1223.1 | 0.58347 | 4.161
2024-12-10 | 3:13 | Data | 0 | 35.485 | 34.56 | 121.947 | 7.64 | 116.306 | 2217.1 | 25.71 | 54.485 | 6.47 | 1.13 | 3.016 | 7477.5 | 0.932 | 97.5 | 72.8 | 1441 | 27.24 | 4860.4 | 1211.4 | 1683.7 | 2094 | 1223.1 | 0.57674 | 4.146
2024-12-10 | 3:13 | Data | 0 | 35.512 | 34.351 | 121.992 | 7.64 | 116.441 | 2215.29 | 25.71 | 54.575 | 6.47 | 1.119 | 3.031 | 7491.07 | 0.938 | 97.5 | 73 | 1440 | 27.24 | 4869.2 | 1223.3 | 1691.6 | 2107.3 | 1223.1 | 0.57941 | 4.15
2024-12-10 | 3:13 | Data | 0 | 35.37 | 34.567 | 121.947 | 7.64 | 116.351 | 2216.2 | 25.71 | 54.575 | 6.47 | 1.116 | 3.029 | 7472.98 | 0.749 | 97.5 | 73.1 | 1441 | 27.29 | 4857.4 | 1232.5 | 1693 | 2111 | 1223.1 | 0.5844 | 4.144
2024-12-10 | 3:13 | Data | 0 | 35.485 | 34.391 | 121.992 | 7.64 | 116.351 | 2216.2 | 25.71 | 54.304 | 6.47 | 1.117 | 3.033 | 7491.07 | 1.094 | 97.5 | 73.1 | 1441 | 27.15 | 4869.2 | 1229.6 | 1681.1 | 2100.9 | 1223.1 | 0.58504 | 4.149
2024-12-10 | 3:13 | Data | 0 | 35.654 | 34.776 | 122.083 | 7.64 | 116.351 | 2217.1 | 25.71 | 54.394 | 6.47 | 1.119 | 3.031 | 7500.11 | 0.932 | 97.5 | 73 | 1441 | 27.15 | 4875.1 | 1211.7 | 1677.6 | 2089.7 | 1223.1 | 0.57793 | 4.151
2024-12-10 | 3:13 | Data | 0 | 35.431 | 34.391 | 121.992 | 7.64 | 116.306 | 2217.1 | 25.71 | 54.485 | 6.47 | 1.116 | 3.026 | 7495.59 | 1.087 | 97.5 | 73.1 | 1441 | 27.24 | 4872.1 | 1212.7 | 1686.5 | 2094.9 | 1223.1 | 0.57757 | 4.142
2024-12-10 | 3:13 | Data | 0 | 35.485 | 34.391 | 121.992 | 7.64 | 116.306 | 2215.29 | 25.71 | 54.575 | 6.47 | 1.121 | 3.023 | 7491.07 | 1.033 | 97.5 | 73 | 1441 | 27.29 | 4869.2 | 1209.4 | 1690.6 | 2095.7 | 1223.1 | 0.57693 | 4.143
2024-12-10 | 3:13 | Data | 0 | 35.262 | 34.513 | 121.947 | 7.64 | 116.351 | 2318.33 | 25.71 | 54.485 | 6.47 | 1.131 | 3.044 | 7504.64 | 0.918 | 97.7 | 72.9 | 1509 | 27.24 | 4878 | 1222.4 | 1702.7 | 2114.9 | 1223.1 | 0.57687 | 4.176
2024-12-10 | 3:13 | Data | 0 | 35.694 | 34.567 | 122.083 | 7.64 | 116.306 | 2247.83 | 25.71 | 54.485 | 6.47 | 1.122 | 3.041 | 7509.16 | 1.026 | 97.6 | 73 | 1459 | 27.24 | 4881 | 1225.5 | 1698.1 | 2108.1 | 1223.1 | 0.57648 | 4.163
2024-12-10 | 3:13 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2227.04 | 25.71 | 54.575 | 6.47 | 1.116 | 3.046 | 7504.64 | 0.918 | 97.5 | 73.2 | 1447 | 27.29 | 4878 | 1223.6 | 1695.5 | 2109 | 1223.1 | 0.57813 | 4.161
2024-12-10 | 3:13 | Data | 0 | 35.485 | 34.783 | 122.083 | 7.64 | 116.306 | 2222.52 | 25.71 | 54.485 | 6.47 | 1.129 | 3.035 | 7509.16 | 0.749 | 97.5 | 72.9 | 1444 | 27.29 | 4881 | 1216.4 | 1693 | 2104.4 | 1223.1 | 0.57727 | 4.163
2024-12-10 | 3:13 | Data | 0 | 35.485 | 34.54 | 121.947 | 7.64 | 116.306 | 2225.23 | 25.71 | 54.575 | 6.47 | 1.121 | 3.042 | 7509.16 | 0.857 | 97.6 | 73.1 | 1446 | 27.24 | 4881 | 1221.5 | 1675.4 | 2096.4 | 1223.1 | 0.58137 | 4.162
2024-12-10 | 3:13 | Data | 0 | 35.471 | 34.594 | 122.037 | 7.64 | 116.351 | 2224.33 | 25.71 | 54.485 | 6.47 | 1.122 | 3.04 | 7531.77 | 1.019 | 97.6 | 73 | 1446 | 27.29 | 4895.6 | 1230.4 | 1699.3 | 2115.1 | 1223.1 | 0.581 | 4.163
2024-12-10 | 3:13 | Data | 0 | 35.478 | 34.567 | 122.083 | 7.64 | 116.306 | 2224.33 | 25.71 | 54.485 | 6.47 | 1.124 | 3.031 | 7531.77 | 0.918 | 97.6 | 72.9 | 1446 | 27.24 | 4895.6 | 1237.7 | 1677.7 | 2102 | 1223.1 | 0.58664 | 4.155
2024-12-10 | 3:13 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2225.23 | 25.71 | 54.485 | 6.47 | 1.124 | 3.037 | 7504.64 | 0.918 | 97.6 | 73 | 1446 | 27.24 | 4878 | 1219 | 1688.1 | 2101.3 | 1223.1 | 0.58015 | 4.162
2024-12-10 | 3:14 | Data | 0 | 35.262 | 34.722 | 121.902 | 7.64 | 116.306 | 2225.23 | 25.7 | 54.575 | 6.47 | 1.132 | 3.034 | 7531.77 | 0.857 | 97.5 | 72.8 | 1446 | 27.29 | 4895.6 | 1220.5 | 1691 | 2105.2 | 1223.1 | 0.57917 | 4.167
2024-12-10 | 3:14 | Data | 0 | 35.478 | 34.567 | 122.037 | 7.64 | 116.351 | 2222.52 | 25.7 | 54.575 | 6.47 | 1.124 | 3.05 | 7545.34 | 0.918 | 97.5 | 73.1 | 1445 | 27.29 | 4904.5 | 1223.3 | 1692.3 | 2108.1 | 1223.1 | 0.57853 | 4.172
2024-12-10 | 3:14 | Data | 0 | 35.431 | 34.567 | 121.947 | 7.64 | 116.261 | 2225.23 | 25.71 | 54.485 | 6.47 | 1.121 | 3.042 | 7563.42 | 1.026 | 97.6 | 73.1 | 1446 | 27.24 | 4916.2 | 1201.5 | 1675.8 | 2084.1 | 1223.1 | 0.57547 | 4.162
2024-12-10 | 3:14 | Data | 0 | 35.478 | 34.567 | 121.947 | 7.64 | 116.306 | 2225.23 | 25.72 | 54.575 | 6.48 | 1.126 | 3.045 | 7576.99 | 0.918 | 97.5 | 73 | 1446 | 27.29 | 4925 | 1221.4 | 1695.7 | 2111 | 1223.1 | 0.5748 | 4.17
2024-12-10 | 3:14 | Data | 0 | 35.431 | 34.384 | 121.992 | 7.64 | 116.306 | 2225.23 | 25.72 | 54.485 | 6.47 | 1.121 | 3.034 | 7576.99 | 0.918 | 97.6 | 73 | 1446 | 27.29 | 4925 | 1211 | 1691.1 | 2100.9 | 1223.1 | 0.57561 | 4.155
2024-12-10 | 3:14 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.306 | 2224.33 | 25.71 | 54.575 | 6.47 | 1.118 | 3.035 | 7563.42 | 0.918 | 97.6 | 73.1 | 1446 | 27.24 | 4916.2 | 1236.3 | 1696.7 | 2117 | 1223.1 | 0.5856 | 4.151
2024-12-10 | 3:14 | Data | 0 | 35.471 | 34.735 | 121.992 | 7.64 | 116.306 | 2225.23 | 25.71 | 54.485 | 6.47 | 1.121 | 3.033 | 7554.38 | 0.918 | 97.6 | 73 | 1447 | 27.24 | 4910.3 | 1214 | 1686.5 | 2093.4 | 1223.1 | 0.58032 | 4.153
2024-12-10 | 3:14 | Data | 0 | 35.539 | 34.411 | 122.037 | 7.64 | 116.351 | 2223.43 | 25.71 | 54.485 | 6.47 | 1.124 | 3.034 | 7545.34 | 0.918 | 97.5 | 72.9 | 1445 | 27.24 | 4904.5 | 1219.9 | 1695.7 | 2109.6 | 1223.1 | 0.57709 | 4.155
2024-12-10 | 3:14 | Data | 0 | 35.262 | 34.54 | 121.992 | 7.64 | 116.261 | 2222.52 | 25.72 | 54.846 | 6.47 | 1.128 | 3.028 | 7527.25 | 0.803 | 97.5 | 72.9 | 1445 | 27.38 | 4892.7 | 1224.1 | 1679.7 | 2097.1 | 1223.1 | 0.5819 | 4.156
2024-12-10 | 3:14 | Data | 0 | 35.458 | 34.58 | 121.992 | 7.64 | 116.351 | 2214.39 | 25.71 | 54.485 | 6.47 | 1.122 | 3.039 | 7549.86 | 0.945 | 97.5 | 73 | 1439 | 27.24 | 4907.4 | 1231 | 1716.3 | 2130.2 | 1223.1 | 0.57752 | 4.161
2024-12-10 | 3:14 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.306 | 2218.91 | 25.71 | 54.575 | 6.47 | 1.121 | 3.052 | 7545.34 | 0.918 | 97.5 | 73.1 | 1442 | 27.24 | 4904.5 | 1355 | 2186.8 | 2103.8 | 1223.1 | 0.57627 | 4.173
2024-12-10 | 3:14 | Data | 0 | 35.478 | 34.567 | 121.992 | 7.64 | 116.306 | 2220.72 | 25.71 | 54.575 | 6.47 | 1.121 | 3.045 | 7531.77 | 0.918 | 97.5 | 73.1 | 1443 | 27.24 | 4895.6 | 2303.5 | 2360.1 | 3446.9 | 1223.1 | 0.65284 | 4.166
2024-12-10 | 3:14 | Data | 0 | 35.37 | 34.351 | 121.992 | 7.64 | 116.306 | 2216.2 | 25.71 | 54.485 | 6.48 | 1.126 | 3.053 | 7549.86 | 0.79 | 97.5 | 73 | 1441 | 27.29 | 4907.4 | 2283.5 | 2351.9 | 3426.7 | 1223.1 | 0.65135 | 4.18
2024-12-10 | 3:14 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.396 | 2213.49 | 25.71 | 54.575 | 6.47 | 1.121 | 3.045 | 7563.42 | 0.905 | 97.5 | 73.1 | 1438 | 27.29 | 4916.2 | 2299 | 2364.9 | 3444.1 | 1223.1 | 0.65164 | 4.165
2024-12-10 | 3:14 | Data | 0 | 35.485 | 34.391 | 121.947 | 7.64 | 116.306 | 2210.77 | 25.71 | 54.575 | 6.47 | 1.134 | 3.022 | 7549.86 | 1.094 | 97.5 | 72.7 | 1437 | 27.24 | 4907.4 | 2320.6 | 2344.7 | 3448.8 | 1223.1 | 0.65513 | 4.156
2024-12-10 | 3:14 | Data | 0 | 35.512 | 34.567 | 122.037 | 7.64 | 116.351 | 2213.49 | 25.71 | 54.575 | 6.47 | 1.131 | 3.017 | 7545.34 | 0.918 | 97.5 | 72.7 | 1439 | 27.29 | 4904.5 | 2327.9 | 2345 | 3448.6 | 1223.1 | 0.65889 | 4.148
2024-12-10 | 3:14 | Data | 0 | 35.478 | 34.567 | 121.992 | 7.64 | 116.306 | 2213.49 | 25.72 | 54.575 | 6.47 | 1.129 | 3.039 | 7554.38 | 0.932 | 97.5 | 72.9 | 1439 | 27.29 | 4910.3 | 2307.3 | 2368.5 | 3452.8 | 1223.1 | 0.65409 | 4.168
2024-12-10 | 3:14 | Data | 0 | 35.309 | 34.364 | 121.992 | 7.64 | 116.306 | 2210.77 | 25.71 | 54.485 | 6.47 | 1.131 | 3.041 | 7531.77 | 0.878 | 97.5 | 72.9 | 1437 | 27.29 | 4895.6 | 2315.4 | 2336 | 3441.5 | 1223.1 | 0.65748 | 4.171
2024-12-10 | 3:15 | Data | 0 | 35.471 | 34.567 | 122.037 | 7.64 | 116.351 | 2210.77 | 25.7 | 54.575 | 6.47 | 1.131 | 3.031 | 7531.77 | 0.972 | 97.5 | 72.8 | 1437 | 27.29 | 4895.6 | 2283.8 | 2350.1 | 3426.1 | 1223.1 | 0.64977 | 4.162
2024-12-10 | 3:15 | Data | 0 | 35.478 | 34.567 | 121.947 | 7.64 | 116.261 | 2210.77 | 25.7 | 54.485 | 6.47 | 1.13 | 3.043 | 7522.72 | 0.891 | 97.5 | 72.9 | 1438 | 27.24 | 4889.8 | 2317.1 | 2361.8 | 3459.6 | 1223.1 | 0.6534 | 4.172
2024-12-10 | 3:15 | Data | 0 | 35.255 | 34.56 | 121.902 | 7.64 | 116.306 | 2208.97 | 25.7 | 54.575 | 6.47 | 1.13 | 3.036 | 7518.2 | 0.81 | 97.5 | 72.9 | 1436 | 27.29 | 4886.8 | 2307 | 2335.7 | 3433.9 | 1223.1 | 0.65426 | 4.166
2024-12-10 | 3:15 | Data | 0 | 35.485 | 34.769 | 121.992 | 7.64 | 116.351 | 2208.97 | 25.69 | 54.485 | 6.47 | 1.132 | 3.044 | 7518.2 | 0.749 | 97.5 | 72.9 | 1436 | 27.29 | 4886.8 | 2316.8 | 2343.2 | 3442.4 | 1223.1 | 0.65799 | 4.176
2024-12-10 | 3:15 | Data | 0 | 35.255 | 34.513 | 121.947 | 7.64 | 116.306 | 2208.97 | 25.69 | 54.485 | 6.47 | 1.121 | 3.06 | 7504.64 | 0.918 | 97.5 | 73.2 | 1435 | 27.24 | 4878 | 2307.3 | 2336.1 | 3434.6 | 1223.1 | 0.65478 | 4.18
2024-12-10 | 3:15 | Data | 0 | 35.37 | 34.553 | 121.947 | 7.64 | 116.306 | 2208.97 | 25.68 | 54.575 | 6.48 | 1.126 | 3.054 | 7513.68 | 0.891 | 97.5 | 73.1 | 1435 | 27.24 | 4883.9 | 2300.1 | 2353.7 | 3446.9 | 1223.1 | 0.65067 | 4.18
2024-12-10 | 3:15 | Data | 0 | 35.255 | 34.54 | 121.947 | 7.64 | 116.261 | 2123.1 | 25.68 | 54.394 | 6.47 | 1.124 | 3.03 | 7504.64 | 0.803 | 97.4 | 72.9 | 1379 | 27.24 | 4878 | 2302.8 | 2364.8 | 3450.3 | 1223.1 | 0.64983 | 4.154
2024-12-10 | 3:15 | Data | 0 | 35.485 | 34.654 | 122.037 | 7.64 | 116.306 | 2203.54 | 25.67 | 54.485 | 6.47 | 1.124 | 3.036 | 7495.59 | 0.918 | 97.5 | 73 | 1433 | 27.29 | 4872.1 | 2312.5 | 2336.6 | 3436.5 | 1223.1 | 0.65776 | 4.161
2024-12-10 | 3:15 | Data | 0 | 35.269 | 34.567 | 122.037 | 7.64 | 116.306 | 2206.25 | 25.68 | 54.575 | 6.47 | 1.125 | 3.05 | 7491.07 | 0.864 | 97.5 | 73.1 | 1434 | 27.29 | 4869.2 | 2308.4 | 2373.2 | 3460.2 | 1223.1 | 0.65273 | 4.175
2024-12-10 | 3:15 | Data | 0 | 35.255 | 34.56 | 121.992 | 7.64 | 116.306 | 2207.16 | 25.67 | 54.575 | 6.47 | 1.12 | 3.036 | 7495.59 | 0.891 | 97.5 | 73.1 | 1435 | 27.29 | 4872.1 | 2285.2 | 2355.7 | 3429.4 | 1223.1 | 0.65002 | 4.156
2024-12-10 | 3:15 | Data | 0 | 35.269 | 34.553 | 121.947 | 7.64 | 116.306 | 2210.77 | 25.67 | 54.485 | 6.47 | 1.118 | 3.026 | 7513.68 | 0.743 | 97.5 | 73 | 1438 | 27.24 | 4883.9 | 2304.8 | 2345 | 3442.4 | 1223.1 | 0.65422 | 4.144
2024-12-10 | 3:15 | Data | 0 | 35.377 | 34.567 | 121.947 | 7.64 | 116.306 | 2228.85 | 25.67 | 54.485 | 6.47 | 1.114 | 3.024 | 7509.16 | 0.749 | 97.6 | 73.1 | 1448 | 27.29 | 4881 | 2306 | 2352.1 | 3438.7 | 1223.1 | 0.65389 | 4.137
2024-12-10 | 3:15 | Data | 0 | 35.485 | 34.364 | 121.992 | 7.64 | 116.351 | 2227.04 | 25.68 | 54.575 | 6.47 | 1.124 | 3.029 | 7522.72 | 1.094 | 97.5 | 72.9 | 1448 | 27.29 | 4889.8 | 2301.5 | 2362.3 | 3452.1 | 1223.1 | 0.65126 | 4.155
2024-12-10 | 3:15 | Data | 0 | 35.478 | 34.567 | 121.992 | 7.64 | 116.306 | 2229.75 | 25.68 | 54.485 | 6.47 | 1.127 | 3.036 | 7527.25 | 0.918 | 97.6 | 72.9 | 1449 | 27.24 | 4892.7 | 2301.2 | 2363.2 | 3442 | 1223.1 | 0.6529 | 4.163
2024-12-10 | 3:15 | Data | 0 | 35.431 | 34.398 | 121.947 | 7.64 | 116.351 | 2229.75 | 25.67 | 54.485 | 6.47 | 1.12 | 3.048 | 7504.64 | 0.911 | 97.6 | 73.1 | 1450 | 27.29 | 4878 | 2294 | 2354.3 | 3435.8 | 1223.1 | 0.65124 | 4.169
2024-12-10 | 3:15 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2231.56 | 25.68 | 54.575 | 6.47 | 1.131 | 3.039 | 7491.07 | 0.918 | 97.6 | 72.9 | 1451 | 27.24 | 4869.2 | 2303.4 | 2343.3 | 3437.1 | 1223.1 | 0.65362 | 4.17
2024-12-10 | 3:15 | Data | 0 | 35.498 | 34.567 | 122.037 | 7.64 | 116.306 | 2230.66 | 25.67 | 54.575 | 6.47 | 1.122 | 3.046 | 7482.02 | 0.918 | 97.6 | 73 | 1450 | 27.24 | 4863.3 | 2302.3 | 2347.8 | 3432.1 | 1223.1 | 0.65643 | 4.17
2024-12-10 | 3:15 | Data | 0 | 35.444 | 34.567 | 121.947 | 7.64 | 116.306 | 2235.18 | 25.69 | 54.485 | 6.47 | 1.116 | 3.05 | 7491.07 | 0.905 | 97.6 | 73.2 | 1453 | 27.29 | 4869.2 | 2293.6 | 2303 | 3400.8 | 1223.1 | 0.65954 | 4.166
2024-12-10 | 3:16 | Data | 0 | 35.262 | 34.553 | 121.947 | 7.64 | 116.306 | 2225.23 | 25.69 | 54.575 | 6.47 | 1.124 | 3.029 | 7491.07 | 0.83 | 97.5 | 72.9 | 1446 | 27.29 | 4869.2 | 2295.8 | 2314 | 3409.7 | 1223.1 | 0.65825 | 4.153
2024-12-10 | 3:16 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.351 | 2229.75 | 25.68 | 54.485 | 6.47 | 1.126 | 3.03 | 7495.59 | 0.918 | 97.6 | 72.9 | 1449 | 27.24 | 4872.1 | 2296.8 | 2340.3 | 3431.8 | 1223.1 | 0.65342 | 4.156
2024-12-10 | 3:16 | Data | 0 | 35.377 | 34.567 | 122.037 | 7.64 | 116.351 | 2230.66 | 25.69 | 54.575 | 6.47 | 1.127 | 3.058 | 7472.98 | 0.905 | 97.6 | 73.1 | 1450 | 27.24 | 4857.4 | 2295.5 | 2329.8 | 3419.4 | 1223.1 | 0.65356 | 4.186
2024-12-10 | 3:16 | Data | 0 | 35.512 | 34.405 | 122.037 | 7.64 | 116.351 | 2230.66 | 25.69 | 54.575 | 6.47 | 1.133 | 3.046 | 7491.07 | 0.79 | 97.6 | 72.9 | 1449 | 27.24 | 4869.2 | 2306.2 | 2343.3 | 3435.7 | 1223.1 | 0.65438 | 4.18
2024-12-10 | 3:16 | Data | 0 | 35.485 | 34.607 | 122.083 | 7.64 | 116.351 | 2230.66 | 25.69 | 54.575 | 6.47 | 1.131 | 3.05 | 7491.07 | 0.749 | 97.6 | 72.9 | 1450 | 27.29 | 4869.2 | 2304.5 | 2343 | 3437.1 | 1223.1 | 0.65317 | 4.18
2024-12-10 | 3:16 | Data | 0 | 35.586 | 34.567 | 122.128 | 7.64 | 116.351 | 2230.66 | 25.69 | 54.485 | 6.47 | 1.124 | 3.074 | 7495.59 | 1.121 | 97.6 | 73.2 | 1449 | 27.29 | 4872.1 | 2294 | 2350.9 | 3434 | 1223.1 | 0.65306 | 4.198
2024-12-10 | 3:16 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.306 | 2227.95 | 25.7 | 54.575 | 6.47 | 1.121 | 3.059 | 7495.59 | 0.803 | 97.6 | 73.2 | 1448 | 27.29 | 4872.1 | 2314.9 | 2354.9 | 3446.7 | 1223.2 | 0.65757 | 4.18
2024-12-10 | 3:16 | Data | 0 | 35.289 | 34.54 | 122.083 | 7.64 | 116.351 | 2227.95 | 25.69 | 54.485 | 6.47 | 1.127 | 3.065 | 7491.07 | 0.857 | 97.6 | 73.1 | 1448 | 27.24 | 4869.2 | 2293.2 | 2335.3 | 3422 | 1223.2 | 0.656 | 4.192
2024-12-10 | 3:16 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2224.33 | 25.69 | 54.485 | 6.47 | 1.127 | 3.024 | 7495.59 | 0.918 | 97.5 | 72.8 | 1445 | 27.24 | 4872.1 | 2293.7 | 2306.2 | 3407.1 | 1223.2 | 0.65695 | 4.151
2024-12-10 | 3:16 | Data | 0 | 35.478 | 34.789 | 122.083 | 7.64 | 116.306 | 2224.33 | 25.69 | 54.575 | 6.47 | 1.125 | 3.035 | 7495.59 | 0.952 | 97.5 | 72.9 | 1445 | 27.24 | 4872.1 | 2295.8 | 2312.7 | 3407.7 | 1223.2 | 0.65796 | 4.159
2024-12-10 | 3:16 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2226.14 | 25.69 | 54.575 | 6.47 | 1.122 | 3.041 | 7495.59 | 0.918 | 97.6 | 73 | 1448 | 27.24 | 4872.1 | 2318.8 | 2337.3 | 3445.9 | 1223.2 | 0.65606 | 4.163
2024-12-10 | 3:16 | Data | 0 | 35.458 | 34.681 | 121.992 | 7.64 | 116.306 | 2225.23 | 25.7 | 54.304 | 6.47 | 1.121 | 3.041 | 7491.07 | 1.087 | 97.6 | 73 | 1446 | 27.15 | 4869.2 | 2313.2 | 2332.6 | 3436.7 | 1223.2 | 0.65838 | 4.163
2024-12-10 | 3:16 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.351 | 2225.23 | 25.7 | 54.214 | 6.47 | 1.132 | 3.026 | 7495.59 | 0.918 | 97.6 | 72.8 | 1446 | 27.11 | 4872.1 | 2303.5 | 2324.8 | 3414.8 | 1223.2 | 0.65857 | 4.159
2024-12-10 | 3:16 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.261 | 2224.33 | 25.7 | 54.304 | 6.48 | 1.128 | 3.025 | 7504.64 | 0.918 | 97.6 | 72.8 | 1446 | 27.11 | 4878 | 2304.7 | 2321.5 | 3419.1 | 1223.2 | 0.65434 | 4.151
2024-12-10 | 3:16 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.396 | 2225.23 | 25.69 | 54.214 | 6.47 | 1.121 | 3.04 | 7495.59 | 0.918 | 97.6 | 73.1 | 1446 | 27.11 | 4872.1 | 2324.2 | 2343.3 | 3445.9 | 1223.2 | 0.65856 | 4.161
2024-12-10 | 3:16 | Data | 0 | 35.512 | 34.567 | 122.037 | 7.64 | 116.306 | 2222.52 | 25.69 | 54.304 | 6.47 | 1.118 | 3.037 | 7509.16 | 0.702 | 97.6 | 73.1 | 1445 | 27.11 | 4881 | 2293 | 2328.9 | 3423.8 | 1223.2 | 0.65067 | 4.155
2024-12-10 | 3:16 | Data | 0 | 35.37 | 34.553 | 122.083 | 7.64 | 116.396 | 2220.72 | 25.7 | 54.575 | 6.47 | 1.127 | 3.043 | 7504.64 | 0.918 | 97.5 | 73 | 1443 | 27.29 | 4878 | 2325.2 | 2325.5 | 3442.3 | 1223.2 | 0.65693 | 4.17
2024-12-10 | 3:17 | Data | 0 | 35.485 | 34.681 | 121.992 | 7.64 | 116.351 | 2218.91 | 25.69 | 54.575 | 6.47 | 1.121 | 3.037 | 7531.77 | 0.979 | 97.5 | 73 | 1442 | 27.24 | 4895.6 | 2308.9 | 2339.6 | 3436.7 | 1223.2 | 0.65456 | 4.159
2024-12-10 | 3:17 | Data | 0 | 35.458 | 34.567 | 121.992 | 7.64 | 116.351 | 2218.91 | 25.69 | 54.304 | 6.47 | 1.121 | 3.022 | 7531.77 | 0.911 | 97.6 | 72.9 | 1443 | 27.15 | 4895.6 | 2304.3 | 2352.6 | 3436.6 | 1223.2 | 0.65342 | 4.142
2024-12-10 | 3:17 | Data | 0 | 35.458 | 34.567 | 122.083 | 7.64 | 116.396 | 2218.91 | 25.71 | 54.214 | 6.47 | 1.12 | 3.035 | 7531.77 | 0.905 | 97.6 | 73.1 | 1442 | 27.11 | 4895.6 | 2309.6 | 2322.6 | 3422.7 | 1223.2 | 0.65619 | 4.155
2024-12-10 | 3:17 | Data | 0 | 35.174 | 34.567 | 121.992 | 7.64 | 116.351 | 2220.72 | 25.7 | 54.214 | 6.47 | 1.124 | 3.037 | 7522.72 | 0.797 | 97.6 | 73 | 1442 | 27.15 | 4889.8 | 2319.8 | 2339.5 | 3441.4 | 1223.2 | 0.65793 | 4.163
2024-12-10 | 3:17 | Data | 0 | 35.708 | 34.411 | 122.037 | 7.64 | 116.441 | 2218.91 | 25.71 | 54.304 | 6.47 | 1.121 | 3.041 | 7536.29 | 0.918 | 97.6 | 73.1 | 1442 | 27.15 | 4898.6 | 2302.7 | 2333.5 | 3429.1 | 1223.2 | 0.65414 | 4.162
2024-12-10 | 3:17 | Data | 0 | 35.491 | 34.769 | 122.128 | 7.64 | 116.441 | 2218 | 25.69 | 54.304 | 6.47 | 1.12 | 3.047 | 7522.72 | 0.743 | 97.6 | 73.1 | 1442 | 27.15 | 4889.8 | 2311.5 | 2338 | 3437.5 | 1223.2 | 0.6516 | 4.167
2024-12-10 | 3:17 | Data | 0 | 35.383 | 34.567 | 122.083 | 7.64 | 116.396 | 2218.91 | 25.7 | 54.214 | 6.47 | 1.118 | 3.058 | 7518.2 | 0.905 | 97.6 | 73.2 | 1442 | 27.15 | 4886.8 | 2299.6 | 2338.3 | 3429.6 | 1223.2 | 0.65443 | 4.177
2024-12-10 | 3:17 | Data | 0 | 35.458 | 34.594 | 122.037 | 7.64 | 116.351 | 2218.91 | 25.7 | 54.304 | 6.46 | 1.119 | 3.054 | 7518.2 | 1.026 | 97.6 | 73.2 | 1442 | 27.11 | 4886.8 | 2300.4 | 2368.4 | 3442.9 | 1223.2 | 0.65328 | 4.173
2024-12-10 | 3:17 | Data | 0 | 35.377 | 34.567 | 122.037 | 7.64 | 116.396 | 2222.52 | 25.7 | 54.575 | 6.47 | 1.119 | 3.04 | 7513.68 | 0.83 | 97.5 | 73.1 | 1445 | 27.24 | 4883.9 | 2308.6 | 2313.1 | 3420.5 | 1223.2 | 0.65778 | 4.159
2024-12-10 | 3:17 | Data | 0 | 35.471 | 34.398 | 121.992 | 7.65 | 116.351 | 2222.52 | 25.71 | 54.304 | 6.47 | 1.121 | 3.041 | 7531.77 | 0.911 | 97.6 | 73.1 | 1445 | 27.15 | 4895.6 | 2302.7 | 2347 | 3430 | 1223.2 | 0.65521 | 4.162
2024-12-10 | 3:17 | Data | 0 | 35.64 | 34.789 | 122.037 | 7.64 | 116.396 | 2222.52 | 25.71 | 54.665 | 6.47 | 1.127 | 3.04 | 7527.25 | 0.905 | 97.5 | 73 | 1444 | 27.29 | 4892.7 | 2290.8 | 2325.5 | 3417 | 1223.2 | 0.65354 | 4.167
2024-12-10 | 3:17 | Data | 0 | 35.66 | 34.621 | 122.083 | 7.64 | 116.441 | 2220.72 | 25.71 | 54.214 | 6.47 | 1.125 | 3.057 | 7522.72 | 0.911 | 97.6 | 73.1 | 1443 | 27.15 | 4889.8 | 2311.8 | 2380.2 | 3462.6 | 1223.2 | 0.65049 | 4.182
2024-12-10 | 3:17 | Data | 0 | 35.383 | 34.681 | 121.992 | 7.64 | 116.441 | 2218.91 | 25.71 | 54.304 | 6.47 | 1.126 | 3.047 | 7518.2 | 0.878 | 97.6 | 73 | 1442 | 27.15 | 4886.8 | 2311.5 | 2327.1 | 3428.9 | 1223.2 | 0.65741 | 4.174
2024-12-10 | 3:17 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.396 | 2218.91 | 25.7 | 54.575 | 6.47 | 1.12 | 3.054 | 7531.77 | 0.918 | 97.5 | 73.2 | 1442 | 27.29 | 4895.6 | 2278.9 | 2338.7 | 3415.3 | 1223.2 | 0.6518 | 4.174
2024-12-10 | 3:17 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.441 | 2223.43 | 25.71 | 54.485 | 6.47 | 1.127 | 3.031 | 7522.72 | 0.918 | 97.5 | 72.9 | 1445 | 27.29 | 4889.8 | 2310.9 | 2316.9 | 3419.7 | 1223.2 | 0.65762 | 4.16
2024-12-10 | 3:17 | Data | 0 | 35.471 | 34.567 | 122.083 | 7.64 | 116.351 | 2222.52 | 25.71 | 54.485 | 6.47 | 1.121 | 3.059 | 7518.2 | 0.918 | 97.5 | 73.2 | 1445 | 27.24 | 4886.8 | 2292.9 | 2323.9 | 3412.4 | 1223.2 | 0.65739 | 4.18
2024-12-10 | 3:17 | Data | 0 | 35.485 | 34.789 | 122.037 | 7.64 | 116.396 | 2222.52 | 25.71 | 54.575 | 6.47 | 1.127 | 3.059 | 7518.2 | 0.857 | 97.5 | 73.1 | 1445 | 27.29 | 4886.8 | 2311.4 | 2339.7 | 3437.1 | 1223.2 | 0.65585 | 4.187
2024-12-10 | 3:17 | Data | 0 | 35.275 | 34.783 | 122.128 | 7.64 | 116.441 | 2224.33 | 25.71 | 54.485 | 6.48 | 1.127 | 3.045 | 7518.2 | 0.803 | 97.6 | 73 | 1446 | 27.2 | 4886.8 | 2312 | 2354.9 | 3446.1 | 1223.2 | 0.65641 | 4.171
2024-12-10 | 3:18 | Data | 0 | 35.323 | 34.661 | 122.083 | 7.64 | 116.396 | 2218 | 25.71 | 54.485 | 6.47 | 1.119 | 3.035 | 7518.2 | 0.864 | 97.5 | 73.1 | 1442 | 27.29 | 4886.8 | 2294.4 | 2326.3 | 3416.9 | 1223.2 | 0.65558 | 4.153
2024-12-10 | 3:18 | Data | 0 | 35.485 | 34.587 | 121.992 | 7.64 | 116.441 | 2222.52 | 25.71 | 54.485 | 6.47 | 1.127 | 3.054 | 7531.77 | 0.878 | 97.5 | 73.1 | 1445 | 27.24 | 4895.6 | 2304.1 | 2337.1 | 3431.2 | 1223.2 | 0.65155 | 4.182
2024-12-10 | 3:18 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.396 | 2225.23 | 25.71 | 54.485 | 6.47 | 1.129 | 3.059 | 7549.86 | 0.918 | 97.5 | 73 | 1446 | 27.29 | 4907.4 | 2304.2 | 2349.7 | 3440.7 | 1223.2 | 0.65141 | 4.187
2024-12-10 | 3:18 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.351 | 2221.62 | 25.71 | 54.575 | 6.47 | 1.117 | 3.037 | 7531.77 | 0.918 | 97.5 | 73.1 | 1445 | 27.29 | 4895.6 | 2305.9 | 2357.7 | 3448.5 | 1223.2 | 0.65073 | 4.154
2024-12-10 | 3:18 | Data | 0 | 35.485 | 34.567 | 122.128 | 7.64 | 116.396 | 2222.52 | 25.7 | 54.485 | 6.47 | 1.128 | 3.025 | 7549.86 | 0.918 | 97.5 | 72.9 | 1445 | 27.24 | 4907.4 | 2315 | 2369.5 | 3453.4 | 1223.2 | 0.65336 | 4.151
2024-12-10 | 3:18 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.396 | 2222.52 | 25.72 | 54.575 | 6.47 | 1.127 | 3.048 | 7549.86 | 0.918 | 97.5 | 73 | 1445 | 27.29 | 4907.4 | 2288.4 | 2362.1 | 3436.5 | 1223.2 | 0.64877 | 4.176
2024-12-10 | 3:18 | Data | 0 | 35.512 | 34.567 | 122.037 | 7.64 | 116.351 | 2222.52 | 25.71 | 54.485 | 6.47 | 1.121 | 3.067 | 7549.86 | 0.918 | 97.5 | 73.2 | 1445 | 27.24 | 4907.4 | 2306.2 | 2351.7 | 3440.1 | 1223.2 | 0.65209 | 4.189
2024-12-10 | 3:18 | Data | 0 | 35.485 | 34.567 | 122.128 | 7.64 | 116.351 | 2221.62 | 25.71 | 54.575 | 6.47 | 1.12 | 3.043 | 7554.38 | 0.918 | 97.5 | 73.1 | 1444 | 27.29 | 4910.3 | 2315.7 | 2331.1 | 3433.6 | 1223.2 | 0.65767 | 4.162
2024-12-10 | 3:18 | Data | 0 | 35.485 | 34.607 | 122.083 | 7.64 | 116.351 | 2222.52 | 25.71 | 54.485 | 6.47 | 1.127 | 3.048 | 7549.86 | 0.878 | 97.5 | 73 | 1445 | 27.29 | 4907.4 | 2301.9 | 2350.4 | 3436.9 | 1223.2 | 0.6539 | 4.175
2024-12-10 | 3:18 | Data | 0 | 35.714 | 34.796 | 122.037 | 7.64 | 116.441 | 2222.52 | 25.71 | 54.485 | 6.47 | 1.125 | 3.041 | 7549.86 | 0.918 | 97.5 | 73 | 1445 | 27.29 | 4907.4 | 2299.5 | 2356.2 | 3446.2 | 1223.2 | 0.64934 | 4.166
2024-12-10 | 3:18 | Data | 0 | 35.512 | 34.614 | 122.128 | 7.64 | 116.441 | 2222.52 | 25.71 | 54.575 | 6.47 | 1.117 | 3.034 | 7549.86 | 0.749 | 97.5 | 73.1 | 1445 | 27.29 | 4907.4 | 2305.3 | 2344.7 | 3433.2 | 1223.2 | 0.65525 | 4.152
2024-12-10 | 3:18 | Data | 0 | 35.714 | 34.668 | 122.128 | 7.64 | 116.441 | 2220.72 | 25.71 | 54.485 | 6.47 | 1.122 | 3.034 | 7545.34 | 0.851 | 97.5 | 73 | 1443 | 27.29 | 4904.5 | 2290.8 | 2353 | 3431.4 | 1223.2 | 0.65092 | 4.158
2024-12-10 | 3:18 | Data | 0 | 35.539 | 34.58 | 122.083 | 7.64 | 116.441 | 2216.2 | 25.71 | 54.575 | 6.47 | 1.124 | 3.021 | 7563.42 | 0.905 | 97.5 | 72.9 | 1441 | 27.29 | 4916.2 | 2296.1 | 2363.5 | 3441.3 | 1223.2 | 0.65048 | 4.145
2024-12-10 | 3:18 | Data | 0 | 35.701 | 34.796 | 122.037 | 7.64 | 116.441 | 2216.2 | 25.71 | 54.575 | 6.47 | 1.121 | 3.02 | 7563.42 | 0.918 | 97.5 | 72.9 | 1441 | 27.24 | 4916.2 | 2307.3 | 2369 | 3457 | 1223.2 | 0.64973 | 4.141
2024-12-10 | 3:18 | Data | 0 | 35.546 | 34.573 | 122.083 | 7.64 | 116.441 | 2220.72 | 25.71 | 54.575 | 6.47 | 1.13 | 3.044 | 7545.34 | 0.911 | 97.5 | 72.9 | 1442 | 27.29 | 4904.5 | 2299.2 | 2370.2 | 3445.6 | 1223.2 | 0.6497 | 4.172
2024-12-10 | 3:18 | Data | 0 | 35.714 | 34.789 | 122.037 | 7.64 | 116.441 | 2216.2 | 25.71 | 54.575 | 6.47 | 1.122 | 3.06 | 7549.86 | 0.749 | 97.5 | 73.2 | 1441 | 27.29 | 4907.4 | 2294 | 2347.2 | 3432.7 | 1223.2 | 0.65214 | 4.181
2024-12-10 | 3:18 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.396 | 2216.2 | 25.71 | 54.485 | 6.47 | 1.127 | 3.06 | 7576.99 | 1.094 | 97.5 | 73.1 | 1441 | 27.29 | 4925 | 1216.9 | 1704.9 | 2112.7 | 1223.2 | 0.57556 | 4.187
2024-12-10 | 3:18 | Data | 0 | 35.687 | 34.587 | 121.947 | 7.64 | 116.396 | 2212.58 | 25.71 | 54.485 | 6.47 | 1.127 | 3.036 | 7563.42 | 1.107 | 97.5 | 72.9 | 1439 | 27.24 | 4916.2 | 1224.5 | 1720.9 | 2131.4 | 1223.2 | 0.57449 | 4.163
2024-12-10 | 3:19 | Data | 0 | 35.714 | 34.58 | 122.128 | 7.64 | 116.487 | 2213.49 | 25.71 | 54.485 | 6.47 | 1.122 | 3.02 | 7554.38 | 0.878 | 97.5 | 72.9 | 1439 | 27.24 | 4910.3 | 1218.1 | 1716.9 | 2122.7 | 1223.3 | 0.57902 | 4.142
2024-12-10 | 3:19 | Data | 0 | 35.714 | 34.621 | 122.218 | 7.64 | 116.441 | 2213.49 | 25.71 | 54.485 | 6.47 | 1.126 | 3.04 | 7563.42 | 1.033 | 97.5 | 73 | 1439 | 27.24 | 4916.2 | 1216.6 | 1685.5 | 2096.7 | 1223.3 | 0.57878 | 4.166
2024-12-10 | 3:19 | Data | 0 | 35.485 | 34.58 | 122.128 | 7.64 | 116.441 | 2216.2 | 25.71 | 54.575 | 6.47 | 1.134 | 3.047 | 7567.95 | 0.891 | 97.5 | 72.9 | 1441 | 27.29 | 4919.2 | 1210.6 | 1710.4 | 2112.9 | 1223.3 | 0.57276 | 4.182
2024-12-10 | 3:19 | Data | 0 | 35.491 | 34.783 | 122.128 | 7.64 | 116.396 | 2218.91 | 25.71 | 54.575 | 6.47 | 1.122 | 3.045 | 7554.38 | 0.83 | 97.5 | 73.1 | 1442 | 27.29 | 4910.3 | 1215.9 | 1686.8 | 2099.7 | 1223.3 | 0.57777 | 4.166
2024-12-10 | 3:19 | Data | 0 | 35.687 | 34.567 | 122.128 | 7.64 | 116.396 | 2216.2 | 25.71 | 54.485 | 6.47 | 1.112 | 3.022 | 7536.29 | 0.965 | 97.5 | 73.1 | 1441 | 27.29 | 4898.6 | 1239.7 | 1721 | 2140.9 | 1223.3 | 0.57859 | 4.134
2024-12-10 | 3:19 | Data | 0 | 35.485 | 34.573 | 122.083 | 7.64 | 116.396 | 2217.1 | 25.69 | 54.394 | 6.48 | 1.126 | 3.034 | 7549.86 | 0.905 | 97.5 | 72.9 | 1441 | 27.24 | 4907.4 | 1220.6 | 1691.6 | 2107.4 | 1223.3 | 0.57566 | 4.161
2024-12-10 | 3:19 | Data | 0 | 35.654 | 34.796 | 122.037 | 7.65 | 116.441 | 2216.2 | 25.7 | 54.575 | 6.47 | 1.127 | 3.043 | 7549.86 | 0.911 | 97.5 | 73 | 1441 | 27.24 | 4907.4 | 1221.4 | 1691.7 | 2106.3 | 1223.3 | 0.57729 | 4.17
2024-12-10 | 3:19 | Data | 0 | 35.6 | 34.783 | 122.128 | 7.64 | 116.441 | 2213.49 | 25.7 | 54.575 | 6.47 | 1.126 | 3.03 | 7545.34 | 0.918 | 97.5 | 72.9 | 1439 | 27.29 | 4904.5 | 1221.9 | 1704.3 | 2115.7 | 1223.3 | 0.57352 | 4.156
2024-12-10 | 3:19 | Data | 0 | 35.289 | 34.681 | 122.083 | 7.64 | 116.396 | 2213.49 | 25.7 | 54.575 | 6.47 | 1.13 | 3.054 | 7549.86 | 0.864 | 97.5 | 73 | 1439 | 27.29 | 4907.4 | 1223.1 | 1714.3 | 2124.9 | 1223.3 | 0.57447 | 4.182
2024-12-10 | 3:19 | Data | 0 | 35.491 | 34.567 | 122.037 | 7.64 | 116.396 | 2213.49 | 25.69 | 54.485 | 6.47 | 1.122 | 3.057 | 7545.34 | 0.918 | 97.5 | 73.1 | 1439 | 27.24 | 4904.5 | 1235.8 | 1738.3 | 2152.6 | 1223.3 | 0.5746 | 4.179
2024-12-10 | 3:19 | Data | 0 | 35.795 | 34.796 | 122.083 | 7.64 | 116.441 | 2213.49 | 25.69 | 54.575 | 6.47 | 1.124 | 3.047 | 7549.86 | 0.756 | 97.5 | 73.1 | 1439 | 27.24 | 4907.4 | 1210 | 1740.3 | 2137 | 1223.3 | 0.56902 | 4.171
2024-12-10 | 3:19 | Data | 0 | 35.701 | 34.816 | 122.173 | 7.64 | 116.441 | 2212.58 | 25.7 | 54.575 | 6.47 | 1.118 | 3.047 | 7545.34 | 0.756 | 97.5 | 73.2 | 1439 | 27.24 | 4904.5 | 1215 | 1731.7 | 2136.5 | 1223.3 | 0.56859 | 4.165
2024-12-10 | 3:19 | Data | 0 | 35.485 | 34.796 | 122.128 | 7.64 | 116.441 | 2212.58 | 25.69 | 54.665 | 6.47 | 1.119 | 3.057 | 7545.34 | 0.871 | 97.5 | 73.2 | 1438 | 27.24 | 4904.5 | 1227.6 | 1728.6 | 2141.9 | 1223.3 | 0.57822 | 4.175
2024-12-10 | 3:19 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2213.49 | 25.69 | 54.485 | 6.47 | 1.12 | 3.05 | 7531.77 | 0.918 | 97.5 | 73.1 | 1439 | 27.24 | 4895.6 | 1230.7 | 1704.8 | 2117.7 | 1223.3 | 0.58577 | 4.17
2024-12-10 | 3:19 | Data | 0 | 35.6 | 34.783 | 122.037 | 7.64 | 116.396 | 2216.2 | 25.69 | 54.575 | 6.47 | 1.126 | 3.045 | 7558.9 | 0.918 | 97.5 | 73 | 1441 | 27.24 | 4913.3 | 1217.2 | 1721.1 | 2127 | 1223.3 | 0.57205 | 4.171
2024-12-10 | 3:19 | Data | 0 | 35.714 | 34.681 | 122.083 | 7.64 | 116.441 | 2220.72 | 25.69 | 54.575 | 6.47 | 1.122 | 3.05 | 7554.38 | 0.918 | 97.5 | 73.1 | 1442 | 27.24 | 4910.3 | 1233.1 | 1716.3 | 2131.8 | 1223.3 | 0.57821 | 4.172
2024-12-10 | 3:19 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.351 | 2218 | 25.7 | 54.575 | 6.47 | 1.127 | 3.031 | 7545.34 | 0.918 | 97.5 | 72.9 | 1442 | 27.33 | 4904.5 | 1211.5 | 1706 | 2112 | 1223.3 | 0.57371 | 4.16
2024-12-10 | 3:20 | Data | 0 | 35.485 | 34.668 | 122.128 | 7.64 | 116.351 | 2218.91 | 25.7 | 54.485 | 6.47 | 1.125 | 3.029 | 7563.42 | 0.959 | 97.5 | 72.9 | 1443 | 27.29 | 4916.2 | 1240.4 | 1706 | 2126.7 | 1223.3 | 0.58319 | 4.154
2024-12-10 | 3:20 | Data | 0 | 35.316 | 34.567 | 122.037 | 7.64 | 116.396 | 2222.52 | 25.68 | 54.485 | 6.46 | 1.116 | 3.041 | 7545.34 | 0.837 | 97.5 | 73.2 | 1445 | 27.24 | 4904.5 | 1231.8 | 1725.5 | 2137 | 1223.3 | 0.57651 | 4.157
2024-12-10 | 3:20 | Data | 0 | 35.397 | 34.526 | 122.128 | 7.64 | 116.396 | 2222.52 | 25.69 | 54.485 | 6.47 | 1.114 | 3.044 | 7549.86 | 0.79 | 97.5 | 73.2 | 1445 | 27.24 | 4907.4 | 1237 | 1734.1 | 2148.4 | 1223.3 | 0.5748 | 4.159
2024-12-10 | 3:20 | Data | 0 | 35.491 | 34.681 | 122.037 | 7.64 | 116.396 | 2227.95 | 25.69 | 54.485 | 6.47 | 1.112 | 3.033 | 7531.77 | 0.918 | 97.6 | 73.2 | 1448 | 27.24 | 4895.6 | 1226.7 | 1712.9 | 2125.4 | 1223.3 | 0.57696 | 4.145
2024-12-10 | 3:20 | Data | 0 | 35.512 | 34.594 | 122.083 | 7.64 | 116.441 | 2227.04 | 25.7 | 54.575 | 6.47 | 1.119 | 3.037 | 7531.77 | 0.81 | 97.6 | 73.1 | 1448 | 27.29 | 4895.6 | 1204.9 | 1746.4 | 2141.3 | 1223.3 | 0.56109 | 4.156
2024-12-10 | 3:20 | Data | 0 | 35.491 | 34.951 | 122.083 | 7.64 | 116.396 | 2227.95 | 25.69 | 54.485 | 6.47 | 1.131 | 3.038 | 7549.86 | 0.743 | 97.6 | 72.9 | 1448 | 27.24 | 4907.4 | 1214.2 | 1730.5 | 2132.4 | 1223.3 | 0.56909 | 4.169
2024-12-10 | 3:20 | Data | 0 | 35.316 | 34.762 | 122.083 | 7.64 | 116.396 | 2228.85 | 25.69 | 54.394 | 6.47 | 1.131 | 3.03 | 7549.86 | 0.763 | 97.6 | 72.8 | 1448 | 27.2 | 4907.4 | 1207.5 | 1751 | 2147 | 1223.3 | 0.56164 | 4.161
2024-12-10 | 3:20 | Data | 0 | 35.6 | 34.789 | 122.037 | 7.64 | 116.441 | 2226.14 | 25.7 | 54.575 | 6.47 | 1.127 | 3.035 | 7536.29 | 0.918 | 97.5 | 72.9 | 1446 | 27.24 | 4898.6 | 1201 | 1688.2 | 2091 | 1223.3 | 0.57337 | 4.162
2024-12-10 | 3:20 | Data | 0 | 35.37 | 34.465 | 121.992 | 7.64 | 116.396 | 2227.95 | 25.69 | 54.485 | 6.47 | 1.13 | 3.076 | 7531.77 | 0.918 | 97.6 | 73.1 | 1448 | 27.29 | 4895.6 | 1212.9 | 1689.8 | 2096.2 | 1223.3 | 0.5761 | 4.206
2024-12-10 | 3:20 | Data | 0 | 35.485 | 34.783 | 121.992 | 7.64 | 116.351 | 2226.14 | 25.69 | 54.575 | 6.47 | 1.128 | 3.056 | 7531.77 | 0.749 | 97.5 | 73.1 | 1447 | 27.29 | 4895.6 | 1207.2 | 1682.3 | 2089.8 | 1223.3 | 0.57774 | 4.185
2024-12-10 | 3:20 | Data | 0 | 35.485 | 34.58 | 122.083 | 7.64 | 116.396 | 2226.14 | 25.7 | 54.485 | 6.47 | 1.125 | 3.011 | 7536.29 | 0.871 | 97.6 | 72.8 | 1447 | 27.24 | 4898.6 | 1197.7 | 1712.5 | 2112.6 | 1223.3 | 0.5663 | 4.136
2024-12-10 | 3:20 | Data | 0 | 35.485 | 34.567 | 122.128 | 7.64 | 116.396 | 2228.85 | 25.69 | 54.575 | 6.47 | 1.131 | 3.024 | 7531.77 | 0.918 | 97.6 | 72.8 | 1449 | 27.24 | 4895.6 | 1208.9 | 1714.2 | 2114.9 | 1223.3 | 0.57076 | 4.154
2024-12-10 | 3:20 | Data | 0 | 35.701 | 34.594 | 122.128 | 7.64 | 116.441 | 2226.14 | 25.7 | 54.575 | 6.47 | 1.13 | 3.053 | 7518.2 | 0.925 | 97.5 | 73 | 1446 | 27.29 | 4886.8 | 1228.6 | 1696.9 | 2106.4 | 1223.3 | 0.577 | 4.182
2024-12-10 | 3:20 | Data | 0 | 35.708 | 34.465 | 122.173 | 7.64 | 116.487 | 2225.23 | 25.69 | 54.575 | 6.47 | 1.121 | 3.034 | 7531.77 | 0.911 | 97.5 | 73 | 1446 | 27.29 | 4895.6 | 1224.6 | 1700.6 | 2115.3 | 1223.3 | 0.57339 | 4.154
2024-12-10 | 3:20 | Data | 0 | 35.37 | 34.364 | 122.128 | 7.64 | 116.441 | 2225.23 | 25.69 | 54.575 | 6.47 | 1.121 | 3.026 | 7531.77 | 0.905 | 97.5 | 73 | 1446 | 27.29 | 4895.6 | 1222.9 | 1723 | 2128.6 | 1223.3 | 0.57327 | 4.146
2024-12-10 | 3:20 | Data | 0 | 35.512 | 34.573 | 122.128 | 7.64 | 116.396 | 2225.23 | 25.7 | 54.485 | 6.46 | 1.124 | 3.026 | 7536.29 | 0.918 | 97.6 | 72.9 | 1446 | 27.24 | 4898.6 | 1210.8 | 1736.4 | 2135.2 | 1223.3 | 0.56468 | 4.151
2024-12-10 | 3:20 | Data | 0 | 35.6 | 34.681 | 122.083 | 7.64 | 116.441 | 2224.33 | 25.71 | 54.575 | 6.47 | 1.129 | 3.025 | 7531.77 | 0.716 | 97.5 | 72.8 | 1446 | 27.29 | 4895.6 | 1239.4 | 1741.4 | 2151.9 | 1223.3 | 0.57285 | 4.153
2024-12-10 | 3:20 | Data | 0 | 35.64 | 34.594 | 122.083 | 7.64 | 116.396 | 2222.52 | 25.69 | 54.485 | 6.47 | 1.128 | 3.024 | 7531.77 | 1.114 | 97.5 | 72.8 | 1445 | 27.29 | 4895.6 | 1230.2 | 1736.4 | 2146 | 1223.3 | 0.57091 | 4.152
2024-12-10 | 3:21 | Data | 0 | 35.491 | 34.567 | 122.083 | 7.64 | 116.396 | 2222.52 | 25.69 | 54.575 | 6.47 | 1.129 | 3.034 | 7531.77 | 0.918 | 97.5 | 72.9 | 1445 | 27.29 | 4895.6 | 1219.9 | 1698.6 | 2112.5 | 1223.3 | 0.57623 | 4.161
2024-12-10 | 3:21 | Data | 0 | 35.464 | 34.735 | 122.083 | 7.64 | 116.351 | 2222.52 | 25.69 | 54.485 | 6.47 | 1.124 | 3.054 | 7531.77 | 0.918 | 97.5 | 73.1 | 1445 | 27.29 | 4895.6 | 1221.4 | 1708.7 | 2119.9 | 1223.3 | 0.57582 | 4.177
2024-12-10 | 3:21 | Data | 0 | 35.485 | 34.681 | 122.083 | 7.64 | 116.441 | 2227.95 | 25.7 | 54.485 | 6.47 | 1.124 | 3.05 | 7527.25 | 0.803 | 97.6 | 73.1 | 1448 | 27.24 | 4892.7 | 1210.5 | 1703.2 | 2115.8 | 1223.3 | 0.57727 | 4.174
2024-12-10 | 3:21 | Data | 0 | 35.431 | 34.567 | 122.083 | 7.64 | 116.396 | 2221.62 | 25.69 | 54.485 | 6.47 | 1.122 | 3.037 | 7549.86 | 0.898 | 97.5 | 73 | 1444 | 27.24 | 4907.4 | 1230.4 | 1693.4 | 2112.2 | 1223.3 | 0.58208 | 4.16
2024-12-10 | 3:21 | Data | 0 | 35.701 | 34.594 | 122.128 | 7.64 | 116.487 | 2220.72 | 25.7 | 54.485 | 6.47 | 1.122 | 3.056 | 7549.86 | 0.891 | 97.5 | 73.2 | 1442 | 27.2 | 4907.4 | 1230.8 | 1710.3 | 2125.2 | 1223.3 | 0.5819 | 4.178
2024-12-10 | 3:21 | Data | 0 | 35.289 | 34.56 | 122.037 | 7.64 | 116.396 | 2216.2 | 25.69 | 54.575 | 6.47 | 1.124 | 3.054 | 7549.86 | 0.709 | 97.5 | 73.1 | 1441 | 27.24 | 4907.4 | 1232.8 | 1728.4 | 2142.1 | 1223.3 | 0.57551 | 4.179
2024-12-10 | 3:21 | Data | 0 | 35.512 | 34.567 | 122.083 | 7.64 | 116.441 | 2216.2 | 25.7 | 54.575 | 6.47 | 1.124 | 3.04 | 7545.34 | 0.918 | 97.5 | 73 | 1441 | 27.29 | 4904.5 | 1228.4 | 1704.7 | 2123 | 1223.3 | 0.58089 | 4.164
2024-12-10 | 3:21 | Data | 0 | 35.687 | 34.573 | 122.128 | 7.64 | 116.396 | 2220.72 | 25.68 | 54.575 | 6.47 | 1.119 | 3.043 | 7549.86 | 0.918 | 97.5 | 73.1 | 1443 | 27.29 | 4907.4 | 1211.4 | 1709.9 | 2114.6 | 1223.3 | 0.57249 | 4.161
2024-12-10 | 3:21 | Data | 0 | 35.262 | 34.567 | 122.037 | 7.64 | 116.396 | 2216.2 | 25.69 | 54.575 | 6.47 | 1.121 | 3.037 | 7554.38 | 0.878 | 97.5 | 73 | 1441 | 27.24 | 4910.3 | 1227.5 | 1724.1 | 2133.8 | 1223.3 | 0.57428 | 4.158
2024-12-10 | 3:21 | Data | 0 | 35.485 | 34.567 | 121.947 | 7.64 | 116.396 | 2212.58 | 25.69 | 54.485 | 6.47 | 1.116 | 3.029 | 7558.9 | 0.918 | 97.5 | 73.1 | 1438 | 27.24 | 4913.3 | 1209.8 | 1718.9 | 2113 | 1223.3 | 0.57077 | 4.146
2024-12-10 | 3:21 | Data | 0 | 35.37 | 34.567 | 122.037 | 7.64 | 116.306 | 2216.2 | 25.69 | 54.575 | 6.47 | 1.122 | 3.043 | 7567.95 | 0.743 | 97.5 | 73.1 | 1441 | 27.29 | 4919.2 | 1225.5 | 1734.3 | 2139.9 | 1223.3 | 0.57042 | 4.165
2024-12-10 | 3:21 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.351 | 2215.29 | 25.69 | 54.485 | 6.47 | 1.124 | 3.054 | 7590.56 | 0.918 | 97.5 | 73.1 | 1440 | 27.24 | 4933.9 | 1235.8 | 1727.9 | 2140.3 | 1223.3 | 0.57726 | 4.178
2024-12-10 | 3:21 | Data | 0 | 35.478 | 34.553 | 122.037 | 7.64 | 116.351 | 2214.39 | 25.69 | 54.485 | 6.47 | 1.121 | 3.043 | 7567.95 | 0.945 | 97.5 | 73.1 | 1439 | 27.29 | 4919.2 | 1225.7 | 1723.5 | 2130.8 | 1223.3 | 0.57385 | 4.164
2024-12-10 | 3:21 | Data | 0 | 35.593 | 34.573 | 122.083 | 7.64 | 116.441 | 2213.49 | 25.69 | 54.485 | 6.47 | 1.116 | 3.026 | 7563.42 | 0.905 | 97.5 | 73.1 | 1439 | 27.29 | 4916.2 | 1226.5 | 1711.9 | 2125.5 | 1223.3 | 0.57537 | 4.142
2024-12-10 | 3:21 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2213.49 | 25.69 | 54.485 | 6.47 | 1.125 | 3.025 | 7576.99 | 0.918 | 97.5 | 72.9 | 1439 | 27.29 | 4925 | 1220.4 | 1712.6 | 2119.3 | 1223.3 | 0.57494 | 4.15
2024-12-10 | 3:21 | Data | 0 | 35.485 | 34.452 | 121.992 | 7.64 | 116.396 | 2216.2 | 25.7 | 54.575 | 6.47 | 1.131 | 3.035 | 7563.42 | 0.932 | 97.5 | 72.8 | 1441 | 27.24 | 4916.2 | 1236.2 | 1711.1 | 2129.5 | 1223.3 | 0.57916 | 4.167
2024-12-10 | 3:21 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.351 | 2218.91 | 25.7 | 54.304 | 6.47 | 1.12 | 3.035 | 7576.99 | 0.918 | 97.6 | 73.1 | 1442 | 27.15 | 4925 | 1231.8 | 1703.1 | 2117.6 | 1223.3 | 0.58069 | 4.155
2024-12-10 | 3:21 | Data | 0 | 35.512 | 34.567 | 122.037 | 7.64 | 116.441 | 2218.91 | 25.69 | 54.485 | 6.46 | 1.12 | 3.036 | 7558.9 | 0.918 | 97.5 | 73.1 | 1442 | 27.29 | 4913.3 | 1237.8 | 1724.3 | 2140.6 | 1223.3 | 0.5777 | 4.155
2024-12-10 | 3:22 | Data | 0 | 35.485 | 34.398 | 121.992 | 7.64 | 116.351 | 2218 | 25.7 | 54.575 | 6.47 | 1.129 | 3.045 | 7572.47 | 0.905 | 97.5 | 72.9 | 1442 | 27.29 | 4922.1 | 1230.1 | 1727.4 | 2137.4 | 1223.3 | 0.57516 | 4.172
2024-12-10 | 3:22 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.396 | 2217.1 | 25.69 | 54.575 | 6.47 | 1.13 | 3.056 | 7563.42 | 0.918 | 97.5 | 73 | 1441 | 27.29 | 4916.2 | 1231.1 | 1728.5 | 2141.7 | 1223.3 | 0.5745 | 4.186
2024-12-10 | 3:22 | Data | 0 | 35.262 | 34.553 | 121.992 | 7.64 | 116.306 | 2218.91 | 25.69 | 54.575 | 6.47 | 1.117 | 3.04 | 7563.42 | 0.918 | 97.5 | 73.1 | 1442 | 27.29 | 4916.2 | 1231.1 | 1710.5 | 2125.3 | 1223.3 | 0.57849 | 4.156
2024-12-10 | 3:22 | Data | 0 | 35.37 | 34.513 | 121.902 | 7.64 | 116.306 | 2216.2 | 25.69 | 54.485 | 6.47 | 1.118 | 3.04 | 7581.51 | 0.824 | 97.5 | 73.1 | 1441 | 27.2 | 4928 | 1222.6 | 1712.1 | 2120.7 | 1223.3 | 0.57683 | 4.159
2024-12-10 | 3:22 | Data | 0 | 35.66 | 34.783 | 122.173 | 7.64 | 116.396 | 2218.91 | 25.69 | 54.575 | 6.47 | 1.12 | 3.044 | 7563.42 | 0.918 | 97.5 | 73.1 | 1442 | 27.29 | 4916.2 | 1221.7 | 1705.7 | 2117.1 | 1223.3 | 0.57529 | 4.163
2024-12-10 | 3:22 | Data | 0 | 35.309 | 34.513 | 121.947 | 7.64 | 116.261 | 2220.72 | 25.7 | 54.575 | 6.47 | 1.131 | 3.022 | 7572.47 | 0.749 | 97.5 | 72.8 | 1442 | 27.29 | 4922.1 | 1222.5 | 1731.6 | 2140.3 | 1223.3 | 0.57085 | 4.152
2024-12-10 | 3:22 | Data | 0 | 35.485 | 34.364 | 122.083 | 7.64 | 116.306 | 2270.43 | 25.69 | 54.575 | 6.47 | 1.13 | 3.047 | 7581.51 | 1.094 | 97.6 | 72.9 | 1476 | 27.29 | 4928 | 1210.3 | 1714.5 | 2120.9 | 1223.3 | 0.56936 | 4.178
2024-12-10 | 3:22 | Data | 0 | 35.37 | 34.479 | 121.992 | 7.64 | 116.306 | 2274.04 | 25.69 | 54.485 | 6.47 | 1.125 | 3.036 | 7576.99 | 0.857 | 97.6 | 73 | 1478 | 27.24 | 4925 | 1226.1 | 1724.8 | 2135.8 | 1223.3 | 0.57193 | 4.161
2024-12-10 | 3:22 | Data | 0 | 35.262 | 34.56 | 121.992 | 7.64 | 116.306 | 2274.95 | 25.69 | 54.485 | 6.47 | 1.127 | 3.016 | 7590.56 | 0.716 | 97.6 | 72.8 | 1479 | 27.24 | 4933.9 | 1224.8 | 1698.5 | 2114.1 | 1223.3 | 0.57372 | 4.142
2024-12-10 | 3:22 | Data | 0 | 35.485 | 34.675 | 121.992 | 7.64 | 116.396 | 2274.95 | 25.69 | 54.575 | 6.47 | 1.127 | 3.03 | 7586.04 | 0.716 | 97.6 | 72.9 | 1479 | 27.24 | 4930.9 | 1217.4 | 1701 | 2112.5 | 1223.3 | 0.575 | 4.157
2024-12-10 | 3:22 | Data | 0 | 35.458 | 34.567 | 121.947 | 7.64 | 116.351 | 2226.14 | 25.7 | 54.575 | 6.47 | 1.128 | 3.036 | 7572.47 | 0.905 | 97.6 | 72.9 | 1446 | 27.24 | 4922.1 | 1226.2 | 1716.1 | 2127.4 | 1223.3 | 0.57632 | 4.165
2024-12-10 | 3:22 | Data | 0 | 35.485 | 34.56 | 122.083 | 7.64 | 116.351 | 2218.91 | 25.69 | 54.485 | 6.47 | 1.117 | 3.039 | 7590.56 | 0.925 | 97.5 | 73.1 | 1442 | 27.29 | 4933.9 | 1221.4 | 1706.7 | 2118.7 | 1223.3 | 0.5745 | 4.156
2024-12-10 | 3:22 | Data | 0 | 35.431 | 34.567 | 121.947 | 7.64 | 116.306 | 2218.91 | 25.69 | 54.575 | 6.47 | 1.122 | 3.035 | 7576.99 | 0.911 | 97.5 | 73 | 1442 | 27.29 | 4925 | 1206.1 | 1681.7 | 2091.1 | 1223.3 | 0.57846 | 4.157
2024-12-10 | 3:22 | Data | 0 | 35.431 | 34.56 | 121.992 | 7.64 | 116.306 | 2223.43 | 25.69 | 54.394 | 6.47 | 1.122 | 3.045 | 7576.99 | 0.925 | 97.5 | 73.1 | 1445 | 27.24 | 4925 | 1218.2 | 1716.4 | 2122.8 | 1223.3 | 0.57282 | 4.167
2024-12-10 | 3:22 | Data | 0 | 35.262 | 34.452 | 121.992 | 7.64 | 116.306 | 2225.23 | 25.7 | 54.575 | 6.47 | 1.125 | 3.026 | 7572.47 | 0.911 | 97.5 | 72.9 | 1446 | 27.29 | 4922.1 | 1227.1 | 1723.7 | 2136 | 1223.3 | 0.57334 | 4.151
2024-12-10 | 3:22 | Data | 0 | 35.262 | 34.445 | 121.992 | 7.64 | 116.306 | 2227.04 | 25.69 | 54.485 | 6.47 | 1.13 | 3.035 | 7576.99 | 0.878 | 97.6 | 72.9 | 1448 | 27.24 | 4925 | 1229.6 | 1710.6 | 2126.5 | 1223.3 | 0.57455 | 4.163
2024-12-10 | 3:22 | Data | 0 | 35.282 | 34.344 | 121.992 | 7.64 | 116.306 | 2224.33 | 25.69 | 54.485 | 6.47 | 1.127 | 3.034 | 7586.04 | 0.911 | 97.5 | 72.9 | 1446 | 27.29 | 4930.9 | 1235.6 | 1721.7 | 2135.9 | 1223.3 | 0.57679 | 4.161
2024-12-10 | 3:22 | Data | 0 | 35.309 | 34.344 | 121.992 | 7.64 | 116.351 | 2222.52 | 25.69 | 54.575 | 6.47 | 1.127 | 3.039 | 7576.99 | 0.925 | 97.5 | 73 | 1445 | 27.24 | 4925 | 1226.1 | 1726.4 | 2139.6 | 1223.3 | 0.57126 | 4.167
2024-12-10 | 3:23 | Data | 0 | 35.485 | 34.371 | 122.037 | 7.64 | 116.306 | 2220.72 | 25.7 | 54.485 | 6.47 | 1.122 | 3.031 | 7567.95 | 1.019 | 97.5 | 73 | 1443 | 27.24 | 4919.2 | 1224.5 | 1723 | 2131.9 | 1223.3 | 0.57325 | 4.155
2024-12-10 | 3:23 | Data | 0 | 35.262 | 34.567 | 121.947 | 7.64 | 116.306 | 2217.1 | 25.7 | 54.575 | 6.47 | 1.126 | 3.029 | 7558.9 | 0.878 | 97.5 | 72.9 | 1441 | 27.24 | 4913.3 | 1226 | 1722.2 | 2131 | 1223.3 | 0.57439 | 4.155
2024-12-10 | 3:23 | Data | 0 | 35.485 | 34.364 | 121.992 | 7.64 | 116.261 | 2213.49 | 25.69 | 54.575 | 6.47 | 1.12 | 3.045 | 7269.48 | 1.033 | 97.5 | 73.1 | 1439 | 27.24 | 4725.2 | 1216.9 | 1717.2 | 2123.8 | 1223.3 | 0.57067 | 4.164
2024-12-10 | 3:23 | Data | 0 | 35.255 | 34.445 | 122.037 | 7.64 | 116.306 | 2211.68 | 25.68 | 54.575 | 6.47 | 1.13 | 3.036 | 7441.32 | 0.817 | 97.5 | 72.9 | 1438 | 27.29 | 4836.9 | 1229.6 | 1718.6 | 2131.4 | 1223.3 | 0.57613 | 4.167
2024-12-10 | 3:23 | Data | 0 | 35.458 | 34.54 | 121.992 | 7.64 | 116.306 | 2213.49 | 25.7 | 54.485 | 6.47 | 1.13 | 3.051 | 7531.77 | 0.938 | 97.5 | 73 | 1439 | 27.24 | 4895.6 | 1214.7 | 1714.6 | 2120.2 | 1223.3 | 0.57183 | 4.18
2024-12-10 | 3:23 | Data | 0 | 35.485 | 34.452 | 121.947 | 7.64 | 116.306 | 2213.49 | 25.69 | 54.575 | 6.47 | 1.118 | 3.045 | 7527.25 | 1.033 | 97.5 | 73.1 | 1439 | 27.29 | 4892.7 | 2567.7 | 3222.6 | 4203.8 | 1223.3 | 0.60632 | 4.162
2024-12-10 | 3:23 | Data | 0 | 35.37 | 34.54 | 121.947 | 7.64 | 116.351 | 2211.68 | 25.7 | 54.575 | 6.47 | 1.121 | 3.039 | 7522.72 | 1.006 | 97.5 | 73 | 1438 | 27.29 | 4889.8 | 2297.8 | 2396.2 | 3471 | 1223.3 | 0.64421 | 4.162
2024-12-10 | 3:23 | Data | 0 | 35.255 | 34.378 | 121.902 | 7.64 | 116.351 | 2210.77 | 25.7 | 54.485 | 6.47 | 1.118 | 3.054 | 7518.2 | 0.83 | 97.5 | 73.2 | 1437 | 27.24 | 4886.8 | 2296.4 | 2376.7 | 3454.4 | 1223.3 | 0.64873 | 4.172
2024-12-10 | 3:23 | Data | 0 | 35.147 | 34.54 | 121.902 | 7.64 | 116.215 | 2211.68 | 25.7 | 54.485 | 6.47 | 1.131 | 3.031 | 7504.64 | 0.749 | 97.5 | 72.8 | 1437 | 27.24 | 4878 | 2294.2 | 2391.3 | 3464.5 | 1223.3 | 0.64367 | 4.161
2024-12-10 | 3:23 | Data | 0 | 35.282 | 34.735 | 121.902 | 7.64 | 116.261 | 2208.97 | 25.69 | 54.485 | 6.47 | 1.125 | 3.034 | 7509.16 | 0.891 | 97.5 | 73 | 1435 | 27.24 | 4881 | 2308 | 2389.8 | 3468.4 | 1223.3 | 0.64811 | 4.158
2024-12-10 | 3:23 | Data | 0 | 35.485 | 34.783 | 122.037 | 7.64 | 116.351 | 2208.97 | 25.7 | 54.575 | 6.47 | 1.122 | 3.039 | 7509.16 | 0.716 | 97.5 | 73 | 1436 | 27.29 | 4881 | 2304.4 | 2368 | 3456.9 | 1223.3 | 0.64984 | 4.162
2024-12-10 | 3:23 | Data | 0 | 35.262 | 34.371 | 121.947 | 7.64 | 116.306 | 2210.77 | 25.68 | 54.665 | 6.47 | 1.13 | 3.026 | 7491.07 | 1.053 | 97.5 | 72.8 | 1437 | 27.29 | 4869.2 | 2297.1 | 2387.1 | 3465.5 | 1223.4 | 0.64399 | 4.155
2024-12-10 | 3:23 | Data | 0 | 35.255 | 34.594 | 121.992 | 7.64 | 116.351 | 2211.68 | 25.69 | 54.575 | 6.47 | 1.121 | 3.038 | 7491.07 | 0.79 | 97.5 | 73.1 | 1438 | 27.29 | 4869.2 | 2309.4 | 2378.6 | 3460.2 | 1223.4 | 0.65181 | 4.159
2024-12-10 | 3:23 | Data | 0 | 35.498 | 34.486 | 122.037 | 7.64 | 116.351 | 2208.06 | 25.67 | 54.304 | 6.47 | 1.12 | 3.027 | 7491.07 | 0.965 | 97.5 | 73 | 1435 | 27.15 | 4869.2 | 2293.3 | 2385.2 | 3461.2 | 1223.4 | 0.64554 | 4.147
2024-12-10 | 3:23 | Data | 0 | 35.485 | 34.357 | 122.083 | 7.64 | 116.306 | 2211.68 | 25.68 | 54.575 | 6.47 | 1.118 | 3.026 | 7504.64 | 0.925 | 97.5 | 73 | 1437 | 27.29 | 4878 | 2299.3 | 2371.7 | 3456.4 | 1223.4 | 0.64737 | 4.143
2024-12-10 | 3:23 | Data | 0 | 35.464 | 34.344 | 121.947 | 7.64 | 116.396 | 2210.77 | 25.67 | 54.485 | 6.47 | 1.124 | 3.036 | 7495.59 | 1.019 | 97.5 | 73 | 1437 | 27.24 | 4872.1 | 2295.1 | 2372.4 | 3449.3 | 1223.4 | 0.64698 | 4.159
2024-12-10 | 3:23 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.306 | 2205.35 | 25.66 | 54.394 | 6.47 | 1.117 | 3.047 | 7491.07 | 0.918 | 97.5 | 73.2 | 1433 | 27.15 | 4869.2 | 2299.3 | 2354.9 | 3441.3 | 1223.4 | 0.6531 | 4.163
2024-12-10 | 3:24 | Data | 0 | 35.458 | 34.391 | 121.992 | 7.64 | 116.306 | 2206.25 | 25.67 | 54.304 | 6.47 | 1.12 | 3.041 | 7500.11 | 0.911 | 97.5 | 73.1 | 1434 | 27.2 | 4875.1 | 2287.7 | 2370.1 | 3444.3 | 1223.4 | 0.6448 | 4.161
2024-12-10 | 3:24 | Data | 0 | 35.154 | 34.56 | 121.947 | 7.64 | 116.261 | 2205.35 | 25.66 | 54.485 | 6.47 | 1.118 | 3.041 | 7509.16 | 0.716 | 97.5 | 73.1 | 1434 | 27.24 | 4881 | 2306.2 | 2385.8 | 3472.2 | 1223.4 | 0.64726 | 4.159
2024-12-10 | 3:24 | Data | 0 | 35.532 | 34.567 | 122.128 | 7.64 | 116.306 | 2206.25 | 25.65 | 54.575 | 6.47 | 1.121 | 3.043 | 7518.2 | 0.932 | 97.5 | 73.1 | 1434 | 27.2 | 4886.8 | 2293.2 | 2363.6 | 3441.7 | 1223.4 | 0.64746 | 4.163
2024-12-10 | 3:24 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.351 | 2206.25 | 25.64 | 54.575 | 6.47 | 1.132 | 3.031 | 7504.64 | 0.918 | 97.5 | 72.8 | 1434 | 27.29 | 4878 | 2278.5 | 2369.9 | 3439.1 | 1223.4 | 0.64552 | 4.163
2024-12-10 | 3:24 | Data | 0 | 35.282 | 34.459 | 121.992 | 7.64 | 116.351 | 2343.64 | 25.66 | 54.575 | 6.47 | 1.118 | 3.038 | 7504.64 | 1.121 | 97.7 | 73.1 | 1524 | 27.24 | 4878 | 2308.6 | 2362.9 | 3453.7 | 1223.4 | 0.65085 | 4.155
2024-12-10 | 3:24 | Data | 0 | 35.37 | 34.56 | 121.992 | 7.64 | 116.306 | 2230.66 | 25.66 | 54.485 | 6.47 | 1.127 | 3.026 | 7504.64 | 0.891 | 97.6 | 72.9 | 1450 | 27.24 | 4878 | 2304.8 | 2347.7 | 3443.5 | 1223.4 | 0.65309 | 4.151
2024-12-10 | 3:24 | Data | 0 | 35.262 | 34.567 | 122.037 | 7.64 | 116.306 | 2229.75 | 25.66 | 54.304 | 6.47 | 1.125 | 3.035 | 7518.2 | 0.871 | 97.6 | 72.9 | 1450 | 27.15 | 4886.8 | 2315.4 | 2373.9 | 3464 | 1223.4 | 0.65151 | 4.159
2024-12-10 | 3:24 | Data | 0 | 35.485 | 34.621 | 121.992 | 7.64 | 116.396 | 2227.95 | 25.66 | 54.304 | 6.47 | 1.12 | 3.024 | 7504.64 | 0.925 | 97.6 | 73 | 1448 | 27.15 | 4878 | 2283.9 | 2358.3 | 3432.1 | 1223.4 | 0.64763 | 4.145
2024-12-10 | 3:24 | Data | 0 | 35.37 | 34.567 | 121.992 | 7.64 | 116.306 | 2227.95 | 25.66 | 54.304 | 6.47 | 1.122 | 3.038 | 7509.16 | 1.013 | 97.6 | 73 | 1448 | 27.15 | 4881 | 2301.4 | 2362.5 | 3449.3 | 1223.4 | 0.64851 | 4.161
2024-12-10 | 3:24 | Data | 0 | 35.437 | 34.567 | 122.037 | 7.64 | 116.306 | 2222.52 | 25.66 | 54.485 | 6.47 | 1.119 | 3.019 | 7504.64 | 0.911 | 97.5 | 73 | 1445 | 27.24 | 4878 | 2290.3 | 2384.4 | 3459.4 | 1223.4 | 0.64567 | 4.139
2024-12-10 | 3:24 | Data | 0 | 35.329 | 34.567 | 122.173 | 7.64 | 116.396 | 2222.52 | 25.68 | 54.485 | 6.47 | 1.132 | 3.03 | 7504.64 | 0.709 | 97.5 | 72.8 | 1445 | 27.24 | 4878 | 2300.8 | 2378.8 | 3459.7 | 1223.4 | 0.64742 | 4.163
2024-12-10 | 3:24 | Data | 0 | 35.37 | 34.735 | 122.037 | 7.64 | 116.396 | 2221.62 | 25.66 | 54.575 | 6.47 | 1.129 | 3.033 | 7504.64 | 0.851 | 97.5 | 72.9 | 1445 | 27.29 | 4878 | 2298 | 2383 | 3461.3 | 1223.4 | 0.64429 | 4.161
2024-12-10 | 3:24 | Data | 0 | 35.37 | 34.567 | 122.037 | 7.64 | 116.351 | 2225.23 | 25.68 | 54.485 | 6.47 | 1.12 | 3.034 | 7518.2 | 0.716 | 97.6 | 73 | 1446 | 27.24 | 4886.8 | 2316.3 | 2375.6 | 3464.1 | 1223.4 | 0.65227 | 4.153
2024-12-10 | 3:24 | Data | 0 | 35.431 | 34.479 | 122.083 | 7.64 | 116.396 | 2225.23 | 25.68 | 54.575 | 6.47 | 1.117 | 3.03 | 7518.2 | 1.053 | 97.5 | 73.1 | 1446 | 27.24 | 4886.8 | 2291.3 | 2360.5 | 3448.5 | 1223.4 | 0.64937 | 4.146
2024-12-10 | 3:24 | Data | 0 | 35.478 | 34.567 | 121.902 | 7.64 | 116.351 | 2225.23 | 25.67 | 54.575 | 6.47 | 1.121 | 3.034 | 7518.2 | 0.918 | 97.5 | 73 | 1446 | 27.29 | 4886.8 | 2307 | 2361.6 | 3453 | 1223.4 | 0.651 | 4.154
2024-12-10 | 3:24 | Data | 0 | 35.485 | 34.621 | 121.992 | 7.64 | 116.351 | 2227.95 | 25.67 | 54.485 | 6.46 | 1.122 | 3.039 | 7531.77 | 0.803 | 97.6 | 73 | 1448 | 27.29 | 4895.6 | 2281.2 | 2359.9 | 3435.1 | 1223.4 | 0.64792 | 4.161
2024-12-10 | 3:24 | Data | 0 | 35.593 | 34.749 | 122.128 | 7.64 | 116.396 | 2224.33 | 25.68 | 54.485 | 6.47 | 1.129 | 3.046 | 7531.77 | 1.087 | 97.6 | 73 | 1446 | 27.24 | 4895.6 | 2309.1 | 2365.2 | 3450 | 1223.4 | 0.65125 | 4.176
2024-12-10 | 3:24 | Data | 0 | 35.681 | 34.796 | 122.083 | 7.64 | 116.396 | 2224.33 | 25.68 | 54.485 | 6.47 | 1.124 | 3.035 | 7531.77 | 0.911 | 97.6 | 73 | 1446 | 27.2 | 4895.6 | 2311.2 | 2370.3 | 3454.8 | 1223.4 | 0.65339 | 4.161
2024-12-10 | 3:25 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.441 | 2225.23 | 25.68 | 54.394 | 6.47 | 1.128 | 3.036 | 7531.77 | 0.918 | 97.6 | 72.9 | 1446 | 27.2 | 4895.6 | 2305.9 | 2352.3 | 3445.7 | 1223.4 | 0.65208 | 4.164
2024-12-10 | 3:25 | Data | 0 | 35.377 | 34.567 | 122.037 | 7.64 | 116.351 | 2225.23 | 25.68 | 54.575 | 6.46 | 1.13 | 3.051 | 7839.28 | 0.905 | 97.5 | 73 | 1446 | 27.29 | 5095.5 | 2304.2 | 2389 | 3465.3 | 1223.4 | 0.64812 | 4.18
2024-12-10 | 3:25 | Data | 0 | 35.491 | 34.567 | 122.037 | 7.64 | 116.396 | 2223.43 | 25.67 | 54.575 | 6.47 | 1.128 | 3.04 | 7807.62 | 0.918 | 97.5 | 72.9 | 1445 | 27.29 | 5075 | 2282.1 | 2393.1 | 3457.7 | 1223.4 | 0.64044 | 4.168
2024-12-10 | 3:25 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.396 | 2221.62 | 25.68 | 54.575 | 6.47 | 1.129 | 3.039 | 7527.25 | 0.918 | 97.5 | 72.9 | 1445 | 27.29 | 4892.7 | 2305.1 | 2380.9 | 3459.8 | 1223.4 | 0.64748 | 4.168
2024-12-10 | 3:25 | Data | 0 | 35.37 | 34.567 | 121.992 | 7.64 | 116.306 | 2222.52 | 25.67 | 54.485 | 6.47 | 1.121 | 3.006 | 7518.2 | 0.817 | 97.5 | 72.8 | 1445 | 27.29 | 4886.8 | 2300.2 | 2369.1 | 3452.5 | 1223.4 | 0.64951 | 4.127
2024-12-10 | 3:25 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.441 | 2222.52 | 25.68 | 54.575 | 6.47 | 1.122 | 3.013 | 7518.2 | 0.918 | 97.5 | 72.9 | 1444 | 27.24 | 4886.8 | 2299 | 2346.2 | 3434.3 | 1223.4 | 0.6526 | 4.134
2024-12-10 | 3:25 | Data | 0 | 35.485 | 34.594 | 121.947 | 7.64 | 116.351 | 2222.52 | 25.68 | 54.485 | 6.46 | 1.117 | 3.055 | 7518.2 | 0.891 | 97.5 | 73.2 | 1445 | 27.24 | 4886.8 | 2308.1 | 2372.1 | 3453.5 | 1223.4 | 0.6517 | 4.172
2024-12-10 | 3:25 | Data | 0 | 35.485 | 34.371 | 122.037 | 7.64 | 116.351 | 2225.23 | 25.67 | 54.485 | 6.47 | 1.118 | 3.04 | 7522.72 | 0.965 | 97.5 | 73.1 | 1446 | 27.24 | 4889.8 | 2306.8 | 2375.1 | 3456.7 | 1223.4 | 0.65412 | 4.158
2024-12-10 | 3:25 | Data | 0 | 35.431 | 34.567 | 121.992 | 7.64 | 116.351 | 2222.52 | 25.68 | 54.575 | 6.47 | 1.121 | 3.046 | 7536.29 | 0.911 | 97.5 | 73.1 | 1445 | 27.24 | 4898.6 | 2289.6 | 2382.2 | 3450.4 | 1223.4 | 0.64605 | 4.169
2024-12-10 | 3:25 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.306 | 2226.14 | 25.67 | 54.575 | 6.47 | 1.115 | 3.059 | 7531.77 | 0.918 | 97.5 | 73.3 | 1447 | 27.29 | 4895.6 | 2294.1 | 2362.6 | 3442.8 | 1223.4 | 0.65073 | 4.174
2024-12-10 | 3:25 | Data | 0 | 35.505 | 34.553 | 121.992 | 7.64 | 116.306 | 2227.95 | 25.69 | 54.575 | 6.47 | 1.125 | 3.028 | 7531.77 | 0.945 | 97.6 | 72.9 | 1448 | 27.24 | 4895.6 | 2294.7 | 2363.5 | 3446.2 | 1223.4 | 0.64793 | 4.154
2024-12-10 | 3:25 | Data | 0 | 35.458 | 34.789 | 122.037 | 7.64 | 116.396 | 2229.75 | 25.69 | 54.756 | 6.47 | 1.124 | 3.055 | 7518.2 | 0.898 | 97.5 | 73.1 | 1450 | 27.38 | 4886.8 | 2302.1 | 2347.7 | 3436.7 | 1223.4 | 0.65092 | 4.179
2024-12-10 | 3:25 | Data | 0 | 35.6 | 34.573 | 122.083 | 7.64 | 116.441 | 2232.47 | 25.69 | 54.304 | 6.47 | 1.125 | 3.043 | 7527.25 | 0.959 | 97.6 | 73 | 1451 | 27.15 | 4892.7 | 2320.3 | 2372.4 | 3459.4 | 1223.4 | 0.65413 | 4.167
2024-12-10 | 3:25 | Data | 0 | 35.681 | 34.742 | 122.218 | 7.64 | 116.396 | 2349.06 | 25.7 | 54.214 | 6.47 | 1.121 | 3.029 | 7531.77 | 1.134 | 97.7 | 73 | 1527 | 27.11 | 4895.6 | 2314.3 | 2364.6 | 3455.4 | 1223.4 | 0.65499 | 4.151
2024-12-10 | 3:25 | Data | 0 | 35.485 | 34.742 | 122.037 | 7.64 | 116.396 | 2175.52 | 25.67 | 54.304 | 6.47 | 1.12 | 3.047 | 7531.77 | 0.803 | 97.5 | 73.1 | 1414 | 27.15 | 4895.6 | 2304 | 2359.4 | 3447.7 | 1223.4 | 0.65154 | 4.166
2024-12-10 | 3:25 | Data | 0 | 35.431 | 34.573 | 122.128 | 7.64 | 116.441 | 2164.68 | 25.68 | 54.304 | 6.47 | 1.124 | 3.045 | 7531.77 | 0.722 | 97.5 | 73 | 1407 | 27.15 | 4895.6 | 2314 | 2346.5 | 3443.7 | 1223.4 | 0.65356 | 4.169
2024-12-10 | 3:25 | Data | 0 | 35.6 | 34.459 | 121.992 | 7.64 | 116.396 | 2172.81 | 25.68 | 54.033 | 6.47 | 1.13 | 3.035 | 7531.77 | 0.932 | 97.5 | 72.9 | 1412 | 27.02 | 4895.6 | 2299.2 | 2363.8 | 3445.7 | 1223.4 | 0.65024 | 4.165
2024-12-10 | 3:25 | Data | 0 | 35.485 | 34.607 | 121.992 | 7.64 | 116.396 | 2174.62 | 25.68 | 54.214 | 6.47 | 1.128 | 3.035 | 7549.86 | 0.83 | 97.5 | 72.9 | 1414 | 27.15 | 4907.4 | 2295.4 | 2347.9 | 3438.5 | 1223.4 | 0.65211 | 4.163
2024-12-10 | 3:26 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.396 | 2177.33 | 25.69 | 54.485 | 6.47 | 1.131 | 3.018 | 7545.34 | 0.905 | 97.5 | 72.8 | 1416 | 27.24 | 4904.5 | 2293.7 | 2366.9 | 3451.2 | 1223.4 | 0.64632 | 4.15
2024-12-10 | 3:26 | Data | 0 | 35.714 | 34.621 | 122.173 | 7.64 | 116.487 | 2182.75 | 25.69 | 54.485 | 6.47 | 1.122 | 3.023 | 7549.86 | 0.918 | 97.5 | 72.9 | 1418 | 27.24 | 4907.4 | 2301.7 | 2363.9 | 3454.4 | 1223.4 | 0.64712 | 4.145
2024-12-10 | 3:26 | Data | 0 | 35.539 | 34.567 | 122.037 | 7.64 | 116.396 | 2283.08 | 25.69 | 54.575 | 6.47 | 1.125 | 3.045 | 7545.34 | 0.938 | 97.6 | 73 | 1484 | 27.24 | 4904.5 | 2310 | 2365.2 | 3462.5 | 1223.4 | 0.65186 | 4.17
2024-12-10 | 3:26 | Data | 0 | 35.485 | 34.675 | 122.083 | 7.64 | 116.396 | 2281.27 | 25.69 | 54.575 | 6.47 | 1.121 | 3.046 | 7545.34 | 0.871 | 97.6 | 73.1 | 1482 | 27.24 | 4904.5 | 2317.1 | 2355.1 | 3457.1 | 1223.4 | 0.65168 | 4.167
2024-12-10 | 3:26 | Data | 0 | 35.329 | 34.681 | 122.083 | 7.64 | 116.441 | 2277.66 | 25.68 | 54.485 | 6.47 | 1.118 | 3.029 | 7518.2 | 0.722 | 97.6 | 73 | 1480 | 27.24 | 4886.8 | 2314 | 2382.8 | 3474.9 | 1223.5 | 0.65138 | 4.147
2024-12-10 | 3:26 | Data | 0 | 35.525 | 34.573 | 122.083 | 7.64 | 116.487 | 2275.85 | 25.69 | 54.394 | 6.47 | 1.118 | 3.04 | 7522.72 | 0.911 | 97.6 | 73.1 | 1480 | 27.24 | 4889.8 | 2303.1 | 2351.8 | 3466.7 | 1223.5 | 0.64974 | 4.158
2024-12-10 | 3:26 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.396 | 2175.52 | 25.69 | 54.304 | 6.47 | 1.134 | 3.044 | 7522.72 | 0.918 | 97.5 | 72.8 | 1414 | 27.11 | 4889.8 | 2325.6 | 2349.9 | 3453.4 | 1223.5 | 0.65896 | 4.179
2024-12-10 | 3:26 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.396 | 2178.24 | 25.69 | 54.214 | 6.47 | 1.133 | 3.044 | 7518.2 | 0.918 | 97.5 | 72.9 | 1415 | 27.11 | 4886.8 | 2322.1 | 2361 | 3460.2 | 1223.5 | 0.65532 | 4.177
2024-12-10 | 3:26 | Data | 0 | 35.687 | 34.965 | 122.173 | 7.64 | 116.441 | 2180.04 | 25.69 | 54.304 | 6.47 | 1.128 | 3.033 | 7518.2 | 1.033 | 97.5 | 72.9 | 1417 | 27.15 | 4886.8 | 2336.6 | 2357 | 3442.8 | 1223.5 | 0.65205 | 4.161
2024-12-10 | 3:26 | Data | 0 | 35.485 | 34.567 | 122.128 | 7.64 | 116.396 | 2183.66 | 25.7 | 54.214 | 6.46 | 1.121 | 3.045 | 7518.2 | 0.918 | 97.5 | 73.1 | 1419 | 27.15 | 4886.8 | 2355.2 | 2384 | 3501.2 | 1223.5 | 0.65445 | 4.167
2024-12-10 | 3:26 | Data | 0 | 35.512 | 34.675 | 122.083 | 7.64 | 116.441 | 2178.24 | 25.68 | 54.575 | 6.46 | 1.121 | 3.051 | 7518.2 | 0.716 | 97.5 | 73.1 | 1416 | 27.29 | 4886.8 | 2327.5 | 2373.2 | 3473.4 | 1223.5 | 0.64905 | 4.171
2024-12-10 | 3:26 | Data | 0 | 35.694 | 34.594 | 122.083 | 7.64 | 116.487 | 2180.04 | 25.69 | 54.485 | 6.46 | 1.124 | 3.038 | 7531.77 | 1.033 | 97.5 | 73 | 1417 | 27.29 | 4895.6 | 2346.7 | 2370 | 3487.5 | 1223.5 | 0.65447 | 4.161
2024-12-10 | 3:26 | Data | 0 | 35.485 | 34.796 | 122.173 | 7.64 | 116.487 | 2180.95 | 25.7 | 54.485 | 6.47 | 1.131 | 3.037 | 7518.2 | 0.972 | 97.5 | 72.8 | 1417 | 27.29 | 4886.8 | 2325.3 | 2366.7 | 3470.5 | 1223.5 | 0.6504 | 4.17
2024-12-10 | 3:26 | Data | 0 | 35.586 | 34.459 | 121.992 | 7.64 | 116.441 | 2178.24 | 25.69 | 54.756 | 6.47 | 1.129 | 3.045 | 7518.2 | 0.952 | 97.5 | 73 | 1416 | 27.38 | 4886.8 | 2342.2 | 2368.8 | 3480.4 | 1223.5 | 0.6534 | 4.173
2024-12-10 | 3:26 | Data | 0 | 35.6 | 34.594 | 122.037 | 7.64 | 116.396 | 2189.08 | 25.7 | 54.304 | 6.47 | 1.127 | 3.024 | 7504.64 | 0.83 | 97.5 | 72.9 | 1422 | 27.15 | 4878 | 2323.5 | 2388.5 | 3483.6 | 1223.5 | 0.64857 | 4.149
2024-12-10 | 3:26 | Data | 0 | 35.694 | 34.594 | 122.218 | 7.64 | 116.487 | 2191.79 | 25.69 | 54.394 | 6.47 | 1.129 | 3.041 | 7518.2 | 0.918 | 97.5 | 72.9 | 1425 | 27.24 | 4886.8 | 2320.8 | 2389.9 | 3479.9 | 1223.5 | 0.64885 | 4.169
2024-12-10 | 3:26 | Data | 0 | 35.491 | 34.567 | 122.037 | 7.64 | 116.396 | 2194.5 | 25.68 | 54.394 | 6.46 | 1.128 | 3.046 | 7509.16 | 0.911 | 97.5 | 73 | 1426 | 27.24 | 4881 | 2310.3 | 2392.7 | 3476.6 | 1223.5 | 0.64488 | 4.175
2024-12-10 | 3:26 | Data | 0 | 35.512 | 34.783 | 122.037 | 7.64 | 116.441 | 2274.04 | 25.69 | 54.394 | 6.47 | 1.129 | 3.052 | 7518.2 | 0.81 | 97.6 | 73 | 1479 | 27.15 | 4886.8 | 2356.4 | 2377.9 | 3495.7 | 1223.5 | 0.65758 | 4.181
2024-12-10 | 3:27 | Data | 0 | 35.498 | 34.789 | 122.173 | 7.64 | 116.441 | 2190.89 | 25.69 | 54.304 | 6.47 | 1.12 | 3.039 | 7518.2 | 0.817 | 97.5 | 73.1 | 1422 | 27.15 | 4886.8 | 2340.4 | 2385.5 | 3494.9 | 1223.5 | 0.65051 | 4.157
2024-12-10 | 3:27 | Data | 0 | 35.6 | 34.567 | 122.083 | 7.64 | 116.441 | 2175.52 | 25.69 | 54.304 | 6.46 | 1.121 | 3.052 | 7518.2 | 0.932 | 97.5 | 73.1 | 1414 | 27.15 | 4886.8 | 2342.8 | 2389.9 | 3495.2 | 1223.5 | 0.65234 | 4.172
2024-12-10 | 3:27 | Data | 0 | 35.485 | 34.769 | 122.128 | 7.64 | 116.487 | 2181.85 | 25.68 | 54.214 | 6.47 | 1.127 | 3.036 | 7504.64 | 0.891 | 97.5 | 72.9 | 1419 | 27.15 | 4878 | 2310.8 | 2371 | 3462.4 | 1223.5 | 0.65166 | 4.163
2024-12-10 | 3:27 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.396 | 2182.75 | 25.69 | 54.575 | 6.47 | 1.126 | 3.031 | 7509.16 | 0.918 | 97.5 | 72.9 | 1419 | 27.29 | 4881 | 2314.8 | 2370.4 | 3463.9 | 1223.5 | 0.65073 | 4.158
2024-12-10 | 3:27 | Data | 0 | 35.491 | 34.567 | 122.128 | 7.64 | 116.441 | 2177.33 | 25.69 | 54.304 | 6.47 | 1.131 | 3.035 | 7509.16 | 0.803 | 97.5 | 72.8 | 1415 | 27.15 | 4881 | 2322.8 | 2354.2 | 3463.1 | 1223.5 | 0.6535 | 4.166
2024-12-10 | 3:27 | Data | 0 | 35.714 | 34.749 | 122.173 | 7.64 | 116.487 | 2178.24 | 25.68 | 54.304 | 6.47 | 1.131 | 3.035 | 7504.64 | 0.918 | 97.5 | 72.9 | 1416 | 27.2 | 4878 | 2347.3 | 2379.5 | 3494.2 | 1223.5 | 0.65442 | 4.165
2024-12-10 | 3:27 | Data | 0 | 35.485 | 34.769 | 122.083 | 7.64 | 116.441 | 2180.04 | 25.69 | 54.304 | 6.46 | 1.124 | 3.047 | 7509.16 | 0.945 | 97.5 | 73.1 | 1418 | 27.15 | 4881 | 2316.2 | 2360.6 | 3458.6 | 1223.5 | 0.65197 | 4.17
2024-12-10 | 3:27 | Data | 0 | 35.485 | 34.681 | 122.128 | 7.64 | 116.396 | 2183.66 | 25.67 | 54.214 | 6.46 | 1.118 | 3.054 | 7518.2 | 0.918 | 97.5 | 73.2 | 1419 | 27.11 | 4886.8 | 2342 | 2385.9 | 3495.7 | 1223.5 | 0.65106 | 4.172
2024-12-10 | 3:27 | Data | 0 | 35.714 | 34.965 | 122.263 | 7.64 | 116.487 | 2186.37 | 25.69 | 54.485 | 6.47 | 1.124 | 3.035 | 7513.68 | 0.749 | 97.5 | 73 | 1421 | 27.24 | 4883.9 | 2312.5 | 2400.3 | 3481.5 | 1223.5 | 0.64781 | 4.16
2024-12-10 | 3:27 | Data | 0 | 35.491 | 34.621 | 122.128 | 7.64 | 116.487 | 2186.37 | 25.69 | 54.214 | 6.47 | 1.12 | 3.037 | 7341.83 | 1.006 | 97.5 | 73.1 | 1421 | 27.11 | 4772.2 | 2318.2 | 2386 | 3469.6 | 1223.5 | 0.65166 | 4.157
2024-12-10 | 3:27 | Data | 0 | 35.464 | 34.567 | 122.037 | 7.64 | 116.396 | 2189.08 | 25.68 | 54.304 | 6.47 | 1.125 | 3.043 | 7341.83 | 0.918 | 97.5 | 73 | 1423 | 27.15 | 4772.2 | 2266.6 | 2383.3 | 3433.1 | 1223.5 | 0.64375 | 4.168
2024-12-10 | 3:27 | Data | 0 | 35.66 | 34.621 | 122.128 | 7.64 | 116.441 | 2189.08 | 25.67 | 54.394 | 6.47 | 1.126 | 3.034 | 7341.83 | 1.087 | 97.5 | 72.9 | 1423 | 27.24 | 4772.2 | 2250.7 | 2372.3 | 3417.9 | 1223.5 | 0.64387 | 4.16
2024-12-10 | 3:27 | Data | 0 | 35.573 | 34.675 | 122.128 | 7.64 | 116.396 | 2187.27 | 25.67 | 54.575 | 6.47 | 1.126 | 3.026 | 7337.31 | 0.898 | 97.5 | 72.9 | 1422 | 27.24 | 4769.3 | 2259.3 | 2336.2 | 3399.8 | 1223.5 | 0.64846 | 4.151
2024-12-10 | 3:27 | Data | 0 | 35.485 | 34.681 | 121.992 | 7.64 | 116.351 | 2188.18 | 25.69 | 54.304 | 6.47 | 1.128 | 3.035 | 7518.2 | 0.803 | 97.5 | 72.9 | 1422 | 27.15 | 4886.8 | 2259.6 | 2339.6 | 3401.3 | 1223.5 | 0.64702 | 4.163
2024-12-10 | 3:27 | Data | 0 | 35.485 | 34.681 | 122.037 | 7.64 | 116.441 | 2189.08 | 25.68 | 54.214 | 6.46 | 1.121 | 3.024 | 7522.72 | 0.918 | 97.5 | 72.9 | 1423 | 27.15 | 4889.8 | 2253.1 | 2344.2 | 3397.1 | 1223.5 | 0.6476 | 4.145
2024-12-10 | 3:27 | Data | 0 | 35.485 | 34.594 | 122.037 | 7.64 | 116.441 | 2191.79 | 25.69 | 54.304 | 6.47 | 1.127 | 3.043 | 7522.72 | 0.891 | 97.5 | 73 | 1424 | 27.15 | 4889.8 | 2249.5 | 2330.8 | 3385.1 | 1223.5 | 0.64868 | 4.17
2024-12-10 | 3:27 | Data | 0 | 35.444 | 34.783 | 122.173 | 7.64 | 116.441 | 2197.22 | 25.68 | 54.304 | 6.47 | 1.126 | 3.04 | 7531.77 | 0.844 | 97.5 | 73 | 1428 | 27.11 | 4895.6 | 2246.2 | 2348.8 | 3395.3 | 1223.5 | 0.64503 | 4.166
2024-12-10 | 3:27 | Data | 0 | 35.471 | 34.567 | 122.083 | 7.64 | 116.396 | 2199.02 | 25.68 | 54.304 | 6.47 | 1.121 | 3.047 | 7536.29 | 1.087 | 97.5 | 73.1 | 1429 | 27.11 | 4898.6 | 2244.7 | 2363.4 | 3405.3 | 1223.5 | 0.64446 | 4.168
2024-12-10 | 3:28 | Data | 0 | 35.485 | 34.681 | 122.083 | 7.64 | 116.396 | 2199.93 | 25.68 | 54.304 | 6.47 | 1.117 | 3.04 | 7518.2 | 0.918 | 97.5 | 73.2 | 1430 | 27.15 | 4886.8 | 2316.7 | 2384.7 | 3479.6 | 1223.5 | 0.64738 | 4.157
2024-12-10 | 3:28 | Data | 0 | 35.708 | 34.573 | 122.128 | 7.64 | 116.441 | 2205.35 | 25.68 | 54.304 | 6.47 | 1.126 | 3.023 | 7531.77 | 0.932 | 97.5 | 72.9 | 1434 | 27.15 | 4895.6 | 2327 | 2375.4 | 3472.6 | 1223.5 | 0.65236 | 4.148
2024-12-10 | 3:28 | Data | 0 | 35.573 | 34.567 | 122.128 | 7.64 | 116.396 | 2208.97 | 25.67 | 54.304 | 6.47 | 1.121 | 3.025 | 7518.2 | 0.925 | 97.5 | 73 | 1436 | 27.15 | 4886.8 | 2310.4 | 2372.8 | 3461.7 | 1223.5 | 0.64992 | 4.145
2024-12-10 | 3:28 | Data | 0 | 35.485 | 34.553 | 122.037 | 7.64 | 116.351 | 2213.49 | 25.68 | 54.214 | 6.47 | 1.118 | 3.039 | 7531.77 | 0.938 | 97.6 | 73.1 | 1439 | 27.11 | 4895.6 | 2303.7 | 2380.2 | 3463.6 | 1223.5 | 0.64772 | 4.158
2024-12-10 | 3:28 | Data | 0 | 35.701 | 34.573 | 122.037 | 7.64 | 116.441 | 2213.49 | 25.68 | 54.304 | 6.46 | 1.126 | 3.019 | 7545.34 | 0.999 | 97.5 | 72.8 | 1439 | 27.2 | 4904.5 | 2300.8 | 2363.5 | 3444.6 | 1223.5 | 0.64972 | 4.145
2024-12-10 | 3:28 | Data | 0 | 35.262 | 34.567 | 122.037 | 7.64 | 116.306 | 2210.77 | 25.68 | 54.214 | 6.47 | 1.135 | 3.025 | 7531.77 | 0.803 | 97.5 | 72.7 | 1437 | 27.11 | 4895.6 | 2304.6 | 2389.2 | 3466.6 | 1223.5 | 0.64726 | 4.16
2024-12-10 | 3:28 | Data | 0 | 35.532 | 34.567 | 122.083 | 7.64 | 116.396 | 2214.39 | 25.67 | 54.214 | 6.46 | 1.127 | 3.035 | 7531.77 | 0.918 | 97.6 | 72.9 | 1439 | 27.11 | 4895.6 | 2304.3 | 2354.7 | 3443.6 | 1223.5 | 0.65144 | 4.161
2024-12-10 | 3:28 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.351 | 2210.77 | 25.68 | 54.304 | 6.46 | 1.113 | 3.04 | 7531.77 | 0.918 | 97.5 | 73.2 | 1437 | 27.15 | 4895.6 | 2319.5 | 2359.2 | 3457.8 | 1223.5 | 0.65295 | 4.153
2024-12-10 | 3:28 | Data | 0 | 35.377 | 34.567 | 122.083 | 7.64 | 116.396 | 2208.97 | 25.67 | 54.394 | 6.47 | 1.12 | 3.03 | 7549.86 | 0.891 | 97.5 | 73 | 1436 | 27.11 | 4907.4 | 2304.2 | 2367.8 | 3455.4 | 1223.5 | 0.64925 | 4.148
2024-12-10 | 3:28 | Data | 0 | 35.593 | 34.675 | 122.128 | 7.64 | 116.351 | 2208.06 | 25.68 | 54.304 | 6.47 | 1.122 | 3.046 | 7549.86 | 0.776 | 97.5 | 73.1 | 1435 | 27.15 | 4907.4 | 2301.8 | 2369.5 | 3463.4 | 1223.5 | 0.64951 | 4.168
2024-12-10 | 3:28 | Data | 0 | 35.654 | 34.567 | 122.083 | 7.64 | 116.396 | 2208.06 | 25.68 | 54.214 | 6.46 | 1.122 | 3.054 | 7527.25 | 0.938 | 97.5 | 73.1 | 1436 | 27.15 | 4892.7 | 2313.6 | 2368.1 | 3459.4 | 1223.5 | 0.64936 | 4.177
2024-12-10 | 3:28 | Data | 0 | 35.505 | 34.567 | 122.037 | 7.64 | 116.396 | 2208.06 | 25.67 | 54.214 | 6.47 | 1.119 | 3.045 | 7531.77 | 0.918 | 97.5 | 73.1 | 1435 | 27.15 | 4895.6 | 2301.4 | 2391.3 | 3464.2 | 1223.5 | 0.64448 | 4.164
2024-12-10 | 3:28 | Data | 0 | 35.397 | 34.567 | 122.037 | 7.64 | 116.396 | 2205.35 | 25.66 | 54.304 | 6.47 | 1.124 | 3.035 | 7549.86 | 0.918 | 97.5 | 73 | 1434 | 27.15 | 4907.4 | 2300.3 | 2389.7 | 3462.6 | 1223.5 | 0.64492 | 4.16
2024-12-10 | 3:28 | Data | 0 | 35.485 | 34.513 | 121.992 | 7.64 | 116.351 | 2208.06 | 25.68 | 54.214 | 6.47 | 1.112 | 3.048 | 7531.77 | 0.938 | 97.5 | 73.3 | 1435 | 27.11 | 4895.6 | 2318.8 | 2393.2 | 3482.1 | 1223.5 | 0.64845 | 4.161
2024-12-10 | 3:28 | Data | 0 | 35.255 | 34.513 | 121.947 | 7.64 | 116.306 | 2214.39 | 25.67 | 54.304 | 6.47 | 1.121 | 3.054 | 7527.25 | 1.006 | 97.5 | 73.2 | 1440 | 27.15 | 4892.7 | 2313.2 | 2409.7 | 3488.7 | 1223.6 | 0.64402 | 4.175
2024-12-10 | 3:28 | Data | 0 | 35.431 | 34.675 | 122.083 | 7.64 | 116.351 | 2217.1 | 25.67 | 54.214 | 6.47 | 1.13 | 3.052 | 7545.34 | 0.905 | 97.6 | 73 | 1441 | 27.11 | 4904.5 | 2327.2 | 2381.3 | 3478.9 | 1223.6 | 0.65038 | 4.181
2024-12-10 | 3:28 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.396 | 2215.29 | 25.68 | 54.575 | 6.47 | 1.131 | 3.035 | 7549.86 | 0.918 | 97.5 | 72.8 | 1441 | 27.29 | 4907.4 | 2292.3 | 2377.9 | 3453.4 | 1223.6 | 0.64715 | 4.166
2024-12-10 | 3:29 | Data | 0 | 35.586 | 34.371 | 122.083 | 7.64 | 116.351 | 2217.1 | 25.68 | 54.304 | 6.47 | 1.129 | 3.042 | 7549.86 | 0.925 | 97.5 | 72.9 | 1441 | 27.15 | 4907.4 | 2311.4 | 2364.8 | 3454 | 1223.6 | 0.65311 | 4.171
2024-12-10 | 3:29 | Data | 0 | 35.478 | 34.567 | 122.037 | 7.64 | 116.351 | 2215.29 | 25.67 | 54.485 | 6.46 | 1.122 | 3.025 | 7554.38 | 0.945 | 97.5 | 72.9 | 1440 | 27.24 | 4910.3 | 2318.7 | 2366.3 | 3462.3 | 1223.6 | 0.65254 | 4.148
2024-12-10 | 3:29 | Data | 0 | 35.485 | 34.452 | 121.992 | 7.64 | 116.306 | 2214.39 | 25.67 | 54.304 | 6.47 | 1.126 | 3.052 | 7527.25 | 0.918 | 97.5 | 73.1 | 1439 | 27.15 | 4892.7 | 2308.7 | 2351.6 | 3444.3 | 1223.6 | 0.65287 | 4.177
2024-12-10 | 3:29 | Data | 0 | 35.397 | 34.344 | 121.992 | 7.64 | 116.396 | 2218 | 25.68 | 54.214 | 6.47 | 1.119 | 3.047 | 7531.77 | 0.952 | 97.6 | 73.2 | 1442 | 27.15 | 4895.6 | 2296.8 | 2384.7 | 3461.5 | 1223.6 | 0.64664 | 4.167
2024-12-10 | 3:29 | Data | 0 | 35.255 | 34.56 | 121.947 | 7.64 | 116.351 | 2218 | 25.68 | 54.485 | 6.47 | 1.127 | 3.048 | 7531.77 | 0.898 | 97.5 | 73 | 1442 | 27.24 | 4895.6 | 2303.5 | 2415 | 3477.2 | 1223.6 | 0.64076 | 4.175
2024-12-10 | 3:29 | Data | 0 | 35.262 | 34.735 | 122.083 | 7.64 | 116.351 | 2210.77 | 25.68 | 54.485 | 6.47 | 1.117 | 3.064 | 7934.25 | 0.749 | 97.5 | 73.3 | 1438 | 27.29 | 5157.3 | 2306.6 | 2416.6 | 3480.5 | 1223.6 | 0.64308 | 4.182
2024-12-10 | 3:29 | Data | 0 | 35.512 | 34.398 | 122.037 | 7.64 | 116.441 | 2220.72 | 25.68 | 54.214 | 6.47 | 1.122 | 3.035 | 7920.68 | 1.033 | 97.6 | 73 | 1442 | 27.11 | 5148.4 | 2305.1 | 2404.5 | 3481.6 | 1223.6 | 0.64061 | 4.157
2024-12-10 | 3:29 | Data | 0 | 35.485 | 34.573 | 122.037 | 7.64 | 116.396 | 2218 | 25.69 | 54.214 | 6.46 | 1.131 | 3.035 | 7518.2 | 0.911 | 97.6 | 72.9 | 1442 | 27.11 | 4886.8 | 2312.1 | 2403.8 | 3480.7 | 1223.6 | 0.64507 | 4.164
2024-12-10 | 3:29 | Data | 0 | 35.37 | 34.567 | 122.128 | 7.64 | 116.351 | 2216.2 | 25.69 | 54.214 | 6.47 | 1.122 | 3.055 | 7527.25 | 1.006 | 97.6 | 73.1 | 1441 | 27.11 | 4892.7 | 2302.6 | 2408 | 3472.6 | 1223.6 | 0.64359 | 4.178
2024-12-10 | 3:29 | Data | 0 | 35.512 | 34.567 | 122.083 | 7.64 | 116.441 | 2218.91 | 25.69 | 54.394 | 6.47 | 1.118 | 3.058 | 7518.2 | 0.925 | 97.5 | 73.2 | 1442 | 27.2 | 4886.8 | 2291.7 | 2392.2 | 3465.5 | 1223.6 | 0.64302 | 4.176
2024-12-10 | 3:29 | Data | 0 | 35.708 | 34.783 | 122.128 | 7.64 | 116.487 | 2217.1 | 25.71 | 54.394 | 6.47 | 1.121 | 3.042 | 7504.64 | 0.817 | 97.5 | 73 | 1441 | 27.24 | 4878 | 2302.2 | 2358.9 | 3447.3 | 1223.6 | 0.65135 | 4.164
2024-12-10 | 3:29 | Data | 0 | 35.714 | 34.479 | 122.083 | 7.64 | 116.487 | 2221.62 | 25.7 | 54.485 | 6.46 | 1.12 | 3.025 | 7518.2 | 0.83 | 97.5 | 73 | 1445 | 27.24 | 4886.8 | 2288.4 | 2380.6 | 3448.9 | 1223.6 | 0.64542 | 4.144
2024-12-10 | 3:29 | Data | 0 | 35.654 | 34.783 | 122.128 | 7.64 | 116.441 | 2225.23 | 25.71 | 54.394 | 6.46 | 1.127 | 3.038 | 7509.16 | 0.918 | 97.6 | 72.9 | 1446 | 27.24 | 4881 | 2294.3 | 2351.2 | 3434.1 | 1223.6 | 0.65013 | 4.165
2024-12-10 | 3:29 | Data | 0 | 35.687 | 34.621 | 122.128 | 7.64 | 116.441 | 2220.72 | 25.72 | 54.033 | 6.47 | 1.129 | 3.053 | 7509.16 | 0.918 | 97.6 | 73 | 1443 | 27.06 | 4881 | 2295.1 | 2356.1 | 3442 | 1223.6 | 0.64835 | 4.183
2024-12-10 | 3:29 | Data | 0 | 35.6 | 34.594 | 122.083 | 7.64 | 116.441 | 2224.33 | 25.71 | 54.485 | 6.47 | 1.13 | 3.046 | 7504.64 | 0.878 | 97.6 | 72.9 | 1446 | 27.2 | 4878 | 2303.5 | 2392.3 | 3467.7 | 1223.6 | 0.64681 | 4.176
2024-12-10 | 3:29 | Data | 0 | 35.701 | 34.796 | 122.128 | 7.64 | 116.441 | 2225.23 | 25.71 | 54.214 | 6.47 | 1.124 | 3.035 | 7504.64 | 0.925 | 97.6 | 73 | 1446 | 27.2 | 4878 | 2300.8 | 2391 | 3463.5 | 1223.6 | 0.64781 | 4.16
2024-12-10 | 3:29 | Data | 0 | 35.586 | 34.567 | 122.083 | 7.64 | 116.396 | 2223.43 | 25.71 | 54.575 | 6.47 | 1.131 | 3.027 | 7518.2 | 0.803 | 97.6 | 72.8 | 1447 | 27.24 | 4886.8 | 2302.5 | 2408.9 | 3478.6 | 1223.6 | 0.64463 | 4.159
2024-12-10 | 3:29 | Data | 0 | 35.701 | 34.594 | 122.083 | 7.64 | 116.396 | 2230.66 | 25.71 | 54.304 | 6.47 | 1.131 | 3.03 | 7518.2 | 0.918 | 97.6 | 72.8 | 1450 | 27.15 | 4886.8 | 2289.2 | 2421.5 | 3471.4 | 1223.6 | 0.63889 | 4.16
2024-12-10 | 3:30 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.396 | 2227.04 | 25.71 | 54.214 | 6.46 | 1.13 | 3.03 | 7518.2 | 0.918 | 97.6 | 72.8 | 1448 | 27.11 | 4886.8 | 2313.3 | 2435.2 | 3499.9 | 1223.6 | 0.64272 | 4.16
2024-12-10 | 3:30 | Data | 0 | 35.586 | 34.789 | 122.128 | 7.64 | 116.396 | 2232.47 | 25.71 | 54.304 | 6.46 | 1.128 | 3.023 | 7504.64 | 0.911 | 97.6 | 72.8 | 1451 | 27.15 | 4878 | 2312.6 | 2403.3 | 3469.5 | 1223.6 | 0.64319 | 4.15
2024-12-10 | 3:30 | Data | 0 | 35.485 | 34.769 | 122.037 | 7.64 | 116.351 | 2239.7 | 25.71 | 54.214 | 6.46 | 1.127 | 3.023 | 7500.11 | 0.743 | 97.6 | 72.8 | 1455 | 27.06 | 4875.1 | 2293.5 | 2378.2 | 3452.2 | 1223.6 | 0.64625 | 4.149
2024-12-10 | 3:30 | Data | 0 | 35.708 | 34.58 | 122.037 | 7.64 | 116.396 | 2236.08 | 25.71 | 54.485 | 6.47 | 1.117 | 3.031 | 7929.72 | 0.945 | 97.6 | 73.1 | 1453 | 27.24 | 5154.3 | 2290 | 2374.9 | 3442.3 | 1223.6 | 0.64502 | 4.147
2024-12-10 | 3:30 | Data | 0 | 35.512 | 34.567 | 122.128 | 7.64 | 116.441 | 2239.7 | 25.71 | 54.304 | 6.46 | 1.119 | 3.028 | 7536.29 | 0.891 | 97.6 | 73 | 1455 | 27.15 | 4898.6 | 2304.6 | 2341.6 | 3451 | 1223.6 | 0.65089 | 4.148
2024-12-10 | 3:30 | Data | 0 | 35.316 | 34.546 | 121.992 | 7.64 | 116.306 | 2236.08 | 25.7 | 54.485 | 6.47 | 1.124 | 3.031 | 7527.25 | 0.803 | 97.6 | 72.9 | 1453 | 27.24 | 4892.7 | 2284.6 | 2348.2 | 3422.2 | 1223.6 | 0.64958 | 4.158
2024-12-10 | 3:30 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.351 | 2232.47 | 25.71 | 54.304 | 6.46 | 1.131 | 3.037 | 7518.2 | 0.918 | 97.6 | 72.9 | 1451 | 27.11 | 4886.8 | 2292.7 | 2359.9 | 3442.3 | 1223.6 | 0.64911 | 4.168
2024-12-10 | 3:30 | Data | 0 | 35.282 | 34.762 | 122.037 | 7.64 | 116.351 | 2232.47 | 25.71 | 54.214 | 6.47 | 1.121 | 3.053 | 7536.29 | 0.918 | 97.6 | 73.1 | 1451 | 27.15 | 4898.6 | 2285.4 | 2361.2 | 3433.3 | 1223.6 | 0.65124 | 4.175
2024-12-10 | 3:30 | Data | 0 | 35.485 | 34.783 | 122.128 | 7.64 | 116.441 | 2232.47 | 25.71 | 54.304 | 6.46 | 1.121 | 3.04 | 7549.86 | 0.743 | 97.6 | 73 | 1451 | 27.15 | 4907.4 | 2315.5 | 2363.9 | 3454.7 | 1223.6 | 0.65448 | 4.161
2024-12-10 | 3:30 | Data | 0 | 35.485 | 34.58 | 122.037 | 7.63 | 116.396 | 2235.18 | 25.71 | 54.304 | 6.47 | 1.124 | 3.042 | 7368.97 | 0.905 | 97.6 | 73 | 1453 | 27.15 | 4789.8 | 2274.2 | 2370.8 | 3436 | 1223.6 | 0.64332 | 4.166
2024-12-10 | 3:30 | Data | 0 | 35.471 | 34.567 | 122.037 | 7.64 | 116.441 | 2235.18 | 25.71 | 54.575 | 6.46 | 1.12 | 3.031 | 7337.31 | 0.918 | 97.6 | 73 | 1453 | 27.29 | 4769.3 | 2317.2 | 2415.1 | 3491.5 | 1223.6 | 0.64532 | 4.152
2024-12-10 | 3:30 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.396 | 2236.08 | 25.71 | 54.214 | 6.47 | 1.126 | 3.041 | 7337.31 | 0.911 | 97.6 | 73 | 1453 | 27.11 | 4769.3 | 2296.1 | 2419.5 | 3477.5 | 1223.6 | 0.64315 | 4.166
2024-12-10 | 3:30 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.396 | 2232.47 | 25.71 | 54.214 | 6.47 | 1.121 | 3.05 | 7554.38 | 0.918 | 97.6 | 73.1 | 1451 | 27.15 | 4910.3 | 2296.3 | 2384.7 | 3455.5 | 1223.6 | 0.64941 | 4.17
2024-12-10 | 3:30 | Data | 0 | 35.485 | 34.567 | 122.128 | 7.64 | 116.396 | 2236.08 | 25.71 | 54.304 | 6.47 | 1.126 | 3.038 | 7567.95 | 0.918 | 97.6 | 73 | 1453 | 27.11 | 4919.2 | 2297.2 | 2340.3 | 3432.4 | 1223.6 | 0.65324 | 4.164
2024-12-10 | 3:30 | Data | 0 | 35.37 | 34.567 | 122.083 | 7.64 | 116.396 | 2238.79 | 25.71 | 54.214 | 6.47 | 1.126 | 3.045 | 7563.42 | 0.749 | 97.6 | 73 | 1455 | 27.11 | 4916.2 | 2299.5 | 2345 | 3436 | 1223.6 | 0.65236 | 4.171
2024-12-10 | 3:30 | Data | 0 | 35.687 | 34.567 | 122.218 | 7.64 | 116.487 | 2241.5 | 25.71 | 54.033 | 6.47 | 1.129 | 3.05 | 7558.9 | 0.959 | 97.6 | 73 | 1458 | 27.02 | 4913.3 | 2297.5 | 2324.9 | 3419.1 | 1223.6 | 0.65482 | 4.178
2024-12-10 | 3:31 | Data | 0 | 35.701 | 34.621 | 122.083 | 7.64 | 116.441 | 2241.5 | 25.7 | 54.575 | 6.47 | 1.121 | 3.041 | 7558.9 | 0.972 | 97.6 | 73.1 | 1457 | 27.29 | 4913.3 | 2277.5 | 2334.6 | 3414.2 | 1223.6 | 0.65156 | 4.161
2024-12-10 | 3:31 | Data | 0 | 35.491 | 34.796 | 122.218 | 7.64 | 116.532 | 2238.79 | 25.71 | 54.304 | 6.47 | 1.122 | 3.042 | 7549.86 | 0.81 | 97.6 | 73.1 | 1455 | 27.15 | 4907.4 | 2297 | 2362 | 3440.3 | 1223.6 | 0.65051 | 4.163
2024-12-10 | 3:31 | Data | 0 | 35.491 | 34.567 | 122.083 | 7.64 | 116.441 | 2128.52 | 25.71 | 54.575 | 6.47 | 1.138 | 3.028 | 7554.38 | 0.918 | 97.4 | 72.7 | 1384 | 27.29 | 4910.3 | 2306.9 | 2360.7 | 3448.3 | 1223.6 | 0.64943 | 4.165
2024-12-10 | 3:31 | Data | 0 | 35.701 | 34.573 | 122.128 | 7.64 | 116.441 | 2229.75 | 25.72 | 54.485 | 6.46 | 1.136 | 3.03 | 7563.42 | 0.972 | 97.6 | 72.7 | 1449 | 27.29 | 4916.2 | 2295.1 | 2374.8 | 3457.5 | 1223.6 | 0.64552 | 4.166
2024-12-10 | 3:31 | Data | 0 | 35.498 | 34.627 | 121.992 | 7.64 | 116.441 | 2235.18 | 25.71 | 54.214 | 6.47 | 1.13 | 3.035 | 7563.42 | 0.803 | 97.6 | 72.9 | 1452 | 27.15 | 4916.2 | 2305.6 | 2408.8 | 3475.7 | 1223.6 | 0.64459 | 4.164
2024-12-10 | 3:31 | Data | 0 | 35.883 | 34.627 | 122.173 | 7.64 | 116.441 | 2229.75 | 25.71 | 54.214 | 6.47 | 1.128 | 3.042 | 7563.42 | 1.053 | 97.6 | 73 | 1450 | 27.11 | 4916.2 | 2295.2 | 2402.3 | 3472.5 | 1223.6 | 0.64477 | 4.17
2024-12-10 | 3:31 | Data | 0 | 35.485 | 34.742 | 122.083 | 7.64 | 116.351 | 2233.37 | 25.71 | 54.304 | 6.47 | 1.127 | 3.037 | 7576.99 | 0.918 | 97.6 | 72.9 | 1452 | 27.11 | 4925 | 2273.3 | 2371.9 | 3435.4 | 1223.6 | 0.64346 | 4.164
2024-12-10 | 3:31 | Data | 0 | 35.262 | 34.553 | 122.037 | 7.64 | 116.351 | 2227.95 | 25.71 | 54.214 | 6.47 | 1.131 | 3.05 | 7563.42 | 0.884 | 97.6 | 72.9 | 1449 | 27.15 | 4916.2 | 2285 | 2372.4 | 3444 | 1223.6 | 0.6457 | 4.181
2024-12-10 | 3:31 | Data | 0 | 35.485 | 34.573 | 122.128 | 7.64 | 116.441 | 2232.47 | 25.71 | 54.304 | 6.47 | 1.13 | 3.065 | 7576.99 | 0.83 | 97.6 | 73.1 | 1451 | 27.15 | 4925 | 2309.8 | 2379.4 | 3458.4 | 1223.7 | 0.64864 | 4.195
2024-12-10 | 3:31 | Data | 0 | 35.708 | 34.567 | 122.128 | 7.64 | 116.441 | 2233.37 | 25.71 | 54.485 | 6.46 | 1.126 | 3.044 | 7581.51 | 1.013 | 97.6 | 73 | 1451 | 27.24 | 4928 | 2298.2 | 2356.1 | 3440.1 | 1223.7 | 0.64921 | 4.17
2024-12-10 | 3:31 | Data | 0 | 35.708 | 34.58 | 122.128 | 7.64 | 116.396 | 2232.47 | 25.71 | 54.485 | 6.47 | 1.125 | 3.044 | 7586.04 | 0.884 | 97.6 | 73 | 1451 | 27.29 | 4930.9 | 2280.8 | 2350.7 | 3421.3 | 1223.7 | 0.64759 | 4.169
2024-12-10 | 3:31 | Data | 0 | 35.66 | 34.789 | 122.173 | 7.64 | 116.441 | 2233.37 | 25.71 | 54.304 | 6.47 | 1.128 | 3.073 | 7590.56 | 0.911 | 97.6 | 73.1 | 1452 | 27.15 | 4933.9 | 2302.3 | 2364.2 | 3448.5 | 1223.7 | 0.64968 | 4.199
2024-12-10 | 3:31 | Data | 0 | 35.498 | 34.681 | 122.128 | 7.64 | 116.396 | 2232.47 | 25.7 | 54.575 | 6.47 | 1.131 | 3.067 | 7586.04 | 0.918 | 97.6 | 73.1 | 1452 | 27.29 | 4930.9 | 2290 | 2373.7 | 3448.5 | 1223.7 | 0.64645 | 4.199
2024-12-10 | 3:31 | Data | 0 | 35.485 | 34.452 | 122.128 | 7.64 | 116.441 | 2233.37 | 25.71 | 54.304 | 6.46 | 1.129 | 3.048 | 7590.56 | 0.918 | 97.6 | 73 | 1451 | 27.15 | 4933.9 | 2284.4 | 2378.1 | 3455.5 | 1223.7 | 0.64865 | 4.177
2024-12-10 | 3:31 | Data | 0 | 35.539 | 34.742 | 122.173 | 7.64 | 116.487 | 2233.37 | 25.71 | 54.214 | 6.47 | 1.129 | 3.023 | 7590.56 | 0.918 | 97.6 | 72.8 | 1452 | 27.15 | 4933.9 | 2321.5 | 2369.8 | 3459.9 | 1223.7 | 0.64901 | 4.151
2024-12-10 | 3:31 | Data | 0 | 35.491 | 34.681 | 122.173 | 7.64 | 116.441 | 2232.47 | 25.71 | 54.304 | 6.47 | 1.124 | 3.026 | 7590.56 | 0.911 | 97.6 | 72.9 | 1451 | 27.15 | 4933.9 | 2292.7 | 2380.3 | 3450.5 | 1223.7 | 0.64504 | 4.15
2024-12-10 | 3:31 | Data | 0 | 35.687 | 34.796 | 122.128 | 7.64 | 116.441 | 2230.66 | 25.72 | 54.214 | 6.47 | 1.121 | 3.043 | 7581.51 | 0.911 | 97.6 | 73.1 | 1450 | 27.15 | 4928 | 2289.3 | 2379.8 | 3454.1 | 1223.7 | 0.64314 | 4.163
2024-12-10 | 3:31 | Data | 0 | 35.485 | 34.783 | 122.083 | 7.64 | 116.487 | 2229.75 | 25.71 | 54.304 | 6.47 | 1.131 | 3.038 | 7572.47 | 0.743 | 97.6 | 72.9 | 1449 | 27.15 | 4922.1 | 2308.4 | 2369 | 3457.3 | 1223.7 | 0.65162 | 4.169
2024-12-10 | 3:32 | Data | 0 | 35.6 | 34.783 | 122.128 | 7.64 | 116.487 | 2230.66 | 25.71 | 54.304 | 6.47 | 1.121 | 3.022 | 7572.47 | 0.932 | 97.6 | 73 | 1449 | 27.15 | 4922.1 | 2303.1 | 2375 | 3455 | 1223.7 | 0.64752 | 4.143
2024-12-10 | 3:32 | Data | 0 | 35.6 | 34.519 | 122.083 | 7.64 | 116.441 | 2230.66 | 25.71 | 54.214 | 6.47 | 1.117 | 3.027 | 7576.99 | 1.121 | 97.6 | 73 | 1449 | 27.11 | 4925 | 2289.3 | 2335.7 | 3422 | 1223.7 | 0.65139 | 4.143
2024-12-10 | 3:32 | Data | 0 | 35.485 | 34.58 | 122.083 | 7.64 | 116.441 | 2229.75 | 25.71 | 54.214 | 6.47 | 1.125 | 3.042 | 7576.99 | 0.891 | 97.6 | 73 | 1450 | 27.15 | 4925 | 2309 | 2372.9 | 3451.8 | 1223.7 | 0.65192 | 4.167
2024-12-10 | 3:32 | Data | 0 | 35.708 | 34.573 | 122.083 | 7.64 | 116.441 | 2230.66 | 25.71 | 54.124 | 6.47 | 1.131 | 3.04 | 7576.99 | 0.932 | 97.6 | 72.9 | 1450 | 27.11 | 4925 | 2308.5 | 2370.7 | 3450.7 | 1223.7 | 0.65205 | 4.17
2024-12-10 | 3:32 | Data | 0 | 35.512 | 34.567 | 122.037 | 7.64 | 116.396 | 2230.66 | 25.71 | 54.304 | 6.46 | 1.131 | 3.033 | 7576.99 | 0.925 | 97.6 | 72.8 | 1450 | 27.11 | 4925 | 2289.9 | 2357.1 | 3431.2 | 1223.7 | 0.64989 | 4.165
2024-12-10 | 3:32 | Data | 0 | 35.714 | 34.594 | 122.218 | 7.64 | 116.532 | 2229.75 | 25.71 | 54.304 | 6.47 | 1.124 | 3.041 | 7576.99 | 1.033 | 97.6 | 73 | 1449 | 27.11 | 4925 | 1969.4 | 2444.8 | 3198.9 | 1223.7 | 0.61767 | 4.165
2024-12-10 | 3:32 | Data | 0 | 35.714 | 34.6 | 122.173 | 7.64 | 116.487 | 2230.66 | 25.71 | 54.214 | 6.47 | 1.118 | 3.051 | 7563.42 | 0.965 | 97.6 | 73.2 | 1450 | 27.11 | 4916.2 | 1211.6 | 1703.9 | 2108.7 | 1223.7 | 0.57472 | 4.17
2024-12-10 | 3:32 | Data | 0 | 35.708 | 34.681 | 122.173 | 7.64 | 116.487 | 2230.66 | 25.71 | 54.214 | 6.47 | 1.12 | 3.074 | 7563.42 | 0.83 | 97.6 | 73.3 | 1449 | 27.15 | 4916.2 | 1203 | 1684.3 | 2088.8 | 1223.7 | 0.57507 | 4.194
2024-12-10 | 3:32 | Data | 0 | 35.512 | 34.573 | 122.128 | 7.64 | 116.441 | 2230.66 | 25.71 | 54.214 | 6.46 | 1.125 | 3.057 | 7563.42 | 0.918 | 97.6 | 73.1 | 1450 | 27.11 | 4916.2 | 1221.7 | 1697.2 | 2112.2 | 1223.7 | 0.57535 | 4.18
2024-12-10 | 3:32 | Data | 0 | 35.66 | 34.796 | 122.218 | 7.64 | 116.487 | 2227.04 | 25.7 | 54.304 | 6.46 | 1.12 | 3.037 | 7554.38 | 0.918 | 97.6 | 73.1 | 1448 | 27.15 | 4910.3 | 1214.7 | 1696.3 | 2105.1 | 1223.7 | 0.57641 | 4.157
2024-12-10 | 3:32 | Data | 0 | 35.66 | 34.58 | 122.083 | 7.64 | 116.441 | 2227.95 | 25.71 | 54.214 | 6.46 | 1.119 | 3.054 | 7545.34 | 1.067 | 97.6 | 73.2 | 1448 | 27.11 | 4904.5 | 1206.2 | 1720.7 | 2118.6 | 1223.7 | 0.56863 | 4.172
2024-12-10 | 3:32 | Data | 0 | 35.66 | 34.627 | 122.218 | 7.64 | 116.441 | 2218.91 | 25.71 | 54.214 | 6.47 | 1.129 | 3.054 | 7567.95 | 0.884 | 97.6 | 73 | 1442 | 27.15 | 4919.2 | 1199.2 | 1715.6 | 2113.9 | 1223.7 | 0.56488 | 4.183
2024-12-10 | 3:32 | Data | 0 | 35.708 | 34.796 | 122.128 | 7.64 | 116.441 | 2227.04 | 25.72 | 54.304 | 6.47 | 1.122 | 3.055 | 7563.42 | 0.722 | 97.6 | 73.1 | 1448 | 27.15 | 4916.2 | 1218.9 | 1713.1 | 2119.9 | 1223.7 | 0.57269 | 4.178
2024-12-10 | 3:32 | Data | 0 | 35.714 | 34.627 | 122.173 | 7.64 | 116.532 | 2227.04 | 25.71 | 54.304 | 6.47 | 1.121 | 3.045 | 7554.38 | 0.871 | 97.6 | 73.1 | 1448 | 27.15 | 4910.3 | 1212.1 | 1724.6 | 2124.9 | 1223.7 | 0.56882 | 4.167
2024-12-10 | 3:32 | Data | 0 | 35.768 | 34.378 | 122.218 | 7.64 | 116.487 | 2225.23 | 25.71 | 54.304 | 6.47 | 1.131 | 3.022 | 7558.9 | 0.925 | 97.6 | 72.8 | 1446 | 27.11 | 4913.3 | 1213.7 | 1689.9 | 2098.1 | 1223.7 | 0.57551 | 4.152
2024-12-10 | 3:32 | Data | 0 | 35.316 | 34.567 | 122.128 | 7.64 | 116.441 | 2225.23 | 25.71 | 54.214 | 6.46 | 1.127 | 3.029 | 7554.38 | 0.871 | 97.6 | 72.9 | 1447 | 27.11 | 4910.3 | 1210.4 | 1712.9 | 2117.9 | 1223.7 | 0.57105 | 4.156
2024-12-10 | 3:32 | Data | 0 | 35.485 | 34.783 | 122.037 | 7.64 | 116.441 | 2225.23 | 25.71 | 54.304 | 6.46 | 1.124 | 3.035 | 7563.42 | 0.743 | 97.6 | 73 | 1446 | 27.11 | 4916.2 | 1208.8 | 1731 | 2129.4 | 1223.7 | 0.56819 | 4.158
2024-12-10 | 3:32 | Data | 0 | 35.512 | 34.681 | 122.083 | 7.64 | 116.396 | 2218.91 | 25.71 | 54.304 | 6.47 | 1.128 | 3.026 | 7563.42 | 0.925 | 97.6 | 72.8 | 1442 | 27.11 | 4916.2 | 1221.5 | 1726.3 | 2134.2 | 1223.7 | 0.57331 | 4.155
2024-12-10 | 3:33 | Data | 0 | 35.491 | 34.769 | 122.128 | 7.64 | 116.396 | 2222.52 | 25.71 | 53.943 | 6.46 | 1.119 | 3.037 | 7549.86 | 0.743 | 97.6 | 73.1 | 1445 | 27.02 | 4907.4 | 1204.8 | 1719.4 | 2118.1 | 1223.7 | 0.56794 | 4.155
2024-12-10 | 3:33 | Data | 0 | 35.471 | 34.681 | 122.128 | 7.64 | 116.441 | 2222.52 | 25.71 | 54.214 | 6.47 | 1.12 | 3.054 | 7531.77 | 1.026 | 97.6 | 73.2 | 1445 | 27.11 | 4895.6 | 1212.9 | 1727.8 | 2128.5 | 1223.7 | 0.56897 | 4.176
2024-12-10 | 3:33 | Data | 0 | 35.329 | 34.567 | 122.083 | 7.64 | 116.441 | 2222.52 | 25.71 | 54.214 | 6.46 | 1.118 | 3.042 | 7563.42 | 0.722 | 97.6 | 73.1 | 1445 | 27.11 | 4916.2 | 1215.4 | 1710.3 | 2119.1 | 1223.7 | 0.57212 | 4.16
2024-12-10 | 3:33 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.441 | 2222.52 | 25.7 | 54.304 | 6.46 | 1.118 | 3.03 | 7536.29 | 0.918 | 97.6 | 73.1 | 1445 | 27.15 | 4898.6 | 1225.2 | 1728.3 | 2136.4 | 1223.7 | 0.57161 | 4.147
2024-12-10 | 3:33 | Data | 0 | 35.66 | 34.789 | 122.173 | 7.64 | 116.441 | 2225.23 | 25.7 | 54.304 | 6.47 | 1.121 | 3.054 | 7527.25 | 0.918 | 97.6 | 73.1 | 1446 | 27.15 | 4892.7 | 1217.4 | 1734.9 | 2139.8 | 1223.7 | 0.56653 | 4.176
2024-12-10 | 3:33 | Data | 0 | 35.498 | 34.567 | 122.037 | 7.64 | 116.441 | 2225.23 | 25.71 | 54.485 | 6.47 | 1.121 | 3.047 | 7549.86 | 0.918 | 97.6 | 73.1 | 1447 | 27.24 | 4907.4 | 1211.1 | 1716 | 2118.1 | 1223.7 | 0.57034 | 4.168
2024-12-10 | 3:33 | Data | 0 | 35.498 | 34.567 | 122.083 | 7.64 | 116.441 | 2225.23 | 25.71 | 54.304 | 6.47 | 1.125 | 3.05 | 7558.9 | 0.918 | 97.6 | 73.1 | 1446 | 27.15 | 4913.3 | 1203.3 | 1703.3 | 2103.8 | 1223.7 | 0.57093 | 4.175
2024-12-10 | 3:33 | Data | 0 | 35.478 | 34.567 | 122.083 | 7.64 | 116.351 | 2222.52 | 25.69 | 54.214 | 6.47 | 1.122 | 3.045 | 7545.34 | 0.972 | 97.6 | 73.1 | 1445 | 27.11 | 4904.5 | 1224.1 | 1720 | 2129.6 | 1223.7 | 0.57369 | 4.167
2024-12-10 | 3:33 | Data | 0 | 35.708 | 34.58 | 122.037 | 7.64 | 116.396 | 2221.62 | 25.7 | 54.304 | 6.46 | 1.121 | 3.039 | 7549.86 | 1.019 | 97.6 | 73 | 1444 | 27.15 | 4907.4 | 1220.7 | 1713.8 | 2126.8 | 1223.7 | 0.57522 | 4.161
2024-12-10 | 3:33 | Data | 0 | 35.613 | 34.573 | 122.083 | 7.64 | 116.487 | 2223.43 | 25.71 | 54.485 | 6.46 | 1.125 | 3.047 | 7563.42 | 0.945 | 97.5 | 73 | 1445 | 27.29 | 4916.2 | 1202.6 | 1721.2 | 2116.7 | 1223.7 | 0.5702 | 4.171
2024-12-10 | 3:33 | Data | 0 | 35.917 | 34.634 | 122.173 | 7.64 | 116.487 | 2222.52 | 25.69 | 54.304 | 6.46 | 1.128 | 3.056 | 7563.42 | 1.04 | 97.6 | 73.1 | 1445 | 27.15 | 4916.2 | 1217.3 | 1700.4 | 2108.4 | 1223.7 | 0.57684 | 4.184
2024-12-10 | 3:33 | Data | 0 | 35.289 | 34.553 | 122.037 | 7.64 | 116.396 | 2222.52 | 25.7 | 54.394 | 6.47 | 1.12 | 3.041 | 7563.42 | 0.81 | 97.6 | 73.1 | 1445 | 27.24 | 4916.2 | 1219.8 | 1722.2 | 2126.1 | 1223.7 | 0.57294 | 4.161
2024-12-10 | 3:33 | Data | 0 | 35.539 | 34.749 | 122.128 | 7.64 | 116.487 | 2222.52 | 25.7 | 54.214 | 6.46 | 1.126 | 3.026 | 7563.42 | 0.945 | 97.6 | 72.9 | 1445 | 27.11 | 4916.2 | 1199.1 | 1714.9 | 2112 | 1223.7 | 0.56565 | 4.151
2024-12-10 | 3:33 | Data | 0 | 35.485 | 34.567 | 122.173 | 7.64 | 116.441 | 2330.08 | 25.69 | 54.575 | 6.47 | 1.122 | 3.038 | 7567.95 | 0.918 | 97.7 | 73 | 1517 | 27.24 | 4919.2 | 1219.1 | 1744.1 | 2146.8 | 1223.7 | 0.56722 | 4.161
2024-12-10 | 3:33 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.351 | 2241.5 | 25.69 | 54.394 | 6.47 | 1.125 | 3.068 | 7549.86 | 0.918 | 97.6 | 73.2 | 1456 | 27.2 | 4907.4 | 1230.8 | 1736.4 | 2144.1 | 1223.7 | 0.57198 | 4.192
2024-12-10 | 3:33 | Data | 0 | 35.6 | 34.681 | 122.128 | 7.64 | 116.396 | 2227.95 | 25.69 | 54.214 | 6.47 | 1.125 | 3.036 | 7576.99 | 0.911 | 97.6 | 73 | 1448 | 27.15 | 4925 | 1210 | 1733.5 | 2133.8 | 1223.7 | 0.56544 | 4.161
2024-12-10 | 3:33 | Data | 0 | 35.687 | 34.695 | 122.173 | 7.64 | 116.441 | 2227.95 | 25.7 | 54.304 | 6.47 | 1.124 | 3.037 | 7563.42 | 0.952 | 97.6 | 73 | 1448 | 27.15 | 4916.2 | 1212.5 | 1732.9 | 2132.7 | 1223.7 | 0.56574 | 4.162
2024-12-10 | 3:34 | Data | 0 | 35.485 | 34.769 | 122.083 | 7.64 | 116.396 | 2231.56 | 25.69 | 54.575 | 6.47 | 1.121 | 3.054 | 7567.95 | 0.743 | 97.6 | 73.1 | 1450 | 27.29 | 4919.2 | 1210.7 | 1728.3 | 2128.6 | 1223.7 | 0.56651 | 4.175
2024-12-10 | 3:34 | Data | 0 | 35.714 | 34.594 | 122.128 | 7.64 | 116.487 | 2224.33 | 25.7 | 54.304 | 6.47 | 1.12 | 3.03 | 7572.47 | 0.918 | 97.6 | 73 | 1445 | 27.11 | 4922.1 | 1217.2 | 1732.3 | 2130 | 1223.7 | 0.56498 | 4.149
2024-12-10 | 3:34 | Data | 0 | 35.485 | 34.769 | 122.083 | 7.64 | 116.396 | 2227.95 | 25.7 | 54.485 | 6.47 | 1.129 | 3.024 | 7563.42 | 0.803 | 97.6 | 72.8 | 1448 | 27.2 | 4916.2 | 1213.3 | 1680.4 | 2093 | 1223.7 | 0.57781 | 4.153
2024-12-10 | 3:34 | Data | 0 | 35.701 | 34.796 | 122.173 | 7.64 | 116.487 | 2229.75 | 25.69 | 54.304 | 6.47 | 1.136 | 3.047 | 7572.47 | 0.911 | 97.6 | 72.8 | 1449 | 27.2 | 4922.1 | 1220.8 | 1701.8 | 2115.1 | 1223.7 | 0.57768 | 4.183
2024-12-10 | 3:34 | Data | 0 | 35.654 | 34.58 | 122.083 | 7.64 | 116.351 | 2222.52 | 25.71 | 54.485 | 6.46 | 1.128 | 3.042 | 7563.42 | 0.938 | 97.5 | 73 | 1445 | 27.24 | 4916.2 | 1233.1 | 1718.6 | 2131.7 | 1223.7 | 0.57779 | 4.17
2024-12-10 | 3:34 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.396 | 2222.52 | 25.7 | 54.304 | 6.47 | 1.121 | 3.029 | 7563.42 | 0.918 | 97.6 | 73 | 1445 | 27.11 | 4916.2 | 1217.9 | 1702.5 | 2113.4 | 1223.7 | 0.57558 | 4.15
2024-12-10 | 3:34 | Data | 0 | 35.539 | 34.573 | 122.037 | 7.64 | 116.396 | 2224.33 | 25.71 | 54.304 | 6.47 | 1.126 | 3.04 | 7563.42 | 0.803 | 97.6 | 73 | 1446 | 27.15 | 4916.2 | 1206.6 | 1737.6 | 2130.8 | 1223.7 | 0.56553 | 4.166
2024-12-10 | 3:34 | Data | 0 | 35.323 | 34.465 | 121.947 | 7.64 | 116.396 | 2228.85 | 25.7 | 54.214 | 6.47 | 1.122 | 3.043 | 7563.42 | 0.81 | 97.6 | 73.1 | 1448 | 27.15 | 4916.2 | 1208.3 | 1713.4 | 2113.9 | 1223.7 | 0.57 | 4.165
2024-12-10 | 3:34 | Data | 0 | 35.498 | 34.567 | 122.037 | 7.64 | 116.441 | 2225.23 | 25.69 | 54.304 | 6.46 | 1.121 | 3.037 | 7545.34 | 0.918 | 97.6 | 73 | 1446 | 27.15 | 4904.5 | 1229.2 | 1714.7 | 2122.7 | 1223.7 | 0.57592 | 4.158
2024-12-10 | 3:34 | Data | 0 | 35.485 | 34.567 | 122.037 | 7.64 | 116.396 | 2225.23 | 25.69 | 54.304 | 6.47 | 1.116 | 3.025 | 7563.42 | 0.918 | 97.6 | 73 | 1446 | 27.15 | 4916.2 | 1218.2 | 1737.9 | 2138.1 | 1223.7 | 0.56845 | 4.141
2024-12-10 | 3:34 | Data | 0 | 35.478 | 34.567 | 122.037 | 7.64 | 116.396 | 2226.14 | 25.69 | 54.485 | 6.46 | 1.121 | 3.022 | 7558.9 | 0.803 | 97.6 | 72.9 | 1446 | 27.24 | 4913.3 | 1221.8 | 1718.5 | 2128.1 | 1223.7 | 0.57085 | 4.142
2024-12-10 | 3:34 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.441 | 2224.33 | 25.69 | 54.214 | 6.46 | 1.125 | 3.042 | 7563.42 | 0.918 | 97.6 | 73 | 1446 | 27.15 | 4916.2 | 1222.5 | 1728.3 | 2135 | 1223.7 | 0.57013 | 4.167
2024-12-10 | 3:34 | Data | 0 | 35.485 | 34.452 | 122.037 | 7.64 | 116.396 | 2225.23 | 25.7 | 54.304 | 6.47 | 1.124 | 3.046 | 7576.99 | 1.033 | 97.6 | 73 | 1446 | 27.11 | 4925 | 1217 | 1724.8 | 2129.5 | 1223.7 | 0.57007 | 4.17
2024-12-10 | 3:34 | Data | 0 | 35.512 | 34.594 | 122.037 | 7.64 | 116.351 | 2224.33 | 25.69 | 54.665 | 6.46 | 1.126 | 3.043 | 7572.47 | 0.871 | 97.5 | 73 | 1446 | 27.33 | 4922.1 | 1210.3 | 1721.6 | 2120.3 | 1223.7 | 0.57018 | 4.17
2024-12-10 | 3:34 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.351 | 2222.52 | 25.69 | 54.214 | 6.46 | 1.132 | 3.048 | 7549.86 | 0.918 | 97.6 | 72.9 | 1445 | 27.06 | 4907.4 | 1201.6 | 1694.2 | 2099.1 | 1223.7 | 0.5707 | 4.18
2024-12-10 | 3:34 | Data | 0 | 35.512 | 34.567 | 122.037 | 7.64 | 116.441 | 2225.23 | 25.7 | 54.575 | 6.46 | 1.128 | 3.035 | 7558.9 | 0.918 | 97.5 | 72.9 | 1446 | 27.24 | 4913.3 | 1211.2 | 1676.8 | 2088.8 | 1223.7 | 0.57785 | 4.163
2024-12-10 | 3:34 | Data | 0 | 35.377 | 34.567 | 122.128 | 7.64 | 116.441 | 2226.14 | 25.7 | 54.304 | 6.47 | 1.129 | 3.036 | 7576.99 | 0.749 | 97.6 | 72.9 | 1448 | 27.15 | 4925 | 1222.9 | 1707.3 | 2119.7 | 1223.7 | 0.57619 | 4.165
2024-12-10 | 3:34 | Data | 0 | 35.485 | 34.567 | 121.992 | 7.64 | 116.396 | 2225.23 | 25.7 | 54.214 | 6.47 | 1.124 | 3.031 | 7563.42 | 0.918 | 97.6 | 72.9 | 1446 | 27.15 | 4916.2 | 1207.9 | 1719.2 | 2121.9 | 1223.7 | 0.56761 | 4.155
2024-12-10 | 3:35 | Data | 0 | 35.708 | 34.796 | 122.083 | 7.64 | 116.441 | 2222.52 | 25.7 | 54.304 | 6.47 | 1.116 | 3.019 | 7549.86 | 0.918 | 97.6 | 73 | 1444 | 27.15 | 4907.4 | 1237.1 | 1725 | 2139.6 | 1223.7 | 0.57749 | 4.135
2024-12-10 | 3:35 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.396 | 2223.43 | 25.7 | 54.214 | 6.47 | 1.124 | 3.04 | 7545.34 | 0.918 | 97.6 | 73 | 1445 | 27.11 | 4904.5 | 1227 | 1723.6 | 2126.6 | 1223.7 | 0.57469 | 4.163
2024-12-10 | 3:35 | Data | 0 | 35.262 | 34.729 | 122.037 | 7.64 | 116.351 | 2222.52 | 25.71 | 54.485 | 6.46 | 1.128 | 3.036 | 7531.77 | 0.763 | 97.5 | 72.9 | 1445 | 27.24 | 4895.6 | 1207.5 | 1727 | 2130.6 | 1223.7 | 0.56831 | 4.164
2024-12-10 | 3:35 | Data | 0 | 35.282 | 34.789 | 122.083 | 7.64 | 116.396 | 2225.23 | 25.7 | 54.214 | 6.46 | 1.131 | 3.043 | 7545.34 | 0.689 | 97.6 | 72.9 | 1446 | 27.11 | 4904.5 | 1217.3 | 1750.6 | 2150.1 | 1223.7 | 0.56356 | 4.174
2024-12-10 | 3:35 | Data | 0 | 35.66 | 34.567 | 122.128 | 7.64 | 116.441 | 2227.95 | 25.69 | 54.214 | 6.47 | 1.129 | 3.045 | 7536.29 | 0.959 | 97.6 | 73 | 1448 | 27.11 | 4898.6 | 1236.7 | 1745.7 | 2155.9 | 1223.7 | 0.57186 | 4.173
2024-12-10 | 3:35 | Data | 0 | 35.262 | 34.567 | 122.083 | 7.64 | 116.441 | 2227.95 | 25.71 | 54.485 | 6.47 | 1.126 | 3.048 | 7554.38 | 0.689 | 97.5 | 73 | 1448 | 27.29 | 4910.3 | 1212.7 | 1699 | 2107.6 | 1223.7 | 0.57391 | 4.173
2024-12-10 | 3:35 | Data | 0 | 35.458 | 34.567 | 122.037 | 7.64 | 116.351 | 2222.52 | 25.71 | 54.485 | 6.47 | 1.122 | 3.043 | 7558.9 | 1.026 | 97.5 | 73.1 | 1445 | 27.24 | 4913.3 | 1219.7 | 1699.2 | 2109.7 | 1223.7 | 0.57671 | 4.165
2024-12-10 | 3:35 | Data | 0 | 35.37 | 34.567 | 122.037 | 7.64 | 116.396 | 2225.23 | 25.69 | 54.575 | 6.46 | 1.129 | 3.046 | 7558.9 | 0.716 | 97.6 | 72.9 | 1446 | 27.29 | 4913.3 | 1220.3 | 1699.7 | 2109.4 | 1223.7 | 0.57763 | 4.176
2024-12-10 | 3:35 | Data | 0 | 35.458 | 34.56 | 122.173 | 7.64 | 116.441 | 2225.23 | 25.71 | 54.485 | 6.47 | 1.131 | 3.02 | 7563.42 | 1.04 | 97.5 | 72.8 | 1446 | 27.29 | 4916.2 | 1219.5 | 1705 | 2113.3 | 1223.7 | 0.5757 | 4.151
2024-12-10 | 3:35 | Data | 0 | 35.485 | 34.567 | 122.083 | 7.64 | 116.351 | 2221.62 | 25.69 | 54.214 | 6.47 | 1.119 | 3.051 | 7549.86 | 0.918 | 97.6 | 73.2 | 1445 | 27.11 | 4907.4 | 1211.8 | 1708.7 | 2113.6 | 1223.7 | 0.57232 | 4.17
2024-12-10 | 3:35 | Data | 0 | 35.525 | 34.567 | 122.037 | 7.64 | 116.396 | 2218.91 | 25.71 | 54.304 | 6.47 | 1.12 | 3.059 | 7549.86 | 0.925 | 97.6 | 73.2 | 1442 | 27.15 | 4907.4 | 1201.8 | 1687.1 | 2090.3 | 1223.7 | 0.57407 | 4.18
2024-12-10 | 3:35 | Data | 0 | 35.485 | 34.783 | 122.037 | 7.64 | 116.351 | 2218.91 | 25.71 | 54.214 | 6.47 | 1.129 | 3.046 | 7536.29 | 0.83 | 97.6 | 73 | 1443 | 27.11 | 4898.6 | 1222.3 | 1723.8 | 2132.3 | 1223.8 | 0.5728 | 4.175
2024-12-10 | 3:35 | Data | 0 | 35.485 | 34.614 | 122.083 | 7.64 | 116.396 | 2218.91 | 25.71 | 54.304 | 6.47 | 1.126 | 3.029 | 7531.77 | 0.817 | 97.6 | 72.9 | 1442 | 27.15 | 4895.6 | 1205.9 | 1744.3 | 2141.7 | 1223.8 | 0.56167 | 4.154
2024-12-10 | 3:35 | Data | 0 | 35.708 | 34.573 | 122.218 | 7.64 | 116.396 | 2220.72 | 25.71 | 54.304 | 6.47 | 1.129 | 3.02 | 7531.77 | 0.918 | 97.6 | 72.8 | 1442 | 27.15 | 4895.6 | 1216.7 | 1727.4 | 2132.6 | 1223.8 | 0.56975 | 4.149
2024-12-10 | 3:35 | Data | 0 | 35.485 | 34.567 | 121.947 | 7.64 | 116.215 | 2217.1 | 25.71 | 54.304 | 6.46 | 1.121 | 3.037 | 7531.77 | 0.743 | 97.5 | 73 | 1441 | 27.15 | 4895.6 | 1209 | 1748.2 | 2141.8 | 1223.8 | 0.56271 | 4.159
2024-12-10 | 3:35 | Data | 0 | 35.485 | 34.627 | 122.083 | 7.64 | 116.441 | 2222.52 | 25.7 | 54.214 | 6.47 | 1.119 | 3.041 | 7527.25 | 0.918 | 97.6 | 73.1 | 1445 | 27.15 | 4892.7 | 1216.8 | 1726.2 | 2129.3 | 1223.8 | 0.57108 | 4.159
2024-12-10 | 3:35 | Data | 0 | 35.485 | 34.526 | 122.037 | 7.64 | 116.351 | 2224.33 | 25.71 | 54.214 | 6.46 | 1.121 | 3.035 | 7531.77 | 0.803 | 97.6 | 73 | 1446 | 27.11 | 4895.6 | 1218.3 | 1723.1 | 2128 | 1223.8 | 0.57189 | 4.157
2024-12-10 | 3:35 | Data | 0 | 35.37 | 34.567 | 121.902 | 7.64 | 116.306 | 2222.52 | 25.69 | 54.304 | 6.46 | 1.121 | 3.025 | 7531.77 | 0.905 | 97.6 | 73 | 1445 | 27.15 | 4895.6 | 1229.4 | 1695.6 | 2111.2 | 1223.8 | 0.57909 | 4.145
2024-12-10 | 3:36 | Data | 0 | 35.478 | 34.567 | 121.992 | 7.64 | 116.351 | 2224.33 | 25.69 | 54.214 | 6.47 | 1.12 | 3.019 | 7531.77 | 0.918 | 97.6 | 72.9 | 1445 | 27.11 | 4895.6 | 1219.8 | 1701.6 | 2112.4 | 1223.8 | 0.57576 | 4.139
2024-12-10 | 3:36 | Data | 0 | 35.37 | 34.553 | 122.037 | 7.64 | 116.351 | 2226.14 | 25.69 | 54.214 | 6.47 | 1.121 | 3.033 | 7563.42 | 0.824 | 97.6 | 73 | 1446 | 27.15 | 4916.2 | 1218.6 | 1687.5 | 2100.7 | 1223.8 | 0.57908 | 4.153
2024-12-10 | 3:36 | Data | 0 | 35.708 | 34.567 | 122.037 | 7.64 | 116.396 | 2226.14 | 25.7 | 54.304 | 6.47 | 1.132 | 3.05 | 7563.42 | 0.83 | 97.6 | 72.9 | 1448 | 27.11 | 4916.2 | 1226.6 | 1689.8 | 2105.9 | 1223.8 | 0.58228 | 4.182
2024-12-10 | 3:36 | Data | 0 | 35.539 | 34.594 | 122.128 | 7.64 | 116.396 | 2227.95 | 25.71 | 54.394 | 6.47 | 1.119 | 3.05 | 7563.42 | 0.898 | 97.6 | 73.2 | 1448 | 27.15 | 4916.2 | 1197.7 | 1705.7 | 2100.9 | 1223.8 | 0.57719 | 4.167
2024-12-10 | 3:36 | Data | 0 | 35.309 | 34.351 | 121.947 | 7.64 | 116.306 | 2227.95 | 25.69 | 54.214 | 6.47 | 1.122 | 3.026 | 7563.42 | 0.898 | 97.6 | 72.9 | 1448 | 27.15 | 4916.2 | 1214.5 | 1695.1 | 2104.1 | 1223.8 | 0.57674 | 4.149
2024-12-10 | 3:36 | Data | 0 | 35.167 | 34.222 | 124.751 | 7.64 | 118.701 | 2227.04 | 25.7 | 54.214 | 6.47 | 1.125 | 3.03 | 7558.9 | 0.898 | 97.6 | 72.9 | 1448 | 27.11 | 4913.3 | 1206.6 | 1708.3 | 2110.6 | 1223.8 | 0.56984 | 4.155
2024-12-10 | 3:36 | Data | 0 | 34.756 | 33.594 | 135.969 | 7.64 | 129.141 | 2225.23 | 25.7 | 54.485 | 6.47 | 1.137 | 3.144 | 7567.95 | 1.33 | 97.5 | 73.4 | 1446 | 27.24 | 4919.2 | 1312.7 | 1784 | 2232.3 | 1223.8 | 0.58516 | 4.279
2024-12-10 | 3:36 | Data | 0 | 34.56 | 33.21 | 146.599 | 7.64 | 138.857 | 2222.52 | 25.69 | 54.846 | 6.47 | 1.181 | 3.391 | 7563.42 | 1.242 | 97.5 | 74.2 | 1445 | 27.38 | 4916.2 | 1405 | 1882.5 | 2364.6 | 1223.8 | 0.59212 | 4.572
2024-12-10 | 3:36 | Data | 0 | 33.871 | 32.393 | 155.374 | 7.64 | 146.992 | 2223.43 | 25.69 | 54.846 | 6.47 | 1.215 | 3.635 | 7563.42 | 1.58 | 97.5 | 74.9 | 1445 | 27.42 | 4916.2 | 1489.7 | 1945.4 | 2462.1 | 1223.8 | 0.60616 | 4.848
2024-12-10 | 3:36 | Data | 0 | 33.642 | 32.028 | 162.701 | 7.64 | 153.726 | 2222.52 | 25.69 | 54.575 | 6.47 | 1.242 | 3.826 | 7554.38 | 1.614 | 97.5 | 75.5 | 1445 | 27.29 | 4910.3 | 1538.1 | 1973.9 | 2518.2 | 1223.8 | 0.60795 | 5.068
2024-12-10 | 3:36 | Data | 0 | 33.851 | 32.082 | 168.943 | 7.64 | 159.466 | 2220.72 | 25.69 | 53.672 | 6.46 | 1.255 | 4.002 | 7518.2 | 1.728 | 97.6 | 76.1 | 1442 | 26.84 | 4886.8 | 1619.5 | 2044.6 | 2608.1 | 1223.8 | 0.61724 | 5.257
2024-12-10 | 3:36 | Data | 0 | 33.216 | 31.684 | 173.783 | 7.64 | 163.94 | 2218 | 25.7 | 52.679 | 6.45 | 1.282 | 4.124 | 7545.34 | 1.674 | 97.6 | 76.3 | 1442 | 26.34 | 4904.5 | 1650.9 | 2095.1 | 2680.4 | 1223.8 | 0.61589 | 5.406
2024-12-10 | 3:36 | Data | 0 | 33.405 | 31.366 | 177.764 | 7.64 | 167.601 | 2218.91 | 25.68 | 51.144 | 6.44 | 1.304 | 4.242 | 7595.08 | 1.816 | 97.7 | 76.5 | 1442 | 25.57 | 4936.8 | 1700.9 | 2098.6 | 2713.3 | 1223.8 | 0.62468 | 5.547
2024-12-10 | 3:36 | Data | 0 | 32.953 | 31.009 | 180.885 | 7.64 | 170.583 | 2216.2 | 25.64 | 49.7 | 6.42 | 1.312 | 4.333 | 7644.82 | 1.782 | 97.8 | 76.7 | 1441 | 24.85 | 4969.1 | 2787.6 | 2723 | 4021.1 | 1223.8 | 0.67555 | 5.646
2024-12-10 | 3:36 | Data | 0 | 33.176 | 31.333 | 183.508 | 7.64 | 172.843 | 2217.1 | 25.64 | 48.255 | 6.41 | 1.32 | 4.392 | 7708.14 | 1.863 | 97.8 | 76.9 | 1441 | 24.08 | 5010.3 | 2809.3 | 2759.7 | 4062.8 | 1223.8 | 0.67329 | 5.714
2024-12-10 | 3:36 | Data | 0 | 32.723 | 31.191 | 185.589 | 7.64 | 174.741 | 2217.1 | 25.62 | 47.082 | 6.4 | 1.34 | 4.447 | 7771.45 | 1.735 | 97.9 | 76.9 | 1441 | 23.54 | 5051.4 | 2846.8 | 2802.2 | 4114.2 | 1223.8 | 0.6737 | 5.787
2024-12-10 | 3:36 | Data | 0 | 32.737 | 31.245 | 187.172 | 7.64 | 176.233 | 2216.2 | 25.63 | 46.269 | 6.39 | 1.338 | 4.472 | 7839.28 | 1.742 | 97.9 | 77 | 1441 | 23.13 | 5095.5 | 2870.6 | 2793 | 4123.3 | 1223.8 | 0.67867 | 5.809
2024-12-10 | 3:36 | Data | 0 | 32.723 | 30.705 | 188.348 | 7.64 | 177.453 | 2216.2 | 25.62 | 45.457 | 6.38 | 1.351 | 4.509 | 7907.11 | 1.971 | 97.9 | 76.9 | 1441 | 22.68 | 5139.6 | 2885 | 2842.5 | 4172.7 | 1223.8 | 0.67438 | 5.861
2024-12-10 | 3:37 | Data | 0 | 32.723 | 30.678 | 189.253 | 7.64 | 178.221 | 2216.2 | 25.61 | 44.644 | 6.37 | 1.349 | 4.557 | 7956.86 | 2.019 | 98 | 77.2 | 1441 | 22.28 | 5172 | 2889.3 | 2831.7 | 4169 | 1223.8 | 0.67353 | 5.906
2024-12-10 | 3:37 | Data | 0 | 32.514 | 30.651 | 189.479 | 7.64 | 178.492 | 2216.2 | 25.61 | 44.102 | 6.36 | 1.349 | 4.546 | 8002.08 | 1.85 | 98 | 77.1 | 1441 | 22.05 | 5201.4 | 2890 | 2821.5 | 4156.5 | 1223.8 | 0.67971 | 5.895
2024-12-10 | 3:37 | Data | 0 | 32.723 | 30.766 | 190.384 | 7.64 | 179.215 | 2211.68 | 25.61 | 43.47 | 6.35 | 1.356 | 4.559 | 8056.35 | 2.066 | 98 | 77.1 | 1438 | 21.74 | 5236.6 | 2921.6 | 2861.3 | 4205.3 | 1223.8 | 0.67799 | 5.914
2024-12-10 | 3:37 | Data | 0 | 32.426 | 30.766 | 190.474 | 7.64 | 179.351 | 2212.58 | 25.61 | 43.2 | 6.35 | 1.353 | 4.56 | 8097.05 | 1.796 | 98 | 77.1 | 1438 | 21.6 | 5263.1 | 2920.3 | 2839.1 | 4179.7 | 1223.8 | 0.67993 | 5.913
2024-12-10 | 3:37 | Data | 0 | 32.737 | 30.651 | 190.384 | 7.64 | 179.306 | 2216.2 | 25.61 | 42.838 | 6.35 | 1.358 | 4.571 | 8133.23 | 1.951 | 98.1 | 77.1 | 1441 | 21.42 | 5286.6 | 2915.2 | 2848.2 | 4191.4 | 1223.8 | 0.67813 | 5.929
2024-12-10 | 3:37 | Data | 0 | 32.75 | 30.664 | 190.384 | 7.64 | 179.396 | 2217.1 | 25.6 | 42.658 | 6.35 | 1.359 | 4.581 | 8182.97 | 2.025 | 98.1 | 77.1 | 1441 | 21.33 | 5318.9 | 2891.2 | 2883.1 | 4204.6 | 1223.8 | 0.66972 | 5.941
2024-12-10 | 3:37 | Data | 0 | 32.879 | 30.982 | 190.655 | 7.64 | 179.487 | 2217.1 | 25.6 | 42.387 | 6.34 | 1.353 | 4.554 | 8219.15 | 1.877 | 98.1 | 77.1 | 1441 | 21.19 | 5342.4 | 2912.2 | 2894.3 | 4219.8 | 1223.8 | 0.67594 | 5.907
2024-12-10 | 3:37 | Data | 0 | 32.717 | 30.752 | 190.384 | 7.64 | 179.441 | 2217.1 | 25.6 | 42.477 | 6.34 | 1.353 | 4.571 | 8951.75 | 2.106 | 98.1 | 77.2 | 1441 | 21.19 | 5818.6 | 2912.2 | 2875.3 | 4208.4 | 1223.8 | 0.67379 | 5.924
2024-12-10 | 3:37 | Data | 0 | 32.683 | 30.853 | 190.474 | 7.64 | 179.396 | 2218.91 | 25.6 | 42.387 | 6.34 | 1.353 | 4.581 | 8291.5 | 1.951 | 98.1 | 77.2 | 1442 | 21.19 | 5389.5 | 2919.2 | 2867 | 4205.9 | 1223.8 | 0.67127 | 5.934
2024-12-10 | 3:37 | Data | 0 | 32.568 | 30.678 | 190.474 | 7.64 | 179.351 | 2218.91 | 25.59 | 42.297 | 6.34 | 1.356 | 4.571 | 8305.07 | 1.789 | 98.1 | 77.1 | 1442 | 21.19 | 5398.3 | 2921.2 | 2845.3 | 4189.5 | 1223.8 | 0.68077 | 5.926
2024-12-10 | 3:37 | Data | 0 | 32.501 | 30.651 | 190.338 | 7.64 | 179.351 | 2221.62 | 25.6 | 42.297 | 6.34 | 1.346 | 4.565 | 8350.29 | 1.843 | 98.1 | 77.2 | 1444 | 21.19 | 5427.7 | 2917.9 | 2816.4 | 4171 | 1223.8 | 0.68225 | 5.911
2024-12-10 | 3:37 | Data | 0 | 32.723 | 30.759 | 190.429 | 7.64 | 179.487 | 2222.52 | 25.6 | 42.387 | 6.34 | 1.358 | 4.55 | 8372.9 | 1.85 | 98.1 | 77 | 1445 | 21.24 | 5442.4 | 2910.1 | 2802.5 | 4158 | 1223.8 | 0.68272 | 5.909
2024-12-10 | 3:37 | Data | 0 | 32.723 | 30.718 | 190.474 | 7.64 | 179.487 | 2225.23 | 25.59 | 42.387 | 6.34 | 1.359 | 4.563 | 8400.04 | 1.762 | 98.1 | 77 | 1446 | 21.19 | 5460 | 2893.2 | 2831.2 | 4165.8 | 1223.8 | 0.67851 | 5.922
2024-12-10 | 3:37 | Data | 0 | 32.474 | 30.691 | 190.61 | 7.65 | 179.577 | 2228.85 | 25.6 | 42.568 | 6.34 | 1.358 | 4.561 | 8440.74 | 1.87 | 98.1 | 77.1 | 1448 | 21.28 | 5486.5 | 2902.6 | 2842.5 | 4179.4 | 1223.8 | 0.67763 | 5.919
2024-12-10 | 3:37 | Data | 0 | 32.777 | 30.448 | 190.474 | 7.64 | 179.532 | 2229.75 | 25.6 | 42.387 | 6.34 | 1.366 | 4.569 | 8445.26 | 2.073 | 98.1 | 77 | 1449 | 21.19 | 5489.4 | 2897.3 | 2880.6 | 4203.4 | 1223.8 | 0.67026 | 5.934
2024-12-10 | 3:37 | Data | 0 | 32.534 | 30.597 | 190.519 | 7.64 | 179.532 | 2228.85 | 25.61 | 42.658 | 6.34 | 1.362 | 4.577 | 8472.39 | 1.965 | 98.1 | 77.1 | 1449 | 21.33 | 5507.1 | 2899.4 | 2869.3 | 4198.1 | 1223.8 | 0.67388 | 5.939
2024-12-10 | 3:37 | Data | 0 | 32.96 | 30.887 | 190.7 | 7.64 | 179.622 | 2228.85 | 25.6 | 42.658 | 6.34 | 1.369 | 4.563 | 8490.48 | 1.857 | 98.1 | 76.9 | 1449 | 21.28 | 5518.8 | 2914.1 | 2875.9 | 4208.8 | 1223.8 | 0.67418 | 5.932
2024-12-10 | 3:38 | Data | 0 | 32.696 | 30.651 | 190.519 | 7.64 | 179.532 | 2231.56 | 25.6 | 42.658 | 6.34 | 1.359 | 4.547 | 8495 | 2.073 | 98.1 | 77 | 1450 | 21.33 | 5521.8 | 2893.6 | 2890.7 | 4206.6 | 1223.8 | 0.67021 | 5.907
2024-12-10 | 3:38 | Data | 0 | 32.96 | 30.88 | 191.605 | 7.64 | 180.481 | 2229.75 | 25.61 | 42.658 | 6.34 | 1.36 | 4.55 | 8526.66 | 2.073 | 98.1 | 77 | 1449 | 21.37 | 5542.3 | 2908.6 | 2885.2 | 4211.1 | 1223.8 | 0.67367 | 5.911
2024-12-10 | 3:38 | Data | 0 | 32.696 | 30.658 | 191.56 | 7.64 | 180.526 | 2229.75 | 25.6 | 42.658 | 6.34 | 1.357 | 4.593 | 8535.7 | 2.073 | 98.1 | 77.2 | 1449 | 21.33 | 5548.2 | 2919 | 2882.7 | 4220.5 | 1223.8 | 0.67426 | 5.95
2024-12-10 | 3:38 | Data | 0 | 32.669 | 30.671 | 191.469 | 7.64 | 180.436 | 2230.66 | 25.61 | 42.658 | 6.34 | 1.361 | 4.616 | 8526.66 | 1.978 | 98.1 | 77.2 | 1450 | 21.33 | 5542.3 | 2912.5 | 2858.3 | 4207.7 | 1223.8 | 0.67653 | 5.977
2024-12-10 | 3:38 | Data | 0 | 32.521 | 30.543 | 191.469 | 7.64 | 180.436 | 2227.04 | 25.61 | 42.658 | 6.34 | 1.358 | 4.599 | 8535.7 | 2.248 | 98.1 | 77.2 | 1448 | 21.28 | 5548.2 | 2907.2 | 2848.4 | 4187 | 1223.8 | 0.67678 | 5.958
2024-12-10 | 3:38 | Data | 0 | 32.723 | 30.651 | 191.56 | 7.64 | 180.39 | 2229.75 | 25.61 | 42.658 | 6.34 | 1.351 | 4.569 | 8558.31 | 2.073 | 98.1 | 77.2 | 1449 | 21.33 | 5562.9 | 2906.4 | 2828.4 | 4170.2 | 1223.9 | 0.67985 | 5.921
2024-12-10 | 3:38 | Data | 0 | 32.582 | 30.597 | 191.786 | 7.64 | 180.662 | 2230.66 | 25.6 | 42.387 | 6.34 | 1.345 | 4.545 | 8567.36 | 1.971 | 98.1 | 77.2 | 1450 | 21.24 | 5568.8 | 2914.3 | 2815.3 | 4165.7 | 1223.9 | 0.67973 | 5.888
2024-12-10 | 3:38 | Data | 0 | 32.609 | 30.651 | 192.012 | 7.64 | 180.707 | 2230.66 | 25.61 | 42.658 | 6.34 | 1.347 | 4.595 | 8594.49 | 1.857 | 98.1 | 77.3 | 1450 | 21.33 | 5586.4 | 2904.6 | 2832.3 | 4175.3 | 1223.9 | 0.67842 | 5.941
2024-12-10 | 3:38 | Data | 0 | 32.514 | 30.442 | 191.967 | 7.64 | 180.933 | 2229.75 | 25.61 | 42.658 | 6.34 | 1.345 | 4.619 | 8603.54 | 2.025 | 98.1 | 77.4 | 1449 | 21.33 | 5592.3 | 2940.3 | 2842.4 | 4206.5 | 1223.9 | 0.68167 | 5.963
2024-12-10 | 3:38 | Data | 0 | 32.669 | 30.651 | 192.012 | 7.64 | 180.797 | 2230.66 | 25.61 | 42.658 | 6.34 | 1.351 | 4.616 | 8608.06 | 2.046 | 98.1 | 77.4 | 1450 | 21.33 | 5595.2 | 2906.9 | 2880.8 | 4209.9 | 1223.9 | 0.67522 | 5.967
2024-12-10 | 3:38 | Data | 0 | 33.048 | 30.685 | 192.012 | 7.64 | 180.933 | 2229.75 | 25.61 | 42.568 | 6.34 | 1.351 | 4.582 | 8585.45 | 2.086 | 98.1 | 77.3 | 1449 | 21.33 | 5580.5 | 2925.9 | 2853.7 | 4202.2 | 1223.9 | 0.67912 | 5.932
2024-12-10 | 3:38 | Data | 0 | 32.494 | 30.759 | 192.012 | 7.64 | 180.842 | 2229.75 | 25.61 | 42.658 | 6.34 | 1.351 | 4.564 | 8372.9 | 1.87 | 98.1 | 77.2 | 1449 | 21.33 | 5442.4 | 2923.6 | 2887.3 | 4223.1 | 1223.9 | 0.67497 | 5.915
2024-12-10 | 3:38 | Data | 0 | 32.602 | 30.442 | 191.967 | 7.64 | 180.797 | 2230.66 | 25.61 | 42.929 | 6.34 | 1.353 | 4.578 | 8372.9 | 2.052 | 98.1 | 77.2 | 1449 | 21.42 | 5442.4 | 2917.9 | 2890 | 4222.4 | 1223.9 | 0.66977 | 5.931
2024-12-10 | 3:38 | Data | 0 | 32.568 | 30.637 | 192.102 | 7.64 | 180.933 | 2230.66 | 25.61 | 42.658 | 6.34 | 1.358 | 4.586 | 8372.9 | 1.897 | 98.1 | 77.2 | 1449 | 21.33 | 5442.4 | 2925.7 | 2898.6 | 4233.6 | 1223.9 | 0.67482 | 5.943
2024-12-10 | 3:38 | Data | 0 | 32.494 | 30.435 | 192.102 | 7.65 | 180.797 | 2233.37 | 25.61 | 42.568 | 6.34 | 1.362 | 4.588 | 8390.99 | 2.059 | 98.1 | 77.1 | 1452 | 21.33 | 5454.1 | 2909.6 | 2891.1 | 4215.4 | 1223.9 | 0.67303 | 5.95
2024-12-10 | 3:38 | Data | 0 | 32.831 | 30.651 | 192.012 | 7.64 | 180.978 | 2232.47 | 25.61 | 42.658 | 6.35 | 1.363 | 4.569 | 8599.01 | 2.093 | 98.1 | 77 | 1451 | 21.33 | 5589.4 | 2910 | 2861.5 | 4206.3 | 1223.9 | 0.67297 | 5.932
2024-12-10 | 3:38 | Data | 0 | 32.507 | 30.61 | 192.012 | 7.64 | 180.797 | 2233.37 | 25.61 | 42.658 | 6.34 | 1.359 | 4.585 | 8608.06 | 1.931 | 98.1 | 77.1 | 1451 | 21.33 | 5595.2 | 2921.4 | 2845.1 | 4194.1 | 1223.9 | 0.68067 | 5.943
2024-12-10 | 3:38 | Data | 0 | 32.622 | 30.651 | 191.921 | 7.63 | 180.842 | 2231.56 | 25.61 | 42.658 | 6.34 | 1.357 | 4.588 | 8621.63 | 1.857 | 98.1 | 77.2 | 1451 | 21.37 | 5604.1 | 2913.9 | 2847.1 | 4189 | 1223.9 | 0.67776 | 5.945
2024-12-10 | 3:39 | Data | 0 | 32.919 | 30.455 | 191.967 | 7.64 | 180.842 | 2235.18 | 25.61 | 42.658 | 6.34 | 1.373 | 4.574 | 8608.06 | 2.282 | 98.1 | 76.9 | 1453 | 21.28 | 5595.2 | 2905.9 | 2839.3 | 4177.4 | 1223.9 | 0.67879 | 5.948
2024-12-10 | 3:39 | Data | 0 | 32.818 | 30.651 | 191.967 | 7.64 | 180.842 | 2233.37 | 25.61 | 42.568 | 6.34 | 1.371 | 4.603 | 8630.67 | 2.154 | 98.1 | 77 | 1451 | 21.33 | 5609.9 | 2906.3 | 2874.6 | 4203.2 | 1223.9 | 0.67472 | 5.974
2024-12-10 | 3:39 | Data | 0 | 32.555 | 30.766 | 192.012 | 7.63 | 180.842 | 2233.37 | 25.61 | 42.658 | 6.34 | 1.364 | 4.589 | 8648.76 | 1.965 | 98.1 | 77.1 | 1451 | 21.33 | 5621.7 | 2924.5 | 2849.8 | 4202.5 | 1223.9 | 0.67791 | 5.955
2024-12-10 | 3:39 | Data | 0 | 32.723 | 30.766 | 191.876 | 7.64 | 180.797 | 2232.47 | 25.61 | 42.658 | 6.34 | 1.367 | 4.605 | 8644.24 | 1.958 | 98.1 | 77.1 | 1452 | 21.33 | 5618.8 | 2912.8 | 2875.1 | 4208.8 | 1223.9 | 0.67424 | 5.97
2024-12-10 | 3:39 | Data | 0 | 32.609 | 30.766 | 192.057 | 7.64 | 180.842 | 2233.37 | 25.61 | 42.658 | 6.34 | 1.373 | 4.613 | 8648.76 | 1.917 | 98.1 | 77.1 | 1452 | 21.33 | 5621.7 | 2921.9 | 2878.9 | 4214.8 | 1223.9 | 0.67495 | 5.986
2024-12-10 | 3:39 | Data | 0 | 32.953 | 30.779 | 192.148 | 7.64 | 181.068 | 2232.47 | 25.61 | 42.658 | 6.34 | 1.362 | 4.596 | 8621.63 | 1.917 | 98.1 | 77.1 | 1452 | 21.28 | 5604.1 | 2900.1 | 2891.7 | 4213.9 | 1223.9 | 0.67083 | 5.958
2024-12-10 | 3:39 | Data | 0 | 33.027 | 30.901 | 192.102 | 7.64 | 180.978 | 2235.18 | 25.61 | 42.658 | 6.34 | 1.367 | 4.598 | 8617.1 | 2.241 | 98.1 | 77.1 | 1453 | 21.33 | 5601.1 | 2912.6 | 2877.6 | 4200.9 | 1223.9 | 0.67392 | 5.966
2024-12-10 | 3:39 | Data | 0 | 32.609 | 30.968 | 192.102 | 7.63 | 180.797 | 2235.18 | 25.61 | 42.658 | 6.34 | 1.365 | 4.594 | 8617.1 | 1.944 | 98.1 | 77.1 | 1452 | 21.37 | 5601.1 | 2916.5 | 2879.7 | 4215.2 | 1223.9 | 0.67437 | 5.958
2024-12-10 | 3:39 | Data | 0 | 32.555 | 30.651 | 192.012 | 7.64 | 180.797 | 2236.08 | 25.61 | 42.748 | 6.34 | 1.358 | 4.577 | 8626.15 | 1.87 | 98.1 | 77.1 | 1453 | 21.33 | 5607 | 2897.6 | 2873.6 | 4198 | 1223.9 | 0.67264 | 5.935
2024-12-10 | 3:39 | Data | 0 | 32.507 | 30.651 | 192.057 | 7.63 | 180.933 | 2233.37 | 25.61 | 42.658 | 6.34 | 1.36 | 4.576 | 8626.15 | 1.85 | 98.1 | 77.1 | 1452 | 21.33 | 5607 | 2907 | 2874.3 | 4207.3 | 1223.9 | 0.67508 | 5.935
2024-12-10 | 3:39 | Data | 0 | 32.622 | 30.651 | 192.012 | 7.64 | 180.797 | 2239.7 | 25.61 | 42.658 | 6.34 | 1.359 | 4.586 | 8626.15 | 1.857 | 98.1 | 77.1 | 1455 | 21.37 | 5607 | 2922.9 | 2856 | 4203.5 | 1223.9 | 0.67863 | 5.944
2024-12-10 | 3:39 | Data | 0 | 32.507 | 30.752 | 191.921 | 7.64 | 180.842 | 2227.04 | 25.61 | 42.658 | 6.34 | 1.356 | 4.582 | 8630.67 | 1.897 | 98.1 | 77.2 | 1448 | 21.33 | 5609.9 | 2906.5 | 2837.4 | 4176.9 | 1223.9 | 0.67722 | 5.938
2024-12-10 | 3:39 | Data | 0 | 32.696 | 30.651 | 191.921 | 7.64 | 180.797 | 2229.75 | 25.61 | 42.658 | 6.34 | 1.359 | 4.596 | 8635.19 | 2.066 | 98.1 | 77.2 | 1450 | 21.37 | 5612.9 | 2917.5 | 2844.8 | 4192.1 | 1223.9 | 0.67888 | 5.954
2024-12-10 | 3:39 | Data | 0 | 32.831 | 30.772 | 192.057 | 7.63 | 180.933 | 2229.75 | 25.61 | 42.658 | 6.34 | 1.359 | 4.606 | 8635.19 | 1.904 | 98.1 | 77.2 | 1450 | 21.28 | 5612.9 | 2910.1 | 2819.6 | 4168.6 | 1223.9 | 0.68026 | 5.965
2024-12-10 | 3:39 | Data | 0 | 32.501 | 30.644 | 191.967 | 7.64 | 180.842 | 2222.52 | 25.61 | 42.658 | 6.34 | 1.361 | 4.616 | 8639.71 | 1.857 | 98.1 | 77.2 | 1445 | 21.33 | 5615.8 | 2919.9 | 2841.8 | 4187.1 | 1223.9 | 0.68104 | 5.978
2024-12-10 | 3:39 | Data | 0 | 32.609 | 31.036 | 192.148 | 7.63 | 180.842 | 2227.95 | 25.61 | 42.658 | 6.34 | 1.357 | 4.603 | 8639.71 | 2.052 | 98.1 | 77.2 | 1448 | 21.33 | 5615.8 | 2905.6 | 2840.1 | 4195.3 | 1223.9 | 0.67647 | 5.96
2024-12-10 | 3:39 | Data | 0 | 32.501 | 30.482 | 192.012 | 7.64 | 180.842 | 2226.14 | 25.61 | 42.658 | 6.34 | 1.349 | 4.598 | 8644.24 | 2.005 | 98.1 | 77.3 | 1447 | 21.33 | 5618.8 | 2913.8 | 2870.5 | 4204.3 | 1223.9 | 0.67527 | 5.949
2024-12-10 | 3:39 | Data | 0 | 32.75 | 30.55 | 191.967 | 7.64 | 180.933 | 2224.33 | 25.61 | 42.658 | 6.34 | 1.349 | 4.572 | 8648.76 | 2.073 | 98.1 | 77.2 | 1446 | 21.33 | 5621.7 | 2921.8 | 2871.2 | 4213.9 | 1223.9 | 0.67525 | 5.922
2024-12-10 | 3:40 | Data | 0 | 32.723 | 30.651 | 192.057 | 7.64 | 180.933 | 2224.33 | 25.61 | 42.568 | 6.34 | 1.353 | 4.576 | 8662.33 | 1.958 | 98.1 | 77.2 | 1446 | 21.28 | 5630.5 | 2905.2 | 2885.3 | 4209.6 | 1223.9 | 0.67221 | 5.928
2024-12-10 | 3:40 | Data | 0 | 32.568 | 30.766 | 192.193 | 7.64 | 181.023 | 2222.52 | 25.61 | 42.568 | 6.34 | 1.357 | 4.585 | 8648.76 | 1.857 | 98.1 | 77.2 | 1445 | 21.33 | 5621.7 | 2931.7 | 2869.8 | 4216.7 | 1223.9 | 0.67738 | 5.941
2024-12-10 | 3:40 | Data | 0 | 32.568 | 30.651 | 192.102 | 7.64 | 180.842 | 2222.52 | 25.61 | 42.658 | 6.34 | 1.361 | 4.597 | 8671.37 | 2.025 | 98.1 | 77.2 | 1445 | 21.33 | 5636.4 | 2932.1 | 2854.8 | 4206.9 | 1223.9 | 0.67871 | 5.958
2024-12-10 | 3:40 | Data | 0 | 32.501 | 30.651 | 191.967 | 7.64 | 180.797 | 2222.52 | 25.61 | 42.658 | 6.34 | 1.367 | 4.624 | 8680.41 | 1.958 | 98.1 | 77.2 | 1445 | 21.33 | 5642.3 | 2935.8 | 2824.2 | 4186.5 | 1223.9 | 0.68499 | 5.99
2024-12-10 | 3:40 | Data | 0 | 32.669 | 30.448 | 192.057 | 7.64 | 180.842 | 2223.43 | 25.61 | 42.748 | 6.34 | 1.364 | 4.631 | 8639.71 | 2.194 | 98.1 | 77.2 | 1445 | 21.33 | 5615.8 | 2916.9 | 2834.8 | 4185.4 | 1223.9 | 0.67975 | 5.994
2024-12-10 | 3:40 | Data | 0 | 32.899 | 30.685 | 192.148 | 7.64 | 180.978 | 2222.52 | 25.61 | 42.658 | 6.33 | 1.362 | 4.612 | 8635.19 | 2.154 | 98.1 | 77.2 | 1445 | 21.33 | 5612.9 | 2906.7 | 2823.6 | 4169.9 | 1223.9 | 0.67971 | 5.975
2024-12-10 | 3:40 | Data | 0 | 32.514 | 30.428 | 192.102 | 7.64 | 180.707 | 2221.62 | 25.61 | 42.658 | 6.34 | 1.359 | 4.585 | 8648.76 | 1.965 | 98.1 | 77.1 | 1445 | 21.33 | 5621.7 | 2917.8 | 2832.9 | 4182.5 | 1224 | 0.68067 | 5.944
2024-12-10 | 3:40 | Data | 0 | 32.75 | 30.651 | 192.057 | 7.64 | 180.842 | 2221.62 | 25.61 | 42.658 | 6.34 | 1.357 | 4.606 | 8644.24 | 2.073 | 98.1 | 77.3 | 1445 | 21.28 | 5618.8 | 2912.7 | 2823.9 | 4171.8 | 1224 | 0.68089 | 5.961
2024-12-10 | 3:40 | Data | 0 | 32.946 | 30.874 | 192.012 | 7.64 | 180.933 | 2221.62 | 25.61 | 42.658 | 6.34 | 1.358 | 4.605 | 8693.98 | 1.971 | 98.1 | 77.2 | 1445 | 21.28 | 5651.1 | 2909.9 | 2845 | 4186.8 | 1224 | 0.67747 | 5.963
2024-12-10 | 3:40 | Data | 0 | 32.723 | 31.069 | 192.102 | 7.64 | 180.978 | 2222.52 | 25.61 | 42.658 | 6.34 | 1.351 | 4.605 | 8680.41 | 1.87 | 98.1 | 77.3 | 1445 | 21.33 | 5642.3 | 2914.7 | 2869.9 | 4207.9 | 1224 | 0.67757 | 5.956
2024-12-10 | 3:40 | Data | 0 | 32.609 | 31.09 | 192.012 | 7.64 | 180.752 | 2222.52 | 25.61 | 42.658 | 6.34 | 1.355 | 4.604 | 8666.85 | 2.032 | 98.1 | 77.3 | 1445 | 21.37 | 5633.5 | 2906 | 2873.5 | 4201.5 | 1224 | 0.67299 | 5.96
2024-12-10 | 3:40 | Data | 0 | 32.501 | 30.752 | 192.057 | 7.64 | 180.933 | 2222.52 | 25.61 | 42.748 | 6.34 | 1.358 | 4.594 | 8662.33 | 1.843 | 98.1 | 77.2 | 1445 | 21.33 | 5630.5 | 2912.2 | 2871.4 | 4204.2 | 1224 | 0.67522 | 5.952
2024-12-10 | 3:40 | Data | 0 | 32.852 | 30.928 | 192.102 | 7.64 | 180.842 | 2223.43 | 25.61 | 42.658 | 6.34 | 1.356 | 4.598 | 8617.1 | 2.127 | 98.1 | 77.2 | 1445 | 21.33 | 5601.1 | 2916.8 | 2856.3 | 4186.4 | 1224 | 0.67558 | 5.953
2024-12-10 | 3:40 | Data | 0 | 32.723 | 30.658 | 192.012 | 7.64 | 180.842 | 2227.95 | 25.61 | 42.658 | 6.34 | 1.371 | 4.563 | 8603.54 | 2.046 | 98.1 | 76.9 | 1448 | 21.33 | 5592.3 | 2923.7 | 2853.7 | 4200 | 1224 | 0.67955 | 5.935
2024-12-10 | 3:40 | Data | 0 | 32.609 | 30.536 | 191.921 | 7.64 | 180.752 | 2227.95 | 25.61 | 42.658 | 6.34 | 1.373 | 4.595 | 8621.63 | 1.87 | 98.1 | 77 | 1448 | 21.33 | 5604.1 | 2906.9 | 2823.6 | 4165.9 | 1224 | 0.67991 | 5.967
2024-12-10 | 3:40 | Data | 0 | 32.683 | 30.651 | 192.057 | 7.64 | 180.933 | 2226.14 | 25.61 | 42.658 | 6.34 | 1.365 | 4.585 | 8626.15 | 2.066 | 98.1 | 77.1 | 1447 | 21.33 | 5607 | 2915.8 | 2824 | 4173.7 | 1224 | 0.68152 | 5.95
2024-12-10 | 3:40 | Data | 0 | 32.777 | 30.631 | 192.148 | 7.64 | 180.978 | 2227.95 | 25.61 | 42.658 | 6.34 | 1.36 | 4.598 | 8639.71 | 1.904 | 98.1 | 77.2 | 1448 | 21.33 | 5615.8 | 2914.6 | 2791.7 | 4153.5 | 1224 | 0.68485 | 5.957
2024-12-10 | 3:41 | Data | 0 | 32.73 | 30.61 | 192.102 | 7.64 | 180.933 | 2227.95 | 25.61 | 42.658 | 6.34 | 1.358 | 4.611 | 8648.76 | 1.958 | 98.1 | 77.2 | 1448 | 21.33 | 5621.7 | 2914.3 | 2839.2 | 4183.9 | 1224 | 0.67947 | 5.969
2024-12-10 | 3:41 | Data | 0 | 32.588 | 30.813 | 192.148 | 7.64 | 180.978 | 2227.04 | 25.61 | 42.658 | 6.34 | 1.365 | 4.624 | 8644.24 | 1.803 | 98.1 | 77.2 | 1448 | 21.33 | 5618.8 | 2906 | 2836.8 | 4183.3 | 1224 | 0.6764 | 5.988
2024-12-10 | 3:41 | Data | 0 | 32.737 | 30.928 | 192.012 | 7.64 | 180.978 | 2232.47 | 25.61 | 42.658 | 6.34 | 1.367 | 4.627 | 8644.24 | 1.897 | 98.1 | 77.2 | 1452 | 21.33 | 5618.8 | 2943.3 | 2830.9 | 4196.9 | 1224 | 0.685 | 5.995
2024-12-10 | 3:41 | Data | 0 | 32.717 | 30.86 | 192.012 | 7.64 | 180.933 | 2227.95 | 25.61 | 42.658 | 6.34 | 1.367 | 4.583 | 8662.33 | 1.917 | 98.1 | 77 | 1448 | 21.33 | 5630.5 | 2915.8 | 2846.4 | 4190.4 | 1224 | 0.6794 | 5.95
2024-12-10 | 3:41 | Data | 0 | 32.946 | 30.732 | 192.102 | 7.64 | 180.978 | 2228.85 | 25.61 | 42.658 | 6.34 | 1.367 | 4.588 | 8648.76 | 2.025 | 98.1 | 77.1 | 1448 | 21.28 | 5621.7 | 2899.2 | 2835.1 | 4168.6 | 1224 | 0.67839 | 5.954
2024-12-10 | 3:41 | Data | 0 | 32.723 | 30.651 | 191.921 | 7.64 | 180.797 | 2227.95 | 25.61 | 42.658 | 6.34 | 1.372 | 4.594 | 8648.76 | 1.87 | 98.1 | 77 | 1448 | 21.33 | 5621.7 | 2910.5 | 2828.8 | 4174.9 | 1224 | 0.67969 | 5.967
2024-12-10 | 3:41 | Data | 0 | 32.609 | 30.651 | 192.012 | 7.64 | 180.933 | 2221.62 | 25.61 | 42.658 | 6.34 | 1.372 | 4.603 | 8653.28 | 1.87 | 98.1 | 77 | 1444 | 21.37 | 5624.6 | 2920.9 | 2824.3 | 4178.7 | 1224 | 0.68265 | 5.974
2024-12-10 | 3:41 | Data | 0 | 32.737 | 30.853 | 192.012 | 7.63 | 180.933 | 2227.95 | 25.61 | 42.658 | 6.34 | 1.377 | 4.6 | 8603.54 | 1.965 | 98.1 | 77 | 1448 | 21.33 | 5592.3 | 2908.8 | 2824.4 | 4171.4 | 1224 | 0.68042 | 5.977
2024-12-10 | 3:41 | Data | 0 | 32.926 | 30.448 | 192.057 | 7.64 | 181.023 | 2124.01 | 25.61 | 42.748 | 6.34 | 1.37 | 4.605 | 8571.88 | 1.931 | 98 | 77.1 | 1381 | 21.33 | 5571.7 | 2910.2 | 2824.1 | 4175.2 | 1224 | 0.68027 | 5.976
2024-12-10 | 3:41 | Data | 0 | 32.892 | 30.88 | 192.193 | 7.64 | 180.933 | 2228.85 | 25.61 | 42.568 | 6.34 | 1.364 | 4.6 | 8576.4 | 2.052 | 98.1 | 77.1 | 1449 | 21.33 | 5574.7 | 2905.3 | 2816.8 | 4166.9 | 1224 | 0.68216 | 5.965
2024-12-10 | 3:41 | Data | 0 | 32.865 | 30.941 | 192.102 | 7.64 | 181.023 | 2230.66 | 25.61 | 42.658 | 6.34 | 1.358 | 4.58 | 8580.93 | 2.133 | 98.1 | 77.1 | 1449 | 21.37 | 5577.6 | 2916.8 | 2830.2 | 4182.2 | 1224 | 0.68092 | 5.938
2024-12-10 | 3:41 | Data | 0 | 32.683 | 30.88 | 192.057 | 7.64 | 180.978 | 2229.75 | 25.61 | 42.658 | 6.34 | 1.361 | 4.595 | 8603.54 | 2.059 | 98.1 | 77.1 | 1449 | 21.33 | 5592.3 | 2906.2 | 2831.3 | 4173.4 | 1224 | 0.68107 | 5.955
2024-12-10 | 3:41 | Data | 0 | 32.555 | 30.651 | 191.921 | 7.63 | 180.933 | 2225.23 | 25.61 | 42.658 | 6.34 | 1.355 | 4.601 | 8612.58 | 1.87 | 98.1 | 77.3 | 1446 | 21.28 | 5598.2 | 2918.1 | 2861.7 | 4203.2 | 1224 | 0.67818 | 5.956
2024-12-10 | 3:41 | Data | 0 | 32.723 | 31.09 | 192.057 | 7.64 | 180.978 | 2227.04 | 25.61 | 42.658 | 6.34 | 1.355 | 4.605 | 8612.58 | 1.823 | 98.1 | 77.3 | 1448 | 21.33 | 5598.2 | 2939.8 | 2851.8 | 4207.6 | 1224 | 0.68087 | 5.96
2024-12-10 | 3:41 | Data | 0 | 32.696 | 30.651 | 192.057 | 7.64 | 180.933 | 2227.95 | 25.61 | 42.658 | 6.35 | 1.361 | 4.585 | 8608.06 | 2.073 | 98.1 | 77.1 | 1448 | 21.37 | 5595.2 | 2914.7 | 2847.2 | 4193.7 | 1224 | 0.67782 | 5.945
2024-12-10 | 3:41 | Data | 0 | 32.919 | 30.705 | 192.057 | 7.64 | 180.978 | 2227.04 | 25.61 | 42.568 | 6.34 | 1.356 | 4.593 | 8612.58 | 2.066 | 98.1 | 77.2 | 1448 | 21.33 | 5598.2 | 2906.5 | 2830.5 | 4170 | 1224 | 0.68023 | 5.949
2024-12-10 | 3:41 | Data | 0 | 32.838 | 30.86 | 191.967 | 7.64 | 180.933 | 2227.04 | 25.62 | 42.658 | 6.34 | 1.357 | 4.601 | 8608.06 | 2.066 | 98.1 | 77.2 | 1448 | 21.33 | 5595.2 | 2901.2 | 2841.6 | 4178.2 | 1224 | 0.67746 | 5.958
2024-12-10 | 3:41 | Data | 0 | 32.615 | 30.739 | 192.102 | 7.63 | 181.023 | 2228.85 | 25.62 | 42.658 | 6.34 | 1.359 | 4.577 | 8612.58 | 1.917 | 98.1 | 77.1 | 1449 | 21.28 | 5598.2 | 2932.5 | 2831.1 | 4191.9 | 1224 | 0.68245 | 5.936
2024-12-10 | 3:42 | Data | 0 | 32.75 | 30.678 | 192.148 | 7.64 | 181.068 | 2227.04 | 25.62 | 42.658 | 6.35 | 1.358 | 4.598 | 8621.63 | 1.917 | 98.1 | 77.2 | 1448 | 21.33 | 5604.1 | 2920.2 | 2880.5 | 4217.4 | 1224 | 0.67548 | 5.956
2024-12-10 | 3:42 | Data | 0 | 32.75 | 30.766 | 192.102 | 7.64 | 180.842 | 2225.23 | 25.63 | 42.568 | 6.34 | 1.358 | 4.591 | 8608.06 | 2.073 | 98.1 | 77.2 | 1447 | 21.28 | 5595.2 | 2912.8 | 2876.3 | 4215.3 | 1224 | 0.67226 | 5.949
2024-12-10 | 3:42 | Data | 0 | 32.845 | 30.597 | 192.148 | 7.63 | 181.023 | 2225.23 | 25.61 | 42.658 | 6.34 | 1.353 | 4.603 | 8617.1 | 1.985 | 98.1 | 77.3 | 1446 | 21.37 | 5601.1 | 2915.7 | 2864 | 4205.3 | 1224 | 0.6761 | 5.957
2024-12-10 | 3:42 | Data | 0 | 32.723 | 30.658 | 191.967 | 7.64 | 180.933 | 2224.33 | 25.61 | 42.658 | 6.34 | 1.364 | 4.581 | 8621.63 | 2.059 | 98.1 | 77.1 | 1446 | 21.33 | 5604.1 | 2913.9 | 2854.4 | 4199.2 | 1224 | 0.67667 | 5.945
2024-12-10 | 3:42 | Data | 0 | 32.71 | 30.61 | 191.967 | 7.64 | 180.933 | 2223.43 | 25.61 | 42.658 | 6.34 | 1.366 | 4.601 | 8608.06 | 1.985 | 98.1 | 77.1 | 1445 | 21.33 | 5595.2 | 2918.7 | 2828.3 | 4188.1 | 1224 | 0.68175 | 5.967
2024-12-10 | 3:42 | Data | 0 | 32.737 | 30.853 | 192.102 | 7.64 | 180.842 | 2221.62 | 25.61 | 42.658 | 6.34 | 1.366 | 4.595 | 8621.63 | 1.958 | 98.1 | 77.1 | 1445 | 21.33 | 5604.1 | 2913.1 | 2840.9 | 4189.5 | 1224 | 0.67834 | 5.96
2024-12-10 | 3:42 | Data | 0 | 32.683 | 30.651 | 192.102 | 7.63 | 181.023 | 2216.2 | 25.61 | 42.658 | 6.35 | 1.359 | 4.6 | 8621.63 | 2.046 | 98.1 | 77.2 | 1441 | 21.33 | 5604.1 | 2911.9 | 2836.8 | 4183.1 | 1224 | 0.68003 | 5.96
2024-12-10 | 3:42 | Data | 0 | 33.054 | 31.103 | 192.148 | 7.64 | 180.933 | 2218.91 | 25.61 | 42.658 | 6.34 | 1.349 | 4.596 | 8630.67 | 2.066 | 98.1 | 77.3 | 1442 | 21.33 | 5609.9 | 2903.1 | 2830.8 | 4173.1 | 1224.1 | 0.67866 | 5.945
2024-12-10 | 3:42 | Data | 0 | 32.946 | 30.88 | 192.148 | 7.64 | 181.068 | 2220.72 | 25.61 | 42.658 | 6.35 | 1.358 | 4.598 | 8630.67 | 2.073 | 98.1 | 77.2 | 1442 | 21.28 | 5609.9 | 2903.6 | 2837.4 | 4178.2 | 1224.1 | 0.67668 | 5.955
2024-12-10 | 3:42 | Data | 0 | 32.73 | 30.853 | 192.102 | 7.64 | 180.933 | 2220.72 | 25.62 | 42.658 | 6.34 | 1.358 | 4.596 | 8648.76 | 1.87 | 98.1 | 77.2 | 1442 | 21.33 | 5621.7 | 2900.1 | 2848.6 | 4185.2 | 1224.1 | 0.67852 | 5.953
2024-12-10 | 3:42 | Data | 0 | 32.723 | 30.766 | 192.012 | 7.64 | 180.797 | 2216.2 | 25.63 | 42.658 | 6.34 | 1.353 | 4.593 | 8635.19 | 1.958 | 98.1 | 77.2 | 1441 | 21.33 | 5612.9 | 2916.3 | 2870.2 | 4208.5 | 1224.1 | 0.67615 | 5.946
2024-12-10 | 3:42 | Data | 0 | 32.555 | 30.766 | 192.012 | 7.63 | 180.752 | 2213.49 | 25.62 | 42.658 | 6.34 | 1.352 | 4.588 | 8630.67 | 1.938 | 98.1 | 77.2 | 1439 | 21.33 | 5609.9 | 2911.2 | 2893.2 | 4218.8 | 1224.1 | 0.6733 | 5.941
2024-12-10 | 3:42 | Data | 0 | 32.723 | 30.664 | 191.967 | 7.63 | 180.842 | 2217.1 | 25.61 | 42.568 | 6.34 | 1.357 | 4.593 | 8630.67 | 2.059 | 98.1 | 77.2 | 1441 | 21.28 | 5609.9 | 2919.7 | 2880.8 | 4218 | 1224.1 | 0.67421 | 5.95
2024-12-10 | 3:42 | Data | 0 | 32.501 | 30.556 | 192.057 | 7.64 | 180.842 | 2216.2 | 25.63 | 42.658 | 6.34 | 1.353 | 4.603 | 8648.76 | 2.14 | 98.1 | 77.3 | 1441 | 21.28 | 5621.7 | 2916.4 | 2889.9 | 4223.1 | 1224.1 | 0.67288 | 5.956
2024-12-10 | 3:42 | Data | 0 | 33.027 | 30.509 | 192.057 | 7.64 | 180.978 | 2216.2 | 25.62 | 42.658 | 6.34 | 1.357 | 4.594 | 8644.24 | 2.073 | 98.1 | 77.2 | 1441 | 21.33 | 5618.8 | 2909.3 | 2895.9 | 4222 | 1224.1 | 0.6721 | 5.95
2024-12-10 | 3:42 | Data | 0 | 32.737 | 30.995 | 191.967 | 7.63 | 180.978 | 2217.1 | 25.62 | 42.658 | 6.34 | 1.36 | 4.598 | 8653.28 | 1.85 | 98.1 | 77.2 | 1441 | 21.33 | 5624.6 | 2912.1 | 2898.1 | 4225.6 | 1224.1 | 0.67156 | 5.96
2024-12-10 | 3:42 | Data | 0 | 33.122 | 30.894 | 192.102 | 7.64 | 181.023 | 2220.72 | 25.62 | 42.658 | 6.34 | 1.352 | 4.585 | 8644.24 | 2.039 | 98.1 | 77.2 | 1442 | 21.37 | 5618.8 | 2904.4 | 2862.1 | 4210.4 | 1224.1 | 0.67457 | 5.937
2024-12-10 | 3:42 | Data | 0 | 32.75 | 30.853 | 192.012 | 7.64 | 180.978 | 2218.91 | 25.62 | 42.658 | 6.34 | 1.36 | 4.602 | 8648.76 | 1.965 | 98.1 | 77.2 | 1442 | 21.33 | 5621.7 | 2926.9 | 2875.8 | 4219.7 | 1224.1 | 0.67576 | 5.964
2024-12-10 | 3:43 | Data | 0 | 33.122 | 30.685 | 192.012 | 7.64 | 180.978 | 2218.91 | 25.63 | 42.658 | 6.34 | 1.359 | 4.61 | 8635.19 | 1.992 | 98.1 | 77.2 | 1442 | 21.33 | 5612.9 | 2907.8 | 2858.4 | 4198.4 | 1224.1 | 0.67492 | 5.969
2024-12-10 | 3:43 | Data | 0 | 33.061 | 30.934 | 192.148 | 7.64 | 181.023 | 2218 | 25.62 | 42.658 | 6.34 | 1.363 | 4.612 | 8635.19 | 2.019 | 98.1 | 77.2 | 1442 | 21.33 | 5612.9 | 2915 | 2833.9 | 4180.1 | 1224.1 | 0.67953 | 5.975
2024-12-10 | 3:43 | Data | 0 | 32.568 | 30.651 | 192.102 | 7.64 | 180.933 | 2218.91 | 25.62 | 42.748 | 6.34 | 1.353 | 4.578 | 8648.76 | 2.019 | 98.1 | 77.2 | 1442 | 21.33 | 5621.7 | 2925.3 | 2845.6 | 4196.2 | 1224.1 | 0.67566 | 5.931
2024-12-10 | 3:43 | Data | 0 | 32.784 | 30.779 | 192.148 | 7.63 | 181.023 | 2222.52 | 25.62 | 42.658 | 6.34 | 1.359 | 4.564 | 8635.19 | 2.046 | 98.1 | 77.1 | 1445 | 21.28 | 5612.9 | 2922.5 | 2856.1 | 4204.4 | 1224.1 | 0.67747 | 5.923
2024-12-10 | 3:43 | Data | 0 | 32.514 | 30.874 | 192.148 | 7.63 | 180.933 | 2222.52 | 25.62 | 42.658 | 6.34 | 1.366 | 4.592 | 8630.67 | 1.823 | 98.1 | 77.1 | 1445 | 21.33 | 5609.9 | 2911.1 | 2859.4 | 4200.3 | 1224.1 | 0.67739 | 5.958
2024-12-10 | 3:43 | Data | 0 | 32.744 | 30.658 | 192.057 | 7.64 | 180.978 | 2222.52 | 25.63 | 42.658 | 6.34 | 1.37 | 4.628 | 8635.19 | 1.877 | 98.1 | 77.2 | 1445 | 21.33 | 5612.9 | 2921.6 | 2891.2 | 4225.2 | 1224.1 | 0.67328 | 5.998
2024-12-10 | 3:43 | Data | 0 | 32.494 | 30.651 | 192.012 | 7.64 | 180.842 | 2226.14 | 25.62 | 42.658 | 6.34 | 1.367 | 4.592 | 8630.67 | 2.019 | 98.1 | 77.1 | 1446 | 21.33 | 5609.9 | 2908.8 | 2872.5 | 4202.4 | 1224.1 | 0.67556 | 5.96
2024-12-10 | 3:43 | Data | 0 | 32.723 | 30.651 | 191.967 | 7.63 | 180.842 | 2225.23 | 25.62 | 42.658 | 6.35 | 1.359 | 4.561 | 8621.63 | 2.073 | 98.1 | 77 | 1446 | 21.33 | 5604.1 | 2898.1 | 2871.7 | 4198.9 | 1224.1 | 0.67211 | 5.922
2024-12-10 | 3:43 | Data | 0 | 32.994 | 30.658 | 192.148 | 7.64 | 180.978 | 2227.04 | 25.62 | 42.658 | 6.34 | 1.357 | 4.576 | 8621.63 | 2.12 | 98.1 | 77.1 | 1448 | 21.28 | 5604.1 | 2894.5 | 2885.1 | 4204.9 | 1224.1 | 0.67038 | 5.931
2024-12-10 | 3:43 | Data | 0 | 32.784 | 30.853 | 191.921 | 7.63 | 180.978 | 2225.23 | 25.62 | 42.658 | 6.34 | 1.36 | 4.603 | 8621.63 | 2.079 | 98.1 | 77.2 | 1446 | 21.37 | 5604.1 | 2920.5 | 2882.5 | 4219.2 | 1224.1 | 0.67522 | 5.963
2024-12-10 | 3:43 | Data | 0 | 32.615 | 30.88 | 192.057 | 7.64 | 180.978 | 2225.23 | 25.63 | 42.658 | 6.34 | 1.367 | 4.585 | 8626.15 | 1.796 | 98.1 | 77 | 1446 | 21.28 | 5607 | 2920.7 | 2875 | 4212.2 | 1224.1 | 0.67605 | 5.951
2024-12-10 | 3:43 | Data | 0 | 32.507 | 30.651 | 192.102 | 7.63 | 181.023 | 2225.23 | 25.62 | 42.748 | 6.34 | 1.369 | 4.602 | 8621.63 | 1.958 | 98.1 | 77.1 | 1446 | 21.37 | 5604.1 | 2921.7 | 2864 | 4209.6 | 1224.1 | 0.67674 | 5.972
2024-12-10 | 3:43 | Data | 0 | 32.953 | 30.988 | 192.148 | 7.64 | 180.978 | 2227.95 | 25.62 | 42.658 | 6.35 | 1.365 | 4.572 | 8621.63 | 1.857 | 98.1 | 77 | 1449 | 21.33 | 5604.1 | 2921.4 | 2866.6 | 4215.8 | 1224.1 | 0.67771 | 5.938
2024-12-10 | 3:43 | Data | 0 | 32.541 | 30.968 | 192.148 | 7.64 | 180.933 | 2235.18 | 25.62 | 42.658 | 6.35 | 1.365 | 4.58 | 8599.01 | 1.749 | 98.1 | 77 | 1453 | 21.33 | 5589.4 | 2905.3 | 2840.7 | 4185.3 | 1224.1 | 0.67661 | 5.946
2024-12-10 | 3:43 | Data | 0 | 32.73 | 30.766 | 192.057 | 7.63 | 180.978 | 2231.56 | 25.63 | 42.568 | 6.34 | 1.366 | 4.575 | 8594.49 | 1.958 | 98.1 | 77 | 1450 | 21.33 | 5586.4 | 2924.5 | 2855.1 | 4200.4 | 1224.1 | 0.68039 | 5.941
2024-12-10 | 3:43 | Data | 0 | 32.75 | 30.651 | 192.102 | 7.63 | 180.978 | 2230.66 | 25.62 | 42.658 | 6.34 | 1.367 | 4.578 | 8599.01 | 2.073 | 98.1 | 77 | 1449 | 21.33 | 5589.4 | 2925.5 | 2861 | 4204.3 | 1224.1 | 0.6798 | 5.945
2024-12-10 | 3:43 | Data | 0 | 32.892 | 30.988 | 191.967 | 7.63 | 181.023 | 2229.75 | 25.62 | 42.658 | 6.35 | 1.365 | 4.581 | 8576.4 | 2.019 | 98.1 | 77 | 1450 | 21.33 | 5574.7 | 2913.9 | 2852.5 | 4197.1 | 1224.1 | 0.67602 | 5.946
2024-12-10 | 3:43 | Data | 0 | 32.737 | 30.88 | 192.238 | 7.64 | 181.023 | 2231.56 | 25.62 | 42.658 | 6.34 | 1.376 | 4.613 | 8608.06 | 1.843 | 98.1 | 77 | 1450 | 21.37 | 5595.2 | 2915.4 | 2860.1 | 4199.7 | 1224.1 | 0.67734 | 5.989
2024-12-10 | 3:44 | Data | 0 | 33.162 | 30.793 | 192.238 | 7.64 | 181.068 | 2233.37 | 25.62 | 42.658 | 6.34 | 1.362 | 4.595 | 8608.06 | 2.187 | 98.1 | 77.1 | 1452 | 21.33 | 5595.2 | 2929.9 | 2871.9 | 4212 | 1224.1 | 0.67524 | 5.957
2024-12-10 | 3:44 | Data | 0 | 33.061 | 30.671 | 192.102 | 7.63 | 180.978 | 2232.47 | 25.62 | 42.658 | 6.34 | 1.358 | 4.598 | 8608.06 | 2.073 | 98.1 | 77.2 | 1451 | 21.33 | 5595.2 | 2927.8 | 2882.3 | 4225.7 | 1224.1 | 0.675 | 5.957
2024-12-10 | 3:44 | Data | 0 | 32.838 | 30.88 | 192.057 | 7.63 | 180.978 | 2233.37 | 25.63 | 42.658 | 6.34 | 1.361 | 4.613 | 8608.06 | 1.857 | 98.1 | 77.2 | 1452 | 21.33 | 5595.2 | 2920.1 | 2881.8 | 4216.8 | 1224.1 | 0.6754 | 5.973
2024-12-10 | 3:44 | Data | 0 | 32.622 | 30.766 | 192.102 | 7.63 | 180.978 | 2232.47 | 25.62 | 42.658 | 6.34 | 1.37 | 4.6 | 8621.63 | 1.944 | 98.1 | 77.1 | 1451 | 21.28 | 5604.1 | 2904.9 | 2900.4 | 4221.5 | 1224.1 | 0.67499 | 5.97
2024-12-10 | 3:44 | Data | 0 | 32.723 | 31.036 | 192.057 | 7.63 | 180.933 | 2230.66 | 25.63 | 42.568 | 6.34 | 1.371 | 4.619 | 8608.06 | 1.958 | 98.1 | 77.1 | 1450 | 21.28 | 5595.2 | 2916.8 | 2859.3 | 4199 | 1224.1 | 0.67773 | 5.989
2024-12-10 | 3:44 | Data | 0 | 32.757 | 30.968 | 192.238 | 7.64 | 181.068 | 2230.66 | 25.63 | 42.658 | 6.34 | 1.361 | 4.609 | 8621.63 | 1.904 | 98.1 | 77.2 | 1449 | 21.33 | 5604.1 | 2918.2 | 2884.9 | 4219.5 | 1224.1 | 0.67416 | 5.971
2024-12-10 | 3:44 | Data | 0 | 32.507 | 30.826 | 192.102 | 7.64 | 180.978 | 2229.75 | 25.62 | 42.658 | 6.35 | 1.353 | 4.597 | 8621.63 | 1.87 | 98.1 | 77.3 | 1449 | 21.33 | 5604.1 | 2923.1 | 2873.7 | 4215.2 | 1224.1 | 0.67626 | 5.95
2024-12-10 | 3:44 | Data | 0 | 32.98 | 30.934 | 192.148 | 7.63 | 181.023 | 2232.47 | 25.62 | 42.568 | 6.34 | 1.367 | 4.585 | 8626.15 | 1.971 | 98.1 | 77 | 1451 | 21.33 | 5607 | 2912.6 | 2857.3 | 4192.4 | 1224.1 | 0.6774 | 5.951
2024-12-10 | 3:44 | Data | 0 | 32.953 | 31.191 | 192.193 | 7.64 | 181.068 | 2233.37 | 25.63 | 42.748 | 6.34 | 1.369 | 4.593 | 8621.63 | 1.863 | 98.1 | 77 | 1451 | 21.33 | 5604.1 | 2914.5 | 2856.5 | 4202 | 1224.2 | 0.67541 | 5.963
2024-12-10 | 3:44 | Data | 0 | 33.007 | 30.88 | 192.238 | 7.63 | 181.114 | 2232.47 | 25.63 | 42.568 | 6.34 | 1.366 | 4.605 | 8648.76 | 1.971 | 98.1 | 77.1 | 1451 | 21.28 | 5621.7 | 2908.1 | 2844.9 | 4183.5 | 1224.2 | 0.67832 | 5.97
2024-12-10 | 3:44 | Data | 0 | 32.609 | 30.968 | 192.102 | 7.64 | 181.023 | 2238.79 | 25.62 | 42.206 | 6.34 | 1.358 | 4.599 | 8644.24 | 2.039 | 98.1 | 77.2 | 1454 | 21.06 | 5618.8 | 2924.5 | 2825.2 | 4180.2 | 1224.2 | 0.68268 | 5.958
2024-12-10 | 3:44 | Data | 0 | 32.98 | 30.88 | 192.102 | 7.63 | 181.023 | 2240.6 | 25.62 | 42.568 | 6.34 | 1.353 | 4.612 | 8648.76 | 1.877 | 98.1 | 77.3 | 1456 | 21.33 | 5621.7 | 2923.1 | 2849.1 | 4198.8 | 1224.2 | 0.68018 | 5.965
2024-12-10 | 3:44 | Data | 0 | 32.723 | 30.448 | 192.057 | 7.64 | 180.933 | 2245.12 | 25.62 | 42.658 | 6.34 | 1.356 | 4.617 | 8648.76 | 2.16 | 98.1 | 77.3 | 1459 | 21.33 | 5621.7 | 2908.3 | 2875.8 | 4207.5 | 1224.2 | 0.67381 | 5.973
2024-12-10 | 3:44 | Data | 0 | 32.669 | 30.651 | 192.012 | 7.64 | 180.933 | 2241.5 | 25.63 | 42.658 | 6.34 | 1.365 | 4.601 | 8644.24 | 2.066 | 98.1 | 77.1 | 1458 | 21.33 | 5618.8 | 2924 | 2902 | 4233.9 | 1224.2 | 0.672 | 5.968
2024-12-10 | 3:44 | Data | 0 | 32.696 | 30.88 | 191.967 | 7.63 | 180.933 | 2242.41 | 25.62 | 42.658 | 6.34 | 1.364 | 4.609 | 8639.71 | 2.019 | 98.1 | 77.2 | 1457 | 21.28 | 5615.8 | 2915.9 | 2900.4 | 4232.2 | 1224.2 | 0.6706 | 5.973
2024-12-10 | 3:44 | Data | 0 | 32.967 | 30.88 | 192.148 | 7.64 | 181.023 | 2235.18 | 25.63 | 42.658 | 6.34 | 1.361 | 4.611 | 8603.54 | 1.87 | 98.1 | 77.2 | 1452 | 21.33 | 5592.3 | 2929.9 | 2871.6 | 4221.6 | 1224.2 | 0.67577 | 5.972
2024-12-10 | 3:44 | Data | 0 | 32.777 | 30.88 | 192.102 | 7.64 | 180.933 | 2233.37 | 25.62 | 42.658 | 6.34 | 1.358 | 4.6 | 8608.06 | 1.843 | 98.1 | 77.2 | 1451 | 21.33 | 5595.2 | 2934.1 | 2868.9 | 4222.4 | 1224.2 | 0.67675 | 5.956
2024-12-10 | 3:44 | Data | 0 | 32.507 | 30.712 | 192.012 | 7.64 | 180.933 | 2232.47 | 25.63 | 42.658 | 6.34 | 1.369 | 4.6 | 8612.58 | 2.073 | 98.1 | 77.1 | 1452 | 21.33 | 5598.2 | 2914.4 | 2859.4 | 4201.5 | 1224.2 | 0.67684 | 5.969
2024-12-10 | 3:45 | Data | 0 | 33 | 30.658 | 192.193 | 7.63 | 180.978 | 2232.47 | 25.62 | 42.748 | 6.34 | 1.367 | 4.6 | 8603.54 | 2.127 | 98.1 | 77.1 | 1451 | 21.33 | 5592.3 | 2927.8 | 2838 | 4195.9 | 1224.2 | 0.67967 | 5.968
2024-12-10 | 3:45 | Data | 0 | 32.723 | 30.88 | 192.057 | 7.64 | 180.933 | 2233.37 | 25.63 | 42.568 | 6.34 | 1.358 | 4.598 | 8626.15 | 2.066 | 98.1 | 77.2 | 1452 | 21.33 | 5607 | 2920.1 | 2853.9 | 4204.9 | 1224.2 | 0.67871 | 5.954
2024-12-10 | 3:45 | Data | 0 | 33.041 | 30.685 | 192.193 | 7.64 | 181.114 | 2226.14 | 25.63 | 42.658 | 6.35 | 1.36 | 4.579 | 8237.24 | 2.201 | 98.1 | 77.1 | 1448 | 21.33 | 5354.2 | 2920.3 | 2861 | 4208.5 | 1224.2 | 0.67761 | 5.941
2024-12-10 | 3:45 | Data | 0 | 32.838 | 31.056 | 192.057 | 7.63 | 180.933 | 2227.04 | 25.63 | 42.658 | 6.34 | 1.358 | 4.58 | 8594.49 | 2.005 | 98.1 | 77.1 | 1448 | 21.28 | 5586.4 | 2917.8 | 2845.2 | 4191.6 | 1224.2 | 0.67889 | 5.938
2024-12-10 | 3:45 | Data | 0 | 33.041 | 30.671 | 192.148 | 7.64 | 181.023 | 2225.23 | 25.62 | 42.477 | 6.34 | 1.361 | 4.575 | 8630.67 | 2.079 | 98.1 | 77.1 | 1446 | 21.24 | 5609.9 | 2921 | 2859.6 | 4203.4 | 1224.2 | 0.67724 | 5.937
2024-12-10 | 3:45 | Data | 0 | 32.588 | 30.651 | 192.148 | 7.64 | 181.023 | 2224.33 | 25.63 | 42.387 | 6.34 | 1.365 | 4.582 | 8639.71 | 1.863 | 98.1 | 77 | 1446 | 21.24 | 5615.8 | 2919.1 | 2859.7 | 4198.4 | 1224.2 | 0.67741 | 5.946
2024-12-10 | 3:45 | Data | 0 | 32.845 | 30.678 | 192.057 | 7.63 | 181.023 | 2225.23 | 25.62 | 42.658 | 6.34 | 1.365 | 4.583 | 8630.67 | 1.971 | 98.1 | 77.1 | 1446 | 21.33 | 5609.9 | 2923.5 | 2882.5 | 4223.1 | 1224.2 | 0.67426 | 5.948
2024-12-10 | 3:45 | Data | 0 | 32.534 | 30.651 | 192.148 | 7.64 | 180.933 | 2220.72 | 25.62 | 42.658 | 6.34 | 1.362 | 4.598 | 8626.15 | 1.857 | 98.1 | 77.1 | 1442 | 21.37 | 5607 | 2909.5 | 2898.3 | 4229 | 1224.2 | 0.67025 | 5.96
2024-12-10 | 3:45 | Data | 0 | 32.555 | 30.766 | 192.148 | 7.64 | 181.023 | 2225.23 | 25.63 | 42.568 | 6.34 | 1.36 | 4.604 | 8635.19 | 1.911 | 98.1 | 77.2 | 1447 | 21.28 | 5612.9 | 2919.3 | 2895.3 | 4223.1 | 1224.2 | 0.67448 | 5.963
2024-12-10 | 3:45 | Data | 0 | 32.798 | 30.658 | 192.102 | 7.64 | 181.068 | 2222.52 | 25.62 | 42.658 | 6.34 | 1.367 | 4.603 | 8630.67 | 1.884 | 98.1 | 77.1 | 1445 | 21.33 | 5609.9 | 2919.8 | 2885.7 | 4224.7 | 1224.2 | 0.6745 | 5.971
2024-12-10 | 3:45 | Data | 0 | 32.791 | 30.88 | 192.057 | 7.64 | 180.933 | 2220.72 | 25.63 | 42.658 | 6.34 | 1.361 | 4.592 | 8621.63 | 1.857 | 98.1 | 77.1 | 1443 | 21.37 | 5604.1 | 2892.8 | 2866.9 | 4188 | 1224.2 | 0.67539 | 5.954
2024-12-10 | 3:45 | Data | 0 | 32.94 | 30.664 | 192.057 | 7.63 | 181.023 | 2218.91 | 25.62 | 42.658 | 6.34 | 1.345 | 4.597 | 8639.71 | 2.289 | 98.1 | 77.4 | 1442 | 21.33 | 5615.8 | 2920.1 | 2827.8 | 4184.3 | 1224.2 | 0.6796 | 5.941
2024-12-10 | 3:45 | Data | 0 | 32.831 | 30.88 | 192.238 | 7.63 | 180.933 | 2217.1 | 25.62 | 42.568 | 6.35 | 1.361 | 4.596 | 8630.67 | 1.85 | 98.1 | 77.2 | 1442 | 21.33 | 5609.9 | 2910.3 | 2851.5 | 4190 | 1224.2 | 0.6782 | 5.957
2024-12-10 | 3:45 | Data | 0 | 32.723 | 30.658 | 192.057 | 7.64 | 180.933 | 2218 | 25.63 | 42.658 | 6.34 | 1.362 | 4.601 | 8635.19 | 2.066 | 98.1 | 77.2 | 1442 | 21.33 | 5612.9 | 2908.4 | 2840.3 | 4182.9 | 1224.2 | 0.67831 | 5.964
2024-12-10 | 3:45 | Data | 0 | 33 | 30.658 | 192.102 | 7.63 | 181.023 | 2218 | 25.62 | 42.658 | 6.35 | 1.372 | 4.586 | 8666.85 | 1.978 | 98.1 | 77 | 1442 | 21.33 | 5633.5 | 2917.1 | 2829.4 | 4176.3 | 1224.2 | 0.68172 | 5.958
2024-12-10 | 3:45 | Data | 0 | 32.582 | 30.766 | 192.012 | 7.64 | 180.933 | 2218 | 25.62 | 42.658 | 6.35 | 1.364 | 4.592 | 8648.76 | 2.019 | 98.1 | 77.1 | 1441 | 21.33 | 5621.7 | 2927.5 | 2877.3 | 4221.1 | 1224.2 | 0.67654 | 5.956
2024-12-10 | 3:45 | Data | 0 | 32.946 | 30.887 | 192.102 | 7.64 | 180.978 | 2216.2 | 25.62 | 42.658 | 6.34 | 1.36 | 4.602 | 8648.76 | 1.951 | 98.1 | 77.2 | 1441 | 21.33 | 5621.7 | 2911.7 | 2845.9 | 4189.3 | 1224.2 | 0.67702 | 5.961
2024-12-10 | 3:46 | Data | 0 | 32.906 | 30.894 | 192.102 | 7.63 | 181.023 | 2210.77 | 25.63 | 42.658 | 6.34 | 1.358 | 4.602 | 8644.24 | 2.046 | 98.1 | 77.2 | 1437 | 21.33 | 5618.8 | 2925.1 | 2861.5 | 4225.2 | 1224.2 | 0.67905 | 5.96
2024-12-10 | 3:46 | Data | 0 | 32.75 | 30.867 | 192.102 | 7.63 | 181.023 | 2227.95 | 25.62 | 42.568 | 6.34 | 1.364 | 4.574 | 8657.8 | 1.911 | 98.1 | 77 | 1448 | 21.33 | 5627.6 | 2926.9 | 2865.5 | 4213.7 | 1224.2 | 0.67738 | 5.938
2024-12-10 | 3:46 | Data | 0 | 32.723 | 30.826 | 192.012 | 7.64 | 180.797 | 2221.62 | 25.62 | 42.658 | 6.34 | 1.357 | 4.576 | 8648.76 | 2.073 | 98.1 | 77.1 | 1445 | 21.33 | 5621.7 | 2930.2 | 2859 | 4211.4 | 1224.2 | 0.68007 | 5.932
2024-12-10 | 3:46 | Data | 0 | 33.257 | 30.914 | 192.283 | 7.63 | 181.068 | 2223.43 | 25.62 | 42.838 | 6.34 | 1.369 | 4.576 | 8644.24 | 1.998 | 98.1 | 77 | 1445 | 21.42 | 5618.8 | 2916.5 | 2859.5 | 4201.8 | 1224.2 | 0.67611 | 5.944
2024-12-10 | 3:46 | Data | 0 | 32.838 | 30.88 | 192.057 | 7.64 | 180.933 | 2222.52 | 25.62 | 42.748 | 6.34 | 1.358 | 4.588 | 8662.33 | 2.025 | 98.1 | 77.2 | 1445 | 21.37 | 5630.5 | 2905.7 | 2850.2 | 4190.9 | 1224.2 | 0.67637 | 5.945
2024-12-10 | 3:46 | Data | 0 | 32.723 | 30.658 | 192.148 | 7.63 | 180.978 | 2222.52 | 25.63 | 42.748 | 6.34 | 1.362 | 4.624 | 8666.85 | 2.066 | 98.1 | 77.2 | 1445 | 21.33 | 5633.5 | 2916.4 | 2826 | 4174.7 | 1224.2 | 0.68192 | 5.986
2024-12-10 | 3:46 | Data | 0 | 32.723 | 30.772 | 192.057 | 7.64 | 180.978 | 2222.52 | 25.62 | 42.297 | 6.34 | 1.359 | 4.594 | 8657.8 | 1.951 | 98.1 | 77.2 | 1444 | 21.1 | 5627.6 | 2937.7 | 2846.5 | 4203.4 | 1224.2 | 0.68188 | 5.954
2024-12-10 | 3:46 | Data | 0 | 32.723 | 30.658 | 192.012 | 7.64 | 181.023 | 2222.52 | 25.62 | 42.477 | 6.34 | 1.363 | 4.61 | 8662.33 | 2.046 | 98.1 | 77.2 | 1445 | 21.28 | 5630.5 | 2924.4 | 2839.1 | 4195.1 | 1224.2 | 0.68036 | 5.972
2024-12-10 | 3:46 | Data | 0 | 32.73 | 30.88 | 192.102 | 7.64 | 180.978 | 2225.23 | 25.63 | 42.206 | 6.34 | 1.36 | 4.582 | 8644.24 | 1.958 | 98.1 | 77.1 | 1446 | 21.15 | 5618.8 | 2908.1 | 2847.4 | 4188.8 | 1224.2 | 0.67619 | 5.942
2024-12-10 | 3:46 | Data | 0 | 33.162 | 30.934 | 192.148 | 7.63 | 181.068 | 2225.23 | 25.62 | 42.658 | 6.34 | 1.357 | 4.589 | 8648.76 | 2.046 | 98.1 | 77.2 | 1446 | 21.33 | 5621.7 | 1829.3 | 2289.6 | 2941.6 | 1224.2 | 0.61957 | 5.946
2024-12-10 | 3:46 | Data | 0 | 32.737 | 30.671 | 192.102 | 7.63 | 181.023 | 2227.95 | 25.62 | 42.658 | 6.34 | 1.36 | 4.592 | 8644.24 | 1.971 | 98.1 | 77.1 | 1448 | 21.33 | 5618.8 | 1831.8 | 2291.2 | 2944.8 | 1224.3 | 0.61926 | 5.952
2024-12-10 | 3:46 | Data | 0 | 33.183 | 30.779 | 192.238 | 7.64 | 181.068 | 2227.95 | 25.62 | 42.929 | 6.34 | 1.357 | 4.597 | 8648.76 | 1.985 | 98.1 | 77.2 | 1448 | 21.42 | 5621.7 | 1829.8 | 2315.7 | 2962.8 | 1224.3 | 0.6147 | 5.952
2024-12-10 | 3:46 | Data | 0 | 32.94 | 30.88 | 192.148 | 7.63 | 181.023 | 2227.95 | 25.63 | 42.658 | 6.35 | 1.365 | 4.596 | 8648.76 | 2.059 | 98.1 | 77.1 | 1448 | 21.37 | 5621.7 | 1827.9 | 2319.4 | 2963.8 | 1224.3 | 0.6143 | 5.96
2024-12-10 | 3:46 | Data | 0 | 32.588 | 30.759 | 192.148 | 7.64 | 180.978 | 2225.23 | 25.63 | 42.658 | 6.34 | 1.358 | 4.604 | 8635.19 | 1.668 | 98.1 | 77.2 | 1446 | 21.33 | 5612.9 | 1833 | 2307.4 | 2956.6 | 1224.3 | 0.61552 | 5.961
2024-12-10 | 3:46 | Data | 0 | 32.568 | 30.658 | 192.012 | 7.63 | 180.978 | 2224.33 | 25.63 | 42.658 | 6.34 | 1.356 | 4.604 | 8635.19 | 1.85 | 98.1 | 77.3 | 1446 | 21.33 | 5612.9 | 1838.3 | 2298.3 | 2952.9 | 1224.3 | 0.62041 | 5.959
2024-12-10 | 3:46 | Data | 0 | 32.642 | 31.076 | 192.102 | 7.64 | 180.978 | 2225.23 | 25.63 | 42.658 | 6.35 | 1.364 | 4.613 | 8617.1 | 1.904 | 98.1 | 77.2 | 1446 | 21.28 | 5601.1 | 1830.4 | 2268.8 | 2927 | 1224.3 | 0.62258 | 5.977
2024-12-10 | 3:46 | Data | 0 | 33.162 | 30.907 | 192.193 | 7.64 | 181.068 | 2225.23 | 25.62 | 42.568 | 6.34 | 1.36 | 4.601 | 8626.15 | 1.985 | 98.1 | 77.2 | 1446 | 21.33 | 5607 | 1825.4 | 2248.3 | 2907.5 | 1224.3 | 0.62493 | 5.96
2024-12-10 | 3:46 | Data | 0 | 32.777 | 30.766 | 192.057 | 7.63 | 181.023 | 2227.95 | 25.63 | 42.658 | 6.34 | 1.358 | 4.601 | 8599.01 | 2.079 | 98.1 | 77.2 | 1448 | 21.33 | 5589.4 | 1835.3 | 2257.4 | 2920.5 | 1224.3 | 0.62631 | 5.959
2024-12-10 | 3:47 | Data | 0 | 32.784 | 30.84 | 192.102 | 7.63 | 181.068 | 2227.95 | 25.61 | 42.658 | 6.34 | 1.355 | 4.614 | 8603.54 | 1.958 | 98.1 | 77.3 | 1448 | 21.33 | 5592.3 | 1851.3 | 2264.4 | 2935.7 | 1224.3 | 0.62694 | 5.969
2024-12-10 | 3:47 | Data | 0 | 32.953 | 30.88 | 192.148 | 7.63 | 180.978 | 2229.75 | 25.63 | 42.658 | 6.34 | 1.36 | 4.616 | 8608.06 | 1.958 | 98.1 | 77.2 | 1449 | 21.33 | 5595.2 | 1840.7 | 2271.1 | 2934.7 | 1224.3 | 0.62475 | 5.975
2024-12-10 | 3:47 | Data | 0 | 32.629 | 30.88 | 192.148 | 7.63 | 181.068 | 2225.23 | 25.62 | 42.658 | 6.34 | 1.36 | 4.603 | 8626.15 | 2.005 | 98.1 | 77.2 | 1446 | 21.28 | 5607 | 1839 | 2265.8 | 2928.5 | 1224.3 | 0.62346 | 5.963
2024-12-10 | 3:47 | Data | 0 | 32.946 | 30.725 | 192.193 | 7.63 | 181.023 | 2231.56 | 25.63 | 42.658 | 6.34 | 1.358 | 4.609 | 8594.49 | 2.221 | 98.1 | 77.2 | 1450 | 21.33 | 5586.4 | 1848 | 2251.8 | 2923.6 | 1224.3 | 0.62978 | 5.966
2024-12-10 | 3:47 | Data | 0 | 32.73 | 30.705 | 192.148 | 7.63 | 180.978 | 2233.37 | 25.63 | 42.658 | 6.34 | 1.366 | 4.598 | 8603.54 | 1.843 | 98.1 | 77.1 | 1451 | 21.33 | 5592.3 | 1824.4 | 2252.8 | 2910.6 | 1224.3 | 0.62419 | 5.963
2024-12-10 | 3:47 | Data | 0 | 32.723 | 30.691 | 191.967 | 7.63 | 180.978 | 2233.37 | 25.62 | 42.658 | 6.34 | 1.364 | 4.577 | 8612.58 | 2.032 | 98.1 | 77 | 1452 | 21.33 | 5598.2 | 1837.5 | 2267.8 | 2930.5 | 1224.3 | 0.62487 | 5.941
2024-12-10 | 3:47 | Data | 0 | 32.825 | 31.137 | 192.102 | 7.63 | 180.842 | 2227.95 | 25.62 | 42.297 | 6.35 | 1.359 | 4.588 | 8599.01 | 2.093 | 98.1 | 77.1 | 1448 | 21.15 | 5589.4 | 1838.9 | 2251.7 | 2917.1 | 1224.3 | 0.62832 | 5.947
2024-12-10 | 3:47 | Data | 0 | 33.135 | 30.934 | 192.238 | 7.64 | 181.068 | 2232.47 | 25.63 | 42.658 | 6.34 | 1.361 | 4.616 | 8630.67 | 1.863 | 98.1 | 77.2 | 1452 | 21.28 | 5609.9 | 1813.2 | 2250.8 | 2901.8 | 1224.3 | 0.62208 | 5.977
2024-12-10 | 3:47 | Data | 0 | 32.953 | 30.88 | 192.148 | 7.64 | 181.068 | 2235.18 | 25.63 | 42.748 | 6.34 | 1.36 | 4.619 | 8635.19 | 1.87 | 98.1 | 77.3 | 1453 | 21.33 | 5612.9 | 1825.7 | 2249.9 | 2909.2 | 1224.3 | 0.62526 | 5.98
2024-12-10 | 3:47 | Data | 0 | 32.94 | 30.88 | 192.012 | 7.64 | 180.978 | 2235.18 | 25.63 | 42.568 | 6.35 | 1.371 | 4.587 | 8648.76 | 2.073 | 98.1 | 77 | 1453 | 21.33 | 5621.7 | 1834.1 | 2262.4 | 2923.9 | 1224.3 | 0.62493 | 5.958
2024-12-10 | 3:47 | Data | 0 | 32.568 | 30.772 | 192.102 | 7.64 | 180.933 | 2236.08 | 25.62 | 42.658 | 6.34 | 1.367 | 4.602 | 8657.8 | 1.843 | 98.1 | 77.1 | 1453 | 21.33 | 5627.6 | 1829.5 | 2273.9 | 2929.3 | 1224.3 | 0.62182 | 5.968
2024-12-10 | 3:47 | Data | 0 | 32.717 | 30.766 | 192.057 | 7.64 | 180.933 | 2236.08 | 25.63 | 42.658 | 6.34 | 1.37 | 4.619 | 8621.63 | 2.073 | 98.1 | 77.1 | 1453 | 21.33 | 5604.1 | 1830.2 | 2256.4 | 2918.3 | 1224.3 | 0.62421 | 5.99
2024-12-10 | 3:47 | Data | 0 | 32.339 | 30.597 | 192.102 | 7.64 | 180.842 | 2236.08 | 25.63 | 42.658 | 6.34 | 1.362 | 4.618 | 8639.71 | 1.789 | 98.1 | 77.2 | 1453 | 21.33 | 5615.8 | 1847.9 | 2292 | 2960.9 | 1224.3 | 0.61953 | 5.98
2024-12-10 | 3:47 | Data | 0 | 32.777 | 30.88 | 192.148 | 7.64 | 180.933 | 2236.08 | 25.63 | 42.387 | 6.34 | 1.36 | 4.605 | 8657.8 | 1.89 | 98.1 | 77.2 | 1453 | 21.19 | 5627.6 | 1833.3 | 2303.6 | 2954.7 | 1224.3 | 0.61804 | 5.965
2024-12-10 | 3:47 | Data | 0 | 32.94 | 30.658 | 192.102 | 7.64 | 180.978 | 2238.79 | 25.62 | 42.297 | 6.34 | 1.346 | 4.6 | 8621.63 | 2.113 | 98.1 | 77.4 | 1455 | 21.15 | 5604.1 | 1829.6 | 2316 | 2962.3 | 1224.3 | 0.61464 | 5.946
2024-12-10 | 3:47 | Data | 0 | 32.838 | 30.671 | 191.967 | 7.64 | 181.023 | 2236.08 | 25.63 | 42.297 | 6.35 | 1.357 | 4.621 | 8635.19 | 2.059 | 98.1 | 77.3 | 1453 | 21.15 | 5612.9 | 1819.4 | 2298.8 | 2943.4 | 1224.3 | 0.61567 | 5.977
2024-12-10 | 3:47 | Data | 0 | 32.723 | 30.766 | 191.921 | 7.64 | 180.842 | 2236.08 | 25.63 | 42.387 | 6.34 | 1.354 | 4.601 | 8630.67 | 2.073 | 98.1 | 77.3 | 1453 | 21.24 | 5609.9 | 1824.3 | 2310 | 2954.1 | 1224.3 | 0.61753 | 5.955
2024-12-10 | 3:48 | Data | 0 | 32.75 | 30.685 | 192.057 | 7.64 | 181.023 | 2235.18 | 25.62 | 42.387 | 6.35 | 1.356 | 4.6 | 8635.19 | 2.046 | 98.1 | 77.2 | 1453 | 21.19 | 5612.9 | 1810.6 | 2291 | 2931.5 | 1224.3 | 0.61923 | 5.956
2024-12-10 | 3:48 | Data | 0 | 32.892 | 30.786 | 192.057 | 7.64 | 180.933 | 2235.18 | 25.62 | 42.477 | 6.34 | 1.36 | 4.588 | 8630.67 | 2.019 | 98.1 | 77.1 | 1453 | 21.19 | 5609.9 | 1837.7 | 2298.4 | 2952.8 | 1224.3 | 0.61973 | 5.95
2024-12-10 | 3:48 | Data | 0 | 32.723 | 30.766 | 192.057 | 7.64 | 180.978 | 2235.18 | 25.62 | 42.297 | 6.34 | 1.367 | 4.575 | 8630.67 | 2.073 | 98.1 | 77 | 1453 | 21.15 | 5609.9 | 1827.3 | 2290.5 | 2941.1 | 1224.3 | 0.61881 | 5.941
2024-12-10 | 3:48 | Data | 0 | 32.717 | 30.853 | 192.012 | 7.64 | 180.978 | 2235.18 | 25.62 | 42.387 | 6.34 | 1.36 | 4.587 | 8644.24 | 2.059 | 98.1 | 77.1 | 1452 | 21.19 | 5618.8 | 1838 | 2272.3 | 2932 | 1224.3 | 0.62479 | 5.946
2024-12-10 | 3:48 | Data | 0 | 32.528 | 30.651 | 192.102 | 7.64 | 180.978 | 2227.95 | 25.63 | 42.387 | 6.34 | 1.37 | 4.563 | 8680.41 | 1.85 | 98.1 | 76.9 | 1448 | 21.19 | 5642.3 | 1830.4 | 2250.6 | 2913.6 | 1224.3 | 0.62531 | 5.932
2024-12-10 | 3:48 | Data | 0 | 32.494 | 30.644 | 191.876 | 7.64 | 180.842 | 2232.47 | 25.62 | 42.387 | 6.34 | 1.367 | 4.565 | 8662.33 | 1.857 | 98.1 | 77 | 1451 | 21.24 | 5630.5 | 1834.6 | 2258.9 | 2920.6 | 1224.3 | 0.62584 | 5.931
2024-12-10 | 3:48 | Data | 0 | 32.494 | 30.671 | 191.876 | 7.63 | 180.797 | 2233.37 | 25.63 | 42.387 | 6.34 | 1.361 | 4.563 | 8666.85 | 1.971 | 98.1 | 77 | 1451 | 21.19 | 5633.5 | 1829.7 | 2253.9 | 2913.4 | 1224.3 | 0.62555 | 5.924
2024-12-10 | 3:48 | Data | 0 | 32.723 | 30.475 | 192.012 | 7.63 | 180.842 | 2283.08 | 25.62 | 42.387 | 6.34 | 1.357 | 4.586 | 8662.33 | 1.985 | 98.1 | 77.2 | 1484 | 21.15 | 5630.5 | 1831.8 | 2277.7 | 2934.8 | 1224.3 | 0.62137 | 5.943
2024-12-10 | 3:48 | Data | 0 | 32.717 | 30.853 | 192.057 | 7.63 | 180.933 | 2280.37 | 25.62 | 42.387 | 6.34 | 1.358 | 4.57 | 8666.85 | 2.086 | 98.1 | 77.1 | 1482 | 21.19 | 5633.5 | 1828.3 | 2272.3 | 2929.9 | 1224.3 | 0.61898 | 5.928
2024-12-10 | 3:48 | Data | 0 | 32.669 | 30.651 | 191.967 | 7.64 | 180.933 | 2280.37 | 25.62 | 42.297 | 6.34 | 1.36 | 4.593 | 8662.33 | 2.066 | 98.1 | 77.1 | 1482 | 21.15 | 5630.5 | 1841.7 | 2260.4 | 2927.4 | 1224.3 | 0.62638 | 5.954
2024-12-10 | 3:48 | Data | 0 | 32.777 | 30.651 | 192.102 | 7.63 | 180.978 | 2283.08 | 25.62 | 42.387 | 6.34 | 1.361 | 4.607 | 8657.8 | 1.87 | 98.1 | 77.2 | 1484 | 21.24 | 5627.6 | 1842.1 | 2280.4 | 2943.8 | 1224.3 | 0.62331 | 5.968
2024-12-10 | 3:48 | Data | 0 | 32.831 | 30.813 | 192.057 | 7.64 | 180.978 | 2229.75 | 25.63 | 42.568 | 6.34 | 1.359 | 4.596 | 8648.76 | 2.073 | 98.1 | 77.2 | 1449 | 21.28 | 5621.7 | 1831.5 | 2259.9 | 2921.1 | 1224.3 | 0.62401 | 5.955
2024-12-10 | 3:48 | Data | 0 | 32.501 | 30.651 | 191.921 | 7.63 | 180.933 | 2229.75 | 25.63 | 42.568 | 6.34 | 1.365 | 4.61 | 8648.76 | 1.958 | 98.1 | 77.2 | 1450 | 21.33 | 5621.7 | 1823.7 | 2273.2 | 2925.5 | 1224.3 | 0.62063 | 5.976
2024-12-10 | 3:48 | Data | 0 | 32.514 | 30.651 | 191.967 | 7.64 | 180.933 | 2230.66 | 25.63 | 42.658 | 6.34 | 1.363 | 4.609 | 8648.76 | 1.85 | 98.1 | 77.2 | 1449 | 21.33 | 5621.7 | 1822.2 | 2265.6 | 2918.6 | 1224.3 | 0.62165 | 5.972
2024-12-10 | 3:48 | Data | 0 | 32.669 | 30.867 | 192.057 | 7.64 | 180.842 | 2230.66 | 25.62 | 42.387 | 6.34 | 1.355 | 4.586 | 8644.24 | 1.998 | 98.1 | 77.2 | 1450 | 21.24 | 5618.8 | 1838.5 | 2287.6 | 2945.7 | 1224.3 | 0.62147 | 5.941
2024-12-10 | 3:48 | Data | 0 | 32.717 | 30.448 | 191.967 | 7.63 | 180.842 | 2232.47 | 25.62 | 42.658 | 6.34 | 1.369 | 4.589 | 8630.67 | 2.059 | 98.1 | 77 | 1451 | 21.33 | 5609.9 | 1827.6 | 2245.6 | 2905.7 | 1224.3 | 0.62622 | 5.959
2024-12-10 | 3:48 | Data | 0 | 33.054 | 30.671 | 192.102 | 7.64 | 180.978 | 2233.37 | 25.62 | 42.658 | 6.34 | 1.361 | 4.593 | 8648.76 | 2.093 | 98.1 | 77.1 | 1451 | 21.33 | 5621.7 | 1828.9 | 2266.1 | 2922.2 | 1224.3 | 0.62338 | 5.954
2024-12-10 | 3:48 | Data | 0 | 32.723 | 30.536 | 192.057 | 7.63 | 180.933 | 2231.56 | 25.63 | 42.658 | 6.35 | 1.363 | 4.593 | 8639.71 | 2.066 | 98.1 | 77.1 | 1451 | 21.28 | 5615.8 | 1830.3 | 2254.3 | 2913.1 | 1224.3 | 0.6257 | 5.956
2024-12-10 | 3:49 | Data | 0 | 32.642 | 30.428 | 192.193 | 7.63 | 181.023 | 2232.47 | 25.62 | 42.658 | 6.34 | 1.358 | 4.557 | 8626.15 | 2.106 | 98.1 | 77 | 1452 | 21.37 | 5607 | 1825.9 | 2275.2 | 2929.4 | 1224.3 | 0.62066 | 5.915
2024-12-10 | 3:49 | Data | 0 | 32.636 | 30.907 | 191.921 | 7.64 | 180.933 | 2233.37 | 25.62 | 42.658 | 6.34 | 1.361 | 4.587 | 8680.41 | 2.079 | 98.1 | 77.1 | 1452 | 21.33 | 5642.3 | 1838.2 | 2282.8 | 2942.8 | 1224.3 | 0.62232 | 5.948
2024-12-10 | 3:49 | Data | 0 | 32.582 | 30.826 | 191.967 | 7.64 | 180.933 | 2233.37 | 25.62 | 42.658 | 6.34 | 1.364 | 4.605 | 8680.41 | 1.857 | 98.1 | 77.2 | 1451 | 21.33 | 5642.3 | 1844.4 | 2275.6 | 2942.3 | 1224.3 | 0.62488 | 5.968
2024-12-10 | 3:49 | Data | 0 | 33.054 | 30.84 | 191.967 | 7.64 | 180.978 | 2233.37 | 25.63 | 42.658 | 6.34 | 1.361 | 4.592 | 8680.41 | 2.208 | 98.1 | 77.1 | 1452 | 21.33 | 5642.3 | 1842.7 | 2281.9 | 2945.5 | 1224.3 | 0.62315 | 5.953
2024-12-10 | 3:49 | Data | 0 | 32.501 | 30.739 | 192.012 | 7.63 | 180.797 | 2236.08 | 25.62 | 42.658 | 6.34 | 1.356 | 4.602 | 8698.5 | 2.079 | 98.1 | 77.3 | 1452 | 21.33 | 5654 | 1834.7 | 2281.4 | 2938.8 | 1224.3 | 0.62202 | 5.956
2024-12-10 | 3:49 | Data | 0 | 32.723 | 30.651 | 191.876 | 7.64 | 180.933 | 2233.37 | 25.63 | 42.658 | 6.34 | 1.367 | 4.594 | 8662.33 | 1.87 | 98.1 | 77.1 | 1452 | 21.33 | 5630.5 | 1847 | 2281.1 | 2948.1 | 1224.3 | 0.62394 | 5.96
2024-12-10 | 3:49 | Data | 0 | 32.946 | 30.88 | 192.148 | 7.63 | 180.842 | 2235.18 | 25.62 | 42.568 | 6.34 | 1.367 | 4.587 | 8648.76 | 2.052 | 98.1 | 77 | 1453 | 21.28 | 5621.7 | 1839.4 | 2280.1 | 2939.4 | 1224.3 | 0.62295 | 5.954
2024-12-10 | 3:49 | Data | 0 | 32.501 | 30.415 | 191.921 | 7.64 | 180.797 | 2235.18 | 25.62 | 42.206 | 6.34 | 1.357 | 4.598 | 8648.76 | 2.073 | 98.1 | 77.2 | 1453 | 21.06 | 5621.7 | 1845.4 | 2295.8 | 2958.9 | 1224.3 | 0.62113 | 5.957
2024-12-10 | 3:49 | Data | 0 | 32.717 | 30.421 | 191.921 | 7.64 | 180.752 | 2236.08 | 25.63 | 42.658 | 6.34 | 1.354 | 4.602 | 8662.33 | 2.086 | 98.1 | 77.3 | 1453 | 21.37 | 5630.5 | 2942.4 | 2871.4 | 4217.9 | 1224.3 | 0.67966 | 5.956
2024-12-10 | 3:49 | Data | 0 | 32.649 | 30.482 | 191.967 | 7.64 | 180.842 | 2233.37 | 25.62 | 42.748 | 6.35 | 1.357 | 4.585 | 8648.76 | 1.89 | 98.1 | 77.2 | 1452 | 21.37 | 5621.7 | 2935.6 | 2858.1 | 4217.7 | 1224.3 | 0.67853 | 5.941
2024-12-10 | 3:49 | Data | 0 | 32.737 | 30.651 | 191.967 | 7.64 | 180.933 | 2232.47 | 25.62 | 42.658 | 6.35 | 1.359 | 4.597 | 8648.76 | 1.958 | 98.1 | 77.2 | 1452 | 21.33 | 5621.7 | 2926.7 | 2850.1 | 4211.8 | 1224.3 | 0.67616 | 5.956
2024-12-10 | 3:49 | Data | 0 | 32.892 | 30.718 | 191.921 | 7.63 | 180.797 | 2232.47 | 25.63 | 42.658 | 6.35 | 1.369 | 4.605 | 8657.8 | 2.16 | 98.1 | 77.1 | 1452 | 21.28 | 5627.6 | 2953.2 | 2855 | 4228.5 | 1224.3 | 0.67698 | 5.974
2024-12-10 | 3:49 | Data | 0 | 32.723 | 30.651 | 191.831 | 7.64 | 180.842 | 2232.47 | 25.63 | 42.568 | 6.34 | 1.361 | 4.571 | 8635.19 | 1.897 | 98.1 | 77 | 1451 | 21.33 | 5612.9 | 2937.8 | 2851.5 | 4210.1 | 1224.4 | 0.6805 | 5.933
2024-12-10 | 3:49 | Data | 0 | 32.494 | 30.415 | 191.876 | 7.64 | 180.752 | 2232.47 | 25.63 | 42.658 | 6.34 | 1.366 | 4.597 | 8626.15 | 2.255 | 98.1 | 77.1 | 1451 | 21.28 | 5607 | 2931.7 | 2859.8 | 4224.1 | 1224.4 | 0.6771 | 5.962
2024-12-10 | 3:49 | Data | 0 | 32.501 | 30.637 | 191.876 | 7.64 | 180.752 | 2229.75 | 25.62 | 42.658 | 6.34 | 1.367 | 4.605 | 8617.1 | 1.897 | 98.1 | 77.1 | 1449 | 21.33 | 5601.1 | 2946.3 | 2858.3 | 4223.1 | 1224.4 | 0.67982 | 5.971
2024-12-10 | 3:49 | Data | 0 | 32.919 | 30.921 | 192.012 | 7.64 | 180.842 | 2230.66 | 25.63 | 42.658 | 6.35 | 1.362 | 4.581 | 8608.06 | 1.985 | 98.1 | 77.1 | 1450 | 21.33 | 5595.2 | 2942.4 | 2874.6 | 4234.5 | 1224.4 | 0.67692 | 5.943
2024-12-10 | 3:49 | Data | 0 | 32.595 | 30.867 | 192.012 | 7.64 | 180.842 | 2227.95 | 25.62 | 42.748 | 6.34 | 1.357 | 4.593 | 8608.06 | 1.951 | 98.1 | 77.2 | 1449 | 21.37 | 5595.2 | 2934.9 | 2875.3 | 4230.9 | 1224.4 | 0.67637 | 5.95
2024-12-10 | 3:49 | Data | 0 | 32.494 | 30.415 | 191.876 | 7.64 | 180.752 | 2227.04 | 25.61 | 42.658 | 6.34 | 1.357 | 4.6 | 8603.54 | 2.079 | 98.1 | 77.2 | 1448 | 21.33 | 5592.3 | 2946.9 | 2880.4 | 4239.5 | 1224.4 | 0.67852 | 5.958
2024-12-10 | 3:50 | Data | 0 | 32.406 | 30.536 | 191.967 | 7.64 | 180.662 | 2227.95 | 25.62 | 42.658 | 6.34 | 1.36 | 4.578 | 8608.06 | 1.917 | 98.1 | 77.1 | 1448 | 21.28 | 5595.2 | 2950 | 2866.4 | 4226.9 | 1224.4 | 0.68036 | 5.938
2024-12-10 | 3:50 | Data | 0 | 32.615 | 30.651 | 192.012 | 7.63 | 180.842 | 2227.04 | 25.61 | 42.658 | 6.35 | 1.355 | 4.561 | 8608.06 | 1.857 | 98.1 | 77.1 | 1448 | 21.37 | 5595.2 | 2954.5 | 2870.6 | 4235.3 | 1224.4 | 0.68084 | 5.916
2024-12-10 | 3:50 | Data | 0 | 32.494 | 30.536 | 191.967 | 7.64 | 180.752 | 2226.14 | 25.61 | 42.658 | 6.34 | 1.358 | 4.565 | 8608.06 | 2.073 | 98.1 | 77.1 | 1447 | 21.33 | 5595.2 | 2953.2 | 2854.2 | 4227.2 | 1224.4 | 0.68032 | 5.922
2024-12-10 | 3:50 | Data | 0 | 32.777 | 30.658 | 192.012 | 7.64 | 180.933 | 2222.52 | 25.61 | 42.658 | 6.35 | 1.349 | 4.565 | 8784.42 | 2.073 | 98.1 | 77.2 | 1445 | 21.33 | 5709.9 | 2937 | 2866.2 | 4227.6 | 1224.4 | 0.67565 | 5.914
2024-12-10 | 3:50 | Data | 0 | 32.771 | 30.664 | 191.967 | 7.64 | 180.842 | 2225.23 | 25.61 | 42.387 | 6.35 | 1.357 | 4.588 | 8797.99 | 1.89 | 98.1 | 77.2 | 1446 | 21.19 | 5718.7 | 2947.9 | 2850.6 | 4220.4 | 1224.4 | 0.68103 | 5.943
2024-12-10 | 3:50 | Data | 0 | 32.663 | 30.847 | 192.057 | 7.64 | 180.933 | 2225.23 | 25.61 | 42.568 | 6.34 | 1.363 | 4.588 | 8802.51 | 2.073 | 98.1 | 77.1 | 1446 | 21.33 | 5721.6 | 2960.4 | 2866.1 | 4239.6 | 1224.4 | 0.68089 | 5.951
2024-12-10 | 3:50 | Data | 0 | 32.609 | 30.651 | 191.921 | 7.64 | 180.797 | 2224.33 | 25.61 | 42.658 | 6.34 | 1.362 | 4.594 | 8807.04 | 1.944 | 98.1 | 77.1 | 1446 | 21.33 | 5724.6 | 2952.3 | 2869.6 | 4238.9 | 1224.4 | 0.6792 | 5.957
2024-12-10 | 3:50 | Data | 0 | 32.588 | 30.59 | 192.012 | 7.63 | 180.933 | 2225.23 | 25.61 | 42.206 | 6.34 | 1.372 | 4.596 | 8671.37 | 1.911 | 98.1 | 77 | 1446 | 21.06 | 5636.4 | 2950.5 | 2844.2 | 4219.1 | 1224.4 | 0.68286 | 5.968
2024-12-10 | 3:50 | Data | 0 | 32.271 | 30.536 | 191.921 | 7.64 | 180.797 | 2225.23 | 25.61 | 42.658 | 6.34 | 1.361 | 4.561 | 8621.63 | 1.998 | 98.1 | 77 | 1446 | 21.33 | 5604.1 | 2943.8 | 2870.8 | 4233.8 | 1224.4 | 0.67733 | 5.923
2024-12-10 | 3:50 | Data | 0 | 32.494 | 30.624 | 192.148 | 7.63 | 181.068 | 2227.95 | 25.61 | 42.658 | 6.34 | 1.367 | 4.572 | 8626.15 | 1.958 | 98.1 | 77 | 1448 | 21.33 | 5607 | 2959.9 | 2892.2 | 4256.4 | 1224.4 | 0.67956 | 5.939
2024-12-10 | 3:50 | Data | 0 | 32.75 | 30.651 | 192.283 | 7.64 | 181.114 | 2230.66 | 25.62 | 42.658 | 6.35 | 1.354 | 4.582 | 8630.67 | 1.85 | 98.1 | 77.2 | 1450 | 21.33 | 5609.9 | 2881 | 2875.3 | 4183.9 | 1224.4 | 0.67239 | 5.936
2024-12-10 | 3:50 | Data | 0 | 32.973 | 30.82 | 192.374 | 7.64 | 181.249 | 2230.66 | 25.62 | 42.658 | 6.35 | 1.363 | 4.588 | 8603.54 | 2.12 | 98.1 | 77.1 | 1450 | 21.33 | 5592.3 | 2862.3 | 2859.7 | 4165.3 | 1224.4 | 0.671 | 5.95
2024-12-10 | 3:50 | Data | 0 | 32.501 | 30.853 | 192.148 | 7.64 | 181.204 | 2233.37 | 25.62 | 42.568 | 6.35 | 1.365 | 4.584 | 8580.93 | 1.728 | 98.1 | 77.1 | 1452 | 21.28 | 5577.6 | 2857.1 | 2848.2 | 4151.1 | 1224.4 | 0.67129 | 5.95
2024-12-10 | 3:50 | Data | 0 | 32.71 | 30.651 | 192.238 | 7.64 | 181.114 | 2233.37 | 25.62 | 42.568 | 6.35 | 1.359 | 4.585 | 8594.49 | 2.073 | 98.1 | 77.1 | 1451 | 21.33 | 5586.4 | 2869.2 | 2845.5 | 4156.8 | 1224.4 | 0.6746 | 5.943
2024-12-10 | 3:50 | Data | 0 | 32.501 | 30.536 | 192.283 | 7.63 | 181.204 | 2236.08 | 25.62 | 42.568 | 6.34 | 1.363 | 4.587 | 8612.58 | 2.066 | 98.1 | 77.1 | 1453 | 21.28 | 5598.2 | 2885.1 | 2850.8 | 4169.9 | 1224.4 | 0.67419 | 5.95
2024-12-10 | 3:50 | Data | 0 | 32.825 | 30.536 | 192.329 | 7.64 | 181.114 | 2236.08 | 25.61 | 42.748 | 6.34 | 1.369 | 4.609 | 8617.1 | 2.066 | 98.1 | 77.1 | 1453 | 21.33 | 5601.1 | 2861.2 | 2831.3 | 4155.9 | 1224.4 | 0.67628 | 5.978
2024-12-10 | 3:50 | Data | 0 | 32.717 | 30.597 | 192.148 | 7.63 | 181.068 | 2235.18 | 25.61 | 42.658 | 6.34 | 1.366 | 4.621 | 8626.15 | 1.857 | 98.1 | 77.2 | 1453 | 21.33 | 5607 | 2874.3 | 2864.6 | 4172.7 | 1224.4 | 0.67191 | 5.987
2024-12-10 | 3:50 | Data | 0 | 32.885 | 30.88 | 192.329 | 7.64 | 181.249 | 2235.18 | 25.61 | 42.748 | 6.35 | 1.363 | 4.599 | 8648.76 | 2.046 | 98.1 | 77.1 | 1453 | 21.33 | 5621.7 | 2888.1 | 2847.3 | 4168.7 | 1224.4 | 0.6766 | 5.963
2024-12-10 | 3:51 | Data | 0 | 32.332 | 30.624 | 192.193 | 7.63 | 181.114 | 2233.37 | 25.61 | 42.658 | 6.34 | 1.359 | 4.607 | 8635.19 | 1.735 | 98.1 | 77.2 | 1451 | 21.37 | 5612.9 | 2936.6 | 2861.2 | 4218.5 | 1224.4 | 0.68112 | 5.966
2024-12-10 | 3:51 | Data | 0 | 32.528 | 30.421 | 192.283 | 7.64 | 181.068 | 2236.08 | 25.61 | 42.658 | 6.34 | 1.361 | 4.578 | 8635.19 | 1.965 | 98.1 | 77.1 | 1453 | 21.33 | 5612.9 | 2926.4 | 2861.6 | 4205 | 1224.4 | 0.67875 | 5.939
2024-12-10 | 3:51 | Data | 0 | 32.71 | 30.651 | 192.329 | 7.64 | 181.159 | 2232.47 | 25.61 | 42.658 | 6.34 | 1.365 | 4.592 | 8644.24 | 2.066 | 98.1 | 77.1 | 1451 | 21.33 | 5618.8 | 2923.7 | 2881.5 | 4223.9 | 1224.4 | 0.67514 | 5.956
2024-12-10 | 3:51 | Data | 0 | 32.879 | 30.678 | 192.329 | 7.64 | 181.249 | 2232.47 | 25.61 | 42.658 | 6.35 | 1.363 | 4.585 | 8630.67 | 2.16 | 98.1 | 77.1 | 1451 | 21.33 | 5609.9 | 2931.1 | 2868.1 | 4217.2 | 1224.4 | 0.6774 | 5.948
2024-12-10 | 3:51 | Data | 0 | 32.501 | 30.874 | 192.283 | 7.64 | 181.204 | 2233.37 | 25.61 | 42.658 | 6.35 | 1.363 | 4.624 | 8626.15 | 1.762 | 98.1 | 77.2 | 1452 | 21.33 | 5607 | 2932.9 | 2845 | 4205.3 | 1224.4 | 0.68098 | 5.987
2024-12-10 | 3:51 | Data | 0 | 32.507 | 30.86 | 192.329 | 7.64 | 181.204 | 2236.08 | 25.62 | 42.658 | 6.34 | 1.361 | 4.621 | 8621.63 | 1.884 | 98.1 | 77.2 | 1453 | 21.33 | 5604.1 | 2922.4 | 2849.9 | 4203 | 1224.4 | 0.67766 | 5.981
2024-12-10 | 3:51 | Data | 0 | 32.507 | 30.415 | 192.283 | 7.63 | 181.114 | 2233.37 | 25.61 | 42.748 | 6.34 | 1.354 | 4.594 | 8617.1 | 1.911 | 98.1 | 77.2 | 1452 | 21.33 | 5601.1 | 2932.4 | 2852.2 | 4209.3 | 1224.4 | 0.6786 | 5.948
2024-12-10 | 3:51 | Data | 0 | 32.541 | 30.415 | 192.148 | 7.64 | 181.023 | 2233.37 | 25.61 | 42.658 | 6.34 | 1.356 | 4.57 | 8612.58 | 2.086 | 98.1 | 77.1 | 1452 | 21.33 | 5598.2 | 2945.9 | 2841.9 | 4205.7 | 1224.4 | 0.68291 | 5.925
2024-12-10 | 3:51 | Data | 0 | 32.669 | 30.536 | 192.329 | 7.63 | 181.204 | 2235.18 | 25.61 | 42.477 | 6.34 | 1.348 | 4.577 | 8612.58 | 2.066 | 98.1 | 77.2 | 1453 | 21.19 | 5598.2 | 2922.6 | 2835.1 | 4189.9 | 1224.4 | 0.67931 | 5.925
2024-12-10 | 3:51 | Data | 0 | 32.48 | 30.415 | 192.193 | 7.63 | 181.023 | 2233.37 | 25.61 | 42.387 | 6.34 | 1.36 | 4.604 | 8603.54 | 2.073 | 98.1 | 77.2 | 1452 | 21.15 | 5592.3 | 2935.8 | 2869.9 | 4223.9 | 1224.4 | 0.67642 | 5.966
2024-12-10 | 3:51 | Data | 0 | 32.447 | 30.644 | 192.148 | 7.63 | 181.114 | 2234.27 | 25.61 | 42.387 | 6.34 | 1.367 | 4.605 | 8608.06 | 1.85 | 98.1 | 77.1 | 1453 | 21.19 | 5595.2 | 2932.9 | 2844.2 | 4204 | 1224.4 | 0.6796 | 5.97
2024-12-10 | 3:51 | Data | 0 | 32.825 | 30.86 | 192.329 | 7.64 | 181.159 | 2238.79 | 25.61 | 42.387 | 6.34 | 1.355 | 4.603 | 8576.4 | 2.046 | 98.1 | 77.3 | 1455 | 21.15 | 5574.7 | 2929.2 | 2878.6 | 4224 | 1224.4 | 0.67679 | 5.957
2024-12-10 | 3:51 | Data | 0 | 32.602 | 30.84 | 192.193 | 7.63 | 181.114 | 2235.18 | 25.61 | 42.477 | 6.34 | 1.36 | 4.593 | 8603.54 | 1.897 | 98.1 | 77.2 | 1453 | 21.24 | 5592.3 | 2923.7 | 2870.5 | 4222.8 | 1224.5 | 0.67499 | 5.953
2024-12-10 | 3:51 | Data | 0 | 32.933 | 30.482 | 192.238 | 7.64 | 181.159 | 2234.27 | 25.61 | 42.477 | 6.35 | 1.358 | 4.598 | 8608.06 | 2.154 | 98.1 | 77.2 | 1452 | 21.19 | 5595.2 | 2943.6 | 2873.9 | 4227.3 | 1224.5 | 0.6789 | 5.956
2024-12-10 | 3:51 | Data | 0 | 32.696 | 30.698 | 192.193 | 7.64 | 181.159 | 2233.37 | 25.61 | 42.387 | 6.34 | 1.365 | 4.607 | 8612.58 | 1.971 | 98.1 | 77.1 | 1452 | 21.19 | 5598.2 | 2932.4 | 2868.7 | 4219.9 | 1224.5 | 0.67719 | 5.972
2024-12-10 | 3:51 | Data | 0 | 32.42 | 30.428 | 192.148 | 7.64 | 181.159 | 2232.47 | 25.61 | 42.387 | 6.34 | 1.36 | 4.588 | 8612.58 | 1.877 | 98.1 | 77.1 | 1451 | 21.24 | 5598.2 | 2920.6 | 2866.2 | 4210.7 | 1224.5 | 0.6763 | 5.948
2024-12-10 | 3:51 | Data | 0 | 32.723 | 30.205 | 192.238 | 7.64 | 181.159 | 2227.95 | 25.61 | 42.387 | 6.35 | 1.367 | 4.587 | 8603.54 | 2.1 | 98.1 | 77 | 1448 | 21.24 | 5592.3 | 2938.4 | 2858.1 | 4215.9 | 1224.5 | 0.67949 | 5.954
2024-12-10 | 3:52 | Data | 0 | 32.494 | 30.415 | 192.148 | 7.64 | 181.023 | 2223.43 | 25.61 | 42.387 | 6.34 | 1.37 | 4.564 | 8603.54 | 1.877 | 98.1 | 76.9 | 1445 | 21.19 | 5592.3 | 2946.5 | 2877 | 4233.4 | 1224.5 | 0.67788 | 5.934
2024-12-10 | 3:52 | Data | 0 | 32.372 | 30.577 | 192.148 | 7.64 | 181.114 | 2227.04 | 25.61 | 42.387 | 6.35 | 1.366 | 4.557 | 8617.1 | 1.917 | 98.1 | 76.9 | 1448 | 21.19 | 5601.1 | 2937.1 | 2834.8 | 4198.2 | 1224.5 | 0.67709 | 5.922
2024-12-10 | 3:52 | Data | 0 | 32.467 | 30.428 | 192.329 | 7.63 | 181.114 | 2226.14 | 25.61 | 42.387 | 6.35 | 1.358 | 4.617 | 8621.63 | 2.154 | 98.1 | 77.3 | 1447 | 21.19 | 5604.1 | 2919.7 | 2855.4 | 4203.1 | 1224.5 | 0.67722 | 5.975
2024-12-10 | 3:52 | Data | 0 | 32.717 | 30.556 | 192.329 | 7.63 | 181.204 | 2224.33 | 25.61 | 42.387 | 6.35 | 1.361 | 4.612 | 8621.63 | 1.87 | 98.1 | 77.2 | 1446 | 21.19 | 5604.1 | 2938.7 | 2845.2 | 4208.4 | 1224.5 | 0.68125 | 5.974
2024-12-10 | 3:52 | Data | 0 | 32.271 | 30.198 | 192.283 | 7.63 | 181.159 | 2225.23 | 25.61 | 42.387 | 6.35 | 1.371 | 4.609 | 8626.15 | 2.052 | 98.1 | 77.1 | 1446 | 21.19 | 5607 | 2920.3 | 2844.4 | 4193 | 1224.5 | 0.6791 | 5.98
2024-12-10 | 3:52 | Data | 0 | 32.494 | 30.597 | 192.283 | 7.64 | 181.159 | 2229.75 | 25.61 | 42.387 | 6.35 | 1.363 | 4.598 | 8608.06 | 2.032 | 98.1 | 77.1 | 1449 | 21.19 | 5595.2 | 2919.1 | 2871.8 | 4210.3 | 1224.5 | 0.67523 | 5.961
2024-12-10 | 3:52 | Data | 0 | 32.582 | 30.651 | 192.374 | 7.64 | 181.159 | 2225.23 | 25.62 | 42.387 | 6.34 | 1.346 | 4.617 | 8594.49 | 2.16 | 98.1 | 77.4 | 1446 | 21.15 | 5586.4 | 2922.3 | 2850.3 | 4201.4 | 1224.5 | 0.67823 | 5.963
2024-12-10 | 3:52 | Data | 0 | 32.494 | 30.84 | 192.148 | 7.63 | 181.204 | 2227.95 | 25.62 | 42.297 | 6.35 | 1.348 | 4.622 | 8608.06 | 1.904 | 98.1 | 77.4 | 1448 | 21.19 | 5595.2 | 2923.2 | 2850.1 | 4200.7 | 1224.5 | 0.67956 | 5.969
2024-12-10 | 3:52 | Data | 0 | 32.494 | 30.536 | 192.283 | 7.64 | 181.204 | 2230.66 | 25.62 | 42.387 | 6.35 | 1.363 | 4.603 | 8603.54 | 1.958 | 98.1 | 77.2 | 1449 | 21.24 | 5592.3 | 2911.7 | 2841 | 4183.8 | 1224.5 | 0.6782 | 5.966
2024-12-10 | 3:52 | Data | 0 | 32.44 | 30.415 | 192.148 | 7.64 | 181.114 | 2225.23 | 25.62 | 42.387 | 6.35 | 1.365 | 4.598 | 8608.06 | 2.066 | 98.1 | 77.1 | 1446 | 21.19 | 5595.2 | 2905.9 | 2869.2 | 4212.5 | 1224.5 | 0.6782 | 5.963
2024-12-10 | 3:52 | Data | 0 | 32.494 | 30.198 | 192.193 | 7.64 | 181.114 | 2229.75 | 25.62 | 42.387 | 6.35 | 1.364 | 4.582 | 8599.01 | 2.079 | 98.1 | 77.1 | 1449 | 21.19 | 5589.4 | 2929.5 | 2886.1 | 4228.7 | 1224.5 | 0.67345 | 5.947
2024-12-10 | 3:52 | Data | 0 | 32.609 | 30.421 | 192.238 | 7.63 | 181.204 | 2230.66 | 25.65 | 42.387 | 6.35 | 1.37 | 4.586 | 8608.06 | 1.938 | 98.1 | 77 | 1450 | 21.19 | 5595.2 | 2921.3 | 2877.4 | 4219.8 | 1224.5 | 0.67451 | 5.956
2024-12-10 | 3:52 | Data | 0 | 32.44 | 30.644 | 192.238 | 7.64 | 181.159 | 2230.66 | 25.64 | 42.387 | 6.34 | 1.363 | 4.601 | 8599.01 | 2.046 | 98.1 | 77.1 | 1449 | 21.19 | 5589.4 | 2917.9 | 2877.3 | 4215.4 | 1224.5 | 0.67463 | 5.964
2024-12-10 | 3:52 | Data | 0 | 32.44 | 30.529 | 192.238 | 7.63 | 181.114 | 2230.66 | 25.64 | 42.387 | 6.35 | 1.367 | 4.609 | 8612.58 | 2.127 | 98.1 | 77.1 | 1450 | 21.19 | 5598.2 | 2933.4 | 2864.3 | 4215.3 | 1224.5 | 0.67965 | 5.976
2024-12-10 | 3:52 | Data | 0 | 32.494 | 30.469 | 192.238 | 7.64 | 181.023 | 2230.66 | 25.63 | 42.387 | 6.35 | 1.37 | 4.597 | 8635.19 | 2.019 | 98.1 | 77 | 1450 | 21.19 | 5612.9 | 2895.4 | 2865.3 | 4193.1 | 1224.5 | 0.67432 | 5.968
2024-12-10 | 3:52 | Data | 0 | 32.264 | 30.401 | 192.238 | 7.64 | 181.068 | 2226.14 | 25.62 | 42.387 | 6.35 | 1.36 | 4.606 | 8639.71 | 2.079 | 98.1 | 77.2 | 1447 | 21.19 | 5615.8 | 2901.8 | 2874.5 | 4203.2 | 1224.5 | 0.67321 | 5.965
2024-12-10 | 3:52 | Data | 0 | 32.507 | 30.624 | 192.374 | 7.64 | 181.159 | 2222.52 | 25.65 | 42.297 | 6.35 | 1.358 | 4.609 | 8626.15 | 1.958 | 98.1 | 77.2 | 1445 | 21.15 | 5607 | 2926.2 | 2828.4 | 4188.1 | 1224.5 | 0.68052 | 5.967
2024-12-10 | 3:52 | Data | 0 | 32.892 | 30.759 | 192.329 | 7.64 | 181.204 | 2225.23 | 25.63 | 42.658 | 6.35 | 1.355 | 4.594 | 8621.63 | 1.944 | 98.1 | 77.2 | 1446 | 21.33 | 5604.1 | 2903.3 | 2854 | 4188.1 | 1224.5 | 0.67566 | 5.948
2024-12-10 | 3:53 | Data | 0 | 32.71 | 30.651 | 192.238 | 7.63 | 181.159 | 2218.91 | 25.64 | 42.387 | 6.35 | 1.352 | 4.591 | 8630.67 | 1.897 | 98.1 | 77.2 | 1442 | 21.19 | 5609.9 | 2917 | 2871.7 | 4214.5 | 1224.5 | 0.67475 | 5.944
2024-12-10 | 3:53 | Data | 0 | 32.494 | 30.948 | 192.148 | 7.63 | 181.114 | 2218 | 25.64 | 42.387 | 6.35 | 1.365 | 4.576 | 8630.67 | 1.742 | 98.1 | 77 | 1442 | 21.15 | 5609.9 | 2922.7 | 2891.1 | 4227.7 | 1224.5 | 0.67423 | 5.941
2024-12-10 | 3:53 | Data | 0 | 32.71 | 30.475 | 192.329 | 7.64 | 181.204 | 2222.52 | 25.64 | 42.658 | 6.35 | 1.367 | 4.598 | 8635.19 | 2.066 | 98.1 | 77.1 | 1444 | 21.28 | 5612.9 | 2908.8 | 2864 | 4204.1 | 1224.5 | 0.67356 | 5.964
2024-12-10 | 3:53 | Data | 0 | 32.71 | 30.523 | 192.148 | 7.63 | 181.023 | 2223.43 | 25.64 | 42.568 | 6.35 | 1.367 | 4.6 | 8635.19 | 2.154 | 98.1 | 77.1 | 1445 | 21.33 | 5612.9 | 2926.9 | 2877 | 4217.5 | 1224.5 | 0.67768 | 5.968
2024-12-10 | 3:53 | Data | 0 | 32.723 | 30.536 | 192.374 | 7.64 | 181.249 | 2218.91 | 25.64 | 42.658 | 6.35 | 1.357 | 4.611 | 8626.15 | 1.985 | 98.1 | 77.3 | 1442 | 21.28 | 5607 | 2938 | 2868.3 | 4219.9 | 1224.5 | 0.67906 | 5.967
2024-12-10 | 3:53 | Data | 0 | 32.467 | 30.61 | 192.057 | 7.63 | 181.068 | 2218.91 | 25.63 | 42.658 | 6.34 | 1.348 | 4.607 | 8621.63 | 2.039 | 98.1 | 77.4 | 1443 | 21.33 | 5604.1 | 2926.6 | 2834.8 | 4192.7 | 1224.5 | 0.68178 | 5.954
2024-12-10 | 3:53 | Data | 0 | 32.339 | 30.307 | 192.193 | 7.64 | 181.159 | 2224.33 | 25.63 | 42.658 | 6.35 | 1.355 | 4.612 | 8608.06 | 2.086 | 98.1 | 77.3 | 1446 | 21.33 | 5595.2 | 2908.6 | 2861 | 4193.8 | 1224.5 | 0.67665 | 5.968
2024-12-10 | 3:53 | Data | 0 | 32.271 | 30.536 | 192.193 | 7.64 | 181.068 | 2222.52 | 25.63 | 42.568 | 6.35 | 1.362 | 4.596 | 8603.54 | 2.025 | 98.1 | 77.1 | 1445 | 21.28 | 5592.3 | 2917.1 | 2879.7 | 4214.7 | 1224.5 | 0.67494 | 5.958
2024-12-10 | 3:53 | Data | 0 | 32.44 | 30.631 | 192.193 | 7.64 | 181.114 | 2222.52 | 25.63 | 42.658 | 6.35 | 1.367 | 4.617 | 8621.63 | 2.086 | 98.1 | 77.2 | 1445 | 21.28 | 5604.1 | 2935 | 2855.6 | 4211.7 | 1224.5 | 0.67951 | 5.983
2024-12-10 | 3:53 | Data | 0 | 33.102 | 30.705 | 192.329 | 7.64 | 181.294 | 2222.52 | 25.63 | 42.658 | 6.35 | 1.365 | 4.625 | 8639.71 | 2.093 | 98.1 | 77.2 | 1445 | 21.33 | 5615.8 | 2941.2 | 2848.2 | 4208.7 | 1224.5 | 0.68145 | 5.99
2024-12-10 | 3:53 | Data | 0 | 32.487 | 30.421 | 192.193 | 7.64 | 181.068 | 2222.52 | 25.62 | 42.658 | 6.35 | 1.365 | 4.598 | 8635.19 | 2.025 | 98.1 | 77.1 | 1445 | 21.33 | 5612.9 | 2915.7 | 2841.4 | 4192.1 | 1224.5 | 0.67669 | 5.961
2024-12-10 | 3:53 | Data | 0 | 32.669 | 30.651 | 192.148 | 7.63 | 181.159 | 2222.52 | 25.63 | 42.658 | 6.34 | 1.357 | 4.599 | 8653.28 | 2.241 | 98.1 | 77.2 | 1445 | 21.33 | 5624.6 | 2892.9 | 2863.8 | 4194.8 | 1224.5 | 0.6726 | 5.957
2024-12-10 | 3:53 | Data | 0 | 32.501 | 30.624 | 192.193 | 7.64 | 181.159 | 2222.52 | 25.62 | 42.748 | 6.35 | 1.358 | 4.586 | 8648.76 | 1.897 | 98.1 | 77.2 | 1445 | 21.33 | 5621.7 | 2924.9 | 2872.3 | 4215.4 | 1224.5 | 0.67659 | 5.944
2024-12-10 | 3:53 | Data | 0 | 32.494 | 30.361 | 192.193 | 7.64 | 181.068 | 2222.52 | 25.63 | 42.658 | 6.35 | 1.363 | 4.594 | 8644.24 | 2.268 | 98.1 | 77.1 | 1445 | 21.33 | 5618.8 | 2921.1 | 2859.5 | 4205.4 | 1224.5 | 0.67792 | 5.957
2024-12-10 | 3:53 | Data | 0 | 32.669 | 30.766 | 192.329 | 7.63 | 181.159 | 2222.52 | 25.64 | 42.658 | 6.35 | 1.369 | 4.607 | 8639.71 | 2.046 | 98.1 | 77.1 | 1445 | 21.33 | 5615.8 | 2921.8 | 2868.6 | 4210.1 | 1224.6 | 0.67651 | 5.977
2024-12-10 | 3:53 | Data | 0 | 32.264 | 30.536 | 192.102 | 7.64 | 181.068 | 2222.52 | 25.63 | 42.748 | 6.35 | 1.367 | 4.616 | 8612.58 | 2.052 | 98.1 | 77.2 | 1445 | 21.28 | 5598.2 | 2929.7 | 2854.9 | 4198.6 | 1224.6 | 0.68016 | 5.982
2024-12-10 | 3:53 | Data | 0 | 32.271 | 30.246 | 192.193 | 7.64 | 181.114 | 2225.23 | 25.62 | 42.748 | 6.35 | 1.367 | 4.607 | 8635.19 | 1.857 | 98.1 | 77.1 | 1446 | 21.33 | 5612.9 | 2930.9 | 2855 | 4203.6 | 1224.6 | 0.68027 | 5.976
2024-12-10 | 3:53 | Data | 0 | 32.264 | 30.502 | 192.283 | 7.63 | 181.023 | 2227.95 | 25.64 | 42.658 | 6.35 | 1.367 | 4.587 | 8635.19 | 1.857 | 98.1 | 77 | 1448 | 21.33 | 5612.9 | 2921.1 | 2843.3 | 4194.6 | 1224.6 | 0.67923 | 5.956
2024-12-10 | 3:54 | Data | 0 | 32.264 | 30.307 | 192.193 | 7.64 | 181.159 | 2229.75 | 25.64 | 42.748 | 6.35 | 1.358 | 4.588 | 8626.15 | 2.241 | 98.1 | 77.2 | 1449 | 21.33 | 5607 | 2928.9 | 2846.9 | 4199.9 | 1224.6 | 0.67993 | 5.944
2024-12-10 | 3:54 | Data | 0 | 32.548 | 30.428 | 192.283 | 7.63 | 181.204 | 2228.85 | 25.64 | 42.658 | 6.35 | 1.354 | 4.588 | 8621.63 | 2.032 | 98.1 | 77.2 | 1448 | 21.33 | 5604.1 | 2940.4 | 2860.6 | 4221.2 | 1224.6 | 0.68143 | 5.942
2024-12-10 | 3:54 | Data | 0 | 32.318 | 30.624 | 192.102 | 7.63 | 181.159 | 2228.85 | 25.64 | 42.658 | 6.35 | 1.366 | 4.601 | 8621.63 | 1.884 | 98.1 | 77.1 | 1449 | 21.33 | 5604.1 | 2927 | 2874.4 | 4215.2 | 1224.6 | 0.67936 | 5.967
2024-12-10 | 3:54 | Data | 0 | 32.723 | 30.482 | 192.283 | 7.64 | 181.204 | 2234.27 | 25.63 | 42.658 | 6.35 | 1.372 | 4.58 | 8630.67 | 2.005 | 98.1 | 77 | 1452 | 21.33 | 5609.9 | 2921.3 | 2838 | 4185.6 | 1224.6 | 0.682 | 5.952
2024-12-10 | 3:54 | Data | 0 | 32.474 | 30.428 | 192.193 | 7.64 | 181.114 | 2236.98 | 25.63 | 42.658 | 6.35 | 1.367 | 4.579 | 8635.19 | 1.965 | 98.1 | 77 | 1455 | 21.33 | 5612.9 | 2921.5 | 2860.6 | 4204.3 | 1224.6 | 0.67757 | 5.947
2024-12-10 | 3:54 | Data | 0 | 32.271 | 30.415 | 192.238 | 7.64 | 181.114 | 2239.7 | 25.63 | 42.658 | 6.35 | 1.367 | 4.583 | 8635.19 | 1.85 | 98.1 | 77 | 1456 | 21.33 | 5612.9 | 2927.2 | 2840.2 | 4191.4 | 1224.6 | 0.68116 | 5.95
2024-12-10 | 3:54 | Data | 0 | 32.723 | 30.448 | 192.193 | 7.63 | 181.159 | 2238.79 | 25.64 | 42.658 | 6.35 | 1.362 | 4.616 | 8612.58 | 1.958 | 98.1 | 77.2 | 1455 | 21.33 | 5598.2 | 2913.8 | 2844.5 | 4187.6 | 1224.6 | 0.67873 | 5.978
2024-12-10 | 3:54 | Data | 0 | 32.494 | 30.442 | 192.193 | 7.63 | 181.114 | 2244.22 | 25.65 | 42.387 | 6.35 | 1.349 | 4.605 | 8617.1 | 2.025 | 98.1 | 77.3 | 1459 | 21.19 | 5601.1 | 2912.4 | 2845.3 | 4187.8 | 1224.6 | 0.67875 | 5.956
2024-12-10 | 3:54 | Data | 0 | 32.44 | 30.617 | 192.148 | 7.64 | 181.114 | 2244.22 | 25.64 | 42.387 | 6.35 | 1.364 | 4.604 | 8621.63 | 2.019 | 98.1 | 77.1 | 1459 | 21.19 | 5604.1 | 2927.3 | 2844.6 | 4195.2 | 1224.6 | 0.68027 | 5.968
2024-12-10 | 3:54 | Data | 0 | 32.44 | 30.556 | 192.283 | 7.64 | 181.204 | 2241.5 | 25.65 | 42.297 | 6.35 | 1.359 | 4.607 | 8630.67 | 2.147 | 98.1 | 77.2 | 1457 | 21.19 | 5609.9 | 2923 | 2837.4 | 4190.3 | 1224.6 | 0.68015 | 5.966
2024-12-10 | 3:54 | Data | 0 | 32.507 | 30.307 | 192.193 | 7.64 | 181.204 | 2241.5 | 25.64 | 42.477 | 6.35 | 1.361 | 4.589 | 8648.76 | 2.073 | 98.1 | 77.1 | 1457 | 21.19 | 5621.7 | 2930.2 | 2825.3 | 4178 | 1224.6 | 0.68467 | 5.952
2024-12-10 | 3:54 | Data | 0 | 32.494 | 30.739 | 192.329 | 7.63 | 181.159 | 2229.75 | 25.64 | 42.658 | 6.35 | 1.367 | 4.586 | 8644.24 | 1.904 | 98.1 | 77 | 1449 | 21.33 | 5618.8 | 2923 | 2834.2 | 4188.1 | 1224.6 | 0.68011 | 5.952
2024-12-10 | 3:54 | Data | 0 | 32.717 | 30.826 | 192.283 | 7.64 | 181.204 | 2235.18 | 25.64 | 42.748 | 6.34 | 1.367 | 4.611 | 8635.19 | 2.059 | 98.1 | 77.1 | 1453 | 21.33 | 5612.9 | 2928.6 | 2842.3 | 4197.1 | 1224.6 | 0.68379 | 5.978
2024-12-10 | 3:54 | Data | 0 | 32.48 | 30.212 | 192.193 | 7.63 | 181.114 | 2235.18 | 25.65 | 42.658 | 6.35 | 1.354 | 4.615 | 8648.76 | 2.073 | 98.1 | 77.3 | 1453 | 21.33 | 5621.7 | 2911.9 | 2811.2 | 4172.2 | 1224.6 | 0.68084 | 5.969
2024-12-10 | 3:54 | Data | 0 | 32.609 | 30.415 | 192.238 | 7.64 | 181.204 | 2241.5 | 25.64 | 42.658 | 6.35 | 1.356 | 4.594 | 8662.33 | 2.113 | 98.1 | 77.2 | 1457 | 21.33 | 5630.5 | 2918.9 | 2829.7 | 4178.9 | 1224.6 | 0.68225 | 5.949
2024-12-10 | 3:54 | Data | 0 | 32.723 | 30.475 | 192.238 | 7.64 | 181.294 | 2236.08 | 25.65 | 42.387 | 6.35 | 1.358 | 4.598 | 8657.8 | 1.958 | 98.1 | 77.2 | 1453 | 21.24 | 5627.6 | 2906.6 | 2860.5 | 4195.7 | 1224.6 | 0.67649 | 5.956
2024-12-10 | 3:54 | Data | 0 | 32.44 | 30.415 | 192.193 | 7.64 | 181.114 | 2235.18 | 25.64 | 42.116 | 6.35 | 1.362 | 4.601 | 8662.33 | 2.073 | 98.1 | 77.2 | 1453 | 21.06 | 5630.5 | 2923.4 | 2840.3 | 4192.4 | 1224.6 | 0.68063 | 5.963
2024-12-10 | 3:54 | Data | 0 | 32.264 | 30.388 | 192.148 | 7.64 | 181.114 | 2236.08 | 25.63 | 42.387 | 6.34 | 1.374 | 4.598 | 8657.8 | 2.052 | 98.1 | 77 | 1453 | 21.19 | 5627.6 | 2924.9 | 2825.4 | 4178.4 | 1224.6 | 0.68355 | 5.972
2024-12-10 | 3:55 | Data | 0 | 32.831 | 30.435 | 192.329 | 7.64 | 181.159 | 2235.18 | 25.64 | 42.387 | 6.35 | 1.362 | 4.61 | 8630.67 | 1.971 | 98.1 | 77.2 | 1453 | 21.19 | 5609.9 | 2925.1 | 2828.3 | 4183.2 | 1224.6 | 0.68242 | 5.973
2024-12-10 | 3:55 | Data | 0 | 32.494 | 30.59 | 192.238 | 7.64 | 181.114 | 2228.85 | 25.65 | 42.387 | 6.34 | 1.357 | 4.638 | 8608.06 | 2.079 | 98.1 | 77.4 | 1449 | 21.19 | 5595.2 | 2916.2 | 2835.5 | 4186.4 | 1224.6 | 0.67888 | 5.994
2024-12-10 | 3:55 | Data | 0 | 32.663 | 30.482 | 192.283 | 7.63 | 181.114 | 2232.47 | 25.65 | 42.297 | 6.35 | 1.36 | 4.607 | 8617.1 | 2.052 | 98.1 | 77.2 | 1451 | 21.19 | 5601.1 | 2925.8 | 2820.2 | 4179.6 | 1224.6 | 0.68258 | 5.967
2024-12-10 | 3:55 | Data | 0 | 32.447 | 30.421 | 192.238 | 7.63 | 181.114 | 2232.47 | 25.64 | 42.387 | 6.35 | 1.369 | 4.577 | 8617.1 | 1.857 | 98.1 | 77 | 1452 | 21.19 | 5601.1 | 2914.3 | 2859.1 | 4200.1 | 1224.6 | 0.67764 | 5.948
2024-12-10 | 3:55 | Data | 0 | 32.548 | 30.421 | 192.238 | 7.64 | 181.159 | 2233.37 | 25.63 | 42.297 | 6.34 | 1.367 | 4.579 | 8626.15 | 2.066 | 98.1 | 77 | 1452 | 21.19 | 5607 | 2896.8 | 2803 | 4150.2 | 1224.6 | 0.68149 | 5.946
2024-12-10 | 3:55 | Data | 0 | 32.636 | 30.448 | 192.374 | 7.64 | 181.249 | 2232.47 | 25.64 | 42.387 | 6.35 | 1.37 | 4.592 | 8657.8 | 1.978 | 98.1 | 77 | 1452 | 21.24 | 5627.6 | 2925.7 | 2830.8 | 4181.4 | 1224.6 | 0.68066 | 5.963
2024-12-10 | 3:55 | Data | 0 | 32.865 | 30.448 | 192.374 | 7.64 | 181.204 | 2230.66 | 25.65 | 42.387 | 6.35 | 1.354 | 4.595 | 8662.33 | 2.174 | 98.1 | 77.2 | 1450 | 21.19 | 5630.5 | 2900.5 | 2849.1 | 4184.8 | 1224.6 | 0.67591 | 5.949
2024-12-10 | 3:55 | Data | 0 | 32.494 | 30.739 | 192.329 | 7.63 | 181.249 | 2227.04 | 25.64 | 42.477 | 6.35 | 1.358 | 4.588 | 8648.76 | 1.87 | 98.1 | 77.2 | 1448 | 21.24 | 5621.7 | 2909 | 2849.7 | 4186.6 | 1224.6 | 0.67882 | 5.945
2024-12-10 | 3:55 | Data | 0 | 32.48 | 30.651 | 192.238 | 7.64 | 181.114 | 2225.23 | 25.64 | 42.297 | 6.35 | 1.361 | 4.607 | 8671.37 | 1.951 | 98.1 | 77.2 | 1446 | 21.15 | 5636.4 | 2901.2 | 2838.7 | 4175.4 | 1224.6 | 0.67726 | 5.969
2024-12-10 | 3:55 | Data | 0 | 32.521 | 30.415 | 192.193 | 7.63 | 181.114 | 2225.23 | 25.64 | 42.387 | 6.35 | 1.359 | 4.597 | 8693.98 | 2.079 | 98.1 | 77.2 | 1446 | 21.19 | 5651.1 | 2913.1 | 2867.1 | 4206.3 | 1224.6 | 0.67577 | 5.955
2024-12-10 | 3:55 | Data | 0 | 32.582 | 30.536 | 192.283 | 7.63 | 181.114 | 2221.62 | 25.65 | 42.387 | 6.35 | 1.36 | 4.598 | 8689.46 | 1.924 | 98.1 | 77.2 | 1445 | 21.19 | 5648.1 | 2924 | 2879.1 | 4216.9 | 1224.6 | 0.67826 | 5.958
2024-12-10 | 3:55 | Data | 0 | 32.501 | 30.536 | 192.238 | 7.63 | 181.159 | 2221.62 | 25.64 | 42.387 | 6.35 | 1.362 | 4.596 | 8693.98 | 1.965 | 98.1 | 77.1 | 1445 | 21.24 | 5651.1 | 2916.7 | 2878.5 | 4216.3 | 1224.6 | 0.67463 | 5.958
2024-12-10 | 3:55 | Data | 0 | 32.723 | 30.421 | 192.238 | 7.64 | 181.204 | 2218.91 | 25.64 | 42.477 | 6.34 | 1.365 | 4.584 | 8689.46 | 1.877 | 98.1 | 77.1 | 1442 | 21.19 | 5648.1 | 2914.5 | 2864.9 | 4204 | 1224.6 | 0.67631 | 5.948
2024-12-10 | 3:55 | Data | 0 | 32.494 | 30.624 | 192.148 | 7.63 | 181.159 | 2225.23 | 25.64 | 42.387 | 6.35 | 1.356 | 4.583 | 8617.1 | 1.904 | 98.1 | 77.2 | 1446 | 21.19 | 5601.1 | 2899.8 | 2848 | 4183.2 | 1224.6 | 0.67565 | 5.939
2024-12-10 | 3:55 | Data | 0 | 32.494 | 30.415 | 192.283 | 7.64 | 181.159 | 2225.23 | 25.64 | 42.387 | 6.34 | 1.37 | 4.583 | 8626.15 | 2.079 | 98.1 | 77 | 1446 | 21.19 | 5607 | 2924.7 | 2858.8 | 4209.2 | 1224.7 | 0.67644 | 5.953
2024-12-10 | 3:55 | Data | 0 | 32.555 | 30.421 | 192.374 | 7.64 | 181.204 | 2225.23 | 25.64 | 42.387 | 6.35 | 1.363 | 4.574 | 8621.63 | 1.965 | 98.1 | 77 | 1446 | 21.19 | 5604.1 | 2905.1 | 2860 | 4197 | 1224.7 | 0.67537 | 5.935
2024-12-10 | 3:55 | Data | 0 | 32.325 | 30.367 | 192.238 | 7.64 | 181.204 | 2225.23 | 25.64 | 42.387 | 6.34 | 1.355 | 4.567 | 8626.15 | 1.904 | 98.1 | 77.1 | 1446 | 21.19 | 5607 | 2926.7 | 2856.4 | 4217 | 1224.7 | 0.67971 | 5.922
2024-12-10 | 3:56 | Data | 0 | 32.609 | 30.651 | 192.374 | 7.63 | 181.204 | 2222.52 | 25.66 | 42.387 | 6.35 | 1.348 | 4.579 | 8666.85 | 1.897 | 98.1 | 77.3 | 1445 | 21.19 | 5633.5 | 2920.7 | 2833.8 | 4180.8 | 1224.7 | 0.67963 | 5.928
2024-12-10 | 3:56 | Data | 0 | 32.521 | 30.435 | 192.238 | 7.64 | 181.114 | 2222.52 | 25.65 | 42.387 | 6.35 | 1.36 | 4.591 | 8639.71 | 2.025 | 98.1 | 77.1 | 1445 | 21.19 | 5615.8 | 2920.1 | 2823.7 | 4177.1 | 1224.7 | 0.68256 | 5.952
2024-12-10 | 3:56 | Data | 0 | 32.494 | 30.59 | 192.238 | 7.63 | 181.159 | 2222.52 | 25.64 | 42.387 | 6.35 | 1.372 | 4.592 | 8648.76 | 2.079 | 98.1 | 77 | 1445 | 21.24 | 5621.7 | 2911.9 | 2831.5 | 4181.7 | 1224.7 | 0.67908 | 5.964
2024-12-10 | 3:56 | Data | 0 | 32.507 | 30.536 | 192.329 | 7.63 | 181.159 | 2222.52 | 25.65 | 42.387 | 6.35 | 1.36 | 4.585 | 8648.76 | 1.965 | 98.1 | 77.1 | 1445 | 21.19 | 5621.7 | 2931.7 | 2858.2 | 4209.9 | 1224.7 | 0.67934 | 5.946
2024-12-10 | 3:56 | Data | 0 | 32.494 | 30.597 | 192.329 | 7.64 | 181.114 | 2216.2 | 25.65 | 42.297 | 6.35 | 1.363 | 4.571 | 8635.19 | 2.073 | 98.1 | 77 | 1442 | 21.19 | 5612.9 | 2925.7 | 2842.5 | 4198.7 | 1224.7 | 0.67834 | 5.934
2024-12-10 | 3:56 | Data | 0 | 32.602 | 30.644 | 192.329 | 7.64 | 181.114 | 2227.95 | 25.65 | 42.387 | 6.35 | 1.361 | 4.601 | 8621.63 | 2.059 | 98.1 | 77.2 | 1448 | 21.19 | 5604.1 | 2927.1 | 2867.3 | 4215.5 | 1224.7 | 0.67835 | 5.962
2024-12-10 | 3:56 | Data | 0 | 32.723 | 30.705 | 192.374 | 7.63 | 181.249 | 2224.33 | 25.65 | 42.387 | 6.35 | 1.365 | 4.585 | 8617.1 | 2.052 | 98.1 | 77.1 | 1446 | 21.24 | 5601.1 | 2921.2 | 2855.4 | 4204.1 | 1224.7 | 0.67873 | 5.95
2024-12-10 | 3:56 | Data | 0 | 32.285 | 30.624 | 192.374 | 7.63 | 181.159 | 2224.33 | 25.66 | 42.477 | 6.34 | 1.362 | 4.578 | 8635.19 | 1.931 | 98.1 | 77.1 | 1446 | 21.19 | 5612.9 | 2917.8 | 2833.6 | 4182.5 | 1224.7 | 0.6806 | 5.94
2024-12-10 | 3:56 | Data | 0 | 32.386 | 30.529 | 192.329 | 7.64 | 181.159 | 2225.23 | 25.66 | 42.297 | 6.35 | 1.356 | 4.616 | 8662.33 | 1.951 | 98.1 | 77.3 | 1447 | 21.15 | 5630.5 | 2930.9 | 2860.4 | 4210.8 | 1224.7 | 0.67772 | 5.971
2024-12-10 | 3:56 | Data | 0 | 32.852 | 30.489 | 192.283 | 7.64 | 181.294 | 2222.52 | 25.65 | 42.477 | 6.35 | 1.36 | 4.624 | 8644.24 | 2.079 | 98.1 | 77.3 | 1445 | 21.19 | 5618.8 | 2903.1 | 2852.9 | 4184.6 | 1224.7 | 0.67666 | 5.984
2024-12-10 | 3:56 | Data | 0 | 32.521 | 30.415 | 192.238 | 7.64 | 181.159 | 2222.52 | 25.64 | 42.387 | 6.35 | 1.362 | 4.611 | 8657.8 | 1.911 | 98.1 | 77.2 | 1445 | 21.19 | 5627.6 | 2925.2 | 2850 | 4200.2 | 1224.7 | 0.68085 | 5.974
2024-12-10 | 3:56 | Data | 0 | 32.825 | 30.874 | 192.464 | 7.64 | 181.114 | 2222.52 | 25.64 | 42.387 | 6.35 | 1.366 | 4.616 | 8657.8 | 2.052 | 98.1 | 77.2 | 1445 | 21.19 | 5627.6 | 2922.1 | 2838.3 | 4191.3 | 1224.7 | 0.68049 | 5.981
2024-12-10 | 3:56 | Data | 0 | 32.494 | 30.469 | 192.102 | 7.64 | 181.068 | 2222.52 | 25.66 | 42.387 | 6.35 | 1.367 | 4.619 | 8621.63 | 1.978 | 98.1 | 77.2 | 1445 | 21.19 | 5604.1 | 2924.4 | 2836.1 | 4191.6 | 1224.7 | 0.68 | 5.986
2024-12-10 | 3:56 | Data | 0 | 32.507 | 30.428 | 192.329 | 7.64 | 181.249 | 2225.23 | 25.65 | 42.297 | 6.35 | 1.366 | 4.618 | 8621.63 | 2.066 | 98.1 | 77.2 | 1446 | 21.19 | 5604.1 | 2925.3 | 2841.8 | 4195.3 | 1224.7 | 0.67886 | 5.983
2024-12-10 | 3:56 | Data | 0 | 32.467 | 30.529 | 192.329 | 7.63 | 181.114 | 2225.23 | 25.66 | 42.387 | 6.34 | 1.362 | 4.598 | 8621.63 | 2.066 | 98.1 | 77.1 | 1446 | 21.15 | 5604.1 | 2931.7 | 2847.4 | 4200 | 1224.7 | 0.68057 | 5.96
2024-12-10 | 3:56 | Data | 0 | 32.602 | 30.536 | 192.193 | 7.63 | 181.159 | 2224.33 | 25.66 | 42.387 | 6.35 | 1.364 | 4.602 | 8608.06 | 2.086 | 98.1 | 77.1 | 1446 | 21.19 | 5595.2 | 2914.1 | 2825.1 | 4173.9 | 1224.7 | 0.68145 | 5.966
2024-12-10 | 3:56 | Data | 0 | 32.723 | 30.867 | 192.283 | 7.63 | 181.204 | 2227.95 | 25.67 | 42.387 | 6.35 | 1.364 | 4.601 | 8467.87 | 1.897 | 98.1 | 77.1 | 1448 | 21.24 | 5504.1 | 2924.9 | 2835 | 4189.7 | 1224.7 | 0.68081 | 5.966
2024-12-10 | 3:56 | Data | 0 | 32.494 | 30.739 | 192.464 | 7.64 | 181.204 | 2227.04 | 25.65 | 42.477 | 6.35 | 1.359 | 4.596 | 8454.3 | 1.87 | 98.1 | 77.2 | 1448 | 21.15 | 5495.3 | 2919.9 | 2829.8 | 4183.8 | 1224.7 | 0.67976 | 5.955
2024-12-10 | 3:57 | Data | 0 | 32.919 | 30.421 | 192.238 | 7.64 | 181.159 | 2227.95 | 25.66 | 42.387 | 6.35 | 1.37 | 4.607 | 8458.83 | 1.965 | 98.1 | 77.1 | 1448 | 21.19 | 5498.2 | 2921.6 | 2830.2 | 4185 | 1224.7 | 0.68061 | 5.978
2024-12-10 | 3:57 | Data | 0 | 32.44 | 30.516 | 192.193 | 7.64 | 181.114 | 2226.14 | 25.66 | 42.387 | 6.35 | 1.371 | 4.581 | 8458.83 | 1.877 | 98.1 | 77 | 1446 | 21.19 | 5498.2 | 2917 | 2861.9 | 4201.8 | 1224.7 | 0.67703 | 5.952
2024-12-10 | 3:57 | Data | 0 | 32.494 | 30.469 | 192.283 | 7.63 | 181.204 | 2227.04 | 25.67 | 42.387 | 6.35 | 1.369 | 4.58 | 8621.63 | 1.87 | 98.1 | 77 | 1447 | 21.15 | 5604.1 | 2915 | 2854.7 | 4195.8 | 1224.7 | 0.67754 | 5.95
2024-12-10 | 3:57 | Data | 0 | 32.595 | 30.442 | 192.238 | 7.64 | 181.159 | 2224.33 | 25.65 | 42.477 | 6.35 | 1.363 | 4.598 | 8626.15 | 2.16 | 98.1 | 77.1 | 1446 | 21.19 | 5607 | 2911.3 | 2851.9 | 4193 | 1224.7 | 0.67754 | 5.96
2024-12-10 | 3:57 | Data | 0 | 32.696 | 30.651 | 192.419 | 7.64 | 181.294 | 2225.23 | 25.66 | 42.387 | 6.35 | 1.356 | 4.607 | 8648.76 | 2.059 | 98.1 | 77.3 | 1446 | 21.19 | 5621.7 | 2926.4 | 2844.7 | 4195.5 | 1224.7 | 0.68055 | 5.963
2024-12-10 | 3:57 | Data | 0 | 32.494 | 30.415 | 192.238 | 7.63 | 181.159 | 2223.43 | 25.66 | 42.387 | 6.35 | 1.359 | 4.603 | 8657.8 | 2.079 | 98.1 | 77.2 | 1445 | 21.19 | 5627.6 | 2911.8 | 2814.1 | 4171.5 | 1224.7 | 0.68161 | 5.962
2024-12-10 | 3:57 | Data | 0 | 32.602 | 30.651 | 192.419 | 7.63 | 181.249 | 2221.62 | 25.66 | 42.387 | 6.35 | 1.367 | 4.577 | 8680.41 | 2.059 | 98.1 | 77 | 1445 | 21.19 | 5642.3 | 2920.2 | 2839.4 | 4186.9 | 1224.7 | 0.68174 | 5.942
2024-12-10 | 3:57 | Data | 0 | 32.305 | 30.806 | 192.148 | 7.64 | 181.159 | 2216.2 | 25.66 | 42.387 | 6.35 | 1.352 | 4.576 | 8680.41 | 1.749 | 98.1 | 77.2 | 1441 | 21.24 | 5642.3 | 2921.4 | 2846.1 | 4196.3 | 1224.7 | 0.68029 | 5.929
2024-12-10 | 3:57 | Data | 0 | 32.75 | 30.651 | 192.374 | 7.64 | 181.294 | 2225.23 | 25.66 | 42.477 | 6.34 | 1.358 | 4.598 | 8680.41 | 2.079 | 98.1 | 77.2 | 1446 | 21.19 | 5642.3 | 2902.4 | 2820.8 | 4171.7 | 1224.7 | 0.68222 | 5.955
2024-12-10 | 3:57 | Data | 0 | 32.514 | 30.597 | 192.374 | 7.64 | 181.249 | 2225.23 | 25.65 | 42.477 | 6.35 | 1.36 | 4.591 | 8644.24 | 1.958 | 98.1 | 77.1 | 1446 | 21.19 | 5618.8 | 2914.6 | 2822.6 | 4172.5 | 1224.7 | 0.6823 | 5.95
2024-12-10 | 3:57 | Data | 0 | 32.723 | 30.705 | 192.374 | 7.63 | 181.249 | 2225.23 | 25.64 | 42.477 | 6.35 | 1.359 | 4.612 | 8662.33 | 2.073 | 98.1 | 77.2 | 1446 | 21.24 | 5630.5 | 2919 | 2822.8 | 4171.1 | 1224.7 | 0.68251 | 5.971
2024-12-10 | 3:57 | Data | 0 | 32.494 | 30.536 | 192.283 | 7.64 | 181.159 | 2227.95 | 25.65 | 42.387 | 6.34 | 1.357 | 4.601 | 8666.85 | 2.073 | 98.1 | 77.2 | 1448 | 21.19 | 5633.5 | 2918.6 | 2850.5 | 4193.1 | 1224.7 | 0.67926 | 5.958
2024-12-10 | 3:57 | Data | 0 | 32.406 | 30.198 | 192.238 | 7.64 | 181.114 | 2229.75 | 25.66 | 42.387 | 6.35 | 1.36 | 4.588 | 8666.85 | 2.268 | 98.1 | 77.1 | 1449 | 21.19 | 5633.5 | 2932.2 | 2840.2 | 4197.7 | 1224.7 | 0.68094 | 5.948
2024-12-10 | 3:57 | Data | 0 | 32.494 | 30.651 | 192.238 | 7.63 | 181.159 | 2232.47 | 25.66 | 42.387 | 6.35 | 1.372 | 4.603 | 8680.41 | 2.039 | 98.1 | 77 | 1452 | 21.15 | 5642.3 | 2920.8 | 2844.3 | 4193.2 | 1224.7 | 0.67966 | 5.976
2024-12-10 | 3:57 | Data | 0 | 32.696 | 30.853 | 192.329 | 7.64 | 181.249 | 2233.37 | 25.65 | 42.387 | 6.35 | 1.365 | 4.594 | 8693.98 | 1.897 | 98.1 | 77.1 | 1452 | 21.19 | 5651.1 | 2912.3 | 2838.1 | 4182.5 | 1224.8 | 0.67895 | 5.96
2024-12-10 | 3:57 | Data | 0 | 32.271 | 30.536 | 192.283 | 7.64 | 181.114 | 2235.18 | 25.66 | 42.477 | 6.34 | 1.359 | 4.597 | 8693.98 | 2.025 | 98.1 | 77.2 | 1453 | 21.19 | 5651.1 | 2914 | 2846.9 | 4194 | 1224.8 | 0.67734 | 5.956
2024-12-10 | 3:58 | Data | 0 | 32.393 | 30.421 | 192.283 | 7.64 | 181.249 | 2236.08 | 25.65 | 42.387 | 6.35 | 1.36 | 4.598 | 8689.46 | 1.965 | 98.1 | 77.2 | 1453 | 21.19 | 5648.1 | 2918.8 | 2846.1 | 4192.8 | 1224.8 | 0.67871 | 5.959
2024-12-10 | 3:58 | Data | 0 | 32.777 | 30.678 | 192.419 | 7.63 | 181.294 | 2235.18 | 25.66 | 42.387 | 6.34 | 1.354 | 4.607 | 8671.37 | 1.884 | 98.1 | 77.3 | 1453 | 21.19 | 5636.4 | 2918.4 | 2830.2 | 4178.5 | 1224.8 | 0.68172 | 5.961
2024-12-10 | 3:58 | Data | 0 | 32.784 | 30.766 | 192.374 | 7.64 | 181.294 | 2232.47 | 25.66 | 42.477 | 6.35 | 1.357 | 4.607 | 8680.41 | 2.059 | 98.1 | 77.3 | 1452 | 21.19 | 5642.3 | 2915.8 | 2838.9 | 4185.6 | 1224.8 | 0.68017 | 5.964
2024-12-10 | 3:58 | Data | 0 | 32.919 | 30.664 | 192.329 | 7.64 | 181.294 | 2232.47 | 25.68 | 42.477 | 6.35 | 1.359 | 4.6 | 8680.41 | 2.066 | 98.1 | 77.2 | 1452 | 21.15 | 5642.3 | 2909.7 | 2830.7 | 4181.2 | 1224.8 | 0.68013 | 5.96
2024-12-10 | 3:58 | Data | 0 | 32.71 | 30.698 | 192.419 | 7.64 | 181.294 | 2235.18 | 25.66 | 42.387 | 6.34 | 1.372 | 4.61 | 8689.46 | 1.985 | 98.1 | 77.1 | 1453 | 21.19 | 5648.1 | 2917.8 | 2848.1 | 4193.5 | 1224.8 | 0.68071 | 5.983
2024-12-10 | 3:58 | Data | 0 | 32.48 | 30.624 | 192.329 | 7.63 | 181.159 | 2241.5 | 25.66 | 42.387 | 6.35 | 1.367 | 4.616 | 8657.8 | 2.1 | 98.1 | 77.1 | 1457 | 21.19 | 5627.6 | 2917.5 | 2824.9 | 4175.5 | 1224.8 | 0.68159 | 5.984
2024-12-10 | 3:58 | Data | 0 | 32.494 | 30.651 | 192.374 | 7.63 | 181.204 | 2235.18 | 25.66 | 42.477 | 6.34 | 1.364 | 4.607 | 8630.67 | 2.059 | 98.1 | 77.1 | 1453 | 21.19 | 5609.9 | 2911.6 | 2844.2 | 4185.2 | 1224.8 | 0.6801 | 5.971
2024-12-10 | 3:58 | Data | 0 | 32.494 | 30.644 | 192.329 | 7.64 | 181.204 | 2236.08 | 25.67 | 42.387 | 6.35 | 1.355 | 4.598 | 9082.89 | 1.985 | 98.1 | 77.2 | 1453 | 21.15 | 5903.9 | 2916.2 | 2822.5 | 4176.3 | 1224.8 | 0.68131 | 5.952
2024-12-10 | 3:58 | Data | 0 | 32.494 | 30.651 | 192.329 | 7.64 | 181.114 | 2238.79 | 25.67 | 42.387 | 6.35 | 1.354 | 4.599 | 9091.94 | 2.046 | 98.1 | 77.3 | 1455 | 21.15 | 5909.8 | 2917.6 | 2802.1 | 4162.4 | 1224.8 | 0.68395 | 5.952
2024-12-10 | 3:58 | Data | 0 | 32.953 | 30.658 | 192.329 | 7.64 | 181.294 | 2238.79 | 25.67 | 42.297 | 6.35 | 1.36 | 4.621 | 8653.28 | 2.1 | 98.1 | 77.3 | 1455 | 21.15 | 5624.6 | 2916.2 | 2816 | 4171.9 | 1224.8 | 0.6829 | 5.981
2024-12-10 | 3:58 | Data | 0 | 32.494 | 30.529 | 192.283 | 7.64 | 181.159 | 2243.31 | 25.66 | 42.387 | 6.34 | 1.362 | 4.607 | 8621.63 | 1.85 | 98.1 | 77.2 | 1458 | 21.19 | 5604.1 | 2917.6 | 2817 | 4175.1 | 1224.8 | 0.68206 | 5.97
2024-12-10 | 3:58 | Data | 0 | 32.494 | 30.529 | 192.283 | 7.64 | 181.204 | 2233.37 | 25.68 | 42.387 | 6.35 | 1.365 | 4.588 | 8617.1 | 1.965 | 98.1 | 77.1 | 1452 | 21.19 | 5601.1 | 2928.4 | 2838.4 | 4193.6 | 1224.8 | 0.68211 | 5.954
2024-12-10 | 3:58 | Data | 0 | 32.494 | 30.59 | 192.283 | 7.64 | 181.204 | 2236.98 | 25.66 | 42.387 | 6.35 | 1.348 | 4.604 | 8630.67 | 2.079 | 98.1 | 77.3 | 1453 | 21.24 | 5609.9 | 2917.6 | 2867.1 | 4211.3 | 1224.8 | 0.67629 | 5.953
2024-12-10 | 3:58 | Data | 0 | 33.021 | 30.907 | 192.464 | 7.63 | 181.294 | 2236.98 | 25.68 | 42.387 | 6.35 | 1.349 | 4.585 | 8621.63 | 1.938 | 98.1 | 77.3 | 1453 | 21.19 | 5604.1 | 2920.1 | 2827.6 | 4182.1 | 1224.8 | 0.68066 | 5.933
2024-12-10 | 3:58 | Data | 0 | 32.494 | 30.556 | 192.283 | 7.63 | 181.159 | 2229.75 | 25.66 | 42.387 | 6.34 | 1.363 | 4.588 | 8612.58 | 2.052 | 98.1 | 77.1 | 1449 | 21.19 | 5598.2 | 2918.8 | 2832.5 | 4188.6 | 1224.8 | 0.67907 | 5.95
2024-12-10 | 3:58 | Data | 0 | 32.548 | 30.624 | 192.329 | 7.64 | 181.249 | 2233.37 | 25.66 | 42.387 | 6.35 | 1.362 | 4.579 | 8603.54 | 1.904 | 98.1 | 77.1 | 1451 | 21.19 | 5592.3 | 2933.3 | 2859.5 | 4211.4 | 1224.8 | 0.68092 | 5.942
2024-12-10 | 3:58 | Data | 0 | 32.521 | 30.766 | 192.374 | 7.63 | 181.204 | 2227.95 | 25.68 | 42.387 | 6.35 | 1.357 | 4.592 | 8608.06 | 1.857 | 98.1 | 77.2 | 1449 | 21.19 | 5595.2 | 2921.3 | 2813.6 | 4172.2 | 1224.8 | 0.68281 | 5.95
2024-12-10 | 3:58 | Data | 0 | 32.494 | 30.806 | 192.283 | 7.63 | 181.159 | 2229.75 | 25.67 | 42.297 | 6.35 | 1.36 | 4.598 | 8608.06 | 2.005 | 98.1 | 77.2 | 1449 | 21.19 | 5595.2 | 2921.3 | 2827.6 | 4178.3 | 1224.8 | 0.68245 | 5.958
2024-12-10 | 3:59 | Data | 0 | 32.723 | 30.766 | 192.419 | 7.64 | 181.34 | 2227.95 | 25.67 | 42.297 | 6.35 | 1.366 | 4.605 | 8594.49 | 1.958 | 98.1 | 77.1 | 1448 | 21.19 | 5586.4 | 2914.1 | 2834.8 | 4184 | 1224.8 | 0.68036 | 5.972
2024-12-10 | 3:59 | Data | 0 | 32.609 | 30.597 | 192.329 | 7.64 | 181.204 | 2227.95 | 25.67 | 42.387 | 6.35 | 1.358 | 4.597 | 8576.4 | 1.958 | 98.1 | 77.2 | 1448 | 21.19 | 5574.7 | 2932 | 2826.5 | 4187.3 | 1224.8 | 0.68118 | 5.954
2024-12-10 | 3:59 | Data | 0 | 32.285 | 30.415 | 192.238 | 7.64 | 181.159 | 2227.04 | 25.66 | 42.477 | 6.35 | 1.361 | 4.605 | 8580.93 | 1.857 | 98.1 | 77.2 | 1448 | 21.24 | 5577.6 | 2906.2 | 2817.5 | 4168.8 | 1224.8 | 0.67999 | 5.966
2024-12-10 | 3:59 | Data | 0 | 32.723 | 30.664 | 192.329 | 7.63 | 181.249 | 2227.95 | 25.67 | 42.387 | 6.35 | 1.356 | 4.611 | 8576.4 | 2.059 | 98.1 | 77.3 | 1448 | 21.19 | 5574.7 | 2911.7 | 2825.8 | 4178.4 | 1224.8 | 0.68026 | 5.967
2024-12-10 | 3:59 | Data | 0 | 32.609 | 30.691 | 192.374 | 7.64 | 181.294 | 2227.95 | 25.67 | 42.387 | 6.35 | 1.357 | 4.585 | 8639.71 | 1.897 | 98.1 | 77.2 | 1448 | 21.19 | 5615.8 | 2904.8 | 2816.9 | 4167.6 | 1224.8 | 0.68023 | 5.941
2024-12-10 | 3:59 | Data | 0 | 32.946 | 30.658 | 192.374 | 7.63 | 181.294 | 2227.04 | 25.67 | 42.477 | 6.35 | 1.375 | 4.58 | 8608.06 | 2.073 | 98.1 | 76.9 | 1448 | 21.15 | 5595.2 | 2929.1 | 2842.4 | 4197.8 | 1224.8 | 0.6808 | 5.955
2024-12-10 | 3:59 | Data | 0 | 32.521 | 30.624 | 192.283 | 7.64 | 181.159 | 2229.75 | 25.68 | 42.387 | 6.35 | 1.36 | 4.585 | 8599.01 | 1.762 | 98.1 | 77.1 | 1450 | 21.15 | 5589.4 | 2912.9 | 2839.7 | 4187.1 | 1224.8 | 0.67993 | 5.945
2024-12-10 | 3:59 | Data | 0 | 32.669 | 30.86 | 192.419 | 7.64 | 181.204 | 2229.75 | 25.66 | 42.387 | 6.34 | 1.367 | 4.596 | 8621.63 | 2.059 | 98.1 | 77.1 | 1449 | 21.19 | 5604.1 | 2942.2 | 2831.5 | 4200.7 | 1224.8 | 0.68341 | 5.962
2024-12-10 | 3:59 | Data | 0 | 32.285 | 30.651 | 192.374 | 7.63 | 181.204 | 2230.66 | 25.67 | 42.297 | 6.35 | 1.364 | 4.616 | 8621.63 | 2.113 | 98.1 | 77.2 | 1450 | 21.19 | 5604.1 | 2934.2 | 2816.6 | 4182 | 1224.8 | 0.68374 | 5.979
2024-12-10 | 3:59 | Data | 0 | 32.494 | 30.813 | 192.329 | 7.63 | 181.249 | 2235.18 | 25.67 | 42.477 | 6.35 | 1.354 | 4.611 | 8621.63 | 2.039 | 98.1 | 77.3 | 1453 | 21.19 | 5604.1 | 2930.3 | 2835.1 | 4194.3 | 1224.8 | 0.68147 | 5.966
2024-12-10 | 3:59 | Data | 0 | 32.696 | 30.975 | 192.464 | 7.64 | 181.249 | 2235.18 | 25.68 | 42.387 | 6.35 | 1.359 | 4.591 | 8621.63 | 1.904 | 98.1 | 77.2 | 1453 | 21.19 | 5604.1 | 2927.2 | 2835 | 4188.8 | 1224.8 | 0.68132 | 5.95
2024-12-10 | 3:59 | Data | 0 | 32.561 | 30.739 | 192.238 | 7.64 | 181.249 | 2233.37 | 25.68 | 42.387 | 6.35 | 1.358 | 4.611 | 8621.63 | 2.032 | 98.1 | 77.3 | 1452 | 21.19 | 5604.1 | 2935.5 | 2842.3 | 4201.1 | 1224.8 | 0.6829 | 5.968
2024-12-10 | 3:59 | Data | 0 | 32.723 | 30.448 | 192.329 | 7.64 | 181.249 | 2233.37 | 25.68 | 42.387 | 6.35 | 1.366 | 4.642 | 8626.15 | 2.16 | 98.1 | 77.3 | 1452 | 21.15 | 5607 | 2923.4 | 2840.6 | 4197.6 | 1224.8 | 0.68233 | 6.007
2024-12-10 | 3:59 | Data | 0 | 32.48 | 30.813 | 192.238 | 7.64 | 181.204 | 2236.08 | 25.68 | 42.297 | 6.35 | 1.358 | 4.616 | 8608.06 | 2.039 | 98.1 | 77.3 | 1453 | 21.15 | 5595.2 | 2931.5 | 2821.9 | 4187.1 | 1224.8 | 0.68282 | 5.975
2024-12-10 | 3:59 | Data | 0 | 32.723 | 30.658 | 192.193 | 7.63 | 181.159 | 2235.18 | 25.68 | 42.748 | 6.35 | 1.365 | 4.595 | 8612.58 | 2.066 | 98.1 | 77.1 | 1453 | 21.33 | 5598.2 | 2912.9 | 2845.9 | 4194.4 | 1224.8 | 0.67726 | 5.96
2024-12-10 | 3:59 | Data | 0 | 32.696 | 30.759 | 192.419 | 7.64 | 181.34 | 2236.08 | 25.67 | 42.387 | 6.35 | 1.361 | 4.615 | 8608.06 | 2.019 | 98.1 | 77.2 | 1453 | 21.24 | 5595.2 | 2921.4 | 2829.3 | 4184.3 | 1224.8 | 0.68081 | 5.977
2024-12-10 | 3:59 | Data | 0 | 32.663 | 30.435 | 192.283 | 7.64 | 181.249 | 2236.08 | 25.67 | 42.387 | 6.34 | 1.351 | 4.614 | 8608.06 | 1.971 | 98.1 | 77.3 | 1453 | 21.19 | 5595.2 | 2929.2 | 2846.7 | 4199.9 | 1224.8 | 0.68048 | 5.964
2024-12-10 | 3:59 | Data | 0 | 32.359 | 30.624 | 192.329 | 7.63 | 181.204 | 2230.66 | 25.68 | 42.658 | 6.35 | 1.357 | 4.6 | 8612.58 | 1.85 | 98.1 | 77.2 | 1450 | 21.33 | 5598.2 | 2917.3 | 2841.6 | 4192.1 | 1224.9 | 0.67914 | 5.957
2024-12-10 | 4:00 | Data | 0 | 32.696 | 30.651 | 192.329 | 7.64 | 181.294 | 2229.75 | 25.67 | 42.477 | 6.35 | 1.37 | 4.599 | 8626.15 | 2.066 | 98.1 | 77.1 | 1450 | 21.19 | 5607 | 2915.6 | 2854.5 | 4205.6 | 1224.9 | 0.67726 | 5.97
2024-12-10 | 4:00 | Data | 0 | 32.501 | 30.867 | 192.374 | 7.64 | 181.159 | 2229.75 | 25.67 | 42.387 | 6.35 | 1.358 | 4.602 | 8612.58 | 1.931 | 98.1 | 77.2 | 1450 | 21.24 | 5598.2 | 2916.3 | 2849.4 | 4195.8 | 1224.9 | 0.68226 | 5.96
2024-12-10 | 4:00 | Data | 0 | 32.507 | 30.462 | 192.193 | 7.63 | 181.204 | 2229.75 | 25.68 | 42.658 | 6.35 | 1.354 | 4.585 | 8626.15 | 1.992 | 98.1 | 77.2 | 1450 | 21.33 | 5607 | 2910.6 | 2820.2 | 4172 | 1224.9 | 0.68057 | 5.94
2024-12-10 | 4:00 | Data | 0 | 32.723 | 30.853 | 192.374 | 7.64 | 181.294 | 2230.66 | 25.67 | 42.658 | 6.35 | 1.369 | 4.607 | 8617.1 | 1.904 | 98.1 | 77.1 | 1450 | 21.33 | 5601.1 | 2895.8 | 2810.9 | 4153.5 | 1224.9 | 0.68051 | 5.976
2024-12-10 | 4:00 | Data | 0 | 32.393 | 30.793 | 192.283 | 7.63 | 181.204 | 2230.66 | 25.68 | 42.477 | 6.34 | 1.364 | 4.595 | 8621.63 | 1.944 | 98.1 | 77.1 | 1450 | 21.24 | 5604.1 | 2906.4 | 2838.1 | 4180.9 | 1224.9 | 0.67687 | 5.958
2024-12-10 | 4:00 | Data | 0 | 32.494 | 30.651 | 192.329 | 7.64 | 181.204 | 2230.66 | 25.68 | 42.206 | 6.35 | 1.361 | 4.609 | 8621.63 | 1.958 | 98.1 | 77.2 | 1450 | 21.1 | 5604.1 | 2920.2 | 2849.2 | 4196.4 | 1224.9 | 0.67862 | 5.971
2024-12-10 | 4:00 | Data | 0 | 32.723 | 30.941 | 192.374 | 7.63 | 181.34 | 2229.75 | 25.68 | 42.477 | 6.35 | 1.357 | 4.587 | 8816.08 | 1.951 | 98.1 | 77.2 | 1449 | 21.24 | 5730.5 | 2920.5 | 2854.4 | 4200.3 | 1224.9 | 0.67741 | 5.942
2024-12-10 | 4:00 | Data | 0 | 32.548 | 30.826 | 192.283 | 7.64 | 181.294 | 2227.95 | 25.68 | 42.387 | 6.35 | 1.351 | 4.585 | 8856.78 | 1.85 | 98.1 | 77.2 | 1448 | 21.19 | 5756.9 | 2913.8 | 2844.9 | 4188.2 | 1224.9 | 0.67835 | 5.935
2024-12-10 | 4:00 | Data | 0 | 32.717 | 30.651 | 192.283 | 7.64 | 181.204 | 2227.04 | 25.67 | 42.387 | 6.35 | 1.358 | 4.6 | 8838.69 | 1.958 | 98.1 | 77.2 | 1448 | 21.19 | 5745.1 | 2934 | 2834.3 | 4195.7 | 1224.9 | 0.68231 | 5.959
2024-12-10 | 4:00 | Data | 0 | 32.636 | 30.448 | 192.419 | 7.63 | 181.34 | 2222.52 | 25.68 | 42.658 | 6.35 | 1.362 | 4.579 | 8825.13 | 2.019 | 98.1 | 77.1 | 1445 | 21.28 | 5736.3 | 2930.1 | 2829.4 | 4189.4 | 1224.9 | 0.68379 | 5.941
2024-12-10 | 4:00 | Data | 0 | 32.521 | 30.421 | 192.329 | 7.63 | 181.249 | 2222.52 | 25.68 | 42.477 | 6.34 | 1.366 | 4.593 | 8684.94 | 2.079 | 98.1 | 77.1 | 1445 | 21.24 | 5645.2 | 2915.4 | 2838.6 | 4185 | 1224.9 | 0.67902 | 5.958
2024-12-10 | 4:00 | Data | 0 | 32.555 | 30.651 | 192.374 | 7.64 | 181.294 | 2218.91 | 25.67 | 42.387 | 6.35 | 1.358 | 4.594 | 8693.98 | 1.843 | 98.1 | 77.2 | 1442 | 21.19 | 5651.1 | 2940.8 | 2813.3 | 4184.2 | 1224.9 | 0.68512 | 5.953
2024-12-10 | 4:00 | Data | 0 | 32.609 | 30.644 | 192.329 | 7.63 | 181.204 | 2217.1 | 25.67 | 42.477 | 6.34 | 1.363 | 4.588 | 8671.37 | 2.086 | 98.1 | 77.1 | 1441 | 21.15 | 5636.4 | 2932 | 2819.1 | 4183.4 | 1224.9 | 0.68371 | 5.95
2024-12-10 | 4:00 | Data | 0 | 32.487 | 30.415 | 192.193 | 7.63 | 181.204 | 2217.1 | 25.68 | 42.387 | 6.35 | 1.356 | 4.585 | 8684.94 | 2.079 | 98.1 | 77.2 | 1441 | 21.19 | 5645.2 | 2919.6 | 2851.8 | 4196.8 | 1224.9 | 0.67889 | 5.941
2024-12-10 | 4:00 | Data | 0 | 32.548 | 30.637 | 192.329 | 7.63 | 181.249 | 2216.2 | 25.68 | 42.387 | 6.35 | 1.361 | 4.606 | 8644.24 | 1.857 | 98.1 | 77.2 | 1441 | 21.19 | 5618.8 | 2910 | 2853.4 | 4194.9 | 1224.9 | 0.67626 | 5.966
2024-12-10 | 4:00 | Data | 0 | 32.548 | 30.651 | 192.238 | 7.64 | 181.249 | 2216.2 | 25.67 | 42.387 | 6.35 | 1.358 | 4.618 | 8662.33 | 1.857 | 98.1 | 77.3 | 1441 | 21.19 | 5630.5 | 2911.5 | 2820.5 | 4170.7 | 1224.9 | 0.68161 | 5.976
2024-12-10 | 4:00 | Data | 0 | 32.777 | 30.482 | 192.374 | 7.63 | 181.34 | 2211.68 | 25.67 | 42.387 | 6.34 | 1.349 | 4.617 | 8657.8 | 2.019 | 98.1 | 77.4 | 1438 | 21.19 | 5627.6 | 2916.7 | 2813.2 | 4169.1 | 1224.9 | 0.68317 | 5.968
2024-12-10 | 4:00 | Data | 0 | 32.94 | 30.428 | 192.419 | 7.64 | 181.159 | 2217.1 | 25.68 | 42.387 | 6.35 | 1.349 | 4.607 | 8662.33 | 2.086 | 98.1 | 77.3 | 1441 | 21.15 | 5630.5 | 2916.7 | 2830.9 | 4184.3 | 1224.9 | 0.68007 | 5.956
2024-12-10 | 4:01 | Data | 0 | 32.798 | 30.779 | 192.464 | 7.63 | 181.249 | 2216.2 | 25.68 | 42.206 | 6.34 | 1.354 | 4.598 | 8671.37 | 2.066 | 98.1 | 77.3 | 1441 | 21.06 | 5636.4 | 2918.5 | 2825.5 | 4179.1 | 1224.9 | 0.68235 | 5.952
2024-12-10 | 4:01 | Data | 0 | 32.609 | 30.631 | 192.238 | 7.64 | 181.204 | 2218.91 | 25.68 | 42.387 | 6.35 | 1.362 | 4.567 | 8662.33 | 2.079 | 98.1 | 77 | 1442 | 21.19 | 5630.5 | 2912.9 | 2828.2 | 4178.9 | 1224.9 | 0.67966 | 5.929
2024-12-10 | 4:01 | Data | 0 | 32.548 | 30.651 | 192.283 | 7.64 | 181.204 | 2218.91 | 25.67 | 42.387 | 6.35 | 1.353 | 4.575 | 8657.8 | 1.85 | 98.1 | 77.2 | 1442 | 21.19 | 5627.6 | 2917.1 | 2823.1 | 4174.8 | 1224.9 | 0.682 | 5.929
2024-12-10 | 4:01 | Data | 0 | 32.771 | 30.766 | 192.419 | 7.64 | 181.249 | 2218.91 | 25.68 | 42.297 | 6.34 | 1.355 | 4.607 | 8666.85 | 2.1 | 98.1 | 77.3 | 1442 | 21.19 | 5633.5 | 2928.5 | 2828.5 | 4185.2 | 1224.9 | 0.68273 | 5.961
2024-12-10 | 4:01 | Data | 0 | 32.723 | 30.867 | 192.419 | 7.63 | 181.294 | 2222.52 | 25.68 | 42.387 | 6.35 | 1.367 | 4.595 | 8662.33 | 1.89 | 98.1 | 77.1 | 1445 | 21.19 | 5630.5 | 2926.5 | 2831.2 | 4176 | 1224.9 | 0.68375 | 5.962
2024-12-10 | 4:01 | Data | 0 | 32.528 | 30.421 | 192.283 | 7.63 | 181.249 | 2225.23 | 25.68 | 42.477 | 6.35 | 1.357 | 4.567 | 8657.8 | 1.85 | 98.1 | 77.1 | 1446 | 21.24 | 5627.6 | 2917.3 | 2826.8 | 4176.2 | 1224.9 | 0.68197 | 5.923
2024-12-10 | 4:01 | Data | 0 | 32.946 | 30.664 | 192.329 | 7.64 | 181.249 | 2227.04 | 25.67 | 42.387 | 6.35 | 1.355 | 4.588 | 8662.33 | 2.073 | 98.1 | 77.2 | 1448 | 21.19 | 5630.5 | 2913.4 | 2810.8 | 4163.2 | 1224.9 | 0.68238 | 5.942
2024-12-10 | 4:01 | Data | 0 | 32.865 | 30.664 | 192.329 | 7.64 | 181.294 | 2227.95 | 25.68 | 42.477 | 6.35 | 1.354 | 4.587 | 8648.76 | 1.904 | 98.1 | 77.2 | 1448 | 21.19 | 5621.7 | 2925.8 | 2805.6 | 4170.7 | 1224.9 | 0.68538 | 5.941
2024-12-10 | 4:01 | Data | 0 | 32.845 | 30.678 | 192.464 | 7.63 | 181.34 | 2221.62 | 25.68 | 42.387 | 6.34 | 1.36 | 4.616 | 8662.33 | 2.032 | 98.1 | 77.2 | 1442 | 21.19 | 5630.5 | 2898.1 | 2824.3 | 4164.5 | 1224.9 | 0.67935 | 5.977
2024-12-10 | 4:01 | Data | 0 | 32.723 | 30.968 | 192.419 | 7.63 | 181.294 | 2221.62 | 25.68 | 42.387 | 6.35 | 1.351 | 4.612 | 8883.91 | 1.924 | 98.1 | 77.3 | 1445 | 21.15 | 5774.5 | 2903.9 | 2801.5 | 4153.2 | 1224.9 | 0.68234 | 5.963
2024-12-10 | 4:01 | Data | 0 | 32.507 | 30.651 | 192.329 | 7.64 | 181.294 | 2224.33 | 25.68 | 42.387 | 6.35 | 1.351 | 4.595 | 8865.83 | 1.85 | 98.1 | 77.3 | 1446 | 21.19 | 5762.8 | 2928.6 | 2819.9 | 4180 | 1224.9 | 0.68393 | 5.946
2024-12-10 | 4:01 | Data | 0 | 32.717 | 30.55 | 192.193 | 7.63 | 181.204 | 2227.95 | 25.68 | 42.387 | 6.35 | 1.36 | 4.594 | 8883.91 | 1.971 | 98.1 | 77.2 | 1448 | 21.19 | 5774.5 | 2902.1 | 2814.7 | 4161.1 | 1224.9 | 0.68116 | 5.954
2024-12-10 | 4:01 | Data | 0 | 32.494 | 30.644 | 192.283 | 7.63 | 181.204 | 2228.85 | 25.67 | 42.387 | 6.34 | 1.365 | 4.58 | 8883.91 | 2.025 | 98.1 | 77 | 1448 | 21.19 | 5774.5 | 2918.2 | 2813.4 | 4166 | 1224.9 | 0.68524 | 5.945
2024-12-10 | 4:01 | Data | 0 | 32.602 | 30.867 | 192.464 | 7.63 | 181.294 | 2227.95 | 25.67 | 42.387 | 6.35 | 1.37 | 4.606 | 8657.8 | 1.958 | 98.1 | 77.1 | 1448 | 21.19 | 5627.6 | 2907.3 | 2812.6 | 4161.9 | 1224.9 | 0.68228 | 5.975
2024-12-10 | 4:01 | Data | 0 | 32.723 | 30.658 | 192.329 | 7.64 | 181.294 | 2227.95 | 25.68 | 42.387 | 6.34 | 1.364 | 4.606 | 8635.19 | 2.046 | 98.1 | 77.1 | 1448 | 21.19 | 5612.9 | 2908.9 | 2816.7 | 4167.1 | 1224.9 | 0.68103 | 5.969
2024-12-10 | 4:01 | Data | 0 | 32.609 | 30.651 | 192.374 | 7.64 | 181.249 | 2229.75 | 25.69 | 42.387 | 6.35 | 1.356 | 4.584 | 8662.33 | 2.059 | 98.1 | 77.2 | 1449 | 21.19 | 5630.5 | 2931.3 | 2795.7 | 4164.9 | 1224.9 | 0.68798 | 5.94
2024-12-10 | 4:01 | Data | 0 | 32.784 | 30.907 | 192.329 | 7.63 | 181.294 | 2229.75 | 25.68 | 42.387 | 6.35 | 1.36 | 4.598 | 8648.76 | 2.167 | 98.1 | 77.2 | 1450 | 21.15 | 5621.7 | 2898.9 | 2821.6 | 4159.8 | 1224.9 | 0.67889 | 5.96
2024-12-10 | 4:02 | Data | 0 | 32.919 | 30.874 | 192.419 | 7.64 | 181.294 | 2230.66 | 25.69 | 42.658 | 6.35 | 1.355 | 4.634 | 8612.58 | 2.073 | 98.1 | 77.4 | 1450 | 21.33 | 5598.2 | 2910.6 | 2815.2 | 4162.1 | 1225 | 0.68105 | 5.988
2024-12-10 | 4:02 | Data | 0 | 32.582 | 30.543 | 192.374 | 7.64 | 181.204 | 2230.66 | 25.68 | 42.658 | 6.35 | 1.369 | 4.602 | 8608.06 | 2.052 | 98.1 | 77.1 | 1450 | 21.33 | 5595.2 | 2905.1 | 2828.3 | 4174.6 | 1225 | 0.6773 | 5.969
2024-12-10 | 4:02 | Data | 0 | 32.507 | 30.651 | 192.374 | 7.63 | 181.294 | 2232.47 | 25.69 | 42.477 | 6.35 | 1.357 | 4.624 | 8608.06 | 1.965 | 98.1 | 77.3 | 1452 | 21.19 | 5595.2 | 2905.1 | 2823.2 | 4167.9 | 1225 | 0.67988 | 5.98
2024-12-10 | 4:02 | Data | 0 | 32.919 | 30.651 | 192.238 | 7.64 | 181.294 | 2233.37 | 25.67 | 42.387 | 6.35 | 1.361 | 4.602 | 8608.06 | 2.113 | 98.1 | 77.2 | 1452 | 21.24 | 5595.2 | 2902.7 | 2830.2 | 4169.9 | 1225 | 0.67848 | 5.964
2024-12-10 | 4:02 | Data | 0 | 32.892 | 30.705 | 192.464 | 7.64 | 181.249 | 2235.18 | 25.69 | 42.477 | 6.35 | 1.361 | 4.592 | 8635.19 | 2.181 | 98.1 | 77.1 | 1453 | 21.28 | 5612.9 | 2920.3 | 2807.4 | 4169.3 | 1225 | 0.68445 | 5.954
2024-12-10 | 4:02 | Data | 0 | 32.507 | 30.55 | 192.419 | 7.64 | 181.249 | 2232.47 | 25.69 | 42.387 | 6.34 | 1.365 | 4.614 | 8635.19 | 2.052 | 98.1 | 77.2 | 1451 | 21.19 | 5612.9 | 2927.5 | 2832.4 | 4185.8 | 1225 | 0.6831 | 5.979
2024-12-10 | 4:02 | Data | 0 | 32.669 | 30.651 | 192.329 | 7.63 | 181.159 | 2232.47 | 25.69 | 42.387 | 6.34 | 1.361 | 4.623 | 8630.67 | 2.066 | 98.1 | 77.3 | 1451 | 21.19 | 5609.9 | 2946.1 | 2818.2 | 4195.3 | 1225 | 0.68661 | 5.984
2024-12-10 | 4:02 | Data | 0 | 32.885 | 31.076 | 192.419 | 7.63 | 181.249 | 2230.66 | 25.67 | 42.387 | 6.34 | 1.354 | 4.615 | 8635.19 | 1.904 | 98.1 | 77.3 | 1450 | 21.19 | 5612.9 | 2913.1 | 2811.2 | 4164.8 | 1225 | 0.68214 | 5.969
2024-12-10 | 4:02 | Data | 0 | 32.723 | 30.867 | 192.419 | 7.64 | 181.294 | 2228.85 | 25.69 | 42.387 | 6.35 | 1.351 | 4.599 | 8644.24 | 2.066 | 98.1 | 77.3 | 1449 | 21.19 | 5618.8 | 2917.8 | 2831.3 | 4177.9 | 1225 | 0.68161 | 5.951
2024-12-10 | 4:02 | Data | 0 | 32.501 | 30.651 | 192.193 | 7.63 | 181.204 | 2218.91 | 25.69 | 42.387 | 6.34 | 1.356 | 4.596 | 8635.19 | 2.046 | 98.1 | 77.2 | 1443 | 21.15 | 5612.9 | 2920.9 | 2819.5 | 4176.3 | 1225 | 0.68338 | 5.951
2024-12-10 | 4:02 | Data | 0 | 32.521 | 30.651 | 192.283 | 7.63 | 181.294 | 2225.23 | 25.68 | 42.387 | 6.35 | 1.362 | 4.596 | 8662.33 | 1.843 | 98.1 | 77.1 | 1446 | 21.19 | 5630.5 | 2906.8 | 2833.9 | 4186.5 | 1225 | 0.68402 | 5.959
2024-12-10 | 4:02 | Data | 0 | 32.723 | 30.705 | 192.329 | 7.64 | 181.249 | 2227.04 | 25.68 | 42.297 | 6.35 | 1.353 | 4.592 | 8662.33 | 1.897 | 98.1 | 77.2 | 1448 | 21.19 | 5630.5 | 2923.3 | 2831.7 | 4174.1 | 1225 | 0.67988 | 5.945
2024-12-10 | 4:02 | Data | 0 | 32.913 | 30.651 | 192.419 | 7.64 | 181.249 | 2229.75 | 25.67 | 42.387 | 6.35 | 1.361 | 4.597 | 8662.33 | 2.255 | 98.1 | 77.2 | 1449 | 21.19 | 5630.5 | 2922.2 | 2808.9 | 4165.7 | 1225 | 0.68517 | 5.958
2024-12-10 | 4:02 | Data | 0 | 32.555 | 30.853 | 192.329 | 7.64 | 181.204 | 2229.75 | 25.68 | 42.387 | 6.35 | 1.358 | 4.594 | 8657.8 | 1.85 | 98.1 | 77.2 | 1449 | 21.24 | 5627.6 | 2909.9 | 2818.3 | 4172.7 | 1225 | 0.68044 | 5.952
2024-12-10 | 4:02 | Data | 0 | 32.548 | 30.644 | 192.329 | 7.64 | 181.294 | 2227.95 | 25.68 | 42.477 | 6.35 | 1.362 | 4.589 | 8657.8 | 1.863 | 98.1 | 77.1 | 1449 | 21.19 | 5627.6 | 2906.8 | 2843.1 | 4186 | 1225 | 0.67785 | 5.951
2024-12-10 | 4:02 | Data | 0 | 32.919 | 30.664 | 192.464 | 7.63 | 181.249 | 2227.95 | 25.68 | 42.477 | 6.34 | 1.362 | 4.568 | 8657.8 | 2.113 | 98.1 | 77 | 1448 | 21.19 | 5627.6 | 2922.7 | 2833.9 | 4183.8 | 1225 | 0.68151 | 5.93
2024-12-10 | 4:02 | Data | 0 | 32.521 | 30.651 | 192.238 | 7.64 | 181.159 | 2227.95 | 25.67 | 42.297 | 6.35 | 1.357 | 4.572 | 8648.76 | 1.857 | 98.1 | 77.1 | 1448 | 21.19 | 5621.7 | 2920.4 | 2838.4 | 4181.9 | 1225 | 0.67958 | 5.929
2024-12-10 | 4:02 | Data | 0 | 32.453 | 30.739 | 192.329 | 7.63 | 181.294 | 2227.04 | 25.69 | 42.387 | 6.35 | 1.355 | 4.578 | 8644.24 | 1.769 | 98.1 | 77.2 | 1448 | 21.19 | 5618.8 | 2908.9 | 2835.7 | 4180.6 | 1225 | 0.67809 | 5.931
2024-12-10 | 4:03 | Data | 0 | 32.723 | 30.853 | 192.283 | 7.63 | 181.249 | 2227.04 | 25.69 | 42.387 | 6.35 | 1.362 | 4.592 | 8648.76 | 1.958 | 98.1 | 77.1 | 1448 | 21.19 | 5621.7 | 2916.2 | 2828.7 | 4181.9 | 1225 | 0.67906 | 5.955
2024-12-10 | 4:03 | Data | 0 | 32.622 | 30.61 | 192.464 | 7.64 | 181.34 | 2227.95 | 25.68 | 42.387 | 6.35 | 1.358 | 4.589 | 8662.33 | 1.965 | 98.1 | 77.2 | 1448 | 21.19 | 5630.5 | 2930.9 | 2828.9 | 4183.3 | 1225 | 0.68414 | 5.947
2024-12-10 | 4:03 | Data | 0 | 32.501 | 30.759 | 192.374 | 7.64 | 181.294 | 2230.66 | 25.69 | 42.387 | 6.35 | 1.365 | 4.578 | 8662.33 | 1.857 | 98.1 | 77 | 1450 | 21.19 | 5630.5 | 2936.9 | 2826.1 | 4189.6 | 1225 | 0.6832 | 5.942
2024-12-10 | 4:03 | Data | 0 | 32.723 | 30.664 | 192.283 | 7.64 | 181.204 | 2233.37 | 25.68 | 42.387 | 6.35 | 1.363 | 4.619 | 8657.8 | 2.059 | 98.1 | 77.2 | 1452 | 21.19 | 5627.6 | 2912.8 | 2845.8 | 4189.3 | 1225 | 0.67905 | 5.982
2024-12-10 | 4:03 | Data | 0 | 32.501 | 30.766 | 192.374 | 7.63 | 181.249 | 2235.18 | 25.69 | 42.477 | 6.35 | 1.367 | 4.598 | 8662.33 | 1.843 | 98.1 | 77.1 | 1453 | 21.24 | 5630.5 | 2896.3 | 2850 | 4179.8 | 1225 | 0.67635 | 5.966
2024-12-10 | 4:03 | Data | 0 | 32.609 | 30.658 | 192.419 | 7.63 | 181.204 | 2238.79 | 25.68 | 42.297 | 6.35 | 1.372 | 4.574 | 8662.33 | 2.025 | 98.1 | 76.9 | 1455 | 21.24 | 5630.5 | 2912.8 | 2824 | 4179.6 | 1225 | 0.67893 | 5.946
2024-12-10 | 4:03 | Data | 0 | 32.723 | 30.705 | 192.464 | 7.64 | 181.294 | 2238.79 | 25.69 | 42.297 | 6.35 | 1.367 | 4.611 | 8653.28 | 1.965 | 98.1 | 77.1 | 1455 | 21.19 | 5624.6 | 2916 | 2822.9 | 4172.3 | 1225 | 0.68152 | 5.978
2024-12-10 | 4:03 | Data | 0 | 32.501 | 30.651 | 192.419 | 7.64 | 181.34 | 2238.79 | 25.68 | 42.387 | 6.35 | 1.365 | 4.602 | 8635.19 | 1.843 | 98.1 | 77.1 | 1455 | 21.19 | 5612.9 | 2907.1 | 2822.7 | 4166.2 | 1225 | 0.6817 | 5.968
2024-12-10 | 4:03 | Data | 0 | 32.723 | 30.88 | 192.374 | 7.64 | 181.249 | 2241.5 | 25.68 | 42.387 | 6.35 | 1.359 | 4.601 | 8635.19 | 1.843 | 98.1 | 77.2 | 1457 | 21.19 | 5612.9 | 2919.3 | 2813.8 | 4171.7 | 1225 | 0.68301 | 5.96
2024-12-10 | 4:03 | Data | 0 | 32.94 | 30.685 | 192.464 | 7.64 | 181.294 | 2241.5 | 25.69 | 42.477 | 6.35 | 1.367 | 4.6 | 8635.19 | 2.052 | 98.1 | 77.1 | 1457 | 21.19 | 5612.9 | 2893.5 | 2811.9 | 4159.9 | 1225 | 0.67821 | 5.967
2024-12-10 | 4:03 | Data | 0 | 32.514 | 30.651 | 192.374 | 7.63 | 181.294 | 2242.41 | 25.68 | 42.297 | 6.35 | 1.371 | 4.571 | 8608.06 | 1.958 | 98.1 | 76.9 | 1457 | 21.19 | 5595.2 | 2924.7 | 2826.8 | 4182.7 | 1225 | 0.6833 | 5.942
2024-12-10 | 4:03 | Data | 0 | 32.723 | 30.826 | 192.51 | 7.63 | 181.249 | 2241.5 | 25.7 | 42.387 | 6.35 | 1.358 | 4.609 | 8621.63 | 1.958 | 98.1 | 77.2 | 1457 | 21.19 | 5604.1 | 2918.1 | 2817.5 | 4173 | 1225 | 0.68196 | 5.968
2024-12-10 | 4:03 | Data | 0 | 32.723 | 30.658 | 192.374 | 7.64 | 181.249 | 2241.5 | 25.69 | 42.387 | 6.35 | 1.348 | 4.585 | 8599.01 | 2.066 | 98.1 | 77.3 | 1457 | 21.19 | 5589.4 | 2924.5 | 2834.6 | 4186.8 | 1225 | 0.67754 | 5.934
2024-12-10 | 4:03 | Data | 0 | 32.723 | 30.651 | 192.464 | 7.64 | 181.294 | 2241.5 | 25.69 | 42.387 | 6.35 | 1.355 | 4.601 | 8594.49 | 2.073 | 98.1 | 77.3 | 1457 | 21.19 | 5586.4 | 2900.5 | 2815.1 | 4158.9 | 1225 | 0.68134 | 5.956
2024-12-10 | 4:03 | Data | 0 | 32.534 | 30.536 | 192.329 | 7.64 | 181.249 | 2241.5 | 25.69 | 42.387 | 6.34 | 1.361 | 4.618 | 8639.71 | 1.742 | 98.1 | 77.2 | 1457 | 21.19 | 5615.8 | 2900.2 | 2813.6 | 4164 | 1225 | 0.6804 | 5.979
2024-12-10 | 4:03 | Data | 0 | 32.669 | 30.759 | 192.329 | 7.64 | 181.294 | 2241.5 | 25.69 | 42.387 | 6.34 | 1.359 | 4.582 | 8653.28 | 1.843 | 98.1 | 77.1 | 1458 | 21.19 | 5624.6 | 2922.2 | 2824.5 | 4164.6 | 1225 | 0.68337 | 5.943
2024-12-10 | 4:03 | Data | 0 | 32.636 | 30.597 | 192.283 | 7.63 | 181.249 | 2243.31 | 25.68 | 42.387 | 6.35 | 1.358 | 4.585 | 8653.28 | 1.789 | 98.1 | 77.2 | 1458 | 21.19 | 5624.6 | 2909.8 | 2803.2 | 4158.2 | 1225 | 0.68317 | 5.942
2024-12-10 | 4:04 | Data | 0 | 32.723 | 30.968 | 192.283 | 7.64 | 181.249 | 2246.02 | 25.69 | 42.387 | 6.35 | 1.361 | 4.588 | 8657.8 | 1.958 | 98.1 | 77.1 | 1461 | 21.19 | 5627.6 | 2908.8 | 2795.2 | 4148.8 | 1225 | 0.68465 | 5.95
2024-12-10 | 4:04 | Data | 0 | 32.501 | 30.651 | 192.419 | 7.64 | 181.114 | 2244.22 | 25.69 | 42.387 | 6.35 | 1.356 | 4.579 | 8666.85 | 1.958 | 98.1 | 77.1 | 1459 | 21.19 | 5633.5 | 2912.1 | 2793.1 | 4151.6 | 1225 | 0.68423 | 5.935
2024-12-10 | 4:04 | Data | 0 | 32.838 | 30.658 | 192.419 | 7.64 | 181.34 | 2246.02 | 25.69 | 42.477 | 6.35 | 1.366 | 4.576 | 8644.24 | 1.904 | 98.1 | 77 | 1461 | 21.19 | 5618.8 | 2914.6 | 2790.7 | 4151.6 | 1225.1 | 0.68406 | 5.942
2024-12-10 | 4:04 | Data | 0 | 32.953 | 30.678 | 192.419 | 7.63 | 181.385 | 2244.22 | 25.69 | 42.477 | 6.35 | 1.371 | 4.595 | 8621.63 | 1.87 | 98.1 | 77 | 1459 | 21.19 | 5604.1 | 2913 | 2818.1 | 4171.1 | 1225.1 | 0.68102 | 5.966
2024-12-10 | 4:04 | Data | 0 | 32.723 | 30.874 | 192.329 | 7.64 | 181.249 | 2244.22 | 25.69 | 42.477 | 6.36 | 1.373 | 4.598 | 8603.54 | 2.052 | 98.1 | 77 | 1458 | 21.24 | 5592.3 | 2916.6 | 2795.9 | 4153.7 | 1225.1 | 0.68525 | 5.972
2024-12-10 | 4:04 | Data | 0 | 32.507 | 30.678 | 192.283 | 7.64 | 181.204 | 2241.5 | 25.69 | 42.477 | 6.35 | 1.369 | 4.596 | 8626.15 | 1.904 | 98.1 | 77.1 | 1457 | 21.19 | 5607 | 2907.6 | 2806 | 4156.4 | 1225.1 | 0.68278 | 5.963
2024-12-10 | 4:04 | Data | 0 | 32.723 | 30.651 | 192.329 | 7.64 | 181.34 | 2238.79 | 25.68 | 42.387 | 6.35 | 1.36 | 4.613 | 8635.19 | 2.073 | 98.1 | 77.2 | 1455 | 21.24 | 5612.9 | 2915.3 | 2789.6 | 4153.1 | 1225.1 | 0.68502 | 5.972
2024-12-10 | 4:04 | Data | 0 | 32.946 | 30.88 | 192.51 | 7.63 | 181.34 | 2238.79 | 25.7 | 42.387 | 6.35 | 1.369 | 4.607 | 8635.19 | 1.897 | 98.1 | 77.1 | 1455 | 21.24 | 5612.9 | 2910.3 | 2804.4 | 4158.9 | 1225.1 | 0.68454 | 5.975
2024-12-10 | 4:04 | Data | 0 | 32.913 | 30.664 | 192.464 | 7.63 | 181.294 | 2236.08 | 25.7 | 42.387 | 6.35 | 1.362 | 4.559 | 8648.76 | 2.235 | 98.1 | 77 | 1453 | 21.19 | 5621.7 | 2902.4 | 2807.2 | 4154 | 1225.1 | 0.68141 | 5.92
2024-12-10 | 4:04 | Data | 0 | 32.94 | 30.651 | 192.464 | 7.63 | 181.294 | 2235.18 | 25.69 | 42.387 | 6.35 | 1.364 | 4.596 | 8648.76 | 1.897 | 98.1 | 77.1 | 1453 | 21.19 | 5621.7 | 2920.8 | 2725.9 | 4113.7 | 1225.1 | 0.69427 | 5.96
2024-12-10 | 4:04 | Data | 0 | 32.325 | 30.428 | 192.238 | 7.63 | 181.204 | 2233.37 | 25.69 | 42.387 | 6.35 | 1.358 | 4.595 | 8648.76 | 2.019 | 98.1 | 77.2 | 1452 | 21.19 | 5621.7 | 2914.3 | 2792.5 | 4150.6 | 1225.1 | 0.68479 | 5.952
2024-12-10 | 4:04 | Data | 0 | 32.777 | 30.435 | 192.283 | 7.63 | 181.249 | 2230.66 | 25.69 | 42.387 | 6.35 | 1.367 | 4.599 | 8644.24 | 2.066 | 98.1 | 77.1 | 1450 | 21.19 | 5618.8 | 2919.3 | 2822.7 | 4175.2 | 1225.1 | 0.68213 | 5.969
2024-12-10 | 4:04 | Data | 0 | 32.501 | 30.671 | 192.329 | 7.63 | 181.204 | 2227.95 | 25.69 | 42.387 | 6.35 | 1.365 | 4.622 | 8648.76 | 1.796 | 98.1 | 77.2 | 1448 | 21.19 | 5621.7 | 2917.1 | 2803.6 | 4164.7 | 1225.1 | 0.68304 | 5.986
2024-12-10 | 4:04 | Data | 0 | 32.777 | 30.678 | 192.419 | 7.63 | 181.385 | 2227.95 | 25.69 | 42.387 | 6.35 | 1.359 | 4.589 | 8648.76 | 1.992 | 98.1 | 77.1 | 1448 | 21.19 | 5621.7 | 2902.8 | 2820.7 | 4164.5 | 1225.1 | 0.6802 | 5.949
2024-12-10 | 4:04 | Data | 0 | 32.447 | 30.874 | 192.238 | 7.63 | 181.204 | 2227.04 | 25.69 | 42.387 | 6.35 | 1.371 | 4.594 | 8626.15 | 1.803 | 98.1 | 77 | 1448 | 21.19 | 5607 | 2913.4 | 2817.9 | 4167.6 | 1225.1 | 0.68301 | 5.965
2024-12-10 | 4:04 | Data | 0 | 32.44 | 30.766 | 192.374 | 7.63 | 181.249 | 2228.85 | 25.7 | 42.387 | 6.34 | 1.366 | 4.567 | 8617.1 | 1.931 | 98.1 | 77 | 1449 | 21.19 | 5601.1 | 2917.3 | 2796.2 | 4156.6 | 1225.1 | 0.68461 | 5.932
2024-12-10 | 4:04 | Data | 0 | 32.514 | 30.651 | 192.283 | 7.64 | 181.249 | 2230.66 | 25.7 | 42.297 | 6.35 | 1.359 | 4.581 | 8635.19 | 1.85 | 98.1 | 77.1 | 1449 | 21.19 | 5612.9 | 2915.6 | 2807.6 | 4161.2 | 1225.1 | 0.68433 | 5.94
2024-12-10 | 4:04 | Data | 0 | 32.953 | 30.907 | 192.6 | 7.64 | 181.43 | 2230.66 | 25.7 | 42.387 | 6.35 | 1.354 | 4.595 | 8621.63 | 2.046 | 98.1 | 77.2 | 1449 | 21.19 | 5604.1 | 2913.4 | 2811.2 | 4163.5 | 1225.1 | 0.6835 | 5.949
2024-12-10 | 4:04 | Data | 0 | 32.528 | 30.712 | 192.419 | 7.63 | 181.294 | 2230.66 | 25.69 | 42.477 | 6.35 | 1.356 | 4.606 | 8187.49 | 1.958 | 98.1 | 77.3 | 1450 | 21.24 | 5321.9 | 2904 | 2820.6 | 4167.3 | 1225.1 | 0.68032 | 5.961
2024-12-10 | 4:05 | Data | 0 | 33.048 | 30.88 | 192.6 | 7.63 | 181.43 | 2230.66 | 25.69 | 42.477 | 6.35 | 1.367 | 4.593 | 8576.4 | 2.086 | 98.1 | 77.1 | 1449 | 21.19 | 5574.7 | 2916 | 2808.9 | 4167.3 | 1225.1 | 0.68393 | 5.96
2024-12-10 | 4:05 | Data | 0 | 32.696 | 30.664 | 192.51 | 7.63 | 181.385 | 2230.66 | 25.69 | 42.387 | 6.34 | 1.364 | 4.553 | 8571.88 | 1.924 | 98.1 | 77 | 1450 | 21.15 | 5571.7 | 2913.9 | 2789.9 | 4155.9 | 1225.1 | 0.68403 | 5.918
2024-12-10 | 4:05 | Data | 0 | 32.926 | 30.556 | 192.6 | 7.63 | 181.43 | 2229.75 | 25.7 | 42.387 | 6.35 | 1.359 | 4.592 | 8580.93 | 2.127 | 98.1 | 77.2 | 1449 | 21.19 | 5577.6 | 2912.9 | 2811.8 | 4163.2 | 1225.1 | 0.68344 | 5.951
2024-12-10 | 4:05 | Data | 0 | 32.588 | 30.887 | 192.6 | 7.63 | 181.385 | 2229.75 | 25.7 | 42.297 | 6.35 | 1.359 | 4.593 | 8580.93 | 2.16 | 98.1 | 77.2 | 1450 | 21.19 | 5577.6 | 2929.4 | 2816.6 | 4178.5 | 1225.1 | 0.6838 | 5.952
2024-12-10 | 4:05 | Data | 0 | 32.696 | 30.678 | 192.464 | 7.63 | 181.34 | 2229.75 | 25.69 | 42.387 | 6.35 | 1.366 | 4.602 | 8612.58 | 2.012 | 98.1 | 77.1 | 1449 | 21.19 | 5598.2 | 2952.1 | 2811.2 | 4182.3 | 1225.1 | 0.6918 | 5.967
2024-12-10 | 4:05 | Data | 0 | 32.669 | 30.691 | 192.464 | 7.63 | 181.385 | 2225.23 | 25.69 | 42.387 | 6.35 | 1.366 | 4.605 | 8635.19 | 1.985 | 98.1 | 77.1 | 1446 | 21.19 | 5612.9 | 2916.1 | 2817.4 | 4151.6 | 1225.1 | 0.6827 | 5.969
2024-12-10 | 4:05 | Data | 0 | 32.723 | 30.671 | 192.51 | 7.63 | 181.34 | 2228.85 | 25.7 | 42.387 | 6.35 | 1.374 | 4.588 | 8635.19 | 2.052 | 98.1 | 76.9 | 1448 | 21.19 | 5612.9 | 2929.9 | 2817 | 4178.9 | 1225.1 | 0.68454 | 5.963
2024-12-10 | 4:05 | Data | 0 | 32.717 | 30.651 | 192.419 | 7.63 | 181.294 | 2227.04 | 25.7 | 42.568 | 6.35 | 1.361 | 4.58 | 8648.76 | 2.073 | 98.1 | 77.1 | 1448 | 21.24 | 5621.7 | 2910.3 | 2824.7 | 4169.3 | 1225.1 | 0.68128 | 5.941
2024-12-10 | 4:05 | Data | 0 | 32.723 | 30.779 | 192.464 | 7.63 | 181.34 | 2227.95 | 25.69 | 42.477 | 6.35 | 1.358 | 4.613 | 8639.71 | 2.133 | 98.1 | 77.2 | 1448 | 21.19 | 5615.8 | 2917.9 | 2808.8 | 4165.9 | 1225.1 | 0.68473 | 5.97
2024-12-10 | 4:05 | Data | 0 | 32.723 | 30.651 | 192.6 | 7.64 | 181.43 | 2225.23 | 25.69 | 42.387 | 6.35 | 1.373 | 4.622 | 8621.63 | 2.073 | 98.1 | 77.1 | 1446 | 21.19 | 5604.1 | 2898.7 | 2789.6 | 4140.4 | 1225.1 | 0.68295 | 5.995
2024-12-10 | 4:05 | Data | 0 | 32.717 | 30.651 | 192.464 | 7.63 | 181.34 | 2230.66 | 25.69 | 42.116 | 6.34 | 1.364 | 4.606 | 8635.19 | 1.958 | 98.1 | 77.2 | 1450 | 21.06 | 5612.9 | 2907.9 | 2800 | 4153.5 | 1225.1 | 0.68406 | 5.969
2024-12-10 | 4:05 | Data | 0 | 32.723 | 30.968 | 192.69 | 7.63 | 181.294 | 2231.56 | 25.69 | 42.116 | 6.35 | 1.363 | 4.61 | 8635.19 | 1.897 | 98.1 | 77.2 | 1449 | 21.06 | 5612.9 | 2922.9 | 2807.1 | 4172.4 | 1225.1 | 0.68255 | 5.973
2024-12-10 | 4:05 | Data | 0 | 32.561 | 30.745 | 192.464 | 7.63 | 181.385 | 2229.75 | 25.7 | 42.206 | 6.34 | 1.364 | 4.606 | 8648.76 | 1.958 | 98.1 | 77.2 | 1449 | 21.1 | 5621.7 | 2922.8 | 2813.8 | 4171.4 | 1225.1 | 0.68276 | 5.97
2024-12-10 | 4:05 | Data | 0 | 32.609 | 30.766 | 192.51 | 7.63 | 181.385 | 2231.56 | 25.7 | 42.116 | 6.35 | 1.362 | 4.598 | 8648.76 | 1.897 | 98.1 | 77.1 | 1451 | 21.06 | 5621.7 | 2928.8 | 2815.4 | 4179.9 | 1225.1 | 0.68389 | 5.96
2024-12-10 | 4:05 | Data | 0 | 32.386 | 30.421 | 192.51 | 7.63 | 181.294 | 2232.47 | 25.69 | 42.206 | 6.35 | 1.373 | 4.57 | 8648.76 | 2.154 | 98.1 | 76.9 | 1451 | 21.06 | 5621.7 | 2919.3 | 2855.7 | 4196.1 | 1225.1 | 0.68018 | 5.942
2024-12-10 | 4:05 | Data | 0 | 32.332 | 30.637 | 192.51 | 7.63 | 181.385 | 2238.79 | 25.7 | 42.658 | 6.35 | 1.364 | 4.586 | 8648.76 | 1.688 | 98.1 | 77.1 | 1454 | 21.33 | 5621.7 | 2934 | 2841.1 | 4199.4 | 1225.1 | 0.68102 | 5.95
2024-12-10 | 4:05 | Data | 0 | 33.007 | 30.685 | 192.645 | 7.63 | 181.475 | 2233.37 | 25.69 | 42.116 | 6.35 | 1.358 | 4.588 | 8662.33 | 1.884 | 98.1 | 77.2 | 1451 | 21.06 | 5630.5 | 2911 | 2872.1 | 4202.4 | 1225.1 | 0.67537 | 5.946
2024-12-10 | 4:06 | Data | 0 | 32.825 | 30.766 | 192.69 | 7.64 | 181.475 | 2229.75 | 25.69 | 42.116 | 6.36 | 1.363 | 4.607 | 8644.24 | 2.052 | 98.1 | 77.2 | 1450 | 21.06 | 5618.8 | 2927.5 | 2852.6 | 4200.7 | 1225.1 | 0.67904 | 5.969
2024-12-10 | 4:06 | Data | 0 | 32.507 | 30.651 | 192.419 | 7.64 | 181.385 | 2236.08 | 25.69 | 42.116 | 6.35 | 1.361 | 4.613 | 8648.76 | 1.85 | 98.1 | 77.2 | 1453 | 21.06 | 5621.7 | 2908.5 | 2834.9 | 4175.9 | 1225.1 | 0.67877 | 5.974
2024-12-10 | 4:06 | Data | 0 | 32.71 | 30.644 | 192.374 | 7.63 | 181.43 | 2238.79 | 25.7 | 42.116 | 6.34 | 1.366 | 4.602 | 8648.76 | 1.904 | 98.1 | 77.1 | 1456 | 21.06 | 5621.7 | 2916.1 | 2822.2 | 4176.3 | 1225.2 | 0.68044 | 5.967
2024-12-10 | 4:06 | Data | 0 | 32.777 | 30.55 | 192.645 | 7.63 | 181.43 | 2238.79 | 25.7 | 42.116 | 6.35 | 1.362 | 4.611 | 8671.37 | 2.066 | 98.1 | 77.2 | 1456 | 21.1 | 5636.4 | 2939.3 | 2817.3 | 4182.4 | 1225.2 | 0.68594 | 5.973
2024-12-10 | 4:06 | Data | 0 | 32.528 | 30.624 | 192.374 | 7.64 | 181.385 | 2236.98 | 25.69 | 42.116 | 6.35 | 1.367 | 4.598 | 8671.37 | 2.079 | 98.1 | 77.1 | 1456 | 21.06 | 5636.4 | 2914.8 | 2826 | 4185.9 | 1225.2 | 0.68185 | 5.966
2024-12-10 | 4:06 | Data | 0 | 32.75 | 30.448 | 192.419 | 7.64 | 181.385 | 2238.79 | 25.7 | 42.116 | 6.35 | 1.357 | 4.612 | 8671.37 | 2.187 | 98.1 | 77.3 | 1455 | 21.1 | 5636.4 | 2906.7 | 2843.8 | 4174.7 | 1225.2 | 0.67732 | 5.969
2024-12-10 | 4:06 | Data | 0 | 32.71 | 30.82 | 192.51 | 7.63 | 181.34 | 2238.79 | 25.7 | 42.116 | 6.34 | 1.365 | 4.598 | 8662.33 | 1.965 | 98.1 | 77.1 | 1455 | 21.01 | 5630.5 | 2902.2 | 2827.1 | 4169.1 | 1225.2 | 0.68094 | 5.962
2024-12-10 | 4:06 | Data | 0 | 32.433 | 30.651 | 192.419 | 7.63 | 181.34 | 2238.79 | 25.7 | 42.116 | 6.35 | 1.371 | 4.592 | 8671.37 | 1.634 | 98.1 | 77 | 1455 | 21.06 | 5636.4 | 2916.4 | 2831 | 4181.4 | 1225.2 | 0.68065 | 5.963
2024-12-10 | 4:06 | Data | 0 | 32.723 | 30.651 | 192.464 | 7.63 | 181.34 | 2241.5 | 25.69 | 42.026 | 6.35 | 1.369 | 4.616 | 8680.41 | 2.073 | 98.1 | 77.1 | 1457 | 21.06 | 5642.3 | 2920.8 | 2853.7 | 4197.8 | 1225.2 | 0.67917 | 5.985
2024-12-10 | 4:06 | Data | 0 | 32.723 | 30.867 | 192.51 | 7.63 | 181.385 | 2238.79 | 25.69 | 42.206 | 6.35 | 1.358 | 4.588 | 8680.41 | 1.985 | 98.1 | 77.2 | 1455 | 21.06 | 5642.3 | 2924.8 | 2861.6 | 4204.9 | 1225.2 | 0.67797 | 5.948
2024-12-10 | 4:06 | Data | 0 | 32.953 | 31.083 | 192.826 | 7.63 | 181.52 | 2233.37 | 25.7 | 42.387 | 6.34 | 1.365 | 4.576 | 8680.41 | 1.951 | 98.1 | 77 | 1452 | 21.24 | 5642.3 | 2928 | 2845.4 | 4199.5 | 1225.2 | 0.67935 | 5.941
2024-12-10 | 4:06 | Data | 0 | 32.615 | 30.651 | 192.419 | 7.63 | 181.385 | 2236.08 | 25.7 | 42.387 | 6.35 | 1.36 | 4.609 | 8680.41 | 1.897 | 98.1 | 77.2 | 1453 | 21.24 | 5642.3 | 2907.3 | 2853.7 | 4187.3 | 1225.2 | 0.67698 | 5.969
2024-12-10 | 4:06 | Data | 0 | 32.811 | 30.658 | 192.645 | 7.63 | 181.43 | 2233.37 | 25.7 | 42.387 | 6.35 | 1.366 | 4.601 | 8689.46 | 1.877 | 98.1 | 77.1 | 1452 | 21.24 | 5648.1 | 2905.2 | 2851.9 | 4190.6 | 1225.2 | 0.67479 | 5.968
2024-12-10 | 4:06 | Data | 0 | 32.757 | 30.84 | 192.645 | 7.63 | 181.385 | 2232.47 | 25.7 | 42.297 | 6.35 | 1.367 | 4.589 | 8680.41 | 1.931 | 98.1 | 77.1 | 1451 | 21.15 | 5642.3 | 2906.5 | 2844.6 | 4181.8 | 1225.2 | 0.67674 | 5.957
2024-12-10 | 4:06 | Data | 0 | 32.825 | 30.853 | 192.464 | 7.63 | 181.43 | 2232.47 | 25.69 | 42.387 | 6.34 | 1.36 | 4.586 | 8680.41 | 2.12 | 98.1 | 77.1 | 1451 | 21.19 | 5642.3 | 2911.9 | 2844.5 | 4179.8 | 1225.2 | 0.67679 | 5.946
2024-12-10 | 4:06 | Data | 0 | 32.683 | 30.867 | 192.419 | 7.64 | 181.43 | 2233.37 | 25.7 | 42.387 | 6.35 | 1.358 | 4.602 | 8662.33 | 1.884 | 98.1 | 77.2 | 1452 | 21.19 | 5630.5 | 2921.5 | 2837.4 | 4187.3 | 1225.2 | 0.68037 | 5.959
2024-12-10 | 4:06 | Data | 0 | 32.777 | 30.772 | 192.645 | 7.63 | 181.475 | 2236.08 | 25.68 | 42.477 | 6.35 | 1.363 | 4.645 | 8693.98 | 1.958 | 98.1 | 77.3 | 1453 | 21.19 | 5651.1 | 2889.9 | 2843.4 | 4176.7 | 1225.2 | 0.67497 | 6.007
2024-12-10 | 4:06 | Data | 0 | 33.108 | 30.934 | 192.69 | 7.63 | 181.475 | 2235.18 | 25.7 | 42.387 | 6.35 | 1.367 | 4.645 | 8680.41 | 2.086 | 98.1 | 77.3 | 1453 | 21.19 | 5642.3 | 2929.4 | 2841.8 | 4195.5 | 1225.2 | 0.68051 | 6.012
2024-12-10 | 4:07 | Data | 0 | 33.149 | 30.894 | 192.645 | 7.63 | 181.475 | 2236.08 | 25.7 | 42.387 | 6.34 | 1.358 | 4.612 | 8680.41 | 2.147 | 98.1 | 77.2 | 1453 | 21.19 | 5642.3 | 2911.9 | 2880.3 | 4205.5 | 1225.2 | 0.67562 | 5.97
2024-12-10 | 4:07 | Data | 0 | 32.926 | 30.502 | 192.464 | 7.63 | 181.34 | 2234.27 | 25.71 | 42.387 | 6.35 | 1.357 | 4.596 | 8703.03 | 2.181 | 98.1 | 77.2 | 1453 | 21.19 | 5657 | 2918.9 | 2839.7 | 4190.6 | 1225.2 | 0.67799 | 5.95
2024-12-10 | 4:07 | Data | 0 | 32.609 | 30.651 | 192.419 | 7.64 | 181.294 | 2236.08 | 25.69 | 42.297 | 6.35 | 1.359 | 4.579 | 8693.98 | 2.046 | 98.1 | 77.1 | 1453 | 21.15 | 5651.1 | 2933.4 | 2860.2 | 4208.6 | 1225.2 | 0.67572 | 5.938
2024-12-10 | 4:07 | Data | 0 | 32.892 | 30.894 | 192.6 | 7.64 | 181.52 | 2233.37 | 25.69 | 42.387 | 6.34 | 1.361 | 4.618 | 8698.5 | 2.019 | 98.1 | 77.2 | 1452 | 21.19 | 5654 | 2931.4 | 2864.1 | 4212.9 | 1225.2 | 0.67893 | 5.979
2024-12-10 | 4:07 | Data | 0 | 32.838 | 30.988 | 192.6 | 7.63 | 181.475 | 2238.79 | 25.69 | 42.477 | 6.35 | 1.369 | 4.615 | 8703.03 | 1.965 | 98.1 | 77.1 | 1456 | 21.24 | 5657 | 2914.9 | 2866.6 | 4203.3 | 1225.2 | 0.67659 | 5.983
2024-12-10 | 4:07 | Data | 0 | 32.386 | 30.752 | 192.51 | 7.63 | 181.43 | 2229.75 | 25.69 | 42.387 | 6.35 | 1.37 | 4.62 | 8725.64 | 2.025 | 98.1 | 77.1 | 1449 | 21.19 | 5671.7 | 2932.5 | 2843 | 4202.5 | 1225.2 | 0.67976 | 5.992
2024-12-10 | 4:07 | Data | 0 | 32.507 | 30.651 | 192.51 | 7.63 | 181.294 | 2229.75 | 25.69 | 42.387 | 6.35 | 1.369 | 4.614 | 8716.59 | 2.019 | 98.1 | 77.1 | 1449 | 21.19 | 5665.8 | 2920.6 | 2862 | 4203 | 1225.2 | 0.67762 | 5.983
2024-12-10 | 4:07 | Data | 0 | 32.75 | 30.651 | 192.51 | 7.63 | 181.475 | 2226.14 | 25.7 | 42.297 | 6.35 | 1.361 | 4.614 | 8716.59 | 2.079 | 98.1 | 77.2 | 1447 | 21.15 | 5665.8 | 2929.2 | 2866.6 | 4217.8 | 1225.2 | 0.6774 | 5.974
2024-12-10 | 4:07 | Data | 0 | 32.777 | 30.786 | 192.6 | 7.63 | 181.475 | 2224.33 | 25.69 | 42.387 | 6.35 | 1.375 | 4.609 | 8716.59 | 2.052 | 98.1 | 77 | 1446 | 21.19 | 5665.8 | 2900.7 | 2861.5 | 4188.7 | 1225.2 | 0.67671 | 5.983
2024-12-10 | 4:07 | Data | 0 | 32.723 | 30.853 | 192.6 | 7.63 | 181.475 | 2225.23 | 25.69 | 42.387 | 6.35 | 1.373 | 4.614 | 8712.07 | 2.046 | 98.1 | 77.1 | 1446 | 21.19 | 5662.8 | 2926 | 2856.1 | 4206.2 | 1225.2 | 0.67991 | 5.986
2024-12-10 | 4:07 | Data | 0 | 32.723 | 30.705 | 192.329 | 7.63 | 181.249 | 2349.06 | 25.69 | 42.116 | 6.35 | 1.364 | 4.631 | 8716.59 | 1.965 | 98.2 | 77.3 | 1527 | 21.06 | 5665.8 | 2912.9 | 2870.7 | 4204.3 | 1225.2 | 0.67485 | 5.996
2024-12-10 | 4:07 | Data | 0 | 32.609 | 30.651 | 192.6 | 7.63 | 181.43 | 2233.37 | 25.71 | 42.477 | 6.35 | 1.376 | 4.621 | 8730.16 | 1.857 | 98.1 | 77 | 1452 | 21.24 | 5674.6 | 2921.4 | 2860.8 | 4202.6 | 1225.2 | 0.67875 | 5.998
2024-12-10 | 4:07 | Data | 0 | 32.73 | 30.664 | 192.6 | 7.63 | 181.475 | 2233.37 | 25.7 | 42.658 | 6.35 | 1.366 | 4.593 | 8725.64 | 2.046 | 98.1 | 77.1 | 1451 | 21.33 | 5671.7 | 2918 | 2874.5 | 4212.2 | 1225.2 | 0.67508 | 5.96
2024-12-10 | 4:07 | Data | 0 | 32.696 | 30.88 | 192.6 | 7.63 | 181.385 | 2229.75 | 25.7 | 42.387 | 6.35 | 1.374 | 4.607 | 8703.03 | 2.046 | 98.1 | 77 | 1449 | 21.19 | 5657 | 2915 | 2871.5 | 4206.5 | 1225.2 | 0.67639 | 5.983
2024-12-10 | 4:07 | Data | 0 | 32.919 | 30.705 | 192.645 | 7.64 | 181.43 | 2230.66 | 25.71 | 42.297 | 6.35 | 1.361 | 4.616 | 8703.03 | 2.012 | 98.1 | 77.2 | 1450 | 21.15 | 5657 | 2920.7 | 2847.8 | 4196.9 | 1225.2 | 0.67931 | 5.977
2024-12-10 | 4:07 | Data | 0 | 32.946 | 30.766 | 192.51 | 7.63 | 181.475 | 2230.66 | 25.71 | 42.387 | 6.35 | 1.356 | 4.596 | 8716.59 | 1.965 | 98.1 | 77.2 | 1450 | 21.19 | 5665.8 | 2920.8 | 2857.2 | 4201.8 | 1225.2 | 0.67714 | 5.952
2024-12-10 | 4:07 | Data | 0 | 32.676 | 30.583 | 192.419 | 7.63 | 181.43 | 2229.75 | 25.7 | 42.387 | 6.35 | 1.357 | 4.602 | 8707.55 | 2.127 | 98.1 | 77.2 | 1449 | 21.19 | 5659.9 | 2920.1 | 2844.9 | 4190.6 | 1225.2 | 0.67908 | 5.959
2024-12-10 | 4:08 | Data | 0 | 32.98 | 30.88 | 192.69 | 7.63 | 181.52 | 2230.66 | 25.7 | 42.387 | 6.34 | 1.366 | 4.604 | 8703.03 | 1.904 | 98.1 | 77.1 | 1450 | 21.24 | 5657 | 2941.8 | 2839.9 | 4203 | 1225.2 | 0.68313 | 5.969
2024-12-10 | 4:08 | Data | 0 | 33.061 | 30.88 | 192.826 | 7.63 | 181.52 | 2229.75 | 25.71 | 42.477 | 6.35 | 1.366 | 4.591 | 8684.94 | 1.911 | 98.1 | 77.1 | 1449 | 21.19 | 5645.2 | 2918.4 | 2831.2 | 4184.3 | 1225.2 | 0.68078 | 5.957
2024-12-10 | 4:08 | Data | 0 | 32.96 | 30.894 | 192.736 | 7.63 | 181.52 | 2230.66 | 25.72 | 42.297 | 6.34 | 1.362 | 4.595 | 8684.94 | 2.059 | 98.1 | 77.1 | 1450 | 21.19 | 5645.2 | 2920.7 | 2832.6 | 4182.9 | 1225.2 | 0.68187 | 5.957
2024-12-10 | 4:08 | Data | 0 | 32.811 | 31.245 | 192.69 | 7.63 | 181.385 | 2227.04 | 25.71 | 42.387 | 6.35 | 1.362 | 4.621 | 8666.85 | 2.052 | 98.1 | 77.2 | 1448 | 21.19 | 5633.5 | 2929 | 2838.8 | 4195.8 | 1225.3 | 0.68066 | 5.983
2024-12-10 | 4:08 | Data | 0 | 32.723 | 30.941 | 192.464 | 7.63 | 181.43 | 2227.95 | 25.72 | 42.387 | 6.35 | 1.37 | 4.585 | 8662.33 | 1.958 | 98.1 | 77 | 1448 | 21.19 | 5630.5 | 2908.6 | 2845.4 | 4182.4 | 1225.3 | 0.6774 | 5.955
2024-12-10 | 4:08 | Data | 0 | 32.73 | 30.982 | 192.69 | 7.63 | 181.43 | 2227.04 | 25.71 | 42.297 | 6.34 | 1.364 | 4.602 | 8648.76 | 2.012 | 98.1 | 77.1 | 1448 | 21.19 | 5621.7 | 2886.6 | 2881 | 4197.3 | 1225.3 | 0.66997 | 5.965
2024-12-10 | 4:08 | Data | 0 | 32.723 | 31.063 | 192.645 | 7.63 | 181.43 | 2230.66 | 25.71 | 42.387 | 6.35 | 1.355 | 4.602 | 8653.28 | 1.823 | 98.1 | 77.3 | 1449 | 21.19 | 5624.6 | 2921 | 2854 | 4201.5 | 1225.3 | 0.6785 | 5.958
2024-12-10 | 4:08 | Data | 0 | 32.696 | 30.968 | 192.645 | 7.63 | 181.52 | 2227.95 | 25.7 | 42.387 | 6.35 | 1.363 | 4.615 | 8644.24 | 2.059 | 98.1 | 77.2 | 1448 | 21.19 | 5618.8 | 2922.7 | 2849.4 | 4196.1 | 1225.3 | 0.67877 | 5.978
2024-12-10 | 4:08 | Data | 0 | 33.122 | 30.988 | 192.736 | 7.63 | 181.475 | 2227.95 | 25.7 | 42.387 | 6.34 | 1.362 | 4.636 | 8630.67 | 1.951 | 98.1 | 77.3 | 1448 | 21.19 | 5609.9 | 2900.4 | 2829.6 | 4160.7 | 1225.3 | 0.67895 | 5.999
2024-12-10 | 4:08 | Data | 0 | 32.615 | 30.772 | 192.69 | 7.63 | 181.475 | 2227.95 | 25.71 | 42.387 | 6.35 | 1.363 | 4.609 | 8608.06 | 2.16 | 98.1 | 77.2 | 1448 | 21.19 | 5595.2 | 2932.1 | 2835.6 | 4193.9 | 1225.3 | 0.68096 | 5.97
2024-12-10 | 4:08 | Data | 0 | 32.98 | 30.88 | 192.69 | 7.63 | 181.475 | 2227.04 | 25.71 | 42.387 | 6.35 | 1.355 | 4.598 | 8612.58 | 1.762 | 98.1 | 77.2 | 1448 | 21.15 | 5598.2 | 2934.5 | 2838.2 | 4191.2 | 1225.3 | 0.67964 | 5.954
2024-12-10 | 4:08 | Data | 0 | 32.899 | 30.664 | 192.51 | 7.63 | 181.475 | 2227.04 | 25.71 | 42.387 | 6.34 | 1.363 | 4.633 | 8621.63 | 2.059 | 98.1 | 77.3 | 1448 | 21.15 | 5604.1 | 2916 | 2825.1 | 4178.4 | 1225.3 | 0.68031 | 5.996
2024-12-10 | 4:08 | Data | 0 | 33.223 | 30.901 | 192.69 | 7.63 | 181.52 | 2226.14 | 25.71 | 42.387 | 6.35 | 1.364 | 4.605 | 8621.63 | 2.127 | 98.1 | 77.1 | 1447 | 21.19 | 5604.1 | 2921.9 | 2842.1 | 4189.1 | 1225.3 | 0.67951 | 5.969
2024-12-10 | 4:08 | Data | 0 | 32.622 | 30.826 | 192.6 | 7.63 | 181.385 | 2225.23 | 25.71 | 42.477 | 6.34 | 1.377 | 4.614 | 8644.24 | 1.931 | 98.1 | 77 | 1446 | 21.19 | 5618.8 | 2898.8 | 2848.3 | 4182 | 1225.3 | 0.67741 | 5.991
2024-12-10 | 4:08 | Data | 0 | 32.73 | 30.658 | 192.464 | 7.63 | 181.385 | 2218.91 | 25.71 | 42.387 | 6.35 | 1.374 | 4.616 | 8648.76 | 2.066 | 98.1 | 77.1 | 1443 | 21.19 | 5621.7 | 2913.1 | 2848.5 | 4188.8 | 1225.3 | 0.67772 | 5.991
2024-12-10 | 4:08 | Data | 0 | 32.784 | 30.826 | 192.645 | 7.63 | 181.475 | 2222.52 | 25.71 | 42.387 | 6.34 | 1.371 | 4.613 | 8621.63 | 1.688 | 98.1 | 77.1 | 1445 | 21.19 | 5604.1 | 2237.9 | 2774.3 | 3587.2 | 1225.3 | 0.62803 | 5.985
2024-12-10 | 4:08 | Data | 0 | 32.831 | 30.651 | 192.645 | 7.63 | 181.475 | 2223.43 | 25.72 | 42.387 | 6.35 | 1.358 | 4.603 | 8621.63 | 2.093 | 98.1 | 77.2 | 1446 | 21.24 | 5604.1 | 1811.4 | 2316.6 | 2951.6 | 1225.3 | 0.61188 | 5.961
2024-12-10 | 4:08 | Data | 0 | 32.737 | 30.671 | 192.69 | 7.63 | 181.43 | 2222.52 | 25.71 | 42.387 | 6.35 | 1.362 | 4.599 | 8644.24 | 1.998 | 98.1 | 77.1 | 1445 | 21.19 | 5618.8 | 1837.8 | 2310.5 | 2963 | 1225.3 | 0.61758 | 5.962
2024-12-10 | 4:09 | Data | 0 | 32.528 | 30.766 | 192.6 | 7.63 | 181.52 | 2224.33 | 25.72 | 42.387 | 6.35 | 1.358 | 4.598 | 8644.24 | 2.019 | 98.1 | 77.2 | 1446 | 21.19 | 5618.8 | 1837 | 2335.4 | 2981.4 | 1225.3 | 0.61355 | 5.957
2024-12-10 | 4:09 | Data | 0 | 32.94 | 30.894 | 192.645 | 7.63 | 181.52 | 2228.85 | 25.71 | 42.387 | 6.35 | 1.373 | 4.581 | 8621.63 | 2.052 | 98.1 | 77 | 1448 | 21.15 | 5604.1 | 1831.3 | 2278.6 | 2934.4 | 1225.3 | 0.62145 | 5.953
2024-12-10 | 4:09 | Data | 0 | 32.73 | 31.184 | 192.69 | 7.63 | 181.475 | 2227.95 | 25.71 | 42.477 | 6.35 | 1.367 | 4.626 | 8644.24 | 1.877 | 98.1 | 77.2 | 1448 | 21.24 | 5618.8 | 1822.4 | 2269.3 | 2922.1 | 1225.3 | 0.62125 | 5.992
2024-12-10 | 4:09 | Data | 0 | 32.919 | 31.076 | 192.51 | 7.63 | 181.43 | 2225.23 | 25.71 | 42.387 | 6.35 | 1.365 | 4.6 | 8635.19 | 1.971 | 98.1 | 77.1 | 1446 | 21.19 | 5612.9 | 1833.3 | 2284.7 | 2942 | 1225.3 | 0.62079 | 5.965
2024-12-10 | 4:09 | Data | 0 | 32.777 | 30.658 | 192.645 | 7.63 | 181.43 | 2224.33 | 25.69 | 42.297 | 6.35 | 1.354 | 4.554 | 8639.71 | 2.059 | 98.1 | 77.1 | 1446 | 21.19 | 5615.8 | 1843 | 2266.1 | 2933.1 | 1225.3 | 0.62538 | 5.908
2024-12-10 | 4:09 | Data | 0 | 32.723 | 30.826 | 192.419 | 7.63 | 181.43 | 2224.33 | 25.69 | 42.297 | 6.34 | 1.367 | 4.605 | 8648.76 | 2.127 | 98.1 | 77.1 | 1446 | 21.19 | 5621.7 | 1825 | 2270.8 | 2932.4 | 1225.3 | 0.62413 | 5.971
2024-12-10 | 4:09 | Data | 0 | 32.946 | 30.766 | 192.6 | 7.63 | 181.43 | 2225.23 | 25.7 | 42.297 | 6.35 | 1.367 | 4.622 | 8653.28 | 2.093 | 98.1 | 77.2 | 1446 | 21.15 | 5624.6 | 1848 | 2299.7 | 2962.3 | 1225.3 | 0.61864 | 5.988
2024-12-10 | 4:09 | Data | 0 | 33.122 | 30.934 | 192.6 | 7.63 | 181.43 | 2232.47 | 25.69 | 42.477 | 6.35 | 1.363 | 4.611 | 8662.33 | 2.052 | 98.1 | 77.2 | 1451 | 21.19 | 5630.5 | 1831.9 | 2300.8 | 2950.5 | 1225.3 | 0.6188 | 5.974
2024-12-10 | 4:09 | Data | 0 | 32.892 | 30.806 | 192.736 | 7.63 | 181.52 | 2232.47 | 25.7 | 42.387 | 6.35 | 1.367 | 4.615 | 8648.76 | 2.316 | 98.1 | 77.2 | 1451 | 21.24 | 5621.7 | 1853.3 | 2333.5 | 2991.4 | 1225.3 | 0.61656 | 5.981
2024-12-10 | 4:09 | Data | 0 | 32.615 | 30.826 | 192.645 | 7.63 | 181.475 | 2229.75 | 25.69 | 42.387 | 6.35 | 1.369 | 4.604 | 8657.8 | 1.89 | 98.1 | 77.1 | 1450 | 21.19 | 5627.6 | 1844 | 2295.2 | 2957.1 | 1225.3 | 0.62025 | 5.974
2024-12-10 | 4:09 | Data | 0 | 32.953 | 30.766 | 192.645 | 7.63 | 181.43 | 2232.47 | 25.69 | 42.387 | 6.34 | 1.365 | 4.596 | 8648.76 | 1.897 | 98.1 | 77.1 | 1451 | 21.24 | 5621.7 | 1847.5 | 2312.8 | 2971.4 | 1225.3 | 0.61844 | 5.961
2024-12-10 | 4:09 | Data | 0 | 32.926 | 30.786 | 192.6 | 7.63 | 181.43 | 2233.37 | 25.71 | 42.297 | 6.35 | 1.364 | 4.612 | 8657.8 | 1.971 | 98.1 | 77.2 | 1452 | 21.15 | 5627.6 | 1862 | 2301.2 | 2971 | 1225.3 | 0.62426 | 5.977
2024-12-10 | 4:09 | Data | 0 | 32.811 | 30.664 | 192.464 | 7.63 | 181.385 | 2232.47 | 25.69 | 42.477 | 6.35 | 1.371 | 4.646 | 8662.33 | 2.228 | 98.1 | 77.2 | 1451 | 21.24 | 5630.5 | 1829.2 | 2301.3 | 2951.9 | 1225.3 | 0.61748 | 6.017
2024-12-10 | 4:09 | Data | 0 | 32.568 | 30.678 | 192.51 | 7.63 | 181.385 | 2232.47 | 25.7 | 42.297 | 6.35 | 1.362 | 4.645 | 8648.76 | 1.735 | 98.1 | 77.3 | 1452 | 21.19 | 5621.7 | 1839.5 | 2293.1 | 2950.5 | 1225.3 | 0.62116 | 6.006
2024-12-10 | 4:09 | Data | 0 | 32.723 | 30.651 | 192.6 | 7.63 | 181.34 | 2234.27 | 25.69 | 42.477 | 6.35 | 1.352 | 4.607 | 8657.8 | 2.073 | 98.1 | 77.3 | 1452 | 21.24 | 5627.6 | 1825.6 | 2282.7 | 2934.6 | 1225.3 | 0.61972 | 5.96
2024-12-10 | 4:09 | Data | 0 | 32.669 | 30.658 | 192.6 | 7.63 | 181.385 | 2235.18 | 25.69 | 42.387 | 6.35 | 1.357 | 4.599 | 8635.19 | 2.046 | 98.1 | 77.2 | 1453 | 21.19 | 5612.9 | 1832.1 | 2260.8 | 2922.2 | 1225.3 | 0.62432 | 5.956
2024-12-10 | 4:09 | Data | 0 | 32.521 | 30.712 | 192.6 | 7.63 | 181.385 | 2235.18 | 25.7 | 42.297 | 6.35 | 1.358 | 4.597 | 8639.71 | 2.079 | 98.1 | 77.2 | 1453 | 21.19 | 5615.8 | 1845.3 | 2279.6 | 2944.9 | 1225.3 | 0.62391 | 5.954
2024-12-10 | 4:09 | Data | 0 | 32.784 | 31.029 | 192.6 | 7.63 | 181.385 | 2229.75 | 25.7 | 42.387 | 6.35 | 1.364 | 4.6 | 8635.19 | 1.998 | 98.1 | 77.1 | 1450 | 21.19 | 5612.9 | 1826.9 | 2307.3 | 2955.2 | 1225.3 | 0.61613 | 5.963
2024-12-10 | 4:10 | Data | 0 | 32.555 | 30.651 | 192.645 | 7.63 | 181.385 | 2230.66 | 25.7 | 42.297 | 6.34 | 1.36 | 4.6 | 8653.28 | 1.863 | 98.1 | 77.2 | 1450 | 21.19 | 5624.6 | 1839.1 | 2302.5 | 2957.3 | 1225.3 | 0.62291 | 5.96
2024-12-10 | 4:10 | Data | 0 | 32.696 | 30.766 | 192.464 | 7.63 | 181.294 | 2233.37 | 25.69 | 42.387 | 6.35 | 1.354 | 4.58 | 8648.76 | 1.87 | 98.1 | 77.2 | 1451 | 21.19 | 5621.7 | 1828.8 | 2319.3 | 2964.3 | 1225.3 | 0.61435 | 5.934
2024-12-10 | 4:10 | Data | 0 | 32.71 | 31.09 | 192.6 | 7.63 | 181.475 | 2230.66 | 25.7 | 42.929 | 6.35 | 1.362 | 4.582 | 8662.33 | 1.823 | 98.1 | 77.1 | 1450 | 21.46 | 5630.5 | 1829.6 | 2337.9 | 2979.8 | 1225.3 | 0.61178 | 5.943
2024-12-10 | 4:10 | Data | 0 | 33.054 | 30.928 | 192.6 | 7.64 | 181.475 | 2233.37 | 25.7 | 42.387 | 6.35 | 1.367 | 4.606 | 8662.33 | 2.059 | 98.1 | 77.1 | 1452 | 21.19 | 5630.5 | 1843.2 | 2342.2 | 2993.9 | 1225.3 | 0.61378 | 5.971
2024-12-10 | 4:10 | Data | 0 | 32.528 | 30.826 | 192.464 | 7.63 | 181.43 | 2233.37 | 25.69 | 42.387 | 6.35 | 1.357 | 4.598 | 8644.24 | 1.735 | 98.1 | 77.2 | 1451 | 21.19 | 5618.8 | 1826.5 | 2298.9 | 2947.4 | 1225.3 | 0.61757 | 5.953
2024-12-10 | 4:10 | Data | 0 | 32.879 | 31.103 | 192.6 | 7.63 | 181.43 | 2236.08 | 25.69 | 42.387 | 6.34 | 1.357 | 4.594 | 8644.24 | 2.052 | 98.1 | 77.2 | 1453 | 21.19 | 5618.8 | 1834.4 | 2302.2 | 2953.9 | 1225.3 | 0.61892 | 5.95
2024-12-10 | 4:10 | Data | 0 | 32.69 | 30.82 | 192.645 | 7.63 | 181.43 | 2235.18 | 25.7 | 42.477 | 6.35 | 1.358 | 4.586 | 8635.19 | 2.12 | 98.1 | 77.1 | 1453 | 21.24 | 5612.9 | 1831.6 | 2296.9 | 2950.5 | 1225.3 | 0.61798 | 5.944
2024-12-10 | 4:10 | Data | 0 | 32.953 | 30.982 | 192.645 | 7.63 | 181.52 | 2235.18 | 25.7 | 42.387 | 6.34 | 1.36 | 4.626 | 8635.19 | 1.87 | 98.1 | 77.3 | 1453 | 21.19 | 5612.9 | 1836.9 | 2281.4 | 2939.3 | 1225.3 | 0.623 | 5.987
2024-12-10 | 4:10 | Data | 0 | 32.609 | 30.651 | 192.6 | 7.63 | 181.43 | 2235.18 | 25.7 | 42.387 | 6.35 | 1.367 | 4.61 | 8635.19 | 2.174 | 98.1 | 77.1 | 1453 | 21.19 | 5612.9 | 1835.9 | 2273.6 | 2936.3 | 1225.3 | 0.62142 | 5.979
2024-12-10 | 4:10 | Data | 0 | 32.723 | 30.651 | 192.464 | 7.63 | 181.385 | 2227.95 | 25.69 | 42.387 | 6.35 | 1.364 | 4.611 | 8639.71 | 2.066 | 98.1 | 77.2 | 1448 | 21.19 | 5615.8 | 1832.5 | 2290 | 2944.3 | 1225.3 | 0.61967 | 5.973
2024-12-10 | 4:10 | Data | 0 | 32.865 | 30.435 | 192.51 | 7.63 | 181.475 | 2231.56 | 25.7 | 42.297 | 6.35 | 1.362 | 4.602 | 8635.19 | 1.938 | 98.1 | 77.2 | 1450 | 21.19 | 5612.9 | 1844.7 | 2290.3 | 2953.2 | 1225.3 | 0.62223 | 5.964
2024-12-10 | 4:10 | Data | 0 | 32.669 | 30.475 | 192.419 | 7.63 | 181.294 | 2232.47 | 25.7 | 42.387 | 6.35 | 1.366 | 4.605 | 8639.71 | 2.073 | 98.1 | 77.1 | 1451 | 21.24 | 5615.8 | 1847.2 | 2326.8 | 2980.8 | 1225.3 | 0.61598 | 5.97
2024-12-10 | 4:10 | Data | 0 | 32.919 | 31.042 | 192.464 | 7.63 | 181.43 | 2228.85 | 25.69 | 42.387 | 6.34 | 1.365 | 4.628 | 8635.19 | 1.958 | 98.1 | 77.2 | 1448 | 21.24 | 5612.9 | 1825.8 | 2346.4 | 2983.7 | 1225.3 | 0.61009 | 5.993
2024-12-10 | 4:10 | Data | 0 | 32.899 | 30.793 | 192.6 | 7.63 | 181.385 | 2227.04 | 25.69 | 42.477 | 6.35 | 1.357 | 4.595 | 8635.19 | 1.897 | 98.1 | 77.2 | 1448 | 21.24 | 5612.9 | 1855.4 | 2317.9 | 2980.1 | 1225.3 | 0.61941 | 5.951
2024-12-10 | 4:10 | Data | 0 | 32.737 | 30.651 | 192.51 | 7.63 | 181.385 | 2230.66 | 25.69 | 42.297 | 6.35 | 1.362 | 4.616 | 8662.33 | 1.897 | 98.1 | 77.2 | 1450 | 21.15 | 5630.5 | 1825.3 | 2296 | 2949.6 | 1225.3 | 0.61715 | 5.978
2024-12-10 | 4:10 | Data | 0 | 32.946 | 30.793 | 192.6 | 7.63 | 181.475 | 2226.14 | 25.69 | 42.297 | 6.35 | 1.366 | 4.592 | 8662.33 | 1.978 | 98.1 | 77.1 | 1446 | 21.15 | 5630.5 | 1830.7 | 2287 | 2948.9 | 1225.3 | 0.62228 | 5.958
2024-12-10 | 4:10 | Data | 0 | 32.953 | 30.658 | 192.419 | 7.63 | 181.43 | 2225.23 | 25.7 | 42.387 | 6.35 | 1.362 | 4.605 | 8657.8 | 1.904 | 98.1 | 77.2 | 1446 | 21.19 | 5627.6 | 1842.1 | 2276.7 | 2939.5 | 1225.3 | 0.62437 | 5.967
2024-12-10 | 4:10 | Data | 0 | 32.696 | 30.874 | 192.645 | 7.63 | 181.385 | 2226.14 | 25.69 | 42.477 | 6.35 | 1.359 | 4.596 | 8657.8 | 2.012 | 98.1 | 77.2 | 1447 | 21.19 | 5627.6 | 1844.3 | 2264.4 | 2930.1 | 1225.3 | 0.62719 | 5.955
2024-12-10 | 4:11 | Data | 0 | 32.609 | 30.651 | 192.464 | 7.63 | 181.385 | 2227.95 | 25.69 | 42.387 | 6.35 | 1.349 | 4.583 | 8680.41 | 1.87 | 98.1 | 77.3 | 1448 | 21.19 | 5642.3 | 1833.6 | 2244.5 | 2917.5 | 1225.4 | 0.62912 | 5.933
2024-12-10 | 4:11 | Data | 0 | 32.838 | 30.766 | 192.419 | 7.63 | 181.43 | 2232.47 | 25.69 | 42.387 | 6.35 | 1.349 | 4.604 | 8666.85 | 1.87 | 98.1 | 77.3 | 1451 | 21.24 | 5633.5 | 1848 | 2268.2 | 2937 | 1225.4 | 0.62558 | 5.952
2024-12-10 | 4:11 | Data | 0 | 32.94 | 30.435 | 192.374 | 7.63 | 181.385 | 2239.7 | 25.7 | 42.387 | 6.35 | 1.358 | 4.593 | 8671.37 | 2.275 | 98.1 | 77.2 | 1455 | 21.19 | 5636.4 | 1841 | 2256.7 | 2923 | 1225.4 | 0.62785 | 5.95
2024-12-10 | 4:11 | Data | 0 | 32.609 | 30.442 | 192.419 | 7.63 | 181.385 | 2229.75 | 25.7 | 42.387 | 6.35 | 1.363 | 4.598 | 8662.33 | 2.032 | 98.1 | 77.1 | 1449 | 21.15 | 5630.5 | 1835 | 2298.6 | 2951.8 | 1225.4 | 0.61916 | 5.96
2024-12-10 | 4:11 | Data | 0 | 32.723 | 30.874 | 192.464 | 7.63 | 181.385 | 2238.79 | 25.69 | 42.297 | 6.35 | 1.36 | 4.594 | 8635.19 | 2.059 | 98.1 | 77.2 | 1456 | 21.19 | 5612.9 | 1830.5 | 2289.2 | 2942.7 | 1225.4 | 0.61891 | 5.954
2024-12-10 | 4:11 | Data | 0 | 32.723 | 30.651 | 192.464 | 7.63 | 181.34 | 2239.7 | 25.69 | 42.387 | 6.34 | 1.358 | 4.588 | 8635.19 | 2.066 | 98.1 | 77.2 | 1455 | 21.19 | 5612.9 | 1838.7 | 2295.7 | 2951 | 1225.4 | 0.62054 | 5.946
2024-12-10 | 4:11 | Data | 0 | 32.521 | 30.604 | 192.329 | 7.63 | 181.249 | 2238.79 | 25.7 | 42.387 | 6.35 | 1.363 | 4.595 | 8630.67 | 2.194 | 98.1 | 77.1 | 1456 | 21.24 | 5609.9 | 1834.1 | 2289.5 | 2944.4 | 1225.4 | 0.62023 | 5.957
2024-12-10 | 4:11 | Data | 0 | 32.507 | 30.739 | 192.374 | 7.63 | 181.249 | 2238.79 | 25.69 | 42.387 | 6.35 | 1.36 | 4.582 | 8635.19 | 2.012 | 98.1 | 77.1 | 1455 | 21.19 | 5612.9 | 1830.4 | 2287.9 | 2941.8 | 1225.4 | 0.61839 | 5.942
2024-12-10 | 4:11 | Data | 0 | 32.771 | 30.57 | 192.51 | 7.63 | 181.385 | 2238.79 | 25.7 | 42.387 | 6.34 | 1.357 | 4.577 | 8671.37 | 2.248 | 98.1 | 77.1 | 1455 | 21.19 | 5636.4 | 1831.4 | 2285.5 | 2941.4 | 1225.4 | 0.61869 | 5.931
2024-12-10 | 4:11 | Data | 0 | 32.737 | 30.651 | 192.374 | 7.63 | 181.294 | 2230.66 | 25.7 | 42.387 | 6.35 | 1.365 | 4.595 | 8662.33 | 2.066 | 98.1 | 77.1 | 1450 | 21.19 | 5630.5 | 1837.2 | 2268.7 | 2930.5 | 1225.4 | 0.62469 | 5.96
2024-12-10 | 4:11 | Data | 0 | 32.865 | 30.88 | 192.645 | 7.63 | 181.385 | 2235.18 | 25.69 | 42.477 | 6.34 | 1.366 | 4.592 | 8657.8 | 2.262 | 98.1 | 77.1 | 1453 | 21.19 | 5627.6 | 1809 | 2255.2 | 2900.8 | 1225.4 | 0.62404 | 5.958
2024-12-10 | 4:11 | Data | 0 | 32.811 | 30.88 | 192.51 | 7.63 | 181.385 | 2236.08 | 25.69 | 42.477 | 6.35 | 1.358 | 4.595 | 8653.28 | 2.059 | 98.1 | 77.2 | 1453 | 21.24 | 5624.6 | 2079.4 | 2893.9 | 3626.7 | 1225.4 | 0.60228 | 5.953
2024-12-10 | 4:11 | Data | 0 | 32.447 | 30.624 | 192.6 | 7.63 | 181.34 | 2238.79 | 25.69 | 42.387 | 6.35 | 1.373 | 4.588 | 8648.76 | 2.066 | 98.1 | 77 | 1455 | 21.19 | 5621.7 | 2919.9 | 2836.9 | 4188.9 | 1225.4 | 0.67977 | 5.961
2024-12-10 | 4:11 | Data | 0 | 32.723 | 30.448 | 192.464 | 7.63 | 181.385 | 2238.79 | 25.69 | 42.387 | 6.35 | 1.374 | 4.598 | 8657.8 | 2.052 | 98.1 | 77 | 1456 | 21.19 | 5627.6 | 2909.2 | 2852.6 | 4194.5 | 1225.4 | 0.68079 | 5.971
2024-12-10 | 4:11 | Data | 0 | 32.696 | 30.745 | 192.419 | 7.63 | 181.385 | 2235.18 | 25.7 | 42.297 | 6.35 | 1.362 | 4.614 | 8648.76 | 2.113 | 98.1 | 77.2 | 1453 | 21.19 | 5621.7 | 2917.3 | 2858.1 | 4207.6 | 1225.4 | 0.67901 | 5.975
2024-12-10 | 4:11 | Data | 0 | 32.94 | 30.678 | 192.464 | 7.63 | 181.34 | 2236.98 | 25.7 | 42.477 | 6.35 | 1.366 | 4.601 | 8657.8 | 2.073 | 98.1 | 77.1 | 1455 | 21.24 | 5627.6 | 2908.1 | 2848.3 | 4187.7 | 1225.4 | 0.67713 | 5.966
2024-12-10 | 4:11 | Data | 0 | 32.494 | 30.624 | 192.374 | 7.63 | 181.294 | 2236.98 | 25.69 | 42.387 | 6.36 | 1.372 | 4.606 | 8657.8 | 1.87 | 98.1 | 77 | 1454 | 21.19 | 5627.6 | 2922.3 | 2846.7 | 4196.4 | 1225.4 | 0.67931 | 5.979
2024-12-10 | 4:12 | Data | 0 | 32.69 | 30.759 | 192.374 | 7.63 | 181.294 | 2239.7 | 25.69 | 42.387 | 6.35 | 1.36 | 4.612 | 8657.8 | 1.958 | 98.1 | 77.2 | 1455 | 21.19 | 5627.6 | 2895.5 | 2836 | 4170.3 | 1225.4 | 0.6767 | 5.972
2024-12-10 | 4:12 | Data | 0 | 32.494 | 30.421 | 192.329 | 7.63 | 181.294 | 2238.79 | 25.7 | 42.387 | 6.35 | 1.362 | 4.616 | 8657.8 | 2.066 | 98.1 | 77.2 | 1456 | 21.19 | 5627.6 | 2944.2 | 2853.8 | 4210.3 | 1225.4 | 0.67993 | 5.979
2024-12-10 | 4:12 | Data | 0 | 32.514 | 30.543 | 192.51 | 7.63 | 181.34 | 2236.08 | 25.69 | 42.387 | 6.35 | 1.365 | 4.621 | 8639.71 | 2.066 | 98.1 | 77.2 | 1453 | 21.19 | 5615.8 | 2943.6 | 2856.3 | 4220.3 | 1225.4 | 0.67961 | 5.986
2024-12-10 | 4:12 | Data | 0 | 32.501 | 30.462 | 192.464 | 7.63 | 181.294 | 2232.47 | 25.69 | 42.387 | 6.35 | 1.361 | 4.603 | 8621.63 | 1.992 | 98.1 | 77.2 | 1451 | 21.19 | 5604.1 | 2928.3 | 2858.8 | 4211.5 | 1225.4 | 0.68044 | 5.963
2024-12-10 | 4:12 | Data | 0 | 32.494 | 30.428 | 192.374 | 7.63 | 181.249 | 2230.66 | 25.67 | 42.387 | 6.35 | 1.354 | 4.605 | 8621.63 | 2.052 | 98.1 | 77.3 | 1450 | 21.19 | 5604.1 | 2917.8 | 2846.5 | 4196.9 | 1225.4 | 0.67656 | 5.959
2024-12-10 | 4:12 | Data | 0 | 32.521 | 30.651 | 192.51 | 7.63 | 181.294 | 2230.66 | 25.67 | 42.477 | 6.35 | 1.362 | 4.598 | 8621.63 | 1.85 | 98.1 | 77.1 | 1449 | 21.19 | 5604.1 | 2957 | 2814.1 | 4201.1 | 1225.4 | 0.68684 | 5.96
2024-12-10 | 4:12 | Data | 0 | 32.723 | 30.651 | 192.51 | 7.63 | 181.34 | 2238.79 | 25.68 | 42.387 | 6.35 | 1.366 | 4.58 | 8621.63 | 2.073 | 98.1 | 77 | 1456 | 21.24 | 5604.1 | 2935.2 | 2866.3 | 4211.3 | 1225.4 | 0.67674 | 5.947
2024-12-10 | 4:12 | Data | 0 | 32.595 | 30.867 | 192.464 | 7.63 | 181.294 | 2229.75 | 25.68 | 42.477 | 6.35 | 1.37 | 4.616 | 8635.19 | 1.904 | 98.1 | 77.1 | 1450 | 21.24 | 5612.9 | 2956.6 | 2857 | 4225.7 | 1225.4 | 0.68276 | 5.986
2024-12-10 | 4:12 | Data | 0 | 32.413 | 30.523 | 192.374 | 7.63 | 181.385 | 2230.66 | 25.67 | 42.297 | 6.35 | 1.377 | 4.587 | 8635.19 | 1.661 | 98.1 | 76.9 | 1450 | 21.19 | 5612.9 | 2942.8 | 2833.1 | 4202.3 | 1225.4 | 0.6826 | 5.963
2024-12-10 | 4:12 | Data | 0 | 32.494 | 30.624 | 192.329 | 7.63 | 181.204 | 2227.95 | 25.67 | 42.297 | 6.35 | 1.367 | 4.603 | 8635.19 | 1.904 | 98.1 | 77.1 | 1448 | 21.19 | 5612.9 | 2947 | 2854.9 | 4219.4 | 1225.4 | 0.6803 | 5.969
2024-12-10 | 4:12 | Data | 0 | 32.548 | 30.536 | 192.419 | 7.63 | 181.294 | 2227.95 | 25.68 | 42.387 | 6.35 | 1.366 | 4.604 | 8635.19 | 1.965 | 98.1 | 77.1 | 1448 | 21.19 | 5612.9 | 2925.1 | 2865.6 | 4221.7 | 1225.4 | 0.67464 | 5.969
2024-12-10 | 4:12 | Data | 0 | 32.285 | 30.955 | 192.51 | 7.64 | 181.385 | 2227.04 | 25.68 | 42.387 | 6.35 | 1.372 | 4.615 | 8635.19 | 1.877 | 98.1 | 77.1 | 1448 | 21.19 | 5612.9 | 2935 | 2853.7 | 4215 | 1225.4 | 0.68015 | 5.988
2024-12-10 | 4:12 | Data | 0 | 32.723 | 30.705 | 192.419 | 7.63 | 181.385 | 2227.95 | 25.67 | 42.387 | 6.35 | 1.358 | 4.61 | 8635.19 | 2.019 | 98.1 | 77.3 | 1448 | 21.24 | 5612.9 | 2955.8 | 2867.9 | 4238.3 | 1225.4 | 0.67902 | 5.968
2024-12-10 | 4:12 | Data | 0 | 32.696 | 30.475 | 192.419 | 7.63 | 181.249 | 2232.47 | 25.68 | 42.477 | 6.35 | 1.365 | 4.62 | 8635.19 | 2.073 | 98.1 | 77.2 | 1452 | 21.19 | 5612.9 | 2942.3 | 2885.3 | 4238.2 | 1225.4 | 0.67748 | 5.985
2024-12-10 | 4:12 | Data | 0 | 32.386 | 30.415 | 192.51 | 7.63 | 181.34 | 2234.27 | 25.67 | 42.387 | 6.34 | 1.359 | 4.595 | 8648.76 | 1.992 | 98.1 | 77.2 | 1452 | 21.19 | 5621.7 | 2930.2 | 2849.6 | 4204.4 | 1225.4 | 0.67941 | 5.953
2024-12-10 | 4:12 | Data | 0 | 32.501 | 30.59 | 192.419 | 7.63 | 181.249 | 2231.56 | 25.68 | 42.477 | 6.34 | 1.356 | 4.619 | 8648.76 | 2.073 | 98.1 | 77.3 | 1451 | 21.24 | 5621.7 | 2942.5 | 2845.1 | 4217.2 | 1225.4 | 0.67961 | 5.976
2024-12-10 | 4:12 | Data | 0 | 32.636 | 30.415 | 192.419 | 7.63 | 181.34 | 2232.47 | 25.68 | 42.387 | 6.34 | 1.365 | 4.635 | 8639.71 | 2.079 | 98.1 | 77.3 | 1452 | 21.19 | 5615.8 | 2963.7 | 2850 | 4228.5 | 1225.4 | 0.68395 | 5.999
2024-12-10 | 4:12 | Data | 0 | 32.777 | 30.752 | 192.464 | 7.63 | 181.385 | 2234.27 | 25.67 | 42.297 | 6.35 | 1.361 | 4.597 | 8635.19 | 1.877 | 98.1 | 77.2 | 1452 | 21.19 | 5612.9 | 2957 | 2817.3 | 4208.1 | 1225.4 | 0.68385 | 5.958
2024-12-10 | 4:13 | Data | 0 | 32.507 | 30.651 | 192.419 | 7.63 | 181.385 | 2236.08 | 25.68 | 42.297 | 6.35 | 1.353 | 4.593 | 8635.19 | 2.019 | 98.1 | 77.2 | 1453 | 21.19 | 5612.9 | 2963.3 | 2821.3 | 4207.3 | 1225.4 | 0.68849 | 5.947
2024-12-10 | 4:13 | Data | 0 | 32.494 | 30.536 | 192.419 | 7.63 | 181.249 | 2235.18 | 25.67 | 42.387 | 6.35 | 1.365 | 4.616 | 8630.67 | 1.911 | 98.1 | 77.2 | 1453 | 21.19 | 5609.9 | 2938.9 | 2819.2 | 4195.8 | 1225.4 | 0.68222 | 5.98
2024-12-10 | 4:13 | Data | 0 | 32.501 | 30.651 | 192.419 | 7.63 | 181.385 | 2238.79 | 25.68 | 42.387 | 6.34 | 1.359 | 4.613 | 8630.67 | 1.85 | 98.1 | 77.2 | 1455 | 21.24 | 5609.9 | 2948.2 | 2846.1 | 4216.4 | 1225.4 | 0.68167 | 5.972
2024-12-10 | 4:13 | Data | 0 | 32.494 | 30.428 | 192.374 | 7.63 | 181.249 | 2239.7 | 25.67 | 42.387 | 6.35 | 1.366 | 4.589 | 8639.71 | 2.025 | 98.1 | 77.1 | 1455 | 21.19 | 5615.8 | 2956.8 | 2860.5 | 4234.8 | 1225.4 | 0.68198 | 5.958
2024-12-10 | 4:13 | Data | 0 | 32.339 | 30.415 | 192.419 | 7.63 | 181.385 | 2238.79 | 25.68 | 42.477 | 6.35 | 1.367 | 4.594 | 8639.71 | 1.863 | 98.1 | 77.1 | 1455 | 21.19 | 5615.8 | 2950.3 | 2874.5 | 4239.3 | 1225.4 | 0.67781 | 5.961
2024-12-10 | 4:13 | Data | 0 | 32.494 | 30.86 | 192.374 | 7.63 | 181.294 | 2241.5 | 25.7 | 42.658 | 6.34 | 1.371 | 4.598 | 8644.24 | 1.863 | 98.1 | 77 | 1457 | 21.33 | 5618.8 | 2945.6 | 2903.5 | 4253.2 | 1225.4 | 0.67443 | 5.969
2024-12-10 | 4:13 | Data | 0 | 32.494 | 30.415 | 192.329 | 7.63 | 181.249 | 2243.31 | 25.69 | 42.387 | 6.34 | 1.363 | 4.605 | 8648.76 | 2.079 | 98.1 | 77.2 | 1458 | 21.19 | 5621.7 | 2963.5 | 2880.3 | 4245.6 | 1225.5 | 0.68006 | 5.969
2024-12-10 | 4:13 | Data | 0 | 32.609 | 30.739 | 192.464 | 7.63 | 181.385 | 2240.6 | 25.69 | 42.387 | 6.35 | 1.371 | 4.593 | 8644.24 | 2.059 | 98.1 | 77 | 1457 | 21.19 | 5618.8 | 2955 | 2920 | 4272.2 | 1225.5 | 0.67468 | 5.963
2024-12-10 | 4:13 | Data | 0 | 32.501 | 30.644 | 192.51 | 7.63 | 181.43 | 2244.22 | 25.69 | 42.297 | 6.34 | 1.361 | 4.585 | 8644.24 | 1.985 | 98.1 | 77.1 | 1459 | 21.19 | 5618.8 | 2947.9 | 2913.8 | 4266.5 | 1225.5 | 0.67589 | 5.945
2024-12-10 | 4:13 | Data | 0 | 32.609 | 30.813 | 192.464 | 7.63 | 181.249 | 2242.41 | 25.68 | 42.477 | 6.35 | 1.359 | 4.569 | 8644.24 | 2.066 | 98.1 | 77.1 | 1457 | 21.19 | 5618.8 | 2962.1 | 2903.6 | 4263.4 | 1225.5 | 0.67678 | 5.929
2024-12-10 | 4:13 | Data | 0 | 32.494 | 30.415 | 192.374 | 7.63 | 181.34 | 2244.22 | 25.68 | 42.387 | 6.34 | 1.37 | 4.611 | 8635.19 | 2.073 | 98.1 | 77.1 | 1459 | 21.19 | 5612.9 | 2880.8 | 2829.5 | 4152.1 | 1225.5 | 0.67797 | 5.981
2024-12-10 | 4:13 | Data | 0 | 32.636 | 30.624 | 192.283 | 7.63 | 181.385 | 2242.41 | 25.69 | 42.387 | 6.35 | 1.363 | 4.605 | 8635.19 | 1.742 | 98.1 | 77.2 | 1457 | 21.19 | 5612.9 | 2874.8 | 2822.5 | 4143.4 | 1225.5 | 0.67627 | 5.968
2024-12-10 | 4:13 | Data | 0 | 32.548 | 30.529 | 192.419 | 7.63 | 181.385 | 2241.5 | 25.68 | 42.477 | 6.34 | 1.376 | 4.602 | 8635.19 | 1.85 | 98.1 | 77 | 1457 | 21.19 | 5612.9 | 2877.1 | 2822.2 | 4144 | 1225.5 | 0.67747 | 5.978
2024-12-10 | 4:13 | Data | 0 | 32.919 | 30.651 | 192.51 | 7.63 | 181.294 | 2241.5 | 25.69 | 42.387 | 6.35 | 1.367 | 4.592 | 8621.63 | 1.965 | 98.1 | 77.1 | 1458 | 21.19 | 5604.1 | 2876.5 | 2840.3 | 4150.5 | 1225.5 | 0.67748 | 5.96
2024-12-10 | 4:13 | Data | 0 | 32.723 | 30.651 | 192.374 | 7.63 | 181.34 | 2236.98 | 25.68 | 42.387 | 6.35 | 1.367 | 4.592 | 8608.06 | 2.073 | 98.1 | 77.1 | 1455 | 21.19 | 5595.2 | 2885.8 | 2881.6 | 4187.1 | 1225.5 | 0.67327 | 5.96
2024-12-10 | 4:13 | Data | 0 | 32.494 | 30.415 | 192.374 | 7.63 | 181.204 | 2240.6 | 25.69 | 42.477 | 6.35 | 1.37 | 4.605 | 8612.58 | 2.079 | 98.1 | 77.1 | 1456 | 21.19 | 5598.2 | 2869.3 | 2904.8 | 4197.4 | 1225.5 | 0.66602 | 5.974
2024-12-10 | 4:13 | Data | 0 | 32.723 | 30.536 | 192.329 | 7.63 | 181.34 | 2236.08 | 25.69 | 42.387 | 6.35 | 1.364 | 4.606 | 8608.06 | 2.086 | 98.1 | 77.2 | 1453 | 21.19 | 5595.2 | 2864.9 | 2908.1 | 4195.1 | 1225.5 | 0.66539 | 5.969
2024-12-10 | 4:13 | Data | 0 | 32.494 | 30.637 | 192.329 | 7.63 | 181.294 | 2236.08 | 25.69 | 42.387 | 6.35 | 1.357 | 4.588 | 8608.06 | 1.87 | 98.1 | 77.2 | 1453 | 21.19 | 5595.2 | 2868.5 | 2911.4 | 4205 | 1225.5 | 0.66736 | 5.945
2024-12-10 | 4:14 | Data | 0 | 32.737 | 30.455 | 192.51 | 7.63 | 181.43 | 2233.37 | 25.68 | 42.387 | 6.34 | 1.356 | 4.596 | 8621.63 | 2.066 | 98.1 | 77.2 | 1451 | 21.19 | 5604.1 | 2882.5 | 2912.9 | 4205.8 | 1225.5 | 0.66793 | 5.951
2024-12-10 | 4:14 | Data | 0 | 32.723 | 30.759 | 192.419 | 7.63 | 181.34 | 2233.37 | 25.68 | 42.387 | 6.34 | 1.366 | 4.594 | 8608.06 | 1.85 | 98.1 | 77.1 | 1452 | 21.19 | 5595.2 | 2917.2 | 2936 | 4256 | 1225.5 | 0.66843 | 5.959
2024-12-10 | 4:14 | Data | 0 | 32.271 | 30.516 | 192.329 | 7.63 | 181.249 | 2355.39 | 25.67 | 42.387 | 6.34 | 1.362 | 4.591 | 8594.49 | 2.019 | 98.2 | 77.1 | 1531 | 21.19 | 5586.4 | 2943.5 | 2890.4 | 4240.3 | 1225.5 | 0.6756 | 5.954
2024-12-10 | 4:14 | Data | 0 | 32.885 | 30.563 | 192.419 | 7.63 | 181.294 | 2236.98 | 25.67 | 42.297 | 6.35 | 1.361 | 4.594 | 8608.06 | 2.073 | 98.1 | 77.1 | 1453 | 21.19 | 5595.2 | 2933.8 | 2897.7 | 4240.4 | 1225.5 | 0.67376 | 5.955
2024-12-10 | 4:14 | Data | 0 | 32.44 | 30.59 | 192.374 | 7.63 | 181.204 | 2236.08 | 25.67 | 42.387 | 6.34 | 1.362 | 4.607 | 8576.4 | 2.052 | 98.1 | 77.2 | 1453 | 21.19 | 5574.7 | 2920.7 | 2891.1 | 4228.6 | 1225.5 | 0.67299 | 5.969
2024-12-10 | 4:14 | Data | 0 | 32.663 | 30.651 | 192.419 | 7.63 | 181.159 | 2236.08 | 25.68 | 42.387 | 6.35 | 1.349 | 4.598 | 8594.49 | 2.059 | 98.1 | 77.3 | 1453 | 21.19 | 5586.4 | 2934.1 | 2834.2 | 4203.4 | 1225.5 | 0.68175 | 5.947
2024-12-10 | 4:14 | Data | 0 | 32.494 | 30.469 | 192.329 | 7.63 | 181.249 | 2132.14 | 25.67 | 42.387 | 6.35 | 1.355 | 4.579 | 8594.49 | 1.857 | 98 | 77.2 | 1385 | 21.19 | 5586.4 | 2924 | 2866.8 | 4209.4 | 1225.5 | 0.67792 | 5.932
2024-12-10 | 4:14 | Data | 0 | 32.737 | 30.651 | 192.464 | 7.63 | 181.385 | 2215.29 | 25.68 | 42.297 | 6.34 | 1.355 | 4.61 | 8571.88 | 2.066 | 98.1 | 77.3 | 1441 | 21.15 | 5571.7 | 2921.7 | 2893.3 | 4227.9 | 1225.5 | 0.67337 | 5.965
2024-12-10 | 4:14 | Data | 0 | 32.393 | 30.536 | 192.419 | 7.63 | 181.294 | 2218.91 | 25.67 | 42.387 | 6.34 | 1.37 | 4.602 | 8608.06 | 1.884 | 98.1 | 77.1 | 1442 | 21.15 | 5595.2 | 2915.8 | 2902.5 | 4233 | 1225.5 | 0.67024 | 5.972
2024-12-10 | 4:14 | Data | 0 | 32.494 | 30.806 | 192.374 | 7.63 | 181.34 | 2217.1 | 25.68 | 42.477 | 6.35 | 1.36 | 4.578 | 8612.58 | 1.904 | 98.1 | 77.1 | 1441 | 21.19 | 5598.2 | 2929.2 | 2924.8 | 4248.9 | 1225.5 | 0.67356 | 5.938
2024-12-10 | 4:14 | Data | 0 | 32.494 | 30.624 | 192.283 | 7.63 | 181.159 | 2211.68 | 25.67 | 42.387 | 6.34 | 1.347 | 4.594 | 8599.01 | 1.958 | 98.1 | 77.3 | 1438 | 21.19 | 5589.4 | 2937.4 | 2940.8 | 4268.5 | 1225.5 | 0.67106 | 5.941
2024-12-10 | 4:14 | Data | 0 | 32.494 | 30.529 | 192.283 | 7.63 | 181.159 | 2226.14 | 25.68 | 42.387 | 6.34 | 1.358 | 4.577 | 8599.01 | 1.87 | 98.1 | 77.1 | 1446 | 21.24 | 5589.4 | 2943.1 | 2906.5 | 4249.6 | 1225.5 | 0.67425 | 5.934
2024-12-10 | 4:14 | Data | 0 | 32.723 | 30.455 | 192.238 | 7.63 | 181.249 | 2229.75 | 25.67 | 42.116 | 6.35 | 1.356 | 4.579 | 8594.49 | 1.938 | 98.1 | 77.2 | 1450 | 21.06 | 5586.4 | 2926.9 | 2914.5 | 4240.4 | 1225.5 | 0.6688 | 5.934
2024-12-10 | 4:14 | Data | 0 | 32.501 | 30.637 | 192.329 | 7.63 | 181.294 | 2229.75 | 25.67 | 42.116 | 6.37 | 1.363 | 4.594 | 8603.54 | 1.87 | 98.1 | 77.1 | 1449 | 21.06 | 5592.3 | 2899.6 | 2891.4 | 4215.3 | 1225.5 | 0.66941 | 5.956
2024-12-10 | 4:14 | Data | 0 | 32.521 | 30.435 | 192.283 | 7.63 | 181.34 | 2233.37 | 25.68 | 42.116 | 6.35 | 1.352 | 4.592 | 8580.93 | 1.998 | 98.1 | 77.3 | 1451 | 21.06 | 5577.6 | 2935.2 | 2870.4 | 4221.6 | 1225.5 | 0.67774 | 5.942
2024-12-10 | 4:14 | Data | 0 | 32.494 | 30.415 | 192.238 | 7.63 | 181.249 | 2227.04 | 25.67 | 42.116 | 6.34 | 1.36 | 4.579 | 8580.93 | 2.073 | 98.1 | 77.1 | 1448 | 21.06 | 5577.6 | 2937.1 | 2858.9 | 4215.6 | 1225.5 | 0.67965 | 5.938
2024-12-10 | 4:14 | Data | 0 | 32.494 | 30.59 | 192.419 | 7.63 | 181.249 | 2226.14 | 25.67 | 42.206 | 6.34 | 1.362 | 4.596 | 8608.06 | 1.958 | 98.1 | 77.1 | 1448 | 21.1 | 5595.2 | 2943.8 | 2889.2 | 4241.3 | 1225.5 | 0.67675 | 5.958
2024-12-10 | 4:15 | Data | 0 | 32.75 | 30.556 | 192.374 | 7.63 | 181.34 | 2225.23 | 25.68 | 42.116 | 6.35 | 1.351 | 4.571 | 8621.63 | 1.917 | 98.1 | 77.2 | 1447 | 21.06 | 5604.1 | 2908.6 | 2889.5 | 4219.9 | 1225.5 | 0.67138 | 5.922
2024-12-10 | 4:15 | Data | 0 | 32.21 | 30.415 | 192.283 | 7.63 | 181.294 | 2224.33 | 25.68 | 42.206 | 6.35 | 1.374 | 4.578 | 8621.63 | 2.025 | 98.1 | 76.9 | 1446 | 21.06 | 5604.1 | 2924.6 | 2892.8 | 4229.2 | 1225.5 | 0.67325 | 5.951
2024-12-10 | 4:15 | Data | 0 | 32.683 | 30.428 | 192.238 | 7.63 | 181.159 | 2224.33 | 25.67 | 42.116 | 6.35 | 1.363 | 4.618 | 8621.63 | 2.1 | 98.1 | 77.2 | 1446 | 21.1 | 5604.1 | 2914.6 | 2879.5 | 4212.1 | 1225.5 | 0.67468 | 5.981
2024-12-10 | 4:15 | Data | 0 | 32.44 | 30.59 | 192.283 | 7.63 | 181.159 | 2225.23 | 25.67 | 42.116 | 6.34 | 1.358 | 4.625 | 8617.1 | 2.275 | 98.1 | 77.3 | 1446 | 21.06 | 5601.1 | 2913.5 | 2916.3 | 4239.3 | 1225.5 | 0.66955 | 5.982
2024-12-10 | 4:15 | Data | 0 | 32.453 | 30.529 | 192.148 | 7.63 | 181.204 | 2225.23 | 25.68 | 42.116 | 6.35 | 1.366 | 4.616 | 8635.19 | 2.079 | 98.1 | 77.2 | 1446 | 21.06 | 5612.9 | 2930.7 | 2921.2 | 4252.6 | 1225.5 | 0.66999 | 5.983
2024-12-10 | 4:15 | Data | 0 | 32.494 | 30.212 | 192.283 | 7.63 | 181.159 | 2222.52 | 25.67 | 42.026 | 6.34 | 1.357 | 4.598 | 8635.19 | 2.106 | 98.1 | 77.2 | 1445 | 21.01 | 5612.9 | 2918.8 | 2904.3 | 4233.1 | 1225.5 | 0.67117 | 5.954
2024-12-10 | 4:15 | Data | 0 | 32.494 | 30.583 | 192.238 | 7.63 | 181.249 | 2222.52 | 25.7 | 42.116 | 6.34 | 1.347 | 4.596 | 8621.63 | 2.12 | 98.1 | 77.3 | 1445 | 21.06 | 5604.1 | 2924.8 | 2871.2 | 4214.3 | 1225.5 | 0.6768 | 5.942
2024-12-10 | 4:15 | Data | 0 | 32.48 | 30.212 | 192.148 | 7.63 | 181.204 | 2222.52 | 25.69 | 42.116 | 6.34 | 1.352 | 4.583 | 8648.76 | 2.255 | 98.1 | 77.2 | 1445 | 21.1 | 5621.7 | 2930.2 | 2859.4 | 4201.4 | 1225.6 | 0.67803 | 5.934
2024-12-10 | 4:15 | Data | 0 | 32.636 | 30.745 | 192.283 | 7.63 | 181.34 | 2224.33 | 25.71 | 42.387 | 6.34 | 1.367 | 4.598 | 8630.67 | 2.039 | 98.1 | 77.1 | 1446 | 21.15 | 5609.9 | 2909.9 | 2837.5 | 4188.8 | 1225.6 | 0.67701 | 5.964
2024-12-10 | 4:15 | Data | 0 | 32.339 | 30.313 | 192.374 | 7.63 | 181.204 | 2222.52 | 25.72 | 42.026 | 6.35 | 1.363 | 4.579 | 8653.28 | 1.958 | 98.1 | 77.1 | 1445 | 21.06 | 5624.6 | 2936.4 | 2842 | 4202.8 | 1225.6 | 0.68192 | 5.941
2024-12-10 | 4:15 | Data | 0 | 32.264 | 30.415 | 192.329 | 7.64 | 181.204 | 2222.52 | 25.71 | 42.026 | 6.34 | 1.359 | 4.603 | 8648.76 | 2.066 | 98.1 | 77.2 | 1445 | 21.1 | 5621.7 | 2933.1 | 2873 | 4217.7 | 1225.6 | 0.67882 | 5.961
2024-12-10 | 4:15 | Data | 0 | 32.494 | 30.442 | 192.329 | 7.63 | 181.249 | 2222.52 | 25.72 | 42.116 | 6.35 | 1.364 | 4.605 | 8639.71 | 1.958 | 98.1 | 77.1 | 1445 | 21.1 | 5615.8 | 2921.7 | 2892.2 | 4227.3 | 1225.6 | 0.67323 | 5.969
2024-12-10 | 4:15 | Data | 0 | 32.494 | 30.415 | 192.283 | 7.63 | 181.249 | 2221.62 | 25.71 | 42.387 | 6.35 | 1.367 | 4.609 | 8639.71 | 1.965 | 98.1 | 77.1 | 1444 | 21.19 | 5615.8 | 2911.9 | 2894.3 | 4222.3 | 1225.6 | 0.67065 | 5.976
2024-12-10 | 4:15 | Data | 0 | 32.933 | 30.435 | 192.329 | 7.63 | 181.294 | 2221.62 | 25.71 | 42.387 | 6.35 | 1.365 | 4.597 | 8635.19 | 2.14 | 98.1 | 77.1 | 1445 | 21.19 | 5612.9 | 2923.6 | 2887.5 | 4237.4 | 1225.6 | 0.67449 | 5.962
2024-12-10 | 4:15 | Data | 0 | 32.717 | 30.428 | 192.419 | 7.63 | 181.294 | 2222.52 | 25.71 | 42.387 | 6.35 | 1.358 | 4.577 | 8639.71 | 2.248 | 98.1 | 77.1 | 1445 | 21.19 | 5615.8 | 2914.1 | 2874.4 | 4208.2 | 1225.6 | 0.67415 | 5.935
2024-12-10 | 4:15 | Data | 0 | 32.602 | 30.469 | 192.329 | 7.63 | 181.249 | 2225.23 | 25.7 | 42.387 | 6.35 | 1.358 | 4.585 | 8635.19 | 2.167 | 98.1 | 77.2 | 1446 | 21.19 | 5612.9 | 2924.8 | 2880.7 | 4220.9 | 1225.6 | 0.67661 | 5.942
2024-12-10 | 4:15 | Data | 0 | 32.548 | 30.198 | 192.238 | 7.63 | 181.249 | 2224.33 | 25.71 | 42.387 | 6.34 | 1.359 | 4.599 | 8635.19 | 2.086 | 98.1 | 77.2 | 1446 | 21.19 | 5612.9 | 2924.7 | 2859.2 | 4203.2 | 1225.6 | 0.67883 | 5.959
2024-12-10 | 4:15 | Data | 0 | 32.345 | 30.421 | 192.374 | 7.63 | 181.294 | 2225.23 | 25.71 | 42.387 | 6.34 | 1.362 | 4.569 | 8621.63 | 1.674 | 98.1 | 77 | 1446 | 21.19 | 5604.1 | 2916.4 | 2836.4 | 4186.7 | 1225.6 | 0.67899 | 5.931
2024-12-10 | 4:16 | Data | 0 | 32.494 | 30.327 | 192.283 | 7.63 | 181.204 | 2224.33 | 25.71 | 42.387 | 6.35 | 1.365 | 4.565 | 8644.24 | 1.965 | 98.1 | 77 | 1446 | 21.19 | 5618.8 | 2915.9 | 2840.8 | 4186.9 | 1225.6 | 0.67907 | 5.93
2024-12-10 | 4:16 | Data | 0 | 32.379 | 30.59 | 192.329 | 7.63 | 181.204 | 2225.23 | 25.72 | 42.387 | 6.34 | 1.355 | 4.611 | 8644.24 | 2.066 | 98.1 | 77.3 | 1446 | 21.19 | 5618.8 | 2930.2 | 2821.5 | 4186.5 | 1225.6 | 0.67978 | 5.966
2024-12-10 | 4:16 | Data | 0 | 32.271 | 30.577 | 192.329 | 7.63 | 181.159 | 2225.23 | 25.7 | 42.477 | 6.35 | 1.367 | 4.591 | 8653.28 | 1.965 | 98.1 | 77.1 | 1446 | 21.24 | 5624.6 | 2925.4 | 2833.4 | 4191.7 | 1225.6 | 0.68008 | 5.959
2024-12-10 | 4:16 | Data | 0 | 32.548 | 30.219 | 192.283 | 7.63 | 181.204 | 2225.23 | 25.71 | 42.387 | 6.35 | 1.355 | 4.589 | 8662.33 | 1.857 | 98.1 | 77.2 | 1446 | 21.19 | 5630.5 | 2906.6 | 2831.8 | 4177.5 | 1225.6 | 0.67782 | 5.945
2024-12-10 | 4:16 | Data | 0 | 32.264 | 30.415 | 192.329 | 7.63 | 181.204 | 2225.23 | 25.7 | 42.477 | 6.35 | 1.358 | 4.581 | 8657.8 | 2.025 | 98.1 | 77.1 | 1446 | 21.19 | 5627.6 | 2920.3 | 2847.3 | 4197.5 | 1225.6 | 0.67842 | 5.939
2024-12-10 | 4:16 | Data | 0 | 32.494 | 30.442 | 192.283 | 7.63 | 181.249 | 2224.33 | 25.71 | 42.387 | 6.32 | 1.357 | 4.569 | 8648.76 | 1.85 | 98.1 | 77.1 | 1446 | 21.15 | 5621.7 | 2901 | 2839.5 | 4174 | 1225.6 | 0.67687 | 5.926
2024-12-10 | 4:16 | Data | 0 | 33.021 | 30.455 | 192.464 | 7.63 | 181.385 | 2225.23 | 25.72 | 42.387 | 6.35 | 1.363 | 4.591 | 8639.71 | 2.235 | 98.1 | 77.1 | 1446 | 21.19 | 5615.8 | 2924.9 | 2877.4 | 4218.1 | 1225.6 | 0.67652 | 5.952
2024-12-10 | 4:16 | Data | 0 | 32.717 | 30.651 | 192.329 | 7.63 | 181.249 | 2227.04 | 25.7 | 42.387 | 6.35 | 1.36 | 4.577 | 8838.69 | 2.066 | 98.1 | 77.1 | 1448 | 21.19 | 5745.1 | 2895.3 | 2861.8 | 4186.8 | 1225.6 | 0.67442 | 5.937
2024-12-10 | 4:16 | Data | 0 | 32.494 | 30.637 | 192.329 | 7.63 | 181.249 | 2227.95 | 25.71 | 42.387 | 6.34 | 1.36 | 4.569 | 8992.45 | 1.904 | 98.1 | 77.1 | 1448 | 21.15 | 5845.1 | 2908.9 | 2869.6 | 4204.4 | 1225.6 | 0.67634 | 5.928
2024-12-10 | 4:16 | Data | 0 | 32.379 | 30.421 | 192.329 | 7.63 | 181.249 | 2227.95 | 25.71 | 42.477 | 6.35 | 1.365 | 4.61 | 8626.15 | 1.863 | 98.1 | 77.2 | 1448 | 21.19 | 5607 | 2920.9 | 2871.6 | 4208.2 | 1225.6 | 0.67654 | 5.974
2024-12-10 | 4:16 | Data | 0 | 32.723 | 30.577 | 192.283 | 7.63 | 181.249 | 2227.95 | 25.71 | 42.387 | 6.34 | 1.36 | 4.603 | 8635.19 | 1.809 | 98.1 | 77.2 | 1448 | 21.19 | 5612.9 | 2916.1 | 2871.5 | 4207.8 | 1225.6 | 0.67635 | 5.963
2024-12-10 | 4:16 | Data | 0 | 32.494 | 30.273 | 192.238 | 7.63 | 181.249 | 2229.75 | 25.71 | 42.387 | 6.34 | 1.367 | 4.621 | 8648.76 | 1.965 | 98.1 | 77.2 | 1449 | 21.24 | 5621.7 | 2896.3 | 2866.3 | 4191.9 | 1225.6 | 0.674 | 5.989
2024-12-10 | 4:16 | Data | 0 | 32.379 | 30.759 | 192.329 | 7.63 | 181.204 | 2230.66 | 25.71 | 42.387 | 6.35 | 1.361 | 4.572 | 8635.19 | 1.85 | 98.1 | 77.1 | 1449 | 21.19 | 5612.9 | 2920.8 | 2851 | 4192.7 | 1225.6 | 0.67964 | 5.933
2024-12-10 | 4:16 | Data | 0 | 33.115 | 30.617 | 192.464 | 7.63 | 181.43 | 2229.75 | 25.71 | 42.387 | 6.34 | 1.36 | 4.585 | 8648.76 | 1.958 | 98.1 | 77.1 | 1450 | 21.19 | 5621.7 | 2923.2 | 2833.5 | 4185.1 | 1225.6 | 0.68116 | 5.945
2024-12-10 | 4:16 | Data | 0 | 32.825 | 30.712 | 192.464 | 7.63 | 181.34 | 2230.66 | 25.7 | 42.477 | 6.35 | 1.361 | 4.584 | 8653.28 | 1.924 | 98.1 | 77.1 | 1450 | 21.19 | 5624.6 | 2923.1 | 2859.5 | 4204 | 1225.6 | 0.67814 | 5.946
2024-12-10 | 4:16 | Data | 0 | 32.494 | 30.84 | 192.283 | 7.63 | 181.294 | 2229.75 | 25.71 | 42.387 | 6.34 | 1.358 | 4.569 | 8648.76 | 1.965 | 98.1 | 77.1 | 1450 | 21.19 | 5621.7 | 2914.2 | 2881 | 4215.8 | 1225.6 | 0.68064 | 5.927
2024-12-10 | 4:16 | Data | 0 | 32.494 | 30.766 | 192.283 | 7.63 | 181.204 | 2232.47 | 25.71 | 42.387 | 6.36 | 1.372 | 4.579 | 8671.37 | 1.965 | 98.1 | 76.9 | 1452 | 21.19 | 5636.4 | 2909.9 | 2872.1 | 4203.7 | 1225.6 | 0.67339 | 5.95
2024-12-10 | 4:16 | Data | 0 | 32.906 | 30.543 | 192.374 | 7.63 | 181.385 | 2229.75 | 25.71 | 42.387 | 6.34 | 1.371 | 4.598 | 8648.76 | 2.12 | 98.1 | 77 | 1449 | 21.19 | 5621.7 | 2905.5 | 2892.8 | 4210.4 | 1225.6 | 0.67096 | 5.969
2024-12-10 | 4:17 | Data | 0 | 32.285 | 30.415 | 192.329 | 7.63 | 181.204 | 2229.75 | 25.72 | 42.387 | 6.34 | 1.367 | 4.597 | 8635.19 | 1.843 | 98.1 | 77.1 | 1450 | 21.15 | 5612.9 | 2917.9 | 2910.6 | 4210.7 | 1225.6 | 0.67044 | 5.964
2024-12-10 | 4:17 | Data | 0 | 32.467 | 30.415 | 192.238 | 7.63 | 181.114 | 2229.75 | 25.71 | 42.387 | 6.35 | 1.363 | 4.603 | 8648.76 | 2.079 | 98.1 | 77.2 | 1449 | 21.24 | 5621.7 | 2936.6 | 2854.5 | 4210.3 | 1225.6 | 0.67944 | 5.966
2024-12-10 | 4:17 | Data | 0 | 32.501 | 30.509 | 192.329 | 7.63 | 181.294 | 2230.66 | 25.71 | 42.387 | 6.35 | 1.36 | 4.583 | 8630.67 | 2.127 | 98.1 | 77.1 | 1449 | 21.19 | 5609.9 | 2926 | 2846 | 4198 | 1225.6 | 0.6788 | 5.944
2024-12-10 | 4:17 | Data | 0 | 32.717 | 30.543 | 192.283 | 7.63 | 181.34 | 2228.85 | 25.7 | 42.387 | 6.34 | 1.357 | 4.597 | 8635.19 | 2.073 | 98.1 | 77.2 | 1448 | 21.24 | 5612.9 | 2923.1 | 2828.7 | 4178.7 | 1225.6 | 0.68247 | 5.953
2024-12-10 | 4:17 | Data | 0 | 32.582 | 30.651 | 192.329 | 7.63 | 181.249 | 2227.95 | 25.71 | 42.387 | 6.34 | 1.367 | 4.601 | 8825.13 | 2.059 | 98.1 | 77.1 | 1448 | 21.19 | 5736.3 | 2919.8 | 2823 | 4176.7 | 1225.6 | 0.68166 | 5.969
2024-12-10 | 4:17 | Data | 0 | 32.548 | 30.739 | 192.329 | 7.63 | 181.34 | 2227.95 | 25.72 | 42.297 | 6.34 | 1.367 | 4.604 | 8838.69 | 1.911 | 98.1 | 77.1 | 1448 | 21.15 | 5745.1 | 2929.6 | 2847.2 | 4202.2 | 1225.6 | 0.68084 | 5.969
2024-12-10 | 4:17 | Data | 0 | 32.885 | 30.421 | 192.329 | 7.63 | 181.294 | 2229.75 | 25.71 | 42.387 | 6.34 | 1.362 | 4.605 | 8829.65 | 2.079 | 98.1 | 77.2 | 1449 | 21.19 | 5739.3 | 2903 | 2858.8 | 4192.1 | 1225.6 | 0.67685 | 5.968
2024-12-10 | 4:17 | Data | 0 | 32.818 | 30.678 | 192.374 | 7.63 | 181.249 | 2232.47 | 25.71 | 42.387 | 6.34 | 1.361 | 4.592 | 8838.69 | 2.214 | 98.1 | 77.1 | 1451 | 21.19 | 5745.1 | 2923.4 | 2853.9 | 4198.9 | 1225.7 | 0.67851 | 5.953
2024-12-10 | 4:17 | Data | 0 | 32.494 | 30.442 | 192.374 | 7.63 | 181.249 | 2233.37 | 25.71 | 42.297 | 6.34 | 1.363 | 4.595 | 8662.33 | 2.086 | 98.1 | 77.1 | 1452 | 21.19 | 5630.5 | 2903.1 | 2883.3 | 4206.6 | 1225.7 | 0.67173 | 5.958
2024-12-10 | 4:17 | Data | 0 | 32.602 | 30.428 | 192.329 | 7.63 | 181.204 | 2233.37 | 25.71 | 42.387 | 6.34 | 1.36 | 4.625 | 8648.76 | 2.019 | 98.1 | 77.3 | 1451 | 21.24 | 5621.7 | 2927.8 | 2884.2 | 4225.3 | 1225.7 | 0.67545 | 5.988
2024-12-10 | 4:17 | Data | 0 | 32.494 | 30.415 | 192.329 | 7.63 | 181.249 | 2233.37 | 25.71 | 42.477 | 6.34 | 1.352 | 4.606 | 8662.33 | 2.079 | 98.1 | 77.3 | 1452 | 21.24 | 5630.5 | 2931.8 | 2905.2 | 4240.4 | 1225.7 | 0.67426 | 5.958
2024-12-10 | 4:17 | Data | 0 | 32.825 | 30.705 | 192.51 | 7.63 | 181.294 | 2230.66 | 25.71 | 42.387 | 6.34 | 1.358 | 4.575 | 8653.28 | 2.059 | 98.1 | 77.1 | 1450 | 21.24 | 5624.6 | 2904.1 | 2890.8 | 4221 | 1225.7 | 0.67558 | 5.932
2024-12-10 | 4:17 | Data | 0 | 32.474 | 30.516 | 192.238 | 7.64 | 181.204 | 2231.56 | 25.71 | 42.387 | 6.34 | 1.367 | 4.586 | 8662.33 | 2.147 | 98.1 | 77 | 1450 | 21.15 | 5630.5 | 2926.4 | 2902.9 | 4237.2 | 1225.7 | 0.67406 | 5.953
2024-12-10 | 4:17 | Data | 0 | 32.71 | 30.651 | 192.283 | 7.63 | 181.204 | 2230.66 | 25.71 | 42.387 | 6.34 | 1.358 | 4.563 | 8635.19 | 1.958 | 98.1 | 77.1 | 1449 | 21.19 | 5612.9 | 2922.4 | 2893.3 | 4225.7 | 1225.7 | 0.67461 | 5.92
2024-12-10 | 4:17 | Data | 0 | 32.71 | 30.739 | 192.69 | 7.63 | 181.249 | 2229.75 | 25.72 | 42.387 | 6.34 | 1.363 | 4.605 | 8648.76 | 2.127 | 98.1 | 77.2 | 1449 | 21.19 | 5621.7 | 2915.5 | 2863.1 | 4200.8 | 1225.7 | 0.67636 | 5.968
2024-12-10 | 4:17 | Data | 0 | 32.264 | 30.874 | 192.238 | 7.63 | 181.249 | 2232.47 | 25.72 | 42.387 | 6.34 | 1.361 | 4.63 | 8662.33 | 2.032 | 98.1 | 77.3 | 1451 | 21.19 | 5630.5 | 2939.6 | 2865.1 | 4219.7 | 1225.7 | 0.67996 | 5.992
2024-12-10 | 4:17 | Data | 0 | 32.71 | 30.529 | 192.329 | 7.63 | 181.34 | 2233.37 | 25.71 | 42.387 | 6.34 | 1.367 | 4.605 | 8657.8 | 1.897 | 98.1 | 77.1 | 1452 | 21.15 | 5627.6 | 2931.6 | 2851.8 | 4206.6 | 1225.7 | 0.67912 | 5.972
2024-12-10 | 4:17 | Data | 0 | 32.494 | 30.529 | 192.419 | 7.63 | 181.294 | 2233.37 | 25.71 | 42.297 | 6.35 | 1.376 | 4.613 | 8250.8 | 1.87 | 98.1 | 77 | 1452 | 21.19 | 5363 | 2911.7 | 2876.6 | 4211 | 1225.7 | 0.67374 | 5.988
2024-12-10 | 4:18 | Data | 0 | 32.501 | 30.421 | 192.329 | 7.63 | 181.34 | 2235.18 | 25.71 | 42.387 | 6.35 | 1.36 | 4.595 | 8671.37 | 2.066 | 98.1 | 77.2 | 1453 | 21.24 | 5636.4 | 2909.8 | 2895.9 | 4225.4 | 1225.7 | 0.66953 | 5.956
2024-12-10 | 4:18 | Data | 0 | 32.501 | 30.651 | 192.464 | 7.63 | 181.249 | 2233.37 | 25.7 | 42.387 | 6.34 | 1.36 | 4.606 | 8662.33 | 2.019 | 98.1 | 77.2 | 1451 | 21.19 | 5630.5 | 2917 | 2884.1 | 4218.7 | 1225.7 | 0.67353 | 5.967
2024-12-10 | 4:18 | Data | 0 | 32.494 | 30.428 | 192.283 | 7.63 | 181.204 | 2232.47 | 25.71 | 42.116 | 6.34 | 1.354 | 4.581 | 8635.19 | 2.032 | 98.1 | 77.2 | 1452 | 21.06 | 5612.9 | 2925.5 | 2898.9 | 4231.7 | 1225.7 | 0.67358 | 5.934
2024-12-10 | 4:18 | Data | 0 | 32.494 | 30.637 | 192.464 | 7.63 | 181.204 | 2233.37 | 25.71 | 42.116 | 6.34 | 1.367 | 4.598 | 8621.63 | 2.005 | 98.1 | 77.1 | 1452 | 21.06 | 5604.1 | 2930.5 | 2903.1 | 4235.9 | 1225.7 | 0.67395 | 5.965
2024-12-10 | 4:18 | Data | 0 | 32.582 | 30.766 | 192.419 | 7.63 | 181.294 | 2232.47 | 25.71 | 42.116 | 6.34 | 1.369 | 4.592 | 8621.63 | 2.012 | 98.1 | 77 | 1451 | 21.01 | 5604.1 | 2910.4 | 2882.7 | 4212.5 | 1225.7 | 0.67302 | 5.961
2024-12-10 | 4:18 | Data | 0 | 32.494 | 30.469 | 192.329 | 7.63 | 181.204 | 2232.47 | 25.71 | 42.297 | 6.34 | 1.37 | 4.579 | 8639.71 | 2.025 | 98.1 | 77 | 1451 | 21.1 | 5615.8 | 2899.3 | 2865.1 | 4191 | 1225.7 | 0.67401 | 5.949
2024-12-10 | 4:18 | Data | 0 | 32.494 | 30.651 | 192.6 | 7.63 | 181.249 | 2232.47 | 25.73 | 42.116 | 6.35 | 1.364 | 4.579 | 8680.41 | 2.025 | 98.1 | 77.1 | 1452 | 21.1 | 5642.3 | 2925.5 | 2865.7 | 4208.6 | 1225.7 | 0.67807 | 5.941
2024-12-10 | 4:18 | Data | 0 | 32.494 | 30.428 | 192.238 | 7.63 | 181.204 | 2236.08 | 25.71 | 42.387 | 6.34 | 1.37 | 4.582 | 8666.85 | 2.059 | 98.1 | 77 | 1453 | 21.15 | 5633.5 | 2909.3 | 2812.2 | 4167.3 | 1225.7 | 0.68085 | 5.952
2024-12-10 | 4:18 | Data | 0 | 32.777 | 30.583 | 192.464 | 7.63 | 181.294 | 2227.95 | 25.72 | 42.116 | 6.34 | 1.375 | 4.571 | 8662.33 | 1.978 | 98.1 | 76.9 | 1448 | 21.1 | 5630.5 | 2930.7 | 2810.5 | 4178.4 | 1225.7 | 0.68473 | 5.946
2024-12-10 | 4:18 | Data | 0 | 32.271 | 30.462 | 192.329 | 7.63 | 181.34 | 2233.37 | 25.72 | 42.116 | 6.35 | 1.371 | 4.597 | 8648.76 | 1.728 | 98.1 | 77 | 1451 | 21.06 | 5621.7 | 2905.5 | 2821.3 | 4169.6 | 1225.7 | 0.67886 | 5.967
2024-12-10 | 4:18 | Data | 0 | 32.676 | 30.536 | 192.464 | 7.63 | 181.34 | 2232.47 | 25.72 | 42.116 | 6.34 | 1.366 | 4.593 | 8648.76 | 1.742 | 98.1 | 77.1 | 1451 | 21.06 | 5621.7 | 2911.6 | 2846.4 | 4182.7 | 1225.7 | 0.67855 | 5.958
2024-12-10 | 4:18 | Data | 0 | 32.717 | 30.435 | 192.283 | 7.63 | 181.249 | 2233.37 | 25.73 | 42.116 | 6.34 | 1.361 | 4.604 | 8621.63 | 2.154 | 98.1 | 77.2 | 1452 | 21.06 | 5604.1 | 2922.6 | 2878.1 | 4223.2 | 1225.7 | 0.67619 | 5.965
2024-12-10 | 4:18 | Data | 0 | 32.325 | 30.415 | 192.283 | 7.63 | 181.204 | 2233.37 | 25.73 | 42.116 | 6.34 | 1.37 | 4.628 | 8630.67 | 1.863 | 98.1 | 77.2 | 1452 | 21.06 | 5609.9 | 2933.4 | 2868.9 | 4219.2 | 1225.7 | 0.67774 | 5.998
2024-12-10 | 4:18 | Data | 0 | 32.487 | 30.59 | 192.193 | 7.63 | 181.204 | 2233.37 | 25.72 | 42.387 | 6.34 | 1.353 | 4.609 | 8630.67 | 1.958 | 98.1 | 77.3 | 1452 | 21.19 | 5609.9 | 2920.7 | 2871.2 | 4206.4 | 1225.7 | 0.67512 | 5.962
2024-12-10 | 4:18 | Data | 0 | 32.312 | 30.536 | 192.374 | 7.63 | 181.249 | 2233.37 | 25.73 | 42.116 | 6.34 | 1.348 | 4.604 | 8648.76 | 1.863 | 98.1 | 77.4 | 1452 | 21.06 | 5621.7 | 2920.5 | 2879.2 | 4214.5 | 1225.7 | 0.67433 | 5.95
2024-12-10 | 4:18 | Data | 0 | 32.447 | 30.752 | 192.419 | 7.63 | 181.249 | 2232.47 | 25.72 | 42.116 | 6.34 | 1.359 | 4.606 | 8635.19 | 1.931 | 98.1 | 77.2 | 1451 | 21.06 | 5612.9 | 2898.5 | 2874.6 | 4201.1 | 1225.7 | 0.67144 | 5.965
2024-12-10 | 4:18 | Data | 0 | 32.291 | 30.415 | 192.238 | 7.63 | 181.159 | 2233.37 | 25.73 | 41.845 | 6.34 | 1.361 | 4.616 | 8630.67 | 1.857 | 98.1 | 77.2 | 1451 | 20.92 | 5609.9 | 2912.6 | 2856.2 | 4194.7 | 1225.7 | 0.67702 | 5.979
2024-12-10 | 4:18 | Data | 0 | 32.649 | 30.469 | 192.329 | 7.63 | 181.249 | 2233.37 | 25.71 | 42.116 | 6.34 | 1.36 | 4.6 | 8648.76 | 2.046 | 98.1 | 77.2 | 1452 | 21.06 | 5621.7 | 2917 | 2891.3 | 4221.9 | 1225.7 | 0.6739 | 5.96
2024-12-10 | 4:19 | Data | 0 | 32.609 | 30.86 | 192.464 | 7.64 | 181.34 | 2235.18 | 25.72 | 42.116 | 6.34 | 1.367 | 4.588 | 8635.19 | 1.985 | 98.1 | 77 | 1453 | 21.06 | 5612.9 | 2905.7 | 2841.4 | 4182.8 | 1225.7 | 0.67644 | 5.956
2024-12-10 | 4:19 | Data | 0 | 32.69 | 30.651 | 192.238 | 7.63 | 181.249 | 2239.7 | 25.72 | 42.116 | 6.34 | 1.364 | 4.594 | 8635.19 | 2.066 | 98.1 | 77.1 | 1456 | 21.06 | 5612.9 | 2920.4 | 2840.1 | 4186.2 | 1225.7 | 0.68078 | 5.958
2024-12-10 | 4:19 | Data | 0 | 32.609 | 30.428 | 192.419 | 7.63 | 181.294 | 2238.79 | 25.73 | 42.387 | 6.34 | 1.364 | 4.591 | 8639.71 | 2.073 | 98.1 | 77.1 | 1455 | 21.19 | 5615.8 | 2922.8 | 2843.9 | 4191.2 | 1225.7 | 0.67934 | 5.955
2024-12-10 | 4:19 | Data | 0 | 32.521 | 30.543 | 192.374 | 7.63 | 181.294 | 2239.7 | 25.73 | 42.387 | 6.34 | 1.365 | 4.6 | 8639.71 | 1.89 | 98.1 | 77.1 | 1455 | 21.19 | 5615.8 | 2913 | 2839.4 | 4187.8 | 1225.7 | 0.6778 | 5.966
2024-12-10 | 4:19 | Data | 0 | 32.717 | 30.766 | 192.329 | 7.63 | 181.204 | 2236.98 | 25.74 | 42.477 | 6.34 | 1.364 | 4.612 | 8644.24 | 1.958 | 98.1 | 77.2 | 1455 | 21.19 | 5618.8 | 2926.3 | 2824.8 | 4197.8 | 1225.7 | 0.68037 | 5.977
2024-12-10 | 4:19 | Data | 0 | 32.494 | 30.84 | 192.329 | 7.63 | 181.294 | 2238.79 | 25.7 | 42.387 | 6.34 | 1.361 | 4.587 | 8644.24 | 1.816 | 98.1 | 77.1 | 1455 | 21.19 | 5618.8 | 2912.4 | 2860 | 4198.5 | 1225.7 | 0.67523 | 5.948
2024-12-10 | 4:19 | Data | 0 | 32.507 | 30.651 | 192.419 | 7.63 | 181.34 | 2238.79 | 25.73 | 42.387 | 6.34 | 1.369 | 4.578 | 8648.76 | 1.85 | 98.1 | 77 | 1456 | 21.19 | 5621.7 | 2912.4 | 2834.9 | 4178.5 | 1225.7 | 0.67871 | 5.947
2024-12-10 | 4:19 | Data | 0 | 32.278 | 30.705 | 192.329 | 7.63 | 181.249 | 2239.7 | 25.73 | 42.387 | 6.34 | 1.367 | 4.615 | 8648.76 | 1.965 | 98.1 | 77.2 | 1456 | 21.19 | 5621.7 | 2906.3 | 2829.7 | 4174.9 | 1225.7 | 0.67838 | 5.981
2024-12-10 | 4:19 | Data | 0 | 32.507 | 30.644 | 192.464 | 7.63 | 181.294 | 2239.7 | 25.73 | 42.297 | 6.34 | 1.366 | 4.601 | 8648.76 | 1.971 | 98.1 | 77.1 | 1456 | 21.19 | 5621.7 | 2918.1 | 2838 | 4184.4 | 1225.8 | 0.68064 | 5.968
2024-12-10 | 4:19 | Data | 0 | 32.507 | 30.475 | 192.419 | 7.63 | 181.249 | 2243.31 | 25.73 | 42.387 | 6.34 | 1.367 | 4.601 | 8648.76 | 1.965 | 98.1 | 77.1 | 1459 | 21.24 | 5621.7 | 2929.4 | 2855.2 | 4204.2 | 1225.8 | 0.68002 | 5.968
2024-12-10 | 4:19 | Data | 0 | 32.507 | 30.442 | 192.329 | 7.63 | 181.249 | 2242.41 | 25.73 | 42.387 | 6.35 | 1.367 | 4.618 | 8635.19 | 2.025 | 98.1 | 77.2 | 1458 | 21.19 | 5612.9 | 2928.8 | 2864.1 | 4204.8 | 1225.8 | 0.6788 | 5.986
2024-12-10 | 4:19 | Data | 0 | 32.541 | 30.59 | 192.238 | 7.63 | 181.159 | 2242.41 | 25.72 | 42.116 | 6.34 | 1.37 | 4.598 | 8648.76 | 1.87 | 98.1 | 77 | 1458 | 21.1 | 5621.7 | 2916 | 2854.6 | 4197.3 | 1225.8 | 0.67676 | 5.969
2024-12-10 | 4:19 | Data | 0 | 32.838 | 30.88 | 192.51 | 7.63 | 181.34 | 2244.22 | 25.73 | 42.206 | 6.34 | 1.376 | 4.578 | 8644.24 | 2.066 | 98.1 | 76.9 | 1459 | 21.06 | 5618.8 | 2904.8 | 2913.7 | 4224.9 | 1225.8 | 0.67087 | 5.953
2024-12-10 | 4:19 | Data | 0 | 32.285 | 30.415 | 192.464 | 7.63 | 181.294 | 2244.22 | 25.73 | 42.116 | 6.34 | 1.369 | 4.616 | 8635.19 | 1.857 | 98.1 | 77.1 | 1459 | 21.06 | 5612.9 | 2935.2 | 2902.4 | 4241.8 | 1225.8 | 0.67436 | 5.984
2024-12-10 | 4:19 | Data | 0 | 32.723 | 30.448 | 192.329 | 7.63 | 181.249 | 2243.31 | 25.72 | 42.116 | 6.34 | 1.363 | 4.61 | 8630.67 | 2.133 | 98.1 | 77.2 | 1458 | 21.06 | 5609.9 | 2924.4 | 2904.3 | 4242 | 1225.8 | 0.67174 | 5.973
2024-12-10 | 4:19 | Data | 0 | 32.494 | 30.853 | 192.464 | 7.63 | 181.249 | 2244.22 | 25.73 | 42.026 | 6.34 | 1.37 | 4.591 | 8648.76 | 1.931 | 98.1 | 77 | 1459 | 21.01 | 5621.7 | 2919.8 | 2858.8 | 4201.5 | 1225.8 | 0.67658 | 5.962
2024-12-10 | 4:19 | Data | 0 | 32.264 | 30.421 | 192.283 | 7.63 | 181.249 | 2244.22 | 25.73 | 42.116 | 6.34 | 1.369 | 4.558 | 8635.19 | 2.019 | 98.1 | 76.9 | 1459 | 21.06 | 5612.9 | 2921.2 | 2842.8 | 4196.9 | 1225.8 | 0.67818 | 5.927
2024-12-10 | 4:20 | Data | 0 | 32.717 | 30.651 | 192.51 | 7.63 | 181.43 | 2244.22 | 25.73 | 42.116 | 6.34 | 1.37 | 4.567 | 8621.63 | 2.073 | 98.1 | 76.9 | 1459 | 21.06 | 5604.1 | 2935.5 | 2833.9 | 4194.6 | 1225.8 | 0.68273 | 5.937
2024-12-10 | 4:20 | Data | 0 | 32.534 | 30.624 | 192.645 | 7.63 | 181.43 | 2244.22 | 25.73 | 42.116 | 6.34 | 1.367 | 4.598 | 8635.19 | 2.059 | 98.1 | 77.1 | 1459 | 21.06 | 5612.9 | 2924.2 | 2841.8 | 4190.6 | 1225.8 | 0.68094 | 5.967
2024-12-10 | 4:20 | Data | 0 | 32.494 | 30.415 | 192.645 | 7.63 | 181.34 | 2244.22 | 25.73 | 42.116 | 6.34 | 1.369 | 4.628 | 8617.1 | 2.079 | 98.1 | 77.2 | 1459 | 21.06 | 5601.1 | 2913.6 | 2826.2 | 4174.3 | 1225.8 | 0.68115 | 5.998
2024-12-10 | 4:20 | Data | 0 | 32.393 | 30.415 | 192.464 | 7.63 | 181.385 | 2242.41 | 25.73 | 42.026 | 6.34 | 1.376 | 4.629 | 8626.15 | 1.904 | 98.1 | 77.1 | 1457 | 21.06 | 5607 | 2926 | 2836.7 | 4189.9 | 1225.8 | 0.68288 | 6.005
2024-12-10 | 4:20 | Data | 0 | 32.494 | 30.415 | 192.51 | 7.63 | 181.385 | 2236.98 | 25.73 | 42.206 | 6.34 | 1.378 | 4.607 | 8639.71 | 2.079 | 98.1 | 77 | 1455 | 21.06 | 5615.8 | 2922.3 | 2832.4 | 4185.2 | 1225.8 | 0.68035 | 5.985
2024-12-10 | 4:20 | Data | 0 | 32.723 | 30.475 | 192.6 | 7.63 | 181.52 | 2233.37 | 25.73 | 42.116 | 6.34 | 1.375 | 4.614 | 8635.19 | 2.012 | 98.1 | 77 | 1451 | 21.06 | 5612.9 | 2933.5 | 2842 | 4200.7 | 1225.8 | 0.68075 | 5.989
2024-12-10 | 4:20 | Data | 0 | 32.48 | 30.59 | 192.6 | 7.63 | 181.385 | 2239.7 | 25.72 | 42.116 | 6.34 | 1.36 | 4.598 | 8657.8 | 2.073 | 98.1 | 77.2 | 1455 | 21.1 | 5627.6 | 2932.3 | 2866.3 | 4212.7 | 1225.8 | 0.67597 | 5.958
2024-12-10 | 4:20 | Data | 0 | 32.413 | 30.536 | 192.781 | 7.63 | 181.52 | 2238.79 | 25.72 | 42.206 | 6.34 | 1.367 | 4.606 | 8671.37 | 1.998 | 98.1 | 77.1 | 1455 | 21.06 | 5636.4 | 2914.3 | 2866.8 | 4201.3 | 1225.8 | 0.67653 | 5.972
2024-12-10 | 4:20 | Data | 0 | 32.494 | 30.415 | 192.374 | 7.63 | 181.294 | 2239.7 | 25.72 | 42.116 | 6.34 | 1.354 | 4.611 | 8703.03 | 2.079 | 98.1 | 77.3 | 1455 | 21.06 | 5657 | 2911.6 | 2857.8 | 4195.6 | 1225.8 | 0.67678 | 5.965
2024-12-10 | 4:20 | Data | 0 | 32.467 | 30.637 | 192.51 | 7.63 | 181.475 | 2241.5 | 25.73 | 42.116 | 6.34 | 1.366 | 4.604 | 8703.03 | 1.89 | 98.1 | 77.1 | 1457 | 21.06 | 5657 | 2908.4 | 2842.5 | 4182.9 | 1225.8 | 0.67788 | 5.969
2024-12-10 | 4:20 | Data | 0 | 32.271 | 30.644 | 192.69 | 7.63 | 181.385 | 2241.5 | 25.72 | 42.206 | 6.34 | 1.36 | 4.598 | 8703.03 | 1.762 | 98.1 | 77.2 | 1457 | 21.06 | 5657 | 2904.7 | 2840.7 | 4176.7 | 1225.8 | 0.67883 | 5.959
2024-12-10 | 4:20 | Data | 0 | 32.339 | 30.597 | 192.51 | 7.63 | 181.385 | 2238.79 | 25.74 | 42.116 | 6.34 | 1.366 | 4.641 | 8721.11 | 1.911 | 98.1 | 77.3 | 1456 | 21.01 | 5668.7 | 2917 | 2827.8 | 4178.7 | 1225.8 | 0.6812 | 6.007
2024-12-10 | 4:20 | Data | 0 | 32.696 | 30.678 | 192.6 | 7.63 | 181.52 | 2238.79 | 25.73 | 42.116 | 6.34 | 1.367 | 4.607 | 8734.68 | 2.019 | 98.1 | 77.1 | 1455 | 21.06 | 5677.5 | 2933.9 | 2837.7 | 4196.5 | 1225.8 | 0.68264 | 5.975
2024-12-10 | 4:20 | Data | 0 | 32.804 | 30.651 | 192.645 | 7.63 | 181.475 | 2238.79 | 25.73 | 42.116 | 6.34 | 1.376 | 4.591 | 8721.11 | 1.958 | 98.1 | 76.9 | 1455 | 21.1 | 5668.7 | 2928.8 | 2840.2 | 4198.4 | 1225.8 | 0.6806 | 5.968
2024-12-10 | 4:20 | Data | 0 | 32.386 | 30.644 | 192.6 | 7.63 | 181.43 | 2242.41 | 25.72 | 42.116 | 6.35 | 1.371 | 4.598 | 8730.16 | 1.931 | 98.1 | 77 | 1458 | 21.06 | 5674.6 | 2926.8 | 2844.7 | 4195.8 | 1225.8 | 0.68009 | 5.969
2024-12-10 | 4:20 | Data | 0 | 32.501 | 30.637 | 192.736 | 7.63 | 181.52 | 2241.5 | 25.73 | 42.116 | 6.34 | 1.364 | 4.607 | 8693.98 | 1.904 | 98.1 | 77.2 | 1458 | 21.1 | 5651.1 | 2921.3 | 2837 | 4188.1 | 1225.8 | 0.68176 | 5.971
2024-12-10 | 4:21 | Data | 0 | 32.71 | 30.563 | 192.6 | 7.63 | 181.475 | 2242.41 | 25.73 | 42.116 | 6.34 | 1.366 | 4.597 | 8693.98 | 2.127 | 98.1 | 77.1 | 1458 | 21.06 | 5651.1 | 2950.3 | 2840.2 | 4207.1 | 1225.8 | 0.68455 | 5.962
2024-12-10 | 4:21 | Data | 0 | 32.501 | 30.644 | 192.645 | 7.63 | 181.43 | 2239.7 | 25.74 | 42.116 | 6.34 | 1.37 | 4.578 | 8689.46 | 1.87 | 98.1 | 77 | 1455 | 21.06 | 5648.1 | 2920.2 | 2828.3 | 4182.4 | 1225.8 | 0.68153 | 5.948
2024-12-10 | 4:21 | Data | 0 | 32.494 | 30.651 | 192.51 | 7.63 | 181.43 | 2238.79 | 25.73 | 42.116 | 6.34 | 1.365 | 4.568 | 8693.98 | 1.85 | 98.1 | 77 | 1455 | 21.06 | 5651.1 | 2916 | 2829.4 | 4181.3 | 1225.8 | 0.67964 | 5.933
2024-12-10 | 4:21 | Data | 0 | 32.521 | 30.651 | 192.6 | 7.63 | 181.52 | 2238.79 | 25.72 | 42.116 | 6.34 | 1.356 | 4.594 | 8703.03 | 1.857 | 98.1 | 77.2 | 1456 | 21.01 | 5657 | 2929.4 | 2842.3 | 4190.4 | 1225.8 | 0.68179 | 5.95
2024-12-10 | 4:21 | Data | 0 | 32.575 | 30.624 | 192.736 | 7.63 | 181.475 | 2235.18 | 25.73 | 42.206 | 6.34 | 1.361 | 4.599 | 8693.98 | 1.789 | 98.1 | 77.2 | 1453 | 21.1 | 5651.1 | 2921.5 | 2826.7 | 4183.2 | 1225.8 | 0.68173 | 5.96
2024-12-10 | 4:21 | Data | 0 | 32.723 | 30.772 | 192.645 | 7.63 | 181.475 | 2235.18 | 25.73 | 42.116 | 6.34 | 1.374 | 4.593 | 8716.59 | 2.181 | 98.1 | 77 | 1453 | 21.06 | 5665.8 | 2914 | 2838.8 | 4187.9 | 1225.8 | 0.67896 | 5.967
2024-12-10 | 4:21 | Data | 0 | 32.696 | 30.847 | 192.51 | 7.63 | 181.475 | 2229.75 | 25.72 | 42.206 | 6.33 | 1.36 | 4.611 | 8721.11 | 1.958 | 98.1 | 77.2 | 1449 | 21.1 | 5668.7 | 2915.1 | 2830.2 | 4178.7 | 1225.8 | 0.68297 | 5.971
2024-12-10 | 4:21 | Data | 0 | 32.595 | 30.651 | 192.645 | 7.63 | 181.475 | 2235.18 | 25.73 | 42.026 | 6.34 | 1.356 | 4.614 | 8716.59 | 2.059 | 98.1 | 77.3 | 1453 | 21.01 | 5665.8 | 2913.2 | 2837.9 | 4183.6 | 1225.8 | 0.67925 | 5.969
2024-12-10 | 4:21 | Data | 0 | 32.548 | 30.624 | 192.6 | 7.63 | 181.52 | 2235.18 | 25.73 | 42.116 | 6.34 | 1.369 | 4.598 | 8721.11 | 1.958 | 98.1 | 77.1 | 1453 | 21.06 | 5668.7 | 2924 | 2833.8 | 4187.7 | 1225.8 | 0.68079 | 5.967
2024-12-10 | 4:21 | Data | 0 | 32.44 | 30.59 | 192.6 | 7.63 | 181.43 | 2234.27 | 25.74 | 42.387 | 6.34 | 1.356 | 4.576 | 8707.55 | 1.944 | 98.1 | 77.1 | 1452 | 21.19 | 5659.9 | 2930.1 | 2844.7 | 4206.2 | 1225.8 | 0.68127 | 5.931
2024-12-10 | 4:21 | Data | 0 | 32.723 | 30.489 | 192.645 | 7.63 | 181.52 | 2235.18 | 25.73 | 42.116 | 6.34 | 1.367 | 4.569 | 8712.07 | 2.046 | 98.1 | 77 | 1453 | 21.1 | 5662.8 | 2895.6 | 2848.7 | 4180.5 | 1225.9 | 0.67613 | 5.934
2024-12-10 | 4:21 | Data | 0 | 32.413 | 30.766 | 192.6 | 7.63 | 181.43 | 2235.18 | 25.74 | 41.845 | 6.33 | 1.37 | 4.614 | 8743.73 | 1.89 | 98.1 | 77.1 | 1453 | 20.92 | 5683.4 | 2916.1 | 2817.1 | 4171.1 | 1225.9 | 0.68138 | 5.984
2024-12-10 | 4:21 | Data | 0 | 32.94 | 30.678 | 192.645 | 7.64 | 181.475 | 2236.08 | 25.74 | 42.026 | 6.34 | 1.371 | 4.618 | 8730.16 | 2.073 | 98.1 | 77.1 | 1453 | 21.01 | 5674.6 | 2922.2 | 2842.8 | 4190.3 | 1225.9 | 0.67986 | 5.989
2024-12-10 | 4:21 | Data | 0 | 32.494 | 30.651 | 192.51 | 7.63 | 181.475 | 2234.27 | 25.74 | 42.116 | 6.34 | 1.375 | 4.607 | 8716.59 | 1.843 | 98.1 | 77 | 1452 | 21.06 | 5665.8 | 2922.1 | 2866.2 | 4209.8 | 1225.9 | 0.67717 | 5.981
2024-12-10 | 4:21 | Data | 0 | 32.609 | 30.428 | 192.645 | 7.63 | 181.475 | 2233.37 | 25.75 | 42.116 | 6.34 | 1.373 | 4.614 | 8716.59 | 2.093 | 98.1 | 77.1 | 1452 | 21.1 | 5665.8 | 2929.9 | 2869.8 | 4213.7 | 1225.9 | 0.67848 | 5.987
2024-12-10 | 4:21 | Data | 0 | 32.325 | 30.421 | 192.645 | 7.64 | 181.385 | 2232.47 | 25.74 | 42.116 | 6.34 | 1.369 | 4.593 | 8693.98 | 1.958 | 98.1 | 77 | 1451 | 21.06 | 5651.1 | 2926.3 | 2879.7 | 4219.9 | 1225.9 | 0.67612 | 5.962
2024-12-10 | 4:21 | Data | 0 | 32.474 | 30.415 | 192.6 | 7.63 | 181.385 | 2231.56 | 25.74 | 42.116 | 6.34 | 1.374 | 4.606 | 8698.5 | 2.073 | 98.1 | 77 | 1451 | 21.06 | 5654 | 2909.9 | 2869 | 4217.1 | 1225.9 | 0.67687 | 5.98
2024-12-10 | 4:21 | Data | 0 | 32.271 | 30.415 | 192.645 | 7.63 | 181.43 | 2232.47 | 25.74 | 42.116 | 6.34 | 1.366 | 4.597 | 8689.46 | 1.85 | 98.1 | 77.1 | 1451 | 21.06 | 5648.1 | 2934.5 | 2847.2 | 4201 | 1225.9 | 0.68243 | 5.963
2024-12-10 | 4:22 | Data | 0 | 32.494 | 30.82 | 192.51 | 7.63 | 181.475 | 2231.56 | 25.74 | 42.116 | 6.34 | 1.365 | 4.625 | 8671.37 | 1.965 | 98.1 | 77.2 | 1450 | 21.06 | 5636.4 | 2926.3 | 2837.6 | 4190.1 | 1225.9 | 0.68162 | 5.989
2024-12-10 | 4:22 | Data | 0 | 32.494 | 30.415 | 192.6 | 7.63 | 181.385 | 2227.04 | 25.74 | 42.206 | 6.34 | 1.356 | 4.624 | 8703.03 | 2.079 | 98.1 | 77.3 | 1448 | 21.1 | 5657 | 2914.8 | 2853.2 | 4196 | 1225.9 | 0.67787 | 5.979
2024-12-10 | 4:22 | Data | 0 | 32.548 | 30.421 | 192.6 | 7.63 | 181.43 | 2225.23 | 25.74 | 42.116 | 6.33 | 1.369 | 4.617 | 8689.46 | 2.073 | 98.1 | 77.1 | 1446 | 21.06 | 5648.1 | 2928.7 | 2870.7 | 4214.8 | 1225.9 | 0.6776 | 5.988
2024-12-10 | 4:22 | Data | 0 | 32.723 | 30.874 | 192.69 | 7.63 | 181.52 | 2224.33 | 25.75 | 42.116 | 6.34 | 1.369 | 4.632 | 8693.98 | 1.971 | 98.1 | 77.2 | 1446 | 21.1 | 5651.1 | 2909.2 | 2861.9 | 4197.5 | 1225.9 | 0.67566 | 6
2024-12-10 | 4:22 | Data | 0 | 32.44 | 31.029 | 192.6 | 7.63 | 181.475 | 2230.66 | 25.75 | 42.116 | 6.34 | 1.362 | 4.597 | 8680.41 | 1.978 | 98.1 | 77.1 | 1450 | 21.06 | 5642.3 | 2909.2 | 2878.1 | 4206.6 | 1225.9 | 0.67551 | 5.96
2024-12-10 | 4:22 | Data | 0 | 32.507 | 30.759 | 192.51 | 7.63 | 181.43 | 2225.23 | 25.75 | 42.116 | 6.34 | 1.367 | 4.613 | 8693.98 | 1.904 | 98.1 | 77.1 | 1446 | 21.1 | 5651.1 | 2906.3 | 2871.4 | 4205.8 | 1225.9 | 0.67376 | 5.979
2024-12-10 | 4:22 | Data | 0 | 32.669 | 30.475 | 192.464 | 7.63 | 181.385 | 2225.23 | 25.75 | 42.116 | 6.34 | 1.371 | 4.621 | 8671.37 | 2.073 | 98.1 | 77.1 | 1446 | 21.1 | 5636.4 | 2913.7 | 2838.9 | 4186.6 | 1225.9 | 0.67897 | 5.992
2024-12-10 | 4:22 | Data | 0 | 32.669 | 30.644 | 192.51 | 7.63 | 181.385 | 2227.95 | 25.74 | 42.116 | 6.34 | 1.364 | 4.578 | 8662.33 | 2.059 | 98.1 | 77 | 1448 | 21.06 | 5630.5 | 2918 | 2832.6 | 4186.6 | 1225.9 | 0.67917 | 5.942
2024-12-10 | 4:22 | Data | 0 | 32.379 | 30.536 | 192.419 | 7.63 | 181.385 | 2229.75 | 25.75 | 42.116 | 6.34 | 1.362 | 4.606 | 8653.28 | 2.039 | 98.1 | 77.2 | 1449 | 21.06 | 5624.6 | 2896.5 | 2840.6 | 4180.6 | 1225.9 | 0.67836 | 5.967
2024-12-10 | 4:22 | Data | 0 | 32.386 | 30.847 | 192.645 | 7.63 | 181.475 | 2233.37 | 25.75 | 42.116 | 6.34 | 1.359 | 4.602 | 8635.19 | 1.917 | 98.1 | 77.2 | 1452 | 21.06 | 5612.9 | 2909.8 | 2828.1 | 4174.5 | 1225.9 | 0.67902 | 5.961
2024-12-10 | 4:22 | Data | 0 | 32.507 | 30.448 | 192.69 | 7.63 | 181.475 | 2232.47 | 25.75 | 42.206 | 6.34 | 1.361 | 4.604 | 8626.15 | 2.167 | 98.1 | 77.2 | 1451 | 21.06 | 5607 | 2920 | 2834.8 | 4186.3 | 1225.9 | 0.68028 | 5.966
2024-12-10 | 4:22 | Data | 0 | 32.332 | 30.59 | 192.51 | 7.63 | 181.43 | 2233.37 | 25.74 | 42.116 | 6.34 | 1.372 | 4.602 | 8621.63 | 2.032 | 98.1 | 77 | 1452 | 21.06 | 5604.1 | 2923.1 | 2847.9 | 4195 | 1225.9 | 0.67888 | 5.975
2024-12-10 | 4:22 | Data | 0 | 32.494 | 30.651 | 192.6 | 7.63 | 181.475 | 2232.47 | 25.74 | 42.206 | 6.34 | 1.36 | 4.579 | 8630.67 | 2.019 | 98.1 | 77.1 | 1451 | 21.1 | 5609.9 | 2925 | 2863.5 | 4208.8 | 1225.9 | 0.6771 | 5.94
2024-12-10 | 4:22 | Data | 0 | 32.838 | 30.421 | 192.69 | 7.63 | 181.566 | 2233.37 | 25.75 | 42.116 | 6.33 | 1.359 | 4.604 | 8621.63 | 2.093 | 98.1 | 77.2 | 1452 | 21.1 | 5604.1 | 2911.2 | 2866.2 | 4203.3 | 1225.9 | 0.67446 | 5.962
2024-12-10 | 4:22 | Data | 0 | 32.548 | 30.563 | 192.645 | 7.63 | 181.385 | 2232.47 | 25.74 | 42.116 | 6.34 | 1.364 | 4.594 | 8635.19 | 2.025 | 98.1 | 77.1 | 1452 | 21.06 | 5612.9 | 2919.8 | 2859.7 | 4201.9 | 1225.9 | 0.67827 | 5.959
2024-12-10 | 4:22 | Data | 0 | 32.669 | 30.705 | 192.645 | 7.63 | 181.43 | 2233.37 | 25.75 | 42.116 | 6.34 | 1.361 | 4.605 | 8639.71 | 2.127 | 98.1 | 77.2 | 1451 | 21.06 | 5615.8 | 2936.3 | 2849.5 | 4203.2 | 1225.9 | 0.68146 | 5.966
2024-12-10 | 4:22 | Data | 0 | 32.723 | 30.766 | 192.6 | 7.63 | 181.475 | 2230.66 | 25.74 | 42.116 | 6.34 | 1.357 | 4.607 | 8626.15 | 2.073 | 98.1 | 77.3 | 1450 | 21.06 | 5607 | 2924 | 2836.4 | 4187 | 1225.9 | 0.68084 | 5.964
2024-12-10 | 4:22 | Data | 0 | 32.717 | 30.664 | 192.51 | 7.63 | 181.566 | 2227.04 | 25.75 | 42.116 | 6.34 | 1.353 | 4.598 | 8635.19 | 2.059 | 98.1 | 77.3 | 1448 | 21.06 | 5612.9 | 2913.4 | 2845.3 | 4185.6 | 1225.9 | 0.67906 | 5.95
2024-12-10 | 4:23 | Data | 0 | 32.723 | 30.651 | 192.645 | 7.63 | 181.52 | 2227.04 | 25.74 | 42.116 | 6.34 | 1.355 | 4.598 | 8648.76 | 2.073 | 98.1 | 77.3 | 1448 | 21.06 | 5621.7 | 2922.2 | 2826.5 | 4185.4 | 1225.9 | 0.67929 | 5.952
2024-12-10 | 4:23 | Data | 0 | 32.946 | 30.489 | 192.871 | 7.64 | 181.475 | 2228.85 | 25.74 | 42.116 | 6.34 | 1.36 | 4.612 | 8653.28 | 2.073 | 98.1 | 77.2 | 1449 | 21.01 | 5624.6 | 2925.1 | 2820.3 | 4178.2 | 1225.9 | 0.68384 | 5.972
2024-12-10 | 4:23 | Data | 0 | 32.528 | 30.563 | 192.51 | 7.63 | 181.385 | 2229.75 | 25.75 | 42.206 | 6.34 | 1.365 | 4.635 | 8644.24 | 1.971 | 98.1 | 77.3 | 1450 | 21.06 | 5618.8 | 2930 | 2836 | 4193.6 | 1225.9 | 0.68113 | 6
2024-12-10 | 4:23 | Data | 0 | 32.994 | 30.502 | 192.736 | 7.63 | 181.566 | 2236.08 | 25.75 | 42.116 | 6.34 | 1.367 | 4.587 | 8662.33 | 2.025 | 98.1 | 77 | 1453 | 21.06 | 5630.5 | 2928.3 | 2848.4 | 4200.8 | 1225.9 | 0.68117 | 5.953
2024-12-10 | 4:23 | Data | 0 | 32.804 | 30.759 | 192.464 | 7.63 | 181.52 | 2235.18 | 25.75 | 42.116 | 6.34 | 1.372 | 4.584 | 8680.41 | 2.059 | 98.1 | 77 | 1452 | 21.06 | 5642.3 | 2926.6 | 2846 | 4197.2 | 1225.9 | 0.67714 | 5.956
2024-12-10 | 4:23 | Data | 0 | 32.669 | 30.536 | 192.69 | 7.63 | 181.385 | 2235.18 | 25.75 | 42.116 | 6.34 | 1.358 | 4.621 | 8671.37 | 2.046 | 98.1 | 77.3 | 1453 | 21.06 | 5636.4 | 2917.3 | 2848 | 4191.7 | 1225.9 | 0.67815 | 5.98
2024-12-10 | 4:23 | Data | 0 | 32.723 | 30.631 | 192.6 | 7.63 | 181.475 | 2235.18 | 25.74 | 42.116 | 6.34 | 1.349 | 4.607 | 8671.37 | 2.046 | 98.1 | 77.4 | 1453 | 21.06 | 5636.4 | 2916.7 | 2852.5 | 4197.1 | 1225.9 | 0.67723 | 5.958
2024-12-10 | 4:23 | Data | 0 | 32.926 | 30.57 | 192.69 | 7.63 | 181.43 | 2235.18 | 25.75 | 42.116 | 6.34 | 1.353 | 4.6 | 8703.03 | 2.106 | 98.1 | 77.3 | 1453 | 21.06 | 5657 | 2917.3 | 2854.8 | 4201.8 | 1225.9 | 0.67819 | 5.952
2024-12-10 | 4:23 | Data | 0 | 32.933 | 30.658 | 192.69 | 7.63 | 181.52 | 2236.08 | 25.75 | 42.116 | 6.34 | 1.361 | 4.616 | 8630.67 | 1.971 | 98.1 | 77.2 | 1453 | 21.06 | 5609.9 | 2906.9 | 2845.8 | 4182.9 | 1225.9 | 0.67769 | 5.977
2024-12-10 | 4:23 | Data | 0 | 32.494 | 30.516 | 192.464 | 7.63 | 181.385 | 2227.95 | 25.75 | 42.116 | 6.34 | 1.369 | 4.623 | 8635.19 | 1.87 | 98.1 | 77.1 | 1448 | 21.06 | 5612.9 | 2922.7 | 2834.9 | 4186.9 | 1225.9 | 0.68024 | 5.991
2024-12-10 | 4:23 | Data | 0 | 32.94 | 30.705 | 192.69 | 7.63 | 181.475 | 2227.95 | 25.74 | 42.116 | 6.34 | 1.362 | 4.603 | 8648.76 | 1.958 | 98.1 | 77.2 | 1448 | 21.06 | 5621.7 | 2909.1 | 2843.9 | 4186.8 | 1226 | 0.67846 | 5.964
2024-12-10 | 4:23 | Data | 0 | 32.892 | 30.874 | 192.6 | 7.63 | 181.52 | 2229.75 | 25.74 | 42.116 | 6.34 | 1.353 | 4.597 | 8648.76 | 2.073 | 98.1 | 77.3 | 1450 | 21.06 | 5621.7 | 2915.2 | 2856.7 | 4199.5 | 1226 | 0.67774 | 5.95
2024-12-10 | 4:23 | Data | 0 | 32.494 | 30.415 | 192.645 | 7.63 | 181.52 | 2222.52 | 25.75 | 42.116 | 6.34 | 1.366 | 4.612 | 8648.76 | 2.073 | 98.1 | 77.2 | 1445 | 21.1 | 5621.7 | 2938.7 | 2842.1 | 4202.6 | 1226 | 0.68253 | 5.978
2024-12-10 | 4:23 | Data | 0 | 32.825 | 30.651 | 192.736 | 7.63 | 181.52 | 2217.1 | 25.75 | 42.116 | 6.34 | 1.362 | 4.58 | 8648.76 | 2.235 | 98.1 | 77.1 | 1441 | 21.06 | 5621.7 | 2947.6 | 2854.7 | 4219 | 1226 | 0.68238 | 5.942
2024-12-10 | 4:23 | Data | 0 | 32.528 | 30.86 | 192.736 | 7.63 | 181.52 | 2225.23 | 25.74 | 42.206 | 6.34 | 1.374 | 4.551 | 8648.76 | 1.789 | 98.1 | 76.8 | 1446 | 21.1 | 5621.7 | 2945.6 | 2837.7 | 4200.7 | 1226 | 0.68393 | 5.925
2024-12-10 | 4:23 | Data | 0 | 32.723 | 30.651 | 192.6 | 7.63 | 181.475 | 2226.14 | 25.75 | 42.026 | 6.34 | 1.372 | 4.597 | 8653.28 | 2.073 | 98.1 | 77 | 1446 | 21.01 | 5624.6 | 2905.4 | 2841.8 | 4186.8 | 1226 | 0.67724 | 5.968
2024-12-10 | 4:23 | Data | 0 | 32.487 | 30.59 | 192.6 | 7.63 | 181.43 | 2225.23 | 25.74 | 42.116 | 6.34 | 1.36 | 4.603 | 8689.46 | 2.187 | 98.1 | 77.2 | 1446 | 21.06 | 5648.1 | 2916.2 | 2859.8 | 4189.6 | 1226 | 0.67792 | 5.963
2024-12-10 | 4:24 | Data | 0 | 32.723 | 30.651 | 192.69 | 7.63 | 181.52 | 2225.23 | 25.75 | 42.116 | 6.34 | 1.359 | 4.598 | 8707.55 | 1.87 | 98.1 | 77.2 | 1446 | 21.1 | 5659.9 | 2928 | 2823.1 | 4183.2 | 1226 | 0.68296 | 5.959
2024-12-10 | 4:24 | Data | 0 | 32.521 | 30.604 | 192.6 | 7.63 | 181.52 | 2226.14 | 25.74 | 42.116 | 6.34 | 1.364 | 4.595 | 8693.98 | 2.032 | 98.1 | 77.1 | 1447 | 21.06 | 5651.1 | 2934.8 | 2865.9 | 4220.4 | 1226 | 0.67927 | 5.96
2024-12-10 | 4:24 | Data | 0 | 32.94 | 30.88 | 192.736 | 7.63 | 181.475 | 2229.75 | 25.74 | 42.116 | 6.34 | 1.362 | 4.619 | 8689.46 | 2.073 | 98.1 | 77.2 | 1450 | 21.1 | 5648.1 | 2917.1 | 2850.1 | 4192.5 | 1226 | 0.67759 | 5.981
2024-12-10 | 4:24 | Data | 0 | 32.568 | 30.563 | 192.781 | 7.63 | 181.656 | 2233.37 | 25.75 | 42.116 | 6.34 | 1.36 | 4.598 | 8671.37 | 1.978 | 98.1 | 77.2 | 1452 | 21.06 | 5636.4 | 2911.9 | 2844.7 | 4189.1 | 1226 | 0.67827 | 5.958
2024-12-10 | 4:24 | Data | 0 | 32.669 | 30.874 | 192.6 | 7.63 | 181.52 | 2232.47 | 25.74 | 42.206 | 6.34 | 1.364 | 4.606 | 8671.37 | 2.012 | 98.1 | 77.2 | 1451 | 21.1 | 5636.4 | 2922.1 | 2838.6 | 4188.7 | 1226 | 0.68103 | 5.969
2024-12-10 | 4:24 | Data | 0 | 32.919 | 30.651 | 192.645 | 7.63 | 181.566 | 2232.47 | 25.74 | 42.026 | 6.34 | 1.361 | 4.604 | 8680.41 | 2.093 | 98.1 | 77.2 | 1452 | 21.06 | 5642.3 | 2932 | 2830.9 | 4191.8 | 1226 | 0.68216 | 5.965
2024-12-10 | 4:24 | Data | 0 | 32.501 | 30.536 | 192.6 | 7.63 | 181.475 | 2233.37 | 25.74 | 42.116 | 6.34 | 1.357 | 4.597 | 8680.41 | 2.073 | 98.1 | 77.2 | 1451 | 21.06 | 5642.3 | 2917.2 | 2851.9 | 4198.1 | 1226 | 0.67796 | 5.953
2024-12-10 | 4:24 | Data | 0 | 32.946 | 30.448 | 192.645 | 7.63 | 181.566 | 2233.37 | 25.75 | 42.116 | 6.34 | 1.367 | 4.609 | 8693.98 | 2.093 | 98.1 | 77.1 | 1452 | 21.06 | 5651.1 | 2922.9 | 2836.9 | 4180.8 | 1226 | 0.67923 | 5.975
2024-12-10 | 4:24 | Data | 0 | 32.723 | 30.651 | 192.69 | 7.63 | 181.475 | 2232.47 | 25.75 | 42.026 | 6.34 | 1.365 | 4.614 | 8689.46 | 2.073 | 98.1 | 77.2 | 1452 | 21.06 | 5648.1 | 2925.6 | 2862 | 4209.5 | 1226 | 0.67742 | 5.979
2024-12-10 | 4:24 | Data | 0 | 32.305 | 30.644 | 192.645 | 7.63 | 181.475 | 2235.18 | 25.75 | 42.116 | 6.35 | 1.363 | 4.591 | 8693.98 | 1.944 | 98.1 | 77.1 | 1452 | 21.06 | 5651.1 | 2924.4 | 2839 | 4190 | 1226 | 0.68001 | 5.954
2024-12-10 | 4:24 | Data | 0 | 32.501 | 30.469 | 192.645 | 7.63 | 181.43 | 2235.18 | 25.75 | 42.026 | 6.34 | 1.361 | 4.634 | 8689.46 | 1.85 | 98.1 | 77.3 | 1453 | 21.01 | 5648.1 | 2922.9 | 2822.6 | 4185.5 | 1226 | 0.68165 | 5.995
2024-12-10 | 4:24 | Data | 0 | 32.609 | 30.766 | 192.736 | 7.63 | 181.43 | 2236.08 | 25.74 | 42.116 | 6.34 | 1.367 | 4.638 | 8703.03 | 1.897 | 98.1 | 77.2 | 1453 | 21.01 | 5657 | 2917.6 | 2855.7 | 4198 | 1226 | 0.67891 | 6.005
2024-12-10 | 4:24 | Data | 0 | 32.602 | 30.428 | 192.645 | 7.63 | 181.52 | 2235.18 | 25.74 | 42.116 | 6.34 | 1.367 | 4.625 | 8703.03 | 2.066 | 98.1 | 77.2 | 1453 | 21.1 | 5657 | 2929.5 | 2840.4 | 4195.5 | 1226 | 0.68168 | 5.991
2024-12-10 | 4:24 | Data | 0 | 32.946 | 30.793 | 192.69 | 7.63 | 181.52 | 2239.7 | 25.74 | 42.116 | 6.34 | 1.359 | 4.612 | 8689.46 | 1.971 | 98.1 | 77.2 | 1455 | 21.06 | 5648.1 | 2949.7 | 2850 | 4214.9 | 1226 | 0.68326 | 5.971
2024-12-10 | 4:24 | Data | 0 | 32.926 | 31.096 | 192.781 | 7.63 | 181.611 | 2241.5 | 25.74 | 42.206 | 6.34 | 1.359 | 4.6 | 8693.98 | 2.039 | 98.1 | 77.2 | 1457 | 21.1 | 5651.1 | 2920.5 | 2873.8 | 4211.1 | 1226 | 0.67625 | 5.959
2024-12-10 | 4:24 | Data | 0 | 32.609 | 30.651 | 192.6 | 7.63 | 181.385 | 2244.22 | 25.75 | 42.116 | 6.34 | 1.358 | 4.572 | 8689.46 | 2.059 | 98.1 | 77.1 | 1459 | 21.06 | 5648.1 | 2917.8 | 2851.2 | 4198.7 | 1226 | 0.6772 | 5.93
2024-12-10 | 4:24 | Data | 0 | 32.615 | 30.644 | 192.6 | 7.63 | 181.475 | 2244.22 | 25.74 | 42.116 | 6.34 | 1.358 | 4.572 | 8693.98 | 1.89 | 98.1 | 77.1 | 1459 | 21.06 | 5651.1 | 2917.6 | 2852.5 | 4195.2 | 1226 | 0.67811 | 5.931
2024-12-10 | 4:24 | Data | 0 | 32.899 | 30.577 | 192.917 | 7.63 | 181.656 | 2245.12 | 25.75 | 42.206 | 6.34 | 1.357 | 4.626 | 8671.37 | 2.228 | 98.1 | 77.3 | 1459 | 21.06 | 5636.4 | 2928 | 2870.2 | 4221.4 | 1226 | 0.67519 | 5.983
2024-12-10 | 4:25 | Data | 0 | 32.723 | 30.766 | 192.781 | 7.63 | 181.52 | 2244.22 | 25.74 | 42.116 | 6.34 | 1.358 | 4.632 | 8689.46 | 1.958 | 98.1 | 77.3 | 1459 | 21.1 | 5648.1 | 2943 | 2849.2 | 4211.5 | 1226 | 0.67823 | 5.989
2024-12-10 | 4:25 | Data | 0 | 32.568 | 30.448 | 192.781 | 7.63 | 181.611 | 2246.02 | 25.74 | 42.116 | 6.34 | 1.369 | 4.623 | 8680.41 | 1.985 | 98.1 | 77.1 | 1461 | 21.06 | 5642.3 | 2920.5 | 2882.1 | 4222.2 | 1226 | 0.67486 | 5.992
2024-12-10 | 4:25 | Data | 0 | 32.919 | 30.793 | 192.736 | 7.63 | 181.611 | 2241.5 | 25.75 | 42.116 | 6.33 | 1.374 | 4.624 | 8680.41 | 2.066 | 98.1 | 77.1 | 1456 | 21.06 | 5642.3 | 2921.2 | 2868.1 | 4210.4 | 1226 | 0.6756 | 5.997
2024-12-10 | 4:25 | Data | 0 | 32.548 | 30.475 | 192.645 | 7.63 | 181.475 | 2244.22 | 25.75 | 41.845 | 6.34 | 1.373 | 4.633 | 8680.41 | 1.87 | 98.1 | 77.1 | 1459 | 20.92 | 5642.3 | 2908.9 | 2870.2 | 4198.7 | 1226 | 0.67622 | 6.006
2024-12-10 | 4:25 | Data | 0 | 32.568 | 30.435 | 192.645 | 7.63 | 181.566 | 2241.5 | 25.75 | 42.116 | 6.34 | 1.367 | 4.633 | 8680.41 | 2.079 | 98.1 | 77.2 | 1457 | 21.06 | 5642.3 | 2927.6 | 2865 | 4202.9 | 1226 | 0.6786 | 6
2024-12-10 | 4:25 | Data | 0 | 32.723 | 30.664 | 192.69 | 7.63 | 181.611 | 2241.5 | 25.74 | 42.206 | 6.34 | 1.358 | 4.598 | 8680.41 | 2.046 | 98.1 | 77.2 | 1457 | 21.06 | 5642.3 | 2911.8 | 2841.2 | 4186.6 | 1226 | 0.67843 | 5.955
2024-12-10 | 4:25 | Data | 0 | 32.683 | 30.705 | 192.781 | 7.63 | 181.566 | 2241.5 | 25.74 | 41.936 | 6.34 | 1.356 | 4.607 | 8644.24 | 2.133 | 98.1 | 77.3 | 1457 | 20.97 | 5618.8 | 2921.8 | 2827.8 | 4178.8 | 1226 | 0.68184 | 5.963
2024-12-10 | 4:25 | Data | 0 | 32.609 | 30.752 | 192.645 | 7.63 | 181.52 | 2241.5 | 25.75 | 42.116 | 6.34 | 1.358 | 4.616 | 8653.28 | 1.85 | 98.1 | 77.3 | 1458 | 21.06 | 5624.6 | 2929.7 | 2836.5 | 4192.9 | 1226 | 0.68165 | 5.973
2024-12-10 | 4:25 | Data | 0 | 32.919 | 30.705 | 192.826 | 7.63 | 181.656 | 2241.5 | 25.75 | 42.116 | 6.34 | 1.365 | 4.602 | 8648.76 | 2.066 | 98.1 | 77.1 | 1456 | 21.06 | 5621.7 | 2931.2 | 2842.3 | 4200.6 | 1226 | 0.68176 | 5.968
2024-12-10 | 4:25 | Data | 0 | 32.953 | 30.894 | 192.826 | 7.63 | 181.611 | 2238.79 | 25.75 | 42.116 | 6.34 | 1.366 | 4.598 | 8680.41 | 2.046 | 98.1 | 77.1 | 1455 | 21.06 | 5642.3 | 2921.3 | 2845.4 | 4194.6 | 1226 | 0.67895 | 5.962
2024-12-10 | 4:25 | Data | 0 | 32.494 | 30.529 | 192.6 | 7.63 | 181.475 | 2236.08 | 25.74 | 42.116 | 6.34 | 1.365 | 4.62 | 8644.24 | 2.079 | 98.1 | 77.2 | 1453 | 21.01 | 5618.8 | 2913.6 | 2840.1 | 4184.4 | 1226 | 0.67967 | 5.985
2024-12-10 | 4:25 | Data | 0 | 32.501 | 30.745 | 192.736 | 7.63 | 181.52 | 2233.37 | 25.75 | 42.116 | 6.33 | 1.375 | 4.623 | 8630.67 | 1.965 | 98.1 | 77.1 | 1451 | 21.06 | 5609.9 | 2937.9 | 2835.4 | 4200 | 1226.1 | 0.68161 | 5.997
2024-12-10 | 4:25 | Data | 0 | 32.865 | 30.88 | 192.826 | 7.63 | 181.611 | 2232.47 | 25.74 | 42.206 | 6.33 | 1.373 | 4.588 | 8657.8 | 2.059 | 98.1 | 77 | 1451 | 21.06 | 5627.6 | 2920.7 | 2843.3 | 4192.2 | 1226.1 | 0.67954 | 5.96
2024-12-10 | 4:25 | Data | 0 | 32.507 | 30.597 | 192.69 | 7.63 | 181.566 | 2229.75 | 25.75 | 41.845 | 6.34 | 1.373 | 4.58 | 8648.76 | 2.066 | 98.1 | 76.9 | 1450 | 20.92 | 5621.7 | 2918.2 | 2849.4 | 4201.8 | 1226.1 | 0.68063 | 5.953
2024-12-10 | 4:25 | Data | 0 | 32.609 | 30.691 | 192.736 | 7.63 | 181.52 | 2227.95 | 25.75 | 42.116 | 6.34 | 1.361 | 4.593 | 8666.85 | 2.079 | 98.1 | 77.1 | 1449 | 21.06 | 5633.5 | 2919.4 | 2849.9 | 4196.5 | 1226.1 | 0.67772 | 5.954
2024-12-10 | 4:25 | Data | 0 | 32.75 | 30.651 | 192.69 | 7.63 | 181.475 | 2228.85 | 25.75 | 42.116 | 6.34 | 1.355 | 4.593 | 8657.8 | 1.897 | 98.1 | 77.2 | 1448 | 21.06 | 5627.6 | 2916.3 | 2846.2 | 4190.9 | 1226.1 | 0.67811 | 5.948
2024-12-10 | 4:25 | Data | 0 | 32.609 | 30.421 | 192.69 | 7.63 | 181.52 | 2227.95 | 25.75 | 42.026 | 6.34 | 1.357 | 4.604 | 8648.76 | 2.268 | 98.1 | 77.2 | 1448 | 21.06 | 5621.7 | 2915.5 | 2824.3 | 4177.7 | 1226.1 | 0.68047 | 5.96
2024-12-10 | 4:25 | Data | 0 | 32.636 | 30.658 | 192.69 | 7.63 | 181.611 | 2182.75 | 25.75 | 42.116 | 6.34 | 1.366 | 4.631 | 8644.24 | 1.857 | 98.1 | 77.2 | 1418 | 21.06 | 5618.8 | 2910.6 | 2828.2 | 4175.3 | 1226.1 | 0.68026 | 5.997
2024-12-10 | 4:26 | Data | 0 | 32.784 | 30.658 | 192.781 | 7.63 | 181.611 | 2174.62 | 25.74 | 42.116 | 6.34 | 1.363 | 4.591 | 8648.76 | 1.897 | 98.1 | 77.1 | 1414 | 21.06 | 5621.7 | 2907.5 | 2842.5 | 4184.6 | 1226.1 | 0.67799 | 5.954
2024-12-10 | 4:26 | Data | 0 | 32.717 | 30.651 | 192.645 | 7.63 | 181.52 | 2167.39 | 25.74 | 42.116 | 6.34 | 1.369 | 4.58 | 8644.24 | 2.073 | 98.1 | 77 | 1409 | 21.06 | 5618.8 | 2916.6 | 2834.1 | 4186.6 | 1226.1 | 0.68068 | 5.949
2024-12-10 | 4:26 | Data | 0 | 32.71 | 30.806 | 192.781 | 7.63 | 181.611 | 2164.68 | 25.74 | 42.026 | 6.33 | 1.37 | 4.6 | 8648.76 | 2.154 | 98.1 | 77.1 | 1407 | 21.06 | 5621.7 | 2908.6 | 2843.1 | 4194.7 | 1226.1 | 0.6788 | 5.97
2024-12-10 | 4:26 | Data | 0 | 32.865 | 30.658 | 192.826 | 7.63 | 181.611 | 2190.89 | 25.75 | 42.116 | 6.34 | 1.362 | 4.596 | 8648.76 | 1.884 | 98.1 | 77.1 | 1426 | 21.06 | 5621.7 | 2911 | 2850.3 | 4193.1 | 1226.1 | 0.67589 | 5.958
2024-12-10 | 4:26 | Data | 0 | 32.791 | 30.651 | 192.826 | 7.63 | 181.566 | 2221.62 | 25.74 | 42.116 | 6.34 | 1.354 | 4.597 | 8680.41 | 2.046 | 98.1 | 77.2 | 1444 | 21.06 | 5642.3 | 2911.4 | 2853.7 | 4195.8 | 1226.1 | 0.67748 | 5.95
2024-12-10 | 4:26 | Data | 0 | 32.777 | 30.475 | 192.781 | 7.63 | 181.566 | 2218 | 25.74 | 42.116 | 6.33 | 1.359 | 4.629 | 8680.41 | 1.971 | 98.1 | 77.3 | 1442 | 21.06 | 5642.3 | 2927.9 | 2845.6 | 4198 | 1226.1 | 0.68044 | 5.988
2024-12-10 | 4:26 | Data | 0 | 32.75 | 30.536 | 192.69 | 7.63 | 181.611 | 2218.91 | 25.74 | 42.026 | 6.34 | 1.362 | 4.585 | 8684.94 | 2.066 | 98.1 | 77.1 | 1442 | 21.06 | 5645.2 | 2914 | 2837.4 | 4182.8 | 1226.1 | 0.67971 | 5.948
2024-12-10 | 4:26 | Data | 0 | 32.926 | 30.543 | 192.736 | 7.64 | 181.656 | 2218 | 25.75 | 42.206 | 6.34 | 1.361 | 4.604 | 8684.94 | 2.201 | 98.1 | 77.2 | 1442 | 21.1 | 5645.2 | 2918.9 | 2819.9 | 4172.3 | 1226.1 | 0.68262 | 5.965
2024-12-10 | 4:26 | Data | 0 | 32.676 | 30.435 | 192.645 | 7.63 | 181.611 | 2214.39 | 25.76 | 42.116 | 6.34 | 1.36 | 4.598 | 8653.28 | 2.1 | 98.1 | 77.2 | 1439 | 21.06 | 5624.6 | 2938.3 | 2825 | 4191.1 | 1226.1 | 0.68474 | 5.959
2024-12-10 | 4:26 | Data | 0 | 32.831 | 30.833 | 192.736 | 7.63 | 181.611 | 2208.06 | 25.74 | 42.116 | 6.34 | 1.367 | 4.602 | 8644.24 | 2.073 | 98.1 | 77.1 | 1436 | 21.06 | 5618.8 | 2922.1 | 2826 | 4177 | 1226.1 | 0.6823 | 5.972
2024-12-10 | 4:26 | Data | 0 | 32.737 | 30.739 | 192.69 | 7.63 | 181.566 | 2214.39 | 25.75 | 42.116 | 6.34 | 1.38 | 4.589 | 8639.71 | 1.965 | 98.1 | 76.9 | 1439 | 21.06 | 5615.8 | 2918.3 | 2821.3 | 4172.8 | 1226.1 | 0.68146 | 5.969
2024-12-10 | 4:26 | Data | 0 | 32.723 | 30.982 | 192.69 | 7.63 | 181.52 | 2213.49 | 25.75 | 42.206 | 6.34 | 1.367 | 4.6 | 8639.71 | 1.897 | 98.1 | 77.1 | 1439 | 21.06 | 5615.8 | 2911.6 | 2844.3 | 4184.4 | 1226.1 | 0.67945 | 5.968
2024-12-10 | 4:26 | Data | 0 | 32.946 | 30.88 | 192.736 | 7.63 | 181.656 | 2216.2 | 25.75 | 42.116 | 6.33 | 1.36 | 4.619 | 8644.24 | 2.066 | 98.1 | 77.3 | 1440 | 21.06 | 5618.8 | 2924.2 | 2823.7 | 4184.7 | 1226.1 | 0.68308 | 5.98
2024-12-10 | 4:26 | Data | 0 | 32.723 | 30.651 | 192.645 | 7.63 | 181.566 | 2218.91 | 25.75 | 42.026 | 6.34 | 1.354 | 4.616 | 8644.24 | 2.073 | 98.1 | 77.3 | 1442 | 21.06 | 5618.8 | 2917.6 | 2824.9 | 4176.9 | 1226.1 | 0.68177 | 5.969
2024-12-10 | 4:26 | Data | 0 | 33.048 | 30.799 | 192.781 | 7.63 | 181.656 | 2220.72 | 25.74 | 42.206 | 6.33 | 1.367 | 4.632 | 8653.28 | 2.046 | 98.1 | 77.2 | 1442 | 21.06 | 5624.6 | 2924.8 | 2832.5 | 4184.8 | 1226.1 | 0.68221 | 5.998
2024-12-10 | 4:26 | Data | 0 | 32.994 | 30.664 | 192.736 | 7.63 | 181.611 | 2220.72 | 25.75 | 42.206 | 6.33 | 1.361 | 4.628 | 8653.28 | 1.965 | 98.1 | 77.3 | 1442 | 21.06 | 5624.6 | 2906.9 | 2816.4 | 4163 | 1226.1 | 0.68109 | 5.988
2024-12-10 | 4:26 | Data | 0 | 32.879 | 30.651 | 192.736 | 7.63 | 181.566 | 2218.91 | 25.74 | 42.206 | 6.34 | 1.374 | 4.591 | 8662.33 | 2.181 | 98.1 | 77 | 1442 | 21.01 | 5630.5 | 2923.5 | 2827.4 | 4181.2 | 1226.1 | 0.68185 | 5.965
2024-12-10 | 4:26 | Data | 0 | 32.838 | 30.853 | 192.69 | 7.63 | 181.611 | 2221.62 | 25.76 | 42.206 | 6.33 | 1.367 | 4.606 | 8662.33 | 1.877 | 98.1 | 77.1 | 1445 | 21.06 | 5630.5 | 2933.2 | 2833.4 | 4190.9 | 1226.1 | 0.68295 | 5.972
2024-12-10 | 4:27 | Data | 0 | 32.494 | 30.847 | 192.6 | 7.63 | 181.52 | 2221.62 | 25.77 | 42.116 | 6.33 | 1.366 | 4.611 | 8657.8 | 1.911 | 98.1 | 77.2 | 1445 | 21.06 | 5627.6 | 2934.8 | 2846.2 | 4204.7 | 1226.1 | 0.68175 | 5.976
2024-12-10 | 4:27 | Data | 0 | 32.94 | 30.685 | 192.826 | 7.63 | 181.611 | 2218.91 | 25.76 | 42.206 | 6.34 | 1.367 | 4.599 | 8662.33 | 2.113 | 98.1 | 77.1 | 1442 | 21.1 | 5630.5 | 2919.9 | 2831.2 | 4186.3 | 1226.1 | 0.67939 | 5.968
2024-12-10 | 4:27 | Data | 0 | 32.885 | 30.988 | 192.781 | 7.63 | 181.566 | 2222.52 | 25.77 | 42.206 | 6.34 | 1.366 | 4.596 | 8680.41 | 1.965 | 98.1 | 77.1 | 1445 | 21.06 | 5642.3 | 2916 | 2819.9 | 4174.9 | 1226.1 | 0.68194 | 5.961
2024-12-10 | 4:27 | Data | 0 | 32.723 | 30.651 | 192.69 | 7.63 | 181.475 | 2223.43 | 25.75 | 42.206 | 6.34 | 1.366 | 4.598 | 8680.41 | 2.073 | 98.1 | 77.1 | 1445 | 21.1 | 5642.3 | 2930 | 2848.8 | 4201.4 | 1226.1 | 0.68188 | 5.964
2024-12-10 | 4:27 | Data | 0 | 32.561 | 30.678 | 192.781 | 7.63 | 181.566 | 2227.95 | 25.75 | 42.206 | 6.34 | 1.364 | 4.616 | 8662.33 | 1.836 | 98.1 | 77.2 | 1448 | 21.06 | 5630.5 | 2925.8 | 2839.7 | 4191.1 | 1226.1 | 0.68122 | 5.979
2024-12-10 | 4:27 | Data | 0 | 32.723 | 30.671 | 192.781 | 7.63 | 181.611 | 2228.85 | 25.76 | 42.116 | 6.33 | 1.363 | 4.62 | 8657.8 | 1.992 | 98.1 | 77.2 | 1448 | 21.06 | 5627.6 | 2919.2 | 2852.9 | 4198.2 | 1226.1 | 0.67795 | 5.982
2024-12-10 | 4:27 | Data | 0 | 32.507 | 30.651 | 192.736 | 7.63 | 181.475 | 2218 | 25.77 | 42.116 | 6.34 | 1.367 | 4.594 | 8648.76 | 1.958 | 98.1 | 77.1 | 1442 | 21.1 | 5621.7 | 2915.5 | 2846.9 | 4191.4 | 1226.1 | 0.68013 | 5.96
2024-12-10 | 4:27 | Data | 0 | 32.791 | 30.651 | 192.69 | 7.63 | 181.611 | 2225.23 | 25.76 | 42.116 | 6.34 | 1.359 | 4.599 | 8639.71 | 1.877 | 98.1 | 77.2 | 1446 | 21.01 | 5615.8 | 2921.7 | 2853 | 4196.6 | 1226.1 | 0.67861 | 5.961
2024-12-10 | 4:27 | Data | 0 | 32.501 | 30.847 | 192.736 | 7.63 | 181.52 | 2224.33 | 25.76 | 42.116 | 6.34 | 1.358 | 4.607 | 8648.76 | 1.755 | 98.1 | 77.2 | 1446 | 21.06 | 5621.7 | 2923.9 | 2833.1 | 4188.7 | 1226.1 | 0.68034 | 5.966
2024-12-10 | 4:27 | Data | 0 | 33.034 | 30.664 | 192.736 | 7.63 | 181.656 | 2225.23 | 25.76 | 42.116 | 6.34 | 1.37 | 4.597 | 8644.24 | 2.073 | 98.1 | 77 | 1446 | 21.01 | 5618.8 | 2914.6 | 2837 | 4181.3 | 1226.1 | 0.68037 | 5.968
2024-12-10 | 4:27 | Data | 0 | 32.622 | 30.651 | 192.69 | 7.63 | 181.611 | 2227.95 | 25.76 | 42.116 | 6.33 | 1.367 | 4.595 | 8657.8 | 2.059 | 98.1 | 77.1 | 1448 | 21.06 | 5627.6 | 2912 | 2836.2 | 4190.4 | 1226.1 | 0.68019 | 5.962
2024-12-10 | 4:27 | Data | 0 | 32.723 | 30.631 | 192.736 | 7.63 | 181.656 | 2227.04 | 25.76 | 42.026 | 6.34 | 1.363 | 4.611 | 8666.85 | 2.113 | 98.1 | 77.2 | 1448 | 21.06 | 5633.5 | 2915.8 | 2821.2 | 4173.6 | 1226.1 | 0.68037 | 5.974
2024-12-10 | 4:27 | Data | 0 | 32.811 | 31.191 | 192.69 | 7.63 | 181.611 | 2227.95 | 25.75 | 42.116 | 6.33 | 1.37 | 4.607 | 8671.37 | 2.073 | 98.1 | 77.1 | 1448 | 21.01 | 5636.4 | 2914.6 | 2828.4 | 4176.6 | 1226.2 | 0.68124 | 5.978
2024-12-10 | 4:27 | Data | 0 | 32.73 | 30.651 | 192.736 | 7.63 | 181.566 | 2227.95 | 25.76 | 42.026 | 6.34 | 1.365 | 4.619 | 8671.37 | 2.073 | 98.1 | 77.2 | 1448 | 21.01 | 5636.4 | 2916 | 2812.7 | 4168.3 | 1226.2 | 0.68289 | 5.983
2024-12-10 | 4:27 | Data | 0 | 32.339 | 30.597 | 192.69 | 7.63 | 181.52 | 2227.95 | 25.76 | 42.116 | 6.34 | 1.359 | 4.613 | 8662.33 | 1.917 | 98.1 | 77.2 | 1448 | 21.06 | 5630.5 | 2915.9 | 2817.1 | 4170.1 | 1226.2 | 0.68292 | 5.972
2024-12-10 | 4:27 | Data | 0 | 32.919 | 30.664 | 192.736 | 7.63 | 181.611 | 2227.95 | 25.76 | 42.116 | 6.34 | 1.362 | 4.598 | 8680.41 | 2.228 | 98.1 | 77.1 | 1449 | 21.06 | 5642.3 | 2923.5 | 2851.6 | 4195.2 | 1226.2 | 0.67699 | 5.96
2024-12-10 | 4:27 | Data | 0 | 32.555 | 30.651 | 192.826 | 7.63 | 181.611 | 2227.04 | 25.76 | 42.206 | 6.33 | 1.363 | 4.609 | 8693.98 | 1.857 | 98.1 | 77.2 | 1448 | 21.1 | 5651.1 | 2917.3 | 2847.3 | 4191.6 | 1226.2 | 0.67834 | 5.972
2024-12-10 | 4:28 | Data | 0 | 32.926 | 30.874 | 192.736 | 7.63 | 181.566 | 2227.04 | 25.76 | 42.026 | 6.33 | 1.364 | 4.638 | 8693.98 | 2.073 | 98.1 | 77.3 | 1448 | 21.01 | 5651.1 | 2908.3 | 2836.3 | 4180.9 | 1226.2 | 0.67836 | 6.003
2024-12-10 | 4:28 | Data | 0 | 33.169 | 31.265 | 192.781 | 7.63 | 181.701 | 2228.85 | 25.76 | 42.116 | 6.33 | 1.37 | 4.615 | 8693.98 | 1.985 | 98.1 | 77.1 | 1449 | 21.06 | 5651.1 | 2921.1 | 2839.2 | 4188.5 | 1226.2 | 0.6792 | 5.983
2024-12-10 | 4:28 | Data | 0 | 32.501 | 30.664 | 192.6 | 7.63 | 181.52 | 2230.66 | 25.76 | 42.116 | 6.34 | 1.371 | 4.591 | 8671.37 | 2.174 | 98.1 | 77 | 1449 | 21.06 | 5636.4 | 2932.4 | 2825.6 | 4189.5 | 1226.2 | 0.68262 | 5.96
2024-12-10 | 4:28 | Data | 0 | 32.723 | 30.651 | 192.736 | 7.63 | 181.475 | 2229.75 | 25.76 | 42.116 | 6.33 | 1.358 | 4.625 | 8671.37 | 2.073 | 98.1 | 77.3 | 1449 | 21.06 | 5636.4 | 2906.6 | 2831.3 | 4172.8 | 1226.2 | 0.67991 | 5.984
2024-12-10 | 4:28 | Data | 0 | 32.845 | 30.712 | 192.781 | 7.63 | 181.701 | 2229.75 | 25.77 | 42.116 | 6.34 | 1.357 | 4.611 | 8689.46 | 1.971 | 98.1 | 77.3 | 1450 | 21.06 | 5648.1 | 2934.4 | 2824 | 4173 | 1226.2 | 0.68559 | 5.969
2024-12-10 | 4:28 | Data | 0 | 32.723 | 30.853 | 192.826 | 7.63 | 181.566 | 2231.56 | 25.76 | 42.116 | 6.33 | 1.359 | 4.615 | 8693.98 | 2.012 | 98.1 | 77.2 | 1450 | 21.06 | 5651.1 | 2917.4 | 2837.3 | 4183.2 | 1226.2 | 0.67929 | 5.974
2024-12-10 | 4:28 | Data | 0 | 32.946 | 31.056 | 192.736 | 7.63 | 181.566 | 2230.66 | 25.76 | 42.116 | 6.33 | 1.355 | 4.607 | 8712.07 | 1.958 | 98.1 | 77.3 | 1450 | 21.06 | 5662.8 | 2914.9 | 2840 | 4186.8 | 1226.2 | 0.68251 | 5.961
2024-12-10 | 4:28 | Data | 0 | 32.892 | 30.894 | 192.826 | 7.63 | 181.566 | 2227.95 | 25.76 | 42.116 | 6.33 | 1.367 | 4.615 | 8716.59 | 2.147 | 98.1 | 77.2 | 1448 | 21.06 | 5665.8 | 2939.4 | 2843.6 | 4201 | 1226.2 | 0.68303 | 5.982
2024-12-10 | 4:28 | Data | 0 | 32.622 | 30.651 | 192.645 | 7.63 | 181.52 | 2227.95 | 25.76 | 42.116 | 6.34 | 1.371 | 4.611 | 8716.59 | 2.059 | 98.1 | 77.1 | 1448 | 21.06 | 5665.8 | 2928.8 | 2842.9 | 4195.1 | 1226.2 | 0.68138 | 5.981
2024-12-10 | 4:28 | Data | 0 | 32.609 | 30.597 | 192.645 | 7.63 | 181.43 | 2229.75 | 25.77 | 42.116 | 6.33 | 1.364 | 4.611 | 8712.07 | 2.073 | 98.1 | 77.2 | 1449 | 21.06 | 5662.8 | 2921.3 | 2848.7 | 4195.7 | 1226.2 | 0.68095 | 5.975
2024-12-10 | 4:28 | Data | 0 | 32.73 | 30.482 | 192.781 | 7.63 | 181.701 | 2227.95 | 25.76 | 42.116 | 6.33 | 1.358 | 4.615 | 8689.46 | 2.059 | 98.1 | 77.3 | 1448 | 21.06 | 5648.1 | 2925.4 | 2863 | 4206.2 | 1226.2 | 0.67856 | 5.972
2024-12-10 | 4:28 | Data | 0 | 33.048 | 30.718 | 192.781 | 7.63 | 181.611 | 2229.75 | 25.76 | 42.206 | 6.34 | 1.364 | 4.619 | 8721.11 | 2.079 | 98.1 | 77.2 | 1449 | 21.1 | 5668.7 | 2926.1 | 2849.4 | 4201.6 | 1226.2 | 0.67879 | 5.984
2024-12-10 | 4:28 | Data | 0 | 32.723 | 30.651 | 192.6 | 7.63 | 181.566 | 2230.66 | 25.77 | 42.026 | 6.33 | 1.364 | 4.611 | 8707.55 | 1.897 | 98.1 | 77.2 | 1449 | 21.01 | 5659.9 | 2932.8 | 2848.8 | 4202.9 | 1226.2 | 0.68105 | 5.976
2024-12-10 | 4:28 | Data | 0 | 32.777 | 30.826 | 192.781 | 7.63 | 181.566 | 2230.66 | 25.76 | 41.936 | 6.34 | 1.369 | 4.598 | 8703.03 | 2.079 | 98.1 | 77 | 1450 | 20.92 | 5657 | 2935.7 | 2848 | 4200 | 1226.2 | 0.68199 | 5.969
2024-12-10 | 4:28 | Data | 0 | 32.609 | 31.096 | 192.69 | 7.63 | 181.611 | 2224.33 | 25.76 | 42.206 | 6.33 | 1.371 | 4.593 | 8716.59 | 1.965 | 98.1 | 77 | 1446 | 21.1 | 5665.8 | 2919.2 | 2840 | 4187.5 | 1226.2 | 0.67748 | 5.963
2024-12-10 | 4:28 | Data | 0 | 32.629 | 30.651 | 192.736 | 7.63 | 181.611 | 2232.47 | 25.76 | 42.206 | 6.33 | 1.373 | 4.626 | 8693.98 | 1.877 | 98.1 | 77.1 | 1451 | 21.06 | 5651.1 | 2928.4 | 2851.1 | 4204.5 | 1226.2 | 0.67999 | 5.999
2024-12-10 | 4:28 | Data | 0 | 32.723 | 30.651 | 192.69 | 7.63 | 181.611 | 2233.37 | 25.76 | 42.116 | 6.33 | 1.362 | 4.614 | 8689.46 | 2.066 | 98.1 | 77.2 | 1452 | 21.06 | 5648.1 | 2924.6 | 2854.1 | 4203.8 | 1226.2 | 0.67904 | 5.977
2024-12-10 | 4:28 | Data | 0 | 32.615 | 30.678 | 192.736 | 7.63 | 181.566 | 2230.66 | 25.77 | 42.116 | 6.33 | 1.354 | 4.616 | 8693.98 | 1.904 | 98.1 | 77.3 | 1450 | 21.06 | 5651.1 | 2923.3 | 2861.7 | 4206 | 1226.2 | 0.67942 | 5.969
2024-12-10 | 4:29 | Data | 0 | 32.723 | 30.874 | 192.69 | 7.63 | 181.566 | 2235.18 | 25.76 | 41.575 | 6.33 | 1.348 | 4.614 | 8689.46 | 2.039 | 98.1 | 77.4 | 1453 | 20.74 | 5648.1 | 2936.7 | 2844.4 | 4203.7 | 1226.2 | 0.68194 | 5.962
2024-12-10 | 4:29 | Data | 0 | 32.588 | 30.442 | 192.826 | 7.63 | 181.52 | 2231.56 | 25.76 | 42.026 | 6.34 | 1.36 | 4.601 | 8689.46 | 1.843 | 98.1 | 77.2 | 1451 | 21.01 | 5648.1 | 2925.5 | 2882.9 | 4225 | 1226.2 | 0.67465 | 5.96
2024-12-10 | 4:29 | Data | 0 | 32.528 | 30.651 | 192.781 | 7.63 | 181.566 | 2235.18 | 25.76 | 42.116 | 6.33 | 1.37 | 4.626 | 8689.46 | 1.85 | 98.1 | 77.2 | 1453 | 21.06 | 5648.1 | 2932.6 | 2860.4 | 4210.4 | 1226.2 | 0.68003 | 5.997
2024-12-10 | 4:29 | Data | 0 | 32.872 | 30.685 | 192.781 | 7.63 | 181.611 | 2233.37 | 25.76 | 42.116 | 6.33 | 1.369 | 4.621 | 8684.94 | 1.877 | 98.1 | 77.1 | 1452 | 21.06 | 5645.2 | 2931.2 | 2843.6 | 4200.2 | 1226.2 | 0.68178 | 5.991
2024-12-10 | 4:29 | Data | 0 | 32.845 | 30.853 | 192.69 | 7.63 | 181.611 | 2228.85 | 25.76 | 42.116 | 6.33 | 1.367 | 4.596 | 8703.03 | 1.85 | 98.1 | 77.1 | 1449 | 21.01 | 5657 | 2922.6 | 2814 | 4173.9 | 1226.2 | 0.68309 | 5.961
2024-12-10 | 4:29 | Data | 0 | 32.75 | 30.651 | 192.736 | 7.63 | 181.566 | 2224.33 | 25.76 | 42.116 | 6.34 | 1.367 | 4.611 | 8707.55 | 2.073 | 98.1 | 77.1 | 1446 | 21.01 | 5659.9 | 2929.6 | 2837.3 | 4191.1 | 1226.2 | 0.68293 | 5.98
2024-12-10 | 4:29 | Data | 0 | 32.615 | 30.766 | 192.826 | 7.63 | 181.52 | 2225.23 | 25.76 | 42.026 | 6.33 | 1.364 | 4.58 | 8707.55 | 1.836 | 98.1 | 77.1 | 1446 | 21.06 | 5659.9 | 2924.2 | 2835.9 | 4191.3 | 1226.2 | 0.68133 | 5.944
2024-12-10 | 4:29 | Data | 0 | 32.723 | 30.894 | 192.917 | 7.63 | 181.701 | 2222.52 | 25.76 | 42.116 | 6.34 | 1.366 | 4.589 | 8698.5 | 2.208 | 98.1 | 77.1 | 1445 | 21.1 | 5654 | 2931 | 2855.1 | 4205.6 | 1226.2 | 0.68023 | 5.955
2024-12-10 | 4:29 | Data | 0 | 32.723 | 30.887 | 192.962 | 7.63 | 181.656 | 2224.33 | 25.76 | 42.206 | 6.33 | 1.365 | 4.628 | 8689.46 | 2.005 | 98.1 | 77.2 | 1446 | 21.1 | 5648.1 | 2919.9 | 2851.2 | 4198.5 | 1226.2 | 0.67902 | 5.994
2024-12-10 | 4:29 | Data | 0 | 32.514 | 30.691 | 192.69 | 7.63 | 181.566 | 2225.23 | 25.76 | 41.755 | 6.33 | 1.376 | 4.623 | 8671.37 | 1.958 | 98.1 | 77.1 | 1446 | 20.92 | 5636.4 | 2908.1 | 2840.6 | 4184.9 | 1226.2 | 0.67772 | 5.998
2024-12-10 | 4:29 | Data | 0 | 32.811 | 30.88 | 192.781 | 7.63 | 181.611 | 2225.23 | 25.76 | 41.845 | 6.33 | 1.37 | 4.625 | 8698.5 | 2.113 | 98.1 | 77.1 | 1446 | 20.92 | 5654 | 2916.3 | 2855 | 4198.8 | 1226.2 | 0.67692 | 5.996
2024-12-10 | 4:29 | Data | 0 | 32.494 | 30.651 | 192.736 | 7.63 | 181.43 | 2218.91 | 25.77 | 41.845 | 6.33 | 1.365 | 4.618 | 8689.46 | 2.019 | 98.1 | 77.2 | 1442 | 20.92 | 5648.1 | 2921.8 | 2828.2 | 4178 | 1226.2 | 0.6821 | 5.984
2024-12-10 | 4:29 | Data | 0 | 32.501 | 30.651 | 192.736 | 7.63 | 181.52 | 2224.33 | 25.76 | 41.845 | 6.33 | 1.366 | 4.603 | 8698.5 | 1.85 | 98.1 | 77.1 | 1445 | 20.92 | 5654 | 2930.7 | 2841.1 | 4200.2 | 1226.2 | 0.67901 | 5.969